“Additional HILL Characteristics Form”

| HILL Composition* |  |
| --- | --- |
| Motor A Percent of load consisting of 3-phase induction motors with low inertia (H=0.1 sec) driving constant torque loads. These motors are found in commercial/industrial air conditioning compressors and refrigeration systems (not National Electrical Manufactor Association (NEMA), design B). - Smaller 5-15 hp compressor motors typical of rooftop air conditioning units commonly found at grocery stores, consumer products, and malls. - Larger 200-500 hp compressor motors typical of large commercial buildings’ central cooling systems. | % |
| Motor B Percent of load consisting of 3-phase induction motors with high inertia (H=0.25-0.1 sec) driving loads whose torque is proportional to speed squared. These motors are found in commercial ventilation fans and air handling systems. - 5-25 hp fan motors which are normally NEMA, design B. | % |
| Motor C Percent of load consisting of 3-phase induction motors with low inertia (H=0.1-0.2 sec). This represents motors commonly found in commercial water circulation pumps in central cooling systems. - 5-25 hp pump motors which are usually NEMA, design B. | % |
| Motor D Percent of load consisting of 1-phase air conditioners. This represents motors commonly found residential single phase air conditioner. | % |
| Electronic Percent of load consisting of power electronic converters. These are constant active and reactive power loads that include, consumer electronics (Plasma and LED televisions, cell phones and tablets, clocks, radios, etc.), appliance (high efficiency appliances such as refrigerators, washing machines, etc.) and office equipment (printer, copy machines, servers, etc.). | % |
| Static Percent of load will be static. This represents electric ovens, water heaters, incandescent lighting, and all other loads whose behavior changes with voltage magnitude. | % |
| Total Load Percent= | 100 % |

- The listed load characteristics are parameters needed to perform simulations using the composite load model referenced in, “ NERC Technical Reference Document Dynamic Load Modeling, December 2016”.

| Composite Load Model (CLM) |  |
| --- | --- |
| Total installed load (kW) | kW |
| Total installed distributed generation (kW) | kW |
| Total installed low side capacitor bank demand (kVAr) | kVAr |
| Total synchronous motor load (kW) | kW |
| Motor start type |  |
| Motor speed control method |  |
| Data Center Load Information |  |
| Total rated load including IT, power distribution and cooling (kW) | kW |
| Overall data center power factor (Lead/Lag) | (Lead/Lag) |

| Data Center Load Percentage |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | Summer Daytime | Summer nighttime | Winter Daytime | Winter Nighttime |
| Computing/ Server load |  |  |  |  |
| Lighting Load |  |  |  |  |
| Power Distribution losses |  |  |  |  |
| Cooling Load |  |  |  |  |

| Data Center Cooling System |  |  |
| --- | --- | --- |
| Forced Cooling System | ☐ | None |
|  | ☐ | Computer Room Air Conditioners (CRACs) with internal compressors. |
|  | ☐ | Computer Room Air Handlers (CRAHs) with chilled water. |
|  | ☐ | Air-Handling Units (AHUs) dedicated to the data center space. |
|  | ☐ | Other: |
| Cooling system motor driven components | ☐ | Single-speed motors that are operated across the line (Motors connected directly to the AC supply) |
|  | ☐ | Motors controlled by variable/adjustable speed drives or electronically commuted motors (ECMs) |
|  | ☐ | Other: |

Data Center Voltage Performance

| Voltage sag level/duration at which the computer/server load disconnects from the utility system (these may transfer to a local UPS): | volts | sec |
| --- | --- | --- |
| Voltage sag level/duration at which the cooling load disconnects from the system (these may transfer to an emergency generator or local power source): | volts | sec |
| How are voltage sag levels measured for the disconnect action? | ☐ | Per phase |
|  | ☐ | 3-phase RMS |
| Voltage swell level/duration at which the computer/server load disconnects from the utility system (these may transfer to a local UPS): | volts | sec |
| Voltage swell level/duration at which the cooling load disconnects from the system (these may transfer to an emergency generator or local power source): | volts | sec |

| How are voltage swell levels measured for disconnect action? | ☐ | Per phase |
| --- | --- | --- |
|  | ☐ | 3-phase RMS |

| Data Center Frequency Performance |  |
| --- | --- |
| The lowest frequency at which the data center will disconnect from the system: | Hz |
| The highest frequency at which the data center will disconnect from the system: | Hz |

| Data Center Reconnection Method After Automatic Disconnect from Service Provider System |  |  |
| --- | --- | --- |
| Manual | ☐ | Yes |
|  | ☐ | No |

| Immediate Reconnect (No deliberate Time Delay) |  |  | ☐ | Yes | If Yes, Complete the below information. |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | ☐ | No |  |  |
| Vhigh: reconnect when voltage is below: | Volts |  |  | deadband |  | msec |
| Vlow: reconnect when voltage is above: | Volts |  |  | deadband |  | msec |
| fhigh: reconnect when frequency is below: | Hz |  |  | deadband |  | msec |
| flow: reconnect when frequency is above: | Hz |  |  | deadband |  | msec |
| Delayed Reconnect (No deliberate Time Delay) | ☐ | Yes |  | If Yes, Complete the below information. |  |  |
|  | ☐ | No |  |  |  |  |

| Time Delay after voltage is within acceptable limits to reconnect: | sec |  |  |
| --- | --- | --- | --- |
| Vhigh: reconnect when voltage is below: | Volts | deadband | msec |
| Vlow: reconnect when voltage is above: | Volts | deadband | msec |
| Time Delay after frequency is within acceptable limits to reconnect: | sec |  |  |
| fhigh: reconnect when frequency is below: | Hz | deadband | msec |
| flow: reconnect when frequency is above: | Hz | deadband | msec |

Reconnect Loading Process

| Is all load reconnect at once | ☐ | Yes |
| --- | --- | --- |
|  | ☐ | No |
| Continuous ramp rate for ramping to reconnect: | kW/sec |  |
| Number of steps for stepwise ramping to reconnect: | Step(s) |  |
| Load increase per step for stepwise ramping to reconnect: | kW/step |  |

Data Center Emergency Backup Power System Details

| Emergency Generator (EG) capacity: | kW |
| --- | --- |
| Duration of EG based on available fuel: | Hours |
| Battery Energy Storage System (BESS) discharge Capacity | kW |
| Duration of BESS discharge based on fully charged battery capacity | Hours |
| Percent of Data Center load which can be carried by EG and/or BESS: | % |

| Can the Data Center back up power system participate in demand response in a grid emergency or an ancillary service? | ☐ | Yes |
| --- | --- | --- |
|  | ☐ | No |
| In event of a planned or unplanned disconnection from the grid, can the Data Center be islanded and operate with EG and/or BESS? | ☐ | Yes |
|  | ☐ | No |
| What precent of the server farm load could be redistributed to redundant server sites across the world? |  |  |
| If the data center trips offline, what percent of the load will be transferred to other server farms? |  |  |
| How fast can load transfer be completed? |  |  |