Feasibility Study

For

Generation Interconnection

Request

GEN-2005-008

SPP Tariff Studies

(#GEN-2005-008)

September 8, 2005

Executive Summary

<OMITTED TEXT> (Customer) has requested a Feasibility Study for the purpose of interconnecting 130.5MW of wind generation within the service territory of OG&E Electric Services (OKGE) in Harper County Oklahoma. The proposed 138kV point of interconnection is at the existing Woodward 138-69kV Substation in Woodward County. This substation is owned by OKGE. The proposed in-service date is July 31, 2007.

Power flow analysis has indicated that for the powerflow cases studied, it is possible to interconnect the 130.5MW of generation with transmission system reinforcements within the local transmission system. Given the Point of Interconnection at an existing substation, there are additional requirements for interconnection including bus, breaker, switches, relaying, metering, etc. In order to maintain acceptable bus voltages in the local area, the Customer will need to install a staged 45.9MVAR capacitor bank switched at 34.5kV in the Customer’s substation. Dynamic Stability studies performed as part of the impact study will provide guidance as to whether the reactive compensation can be static or must be dynamic (such as a SVC).

The total cost for adding a new 138 terminal to the existing Woodward Substation, the required interconnection facility, is estimated at $473,276 given completed modifications to accommodate GEN-2005-006. Other Network Constraints in the American Electric Power West (AEPW), OKGE and Western Farmers Electric Cooperative (WFEC) systems that may be verified with a transmission service request and associated studies are listed in Table 3. These Network Constraints are in the local area of the new generation when this generation is sunk throughout the SPP footprint for the Energy Resource Interconnection request. With a defined source and sink in a Transmission Service Request, this list of Network Constraints will be refined and expanded to account for all Network Resource Interconnection Upgrade requirements.

In Table 4, a value of Available Transfer Capability (ATC) associated with each overloaded facility is included. These values may be used by the Customer for future analyses including the determination of lower generation capacity levels that may be installed. When transmission service associated with this interconnection is evaluated, the loading of the facilities listed in this table may be greater due to higher priority reservations. If the loading of a facility is higher, the level of ATC will be lower. When a facility is overloaded for more than 10 contingencies, then only the results with the 10 highest loadings may be included in this table.

There are several other proposed generation additions in the general area of the Customer’s facility. It was assumed in this preliminary analysis that these other projects within the AEPW, OKGE and WFEC service territories will be in service. Those previously queued projects that have advanced to nearly complete phases were included in this Feasibility Study. In the event that another request for a generation interconnection with a higher priority withdraws, then this request may have to be re-evaluated to determine the local Network Constraints.

Introduction

<OMITTED TEXT> (Customer) has requested a Feasibility Study for the purpose of interconnecting 130.5MW of wind generation in Harper County Oklahoma within the service territory of OKGE. The existing Woodward 138-69kV Substation is owned by OKGE, and the proposed generation interconnection is within OKGE. The proposed point of interconnection is at the existing Woodward Substation in Woodward County. The proposed in-service date is July 31, 2007.

Interconnection Facilities

The primary objective of this study is to identify the system problems associated with connecting the plant to the area transmission system. The Feasibility and other subsequent Interconnection Studies are designed to identify attachment facilities, Network Upgrades and other direct assignment facilities needed to accept power into the grid at the interconnection receipt point.

The requirements for interconnection consist of adding a new 138kV terminal in the existing Woodward 138-69kV Substation. This 138kV addition shall be constructed and maintained by OKGE. The Customer did not propose a route of its 138kV line to serve its 138-34.5kV facilities. It is assumed that obtaining all necessary right-of-way for the new OKGE 138kV substation facilities will not be a significant expense.

The total cost for OKGE to add a new 138kV terminal in the Woodward substation, the interconnection facility, is estimated at $473,276 given completed modifications to accommodate GEN-2005-006. Other Network Constraints in the AEPW, OKGE and WFEC systems that were identified are listed in Table 3. These estimates will be refined during the development of the impact study based on the final designs. This cost does not include building 138kV line from the Customer substation into the existing Woodward Substation. The Customer is responsible for this 138kV line up to the point of interconnection. This cost does not include the Customer’s 138-34.5kV substation and the cost estimate should be determined by the Customer.

The costs of interconnecting the facility to the OKGE transmission system are listed in Table 2.  These costs do not include any cost that might be associated with short circuit study results or dynamic stability study results.  These costs will be determined when and if a System Impact Study is conducted.

Table 1:  Direct Assignment Facilities

| Facility | ESTIMATED COST (2005 DOLLARS) |
| --- | --- |
| Customer – 138-34.5 kV Substation facilities, including a staged 34.5kV 45.9MVAR switched capacitor bank. | * |
| Customer – 138kV line between Customer substation and upgraded OKGE 138kV Woodward Substation. | * |
| Customer - Right-of-Way for Customer Substation & Line. | * |
| Total | * |

Note:  *Estimates of cost to be determined by Customer.

Table 2:  Required Interconnection Network Upgrade Facilities

| Facility | ESTIMATED COST (2005 DOLLARS) |
| --- | --- |
| OKGE - Add a single 138kV terminal in the existing Woodward 138-69kV Substation. | $473,276 |
| OKGE - Right-of-Way for 138kV terminal addition | 0 |
| Total | $473,276 |

Table 3:  Network Constraints

Facility

AEPW - ELK CITY - *2002-05T 138kV in base case.

OKGE - FPL SWITCH - MOORELAND 138kV in base case.

WFEC - FPL SWITCH - MOORELAND 138kV in base case.

OKGE - GLASS MOUNTAIN - MOORELAND 138kV in base case.

WFEC - GLASS MOUNTAIN - MOORELAND 138kV in base case.

OKGE - KNOBHILL 138-69kV in base case.

OKGE - ALVA - KNOBHILL 69kV

WFEC - BRANTLEY - MORWOOD 69kV

WFEC - BUFFALO - FT SUPPLY 69kV

WFEC - CANTON - OKEENE 69kV

WFEC - CANTON - TALOGA 69kV

WFEC - CARTER JCT - ERICK 69kV

WFEC - CEDARDALE - MOORELAND 138kV

WFEC - CEDARDALE - OKEENE 138kV

OKGE - CLEO CORNER - GLASS MOUNTAIN 138kV

WFEC - DOVER SW - OKEENE 138kV

OKGE - EL RENO - ROMAN NOSE 138kV

WFEC - EL RENO SW - EL RENO 69kV

AEPW - ELK CITY - *2002-05T 138kV

OKGE - FPL SWITCH - MOORELAND 138kV

WFEC - FPL SWITCH - MOORELAND 138kV

OKGE - GLASS MOUNTAIN - MOORELAND 138kV

WFEC - GLASS MOUNTAIN - MOORELAND 138kV

WFEC - HAMON BUTLER - MOREWOOD 69kV

OKGE - KNOBHILL - KNOBHIL4 138-69kV

WFEC - MOORELAND - WOODWARD 69kV

WFEC - MOORELAND 138-69kV

WFEC - MOREWOOD - MOREWOOD SW 138-69kV

Table 3:  Network Constraints

Facility

OKGE - SOUTHARD - ROMAN NOSE 138kV

WFEC - TALOGA 138-69kV

OKGE - WOODWARD - FPL SWITCH 138kV

OKGE - WOODWARD 138-69kV

OKGE - WOODWARD 69kV

WFEC - WOODWARD 69kV

Table 4:  Contingency Analysis Results

| Facility | Model & Contingency | Facility Loading (% Rate B) Or Voltage (PU) | ATC (MW) | Date Required (M/D/Y) |
| --- | --- | --- | --- | --- |
| ELK CITY - *2002-05T 138kV | 07SP, Base Case | 134.5 | 0 | 7/31/2007 |
| ELK CITY - *2002-05T 138kV | 10SP, Base Case | 132.8 | 0 |  |
| ELK CITY - *2002-05T 138kV | 15SP, Base Case | 127.5 | 0 |  |
| ELK CITY - *2002-05T 138kV | 10WP, Base Case | 115.0 | 25 |  |
| ELK CITY - *2002-05T 138kV | 06AP, Base Case | 105.4 | 89 |  |
| ELK CITY - *2002-05T 138kV | 07WP, Base Case | 103.3 | 106 |  |
| FPL SWITCH - MOORELAND 138kV | 06AP, Base Case | 271.1 | 0 | 7/31/2007 |
| FPL SWITCH - MOORELAND 138kV | 07WP, Base Case | 248.1 | 0 |  |
| FPL SWITCH - MOORELAND 138kV | 10WP, Base Case | 242.9 | 0 |  |
| FPL SWITCH - MOORELAND 138kV | 07SP, Base Case | 216.0 | 0 |  |
| FPL SWITCH - MOORELAND 138kV | 10SP, Base Case | 215.9 | 0 |  |
| FPL SWITCH - MOORELAND 138kV | 15SP, Base Case | 214.4 | 0 |  |
| GLASS MOUNTAIN - MOORELAND 138kV | 15SP, Base Case | 116.6 | 39 | 7/31/2007 |
| GLASS MOUNTAIN - MOORELAND 138kV | 10SP, Base Case | 116.2 | 41 |  |
| GLASS MOUNTAIN - MOORELAND 138kV | 07SP, Base Case | 115.8 | 44 |  |
| GLASS MOUNTAIN - MOORELAND 138kV | 10WP, Base Case | 103.2 | 112 |  |
| KNOBHILL - KNOBHIL4 138-( )kV | 15SP, Base Case | 109.9 | 22 | 7/31/2007 |
| KNOBHILL - KNOBHIL4 138-( )kV | 10SP, Base Case | 108.5 | 37 |  |
| KNOBHILL - KNOBHIL4 138-( )kV | 07SP, Base Case | 108.0 | 43 |  |
| KNOBHILL - KNOBHIL4 69-( )kV | 15SP, Base Case | 111.9 | 3 |  |
| KNOBHILL - KNOBHIL4 69-( )kV | 10SP, Base Case | 110.5 | 18 |  |
| KNOBHILL - KNOBHIL4 69-( )kV | 07SP, Base Case | 110.0 | 25 |  |

Note:  When transmission service associated with this interconnection is evaluated, the loading of the facilities listed in this table may be greater due to higher priority reservations. If the loading of a facility is higher, the level of ATC will be lower.

Table 4:  Contingency Analysis Results

| Facility | Model & Contingency | Facility Loading (% Rate B) Or Voltage (PU) | ATC (MW) | Date Required (M/D/Y) |
| --- | --- | --- | --- | --- |
| ALVA - KNOBHILL 69kV | 15SP, 54788-55999, OKGE ENID - WFEC AEP-OP , GLASS MOUNTAIN - MOORELAND 138kV | 124.5 | 0 | 7/31/2007 |
| ALVA - KNOBHILL 69kV | 15SP, 54778-54788, OKGE ENID , CLEO CORNER - GLASS MOUNTAIN 138kV | 123.4 | 0 |  |
| ALVA - KNOBHILL 69kV | 10SP, 54788-55999, OKGE ENID - WFEC AEP-OP , GLASS MOUNTAIN - MOORELAND 138kV | 121.4 | 0 |  |
| ALVA - KNOBHILL 69kV | 10SP, 54778-54788, OKGE ENID , CLEO CORNER - GLASS MOUNTAIN 138kV | 120.3 | 0 |  |
| ALVA - KNOBHILL 69kV | 07SP, 54788-55999, OKGE ENID - WFEC AEP-OP , GLASS MOUNTAIN - MOORELAND 138kV | 118.8 | 0 |  |
| ALVA - KNOBHILL 69kV | 07SP, 54778-54788, OKGE ENID , CLEO CORNER - GLASS MOUNTAIN 138kV | 117.7 | 0 |  |
| ALVA - KNOBHILL 69kV | 15SP, 54716-54794, OKGE ENID , SALINE - KNOBHILL 69kV | 111.9 | 0 |  |
| ALVA - KNOBHILL 69kV | 15SP, 54716-54720, OKGE ENID , SALINE - GOLTRY 69kV | 108.9 | 32 |  |
| ALVA - KNOBHILL 69kV | 10SP, 54716-54794, OKGE ENID , SALINE - KNOBHILL 69kV | 108.8 | 31 |  |
| ALVA - KNOBHILL 69kV | 07SP, 54716-54794, OKGE ENID , SALINE - KNOBHILL 69kV | 106.9 | 54 |  |
| BRANTLEY - MORWOOD 69kV | 07SP, 54121-99940, AEPW WESTERN - , ELK CITY - 2002-05T 138kV | 127.9 | 0 | 7/31/2007 |
| BRANTLEY - MORWOOD 69kV | 10SP, 54121-99940, AEPW WESTERN - , ELK CITY - 2002-05T 138kV | 127.3 | 0 |  |
| BRANTLEY - MORWOOD 69kV | 15SP, 54121-99940, AEPW WESTERN - , ELK CITY - 2002-05T 138kV | 121.2 | 0 |  |
| BRANTLEY - MORWOOD 69kV | 10WP, 54121-99940, AEPW WESTERN - , ELK CITY - 2002-05T 138kV | 108.5 | 64 |  |

Note:  When transmission service associated with this interconnection is evaluated, the loading of the facilities listed in this table may be greater due to higher priority reservations. If the loading of a facility is higher, the level of ATC will be lower.

Table 4:  Contingency Analysis Results

| Facility | Model & Contingency | Facility Loading (% Rate B) Or Voltage (PU) | ATC (MW) | Date Required (M/D/Y) |
| --- | --- | --- | --- | --- |
| BUFFALO - FT SUPPLY 69kV | 15SP, 54794-54795-55732, OKGE ENID , KNOBHILL - KNOBHILL 138-69kV | 110.2 | 33 | 7/31/2007 |
| BUFFALO - FT SUPPLY 69kV | 15SP, 54795-55999, OKGE ENID - WFEC AEP-OP , KNOBHILL - MOORELAND 138kV | 110.1 | 32 |  |
| BUFFALO - FT SUPPLY 69kV | 10SP, 54795-55999, OKGE ENID - WFEC AEP-OP , KNOBHILL - MOORELAND 138kV | 109.0 | 42 |  |
| BUFFALO - FT SUPPLY 69kV | 10SP, 54794-54795-55732, OKGE ENID , KNOBHILL - KNOBHILL 138-69kV | 108.9 | 42 |  |
| BUFFALO - FT SUPPLY 69kV | 07SP, 54795-55999, OKGE ENID - WFEC AEP-OP , KNOBHILL - MOORELAND 138kV | 108.2 | 50 |  |
| BUFFALO - FT SUPPLY 69kV | 07SP, 54794-54795-55732, OKGE ENID , KNOBHILL - KNOBHILL 138-69kV | 108.0 | 51 |  |
| CANTON - OKEENE 69kV | 07SP, 55848-55999, WFEC AEP-OP , CEDARDALE - MOORELAND 138kV | 106.5 | 89 | 7/31/2007 |
| CANTON - OKEENE 69kV | 10SP, 55848-55999, WFEC AEP-OP , CEDARDALE - MOORELAND 138kV | 106.5 | 89 |  |
| CANTON - OKEENE 69kV | 07SP, 55848-56016, WFEC AEP-OP - WFEC AEP-IM , CEDARDALE - OKEENE 138kV | 105.0 | 98 |  |
| CANTON - OKEENE 69kV | 10SP, 55848-56016, WFEC AEP-OP - WFEC AEP-IM , CEDARDALE - OKEENE 138kV | 105.0 | 98 |  |
| CANTON - OKEENE 69kV | 15SP, 55848-55999, WFEC AEP-OP , CEDARDALE - MOORELAND 138kV | 104.4 | 101 |  |
| CANTON - OKEENE 69kV | 15SP, 55848-56016, WFEC AEP-OP - WFEC AEP-IM , CEDARDALE - OKEENE 138kV | 103.0 | 110 |  |

Note:  When transmission service associated with this interconnection is evaluated, the loading of the facilities listed in this table may be greater due to higher priority reservations. If the loading of a facility is higher, the level of ATC will be lower.

Table 4:  Contingency Analysis Results

| Facility | Model & Contingency | Facility Loading (% Rate B) Or Voltage (PU) | ATC (MW) | Date Required (M/D/Y) |
| --- | --- | --- | --- | --- |
| CANTON - TALOGA 69kV | 10SP, 55848-55999, WFEC AEP-OP , CEDARDALE - MOORELAND 138kV | 111.1 | 58 | 7/31/2007 |
| CANTON - TALOGA 69kV | 07SP, 55848-55999, WFEC AEP-OP , CEDARDALE - MOORELAND 138kV | 110.9 | 59 |  |
| CANTON - TALOGA 69kV | 15SP, 55848-55999, WFEC AEP-OP , CEDARDALE - MOORELAND 138kV | 110.9 | 59 |  |
| CANTON - TALOGA 69kV | 10SP, 55848-56016, WFEC AEP-OP - WFEC AEP-IM , CEDARDALE - OKEENE 138kV | 109.6 | 67 |  |
| CANTON - TALOGA 69kV | 07SP, 55848-56016, WFEC AEP-OP - WFEC AEP-IM , CEDARDALE - OKEENE 138kV | 109.5 | 68 |  |
| CANTON - TALOGA 69kV | 15SP, 55848-56016, WFEC AEP-OP - WFEC AEP-IM , CEDARDALE - OKEENE 138kV | 109.5 | 68 |  |
| CANTON - TALOGA 69kV | 10WP, 55848-55999, WFEC AEP-OP , CEDARDALE - MOORELAND 138kV | 100.6 | 127 |  |
| CARTER JCT - ERICK 69kV | 07SP, 54121-99940, AEPW WESTERN - , ELK CITY - 2002-05T 138kV | 137.8 | 0 | 7/31/2007 |
| CARTER JCT - ERICK 69kV | 10SP, 54121-99940, AEPW WESTERN - , ELK CITY - 2002-05T 138kV | 135.1 | 0 |  |
| CARTER JCT - ERICK 69kV | 15SP, 54121-99940, AEPW WESTERN - , ELK CITY - 2002-05T 138kV | 126.2 | 0 |  |
| CARTER JCT - ERICK 69kV | 10WP, 54121-99940, AEPW WESTERN - , ELK CITY - 2002-05T 138kV | 115.8 | 45 |  |
| CARTER JCT - ERICK 69kV | 06AP, 54121-99940, AEPW WESTERN - , ELK CITY - 2002-05T 138kV | 103.8 | 109 |  |
| CARTER JCT - ERICK 69kV | 07WP, 54121-99940, AEPW WESTERN - , ELK CITY - 2002-05T 138kV | 101.4 | 122 |  |

Note:  When transmission service associated with this interconnection is evaluated, the loading of the facilities listed in this table may be greater due to higher priority reservations. If the loading of a facility is higher, the level of ATC will be lower.

Table 4:  Contingency Analysis Results

| Facility | Model & Contingency | Facility Loading (% Rate B) Or Voltage (PU) | ATC (MW) | Date Required (M/D/Y) |
| --- | --- | --- | --- | --- |
| CEDARDALE - MOORELAND 138kV | 07SP, 54121-99940, AEPW WESTERN - , ELK CITY - 2002-05T 138kV | 103.4 | 106 | 7/31/2007 |
| CEDARDALE - MOORELAND 138kV | 10SP, 54121-99940, AEPW WESTERN - , ELK CITY - 2002-05T 138kV | 103.0 | 109 |  |
| CEDARDALE - MOORELAND 138kV | 15SP, 54121-99940, AEPW WESTERN - , ELK CITY - 2002-05T 138kV | 101.4 | 120 |  |
| CEDARDALE - OKEENE 138kV | 07SP, 54121-99940, AEPW WESTERN - , ELK CITY - 2002-05T 138kV | 101.4 | 120 | 7/31/2007 |
| CEDARDALE - OKEENE 138kV | 10SP, 54121-99940, AEPW WESTERN - , ELK CITY - 2002-05T 138kV | 100.9 | 124 |  |
| CLEO CORNER - GLASS MOUNTAIN 138kV | 07SP, 54121-99940, AEPW WESTERN - , ELK CITY - 2002-05T 138kV | 127.2 | 0 | 7/31/2007 |
| CLEO CORNER - GLASS MOUNTAIN 138kV | 10SP, 54121-99940, AEPW WESTERN - , ELK CITY - 2002-05T 138kV | 126.9 | 0 |  |
| CLEO CORNER - GLASS MOUNTAIN 138kV | 15SP, 54121-99940, AEPW WESTERN - , ELK CITY - 2002-05T 138kV | 125.4 | 0 |  |
| CLEO CORNER - GLASS MOUNTAIN 138kV | 10SP, 54787-54822, OKGE ENID - OKGE METRO , DEWEY - SOUTHARD 138kV | 115.5 | 39 |  |
| CLEO CORNER - GLASS MOUNTAIN 138kV | 07SP, 54787-54822, OKGE ENID - OKGE METRO , DEWEY - SOUTHARD 138kV | 115.2 | 41 |  |
| CLEO CORNER - GLASS MOUNTAIN 138kV | 15SP, 54787-54822, OKGE ENID - OKGE METRO , DEWEY - SOUTHARD 138kV | 114.6 | 44 |  |
| CLEO CORNER - GLASS MOUNTAIN 138kV | 10SP, 55848-55999, WFEC AEP-OP , CEDARDALE - MOORELAND 138kV | 113.7 | 44 |  |
| CLEO CORNER - GLASS MOUNTAIN 138kV | 15SP, 55848-55999, WFEC AEP-OP , CEDARDALE - MOORELAND 138kV | 113.5 | 45 |  |
| CLEO CORNER - GLASS MOUNTAIN 138kV | 07SP, 55848-55999, WFEC AEP-OP , CEDARDALE - MOORELAND 138kV | 113.3 | 46 |  |
| CLEO CORNER - GLASS MOUNTAIN 138kV | 10SP, 55848-56016, WFEC AEP-OP - WFEC AEP-IM , CEDARDALE - OKEENE 138kV | 113.1 | 48 |  |

Note:  When transmission service associated with this interconnection is evaluated, the loading of the facilities listed in this table may be greater due to higher priority reservations. If the loading of a facility is higher, the level of ATC will be lower.

Table 4:  Contingency Analysis Results

| Facility | Model & Contingency | Facility Loading (% Rate B) Or Voltage (PU) | ATC (MW) | Date Required (M/D/Y) |
| --- | --- | --- | --- | --- |
| DOVER SW - OKEENE 138kV | 07SP, 54121-99940, AEPW WESTERN - , ELK CITY - 2002-05T 138kV | 125.7 | 4 | 7/31/2007 |
| DOVER SW - OKEENE 138kV | 10SP, 54121-99940, AEPW WESTERN - , ELK CITY - 2002-05T 138kV | 124.8 | 9 |  |
| DOVER SW - OKEENE 138kV | 15SP, 54121-99940, AEPW WESTERN - , ELK CITY - 2002-05T 138kV | 122.2 | 20 |  |
| DOVER SW - OKEENE 138kV | 07SP, 54778-54789, OKGE ENID , CLEO CORNER - MEN TAP 138kV | 119.8 | 32 |  |
| DOVER SW - OKEENE 138kV | 10SP, 54778-54789, OKGE ENID , CLEO CORNER - MEN TAP 138kV | 119.3 | 34 |  |
| DOVER SW - OKEENE 138kV | 15SP, 54778-54789, OKGE ENID , CLEO CORNER - MEN TAP 138kV | 118.6 | 38 |  |
| DOVER SW - OKEENE 138kV | 07SP, 54789-54790, OKGE ENID , MEN TAP - IMO TAP 138kV | 118.6 | 38 |  |
| DOVER SW - OKEENE 138kV | 10SP, 54789-54790, OKGE ENID , MEN TAP - IMO TAP 138kV | 118.0 | 41 |  |
| DOVER SW - OKEENE 138kV | 15SP, 54789-54790, OKGE ENID , MEN TAP - IMO TAP 138kV | 117.1 | 45 |  |
| DOVER SW - OKEENE 138kV | 07SP, 54788-55999, OKGE ENID - WFEC AEP-OP , GLASS MOUNTAIN - MOORELAND 138kV | 116.0 | 45 |  |
| EL RENO - ROMAN NOSE 138kV | 07SP, 54121-99940, AEPW WESTERN - , ELK CITY - 2002-05T 138kV | 112.3 | 69 | 7/31/2007 |
| EL RENO - ROMAN NOSE 138kV | 10SP, 54121-99940, AEPW WESTERN - , ELK CITY - 2002-05T 138kV | 112.0 | 70 |  |
| EL RENO - ROMAN NOSE 138kV | 15SP, 54121-99940, AEPW WESTERN - , ELK CITY - 2002-05T 138kV | 105.4 | 103 |  |
| EL RENO SW - EL RENO 69kV | 10SP, 54787-54822, OKGE ENID - OKGE METRO , DEWEY - SOUTHARD 138kV | 102.7 | 113 | 6/1/2008 |
| EL RENO SW - EL RENO 69kV | 15SP, 54787-54822, OKGE ENID - OKGE METRO , DEWEY - SOUTHARD 138kV | 100.5 | 127 |  |

Note:  When transmission service associated with this interconnection is evaluated, the loading of the facilities listed in this table may be greater due to higher priority reservations. If the loading of a facility is higher, the level of ATC will be lower.

Table 4:  Contingency Analysis Results

| Facility | Model & Contingency | Facility Loading (% Rate B) Or Voltage (PU) | ATC (MW) | Date Required (M/D/Y) |
| --- | --- | --- | --- | --- |
| ELK CITY - *2002-05T 138kV | 07SP, 54787-54822, OKGE ENID - OKGE METRO , DEWEY - SOUTHARD 138kV | 163.5 | 0 | 7/31/2007 |
| ELK CITY - *2002-05T 138kV | 10SP, 54787-54822, OKGE ENID - OKGE METRO , DEWEY - SOUTHARD 138kV | 161.9 | 0 |  |
| ELK CITY - *2002-05T 138kV | 07SP, 54822-54823, OKGE METRO , SOUTHARD - ROMAN NOSE 138kV | 159.9 | 0 |  |
| ELK CITY - *2002-05T 138kV | 07SP, 54778-54789, OKGE ENID , CLEO CORNER - MEN TAP 138kV | 158.2 | 0 |  |
| ELK CITY - *2002-05T 138kV | 10SP, 54822-54823, OKGE METRO , SOUTHARD - ROMAN NOSE 138kV | 158.1 | 0 |  |
| ELK CITY - *2002-05T 138kV | 07SP, 54788-55999, OKGE ENID - WFEC AEP-OP , GLASS MOUNTAIN - MOORELAND 138kV | 157.8 | 0 |  |
| ELK CITY - *2002-05T 138kV | 07SP, 54789-54790, OKGE ENID , MEN TAP - IMO TAP 138kV | 157.3 | 0 |  |
| ELK CITY - *2002-05T 138kV | 07SP, 54778-54788, OKGE ENID , CLEO CORNER - GLASS MOUNTAIN 138kV | 157.2 | 0 |  |
| ELK CITY - *2002-05T 138kV | 07SP, 54819-54823, OKGE METRO , EL RENO - ROMAN NOSE 138kV | 157.1 | 0 |  |
| ELK CITY - *2002-05T 138kV | 10SP, 54778-54789, OKGE ENID , CLEO CORNER - MEN TAP 138kV | 156.3 | 0 |  |

Note:  When transmission service associated with this interconnection is evaluated, the loading of the facilities listed in this table may be greater due to higher priority reservations. If the loading of a facility is higher, the level of ATC will be lower.

Table 4:  Contingency Analysis Results

| Facility | Model & Contingency | Facility Loading (% Rate B) Or Voltage (PU) | ATC (MW) | Date Required (M/D/Y) |
| --- | --- | --- | --- | --- |
| FPL SWITCH - MOORELAND 138kV | 06AP, 54785-54796, OKGE ENID , WOODWARD - IODINE 138kV | 343.0 | 0 | 7/31/2007 |
| FPL SWITCH - MOORELAND 138kV | 06AP, 54787-54796, OKGE ENID , DEWEY - IODINE 138kV | 341.1 | 0 |  |
| FPL SWITCH - MOORELAND 138kV | 10WP, 54785-54796, OKGE ENID , WOODWARD - IODINE 138kV | 324.1 | 0 |  |
| FPL SWITCH - MOORELAND 138kV | 07WP, 54785-54796, OKGE ENID , WOODWARD - IODINE 138kV | 323.8 | 0 |  |
| FPL SWITCH - MOORELAND 138kV | 10WP, 54787-54796, OKGE ENID , DEWEY - IODINE 138kV | 320.6 | 0 |  |
| FPL SWITCH - MOORELAND 138kV | 07WP, 54787-54796, OKGE ENID , DEWEY - IODINE 138kV | 320.2 | 0 |  |
| FPL SWITCH - MOORELAND 138kV | 06AP, 54782-54785-55771, OKGE ENID , WOODWARD 138-69kV | 314.0 | 0 |  |
| FPL SWITCH - MOORELAND 138kV | 10SP, 54785-54796, OKGE ENID , WOODWARD - IODINE 138kV | 303.2 | 0 |  |
| FPL SWITCH - MOORELAND 138kV | 07SP, 54785-54796, OKGE ENID , WOODWARD - IODINE 138kV | 303.1 | 0 |  |
| FPL SWITCH - MOORELAND 138kV | 07WP, 54782-54785-55771, OKGE ENID , WOODWARD 138-69kV | 302.7 | 0 |  |

Note:  When transmission service associated with this interconnection is evaluated, the loading of the facilities listed in this table may be greater due to higher priority reservations. If the loading of a facility is higher, the level of ATC will be lower.

Table 4:  Contingency Analysis Results

| Facility | Model & Contingency | Facility Loading (% Rate B) Or Voltage (PU) | ATC (MW) | Date Required (M/D/Y) |
| --- | --- | --- | --- | --- |
| GLASS MOUNTAIN - MOORELAND 138kV | 07SP, 54121-99940, AEPW WESTERN - , ELK CITY - 2002-05T 138kV | 159.8 | 0 | 7/31/2007 |
| GLASS MOUNTAIN - MOORELAND 138kV | 10SP, 54121-99940, AEPW WESTERN - , ELK CITY - 2002-05T 138kV | 159.5 | 0 |  |
| GLASS MOUNTAIN - MOORELAND 138kV | 15SP, 54121-99940, AEPW WESTERN - , ELK CITY - 2002-05T 138kV | 157.9 | 0 |  |
| GLASS MOUNTAIN - MOORELAND 138kV | 10SP, 54787-54822, OKGE ENID - OKGE METRO , DEWEY - SOUTHARD 138kV | 145.5 | 0 |  |
| GLASS MOUNTAIN - MOORELAND 138kV | 07SP, 54787-54822, OKGE ENID - OKGE METRO , DEWEY - SOUTHARD 138kV | 145.0 | 0 |  |
| GLASS MOUNTAIN - MOORELAND 138kV | 15SP, 54787-54822, OKGE ENID - OKGE METRO , DEWEY - SOUTHARD 138kV | 144.6 | 0 |  |
| GLASS MOUNTAIN - MOORELAND 138kV | 10SP, 55848-55999, WFEC AEP-OP , CEDARDALE - MOORELAND 138kV | 143.2 | 0 |  |
| GLASS MOUNTAIN - MOORELAND 138kV | 15SP, 55848-55999, WFEC AEP-OP , CEDARDALE - MOORELAND 138kV | 143.2 | 0 |  |
| GLASS MOUNTAIN - MOORELAND 138kV | 07SP, 55848-55999, WFEC AEP-OP , CEDARDALE - MOORELAND 138kV | 142.7 | 0 |  |
| GLASS MOUNTAIN - MOORELAND 138kV | 15SP, 55848-56016, WFEC AEP-OP - WFEC AEP-IM , CEDARDALE - OKEENE 138kV | 142.6 | 0 |  |

Note:  When transmission service associated with this interconnection is evaluated, the loading of the facilities listed in this table may be greater due to higher priority reservations. If the loading of a facility is higher, the level of ATC will be lower.

Table 4:  Contingency Analysis Results

| Facility | Model & Contingency | Facility Loading (% Rate B) Or Voltage (PU) | ATC (MW) | Date Required (M/D/Y) |
| --- | --- | --- | --- | --- |
| HAMON BUTLER - MOREWOOD 69kV | 07SP, 55999-56001, WFEC AEP-OP - WFEC AEP-CS , MOORELAND - MOREWOOD SW 138kV | 145.7 | 0 | 7/31/2007 |
| HAMON BUTLER - MOREWOOD 69kV | 10SP, 55999-56001, WFEC AEP-OP - WFEC AEP-CS , MOORELAND - MOREWOOD SW 138kV | 142.0 | 1 |  |
| HAMON BUTLER - MOREWOOD 69kV | 15SP, 55999-56001, WFEC AEP-OP - WFEC AEP-CS , MOORELAND - MOREWOOD SW 138kV | 129.9 | 38 |  |
| HAMON BUTLER - MOREWOOD 69kV | 10WP, 55999-56001, WFEC AEP-OP - WFEC AEP-CS , MOORELAND - MOREWOOD SW 138kV | 103.6 | 119 |  |
| KNOBHILL - KNOBHIL4 138-( )kV | 15SP, 54788-55999, OKGE ENID - WFEC AEP-OP , GLASS MOUNTAIN - MOORELAND 138kV | 148.4 | 0 | 7/31/2007 |
| KNOBHILL - KNOBHIL4 138-( )kV | 15SP, 54778-54788, OKGE ENID , CLEO CORNER - GLASS MOUNTAIN 138kV | 147.4 | 0 |  |
| KNOBHILL - KNOBHIL4 138-( )kV | 10SP, 54788-55999, OKGE ENID - WFEC AEP-OP , GLASS MOUNTAIN - MOORELAND 138kV | 147.0 | 0 |  |
| KNOBHILL - KNOBHIL4 138-( )kV | 07SP, 54788-55999, OKGE ENID - WFEC AEP-OP , GLASS MOUNTAIN - MOORELAND 138kV | 146.3 | 0 |  |
| KNOBHILL - KNOBHIL4 138-( )kV | 10SP, 54778-54788, OKGE ENID , CLEO CORNER - GLASS MOUNTAIN 138kV | 146.1 | 0 |  |
| KNOBHILL - KNOBHIL4 138-( )kV | 07SP, 54778-54788, OKGE ENID , CLEO CORNER - GLASS MOUNTAIN 138kV | 145.4 | 0 |  |
| KNOBHILL - KNOBHIL4 138-( )kV | 15SP, 54121-99940, AEPW WESTERN - , ELK CITY - 2002-05T 138kV | 131.9 | 0 |  |
| KNOBHILL - KNOBHIL4 138-( )kV | 10SP, 54121-99940, AEPW WESTERN - , ELK CITY - 2002-05T 138kV | 131.5 | 0 |  |
| KNOBHILL - KNOBHIL4 138-( )kV | 07SP, 54121-99940, AEPW WESTERN - , ELK CITY - 2002-05T 138kV | 131.4 | 0 |  |
| KNOBHILL - KNOBHIL4 138-( )kV | 15SP, 55848-55999, WFEC AEP-OP , CEDARDALE - MOORELAND 138kV | 131.2 | 0 |  |

Note:  When transmission service associated with this interconnection is evaluated, the loading of the facilities listed in this table may be greater due to higher priority reservations. If the loading of a facility is higher, the level of ATC will be lower.

Table 4:  Contingency Analysis Results

| Facility | Model & Contingency | Facility Loading (% Rate B) Or Voltage (PU) | ATC (MW) | Date Required (M/D/Y) |
| --- | --- | --- | --- | --- |
| KNOBHILL - KNOBHIL4 69-( )kV | 15SP, 54788-55999, OKGE ENID - WFEC AEP-OP , GLASS MOUNTAIN - MOORELAND 138kV | 152.7 | 0 |  |
| KNOBHILL - KNOBHIL4 69-( )kV | 15SP, 54778-54788, OKGE ENID , CLEO CORNER - GLASS MOUNTAIN 138kV | 151.7 | 0 |  |
| KNOBHILL - KNOBHIL4 69-( )kV | 10SP, 54788-55999, OKGE ENID - WFEC AEP-OP , GLASS MOUNTAIN - MOORELAND 138kV | 151.3 | 0 |  |
| KNOBHILL - KNOBHIL4 69-( )kV | 07SP, 54788-55999, OKGE ENID - WFEC AEP-OP , GLASS MOUNTAIN - MOORELAND 138kV | 150.7 | 0 |  |
| KNOBHILL - KNOBHIL4 69-( )kV | 10SP, 54778-54788, OKGE ENID , CLEO CORNER - GLASS MOUNTAIN 138kV | 150.4 | 0 |  |
| KNOBHILL - KNOBHIL4 69-( )kV | 07SP, 54778-54788, OKGE ENID , CLEO CORNER - GLASS MOUNTAIN 138kV | 149.7 | 0 |  |
| KNOBHILL - KNOBHIL4 69-( )kV | 15SP, 54121-99940, AEPW WESTERN - , ELK CITY - 2002-05T 138kV | 134.1 | 0 |  |
| KNOBHILL - KNOBHIL4 69-( )kV | 10SP, 54121-99940, AEPW WESTERN - , ELK CITY - 2002-05T 138kV | 133.7 | 0 |  |
| KNOBHILL - KNOBHIL4 69-( )kV | 07SP, 54121-99940, AEPW WESTERN - , ELK CITY - 2002-05T 138kV | 133.6 | 0 |  |
| KNOBHILL - KNOBHIL4 69-( )kV | 15SP, 55848-55999, WFEC AEP-OP , CEDARDALE - MOORELAND 138kV | 133.6 | 0 |  |

Note:  When transmission service associated with this interconnection is evaluated, the loading of the facilities listed in this table may be greater due to higher priority reservations. If the loading of a facility is higher, the level of ATC will be lower.

Table 4:  Contingency Analysis Results

| Facility | Model & Contingency | Facility Loading (% Rate B) Or Voltage (PU) | ATC (MW) | Date Required (M/D/Y) |
| --- | --- | --- | --- | --- |
| MOORELAND - WOODWARD 69kV | 06AP, 55785-55999, OKGE ENID - WFEC AEP-OP , FPL SWITCH - MOORELAND 138kV | 138.3 | 31 | 10/1/2007 |
| MOORELAND - WOODWARD 69kV | 07WP, 55785-55999, OKGE ENID - WFEC AEP-OP , FPL SWITCH - MOORELAND 138kV | 120.9 | 80 |  |
| MOORELAND - WOODWARD 69kV | 10WP, 55785-55999, OKGE ENID - WFEC AEP-OP , FPL SWITCH - MOORELAND 138kV | 116.7 | 90 |  |
| MOORELAND 138-69kV | 06AP, 55785-55999, OKGE ENID - WFEC AEP-OP , FPL SWITCH - MOORELAND 138kV | 134.9 | 45 | 10/1/2007 |
| MOORELAND 138-69kV | 07WP, 55785-55999, OKGE ENID - WFEC AEP-OP , FPL SWITCH - MOORELAND 138kV | 117.9 | 91 |  |
| MOORELAND 138-69kV | 10WP, 55785-55999, OKGE ENID - WFEC AEP-OP , FPL SWITCH - MOORELAND 138kV | 114.1 | 99 |  |
| MOREWOOD - MOREWOOD SW 138-69kV | 07SP, 54121-99940, AEPW WESTERN - , ELK CITY - 2002-05T 138kV | 133.8 | 0 | 7/31/2007 |
| MOREWOOD - MOREWOOD SW 138-69kV | 10SP, 54121-99940, AEPW WESTERN - , ELK CITY - 2002-05T 138kV | 133.6 | 0 |  |
| MOREWOOD - MOREWOOD SW 138-69kV | 15SP, 54121-99940, AEPW WESTERN - , ELK CITY - 2002-05T 138kV | 131.3 | 0 |  |
| MOREWOOD - MOREWOOD SW 138-69kV | 10WP, 54121-99940, AEPW WESTERN - , ELK CITY - 2002-05T 138kV | 120.0 | 0 |  |
| MOREWOOD - MOREWOOD SW 138-69kV | 07WP, 54121-99940, AEPW WESTERN - , ELK CITY - 2002-05T 138kV | 110.9 | 0 |  |
| MOREWOOD - MOREWOOD SW 138-69kV | 06AP, 54121-99940, AEPW WESTERN - , ELK CITY - 2002-05T 138kV | 106.3 | 53 |  |

Note:  When transmission service associated with this interconnection is evaluated, the loading of the facilities listed in this table may be greater due to higher priority reservations. If the loading of a facility is higher, the level of ATC will be lower.

Table 4:  Contingency Analysis Results

| Facility | Model & Contingency | Facility Loading (% Rate B) Or Voltage (PU) | ATC (MW) | Date Required (M/D/Y) |
| --- | --- | --- | --- | --- |
| SOUTHARD - ROMAN NOSE 138kV | 07SP, 54121-99940, AEPW WESTERN - , ELK CITY - 2002-05T 138kV | 119.3 | 34 | 7/31/2007 |
| SOUTHARD - ROMAN NOSE 138kV | 10SP, 54121-99940, AEPW WESTERN - , ELK CITY - 2002-05T 138kV | 118.6 | 37 |  |
| SOUTHARD - ROMAN NOSE 138kV | 15SP, 54121-99940, AEPW WESTERN - , ELK CITY - 2002-05T 138kV | 111.9 | 70 |  |
| SOUTHARD - ROMAN NOSE 138kV | 07SP, 54778-54789, OKGE ENID , CLEO CORNER - MEN TAP 138kV | 102.6 | 116 |  |
| SOUTHARD - ROMAN NOSE 138kV | 10SP, 54778-54789, OKGE ENID , CLEO CORNER - MEN TAP 138kV | 102.4 | 117 |  |
| SOUTHARD - ROMAN NOSE 138kV | 07SP, 54788-55999, OKGE ENID - WFEC AEP-OP , GLASS MOUNTAIN - MOORELAND 138kV | 102.1 | 119 |  |
| SOUTHARD - ROMAN NOSE 138kV | 10SP, 54788-55999, OKGE ENID - WFEC AEP-OP , GLASS MOUNTAIN - MOORELAND 138kV | 102.1 | 119 |  |
| SOUTHARD - ROMAN NOSE 138kV | 07SP, 54789-54790, OKGE ENID , MEN TAP - IMO TAP 138kV | 101.8 | 121 |  |
| SOUTHARD - ROMAN NOSE 138kV | 07SP, 54778-54788, OKGE ENID , CLEO CORNER - GLASS MOUNTAIN 138kV | 101.6 | 122 |  |
| SOUTHARD - ROMAN NOSE 138kV | 10SP, 54789-54790, OKGE ENID , MEN TAP - IMO TAP 138kV | 101.6 | 122 |  |

Note:  When transmission service associated with this interconnection is evaluated, the loading of the facilities listed in this table may be greater due to higher priority reservations. If the loading of a facility is higher, the level of ATC will be lower.

Table 4:  Contingency Analysis Results

| Facility | Model & Contingency | Facility Loading (% Rate B) Or Voltage (PU) | ATC (MW) | Date Required (M/D/Y) |
| --- | --- | --- | --- | --- |
| TALOGA 138-69kV | 15SP, 54787-54822, OKGE ENID - OKGE METRO , DEWEY - SOUTHARD 138kV | 121.1 | 22 | 7/31/2007 |
| TALOGA 138-69kV | 10SP, 54787-54822, OKGE ENID - OKGE METRO , DEWEY - SOUTHARD 138kV | 120.4 | 24 |  |
| TALOGA 138-69kV | 07SP, 54787-54822, OKGE ENID - OKGE METRO , DEWEY - SOUTHARD 138kV | 120.3 | 25 |  |
| TALOGA 138-69kV | 07SP, 54822-54823, OKGE METRO , SOUTHARD - ROMAN NOSE 138kV | 112.5 | 64 |  |
| TALOGA 138-69kV | 10SP, 54822-54823, OKGE METRO , SOUTHARD - ROMAN NOSE 138kV | 112.2 | 66 |  |
| TALOGA 138-69kV | 15SP, 54822-54823, OKGE METRO , SOUTHARD - ROMAN NOSE 138kV | 111.8 | 68 |  |
| TALOGA 138-69kV | 07SP, 54819-54823, OKGE METRO , EL RENO - ROMAN NOSE 138kV | 106.3 | 97 |  |
| TALOGA 138-69kV | 10SP, 54819-54823, OKGE METRO , EL RENO - ROMAN NOSE 138kV | 106.3 | 97 |  |
| TALOGA 138-69kV | 15SP, 54819-54823, OKGE METRO , EL RENO - ROMAN NOSE 138kV | 105.9 | 99 |  |
| TALOGA 138-69kV | 10WP, 54787-54822, OKGE ENID - OKGE METRO , DEWEY - SOUTHARD 138kV | 102.6 | 116 |  |

Note:  When transmission service associated with this interconnection is evaluated, the loading of the facilities listed in this table may be greater due to higher priority reservations. If the loading of a facility is higher, the level of ATC will be lower.

Table 4:  Contingency Analysis Results

| Facility | Model & Contingency | Facility Loading (% Rate B) Or Voltage (PU) | ATC (MW) | Date Required (M/D/Y) |
| --- | --- | --- | --- | --- |
| WOODWARD - FPL SWITCH 138kV | 06AP, 54785-54796, OKGE ENID , WOODWARD - IODINE 138kV | 109.1 | 109 | 7/31/2007 |
| WOODWARD - FPL SWITCH 138kV | 10SP, 54785-54796, OKGE ENID , WOODWARD - IODINE 138kV | 108.8 | 113 |  |
| WOODWARD - FPL SWITCH 138kV | 07SP, 54785-54796, OKGE ENID , WOODWARD - IODINE 138kV | 108.7 | 114 |  |
| WOODWARD - FPL SWITCH 138kV | 06AP, 54787-54796, OKGE ENID , DEWEY - IODINE 138kV | 108.2 | 111 |  |
| WOODWARD - FPL SWITCH 138kV | 15SP, 54785-54796, OKGE ENID , WOODWARD - IODINE 138kV | 106.9 | 117 |  |
| WOODWARD - FPL SWITCH 138kV | 10SP, 54787-54796, OKGE ENID , DEWEY - IODINE 138kV | 106.0 | 119 |  |
| WOODWARD - FPL SWITCH 138kV | 07SP, 54787-54796, OKGE ENID , DEWEY - IODINE 138kV | 105.9 | 119 |  |
| WOODWARD - FPL SWITCH 138kV | 15SP, 54787-54796, OKGE ENID , DEWEY - IODINE 138kV | 104.2 | 122 |  |
| WOODWARD - FPL SWITCH 138kV | 07WP, 54785-54796, OKGE ENID , WOODWARD - IODINE 138kV | 100.5 | 129 |  |

Note:  When transmission service associated with this interconnection is evaluated, the loading of the facilities listed in this table may be greater due to higher priority reservations. If the loading of a facility is higher, the level of ATC will be lower.

Table 4:  Contingency Analysis Results

| Facility | Model & Contingency | Facility Loading (% Rate B) Or Voltage (PU) | ATC (MW) | Date Required (M/D/Y) |
| --- | --- | --- | --- | --- |
| WOODWARD - WOODWRD2 138-( )kV | 15SP, 55785-55999, OKGE ENID - WFEC AEP-OP , FPL SWITCH - MOORELAND 138kV | 135.9 | 24 | 7/31/2007 |
| WOODWARD - WOODWRD2 138-( )kV | 07WP, 55785-55999, OKGE ENID - WFEC AEP-OP , FPL SWITCH - MOORELAND 138kV | 135.5 | 24 |  |
| WOODWARD - WOODWRD2 138-( )kV | 07SP, 55785-55999, OKGE ENID - WFEC AEP-OP , FPL SWITCH - MOORELAND 138kV | 135.4 | 26 |  |
| WOODWARD - WOODWRD2 138-( )kV | 10SP, 55785-55999, OKGE ENID - WFEC AEP-OP , FPL SWITCH - MOORELAND 138kV | 135.0 | 27 |  |
| WOODWARD - WOODWRD2 138-( )kV | 06AP, 55785-55999, OKGE ENID - WFEC AEP-OP , FPL SWITCH - MOORELAND 138kV | 134.5 | 31 |  |
| WOODWARD - WOODWRD2 138-( )kV | 10WP, 55785-55999, OKGE ENID - WFEC AEP-OP , FPL SWITCH - MOORELAND 138kV | 133.9 | 29 |  |
| WOODWARD - WOODWRD2 69-( )kV | 15SP, 55785-55999, OKGE ENID - WFEC AEP-OP , FPL SWITCH - MOORELAND 138kV | 140.3 | 16 |  |
| WOODWARD - WOODWRD2 69-( )kV | 07WP, 55785-55999, OKGE ENID - WFEC AEP-OP , FPL SWITCH - MOORELAND 138kV | 139.9 | 16 |  |
| WOODWARD - WOODWRD2 69-( )kV | 07SP, 55785-55999, OKGE ENID - WFEC AEP-OP , FPL SWITCH - MOORELAND 138kV | 139.8 | 18 |  |
| WOODWARD - WOODWRD2 69-( )kV | 06AP, 55785-55999, OKGE ENID - WFEC AEP-OP , FPL SWITCH - MOORELAND 138kV | 139.6 | 24 |  |

Note:  When transmission service associated with this interconnection is evaluated, the loading of the facilities listed in this table may be greater due to higher priority reservations. If the loading of a facility is higher, the level of ATC will be lower.

Table 4:  Contingency Analysis Results

| Facility | Model & Contingency | Facility Loading (% Rate B) Or Voltage (PU) | ATC (MW) | Date Required (M/D/Y) |
| --- | --- | --- | --- | --- |
| WOODWARD 69kV | 15SP, 55785-55999, OKGE ENID - WFEC AEP-OP , FPL SWITCH - MOORELAND 138kV | 155.3 | 30 | 7/31/2007 |
| WOODWARD 69kV | 06AP, 55785-55999, OKGE ENID - WFEC AEP-OP , FPL SWITCH - MOORELAND 138kV | 155.2 | 1 |  |
| WOODWARD 69kV | 10SP, 55785-55999, OKGE ENID - WFEC AEP-OP , FPL SWITCH - MOORELAND 138kV | 154.4 | 32 |  |
| WOODWARD 69kV | 07SP, 55785-55999, OKGE ENID - WFEC AEP-OP , FPL SWITCH - MOORELAND 138kV | 153.4 | 33 |  |
| WOODWARD 69kV | 07WP, 55785-55999, OKGE ENID - WFEC AEP-OP , FPL SWITCH - MOORELAND 138kV | 142.1 | 37 |  |
| WOODWARD 69kV | 10WP, 55785-55999, OKGE ENID - WFEC AEP-OP , FPL SWITCH - MOORELAND 138kV | 142.0 | 38 |  |

Note:  When transmission service associated with this interconnection is evaluated, the loading of the facilities listed in this table may be greater due to higher priority reservations. If the loading of a facility is higher, the level of ATC will be lower.

Powerflow Analysis

A powerflow analysis was conducted for the facility using modified versions of models for the 2006 April, Summer and Winter Peak for 2007 and 2010, and the 2015 Summer Peak seasons. This is the end of the current SPP planning horizon. The output of the Customer’s facility was offset in each model by a reduction in output of existing online SPP generation. The proposed in-service date of the generator is July 31, 2007.

The analysis of the Customer’s project indicates that, given the requested generation level of 130.5MW and location, additional criteria violations will occur on the existing AEPW, OKGE and WFEC facilities under steady state conditions in the modeled seasons.

There are several other proposed generation additions in the general area of the Customer’s facility. Local projects that were previously queued were assumed to be in service in this Feasibility Study. Those local projects that were previously queued and have advanced to nearly complete phases were included in this Feasibility Study.

In order to complete valid load flow solutions for one contingency, additional reactive compensation is required in the OKGE area. For an outage of the Elk City – GEN-2002-05 Tap 138kV line, 45.9MVAR is required on this contingency basis to prevent excessive voltage decay. This customer must install approximately 45.9MVAR in a staged capacitor bank switched at 34.5kV in the Customer’s 138-34.5kV Substation. Dynamic Stability studies performed as part of the impact study will provide additional guidance as to whether the reactive compensation can be static or a portion must be dynamic (such as a SVC).

Powerflow Analysis Methodology

The Southwest Power Pool (SPP) criteria states that: “The transmission system of the SPP region shall be planned and constructed so that the contingencies as set forth in the Criteria will meet the applicable NERC Planning Standards for System Adequacy and Security – Transmission System Table l hereafter referred to as NERC Table l) and its applicable standards and measurements”.

Using the created models and the ACCC function of PSS\E, single contingencies in portions or all of the modeled control areas of American Electric Power West, OG&E Electric Services, Western Farmers Electric Cooperative, and Southwestern Public Service Company were applied and the resulting scenarios analyzed.  This satisfies the ‘more probable’ contingency testing criteria mandated by NERC and the SPP criteria.

Conclusion

The minimum cost of interconnecting the Customer project is estimated at $473,276 for OKGE’s interconnection Network Upgrade facilities listed in Table 2 excluding upgrades of other transmission facilities by AEPW, OKGE and WFEC listed in Table 3 of which are Network Constraints. This cost estimate is based on the assumption that the modifications to accommodate GEN-2005-006 are completed. At this time, the cost estimates for other Direct Assignment facilities including those in Table 1 have not been defined by the Customer. As stated earlier, local projects that were previously queued are assumed to be in service in this Feasibility Study. An additional staged 45.9MVAR switched capacitor bank switched at 34.5kV will be required in the Customer’s 138-34.5kV Substation to maintain adequate voltage in the local area.

In Table 4, a value of Available Transfer Capability (ATC) associated with each overloaded facility is included. These values may be used by the Customer to determine lower generation capacity levels that may be installed. When transmission service associated with this interconnection is evaluated, the loading of the facilities listed in this table may be greater due to higher priority reservations. When a facility is overloaded for more than 10 contingencies, then only the results with the 10 highest loadings may be included in this table.

These interconnection costs do not include any cost that may be associated with short circuit or transient stability analysis.  These studies will be performed if the Customer signs a System Impact Study Agreement.

The required interconnection costs listed in Table 2 and other upgrades associated with Network Constraints listed in Table 3 do not include all costs associated with the deliverability of the energy to final customers. These costs are determined by separate studies if the Customer requests transmission service through Southwest Power Pool’s OASIS.

Figure 1:  Proposed Interconnection (Final substation design to be determined) – Woodward District Substation

Figure 2:  Map Of The Surrounding Area