## Table 1
Customer | Study Number | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date without interim redispatch | Deferred Stop Date without interim redispatch | Start Date with interim redispatch | Stop Date with interim redispatch | Note | Mimimum Allocated ATC (MW) within reservation period | Season of Minimum Allocated ATC within reservation period
AEPM | AG2-2006-033 | 1087745 | EES | CSWS | 225 | 2007-01-01 | 2010-01-01 | 2008-06-01 | 2011-06-01 | 2007-04-01 | 2010-04-01 | 1,2 | 0 | 08SP
AEPM | AG2-2006-034 | 1087757 | CSWS | CSWS | 172 | 2008-06-01 | 2028-06-01 | [5 empty] | 0 | 08SP
EDE | AG2-2005-064 | 973355 | KCPL | EDE | 100 | 2010-01-01 | 2030-01-01 |  |  |  |  | 3 | 0 | 11SP
GSEC | AG2-2006-054 | 1090270 | CSWS | CSWS | 10 | 2006-10-01 | 2036-10-01 | 2009-07-01 | 2039-07-01 |  |  |  | 0 | 16SP
GSEC | AG2-2006-133 | 1090487 | SPS | SPS | 150 | 2007-04-01 | 2017-04-01 | 2009-06-01 | 2019-06-01 | 2007-04-01 | 2017-04-01 | 1,2 | 0 | 08SP
INDP | AG1-2006-051 | 1033791 | KCPL | INDN | 50 | 2010-06-01 | 2040-06-01 |  |  |  |  | 3 | 0 | 11SP
KCPS | GEN-2004-008 | 1115127 | KCPL | KCPL | 332 | 2009-06-01 | 2029-06-01 |  |  |  |  | 3 | 0 | 11SP
KCPS | AG1-2006-009 | 1179751 | KCPL | KCPL | 168 | 2009-06-01 | 2029-06-01 |  |  |  |  | 3 | 0 | 11SP
KEPC | AG2-2006-067 | 1090416 | KCPL | WR | 30 | 2010-06-01 | 2030-06-01 | [5 empty] | 0 | 11SP
MIDW | AG2-2006-107 | 1090817 | WR | WR | 25 | 2007-06-01 | 2017-06-01 | 2009-07-01 | 2019-07-01 | 2007-10-01 | 2017-10-01 | 1,2 | 0 | 11SP
MIDW | AG2-2006-108 | 1090829 | WR | WR | 15 | 2008-06-01 | 2028-06-01 | 2009-07-01 | 2029-07-01 | 2008-06-01 | 2028-06-01 | 1,2 | 0 | 16SP
MIDW | AG2-2006-097 | 1090917 | WR | WR | 20 | 2008-06-01 | 2038-06-01 | 2009-07-01 | 2039-07-01 | 2008-06-01 | 2038-06-01 | 1,2 | 0 | 11WP
MIDW | AG2-2006-097 | 1090919 | WR | WR | 5 | 2008-06-01 | 2038-06-01 | 2009-07-01 | 2039-07-01 | 2008-06-01 | 2038-06-01 | 1,2 | 0 | 11WP
MIDW | AG2-2006-097 | 1090920 | WR | WR | 40 | 2008-06-01 | 2038-06-01 | 2009-07-01 | 2039-07-01 | 2008-06-01 | 2038-06-01 | 1,2 | 0 | 11WP
MIDW | AG2-2006-097 | 1090921 | WR | WR | 10 | 2008-06-01 | 2038-06-01 | 2009-07-01 | 2039-07-01 | 2008-06-01 | 2038-06-01 | 1,2 | 0 | 11WP
MIDW | AG2-2006-106 | 1090964 | WR | WR | 35 | 2007-01-01 | 2012-01-01 | 2010-06-01 | 2015-06-01 | 2007-10-01 | 2012-10-01 | 1,2 | 0 | 08SP
MIDW | AG2-2006-106 | 1090965 | WR | WR | 10 | 2007-01-01 | 2012-01-01 | 2010-06-01 | 2015-06-01 | 2007-10-01 | 2012-10-01 | 1,2 | 0 | 08SP
MIDW | AG2-2006-108 | 1091057 | WR | WR | 10 | 2008-06-01 | 2018-06-01 | 2009-07-01 | 2019-07-01 | 2008-06-01 | 2018-06-01 | 1,2 | 0 | 16SP
OGE | AG2-2006-035 | 1087908 | OKGE | EES | 10 | 2006-12-01 | 2011-12-01 | 2007-04-01 | 2012-04-01 | 2007-04-01 | 2012-04-01 | 1,2 | 0 | 0
SPSM | AG2-2006-074 | 1090699 | WPEK | KCPL | 50 | 2006-10-01 | 2007-10-01 | 2007-10-01 | 2008-10-01 |  |  |  | 0 | 07SP
SPSM | AG2-2006-124 | 1090705 | WPEK | KCPL | 50 | 2006-10-01 | 2007-10-01 | 2007-10-01 | 2008-10-01 |  |  |  | 0 | 07SP
UCU | AG2-2006-006 | 1052923 | KCPL | MPS | 160 | 2010-06-01 | 2030-06-01 | [5 empty] | 0 | 11SP
WRGS | AG2-2006-016 | 1076158 | KCPL | AMRN | 20 | 2010-06-01 | 2015-06-01 | [5 empty] | 0 | 11SP
WRGS | AG2-2006-030 | 1086655 | OKGE | WR | 225 | 2006-10-01 | 2026-10-01 | 2009-07-01 | 2029-07-01 | 2007-04-01 | 2027-04-01 | 1,2 | 0 | 16SP
Note 1: Disregard Redispatch shown in Table 6 for limitations identified earlier than the start date with redispatch with the exception of limitations identified in the 2006 Fall Peak, 2007 Spring Peak, 2007 April Minimum, 2007 Summer Shoulder, and 2007 Fall Peak
Note 2: Start and Stop Dates are determined based on customers choosing option to pursue redispatch to start service at Requested Start and Stop Dates or earliest date possible.
Note 3: All previous transmission requests with a source of Iatan II were re-evaluated in this AFS due to attempting to determine an overall solution for the requested service.

## Table 2
Customer | Study Number | Reservation | 9 Engineering and Construction Cost of Upgrades Allocated to Customer for Revenue Requirements | 1Letter of Credit Amount Required | 2Potential Base Plan Engineering and Construction Funding Allowable | NOTE | Additional Engineering and Construction Cost for 3rd Party Upgrades | 3 Total Revenue Requirements for Assigned Upgrades over term of reservation without potential base plan funding allocation | 3 Total Revenue Requirements for Assigned Upgrades over term of reservation WITH potential base plan funding allocation | Point-to-Point Base Rate over reservation period | 4Total Cost of Reservation Assignable to Customer contingent upon base plan funding
AEPM | AG2-2006-033 | 1087745 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | Sch 9 Charges
AEPM | AG2-2006-034 | 1087757 | 3000000 | 0 | 3000000 |  | 0 | 8631816 | 0 | 0 | Sch 9 Charges
EDE | AG2-2005-064 | 973355 | 4733572 | 0 | 3502843 | 10, 8 | 0 | 15077273 | 3920092 | 0 | 3920092
GSEC | AG2-2006-054 | 1090270 | 70000 | 70000 | 0 | 12 | 200000 | 264077 | 264077 | 0 | 464077
GSEC | AG2-2006-133 | 1090487 | 288620 | 288620 | 288620 |  | 0 | 569903.31 | 0 | 0 | Sch 9 Charges
INDP | AG1-2006-051 | 1033791 | 938195 | 938195 | 0 | 8 | 0 | 3340156 | 3340156 | 15840000 | 15840000
KCPS | GEN-2004-008 | 1115127 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | Sch 9 Charges
KCPS | AG1-2006-009 | 1179751 | 4161805 | 3461805 | 4161805 | 8 | 0 | 10566295 | 0 | 0 | Sch 9 Charges
KEPC | AG2-2006-067 | 1090416 | 17090 | 17090 | 17090 |  | 0 | 59915 | 0 | 0 | Sch 9 Charges
MIDW | AG2-2006-107 | 1090817 | 24671.9953 | 0 | 24671.9953 | 6 | 0 | 48847.5435 | 0 | 0 | Sch 9 Charges
MIDW | AG2-2006-108 | 1090829 | 15860.9723 | 0 | 0 | 5 | 0 | 44880.6291 | 44880.6296 | 0 | 44880.6296
MIDW | AG2-2006-097 | 1090917 | 17623.0741 | 0 | 0 | 5 | 0 | 64982.7929 | 64982.7935 | 0 | 64982.7935
MIDW | AG2-2006-097 | 1090919 | 3525.0603 | 0 | 0 | 5 | 0 | 12998.2012 | 12998.2013 | 0 | 12998.2013
MIDW | AG2-2006-097 | 1090920 | 38771.0371 | 0 | 0 | 5 | 0 | 142963.1552 | 142963.1566 | 0 | 142963.1566
MIDW | AG2-2006-097 | 1090921 | 10573.9815 | 0 | 0 | 5 | 0 | 38990.1811 | 38990.1815 | 0 | 38990.1815
MIDW | AG2-2006-106 | 1090964 | 31720.9165 | 0 | 31720.9165 |  | 0 | 52963.7264 | 0 | 0 | Sch 9 Charges
MIDW | AG2-2006-106 | 1090965 | 10573.9815 | 0 | 10573.9815 |  | 0 | 17655.1476 | 0 | 0 | Sch 9 Charges
MIDW | AG2-2006-108 | 1091057 | 10573.9815 | 0 | 0 | 5 | 0 | 22011.7844 | 22011.7846 | 0 | 22011.7846
OGE | AG2-2006-035 | 1087908 | 0 | 0 | 0 |  | 0 | 0 | 0 | 540000 | 540000
SPSM | AG2-2006-074 | 1090699 | 0 | 0 | 0 |  | 0 | 0 | 0 | 528000 | 528000
SPSM | AG2-2006-124 | 1090705 | 0 | 0 | 0 |  | 0 | 0 | 0 | 528000 | 528000
UCU | AG3-2006-018D | 1104638 | 0 | 0 | 0 | 7,13 | 0 | 0 | 0 | 0 | Sch 9 Charges
WRGS | AG2-2006-016 | 1076158 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1080000 | 1080000
WRGS | AG2-2006-030 | 1086655 | 54896021 | 27421315 | 54896021 |  | 0 | 121313926 | 0 | 0 | Sch 9 Charges
Totals |  |  | 68269198 |  | 65933345.8933 |  |  | 160269654.4714 | 7851151.7471
Note 1: Letter of Credit required for financial security for transmission owner for network upgrades is determined by allocated engineering and construction costs less engineering and construction costs for upgrades when network customer is the transmission owner plus network upgrades for assigned upgrades less that $100,000 which are base plan funded but still require a letter of credit.
Note 2. If potential base plan funding is applicable, this value is the lesser of the Engineering and Construction costs of assignable upgrades or the value of base plan funding calculated pursuant to Attachment J, Section III B criteria. Allocation of base plan funding is contingent upon verification of customer agreements meeting Attachment J, Section II B criteria. Not applicable if PTP base rate exceeds revenue requirements.
Note 3: Revenue Requirements (RR) are based upon deferred end dates if applicable. Deferred dates are based upon customer's choice to pursue redispatch. Achievable Base Plan Avoided RR in the case of a Base Plan upgrade being displaced or deferred by an earlier in service date for a Requested Upgrade shall be determined per Attachment J, Section VII.C methodology. Assumption of a 40 year service life is utilized for Base Plan funded projects. A present worth analysis of RR on a common year basis between the Base Plan and Requested Upgrades was performed to determine avoided Base Plan RR due to the displacement or deferral of the Base Plan upgrade by the Requested Upgrade. The incremental increase in present worth of a Requested Upgrade on a common year basis as a Base Plan upgrade is assigned to the transmission requests impacting the upgrade based on the displacement or deferral. If the displacement analysis results in lower RR due to the shorter amortization period of the requested upgrade when compared to a base plan amortization period, then no direct assignment of the upgrade cost is made due to the displacement to an earlier start date.
Note 4. For PTP requests, total cost is based on the higher of the base rate or assigned upgrade revenue requirements. For Network requests, the total cost is based on the assigned upgrade revenue requirement. Allocation of base plan funding will be determined after verification of designated resource meeting Attachment J, Section II B Criteria. Additionally E & C of 3rd Party upgrades is assignable to Customer. Revenue requirements for 3rd Party facilities are not calculated. Total cost to customer is based on assumption of Revenue Requirements with confirmation of base plan funding. Customer is responsible for negotiating redispatch costs if applicable. Customer is also responsible to pay credits for previously assigned upgrades that are impacted by their request. Credits required will be determined at a later date.
Note 5: Total Base plan funding available for 2008 to serve combined M and W system Midwest load based on 333MW of load is up to 416 MW of resources or 102 Additional MW more than forecast. This equates to $18,360,000 potential base plan funding for the full 102MW. 125MW remaining in this study exceeds cap for base funding.
Note 6: Midwest has a maximum of425MW of resources allowable for base funding for year 2007 based on 332MW load.
Note 7: UCU has a maximum of 161MW of resources in 2010 allowable for base funding for year 2010.
Note 8: All previous transmission requests with a source of Iatan II were re-evaluated in this AFS due to attempting to determine an overall solution for the requested service.
Note 9: E & C allocation for determination of allocated revenue requirements does not include those upgrades estimated at $100,000 or less as these are base plan funded. Thus this number sets the cap for base plan funding allowable for remaining assigned upgrades. Allocated E & C in Table 3 does include those upgrades less than $100,000 in order to establish the allocation per request per upgrade detail which is required for Letter of Credit determination.
Note 10: A ratio of total assignable $4,733,572 for 100MW to the assignable portion above 125% resource to load cap or 26MW results in $1,230,749 assignable to the customer.
Note 11: RR with base plan funding may increase or decrease even if no base plan funding is applicable to a particular request if another request that shares the upgrade is now full base plan funded resulting in a different amortization period for the upgrade and thus different RR.
Note 12: $200,000 to install Capacitor at GSEC bus and $70,000 SPS cost for line tap.
Note 13: Customer UCU Study Number AG2-2006-006 Reservation 1052923 for PTP Transmission Service request replaced with equivalent Study Number AG3-2006-018D Reservation 1104638 for NITS request.

## Table 3
Customer | Study Number
AEPM | AG2-2006-033
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AEPM | 1087745 | EES | CSWS | 225 | 2007-01-01 | 2010-01-01 | 2008-06-01 | 2011-06-01 | 0 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0 | 0
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1087745 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1087745 | ALUMAX TAP - NORTHWEST TEXARKANA 138KV CKT 1 | 2008-06-01 | 2008-06-01
| CHAMBER SPRINGS - TONTITOWN 161KV CKT 1 | 2008-12-01 | 2007-06-01
| Chamber Springs - Tontitown 345 kV | 2008-06-01 | 2008-06-01
| Flint Creek - East Centerton 345 kV | 2011-06-01 | 2011-06-01
| LINWOOD - MCWILLIE STREET 138KV CKT 1 | 2007-06-01 | 2008-06-01 |  | Yes
Customer | Study Number
AEPM | AG2-2006-034
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AEPM | 1087757 | CSWS | CSWS | 172 | 2008-06-01 | 2028-06-01 |  |  | 3000000 | 0 | 3000000 | 8631816
[9 empty] | 3000000 | 0 | 3000000 | 8631816
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1087757 | SOUTHWEST SHREVEPORT (SW SHV 1) 345/138/13.8KV TRANSFORMER CKT 1 | 2010-06-01 | 2010-06-01 |  |  | 1500000 | 1500000 | 4315908
| SOUTHWEST SHREVEPORT (SW SHV 2) 345/138/13.8KV TRANSFORMER CKT 2 | 2010-06-01 | 2010-06-01 |  |  | 1500000 | 1500000 | 4315908
[5 empty] | Total | 3000000 | 3000000 | 8631816
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1087757 | 5 TRIBES - HANCOCK 161KV CKT 1 | 2014-06-01 | 2014-06-01
| 5 TRIBES - PECAN CREEK 161KV CKT 1 | 2014-06-01 | 2014-06-01
| AGENCY - PECAN CREEK 161KV CKT 1 | 2014-06-01 | 2014-06-01
| ALUMAX TAP - NORTHWEST TEXARKANA 138KV CKT 1 | 2008-06-01 | 2008-06-01
| CHAMBER SPRINGS - TONTITOWN 161KV CKT 1 | 2008-12-01 | 2007-06-01
| Chamber Springs - Tontitown 345 kV | 2008-06-01 | 2008-06-01
| Flint Creek - East Centerton 345 kV | 2011-06-01 | 2011-06-01
| LINWOOD - MCWILLIE STREET 138KV CKT 1 | 2007-06-01 | 2008-06-01
| PECAN CREEK (PECANCK1) 345/161/13.8KV TRANSFORMER CKT 2 | 2014-06-01 | 2014-06-01
| Siloam Springs - South Fayetteville 161 kV | 2015-06-01 | 2015-06-01
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1087757 | ARCADIA - REDBUD 345 KV CKT 1 | 2006-06-01 | 2006-06-01
| ARCADIA - REDBUD 345 KV CKT 2 | 2006-06-01 | 2006-06-01
| BEELINE - EXPLORER GLENPOOL 138KV CKT 1 | 2009-06-01 | 2009-06-01
| EXPLORER GLENPOOL - RIVERSIDE STATION 138KV CKT 1 AEPW | 2009-06-01 | 2009-06-01
| EXPLORER GLENPOOL - RIVERSIDE STATION 138KV CKT 1 OKGE | 2009-06-01 | 2009-06-01
Customer | Study Number
GSEC | AG2-2006-054
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
GSEC | 1090270 | CSWS | CSWS | 10 | 2006-10-01 | 2036-10-01 | 2009-07-01 | 2039-07-01 | 0 | 0 | 270000 | 264077
[9 empty] | 0 | 0 | 270000 | 264077
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1090270 | GSEC Midway Interconnection #1 | 2011-06-01 | 2011-06-01 |  |  | 70000 | 70000 | 264077
| GSEC Midway Interconnection #2 | 2011-06-01 | 2011-06-01 |  |  | 200000 | 200000 | 0
[5 empty] | Total | 270000 | 270000 | 264077
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1090270 | ALTUS JCT TAP - RUSSELL 138KV CKT 1 | 2014-06-01 | 2014-06-01
| CANADIAN - CEDAR LANE 138KV CKT 1 | 2015-06-01 | 2015-06-01
| Hart Interchange 230/115 kV | 2011-06-01 | 2011-06-01
| Hitchland 345 and 115 kV Interchange | 2010-06-01 | 2010-06-01
| Mooreland - Potter 345 kV SPS | 2015-06-01 | 2015-06-01
| Mooreland - Potter 345 kV WFEC | 2015-06-01 | 2015-06-01
| Mooreland 345/138 kV Transformer | 2015-06-01 | 2015-06-01
| POTTER COUNTY INTERCHANGE (POTTR CO) 345/230/13.2KV TRANSFORMER CKT 2 | 2015-06-01 | 2015-06-01
| SNYDER AEPW- SNYDER WFEC INTERCONNECTION | 2016-06-01 | 2016-06-01
| Spearville - Mooreland 345 kV SUNC | 2015-06-01 | 2015-06-01
| Spearville - Mooreland 345 kV WFEC | 2015-06-01 | 2015-06-01
| Stateline Project | 2014-06-01 | 2014-06-01
| Tex-Hitchland-Sherman Tap 115 kV ckt | 2010-06-01 | 2010-06-01
| THOMAS TAP - WEATHERFORD 69KV CKT 1 | 2014-06-01 | 2014-06-01
| TUCO INTERCHANGE 345/115KV TRANSFORMER CKT 1 | 2015-06-01 | 2015-06-01
| WEATHERFORD SOUTHEAST (WTH_SE) 138/69/13.8KV TRANSFORMER CKT 1 | 2013-06-01 | 2013-06-01
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1090270 | ARCADIA - REDBUD 345 KV CKT 1 | 2006-06-01 | 2006-06-01
| ARCADIA - REDBUD 345 KV CKT 2 | 2006-06-01 | 2006-06-01
| BEELINE - EXPLORER GLENPOOL 138KV CKT 1 | 2009-06-01 | 2009-06-01
| EXPLORER GLENPOOL - RIVERSIDE STATION 138KV CKT 1 AEPW | 2009-06-01 | 2009-06-01
| EXPLORER GLENPOOL - RIVERSIDE STATION 138KV CKT 1 OKGE | 2009-06-01 | 2009-06-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1090270 | HAMON BUTLER - MOREWOOD 69KV CKT 1 | 2006-12-01 | 2008-04-01 |  | No
| RENO - SUMMIT 345KV | 2011-01-01 | 2011-01-01
| WICHITA - RENO 345KV | 2006-12-01 | 2009-07-01 |  | No
Customer | Study Number
GSEC | AG2-2006-133
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
GSEC | 1090487 | SPS | SPS | 150 | 2007-04-01 | 2017-04-01 | 2009-06-01 | 2019-06-01 | 288620 |  | 288620 | 569903
[9 empty] | 288620 | 0 | 288620 | 569903
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1090487 | Mustang-San Andr-Amerada Hess 115KV Displacement | 2007-04-01 | 2008-06-01 |  | Yes | 288620 | 1742892 | 569903
| YOAKUM COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 1 Displacement | 2007-06-01 | 2008-06-01 |  | Yes | 0 | 2500000 | 0
[5 empty] | Total | 288620 | 4242892 | 569903
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1090487 | BC-EARTH INTERCHANGE 115KV | 2016-06-01 | 2016-06-01
| CURRY COUNTY INTERCHANGE - ROOSEVELT COUNTY INTERCHANGE 115KV CKT 2 | 2013-06-01 | 2013-06-01
| Hart Interchange 230/115 kV | 2011-06-01 | 2011-06-01
| Hitchland 345 and 115 kV Interchange | 2010-06-01 | 2010-06-01
| KRESS INTERCHANGE 115/69KV TRANSFORMERS | 2007-04-01 | 2007-04-01
| LC-SOL3 115KV | 2016-06-01 | 2016-06-01
| MUSTANG STATION 230/115KV TRANSFORMER CKT 1 | 2007-04-01 | 2008-06-01 |  | Yes
| Potter - Roosevelt 345KV | 2013-06-01 | 2013-06-01
| Pringle - Etter 115 kV | 2010-06-01 | 2010-06-01
| ROOSEVELT COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 1 | 2013-06-01 | 2013-06-01
| Seven Rivers to Pecos to Potash Junction 230kV | 2007-06-01 | 2009-06-01 |  | Yes
| Tex-Hitchland-Sherman Tap 115 kV ckt | 2010-06-01 | 2010-06-01
| TUCO INTERCHANGE 115/69KV TRANSFORMER | 2008-06-01 | 2008-06-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1090487 | TERRY COUNTY INTERCHANGE 115/69KV TRANSFORMERS | 2007-06-01 | 2007-06-01
Customer | Study Number
KEPC | AG2-2006-067
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
KEPC | 1090416 | KCPL | WR | 30 | 2010-06-01 | 2030-06-01 |  |  | 17090 | 0 | 17090 | 59915
[9 empty] | 17090 | 0 | 17090 | 59915
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1090416 | COFFEYVILLE TAP - DEARING 138KV CKT 1 AEPW Displacement | 2011-06-01 | 2011-06-01 |  |  | 5167 | 500000 | 17801
| COFFEYVILLE TAP - DEARING 138KV CKT 1 WERE Displacement | 2011-06-01 | 2011-06-01 |  |  | 11923 | 3000000 | 42114
| ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 Displacement | 2011-06-01 | 2011-06-01 |  |  | 0 | 5000000 | 0
[5 empty] | Total | 17090 | 8500000 | 59915
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1090416 | CIRCLEVILLE - HOYT HTI SWITCHING JUNCTION 115KV CKT 1 | 2006-12-01 | 2010-06-01
| COFFEYVILLE SUB - CRA 69KV CKT 1 | 2011-06-01 | 2011-06-01
| COFFEYVILLE SUB - DEARING 69KV CKT 1 | 2011-06-01 | 2011-06-01
| COUNTY LINE - HOOK JCT 115KV CKT 1 | 2011-06-01 | 2011-06-01
| COUNTY LINE - TECUMSEH HILL 115KV CKT 1 | 2011-06-01 | 2011-06-01
| CRESWELL (CRESWL1X) 138/69/13.2KV TRANSFORMER | 2012-06-01 | 2012-06-01
| Evans - Grant - Chisolm Rebuild and Conversion Project | 2008-06-01 | 2009-06-01
| HOOK JCT - TECUMSEH ENERGY CENTER 115KV CKT 1 #1 | 2011-06-01 | 2011-06-01
| HOOK JCT - TECUMSEH ENERGY CENTER 115KV CKT 1 #2 | 2011-06-01 | 2011-06-01
| NEOSHO - NORTHEAST PARSONS 138KV CKT 1 | 2013-06-01 | 2013-06-01
| Stranger - Thorton 115 kV | 2010-06-01 | 2010-06-01
| STRANGER CREEK TRANSFORMER CKT 2 | 2011-06-01 | 2011-06-01
| TECUMSEH ENERGY CENTER - TECUMSEH HILL 115KV CKT 1 | 2010-06-01 | 2010-06-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1090416 | IATAN - ST JOE 345KV CKT 1 | 2011-06-01 | 2011-06-01
| RENO - SUMMIT 345KV | 2011-01-01 | 2011-01-01
| WICHITA - RENO 345KV | 2006-12-01 | 2009-07-01
Customer | Study Number
MIDW | AG2-2006-097
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
MIDW | 1090917 | WR | WR | 20 | 2008-06-01 | 2038-06-01 | 2009-07-01 | 2039-07-01 | 0 | 0 | 17623 | 64983
MIDW | 1090919 | WR | WR | 5 | 2008-06-01 | 2038-06-01 | 2009-07-01 | 2039-07-01 | 0 | 0 | 3525 | 12998
MIDW | 1090920 | WR | WR | 40 | 2008-06-01 | 2038-06-01 | 2009-07-01 | 2039-07-01 | 0 | 0 | 38771 | 142963
MIDW | 1090921 | WR | WR | 10 | 2008-06-01 | 2038-06-01 | 2009-07-01 | 2039-07-01 | 0 | 0 | 10574 | 38990
[9 empty] | 0 | 0 | 70493 | 0
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1090917 | ST JOHN CAPACITOR Displacement | 2008-06-01 | 2008-06-01 |  |  | 17623 | 864000 | 64983
[5 empty] | Total | 17623 | 864000 | 64983
1090919 | ST JOHN CAPACITOR Displacement | 2008-06-01 | 2008-06-01 |  |  | 3525 | 864000 | 12998
[5 empty] | Total | 3525 | 864000 | 12998
1090920 | ST JOHN CAPACITOR Displacement | 2008-06-01 | 2008-06-01 |  |  | 38771 | 864000 | 142963
[5 empty] | Total | 38771 | 864000 | 142963
1090921 | ST JOHN CAPACITOR Displacement | 2008-06-01 | 2008-06-01 |  |  | 10574 | 864000 | 38990
[5 empty] | Total | 10574 | 864000 | 38990
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1090917 | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | 2014-06-01 | 2014-06-01
| HUNTSVILLE - ST JOHN 115KV CKT 1 | 2014-06-01 | 2014-06-01
| Mooreland - Potter 345 kV SPS | 2015-06-01 | 2015-06-01
| Mooreland - Potter 345 kV WFEC | 2015-06-01 | 2015-06-01
| Mooreland 345/138 kV Transformer | 2015-06-01 | 2015-06-01
| POTTER COUNTY INTERCHANGE (POTTR CO) 345/230/13.2KV TRANSFORMER CKT 2 | 2015-06-01 | 2015-06-01
| Spearville - Mooreland 345 kV SUNC | 2015-06-01 | 2015-06-01
| Spearville - Mooreland 345 kV WFEC | 2015-06-01 | 2015-06-01
| TUCO INTERCHANGE 345/115KV TRANSFORMER CKT 1 | 2015-06-01 | 2015-06-01
1090919 | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | 2014-06-01 | 2014-06-01
| HUNTSVILLE - ST JOHN 115KV CKT 1 | 2014-06-01 | 2014-06-01
| Mooreland - Potter 345 kV SPS | 2015-06-01 | 2015-06-01
| Mooreland - Potter 345 kV WFEC | 2015-06-01 | 2015-06-01
| Mooreland 345/138 kV Transformer | 2015-06-01 | 2015-06-01
| POTTER COUNTY INTERCHANGE (POTTR CO) 345/230/13.2KV TRANSFORMER CKT 2 | 2015-06-01 | 2015-06-01
| Spearville - Mooreland 345 kV SUNC | 2015-06-01 | 2015-06-01
| Spearville - Mooreland 345 kV WFEC | 2015-06-01 | 2015-06-01
| TUCO INTERCHANGE 345/115KV TRANSFORMER CKT 1 | 2015-06-01 | 2015-06-01
1090920 | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | 2014-06-01 | 2014-06-01
| HUNTSVILLE - ST JOHN 115KV CKT 1 | 2014-06-01 | 2014-06-01
| Mooreland - Potter 345 kV SPS | 2015-06-01 | 2015-06-01
| Mooreland - Potter 345 kV WFEC | 2015-06-01 | 2015-06-01
| Mooreland 345/138 kV Transformer | 2015-06-01 | 2015-06-01
| POTTER COUNTY INTERCHANGE (POTTR CO) 345/230/13.2KV TRANSFORMER CKT 2 | 2015-06-01 | 2015-06-01
| Spearville - Mooreland 345 kV SUNC | 2015-06-01 | 2015-06-01
| Spearville - Mooreland 345 kV WFEC | 2015-06-01 | 2015-06-01
| TUCO INTERCHANGE 345/115KV TRANSFORMER CKT 1 | 2015-06-01 | 2015-06-01
1090921 | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | 2014-06-01 | 2014-06-01
| HUNTSVILLE - ST JOHN 115KV CKT 1 | 2014-06-01 | 2014-06-01
| Mooreland - Potter 345 kV SPS | 2015-06-01 | 2015-06-01
| Mooreland - Potter 345 kV WFEC | 2015-06-01 | 2015-06-01
| Mooreland 345/138 kV Transformer | 2015-06-01 | 2015-06-01
| POTTER COUNTY INTERCHANGE (POTTR CO) 345/230/13.2KV TRANSFORMER CKT 2 | 2015-06-01 | 2015-06-01
| Spearville - Mooreland 345 kV SUNC | 2015-06-01 | 2015-06-01
| Spearville - Mooreland 345 kV WFEC | 2015-06-01 | 2015-06-01
| TUCO INTERCHANGE 345/115KV TRANSFORMER CKT 1 | 2015-06-01 | 2015-06-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1090917 | RENO - SUMMIT 345KV | 2011-01-01 | 2011-01-01
| WICHITA - RENO 345KV | 2006-12-01 | 2009-07-01 |  | Yes
1090919 | RENO - SUMMIT 345KV | 2011-01-01 | 2011-01-01
| WICHITA - RENO 345KV | 2006-12-01 | 2009-07-01 |  | Yes
1090920 | RENO - SUMMIT 345KV | 2011-01-01 | 2011-01-01
| WICHITA - RENO 345KV | 2006-12-01 | 2009-07-01 |  | Yes
1090921 | RENO - SUMMIT 345KV | 2011-01-01 | 2011-01-01
| WICHITA - RENO 345KV | 2006-12-01 | 2009-07-01 |  | Yes
Customer | Study Number
MIDW | AG2-2006-106
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
MIDW | 1090964 | WR | WR | 35 | 2007-01-01 | 2012-01-01 | 2010-06-01 | 2015-06-01 | 31720.9165 | 0 | 31721 | 52964
MIDW | 1090965 | WR | WR | 10 | 2007-01-01 | 2012-01-01 | 2010-06-01 | 2015-06-01 | 10573.9815 | 0 | 10574 | 17655
[9 empty] | 0 | 0 | 42295 | 0
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1090964 | ST JOHN CAPACITOR Displacement | 2008-06-01 | 2008-06-01 |  |  | 31721 | 864000 | 52964
[5 empty] | Total | 31721 | 864000 | 52964
1090965 | ST JOHN CAPACITOR Displacement | 2008-06-01 | 2008-06-01 |  |  | 10574 | 864000 | 17655
[5 empty] | Total | 10574 | 864000 | 17655
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1090964 | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | 2007-06-01 | 2009-06-01 |  | Yes
| CIRCLEVILLE - HOYT HTI SWITCHING JUNCTION 115KV CKT 1 | 2006-12-01 | 2010-06-01 |  | Yes
| CLAY CENTER - GREENLEAF 115KV CKT 1 | 2007-06-01 | 2009-06-01 |  | Yes
| COUNTY LINE - HOOK JCT 115KV CKT 1 | 2011-06-01 | 2011-06-01
| COUNTY LINE - TECUMSEH HILL 115KV CKT 1 | 2011-06-01 | 2011-06-01
| GILL ENERGY CENTER EAST - GILLJCT269.0 69KV CKT 1 | 2007-06-01 | 2008-06-01 | 2007-10-01 | Yes
| GILL ENERGY CENTER EAST - MACARTHUR 69KV CKT 1 #1 | 2007-06-01 | 2007-07-01 |  | Yes
| HAYS PLANT - SOUTH HAYS 115KV CKT 1 | 2008-06-01 | 2009-06-01 | 2008-10-01 | Yes
| HAYS PLANT - VINE STREET 115KV CKT 1 | 2008-06-01 | 2009-06-01 | 2008-10-01 | Yes
| HOOK JCT - TECUMSEH ENERGY CENTER 115KV CKT 1 #1 | 2011-06-01 | 2011-06-01
| HOOK JCT - TECUMSEH ENERGY CENTER 115KV CKT 1 #2 | 2011-06-01 | 2011-06-01
| HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | 2014-06-01 | 2014-06-01
| HUNTSVILLE - ST JOHN 115KV CKT 1 | 2014-06-01 | 2014-06-01
| TECUMSEH ENERGY CENTER - TECUMSEH HILL 115KV CKT 1 | 2010-06-01 | 2010-06-01
1090965 | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | 2007-06-01 | 2009-06-01 |  | Yes
| CIRCLEVILLE - HOYT HTI SWITCHING JUNCTION 115KV CKT 1 | 2006-12-01 | 2010-06-01 |  | Yes
| CLAY CENTER - GREENLEAF 115KV CKT 1 | 2007-06-01 | 2009-06-01 |  | Yes
| COUNTY LINE - HOOK JCT 115KV CKT 1 | 2011-06-01 | 2011-06-01
| COUNTY LINE - TECUMSEH HILL 115KV CKT 1 | 2011-06-01 | 2011-06-01
| GILL ENERGY CENTER EAST - GILLJCT269.0 69KV CKT 1 | 2007-06-01 | 2008-06-01 | 2007-10-01 | Yes
| GILL ENERGY CENTER EAST - MACARTHUR 69KV CKT 1 #1 | 2007-06-01 | 2007-07-01 |  | Yes
| HAYS PLANT - SOUTH HAYS 115KV CKT 1 | 2008-06-01 | 2009-06-01 | 2008-10-01 | Yes
| HAYS PLANT - VINE STREET 115KV CKT 1 | 2008-06-01 | 2009-06-01 | 2008-10-01 | Yes
| HOOK JCT - TECUMSEH ENERGY CENTER 115KV CKT 1 #1 | 2011-06-01 | 2011-06-01
| HOOK JCT - TECUMSEH ENERGY CENTER 115KV CKT 1 #2 | 2011-06-01 | 2011-06-01
| HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | 2014-06-01 | 2014-06-01
| HUNTSVILLE - ST JOHN 115KV CKT 1 | 2014-06-01 | 2014-06-01
| TECUMSEH ENERGY CENTER - TECUMSEH HILL 115KV CKT 1 | 2010-06-01 | 2010-06-01
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1090964 | LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01
1090965 | LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1090964 | HEIZER TO KNOLL 230KV | 2007-06-01 | 2007-10-01 |  | No
| IATAN - ST JOE 345KV CKT 1 | 2011-06-01 | 2011-06-01
| RENO - SUMMIT 345KV | 2011-01-01 | 2011-01-01
| WICHITA - RENO 345KV | 2006-12-01 | 2009-07-01 |  | Yes
1090965 | HEIZER TO KNOLL 230KV | 2007-06-01 | 2007-10-01 |  | No
| IATAN - ST JOE 345KV CKT 1 | 2011-06-01 | 2011-06-01
| RENO - SUMMIT 345KV | 2011-01-01 | 2011-01-01
| WICHITA - RENO 345KV | 2006-12-01 | 2009-07-01 |  | Yes
Customer | Study Number
MIDW | AG2-2006-107
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
MIDW | 1090817 | WR | WR | 25 | 2007-06-01 | 2017-06-01 | 2009-07-01 | 2019-07-02 | 24671.9953 | 0 | 24672 | 48848
[9 empty] | 24671.9953 | 0 | 24672 | 48848
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1090817 | ST JOHN CAPACITOR Displacement | 2008-06-01 | 2008-06-01 |  |  | 24672 | 864000 | 48848
[5 empty] | Total | 24672 | 864000 | 48848
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1090817 | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | 2007-06-01 | 2009-06-01 |  | Yes
| CLAY CENTER - GREENLEAF 115KV CKT 1 | 2007-06-01 | 2009-06-01 |  | Yes
| COUNTY LINE - HOOK JCT 115KV CKT 1 | 2011-06-01 | 2011-06-01
| COUNTY LINE - TECUMSEH HILL 115KV CKT 1 | 2011-06-01 | 2011-06-01
| GILL ENERGY CENTER EAST - GILLJCT269.0 69KV CKT 1 | 2007-06-01 | 2008-06-01 | 2007-10-01 | Yes
| GILL ENERGY CENTER EAST - MACARTHUR 69KV CKT 1 #1 | 2007-06-01 | 2007-07-01 |  | Yes
| HAYS PLANT - SOUTH HAYS 115KV CKT 1 | 2008-06-01 | 2009-06-01 | 2008-10-01 | Yes
| HAYS PLANT - VINE STREET 115KV CKT 1 | 2008-06-01 | 2009-06-01 | 2008-10-01 | Yes
| HOOK JCT - TECUMSEH ENERGY CENTER 115KV CKT 1 #1 | 2011-06-01 | 2011-06-01
| HOOK JCT - TECUMSEH ENERGY CENTER 115KV CKT 1 #2 | 2011-06-01 | 2011-06-01
| HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | 2014-06-01 | 2014-06-01
| HUNTSVILLE - ST JOHN 115KV CKT 1 | 2014-06-01 | 2014-06-01
| Mooreland - Potter 345 kV SPS | 2015-06-01 | 2015-06-01
| Mooreland - Potter 345 kV WFEC | 2015-06-01 | 2015-06-01
| Mooreland 345/138 kV Transformer | 2015-06-01 | 2015-06-01
| POTTER COUNTY INTERCHANGE (POTTR CO) 345/230/13.2KV TRANSFORMER CKT 2 | 2015-06-01 | 2015-06-01
| Spearville - Mooreland 345 kV SUNC | 2015-06-01 | 2015-06-01
| Spearville - Mooreland 345 kV WFEC | 2015-06-01 | 2015-06-01
| TECUMSEH ENERGY CENTER - TECUMSEH HILL 115KV CKT 1 | 2010-06-01 | 2010-06-01
| TUCO INTERCHANGE 345/115KV TRANSFORMER CKT 1 | 2015-06-01 | 2015-06-01
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1090817 | LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1090817 | HEIZER TO KNOLL 230KV | 2007-06-01 | 2007-10-01 |  | No
| IATAN - ST JOE 345KV CKT 1 | 2011-06-01 | 2011-06-01
| RENO - SUMMIT 345KV | 2011-01-01 | 2011-01-01
| WICHITA - RENO 345KV | 2006-12-01 | 2009-07-01 |  | Yes
Customer | Study Number
MIDW | AG2-2006-108
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
MIDW | 1090829 | WR | WR | 15 | 2008-06-01 | 2028-06-01 | 2009-07-01 | 2029-07-01 | 0 | 0 | 10574 | 44880.6291
MIDW | 1091057 | WR | WR | 10 | 2008-06-01 | 2018-06-01 | 2009-07-01 | 2019-07-02 | 0 | 0 | 15861 | 22012
[9 empty] | 0 | 0 | 26435 | 0
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1090829 | ST JOHN CAPACITOR Displacement | 2008-06-01 | 2008-06-01 |  |  | 10574 | 864000 | 44880.6291
[5 empty] | Total | 10574 | 864000 | 44880.6291
1091057 | ST JOHN CAPACITOR Displacement | 2008-06-01 | 2008-06-01 |  |  | 15861 | 864000 | 22012
[5 empty] | Total | 15861 | 864000 | 22012
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1090829 | COUNTY LINE - HOOK JCT 115KV CKT 1 | 2011-06-01 | 2011-06-01
| COUNTY LINE - TECUMSEH HILL 115KV CKT 1 | 2011-06-01 | 2011-06-01
| HAYS PLANT - SOUTH HAYS 115KV CKT 1 | 2008-06-01 | 2009-06-01 | 2008-10-01 | Yes
| HAYS PLANT - VINE STREET 115KV CKT 1 | 2008-06-01 | 2009-06-01 | 2008-10-01 | Yes
| HOOK JCT - TECUMSEH ENERGY CENTER 115KV CKT 1 #1 | 2011-06-01 | 2011-06-01
| HOOK JCT - TECUMSEH ENERGY CENTER 115KV CKT 1 #2 | 2011-06-01 | 2011-06-01
| HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | 2014-06-01 | 2014-06-01
| HUNTSVILLE - ST JOHN 115KV CKT 1 | 2014-06-01 | 2014-06-01
| Mooreland - Potter 345 kV SPS | 2015-06-01 | 2015-06-01
| Mooreland - Potter 345 kV WFEC | 2015-06-01 | 2015-06-01
| Mooreland 345/138 kV Transformer | 2015-06-01 | 2015-06-01
| POTTER COUNTY INTERCHANGE (POTTR CO) 345/230/13.2KV TRANSFORMER CKT 2 | 2015-06-01 | 2015-06-01
| Spearville - Mooreland 345 kV SUNC | 2015-06-01 | 2015-06-01
| Spearville - Mooreland 345 kV WFEC | 2015-06-01 | 2015-06-01
| TECUMSEH ENERGY CENTER - TECUMSEH HILL 115KV CKT 1 | 2010-06-01 | 2010-06-01
| TUCO INTERCHANGE 345/115KV TRANSFORMER CKT 1 | 2015-06-01 | 2015-06-01
1091057 | COUNTY LINE - HOOK JCT 115KV CKT 1 | 2011-06-01 | 2011-06-01
| COUNTY LINE - TECUMSEH HILL 115KV CKT 1 | 2011-06-01 | 2011-06-01
| HAYS PLANT - SOUTH HAYS 115KV CKT 1 | 2008-06-01 | 2009-06-01 | 2008-10-01 | Yes
| HAYS PLANT - VINE STREET 115KV CKT 1 | 2008-06-01 | 2009-06-01 | 2008-10-01 | Yes
| HOOK JCT - TECUMSEH ENERGY CENTER 115KV CKT 1 #1 | 2011-06-01 | 2011-06-01
| HOOK JCT - TECUMSEH ENERGY CENTER 115KV CKT 1 #2 | 2011-06-01 | 2011-06-01
| HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | 2014-06-01 | 2014-06-01
| HUNTSVILLE - ST JOHN 115KV CKT 1 | 2014-06-01 | 2014-06-01
| Mooreland - Potter 345 kV SPS | 2015-06-01 | 2015-06-01
| Mooreland - Potter 345 kV WFEC | 2015-06-01 | 2015-06-01
| Mooreland 345/138 kV Transformer | 2015-06-01 | 2015-06-01
| POTTER COUNTY INTERCHANGE (POTTR CO) 345/230/13.2KV TRANSFORMER CKT 2 | 2015-06-01 | 2015-06-01
| Spearville - Mooreland 345 kV SUNC | 2015-06-01 | 2015-06-01
| Spearville - Mooreland 345 kV WFEC | 2015-06-01 | 2015-06-01
| TECUMSEH ENERGY CENTER - TECUMSEH HILL 115KV CKT 1 | 2010-06-01 | 2010-06-01
| TUCO INTERCHANGE 345/115KV TRANSFORMER CKT 1 | 2015-06-01 | 2015-06-01
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1091057 | LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1090829 | IATAN - ST JOE 345KV CKT 1 | 2011-06-01 | 2011-06-01
| RENO - SUMMIT 345KV | 2011-01-01 | 2011-01-01
| WICHITA - RENO 345KV | 2006-12-01 | 2009-07-01 |  | No
1091057 | IATAN - ST JOE 345KV CKT 1 | 2011-06-01 | 2011-06-01
| RENO - SUMMIT 345KV | 2011-01-01 | 2011-01-01
| WICHITA - RENO 345KV | 2006-12-01 | 2009-07-01 |  | Yes
Customer | Study Number
OGE | AG2-2006-035
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
OGE | 1087908 | OKGE | EES | 10 | 2006-12-01 | 2011-12-01 |  |  | 0 | 540000 | 0 | 0
[9 empty] | 0 | 540000 | 0 | 0
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1087908 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1087908 | ARCADIA - REDBUD 345 KV CKT 1 | 2006-06-01 | 2006-06-01
| ARCADIA - REDBUD 345 KV CKT 2 | 2006-06-01 | 2006-06-01
| FPL SWITCH - MOORELAND 138KV CKT 1 OKGE | 2006-06-01 | 2008-04-01
| FPL SWITCH - MOORELAND 138KV CKT 1 WFEC | 2006-06-01 | 2008-04-01
| LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1087908 | IATAN - ST JOE 345KV CKT 1 | 2011-06-01 | 2011-06-01
Customer | Study Number
SPSM | AG2-2006-074
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
SPSM | 1090699 | WPEK | KCPL | 50 | 2006-10-01 | 2007-10-01 | 2007-10-01 | 2008-10-01 | 0 | 528000 | 0 | 0
[9 empty] | 0 | 528000 | 0 | 0
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1090699 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1090699 | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | 2006-12-01 | 2008-10-01 | 2007-04-01
| GREENSBURG - JUDSON LARGE 115KV CKT 1 | 2007-04-01 | 2007-10-01
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1090699 | LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01
Customer | Study Number
SPSM | AG2-2006-124
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
SPSM | 1090705 | WPEK | KCPL | 50 | 2006-10-01 | 2007-10-01 | 2007-10-01 | 2008-10-01 | 0 | 528000 | 0 | 0
[9 empty] | 0 | 528000 | 0 | 0
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1090705 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1090699 | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | 2006-12-01 | 2008-10-01 | 2007-04-01
| GREENSBURG - JUDSON LARGE 115KV CKT 1 | 2007-04-01 | 2007-10-01
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1090705 | LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01
Customer | Study Number
UCU | AG2-2006-006
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
UCU | 1052923 | KCPL | MPS | 160 | 2010-06-01 | 2030-06-01 |  |  | 0 | 61862400 | 0 | 0
[9 empty] | 0 | 61862400 | 0 | 0
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1052923 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1052923 | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | 2006-12-01 | 2008-10-01 | 2007-04-01 | No
| Stranger - Thorton 115 kV | 2010-06-01 | 2010-06-01
| STRANGER CREEK TRANSFORMER CKT 2 | 2011-06-01 | 2011-06-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1052923 | IATAN - ST JOE 345KV CKT 1 | 2011-06-01 | 2011-06-01
Customer | Study Number
WRGS | AG2-2006-016
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
WRGS | 1076158 | KCPL | AMRN | 20 | 2010-06-01 | 2015-06-01 |  |  | 0 | 1080000 | 0 | 0
[9 empty] | 0 | 1080000 | 0 | 0
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1076158 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1076158 | Stranger - Thorton 115 kV | 2010-06-01 | 2010-06-01
| STRANGER CREEK TRANSFORMER CKT 2 | 2011-06-01 | 2011-06-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1076158 | IATAN - ST JOE 345KV CKT 1 | 2011-06-01 | 2011-06-01
Customer | Study Number
WRGS | AG2-2006-030
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
WRGS | 1086655 | OKGE | WR | 225 | 2006-10-01 | 2026-10-01 | 2009-07-01 | 2029-07-01 | 40500000 | 0 | 54896021 | 121313926
[9 empty] | 40500000 | 0 | 54896021 | 121313926
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1086655 | COFFEYVILLE TAP - DEARING 138KV CKT 1 AEPW Displacement | 6/1/2010* | 6/1/2010* |  |  | 40828 | 500000 | 136797
| COFFEYVILLE TAP - DEARING 138KV CKT 1 WERE Displacement | 6/1/2010* | 6/1/2010* |  |  | 94219 | 3000000 | 324491
| ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 Displacement | 2011-06-01 | 2011-06-01 |  |  | 0 | 5000000 | 0
| Sooner to Rose Hill 345 kV OKGE | 2016-06-01 | 2016-06-01 |  |  | 27380487 | 27500000 | 62306245
| Sooner to Rose Hill 345 kV WERE | 2016-06-01 | 2016-06-01 |  |  | 27380487 | 27500000 | 58546393
[5 empty] | Total | 54896021 | 63500000 | 121313926
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1086655 | COFFEYVILLE SUB - CRA 69KV CKT 1 | 6/1/2010* | 6/1/2010*
| COFFEYVILLE SUB - DEARING 69KV CKT 1 | 6/1/2010* | 6/1/2010*
| CRESWELL (CRESWL1X) 138/69/13.2KV TRANSFORMER | 2012-06-01 | 2012-06-01
| DEARING (DEARIN1X) 138/69/13.2KV TRANSFORMER CKT 1 | 2011-12-01 | 2011-12-01
| Evans - Grant - Chisolm Rebuild and Conversion Project | 2008-06-01 | 2009-06-01 |  | Yes
| GILL ENERGY CENTER EAST - INTERSTATE 138KV CKT 1 | 2012-06-01 | 2012-06-01
| Mooreland - Potter 345 kV SPS | 2015-06-01 | 2015-06-01
| Mooreland - Potter 345 kV WFEC | 2015-06-01 | 2015-06-01
| Mooreland 345/138 kV Transformer | 2015-06-01 | 2015-06-01
| POTTER COUNTY INTERCHANGE (POTTR CO) 345/230/13.2KV TRANSFORMER CKT 2 | 2015-06-01 | 2015-06-01
| Spearville - Mooreland 345 kV SUNC | 2015-06-01 | 2015-06-01
| Spearville - Mooreland 345 kV WFEC | 2015-06-01 | 2015-06-01
| STRANGER CREEK TRANSFORMER CKT 2 | 2011-06-01 | 2011-06-01
| TUCO INTERCHANGE 345/115KV TRANSFORMER CKT 1 | 2015-06-01 | 2015-06-01
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1086655 | LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1086655 | RENO - SUMMIT 345KV | 2011-01-01 | 2011-01-01
| WICHITA - RENO 345KV | 2006-12-01 | 2009-07-01 |  | Yes
* See Note 12 in Table 2
Customer | Study Number
EDE | AG2-2005-064
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
EDE | 973355 | KCPL | EDE | 100 | 2010-01-01 | 2030-01-01 |  |  | 3502843 | 0 | 4733572 | 15077273
[9 empty] | 3502843 | 0 | 4733572 | 15077273
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
973355 | SUB 110 - ORONOGO JCT. - SUB 167 - RIVERTON 161KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 3387204 | 5400000 | 10788850
| SUB 110 - ORONOGO JCT. (ORONOGO) 161/69/12.5KV TRANSFORMER CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 1346368 | 2000000 | 4288423
[5 empty] | Total | 4733572 | 7400000 | 15077273
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
973355 | BULL SHOALS - BULL SHOALS 161KV CKT 1 SWPA | 2011-06-01 | 2011-06-01
| RIVERSIDE CAPACITOR | 2015-06-01 | 2015-06-01
| Line - JOPLIN 59 161 kV - SUB 439 - STATELINE | 2016-06-01 | 2016-06-01
| Line - SUB 59 - JOPLIN 26TH ST. - SUB 258 - GATEWAY SOUTH | 2016-06-01 | 2016-06-01
| XFR - JOPLIN 59 161 kV - SUB 59 - JOPLIN 26TH ST. 69kV | 2016-06-01 | 2016-06-01
Customer | Study Number
INDP | AG1-2006-051
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
INDP | 1033791 | KCPL | INDN | 50 | 2010-06-01 | 2040-06-01 |  |  | 0 | 15840000 | 938195 | 3340156
[9 empty] | 0 | 15840000 | 938195 | 3340156
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1033791 | 166TH STREET - JAGGARD JUNCTION 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 213226 | 1000000 | 1105108.88
| 166TH STREET - JARBALO JUNCTION SWITCHING STATION 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 405130 | 1900000 | 577383.55
| JAGGARD JUNCTION - PENTAGON 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 319839 | 1500000 | 1657663.33
[5 empty] | Total | 938195 | 4400000 | 3340155.76
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1033791 | Stranger - Thorton 115 kV | 2009-06-01 | 2009-06-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1033791 | IATAN - ST JOE 345KV CKT 1 | 2011-06-01 | 2011-06-01
| IATAN5 161 - PLATTE CITY 161KV CKT 1 | 2011-06-01 | 2011-06-01
Note: Expansion Plan Project Stranger - Thorton 115 kV replaces 2006-AG1-AFS-4 assignment of STRANGER CREEK - NW LEAVENWORTH 115KV
Customer | Study Number
KCPS | AG1-2006-009
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
KCPS | 1179751 | KCPL | KCPL | 168 | 2009-06-01 | 2029-06-01 |  |  | 4161805 | 0 | 4161805 | 10566295
[9 empty] | 4161805 | 0 | 4161805 | 10566295
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1179751 | 166TH STREET - JAGGARD JUNCTION 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 786774 | 1000000 | 2927001.15
| 166TH STREET - JARBALO JUNCTION SWITCHING STATION 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 1494870 | 1900000 | 1529260.8
| COLLEGE - CRAIG 161KV CKT 1 | 2016-06-01 | 2016-06-01 |  |  | 700000 | 700000 | 1719531.39
| JAGGARD JUNCTION - PENTAGON 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 1180161 | 1500000 | 4390501.74
[5 empty] | Total | 4161805 | 5100000 | 10566295.08
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1179751 | Stranger - Thorton 115 kV | 2009-06-01 | 2009-06-01
| AVONDALE - GLADSTONE 161KV CKT 1 | 2014-06-01 | 2014-06-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1179751 | IATAN - ST JOE 345KV CKT 1 | 2011-06-01 | 2011-06-01
| IATAN5 161 - PLATTE CITY 161KV CKT 1 | 2011-06-01 | 2011-06-01
Note: Expansion Plan Project Stranger - Thorton 115 kV replaces 2006-AG1-AFS-4 assignment of STRANGER CREEK - NW LEAVENWORTH 115KV
Customer | Study Number
KCPS | GEN-2004-008
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
KCPS | 1115127 | KCPL | KCPL | 332 | 2009-06-01 | 2029-06-01 |  |  | 0 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0 | 0
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1115127 | None
[5 empty] | Total | 0 | 0 | 0

## Table 4
Transmission Owner | Upgrade | Solution | Earliest Data Upgrade Required (COD) | Estimated Date of Upgrade Completion (EOC) | Estimated Engineering & Construction Cost
AEPW | COFFEYVILLE TAP - DEARING 138KV CKT 1 AEPW Displacement | Rebuild 1.09 miles of line using 1590 ACSR | 2011-06-01 | 2011-06-01 | 500000
AEPW | SOUTHWEST SHREVEPORT (SW SHV 1) 345/138/13.8KV TRANSFORMER CKT 1 | Using IEEE Guide for Loading of Mineral-Oil Immersed Power Transformers (C57.91-2000) Re-rate the autos. Replace .two 138 kV breakers and five 138 kV switches. Reset relays and CTs | 2010-06-01 | 2010-06-01 | 1500000
AEPW | SOUTHWEST SHREVEPORT (SW SHV 2) 345/138/13.8KV TRANSFORMER CKT 2 | Using IEEE Guide for Loading of Mineral-Oil Immersed Power Transformers (C57.91-2000) Re-rate the autos. Replace .two 138 kV breakers and five 138 kV switches. Reset relays and CTs | 2010-06-01 | 2010-06-01 | 1500000
EMDE | SUB 110 - ORONOGO JCT. - SUB 167 - RIVERTON 161KV CKT 1 | Reconductor Oronogo 59467 to Riverton 59469 with Bundled 556 ACSR | 2011-06-01 | 2011-06-01 | 5400000
EMDE | SUB 110 - ORONOGO JCT. (ORONOGO) 161/69/12.5KV TRANSFORMER CKT 1 | Installl new 161/12 kV 22.4 transmer and take load off 69 kV system | 2011-06-01 | 2011-06-01 | 2000000
MIDW | ST JOHN CAPACITOR Displacement | 20MVar capacitor at ST John | 2008-06-01 | 2008-06-01 | 864000
OKGE | Sooner to Rose Hill 345 kV OKGE | New 345 kV line from Sooner to Oklahoma/Kansas | 2016-06-01 | 2016-06-01 | 27500000
SPS | GSEC Midway Interconnection #1 | New Delivery Point tapping 69 kV Tie Line from AEPW Shamrock to SPS Magic City | 2011-06-01 | 2011-06-01 | 70000
SPS | Mustang-San Andr-Amerada Hess 115KV Displacement | Terminate V53 at Mustang instead of Denver City - 3 mi of new 115 kV circuit. Mustang-San Andr-Amerada Hess 115 kV ckt | 2007-04-01 | 2008-06-01 | 1742892
SPS | YOAKUM COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 1 Displacement | Upgrade Transformer 230/115 kV 252 MVA | 2007-06-01 | 2008-06-01 | 2500000
WERE | 166TH STREET - JAGGARD JUNCTION 115KV CKT 1 | Tear down and rebuild 3.66 mile 166-Jaggard 115 kV line. | 2009-06-01 | 2009-06-01 | 1000000
WERE | 166TH STREET - JARBALO JUNCTION SWITCHING STATION 115KV CKT 1 | Tear down and rebuild 7.22 mile Jarbalo-166 115 kV line. | 2009-06-01 | 2009-06-01 | 1900000
WERE | COFFEYVILLE TAP - DEARING 138KV CKT 1 WERE Displacement | Tie Line, Rebuild 3.93 miles of 795 ACSR with 1590 ACSR. | 2011-06-01 | 2011-06-01 | 3000000
WERE | JAGGARD JUNCTION - PENTAGON 115KV CKT 1 | Tear down and rebuild Jaggard - Pentagon 115 kV line. | 2009-06-01 | 2009-06-01 | 1500000
WERE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 Displacement | Add third 345-138 kV transformer at Rose Hill | 2011-06-01 | 2011-06-01 | 5000000
WERE | Sooner to Rose Hill 345 kV WERE | New 345 kV line from Oklahoma/Kansas Stateline to Rose Hill | 2016-06-01 | 2016-06-01 | 27500000
Construction Pending Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Transmission Owner | Upgrade | Solution | Earliest Data Upgrade Required (COD) | Estimated Date of Upgrade Completion (EOC)
MIDW | HEIZER TO KNOLL 230KV | Convert Knoll to Heizer 115 kV line to 230kV (already constructed for 230kV). | 2007-06-01 | 2007-10-01
MIPU | IATAN5 161 - PLATTE CITY 161KV CKT 1 | Terminal Equipment | 2011-06-01 | 2011-06-01
MIPU | IATAN - ST JOE 345KV CKT 1 | Circuit Breaker | 2011-06-01 | 2011-06-01
SPS | TERRY COUNTY INTERCHANGE 115/69KV TRANSFORMERS | Upgrade both existing transformer by 10/1/2007 | 2007-06-01 | 2007-06-01
WERE | RENO - SUMMIT 345KV | Install new 50.55-mile 345 kV line from Reno county to Summit; 31 miles of 115 kV line between Circle and S Philips would be rebuilt as double circuit with the 345 kV line to minimize ROW impacts; Substation work required at Summit for new 345 kV terminal | 2011-01-01 | 2011-01-01
WERE | WICHITA - RENO 345KV | Build 345kV from Wichita to Reno Co | 2006-12-01 | 2009-07-01
WFEC | HAMON BUTLER - MOREWOOD 69KV CKT 1 | Reconductor 1/0 to 336 ACSR - 15.0 miles | 2006-12-01 | 2008-04-01
Expansion Plan Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Transmission Owner | Upgrade | Solution | Earliest Data Upgrade Required (COD) | Estimated Date of Upgrade Completion (EOC)
AEPW | ALUMAX TAP - NORTHWEST TEXARKANA 138KV CKT 1 | Rebuild 1.68 miles of 1024 ACAR with 2156 ACSR, Replace wavetrap & jumpers with 2156 ACSR. Replace Switch 2285 @ Alumax Tap. | 2008-06-01 | 2008-06-01
AEPW | CHAMBER SPRINGS - TONTITOWN 161KV CKT 1 | Reconductor 666 ACSR (11.6 mies)and 1272 ACSR (.1 mile) to Drake ACCC (2156 ACSR section 0.6 miles is not replaced) and remove the series reactors at Chamber Springs on the Chamber Springs to Tontitown 161 kV line | 2008-12-01 | 2007-06-01
AEPW | Chamber Springs - Tontitown 345 kV | New 345 kV Line and Tontitown 345/161 kV Transformer | 2008-06-01 | 2008-06-01
AEPW | Flint Creek - East Centerton 345 kV | New 345 kV Line and East Centerton 345/161 kV Transformer | 2011-06-01 | 2011-06-01
AEPW | LINWOOD - MCWILLIE STREET 138KV CKT 1 | Rebuild 2.09 miles of 666 ACSR with 1272 ACSR | 2007-06-01 | 2008-06-01
AEPW | Siloam Springs - South Fayetteville 161 kV | Convert Existing 69 kV Line to 161 kV Operation | 2015-06-01 | 2015-06-01
AEPW | THOMAS TAP - WEATHERFORD 69KV CKT 1 | Rebuild 0.9 miles of 4/0 ACSR with 795 ACSR. Replace Weatherford wavetrap. | 2014-06-01 | 2014-06-01
AEPW | WEATHERFORD SOUTHEAST (WTH_SE) 138/69/13.8KV TRANSFORMER CKT 1 | Install new 90 MVA Auto | 2013-06-01 | 2013-06-01
AEPW/WFEC | SNYDER AEPW- SNYDER WFEC INTERCONNECTION | New Tie line between AEPW's Snyder and WFEC's Snyder | 2016-06-01 | 2016-06-01
EMDE | Line - JOPLIN 59 161 kV - SUB 439 - STATELINE | Install new line from Sub #439 to new Sub Joplin 59. | 2016-06-01 | 2016-06-01
EMDE | Line - SUB 59 - JOPLIN 26TH ST. - SUB 258 - GATEWAY SOUTH | Reconductor 1.6 miles of 69kV Joplin sub 59 to GAT sub 258 with same conductor as 69kV Joplin sub 64 to Joplin sub 145 | 2016-06-01 | 2016-06-01
EMDE | XFR - JOPLIN 59 161 kV - SUB 59 - JOPLIN 26TH ST. 69kV | Install 3-wind transformer from 161 kV Joplin 59 bus to Sub #59 Joplin 26th St. | 2016-06-01 | 2016-06-01
KACP | AVONDALE - GLADSTONE 161KV CKT 1 | Replace 800 amp wavetrap at Gladstone with 1200 amp wavetrap | 2014-06-01 | 2014-06-01
MIDW | HAYS PLANT - SOUTH HAYS 115KV CKT 1 | Reconductor line | 2008-06-01 | 2009-06-01
MIDW | HAYS PLANT - VINE STREET 115KV CKT 1 | Reconductor line | 2008-06-01 | 2009-06-01
MIDW | HUNTSVILLE - ST JOHN 115KV CKT 1 | Rebuild Huntsville - St. John 115 kV line and replace CT, wavetrap, breakers, and relays. | 2014-06-01 | 2014-06-01
MIDW/WERE | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | Rebuild HEC - Huntsville 115 kV line and replace CT, wavetrap and relays. | 2014-06-01 | 2014-06-01
MIPU | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | Replace Wavetrap at Martin City | 2006-12-01 | 2008-10-01
OKGE | 5 TRIBES - HANCOCK 161KV CKT 1 | Replace 800A Wave Trap, increase Relay CTR to 1200-5A. | 2014-06-01 | 2014-06-01
OKGE | 5 TRIBES - PECAN CREEK 161KV CKT 1 | replace 636AS33 conductor with 795AS33 | 2014-06-01 | 2014-06-01
OKGE | AGENCY - PECAN CREEK 161KV CKT 1 | Replace Terminal Equipment | 2014-06-01 | 2014-06-01
OKGE | CANADIAN - CEDAR LANE 138KV CKT 1 | Replace 800A trap at Cedar Lane | 2015-06-01 | 2015-06-01
OKGE | CONTINENTAL BLACKS - OSAGE 69KV CKT 1 | Rebuild & Reconductor 0.57 Miles of 477AS33 to 477 ACCC/TW | 2016-06-01 | 2016-06-01
OKGE | PECAN CREEK (PECANCK1) 345/161/13.8KV TRANSFORMER CKT 2 | Add a 345/161 kV 369MVA transformer | 2014-06-01 | 2014-06-01
SPS | BC-EARTH INTERCHANGE 115KV | Install 1 - 14.4 MVar capacitor bank | 2016-06-01 | 2016-06-01
SPS | CURRY COUNTY INTERCHANGE - ROOSEVELT COUNTY INTERCHANGE 115KV CKT 2 | Upgrade Roosevelt to Curry 115 kV circuit w/795 ACSR | 2013-06-01 | 2013-06-01
SPS | Hart Interchange 230/115 kV | New 230/115 kV Hart Intg with 115 kV 397 ACSR ckt to Kress Int, 3-brkr 230 kV ring, 150 MVA auto, 115 kV terminal | 2011-06-01 | 2011-06-01
SPS | Hitchland 345 and 115 kV Interchange | Three breaker 345 kV bus, 345/115 kV transformer, five 115 kV breakers. | 2010-06-01 | 2010-06-01
SPS | KRESS INTERCHANGE 115/69KV TRANSFORMERS | Upgrade both existing transformer | 2007-04-01 | 2007-04-01
SPS | LC-SOL3 115KV | Install 14.4 MVAR cap at LC SOL | 2016-06-01 | 2016-06-01
SPS | Mooreland - Potter 345 kV SPS | New 345 kV line from Potter to Mooreland on wooden h-frame structures. | 2015-06-01 | 2015-06-01
SPS | MUSTANG STATION 230/115KV TRANSFORMER CKT 1 | Install 252 MVA Transformer | 2007-04-01 | 2008-06-01
SPS | Potter - Roosevelt 345KV | New 345 kV circuit from Potter - Roosevelt 2-795 ACSR & 345/230 kV 560 MVA transformer | 2013-06-01 | 2013-06-01
SPS | POTTER COUNTY INTERCHANGE (POTTR CO) 345/230/13.2KV TRANSFORMER CKT 2 | New 345/230 kV 560 MVA transformer | 2015-06-01 | 2015-06-01
SPS | Pringle - Etter 115 kV | Build New 115 kV line from Pringle to Etter | 2010-06-01 | 2010-06-01
SPS | ROOSEVELT COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 1 | Add 2nd transformer 230/115 kV 252 MVA | 2013-06-01 | 2013-06-01
SPS | Seven Rivers to Pecos to Potash Junction 230kV | Seven Rivers to Pecos to Potash Junction 230kV | 2007-06-01 | 2009-06-01
SPS | Stateline Project | Tap Elk City - Grapevine. New line from Stateline Tap to Graves Co. New 115/69xfmr at Graves Co. | 2014-06-01 | 2014-06-01
SPS | Tex-Hitchland-Sherman Tap 115 kV ckt | Route Sherman Tap to Texas Co in/out of New Hitchland Interchange | 2010-06-01 | 2010-06-01
SPS | TUCO INTERCHANGE 115/69KV TRANSFORMER | Move Load to 115 kV at TUCO | 2008-06-01 | 2008-06-01
SPS | TUCO INTERCHANGE 345/115KV TRANSFORMER CKT 1 | Install 345/115 kV Transformer at Tuco | 2015-06-01 | 2015-06-01
SUNC | Spearville - Mooreland 345 kV SUNC | New 345 kV line from Spearville to Kansas/Oklahoma Stateline | 2015-06-01 | 2015-06-01
WEPL | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 2007-06-01 | 2009-06-01
WEPL | GREENSBURG - JUDSON LARGE 115KV CKT 1 | Replace relaying | 2007-04-01 | 2007-10-01
WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 2007-06-01 | 2009-06-01
WERE | CIRCLEVILLE - HOYT HTI SWITCHING JUNCTION 115KV CKT 1 | Rebuild 16.66 mile Circleville-Hoyt HTI Junction 115 kV line. | 2006-12-01 | 2010-06-01
WERE | COFFEYVILLE SUB - CRA 69KV CKT 1 | Rebuild Coffeyville - CRA 69 kV line. | 2011-06-01 | 2011-06-01
WERE | COFFEYVILLE SUB - DEARING 69KV CKT 1 | Rebuild Dearing - Coffeyville 69 kV line. | 2011-06-01 | 2011-06-01
WERE | COUNTY LINE - HOOK JCT 115KV CKT 1 | Rebuild 2.52 mile line with 1192.5 kcmil ACSR | 2011-06-01 | 2011-06-01
WERE | COUNTY LINE - TECUMSEH HILL 115KV CKT 1 | Tear down and rebuild 5.32 mile Tecumseh Hill-County Line 115 kV line. | 2011-06-01 | 2011-06-01
WERE | CRESWELL (CRESWL1X) 138/69/13.2KV TRANSFORMER | Replace transformers | 2012-06-01 | 2012-06-01
WERE | DEARING (DEARIN1X) 138/69/13.2KV TRANSFORMER CKT 1 | 2nd Dearing 138-69 kV Transformer | 2011-12-01 | 2011-12-01
WERE | Evans - Grant - Chisolm Rebuild and Conversion Project | Build Evans - Grant 138 kV line, Convert Grant - Chisolm 69 kV line to 138 kV, Install New Grant 138/69 kV XFMR. And Rebuild Grant - Grant Jct. 69 kV line. | 2008-06-01 | 2009-06-01
WERE | GILL ENERGY CENTER EAST - GILLJCT269.0 69KV CKT 1 | Rebuild Gill-Gill Jct | 2007-06-01 | 2008-06-01
WERE | GILL ENERGY CENTER EAST - INTERSTATE 138KV CKT 1 | Replace wave trap | 2012-06-01 | 2012-06-01
WERE | GILL ENERGY CENTER EAST - MACARTHUR 69KV CKT 1 #1 | Replace bus, jumpers and disconnect switches at MacArthur 69 kV substation to increase line capacity to conductor rating | 2007-06-01 | 2007-07-01
WERE | HOOK JCT - TECUMSEH ENERGY CENTER 115KV CKT 1 #1 | Replace wave traps on TEC-County Line 115 kV line. | 2011-06-01 | 2011-06-01
WERE | HOOK JCT - TECUMSEH ENERGY CENTER 115KV CKT 1 #2 | Rebuild 1.52 mile line with 1192.5 kcmil ACSR | 2011-06-01 | 2011-06-01
WERE | NEOSHO - NORTHEAST PARSONS 138KV CKT 1 | Replace bus and Jumpers at NE Parsons 138 kV substation | 2013-06-01 | 2013-06-01
WERE | Stranger - Thorton 115 kV | Build Stranger - Thorton 115kV | 2009-06-01 | 2009-06-01
WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 2011-06-01 | 2011-06-01
WERE | TECUMSEH ENERGY CENTER - TECUMSEH HILL 115KV CKT 1 | Uprate 0.24 mile TEC-Tecumseh Hill 115 kV line to 100 degree operation. | 2010-06-01 | 2010-06-01
WFEC | ALTUS JCT TAP - RUSSELL 138KV CKT 1 | Change CT Ratio | 2014-06-01 | 2014-06-01
WFEC | Mooreland - Potter 345 kV WFEC | 345 kV line Terminal | 2015-06-01 | 2015-06-01
WFEC | Mooreland 345/138 kV Transformer | New Mooreland 345/138 kV Transformer | 2015-06-01 | 2015-06-01
WFEC | Spearville - Mooreland 345 kV WFEC | New 345 kV line from Kansas/Oklahoma Stateline to Mooreland | 2015-06-01 | 2015-06-01
Previously Assigned Aggregate Study Upgrades requiring credits to Previous Aggregate Study Customers
Transmission Owner | Upgrade | Solution | Earliest Data Upgrade Required (COD) | Estimated Date of Upgrade Completion (EOC)
AEPW | EXPLORER GLENPOOL - RIVERSIDE STATION 138KV CKT 1 AEPW | Reconductor 1.9 miles with ACCC. Replace wave trap jumpers at Riverside. | 2009-06-01 | 2009-06-01
KACP | LACYGNE - WEST GARDNER 345KV CKT 1 | KCPL Sponsored Project to Reconductor Line to be In-Service by 6/1/2006 | 2006-06-01 | 2006-06-01
OKGE | ARCADIA - REDBUD 345 KV CKT 1 | Sponsored Project to Uprate Terninal Equipment | 2006-06-01 | 2006-06-01
OKGE | ARCADIA - REDBUD 345 KV CKT 2 | Sponsored Project to Uprate Terninal Equipment | 2006-06-01 | 2006-06-01
OKGE | BEELINE - EXPLORER GLENPOOL 138KV CKT 1 | Reconductor .92miles of line with Drake ACCC/TW. | 2009-06-01 | 2009-06-01
OKGE | EXPLORER GLENPOOL - RIVERSIDE STATION 138KV CKT 1 OKGE | Reconductor 1.82 miles line with Drake ACCC/TW. | 2009-06-01 | 2009-06-01
OKGE | FPL SWITCH - MOORELAND 138KV CKT 1 OKGE | OGE would rebuild .18 miles of 267AS33 with 795AS33. This would raise OGE's summer and winter Rate B to 287MVA. The limit will still be at WFEC's Mooreland at 390A & 600A. | 2006-06-01 | 2008-04-01
WFEC | FPL SWITCH - MOORELAND 138KV CKT 1 WFEC | Upgrade terminal equipment FPL Sw & Mooreland | 2006-06-01 | 2008-04-01

## Table 5
Transmission Owner | Upgrade | Solution | Earliest Data Upgrade Required (COD) | Estimated Date of Upgrade Completion (EOC) | Estimated Engineering & Construction Cost
GSEC | GSEC Midway Interconnection #2 | Install 7.2 MVAR Capacitor at GSEC Midway 69 kV | 2011-06-01 | 2011-06-01 | 200000

## Table 6
Upgrade: | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 & CLAY CENTER - GREENLEAF 115KV CKT 1
Limiting Facility: | KELLY - SOUTH SENECA 115KV CKT 1
Direction: | From->To
Line Outage: | CONCORDIA - EAST MANHATTAN 230KV CKT 1
Flowgate: | 57217573371587585686112207SH
Date Redispatch Needed: | 6/1 - 10/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 Summer Shoulder
Reservation | Relief Amount | Aggregate Relief Amount
1090817 | 1.1018 | 3.0849
1090964 | 1.5424 | 3.0849
1090965 | 0.4407 | 3.0849
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.87935 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00423 | -0.88358 | 3
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.87935 | WERE | 'CHANUTE 69KV' | 46.617 | -0.00059 | -0.87876 | 4
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.87935 | WERE | 'CITY OF BURLINGTON 69KV' | 4.8 | -0.00067 | -0.87868 | 4
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.87935 | WERE | 'CITY OF ERIE 69KV' | 23.258 | -0.00059 | -0.87876 | 4
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.87935 | WERE | 'CITY OF FREDONIA 69KV' | 2.496 | -0.00067 | -0.87868 | 4
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.87935 | WERE | 'CITY OF GIRARD 69KV' | 2.989 | -0.00057 | -0.87878 | 4
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.87935 | WERE | 'CITY OF IOLA 69KV' | 19.865 | -0.00052 | -0.87883 | 4
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.87935 | WERE | 'CITY OF MULVANE 69KV' | 6.189 | -0.00183 | -0.87752 | 4
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.87935 | WERE | 'CITY OF WELLINGTON 69KV' | 31.07 | -0.00205 | -0.8773 | 4
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.87935 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.96 | -0.00067 | -0.87868 | 4
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.87935 | WERE | 'EVANS ENERGY CENTER 138KV' | 305 | -0.00181 | -0.87754 | 4
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.87935 | WERE | 'GILL ENERGY CENTER 138KV' | 77 | -0.00262 | -0.87673 | 4
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.87935 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | -0.00169 | -0.87766 | 4
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.87935 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | -0.00193 | -0.87742 | 4
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.87935 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.00179 | -0.88114 | 4
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.87935 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 230.2191 | 0.00132 | -0.88067 | 4
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.87935 | WERE | 'WACO 138KV' | 17.947 | -0.00253 | -0.87682 | 4
WEPL | 'RUSSELL 115KV' | 27.9 | -0.14239 | WEPL | 'GRAY COUNTY WIND FARM 115KV' | 73 | -0.02842 | -0.11397 | 27
WEPL | 'RUSSELL 115KV' | 27.9 | -0.14239 | WEPL | 'JUDSON LARGE 115KV' | 99.9321 | -0.02839 | -0.114 | 27
WERE | 'KNOLL 3 115 115KV' | 75 | -0.06968 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00423 | -0.07391 | 42
WERE | 'KNOLL 3 115 115KV' | 75 | -0.06968 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.00179 | -0.07147 | 43
WERE | 'KNOLL 3 115 115KV' | 75 | -0.06968 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 230.2191 | 0.00132 | -0.071 | 43
WERE | 'KNOLL 3 115 115KV' | 75 | -0.06968 | WERE | 'CITY OF ERIE 69KV' | 23.258 | -0.00059 | -0.06909 | 45
WERE | 'KNOLL 3 115 115KV' | 75 | -0.06968 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.96 | -0.00067 | -0.06901 | 45
WERE | 'KNOLL 3 115 115KV' | 75 | -0.06968 | WERE | 'EVANS ENERGY CENTER 138KV' | 305 | -0.00181 | -0.06787 | 45
WERE | 'KNOLL 3 115 115KV' | 75 | -0.06968 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | -0.00169 | -0.06799 | 45
WERE | 'KNOLL 3 115 115KV' | 75 | -0.06968 | WERE | 'GILL ENERGY CENTER 138KV' | 77 | -0.00262 | -0.06706 | 46
WERE | 'KNOLL 3 115 115KV' | 75 | -0.06968 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | -0.00193 | -0.06775 | 46
WERE | 'KNOLL 3 115 115KV' | 75 | -0.06968 | WERE | 'WACO 138KV' | 17.947 | -0.00253 | -0.06715 | 46
WERE | 'PAWNEE 115KV' | 999 | -0.03835 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00423 | -0.04258 | 72
WERE | 'RICE 115KV' | 999 | -0.03835 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00423 | -0.04258 | 72
WERE | 'PAWNEE 115KV' | 999 | -0.03835 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.00179 | -0.04014 | 77
WERE | 'RICE 115KV' | 999 | -0.03835 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.00179 | -0.04014 | 77
WERE | 'PAWNEE 115KV' | 999 | -0.03835 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 230.2191 | 0.00132 | -0.03967 | 78
WERE | 'RICE 115KV' | 999 | -0.03835 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 230.2191 | 0.00132 | -0.03967 | 78
WERE | 'PAWNEE 115KV' | 999 | -0.03835 | WERE | 'EVANS ENERGY CENTER 138KV' | 305 | -0.00181 | -0.03654 | 84
WERE | 'PAWNEE 115KV' | 999 | -0.03835 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | -0.00169 | -0.03666 | 84
WERE | 'RICE 115KV' | 999 | -0.03835 | WERE | 'EVANS ENERGY CENTER 138KV' | 305 | -0.00181 | -0.03654 | 84
WERE | 'RICE 115KV' | 999 | -0.03835 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | -0.00169 | -0.03666 | 84
WERE | 'PAWNEE 115KV' | 999 | -0.03835 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | -0.00193 | -0.03642 | 85
WERE | 'RICE 115KV' | 999 | -0.03835 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | -0.00193 | -0.03642 | 85
WERE | 'PAWNEE 115KV' | 999 | -0.03835 | WERE | 'GILL ENERGY CENTER 138KV' | 77 | -0.00262 | -0.03573 | 86
WERE | 'RICE 115KV' | 999 | -0.03835 | WERE | 'GILL ENERGY CENTER 138KV' | 77 | -0.00262 | -0.03573 | 86
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.0258 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00423 | -0.03003 | 103
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.02581 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00423 | -0.03004 | 103
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 & CLAY CENTER - GREENLEAF 115KV CKT 1
Limiting Facility: | KELLY - SOUTH SENECA 115KV CKT 1
Direction: | From->To
Line Outage: | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1
Flowgate: | 57217573371CONCNCORD66312207SH
Date Redispatch Needed: | 6/1 - 10/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 Summer Shoulder
Reservation | Relief Amount | Aggregate Relief Amount
1090817 | 1.1018 | 3.0849
1090964 | 1.5424 | 3.0849
1090965 | 0.4407 | 3.0849
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.87935 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00423 | -0.88358 | 3
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.87935 | WERE | 'CHANUTE 69KV' | 46.617 | -0.00059 | -0.87876 | 4
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.87935 | WERE | 'CITY OF BURLINGTON 69KV' | 4.8 | -0.00067 | -0.87868 | 4
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.87935 | WERE | 'CITY OF ERIE 69KV' | 23.258 | -0.00059 | -0.87876 | 4
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.87935 | WERE | 'CITY OF FREDONIA 69KV' | 2.496 | -0.00067 | -0.87868 | 4
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.87935 | WERE | 'CITY OF GIRARD 69KV' | 2.989 | -0.00057 | -0.87878 | 4
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.87935 | WERE | 'CITY OF IOLA 69KV' | 19.865 | -0.00052 | -0.87883 | 4
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.87935 | WERE | 'CITY OF MULVANE 69KV' | 6.189 | -0.00183 | -0.87752 | 4
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.87935 | WERE | 'CITY OF WELLINGTON 69KV' | 31.07 | -0.00205 | -0.8773 | 4
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.87935 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.96 | -0.00067 | -0.87868 | 4
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.87935 | WERE | 'EVANS ENERGY CENTER 138KV' | 305 | -0.00181 | -0.87754 | 4
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.87935 | WERE | 'GILL ENERGY CENTER 138KV' | 77 | -0.00262 | -0.87673 | 4
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.87935 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | -0.00169 | -0.87766 | 4
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.87935 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | -0.00193 | -0.87742 | 4
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.87935 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.00179 | -0.88114 | 4
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.87935 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 230.2191 | 0.00132 | -0.88067 | 4
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.87935 | WERE | 'WACO 138KV' | 17.947 | -0.00253 | -0.87682 | 4
WEPL | 'RUSSELL 115KV' | 27.9 | -0.14239 | WEPL | 'GRAY COUNTY WIND FARM 115KV' | 73 | -0.02842 | -0.11397 | 27
WEPL | 'RUSSELL 115KV' | 27.9 | -0.14239 | WEPL | 'JUDSON LARGE 115KV' | 99.9321 | -0.02839 | -0.114 | 27
WERE | 'KNOLL 3 115 115KV' | 75 | -0.06968 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00423 | -0.07391 | 42
WERE | 'KNOLL 3 115 115KV' | 75 | -0.06968 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.00179 | -0.07147 | 43
WERE | 'KNOLL 3 115 115KV' | 75 | -0.06968 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 230.2191 | 0.00132 | -0.071 | 43
WERE | 'KNOLL 3 115 115KV' | 75 | -0.06968 | WERE | 'CITY OF ERIE 69KV' | 23.258 | -0.00059 | -0.06909 | 45
WERE | 'KNOLL 3 115 115KV' | 75 | -0.06968 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.96 | -0.00067 | -0.06901 | 45
WERE | 'KNOLL 3 115 115KV' | 75 | -0.06968 | WERE | 'EVANS ENERGY CENTER 138KV' | 305 | -0.00181 | -0.06787 | 45
WERE | 'KNOLL 3 115 115KV' | 75 | -0.06968 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | -0.00169 | -0.06799 | 45
WERE | 'KNOLL 3 115 115KV' | 75 | -0.06968 | WERE | 'GILL ENERGY CENTER 138KV' | 77 | -0.00262 | -0.06706 | 46
WERE | 'KNOLL 3 115 115KV' | 75 | -0.06968 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | -0.00193 | -0.06775 | 46
WERE | 'KNOLL 3 115 115KV' | 75 | -0.06968 | WERE | 'WACO 138KV' | 17.947 | -0.00253 | -0.06715 | 46
WERE | 'PAWNEE 115KV' | 999 | -0.03835 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00423 | -0.04258 | 72
WERE | 'RICE 115KV' | 999 | -0.03835 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00423 | -0.04258 | 72
WERE | 'PAWNEE 115KV' | 999 | -0.03835 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.00179 | -0.04014 | 77
WERE | 'RICE 115KV' | 999 | -0.03835 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.00179 | -0.04014 | 77
WERE | 'PAWNEE 115KV' | 999 | -0.03835 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 230.2191 | 0.00132 | -0.03967 | 78
WERE | 'RICE 115KV' | 999 | -0.03835 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 230.2191 | 0.00132 | -0.03967 | 78
WERE | 'PAWNEE 115KV' | 999 | -0.03835 | WERE | 'EVANS ENERGY CENTER 138KV' | 305 | -0.00181 | -0.03654 | 84
WERE | 'PAWNEE 115KV' | 999 | -0.03835 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | -0.00169 | -0.03666 | 84
WERE | 'RICE 115KV' | 999 | -0.03835 | WERE | 'EVANS ENERGY CENTER 138KV' | 305 | -0.00181 | -0.03654 | 84
WERE | 'RICE 115KV' | 999 | -0.03835 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | -0.00169 | -0.03666 | 84
WERE | 'PAWNEE 115KV' | 999 | -0.03835 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | -0.00193 | -0.03642 | 85
WERE | 'RICE 115KV' | 999 | -0.03835 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | -0.00193 | -0.03642 | 85
WERE | 'PAWNEE 115KV' | 999 | -0.03835 | WERE | 'GILL ENERGY CENTER 138KV' | 77 | -0.00262 | -0.03573 | 86
WERE | 'RICE 115KV' | 999 | -0.03835 | WERE | 'GILL ENERGY CENTER 138KV' | 77 | -0.00262 | -0.03573 | 86
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.0258 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00423 | -0.03003 | 103
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.02581 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00423 | -0.03004 | 103
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | CIRCLEVILLE - HOYT HTI SWITCHING JUNCTION 115KV CKT 1
Limiting Facility: | CIRCLEVILLE - HOYT HTI SWITCHING JUNCTION 115KV CKT 1
Direction: | To->From
Line Outage: | CONCORDIA - EAST MANHATTAN 230KV CKT 1
Flowgate: | 57152571651587585686114406WP
Date Redispatch Needed: | 12/1/06 - 4/1/07
Season Flowgate Identified: | 2006 Winter Peak
Reservation | Relief Amount | Aggregate Relief Amount
1090964 | 0.19104 | 0.25472
1090965 | 0.06368 | 0.25472
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'HOLTON 115KV' | 19.8 | -0.67909 | WERE | 'CHANUTE 69KV' | 35.344 | 0.00472 | -0.68381 | 0
WERE | 'HOLTON 115KV' | 19.8 | -0.67909 | WERE | 'CITY OF AUGUSTA 69KV' | 17.252 | -0.00279 | -0.6763 | 0
WERE | 'HOLTON 115KV' | 19.8 | -0.67909 | WERE | 'CITY OF BURLINGTON 69KV' | 4.8 | 0.00844 | -0.68753 | 0
WERE | 'HOLTON 115KV' | 19.8 | -0.67909 | WERE | 'CITY OF ERIE 69KV' | 1.998 | 0.00472 | -0.68381 | 0
WERE | 'HOLTON 115KV' | 19.8 | -0.67909 | WERE | 'CITY OF FREDONIA 69KV' | 1.298 | 0.00377 | -0.68286 | 0
WERE | 'HOLTON 115KV' | 19.8 | -0.67909 | WERE | 'CITY OF GIRARD 69KV' | 1.493 | 0.00585 | -0.68494 | 0
WERE | 'HOLTON 115KV' | 19.8 | -0.67909 | WERE | 'CITY OF IOLA 69KV' | 13.978 | 0.00547 | -0.68456 | 0
WERE | 'HOLTON 115KV' | 19.8 | -0.67909 | WERE | 'CITY OF MULVANE 69KV' | 3.694 | 0.00398 | -0.68307 | 0
WERE | 'HOLTON 115KV' | 19.8 | -0.67909 | WERE | 'CITY OF WELLINGTON 69KV' | 24 | 0.00392 | -0.68301 | 0
WERE | 'HOLTON 115KV' | 19.8 | -0.67909 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.00844 | -0.68753 | 0
WERE | 'HOLTON 115KV' | 19.8 | -0.67909 | WERE | 'COLBY 115KV' | 6.6395 | -0.01029 | -0.6688 | 0
WERE | 'HOLTON 115KV' | 19.8 | -0.67909 | WERE | 'EVANS ENERGY CENTER 138KV' | 118.696 | 0.00599 | -0.68508 | 0
WERE | 'HOLTON 115KV' | 19.8 | -0.67909 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 40 | 0.01275 | -0.69184 | 0
WERE | 'HOLTON 115KV' | 19.8 | -0.67909 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.03451 | -0.7136 | 0
WERE | 'HOLTON 115KV' | 19.8 | -0.67909 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.03481 | -0.7139 | 0
WERE | 'HOLTON 115KV' | 19.8 | -0.67909 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.0283 | -0.70739 | 0
WERE | 'HOLTON 115KV' | 19.8 | -0.67909 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 225.5185 | 0.02863 | -0.70772 | 0
WERE | 'HOLTON 115KV' | 19.8 | -0.67909 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.72266 | 0
WERE | 'HOLTON 115KV' | 19.8 | -0.67909 | WERE | 'WACO 138KV' | 17.953 | 0.00468 | -0.68377 | 0
WERE | 'BROWN COUNTY 115KV' | 5.5 | -0.32638 | WERE | 'CHANUTE 69KV' | 35.344 | 0.00472 | -0.3311 | 1
WERE | 'BROWN COUNTY 115KV' | 5.5 | -0.32638 | WERE | 'CITY OF AUGUSTA 69KV' | 17.252 | -0.00279 | -0.32359 | 1
WERE | 'BROWN COUNTY 115KV' | 5.5 | -0.32638 | WERE | 'CITY OF BURLINGTON 69KV' | 4.8 | 0.00844 | -0.33482 | 1
WERE | 'BROWN COUNTY 115KV' | 5.5 | -0.32638 | WERE | 'CITY OF ERIE 69KV' | 1.998 | 0.00472 | -0.3311 | 1
WERE | 'BROWN COUNTY 115KV' | 5.5 | -0.32638 | WERE | 'CITY OF FREDONIA 69KV' | 1.298 | 0.00377 | -0.33015 | 1
WERE | 'BROWN COUNTY 115KV' | 5.5 | -0.32638 | WERE | 'CITY OF GIRARD 69KV' | 1.493 | 0.00585 | -0.33223 | 1
WERE | 'BROWN COUNTY 115KV' | 5.5 | -0.32638 | WERE | 'CITY OF IOLA 69KV' | 13.978 | 0.00547 | -0.33185 | 1
WERE | 'BROWN COUNTY 115KV' | 5.5 | -0.32638 | WERE | 'CITY OF MULVANE 69KV' | 3.694 | 0.00398 | -0.33036 | 1
WERE | 'BROWN COUNTY 115KV' | 5.5 | -0.32638 | WERE | 'CITY OF WELLINGTON 69KV' | 24 | 0.00392 | -0.3303 | 1
WERE | 'BROWN COUNTY 115KV' | 5.5 | -0.32638 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.00844 | -0.33482 | 1
WERE | 'BROWN COUNTY 115KV' | 5.5 | -0.32638 | WERE | 'COLBY 115KV' | 6.6395 | -0.01029 | -0.31609 | 1
WERE | 'BROWN COUNTY 115KV' | 5.5 | -0.32638 | WERE | 'EVANS ENERGY CENTER 138KV' | 118.696 | 0.00599 | -0.33237 | 1
WERE | 'BROWN COUNTY 115KV' | 5.5 | -0.32638 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 40 | 0.01275 | -0.33913 | 1
WERE | 'BROWN COUNTY 115KV' | 5.5 | -0.32638 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.03451 | -0.36089 | 1
WERE | 'BROWN COUNTY 115KV' | 5.5 | -0.32638 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.03481 | -0.36119 | 1
WERE | 'BROWN COUNTY 115KV' | 5.5 | -0.32638 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.0283 | -0.35468 | 1
WERE | 'BROWN COUNTY 115KV' | 5.5 | -0.32638 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 225.5185 | 0.02863 | -0.35501 | 1
WERE | 'BROWN COUNTY 115KV' | 5.5 | -0.32638 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.36995 | 1
WERE | 'BROWN COUNTY 115KV' | 5.5 | -0.32638 | WERE | 'WACO 138KV' | 17.953 | 0.00468 | -0.33106 | 1
WEPL | 'CLIFTON 115KV' | 70 | -0.1882 | WEPL | 'GRAY COUNTY WIND FARM 115KV' | 36 | -0.00502 | -0.18318 | 1
WEPL | 'CLIFTON 115KV' | 70 | -0.1882 | WEPL | 'JUDSON LARGE 115KV' | 42.102 | -0.00501 | -0.18319 | 1
WEPL | 'GREENLEAF 115KV' | 14.2 | -0.21434 | WEPL | 'GRAY COUNTY WIND FARM 115KV' | 36 | -0.00502 | -0.20932 | 1
WEPL | 'GREENLEAF 115KV' | 14.2 | -0.21434 | WEPL | 'JUDSON LARGE 115KV' | 42.102 | -0.00501 | -0.20933 | 1
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.30778 | WERE | 'CHANUTE 69KV' | 35.344 | 0.00472 | -0.3125 | 1
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.30778 | WERE | 'CITY OF AUGUSTA 69KV' | 17.252 | -0.00279 | -0.30499 | 1
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.30778 | WERE | 'CITY OF BURLINGTON 69KV' | 4.8 | 0.00844 | -0.31622 | 1
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.30778 | WERE | 'CITY OF ERIE 69KV' | 1.998 | 0.00472 | -0.3125 | 1
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.30778 | WERE | 'CITY OF FREDONIA 69KV' | 1.298 | 0.00377 | -0.31155 | 1
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.30778 | WERE | 'CITY OF GIRARD 69KV' | 1.493 | 0.00585 | -0.31363 | 1
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.30778 | WERE | 'CITY OF IOLA 69KV' | 13.978 | 0.00547 | -0.31325 | 1
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.30778 | WERE | 'CITY OF MULVANE 69KV' | 3.694 | 0.00398 | -0.31176 | 1
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.30778 | WERE | 'CITY OF WELLINGTON 69KV' | 24 | 0.00392 | -0.3117 | 1
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.30778 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.00844 | -0.31622 | 1
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.30778 | WERE | 'COLBY 115KV' | 6.6395 | -0.01029 | -0.29749 | 1
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.30778 | WERE | 'EVANS ENERGY CENTER 138KV' | 118.696 | 0.00599 | -0.31377 | 1
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.30778 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 40 | 0.01275 | -0.32053 | 1
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.30778 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.03451 | -0.34229 | 1
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.30778 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.03481 | -0.34259 | 1
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.30778 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.0283 | -0.33608 | 1
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.30778 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 225.5185 | 0.02863 | -0.33641 | 1
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.30778 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.35135 | 1
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.30778 | WERE | 'WACO 138KV' | 17.953 | 0.00468 | -0.31246 | 1
WEPL | 'BELOIT 115KV' | 16.6 | -0.12815 | WEPL | 'GRAY COUNTY WIND FARM 115KV' | 36 | -0.00502 | -0.12313 | 2
WEPL | 'BELOIT 115KV' | 16.6 | -0.12815 | WEPL | 'JUDSON LARGE 115KV' | 42.102 | -0.00501 | -0.12314 | 2
WEPL | 'SMITH CENTER 115KV' | 6.15 | -0.09275 | WEPL | 'GRAY COUNTY WIND FARM 115KV' | 36 | -0.00502 | -0.08773 | 3
WEPL | 'SMITH CENTER 115KV' | 6.15 | -0.09275 | WEPL | 'JUDSON LARGE 115KV' | 42.102 | -0.00501 | -0.08774 | 3
WERE | 'ATWOOD 115KV' | 4 | -0.01002 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.05359 | 5
WERE | 'CITY OF AUGUSTA 69KV' | 10.088 | -0.00279 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.04636 | 5
WERE | 'COLBY 115KV' | 6.3605 | -0.01029 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.05386 | 5
WERE | 'GETTY 69KV' | 35 | -0.00763 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.0512 | 5
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.0043 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.04787 | 5
WERE | 'KNOLL 3 115 115KV' | 75 | -0.00767 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.05124 | 5
WERE | 'ATWOOD 115KV' | 4 | -0.01002 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.03451 | -0.04453 | 6
WERE | 'ATWOOD 115KV' | 4 | -0.01002 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.03481 | -0.04483 | 6
WERE | 'CITY OF FREDONIA 69KV' | 8.996 | 0.00377 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.0398 | 6
WERE | 'CITY OF MULVANE 69KV' | 12.096 | 0.00398 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.03959 | 6
WERE | 'CITY OF NEODESHA 69KV' | 4.5 | 0.00402 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.03955 | 6
WERE | 'CITY OF WELLINGTON 69KV' | 19.5 | 0.00392 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.03965 | 6
WERE | 'CITY OF WINFIELD 69KV' | 40 | 0.00302 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.04055 | 6
WERE | 'COLBY 115KV' | 6.3605 | -0.01029 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.03451 | -0.0448 | 6
WERE | 'COLBY 115KV' | 6.3605 | -0.01029 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.03481 | -0.0451 | 6
WERE | 'GETTY 69KV' | 35 | -0.00763 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.03451 | -0.04214 | 6
WERE | 'GETTY 69KV' | 35 | -0.00763 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.03481 | -0.04244 | 6
WERE | 'KNOLL 3 115 115KV' | 75 | -0.00767 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.03451 | -0.04218 | 6
WERE | 'KNOLL 3 115 115KV' | 75 | -0.00767 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.03481 | -0.04248 | 6
WERE | 'LYONS 115KV' | 999 | 0.00428 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.03929 | 6
WERE | 'OXFORD 138KV' | 3 | 0.00366 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.03991 | 6
WERE | 'PAWNEE 115KV' | 999 | -0.00053 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.0441 | 6
WERE | 'RICE 115KV' | 999 | -0.00053 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.0441 | 6
WERE | 'ST JOHN 115KV' | 7.5 | -0.00053 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.0441 | 6
WERE | 'ATWOOD 115KV' | 4 | -0.01002 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.0283 | -0.03832 | 7
WERE | 'ATWOOD 115KV' | 4 | -0.01002 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 225.5185 | 0.02863 | -0.03865 | 7
WERE | 'CHANUTE 69KV' | 52.456 | 0.00472 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.03885 | 7
WERE | 'CITY OF AUGUSTA 69KV' | 10.088 | -0.00279 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.03451 | -0.0373 | 7
WERE | 'CITY OF AUGUSTA 69KV' | 10.088 | -0.00279 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.03481 | -0.0376 | 7
WERE | 'CITY OF BURLINGTON 69KV' | 7.7 | 0.00844 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.03513 | 7
WERE | 'CITY OF ERIE 69KV' | 24.532 | 0.00472 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.03885 | 7
WERE | 'CITY OF GIRARD 69KV' | 9.207 | 0.00585 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.03772 | 7
WERE | 'CITY OF IOLA 69KV' | 23.65 | 0.00547 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.0381 | 7
WERE | 'COLBY 115KV' | 6.3605 | -0.01029 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.0283 | -0.03859 | 7
WERE | 'COLBY 115KV' | 6.3605 | -0.01029 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 225.5185 | 0.02863 | -0.03892 | 7
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | CIRCLEVILLE - HOYT HTI SWITCHING JUNCTION 115KV CKT 1
Limiting Facility: | CIRCLEVILLE - HOYT HTI SWITCHING JUNCTION 115KV CKT 1
Direction: | To->From
Line Outage: | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1
Flowgate: | 57152571651CONCNCORD66314406WP
Date Redispatch Needed: | 12/1/06 - 4/1/07
Season Flowgate Identified: | 2006 Winter Peak
Reservation | Relief Amount | Aggregate Relief Amount
1090964 | 0.1592 | 0.22288
1090965 | 0.06368 | 0.22288
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'HOLTON 115KV' | 19.8 | -0.67909 | WERE | 'CHANUTE 69KV' | 35.344 | 0.00472 | -0.68381 | 0
WERE | 'HOLTON 115KV' | 19.8 | -0.67909 | WERE | 'CITY OF AUGUSTA 69KV' | 17.252 | -0.00279 | -0.6763 | 0
WERE | 'HOLTON 115KV' | 19.8 | -0.67909 | WERE | 'CITY OF BURLINGTON 69KV' | 4.8 | 0.00844 | -0.68753 | 0
WERE | 'HOLTON 115KV' | 19.8 | -0.67909 | WERE | 'CITY OF ERIE 69KV' | 1.998 | 0.00472 | -0.68381 | 0
WERE | 'HOLTON 115KV' | 19.8 | -0.67909 | WERE | 'CITY OF FREDONIA 69KV' | 1.298 | 0.00377 | -0.68286 | 0
WERE | 'HOLTON 115KV' | 19.8 | -0.67909 | WERE | 'CITY OF GIRARD 69KV' | 1.493 | 0.00585 | -0.68494 | 0
WERE | 'HOLTON 115KV' | 19.8 | -0.67909 | WERE | 'CITY OF IOLA 69KV' | 13.978 | 0.00547 | -0.68456 | 0
WERE | 'HOLTON 115KV' | 19.8 | -0.67909 | WERE | 'CITY OF MULVANE 69KV' | 3.694 | 0.00398 | -0.68307 | 0
WERE | 'HOLTON 115KV' | 19.8 | -0.67909 | WERE | 'CITY OF WELLINGTON 69KV' | 24 | 0.00392 | -0.68301 | 0
WERE | 'HOLTON 115KV' | 19.8 | -0.67909 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.00844 | -0.68753 | 0
WERE | 'HOLTON 115KV' | 19.8 | -0.67909 | WERE | 'COLBY 115KV' | 6.6395 | -0.01029 | -0.6688 | 0
WERE | 'HOLTON 115KV' | 19.8 | -0.67909 | WERE | 'EVANS ENERGY CENTER 138KV' | 118.696 | 0.00599 | -0.68508 | 0
WERE | 'HOLTON 115KV' | 19.8 | -0.67909 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 40 | 0.01275 | -0.69184 | 0
WERE | 'HOLTON 115KV' | 19.8 | -0.67909 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.03451 | -0.7136 | 0
WERE | 'HOLTON 115KV' | 19.8 | -0.67909 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.03481 | -0.7139 | 0
WERE | 'HOLTON 115KV' | 19.8 | -0.67909 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.0283 | -0.70739 | 0
WERE | 'HOLTON 115KV' | 19.8 | -0.67909 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 225.5185 | 0.02863 | -0.70772 | 0
WERE | 'HOLTON 115KV' | 19.8 | -0.67909 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.72266 | 0
WERE | 'HOLTON 115KV' | 19.8 | -0.67909 | WERE | 'WACO 138KV' | 17.953 | 0.00468 | -0.68377 | 0
WERE | 'BROWN COUNTY 115KV' | 5.5 | -0.32638 | WERE | 'CHANUTE 69KV' | 35.344 | 0.00472 | -0.3311 | 1
WERE | 'BROWN COUNTY 115KV' | 5.5 | -0.32638 | WERE | 'CITY OF AUGUSTA 69KV' | 17.252 | -0.00279 | -0.32359 | 1
WERE | 'BROWN COUNTY 115KV' | 5.5 | -0.32638 | WERE | 'CITY OF BURLINGTON 69KV' | 4.8 | 0.00844 | -0.33482 | 1
WERE | 'BROWN COUNTY 115KV' | 5.5 | -0.32638 | WERE | 'CITY OF ERIE 69KV' | 1.998 | 0.00472 | -0.3311 | 1
WERE | 'BROWN COUNTY 115KV' | 5.5 | -0.32638 | WERE | 'CITY OF FREDONIA 69KV' | 1.298 | 0.00377 | -0.33015 | 1
WERE | 'BROWN COUNTY 115KV' | 5.5 | -0.32638 | WERE | 'CITY OF GIRARD 69KV' | 1.493 | 0.00585 | -0.33223 | 1
WERE | 'BROWN COUNTY 115KV' | 5.5 | -0.32638 | WERE | 'CITY OF IOLA 69KV' | 13.978 | 0.00547 | -0.33185 | 1
WERE | 'BROWN COUNTY 115KV' | 5.5 | -0.32638 | WERE | 'CITY OF MULVANE 69KV' | 3.694 | 0.00398 | -0.33036 | 1
WERE | 'BROWN COUNTY 115KV' | 5.5 | -0.32638 | WERE | 'CITY OF WELLINGTON 69KV' | 24 | 0.00392 | -0.3303 | 1
WERE | 'BROWN COUNTY 115KV' | 5.5 | -0.32638 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.00844 | -0.33482 | 1
WERE | 'BROWN COUNTY 115KV' | 5.5 | -0.32638 | WERE | 'COLBY 115KV' | 6.6395 | -0.01029 | -0.31609 | 1
WERE | 'BROWN COUNTY 115KV' | 5.5 | -0.32638 | WERE | 'EVANS ENERGY CENTER 138KV' | 118.696 | 0.00599 | -0.33237 | 1
WERE | 'BROWN COUNTY 115KV' | 5.5 | -0.32638 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 40 | 0.01275 | -0.33913 | 1
WERE | 'BROWN COUNTY 115KV' | 5.5 | -0.32638 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.03451 | -0.36089 | 1
WERE | 'BROWN COUNTY 115KV' | 5.5 | -0.32638 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.03481 | -0.36119 | 1
WERE | 'BROWN COUNTY 115KV' | 5.5 | -0.32638 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.0283 | -0.35468 | 1
WERE | 'BROWN COUNTY 115KV' | 5.5 | -0.32638 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 225.5185 | 0.02863 | -0.35501 | 1
WERE | 'BROWN COUNTY 115KV' | 5.5 | -0.32638 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.36995 | 1
WERE | 'BROWN COUNTY 115KV' | 5.5 | -0.32638 | WERE | 'WACO 138KV' | 17.953 | 0.00468 | -0.33106 | 1
WEPL | 'CLIFTON 115KV' | 70 | -0.1882 | WEPL | 'GRAY COUNTY WIND FARM 115KV' | 36 | -0.00502 | -0.18318 | 1
WEPL | 'CLIFTON 115KV' | 70 | -0.1882 | WEPL | 'JUDSON LARGE 115KV' | 42.102 | -0.00501 | -0.18319 | 1
WEPL | 'GREENLEAF 115KV' | 14.2 | -0.21434 | WEPL | 'GRAY COUNTY WIND FARM 115KV' | 36 | -0.00502 | -0.20932 | 1
WEPL | 'GREENLEAF 115KV' | 14.2 | -0.21434 | WEPL | 'JUDSON LARGE 115KV' | 42.102 | -0.00501 | -0.20933 | 1
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.30778 | WERE | 'CHANUTE 69KV' | 35.344 | 0.00472 | -0.3125 | 1
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.30778 | WERE | 'CITY OF AUGUSTA 69KV' | 17.252 | -0.00279 | -0.30499 | 1
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.30778 | WERE | 'CITY OF BURLINGTON 69KV' | 4.8 | 0.00844 | -0.31622 | 1
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.30778 | WERE | 'CITY OF ERIE 69KV' | 1.998 | 0.00472 | -0.3125 | 1
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.30778 | WERE | 'CITY OF FREDONIA 69KV' | 1.298 | 0.00377 | -0.31155 | 1
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.30778 | WERE | 'CITY OF GIRARD 69KV' | 1.493 | 0.00585 | -0.31363 | 1
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.30778 | WERE | 'CITY OF IOLA 69KV' | 13.978 | 0.00547 | -0.31325 | 1
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.30778 | WERE | 'CITY OF MULVANE 69KV' | 3.694 | 0.00398 | -0.31176 | 1
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.30778 | WERE | 'CITY OF WELLINGTON 69KV' | 24 | 0.00392 | -0.3117 | 1
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.30778 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.00844 | -0.31622 | 1
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.30778 | WERE | 'COLBY 115KV' | 6.6395 | -0.01029 | -0.29749 | 1
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.30778 | WERE | 'EVANS ENERGY CENTER 138KV' | 118.696 | 0.00599 | -0.31377 | 1
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.30778 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 40 | 0.01275 | -0.32053 | 1
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.30778 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.03451 | -0.34229 | 1
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.30778 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.03481 | -0.34259 | 1
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.30778 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.0283 | -0.33608 | 1
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.30778 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 225.5185 | 0.02863 | -0.33641 | 1
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.30778 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.35135 | 1
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.30778 | WERE | 'WACO 138KV' | 17.953 | 0.00468 | -0.31246 | 1
WEPL | 'BELOIT 115KV' | 16.6 | -0.12815 | WEPL | 'GRAY COUNTY WIND FARM 115KV' | 36 | -0.00502 | -0.12313 | 2
WEPL | 'BELOIT 115KV' | 16.6 | -0.12815 | WEPL | 'JUDSON LARGE 115KV' | 42.102 | -0.00501 | -0.12314 | 2
WEPL | 'SMITH CENTER 115KV' | 6.15 | -0.09275 | WEPL | 'GRAY COUNTY WIND FARM 115KV' | 36 | -0.00502 | -0.08773 | 3
WEPL | 'SMITH CENTER 115KV' | 6.15 | -0.09275 | WEPL | 'JUDSON LARGE 115KV' | 42.102 | -0.00501 | -0.08774 | 3
WERE | 'ATWOOD 115KV' | 4 | -0.01002 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.05359 | 4
WERE | 'COLBY 115KV' | 6.3605 | -0.01029 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.05386 | 4
WERE | 'GETTY 69KV' | 35 | -0.00763 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.0512 | 4
WERE | 'KNOLL 3 115 115KV' | 75 | -0.00767 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.05124 | 4
WERE | 'ATWOOD 115KV' | 4 | -0.01002 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.03451 | -0.04453 | 5
WERE | 'ATWOOD 115KV' | 4 | -0.01002 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.03481 | -0.04483 | 5
WERE | 'CITY OF AUGUSTA 69KV' | 10.088 | -0.00279 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.04636 | 5
WERE | 'CITY OF WINFIELD 69KV' | 40 | 0.00302 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.04055 | 5
WERE | 'COLBY 115KV' | 6.3605 | -0.01029 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.03451 | -0.0448 | 5
WERE | 'COLBY 115KV' | 6.3605 | -0.01029 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.03481 | -0.0451 | 5
WERE | 'GETTY 69KV' | 35 | -0.00763 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.03451 | -0.04214 | 5
WERE | 'GETTY 69KV' | 35 | -0.00763 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.03481 | -0.04244 | 5
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.0043 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.04787 | 5
WERE | 'KNOLL 3 115 115KV' | 75 | -0.00767 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.03451 | -0.04218 | 5
WERE | 'KNOLL 3 115 115KV' | 75 | -0.00767 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.03481 | -0.04248 | 5
WERE | 'PAWNEE 115KV' | 999 | -0.00053 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.0441 | 5
WERE | 'RICE 115KV' | 999 | -0.00053 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.0441 | 5
WERE | 'ST JOHN 115KV' | 7.5 | -0.00053 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.0441 | 5
WERE | 'ATWOOD 115KV' | 4 | -0.01002 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.0283 | -0.03832 | 6
WERE | 'ATWOOD 115KV' | 4 | -0.01002 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 225.5185 | 0.02863 | -0.03865 | 6
WERE | 'CHANUTE 69KV' | 52.456 | 0.00472 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.03885 | 6
WERE | 'CITY OF AUGUSTA 69KV' | 10.088 | -0.00279 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.03451 | -0.0373 | 6
WERE | 'CITY OF AUGUSTA 69KV' | 10.088 | -0.00279 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.03481 | -0.0376 | 6
WERE | 'CITY OF BURLINGTON 69KV' | 7.7 | 0.00844 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.03513 | 6
WERE | 'CITY OF ERIE 69KV' | 24.532 | 0.00472 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.03885 | 6
WERE | 'CITY OF FREDONIA 69KV' | 8.996 | 0.00377 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.0398 | 6
WERE | 'CITY OF GIRARD 69KV' | 9.207 | 0.00585 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.03772 | 6
WERE | 'CITY OF IOLA 69KV' | 23.65 | 0.00547 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.0381 | 6
WERE | 'CITY OF MULVANE 69KV' | 12.096 | 0.00398 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.03959 | 6
WERE | 'CITY OF NEODESHA 69KV' | 4.5 | 0.00402 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.03955 | 6
WERE | 'CITY OF WELLINGTON 69KV' | 19.5 | 0.00392 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.03965 | 6
WERE | 'COLBY 115KV' | 6.3605 | -0.01029 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.0283 | -0.03859 | 6
WERE | 'COLBY 115KV' | 6.3605 | -0.01029 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 225.5185 | 0.02863 | -0.03892 | 6
WERE | 'EVANS ENERGY CENTER 138KV' | 674.304 | 0.00599 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.04357 | -0.03758 | 6
WERE | 'GETTY 69KV' | 35 | -0.00763 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.0283 | -0.03593 | 6
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | Evans - Grant - Chisolm Rebuild and Conversion Project
Limiting Facility: | CHISHOLM (CHISLM1X) 138/69/13.2KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | EVANS ENERGY CENTER NORTH - SEDGWICK COUNTY NO. 12 COLWICH 138KV CKT 1
Flowgate: | CHIISLM1X1421570405706512208SP
Date Redispatch Needed: | Starting 2008 6/1 - 10/1 Until EOC
Season Flowgate Identified: | 2008 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1086655 | 2.1802 | 2.1802
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'GILL ENERGY CENTER 69KV' | 73 | -0.05046 | WERE | 'CITY OF ERIE 69KV' | 23.374 | 0.00084 | -0.0513 | 42
WERE | 'GILL ENERGY CENTER 69KV' | 73 | -0.05046 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.98 | 0.00167 | -0.05213 | 42
WERE | 'GILL ENERGY CENTER 69KV' | 73 | -0.05046 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 6e-05 | -0.05052 | 43
WERE | 'GILL ENERGY CENTER 69KV' | 73 | -0.05046 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 6e-05 | -0.05052 | 43
WERE | 'GILL ENERGY CENTER 69KV' | 73 | -0.05046 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | 0.00031 | -0.05077 | 43
WERE | 'GILL ENERGY CENTER 69KV' | 73 | -0.05046 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 229.0237 | 0.0003 | -0.05076 | 43
WERE | 'GILL ENERGY CENTER 69KV' | 73 | -0.05046 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 128 | 0.00035 | -0.05081 | 43
WERE | 'GILL ENERGY CENTER 69KV' | 73 | -0.05046 | WERE | 'BPU - CITY OF MCPHERSON 115KV' | 135 | -0.00136 | -0.0491 | 44
WERE | 'GILL ENERGY CENTER 69KV' | 73 | -0.05046 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 120 | -0.00183 | -0.04863 | 45
WERE | 'GILL ENERGY CENTER 69KV' | 73 | -0.05046 | WERE | 'KNOLL 3 115 115KV' | 75 | -0.00192 | -0.04854 | 45
WERE | 'GILL ENERGY CENTER 69KV' | 73 | -0.05046 | WERE | 'EVANS ENERGY CENTER 138KV' | 431.0884 | -0.00301 | -0.04745 | 46
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | GILL ENERGY CENTER EAST - GILLJCT269.0 69KV CKT 1
Limiting Facility: | GILL ENERGY CENTER EAST - GILLJCT269.0 69KV CKT 1
Direction: | From->To
Line Outage: | GILL ENERGY CENTER EAST - MACARTHUR 69KV CKT 1
Flowgate: | 57795577981577955781311107SP
Date Redispatch Needed: | 6/1/07 - 10/1/07
Season Flowgate Identified: | 2007 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1090817 | 2.3453 | 6.5667
1090964 | 3.2833 | 6.5667
1090965 | 0.9381 | 6.5667
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'CITY OF MULVANE 69KV' | 7.502 | -0.08073 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.23279 | -0.31352 | 21
WERE | 'CITY OF IOLA 69KV' | 13.361 | -0.00105 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.23279 | -0.23384 | 28
WERE | 'CLAY CENTER JUNCTION 115KV' | 15.161 | 0.00069 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.23279 | -0.2321 | 28
WERE | 'GETTY 69KV' | 35 | -0.00422 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.23279 | -0.23701 | 28
WERE | 'HOLTON 115KV' | 19.8 | -0.00022 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.23279 | -0.23301 | 28
WERE | 'JEFFREY ENERGY CENTER 230KV' | 24 | -7e-05 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.23279 | -0.23286 | 28
WERE | 'JEFFREY ENERGY CENTER 345KV' | 42 | -7e-05 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.23279 | -0.23286 | 28
WERE | 'LATHAM1234.0 345KV' | 150 | -0.00298 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.23279 | -0.23577 | 28
WERE | 'LYONS 115KV' | 999 | -0.00036 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.23279 | -0.23315 | 28
WERE | 'NEOSHO ENERGY CENTER 138KV' | 47 | -0.00104 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.23279 | -0.23383 | 28
WERE | 'SMOKYHIL 230 230KV' | 72 | 0.00205 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.23279 | -0.23074 | 28
WERE | 'SOUTH SENECA 115KV' | 16.7 | 0 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.23279 | -0.23279 | 28
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 21.1367 | 0.00286 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.23279 | -0.22993 | 29
WERE | 'GREAT BEND PLANT 69KV' | 10 | 0.00699 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.23279 | -0.2258 | 29
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 133 | 0.00389 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.23279 | -0.2289 | 29
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 12 | 0.0039 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.23279 | -0.22889 | 29
WERE | 'KNOLL 3 115 115KV' | 75 | 0.00351 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.23279 | -0.22928 | 29
WERE | 'PAWNEE 115KV' | 999 | 0.01303 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.23279 | -0.21976 | 30
WERE | 'RICE 115KV' | 999 | 0.01303 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.23279 | -0.21976 | 30
WERE | 'CITY OF WINFIELD 69KV' | 40 | 0.02493 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.23279 | -0.20786 | 32
WERE | 'GETTY 69KV' | 35 | -0.00422 | WERE | 'GILL ENERGY CENTER 138KV' | 171 | 0.07582 | -0.08004 | 82
WERE | 'LATHAM1234.0 345KV' | 150 | -0.00298 | WERE | 'GILL ENERGY CENTER 138KV' | 171 | 0.07582 | -0.0788 | 83
WERE | 'NEOSHO ENERGY CENTER 138KV' | 47 | -0.00104 | WERE | 'GILL ENERGY CENTER 138KV' | 171 | 0.07582 | -0.07686 | 85
WERE | 'LYONS 115KV' | 999 | -0.00036 | WERE | 'GILL ENERGY CENTER 138KV' | 171 | 0.07582 | -0.07618 | 86
WERE | 'JEFFREY ENERGY CENTER 345KV' | 42 | -7e-05 | WERE | 'GILL ENERGY CENTER 138KV' | 171 | 0.07582 | -0.07589 | 87
WERE | 'SMOKYHIL 230 230KV' | 72 | 0.00205 | WERE | 'GILL ENERGY CENTER 138KV' | 171 | 0.07582 | -0.07377 | 89
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 133 | 0.00389 | WERE | 'GILL ENERGY CENTER 138KV' | 171 | 0.07582 | -0.07193 | 91
WERE | 'KNOLL 3 115 115KV' | 75 | 0.00351 | WERE | 'GILL ENERGY CENTER 138KV' | 171 | 0.07582 | -0.07231 | 91
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | GILL ENERGY CENTER EAST - GILLJCT269.0 69KV CKT 1
Limiting Facility: | GILL ENERGY CENTER EAST - GILLJCT269.0 69KV CKT 1
Direction: | From->To
Line Outage: | HOOVER NORTH (HOOVER1X) 138/69/13.2KV TRANSFORMER CKT 1
Flowgate: | 57795577981HOOVOVER1X4211107SP
Date Redispatch Needed: | 6/1/07 - 10/1/07
Season Flowgate Identified: | 2007 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1090817 | 1.612 | 4.5136
1090964 | 2.2568 | 4.5136
1090965 | 0.6448 | 4.5136
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'CITY OF MULVANE 69KV' | 7.502 | -0.0605 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.15879 | -0.21929 | 21
WERE | 'CITY OF IOLA 69KV' | 13.361 | -0.00102 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.15879 | -0.15981 | 28
WERE | 'GETTY 69KV' | 35 | -0.00446 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.15879 | -0.16325 | 28
WERE | 'HOLTON 115KV' | 19.8 | -3e-05 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.15879 | -0.15882 | 28
WERE | 'JEFFREY ENERGY CENTER 230KV' | 24 | 0.00018 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.15879 | -0.15861 | 28
WERE | 'JEFFREY ENERGY CENTER 345KV' | 42 | 0.00017 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.15879 | -0.15862 | 28
WERE | 'LATHAM1234.0 345KV' | 150 | -0.00277 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.15879 | -0.16156 | 28
WERE | 'LYONS 115KV' | 999 | -0.00033 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.15879 | -0.15912 | 28
WERE | 'NEOSHO ENERGY CENTER 138KV' | 47 | -0.001 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.15879 | -0.15979 | 28
WERE | 'SOUTH SENECA 115KV' | 16.7 | 0.0001 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.15879 | -0.15869 | 28
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 21.1367 | 0.0024 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.15879 | -0.15639 | 29
WERE | 'CLAY CENTER JUNCTION 115KV' | 15.161 | 0.00077 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.15879 | -0.15802 | 29
WERE | 'GREAT BEND PLANT 69KV' | 10 | 0.00548 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.15879 | -0.15331 | 29
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 133 | 0.00318 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.15879 | -0.15561 | 29
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 12 | 0.00319 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.15879 | -0.1556 | 29
WERE | 'KNOLL 3 115 115KV' | 75 | 0.00286 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.15879 | -0.15593 | 29
WERE | 'SMOKYHIL 230 230KV' | 72 | 0.00179 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.15879 | -0.157 | 29
WERE | 'PAWNEE 115KV' | 999 | 0.01005 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.15879 | -0.14874 | 30
WERE | 'RICE 115KV' | 999 | 0.01005 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.15879 | -0.14874 | 30
WERE | 'CITY OF WINFIELD 69KV' | 40 | 0.01599 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.15879 | -0.1428 | 32
WERE | 'GETTY 69KV' | 35 | -0.00446 | WERE | 'GILL ENERGY CENTER 138KV' | 171 | 0.05754 | -0.062 | 73
WERE | 'LATHAM1234.0 345KV' | 150 | -0.00277 | WERE | 'GILL ENERGY CENTER 138KV' | 171 | 0.05754 | -0.06031 | 75
WERE | 'NEOSHO ENERGY CENTER 138KV' | 47 | -0.001 | WERE | 'GILL ENERGY CENTER 138KV' | 171 | 0.05754 | -0.05854 | 77
WERE | 'LYONS 115KV' | 999 | -0.00033 | WERE | 'GILL ENERGY CENTER 138KV' | 171 | 0.05754 | -0.05787 | 78
WERE | 'JEFFREY ENERGY CENTER 345KV' | 42 | 0.00017 | WERE | 'GILL ENERGY CENTER 138KV' | 171 | 0.05754 | -0.05737 | 79
WERE | 'SMOKYHIL 230 230KV' | 72 | 0.00179 | WERE | 'GILL ENERGY CENTER 138KV' | 171 | 0.05754 | -0.05575 | 81
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 133 | 0.00318 | WERE | 'GILL ENERGY CENTER 138KV' | 171 | 0.05754 | -0.05436 | 83
WERE | 'KNOLL 3 115 115KV' | 75 | 0.00286 | WERE | 'GILL ENERGY CENTER 138KV' | 171 | 0.05754 | -0.05468 | 83
WERE | 'CITY OF WINFIELD 69KV' | 40 | 0.01599 | WERE | 'GILL ENERGY CENTER 138KV' | 171 | 0.05754 | -0.04155 | 109
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | GILL ENERGY CENTER EAST - MACARTHUR 69KV CKT 1
Limiting Facility: | GILL ENERGY CENTER EAST - MACARTHUR 69KV CKT 1
Direction: | From->To
Line Outage: | GILL ENERGY CENTER EAST - GILLJCT269.0 69KV CKT 1
Flowgate: | 57795578131577955779811107SP
Date Redispatch Needed: | 7/1/07 - 10/1/07
Season Flowgate Identified: | 2007 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1090817 | 2.0172 | 5.6483
1090964 | 2.8241 | 5.6483
1090965 | 0.8069 | 5.6483
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'CITY OF MULVANE 69KV' | 7.502 | -0.08353 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.19986 | -0.28339 | 20
WERE | 'CITY OF IOLA 69KV' | 13.361 | -0.00097 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.19986 | -0.20083 | 28
WERE | 'CLAY CENTER JUNCTION 115KV' | 15.161 | 0.00067 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.19986 | -0.19919 | 28
WERE | 'GETTY 69KV' | 35 | -0.004 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.19986 | -0.20386 | 28
WERE | 'HOLTON 115KV' | 19.8 | -0.00015 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.19986 | -0.20001 | 28
WERE | 'JEFFREY ENERGY CENTER 230KV' | 24 | 1e-05 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.19986 | -0.19985 | 28
WERE | 'JEFFREY ENERGY CENTER 345KV' | 42 | 0 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.19986 | -0.19986 | 28
WERE | 'LATHAM1234.0 345KV' | 150 | -0.00271 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.19986 | -0.20257 | 28
WERE | 'LYONS 115KV' | 999 | -0.00033 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.19986 | -0.20019 | 28
WERE | 'NEOSHO ENERGY CENTER 138KV' | 47 | -0.00096 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.19986 | -0.20082 | 28
WERE | 'SOUTH SENECA 115KV' | 16.7 | 3e-05 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.19986 | -0.19983 | 28
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 21.1367 | 0.00255 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.19986 | -0.19731 | 29
WERE | 'GREAT BEND PLANT 69KV' | 10 | 0.00614 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.19986 | -0.19372 | 29
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 133 | 0.00345 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.19986 | -0.19641 | 29
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 12 | 0.00346 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.19986 | -0.1964 | 29
WERE | 'KNOLL 3 115 115KV' | 75 | 0.00311 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.19986 | -0.19675 | 29
WERE | 'SMOKYHIL 230 230KV' | 72 | 0.00185 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.19986 | -0.19801 | 29
WERE | 'PAWNEE 115KV' | 999 | 0.01139 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.19986 | -0.18847 | 30
WERE | 'RICE 115KV' | 999 | 0.01139 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.19986 | -0.18847 | 30
WERE | 'CITY OF WINFIELD 69KV' | 40 | 0.02087 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.19986 | -0.17899 | 32
WERE | 'GETTY 69KV' | 35 | -0.004 | WERE | 'GILL ENERGY CENTER 138KV' | 171 | 0.06603 | -0.07003 | 81
WERE | 'LATHAM1234.0 345KV' | 150 | -0.00271 | WERE | 'GILL ENERGY CENTER 138KV' | 171 | 0.06603 | -0.06874 | 82
WERE | 'NEOSHO ENERGY CENTER 138KV' | 47 | -0.00096 | WERE | 'GILL ENERGY CENTER 138KV' | 171 | 0.06603 | -0.06699 | 84
WERE | 'LYONS 115KV' | 999 | -0.00033 | WERE | 'GILL ENERGY CENTER 138KV' | 171 | 0.06603 | -0.06636 | 85
WERE | 'JEFFREY ENERGY CENTER 345KV' | 42 | 0 | WERE | 'GILL ENERGY CENTER 138KV' | 171 | 0.06603 | -0.06603 | 86
WERE | 'SMOKYHIL 230 230KV' | 72 | 0.00185 | WERE | 'GILL ENERGY CENTER 138KV' | 171 | 0.06603 | -0.06418 | 88
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 133 | 0.00345 | WERE | 'GILL ENERGY CENTER 138KV' | 171 | 0.06603 | -0.06258 | 90
WERE | 'KNOLL 3 115 115KV' | 75 | 0.00311 | WERE | 'GILL ENERGY CENTER 138KV' | 171 | 0.06603 | -0.06292 | 90
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | GILL ENERGY CENTER EAST - MACARTHUR 69KV CKT 1 #1
Limiting Facility: | GILL ENERGY CENTER EAST - MACARTHUR 69KV CKT 1
Direction: | From->To
Line Outage: | GILLJCT269.0 - OATVILLE 69KV CKT 1
Flowgate: | 57795578131577985782511107SP
Date Redispatch Needed: | 7/1/07 - 10/1/07
Season Flowgate Identified: | 2007 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1090817 | 1.567 | 4.3876
1090964 | 2.1938 | 4.3876
1090965 | 0.6268 | 4.3876
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'CITY OF MULVANE 69KV' | 7.502 | -0.09763 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.15442 | -0.25205 | 17
WERE | 'CITY OF IOLA 69KV' | 13.361 | -0.00091 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.15442 | -0.15533 | 28
WERE | 'GETTY 69KV' | 35 | -0.00398 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.15442 | -0.1584 | 28
WERE | 'HOLTON 115KV' | 19.8 | -2e-05 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.15442 | -0.15444 | 28
WERE | 'JEFFREY ENERGY CENTER 230KV' | 24 | 0.00016 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.15442 | -0.15426 | 28
WERE | 'JEFFREY ENERGY CENTER 345KV' | 42 | 0.00015 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.15442 | -0.15427 | 28
WERE | 'LATHAM1234.0 345KV' | 150 | -0.00245 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.15442 | -0.15687 | 28
WERE | 'LYONS 115KV' | 999 | -0.0003 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.15442 | -0.15472 | 28
WERE | 'NEOSHO ENERGY CENTER 138KV' | 47 | -0.00089 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.15442 | -0.15531 | 28
WERE | 'SOUTH SENECA 115KV' | 16.7 | 0.0001 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.15442 | -0.15432 | 28
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 21.1367 | 0.00221 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.15442 | -0.15221 | 29
WERE | 'CLAY CENTER JUNCTION 115KV' | 15.161 | 0.0007 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.15442 | -0.15372 | 29
WERE | 'GREAT BEND PLANT 69KV' | 10 | 0.00505 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.15442 | -0.14937 | 29
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 133 | 0.00293 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.15442 | -0.15149 | 29
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 12 | 0.00293 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.15442 | -0.15149 | 29
WERE | 'KNOLL 3 115 115KV' | 75 | 0.00263 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.15442 | -0.15179 | 29
WERE | 'SMOKYHIL 230 230KV' | 72 | 0.00164 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.15442 | -0.15278 | 29
WERE | 'PAWNEE 115KV' | 999 | 0.00929 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.15442 | -0.14513 | 30
WERE | 'RICE 115KV' | 999 | 0.00929 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.15442 | -0.14513 | 30
WERE | 'CITY OF WINFIELD 69KV' | 40 | 0.01487 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | 0.15442 | -0.13955 | 31
WERE | 'GETTY 69KV' | 35 | -0.00398 | WERE | 'GILL ENERGY CENTER 138KV' | 171 | 0.0532 | -0.05718 | 77
WERE | 'LATHAM1234.0 345KV' | 150 | -0.00245 | WERE | 'GILL ENERGY CENTER 138KV' | 171 | 0.0532 | -0.05565 | 79
WERE | 'NEOSHO ENERGY CENTER 138KV' | 47 | -0.00089 | WERE | 'GILL ENERGY CENTER 138KV' | 171 | 0.0532 | -0.05409 | 81
WERE | 'LYONS 115KV' | 999 | -0.0003 | WERE | 'GILL ENERGY CENTER 138KV' | 171 | 0.0532 | -0.0535 | 82
WERE | 'JEFFREY ENERGY CENTER 345KV' | 42 | 0.00015 | WERE | 'GILL ENERGY CENTER 138KV' | 171 | 0.0532 | -0.05305 | 83
WERE | 'SMOKYHIL 230 230KV' | 72 | 0.00164 | WERE | 'GILL ENERGY CENTER 138KV' | 171 | 0.0532 | -0.05156 | 85
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 133 | 0.00293 | WERE | 'GILL ENERGY CENTER 138KV' | 171 | 0.0532 | -0.05027 | 87
WERE | 'KNOLL 3 115 115KV' | 75 | 0.00263 | WERE | 'GILL ENERGY CENTER 138KV' | 171 | 0.0532 | -0.05057 | 87
WERE | 'CITY OF WINFIELD 69KV' | 40 | 0.01487 | WERE | 'GILL ENERGY CENTER 138KV' | 171 | 0.0532 | -0.03833 | 114
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | HAYS PLANT - SOUTH HAYS 115KV CKT 1
Limiting Facility: | HAYS PLANT - SOUTH HAYS 115KV CKT 1
Direction: | To->From
Line Outage: | KNOLL 230/115KV TRANSFORMER CKT 1
Flowgate: | 56562565531565585656111208SP
Date Redispatch Needed: | Starting 2008 6/1 - 10/1 Until EOC
Season Flowgate Identified: | 2008 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1090817 | 6.2278 | 23.6788
1090829 | 3.75 | 23.6788
1090964 | 8.7188 | 23.6788
1090965 | 2.4911 | 23.6788
1091057 | 2.4911 | 23.6788
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'KNOLL 3 115 115KV' | 75 | -0.64896 | WERE | 'BPU - CITY OF MCPHERSON 115KV' | 135 | 0.03494 | -0.6839 | 34.6232
WERE | 'KNOLL 3 115 115KV' | 75 | -0.64896 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 180 | 0.03708 | -0.68604 | 34.5152
WERE | 'KNOLL 3 115 115KV' | 75 | -0.64896 | WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 40 | 0.03708 | -0.68604 | 34.5152
WERE | 'KNOLL 3 115 115KV' | 75 | -0.64896 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | 0.02013 | -0.66909 | 35.3896
WERE | 'KNOLL 3 115 115KV' | 75 | -0.64896 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.00657 | -0.65553 | 36.1216
WERE | 'KNOLL 3 115 115KV' | 75 | -0.64896 | WERE | 'CITY OF ERIE 69KV' | 23.374 | 0.00208 | -0.65104 | 36.3707
WERE | 'KNOLL 3 115 115KV' | 75 | -0.64896 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.98 | 0.00308 | -0.65204 | 36.315
WERE | 'KNOLL 3 115 115KV' | 75 | -0.64896 | WERE | 'EVANS ENERGY CENTER 138KV' | 510 | 0.00389 | -0.65285 | 36.2699
WERE | 'KNOLL 3 115 115KV' | 75 | -0.64896 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | 0.00438 | -0.65334 | 36.2427
WERE | 'KNOLL 3 115 115KV' | 75 | -0.64896 | WERE | 'GILL ENERGY CENTER 69KV' | 45 | 0.00418 | -0.65314 | 36.2538
WERE | 'KNOLL 3 115 115KV' | 75 | -0.64896 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.00397 | -0.65293 | 36.2654
WERE | 'KNOLL 3 115 115KV' | 75 | -0.64896 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 105 | 0.00392 | -0.65288 | 36.2682
WERE | 'KNOLL 3 115 115KV' | 75 | -0.64896 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 221.8893 | 0.00429 | -0.65325 | 36.2477
WERE | 'KNOLL 3 115 115KV' | 75 | -0.64896 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 145.8125 | 0.00402 | -0.65298 | 36.2627
WERE | 'KNOLL 3 115 115KV' | 75 | -0.64896 | WERE | 'WACO 138KV' | 17.967 | 0.00433 | -0.65329 | 36.2455
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | LINWOOD - MCWILLIE STREET 138KV CKT 1
Limiting Facility: | LINWOOD - MCWILLIE STREET 138KV CKT 1
Direction: | From->To
Line Outage: | HARTS ISLAND - SOUTH SHREVEPORT 138KV CKT 1
Flowgate: | 53422534281534145344612407SP
Date Redispatch Needed: | 6/1/07 - 10/1/07
Season Flowgate Identified: | 2007 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1087745 | 4.7306 | 4.7306
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.36077 | AEPW | 'COGENTRIX 345KV' | 200 | -0.00426 | -0.35651 | 13
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.36077 | AEPW | 'COMANCHE 138KV' | 160 | -0.00567 | -0.3551 | 13
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.36077 | AEPW | 'COMANCHE 69KV' | 63 | -0.00568 | -0.35509 | 13
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.36077 | AEPW | 'FITZHUGH 161KV' | 31 | -0.00243 | -0.35834 | 13
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.36077 | AEPW | 'FLINT CREEK 161KV' | 420 | -0.00354 | -0.35723 | 13
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.36077 | AEPW | 'KNOXLEE 138KV' | 280.2402 | -0.00927 | -0.3515 | 13
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.36077 | AEPW | 'NORTHEASTERN STATION 138KV' | 405 | -0.00394 | -0.35683 | 13
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.36077 | AEPW | 'NORTHEASTERN STATION 138KV' | 95 | -0.00394 | -0.35683 | 13
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.36077 | AEPW | 'NORTHEASTERN STATION 345KV' | 645 | -0.00393 | -0.35684 | 13
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.36077 | AEPW | 'OEC 345KV' | 269 | -0.00413 | -0.35664 | 13
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.36077 | AEPW | 'RIVERSIDE STATION 138KV' | 646 | -0.00427 | -0.3565 | 13
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.36077 | AEPW | 'SOUTHWESTERN STATION 138KV' | 335 | -0.00561 | -0.35516 | 13
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.36077 | AEPW | 'TULSA POWER STATION 138KV' | 112 | -0.00423 | -0.35654 | 13
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.36077 | AEPW | 'TULSA POWER STATION 138KV' | 147 | -0.00423 | -0.35654 | 13
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.36077 | AEPW | 'WELEETKA 138KV' | 70 | -0.00514 | -0.35563 | 13
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.36077 | AEPW | 'EASTMAN 138KV' | 155 | -0.01316 | -0.34761 | 14
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.36077 | AEPW | 'LEBROCK 345KV' | 515 | -0.01836 | -0.34241 | 14
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.36077 | AEPW | 'PIRKEY GENERATION 138KV' | 475 | -0.02464 | -0.33613 | 14
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.36077 | AEPW | 'WELSH 345KV' | 990 | -0.01279 | -0.34798 | 14
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.36077 | AEPW | 'WILKES 138KV' | 346.8935 | -0.0287 | -0.33207 | 14
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.36077 | AEPW | 'WILKES 345KV' | 311 | -0.01662 | -0.34415 | 14
AEPW | 'LIEBERMAN 138KV' | 137 | -0.21196 | AEPW | 'COGENTRIX 345KV' | 200 | -0.00426 | -0.2077 | 23
AEPW | 'LIEBERMAN 138KV' | 137 | -0.21196 | AEPW | 'COMANCHE 138KV' | 160 | -0.00567 | -0.20629 | 23
AEPW | 'LIEBERMAN 138KV' | 137 | -0.21196 | AEPW | 'COMANCHE 69KV' | 63 | -0.00568 | -0.20628 | 23
AEPW | 'LIEBERMAN 138KV' | 137 | -0.21196 | AEPW | 'FITZHUGH 161KV' | 31 | -0.00243 | -0.20953 | 23
AEPW | 'LIEBERMAN 138KV' | 137 | -0.21196 | AEPW | 'FLINT CREEK 161KV' | 420 | -0.00354 | -0.20842 | 23
AEPW | 'LIEBERMAN 138KV' | 137 | -0.21196 | AEPW | 'KNOXLEE 138KV' | 280.2402 | -0.00927 | -0.20269 | 23
AEPW | 'LIEBERMAN 138KV' | 137 | -0.21196 | AEPW | 'NORTHEASTERN STATION 138KV' | 405 | -0.00394 | -0.20802 | 23
AEPW | 'LIEBERMAN 138KV' | 137 | -0.21196 | AEPW | 'NORTHEASTERN STATION 138KV' | 95 | -0.00394 | -0.20802 | 23
AEPW | 'LIEBERMAN 138KV' | 137 | -0.21196 | AEPW | 'NORTHEASTERN STATION 345KV' | 645 | -0.00393 | -0.20803 | 23
AEPW | 'LIEBERMAN 138KV' | 137 | -0.21196 | AEPW | 'OEC 345KV' | 269 | -0.00413 | -0.20783 | 23
AEPW | 'LIEBERMAN 138KV' | 137 | -0.21196 | AEPW | 'RIVERSIDE STATION 138KV' | 646 | -0.00427 | -0.20769 | 23
AEPW | 'LIEBERMAN 138KV' | 137 | -0.21196 | AEPW | 'SOUTHWESTERN STATION 138KV' | 335 | -0.00561 | -0.20635 | 23
AEPW | 'LIEBERMAN 138KV' | 137 | -0.21196 | AEPW | 'TULSA POWER STATION 138KV' | 112 | -0.00423 | -0.20773 | 23
AEPW | 'LIEBERMAN 138KV' | 137 | -0.21196 | AEPW | 'TULSA POWER STATION 138KV' | 147 | -0.00423 | -0.20773 | 23
AEPW | 'LIEBERMAN 138KV' | 137 | -0.21196 | AEPW | 'WELEETKA 138KV' | 70 | -0.00514 | -0.20682 | 23
AEPW | 'LIEBERMAN 138KV' | 137 | -0.21196 | AEPW | 'EASTMAN 138KV' | 155 | -0.01316 | -0.1988 | 24
AEPW | 'LIEBERMAN 138KV' | 137 | -0.21196 | AEPW | 'LEBROCK 345KV' | 515 | -0.01836 | -0.1936 | 24
AEPW | 'LIEBERMAN 138KV' | 137 | -0.21196 | AEPW | 'WELSH 345KV' | 990 | -0.01279 | -0.19917 | 24
AEPW | 'LIEBERMAN 138KV' | 137 | -0.21196 | AEPW | 'WILKES 345KV' | 311 | -0.01662 | -0.19534 | 24
AEPW | 'LIEBERMAN 138KV' | 137 | -0.21196 | AEPW | 'PIRKEY GENERATION 138KV' | 475 | -0.02464 | -0.18732 | 25
AEPW | 'LIEBERMAN 138KV' | 137 | -0.21196 | AEPW | 'WILKES 138KV' | 346.8935 | -0.0287 | -0.18326 | 26
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.36077 | AEPW | 'LIEBERMAN 138KV' | 91 | -0.21196 | -0.14881 | 32
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | MUSTANG STATION 230/115KV TRANSFORMER CKT 1
Limiting Facility: | MUSTANG STATION 230/115KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | YOAKUM COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 1
Flowgate: | 51966519691518915189011107SP
Date Redispatch Needed: | 6/1/07 - 10/1/07
Season Flowgate Identified: | 2007 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1090487 | 42.1845 | 42.1845
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
SPS | 'MADOX 115KV' | 75 | -0.12508 | SPS | 'MUSTG5 118.0 230KV' | 360 | 0.24436 | -0.36944 | 114
SPS | 'CUNNINGHAM 115KV' | 50.0098 | -0.1221 | SPS | 'MUSTG5 118.0 230KV' | 360 | 0.24436 | -0.36646 | 115
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | MUSTANG STATION 230/115KV TRANSFORMER CKT 1
Limiting Facility: | MUSTANG STATION 230/115KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | YOAKUM COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 1
Flowgate: | 51966519691518915189011407AP
Date Redispatch Needed: | Starting 2007 4/1 - 6/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 April Minimum
Reservation | Relief Amount | Aggregate Relief Amount
1090487 | 24.7304 | 24.7304
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
SPS | 'MUSTANG 115KV' | 150 | -0.44259 | SPS | 'MUSTG5 118.0 230KV' | 125 | 0.24436 | -0.68695 | 36
SPS | 'MUSTANG 115KV' | 150 | -0.44259 | SPS | 'TOLK 230KV' | 1014.384 | 0.01795 | -0.46054 | 54
SPS | 'MUSTANG 115KV' | 150 | -0.44259 | SPS | 'BLACKHAWK 115KV' | 220 | 0.00538 | -0.44797 | 55
SPS | 'MUSTANG 115KV' | 150 | -0.44259 | SPS | 'CZ 69KV' | 35 | 0.00489 | -0.44748 | 55
SPS | 'MUSTANG 115KV' | 150 | -0.44259 | SPS | 'HARRINGTON 230KV' | 706 | 0.00545 | -0.44804 | 55
SPS | 'MUSTANG 115KV' | 150 | -0.44259 | SPS | 'SAN JUAN 230KV' | 54 | 0.00307 | -0.44566 | 55
SPS | 'MUSTANG 115KV' | 150 | -0.44259 | SPS | 'STEER WATER 115KV' | 36 | 0.00508 | -0.44767 | 55
SPS | 'MUSTANG 115KV' | 150 | -0.44259 | SPS | 'WILWIND 230KV' | 72 | 0.00748 | -0.45007 | 55
SPS | 'MUSTANG 115KV' | 150 | -0.44259 | SPS | 'JONES 230KV' | 104 | -0.01198 | -0.43061 | 57
SPS | 'MUSTANG 115KV' | 150 | -0.44259 | SPS | 'LP-BRND2 69KV' | 49.5386 | -0.01318 | -0.42941 | 58
SPS | 'MUSTANG 115KV' | 150 | -0.44259 | SPS | 'CUNNINGHAM 230KV' | 56 | -0.02568 | -0.41691 | 59
SPS | 'CUNNINGHAM 115KV' | 71 | -0.1221 | SPS | 'MUSTG5 118.0 230KV' | 125 | 0.24436 | -0.36646 | 67
SPS | 'CUNNINGHAM 115KV' | 110 | -0.1221 | SPS | 'MUSTG5 118.0 230KV' | 125 | 0.24436 | -0.36646 | 67
SPS | 'MADOX 115KV' | 193 | -0.12508 | SPS | 'MUSTG5 118.0 230KV' | 125 | 0.24436 | -0.36944 | 67
SPS | 'CUNNINGHAM 230KV' | 250 | -0.02568 | SPS | 'MUSTG5 118.0 230KV' | 125 | 0.24436 | -0.27004 | 92
SPS | 'JONES 230KV' | 382 | -0.01198 | SPS | 'MUSTG5 118.0 230KV' | 125 | 0.24436 | -0.25634 | 96
SPS | 'LP-BRND2 69KV' | 182.4614 | -0.01318 | SPS | 'MUSTG5 118.0 230KV' | 125 | 0.24436 | -0.25754 | 96
SPS | 'PLANTX 115KV' | 253 | 0.00765 | SPS | 'MUSTG5 118.0 230KV' | 125 | 0.24436 | -0.23671 | 104
SPS | 'PLANTX 230KV' | 189 | 0.01616 | SPS | 'MUSTG5 118.0 230KV' | 125 | 0.24436 | -0.2282 | 108
SPS | 'TOLK 230KV' | 65.6158 | 0.01795 | SPS | 'MUSTG5 118.0 230KV' | 125 | 0.24436 | -0.22641 | 109
SPS | 'MADOX 115KV' | 193 | -0.12508 | SPS | 'TOLK 230KV' | 1014.384 | 0.01795 | -0.14303 | 173
SPS | 'CUNNINGHAM 115KV' | 71 | -0.1221 | SPS | 'TOLK 230KV' | 1014.384 | 0.01795 | -0.14005 | 177
SPS | 'CUNNINGHAM 115KV' | 110 | -0.1221 | SPS | 'TOLK 230KV' | 1014.384 | 0.01795 | -0.14005 | 177
SPS | 'MADOX 115KV' | 193 | -0.12508 | SPS | 'WILWIND 230KV' | 72 | 0.00748 | -0.13256 | 187
SPS | 'MADOX 115KV' | 193 | -0.12508 | SPS | 'HARRINGTON 230KV' | 706 | 0.00545 | -0.13053 | 189
SPS | 'MADOX 115KV' | 193 | -0.12508 | SPS | 'BLACKHAWK 115KV' | 220 | 0.00538 | -0.13046 | 190
SPS | 'CUNNINGHAM 115KV' | 71 | -0.1221 | SPS | 'WILWIND 230KV' | 72 | 0.00748 | -0.12958 | 191
SPS | 'CUNNINGHAM 115KV' | 110 | -0.1221 | SPS | 'WILWIND 230KV' | 72 | 0.00748 | -0.12958 | 191
SPS | 'CUNNINGHAM 115KV' | 71 | -0.1221 | SPS | 'BLACKHAWK 115KV' | 220 | 0.00538 | -0.12748 | 194
SPS | 'CUNNINGHAM 115KV' | 110 | -0.1221 | SPS | 'BLACKHAWK 115KV' | 220 | 0.00538 | -0.12748 | 194
SPS | 'CUNNINGHAM 115KV' | 71 | -0.1221 | SPS | 'HARRINGTON 230KV' | 706 | 0.00545 | -0.12755 | 194
SPS | 'CUNNINGHAM 115KV' | 110 | -0.1221 | SPS | 'HARRINGTON 230KV' | 706 | 0.00545 | -0.12755 | 194
SPS | 'MADOX 115KV' | 193 | -0.12508 | SPS | 'JONES 230KV' | 104 | -0.01198 | -0.1131 | 219
SPS | 'CUNNINGHAM 115KV' | 110 | -0.1221 | SPS | 'JONES 230KV' | 104 | -0.01198 | -0.11012 | 225
SPS | 'CUNNINGHAM 230KV' | 250 | -0.02568 | SPS | 'TOLK 230KV' | 1014.384 | 0.01795 | -0.04363 | 567
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | MUSTANG STATION 230/115KV TRANSFORMER CKT 1
Limiting Facility: | MUSTANG STATION 230/115KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | YOAKUM COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 1
Flowgate: | 51966519691518915189014107G
Date Redispatch Needed: | Starting 2007 4/1 - 6/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 Spring Peak
Reservation | Relief Amount | Aggregate Relief Amount
1090487 | 2.2108 | 2.2108
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
SPS | 'CUNNINGHAM 115KV' | 71 | -0.1221 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.24436 | -0.36646 | 6
SPS | 'MADOX 115KV' | 75 | -0.12508 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.24436 | -0.36944 | 6
SPS | 'CARLSBAD 69KV' | 18 | -0.03923 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.24436 | -0.28359 | 8
SPS | 'CZ 69KV' | 4 | 0.00489 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.24436 | -0.23947 | 9
SPS | 'HARRINGTON 230KV' | 360 | 0.00544 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.24436 | -0.23892 | 9
SPS | 'HUBRCO2 69KV' | 6 | 0.00538 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.24436 | -0.23898 | 9
SPS | 'LP-BRND2 69KV' | 152 | -0.01318 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.24436 | -0.25754 | 9
SPS | 'MOORE COUNTY 115KV' | 48 | 0.00567 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.24436 | -0.23869 | 9
SPS | 'NICHOLS 115KV' | 107 | 0.00525 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.24436 | -0.23911 | 9
SPS | 'NICHOLS 230KV' | 113.3726 | 0.00538 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.24436 | -0.23898 | 9
SPS | 'PLANTX 115KV' | 48 | 0.00765 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.24436 | -0.23671 | 9
SPS | 'RIVERVIEW 69KV' | 23 | 0.00538 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.24436 | -0.23898 | 9
SPS | 'SIDRCH 69KV' | 6 | 0.00538 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.24436 | -0.23898 | 9
SPS | 'TOLK 230KV' | 65.2912 | 0.01795 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.24436 | -0.22641 | 10
SPS | 'TUCUMCARI 115KV' | 15 | 0.0126 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.24436 | -0.23176 | 10
SPS | 'MADOX 115KV' | 75 | -0.12508 | SPS | 'TOLK 230KV' | 1014.709 | 0.01795 | -0.14303 | 15
SPS | 'CUNNINGHAM 115KV' | 71 | -0.1221 | SPS | 'CAPROCK 115KV' | 80 | 0.0126 | -0.1347 | 16
SPS | 'CUNNINGHAM 115KV' | 71 | -0.1221 | SPS | 'PLANTX 230KV' | 189 | 0.01615 | -0.13825 | 16
SPS | 'CUNNINGHAM 115KV' | 71 | -0.1221 | SPS | 'TOLK 230KV' | 1014.709 | 0.01795 | -0.14005 | 16
SPS | 'MADOX 115KV' | 75 | -0.12508 | SPS | 'CAPROCK 115KV' | 80 | 0.0126 | -0.13768 | 16
SPS | 'MADOX 115KV' | 75 | -0.12508 | SPS | 'PLANTX 230KV' | 189 | 0.01615 | -0.14123 | 16
SPS | 'CUNNINGHAM 115KV' | 71 | -0.1221 | SPS | 'HARRINGTON 230KV' | 706 | 0.00544 | -0.12754 | 17
SPS | 'CUNNINGHAM 115KV' | 71 | -0.1221 | SPS | 'NICHOLS 230KV' | 130.6274 | 0.00538 | -0.12748 | 17
SPS | 'CUNNINGHAM 115KV' | 71 | -0.1221 | SPS | 'PLANTX 115KV' | 205 | 0.00765 | -0.12975 | 17
SPS | 'CUNNINGHAM 115KV' | 71 | -0.1221 | SPS | 'WILWIND 230KV' | 159.9999 | 0.00748 | -0.12958 | 17
SPS | 'MADOX 115KV' | 75 | -0.12508 | SPS | 'HARRINGTON 230KV' | 706 | 0.00544 | -0.13052 | 17
SPS | 'MADOX 115KV' | 75 | -0.12508 | SPS | 'NICHOLS 230KV' | 130.6274 | 0.00538 | -0.13046 | 17
SPS | 'MADOX 115KV' | 75 | -0.12508 | SPS | 'PLANTX 115KV' | 205 | 0.00765 | -0.13273 | 17
SPS | 'MADOX 115KV' | 75 | -0.12508 | SPS | 'SAN JUAN 230KV' | 119.9999 | 0.00307 | -0.12815 | 17
SPS | 'MADOX 115KV' | 75 | -0.12508 | SPS | 'WILWIND 230KV' | 159.9999 | 0.00748 | -0.13256 | 17
SPS | 'CUNNINGHAM 115KV' | 71 | -0.1221 | SPS | 'SAN JUAN 230KV' | 119.9999 | 0.00307 | -0.12517 | 18
SPS | 'CUNNINGHAM 115KV' | 71 | -0.1221 | SPS | 'JONES 230KV' | 486 | -0.01198 | -0.11012 | 20
SPS | 'CUNNINGHAM 115KV' | 71 | -0.1221 | SPS | 'LP-BRND2 69KV' | 80 | -0.01318 | -0.10892 | 20
SPS | 'MADOX 115KV' | 75 | -0.12508 | SPS | 'JONES 230KV' | 486 | -0.01198 | -0.1131 | 20
SPS | 'MADOX 115KV' | 75 | -0.12508 | SPS | 'LP-BRND2 69KV' | 80 | -0.01318 | -0.1119 | 20
SPS | 'MADOX 115KV' | 75 | -0.12508 | SPS | 'CUNNINGHAM 230KV' | 306 | -0.02568 | -0.0994 | 22
SPS | 'CUNNINGHAM 115KV' | 71 | -0.1221 | SPS | 'CUNNINGHAM 230KV' | 306 | -0.02568 | -0.09642 | 23
SPS | 'CARLSBAD 69KV' | 18 | -0.03923 | SPS | 'TOLK 230KV' | 1014.709 | 0.01795 | -0.05718 | 39
SPS | 'CARLSBAD 69KV' | 18 | -0.03923 | SPS | 'PLANTX 230KV' | 189 | 0.01615 | -0.05538 | 40
SPS | 'CARLSBAD 69KV' | 18 | -0.03923 | SPS | 'CAPROCK 115KV' | 80 | 0.0126 | -0.05183 | 43
SPS | 'CARLSBAD 69KV' | 18 | -0.03923 | SPS | 'PLANTX 115KV' | 205 | 0.00765 | -0.04688 | 47
SPS | 'CARLSBAD 69KV' | 18 | -0.03923 | SPS | 'WILWIND 230KV' | 159.9999 | 0.00748 | -0.04671 | 47
SPS | 'CARLSBAD 69KV' | 18 | -0.03923 | SPS | 'HARRINGTON 230KV' | 706 | 0.00544 | -0.04467 | 49
SPS | 'CARLSBAD 69KV' | 18 | -0.03923 | SPS | 'NICHOLS 230KV' | 130.6274 | 0.00538 | -0.04461 | 50
SPS | 'CARLSBAD 69KV' | 18 | -0.03923 | SPS | 'SAN JUAN 230KV' | 119.9999 | 0.00307 | -0.0423 | 52
SPS | 'LP-BRND2 69KV' | 152 | -0.01318 | SPS | 'TOLK 230KV' | 1014.709 | 0.01795 | -0.03113 | 71
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | MUSTANG STATION 230/115KV TRANSFORMER CKT 1
Limiting Facility: | MUSTANG STATION 230/115KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | LEA COUNTY INTERCHANGE - YOAKUM COUNTY INTERCHANGE 230KV CKT 1
Flowgate: | 51966519691522055189111107FA
Date Redispatch Needed: | Starting 2007 10/1 - 12/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 Fall Peak
Reservation | Relief Amount | Aggregate Relief Amount
1090487 | 42.171 | 42.171
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
SPS | 'CUNNINGHAM 115KV' | 71 | -0.21032 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.25702 | -0.46734 | 90
SPS | 'CUNNINGHAM 115KV' | 110 | -0.21032 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.25702 | -0.46734 | 90
SPS | 'MADOX 115KV' | 102.3579 | -0.21294 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.25702 | -0.46996 | 90
SPS | 'CUNNINGHAM 230KV' | 306 | -0.16698 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.25702 | -0.424 | 99
SPS | 'NICHOLS 115KV' | 213 | 0.00271 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.25702 | -0.25431 | 166
SPS | 'NICHOLS 230KV' | 244 | 0.0028 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.25702 | -0.25422 | 166
SPS | 'PLANTX 115KV' | 253 | 0.0048 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.25702 | -0.25222 | 167
SPS | 'TOLK 230KV' | 60.2673 | 0.00822 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.25702 | -0.2488 | 169
SPS | 'PLANTX 230KV' | 189 | 0.0095 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.25702 | -0.24752 | 170
SPS | 'MADOX 115KV' | 102.3579 | -0.21294 | SPS | 'TOLK 230KV' | 1019.733 | 0.00822 | -0.22116 | 191
SPS | 'CUNNINGHAM 115KV' | 71 | -0.21032 | SPS | 'TOLK 230KV' | 1019.733 | 0.00822 | -0.21854 | 193
SPS | 'CUNNINGHAM 115KV' | 110 | -0.21032 | SPS | 'TOLK 230KV' | 1019.733 | 0.00822 | -0.21854 | 193
SPS | 'MADOX 115KV' | 102.3579 | -0.21294 | SPS | 'BLACKHAWK 115KV' | 220 | 0.0028 | -0.21574 | 195
SPS | 'MADOX 115KV' | 102.3579 | -0.21294 | SPS | 'HARRINGTON 230KV' | 1066 | 0.00284 | -0.21578 | 195
SPS | 'MADOX 115KV' | 102.3579 | -0.21294 | SPS | 'WILWIND 230KV' | 160 | 0.00387 | -0.21681 | 195
SPS | 'MADOX 115KV' | 102.3579 | -0.21294 | SPS | 'STEER WATER 115KV' | 79.95 | 0.00262 | -0.21556 | 196
SPS | 'CUNNINGHAM 115KV' | 71 | -0.21032 | SPS | 'WILWIND 230KV' | 160 | 0.00387 | -0.21419 | 197
SPS | 'CUNNINGHAM 115KV' | 110 | -0.21032 | SPS | 'WILWIND 230KV' | 160 | 0.00387 | -0.21419 | 197
SPS | 'CUNNINGHAM 115KV' | 71 | -0.21032 | SPS | 'BLACKHAWK 115KV' | 220 | 0.0028 | -0.21312 | 198
SPS | 'CUNNINGHAM 115KV' | 110 | -0.21032 | SPS | 'BLACKHAWK 115KV' | 220 | 0.0028 | -0.21312 | 198
SPS | 'CUNNINGHAM 115KV' | 71 | -0.21032 | SPS | 'HARRINGTON 230KV' | 1066 | 0.00284 | -0.21316 | 198
SPS | 'CUNNINGHAM 115KV' | 110 | -0.21032 | SPS | 'HARRINGTON 230KV' | 1066 | 0.00284 | -0.21316 | 198
SPS | 'CUNNINGHAM 115KV' | 71 | -0.21032 | SPS | 'STEER WATER 115KV' | 79.95 | 0.00262 | -0.21294 | 198
SPS | 'CUNNINGHAM 115KV' | 110 | -0.21032 | SPS | 'STEER WATER 115KV' | 79.95 | 0.00262 | -0.21294 | 198
SPS | 'MADOX 115KV' | 102.3579 | -0.21294 | SPS | 'CAPROCK 115KV' | 79.95 | -0.00487 | -0.20807 | 203
SPS | 'MADOX 115KV' | 102.3579 | -0.21294 | SPS | 'JONES 230KV' | 486 | -0.00528 | -0.20766 | 203
SPS | 'CUNNINGHAM 115KV' | 71 | -0.21032 | SPS | 'CAPROCK 115KV' | 79.95 | -0.00487 | -0.20545 | 205
SPS | 'CUNNINGHAM 115KV' | 110 | -0.21032 | SPS | 'CAPROCK 115KV' | 79.95 | -0.00487 | -0.20545 | 205
SPS | 'CUNNINGHAM 115KV' | 71 | -0.21032 | SPS | 'JONES 230KV' | 486 | -0.00528 | -0.20504 | 206
SPS | 'CUNNINGHAM 115KV' | 110 | -0.21032 | SPS | 'JONES 230KV' | 486 | -0.00528 | -0.20504 | 206
SPS | 'CUNNINGHAM 230KV' | 306 | -0.16698 | SPS | 'TOLK 230KV' | 1019.733 | 0.00822 | -0.1752 | 241
SPS | 'MADOX 115KV' | 102.3579 | -0.21294 | SPS | 'SAN JUAN 230KV' | 120 | -0.03776 | -0.17518 | 241
SPS | 'CUNNINGHAM 115KV' | 110 | -0.21032 | SPS | 'SAN JUAN 230KV' | 120 | -0.03776 | -0.17256 | 244
SPS | 'CUNNINGHAM 230KV' | 306 | -0.16698 | SPS | 'WILWIND 230KV' | 160 | 0.00387 | -0.17085 | 247
SPS | 'CUNNINGHAM 230KV' | 306 | -0.16698 | SPS | 'HARRINGTON 230KV' | 1066 | 0.00284 | -0.16982 | 248
SPS | 'CUNNINGHAM 230KV' | 306 | -0.16698 | SPS | 'JONES 230KV' | 486 | -0.00528 | -0.1617 | 261
SPS | 'CUNNINGHAM 230KV' | 306 | -0.16698 | SPS | 'SAN JUAN 230KV' | 120 | -0.03776 | -0.12922 | 326
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | MUSTANG STATION 230/115KV TRANSFORMER CKT 1
Limiting Facility: | MUSTANG STATION 230/115KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | LEA COUNTY INTERCHANGE - YOAKUM COUNTY INTERCHANGE 230KV CKT 1
Flowgate: | 51966519691522055189111107SH
Date Redispatch Needed: | 6/1 - 10/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 Summer Shoulder
Reservation | Relief Amount | Aggregate Relief Amount
1090487 | 25.3143 | 25.3143
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
SPS | 'CUNNINGHAM 115KV' | 71 | -0.21033 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.257 | -0.46733 | 54
SPS | 'CUNNINGHAM 115KV' | 110 | -0.21033 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.257 | -0.46733 | 54
SPS | 'MADOX 115KV' | 75 | -0.21295 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.257 | -0.46995 | 54
SPS | 'CUNNINGHAM 230KV' | 110 | -0.16699 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.257 | -0.42399 | 60
SPS | 'LP-BRND2 69KV' | 152 | -0.00604 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.257 | -0.26304 | 96
SPS | 'MOORE COUNTY 115KV' | 48 | 0.00305 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.257 | -0.25395 | 100
SPS | 'NICHOLS 115KV' | 131 | 0.0028 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.257 | -0.2542 | 100
SPS | 'NICHOLS 230KV' | 244 | 0.00289 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.257 | -0.25411 | 100
SPS | 'PLANTX 115KV' | 89.4741 | 0.00502 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.257 | -0.25198 | 100
SPS | 'TOLK 230KV' | 52.0113 | 0.00826 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.257 | -0.24874 | 102
SPS | 'MADOX 115KV' | 75 | -0.21295 | SPS | 'PLANTX 230KV' | 189 | 0.00956 | -0.22251 | 114
SPS | 'MADOX 115KV' | 75 | -0.21295 | SPS | 'TOLK 230KV' | 1027.989 | 0.00826 | -0.22121 | 114
SPS | 'CUNNINGHAM 115KV' | 71 | -0.21033 | SPS | 'PLANTX 230KV' | 189 | 0.00956 | -0.21989 | 115
SPS | 'CUNNINGHAM 115KV' | 110 | -0.21033 | SPS | 'PLANTX 230KV' | 189 | 0.00956 | -0.21989 | 115
SPS | 'CUNNINGHAM 115KV' | 71 | -0.21033 | SPS | 'TOLK 230KV' | 1027.989 | 0.00826 | -0.21859 | 116
SPS | 'CUNNINGHAM 115KV' | 110 | -0.21033 | SPS | 'TOLK 230KV' | 1027.989 | 0.00826 | -0.21859 | 116
SPS | 'MADOX 115KV' | 75 | -0.21295 | SPS | 'PLANTX 115KV' | 163.5259 | 0.00502 | -0.21797 | 116
SPS | 'MADOX 115KV' | 75 | -0.21295 | SPS | 'BLACKHAWK 115KV' | 220 | 0.00288 | -0.21583 | 117
SPS | 'MADOX 115KV' | 75 | -0.21295 | SPS | 'HARRINGTON 230KV' | 1066 | 0.00292 | -0.21587 | 117
SPS | 'MADOX 115KV' | 75 | -0.21295 | SPS | 'NICHOLS 115KV' | 82 | 0.0028 | -0.21575 | 117
SPS | 'MADOX 115KV' | 75 | -0.21295 | SPS | 'STEER WATER 115KV' | 79.9818 | 0.00271 | -0.21566 | 117
SPS | 'MADOX 115KV' | 75 | -0.21295 | SPS | 'WILWIND 230KV' | 159.9636 | 0.00395 | -0.2169 | 117
SPS | 'CUNNINGHAM 115KV' | 71 | -0.21033 | SPS | 'PLANTX 115KV' | 163.5259 | 0.00502 | -0.21535 | 118
SPS | 'CUNNINGHAM 115KV' | 110 | -0.21033 | SPS | 'PLANTX 115KV' | 163.5259 | 0.00502 | -0.21535 | 118
SPS | 'CUNNINGHAM 115KV' | 71 | -0.21033 | SPS | 'WILWIND 230KV' | 159.9636 | 0.00395 | -0.21428 | 118
SPS | 'CUNNINGHAM 115KV' | 110 | -0.21033 | SPS | 'WILWIND 230KV' | 159.9636 | 0.00395 | -0.21428 | 118
SPS | 'CUNNINGHAM 115KV' | 71 | -0.21033 | SPS | 'BLACKHAWK 115KV' | 220 | 0.00288 | -0.21321 | 119
SPS | 'CUNNINGHAM 115KV' | 110 | -0.21033 | SPS | 'BLACKHAWK 115KV' | 220 | 0.00288 | -0.21321 | 119
SPS | 'CUNNINGHAM 115KV' | 71 | -0.21033 | SPS | 'HARRINGTON 230KV' | 1066 | 0.00292 | -0.21325 | 119
SPS | 'CUNNINGHAM 115KV' | 110 | -0.21033 | SPS | 'HARRINGTON 230KV' | 1066 | 0.00292 | -0.21325 | 119
SPS | 'CUNNINGHAM 115KV' | 71 | -0.21033 | SPS | 'NICHOLS 115KV' | 82 | 0.0028 | -0.21313 | 119
SPS | 'CUNNINGHAM 115KV' | 110 | -0.21033 | SPS | 'NICHOLS 115KV' | 82 | 0.0028 | -0.21313 | 119
SPS | 'CUNNINGHAM 115KV' | 71 | -0.21033 | SPS | 'STEER WATER 115KV' | 79.9818 | 0.00271 | -0.21304 | 119
SPS | 'CUNNINGHAM 115KV' | 110 | -0.21033 | SPS | 'STEER WATER 115KV' | 79.9818 | 0.00271 | -0.21304 | 119
SPS | 'MADOX 115KV' | 75 | -0.21295 | SPS | 'CAPROCK 115KV' | 79.9818 | -0.00481 | -0.20814 | 122
SPS | 'MADOX 115KV' | 75 | -0.21295 | SPS | 'JONES 230KV' | 486 | -0.00544 | -0.20751 | 122
SPS | 'MADOX 115KV' | 75 | -0.21295 | SPS | 'LP-BRND2 69KV' | 80 | -0.00604 | -0.20691 | 122
SPS | 'CUNNINGHAM 115KV' | 71 | -0.21033 | SPS | 'CAPROCK 115KV' | 79.9818 | -0.00481 | -0.20552 | 123
SPS | 'CUNNINGHAM 115KV' | 110 | -0.21033 | SPS | 'CAPROCK 115KV' | 79.9818 | -0.00481 | -0.20552 | 123
SPS | 'CUNNINGHAM 115KV' | 71 | -0.21033 | SPS | 'JONES 230KV' | 486 | -0.00544 | -0.20489 | 124
SPS | 'CUNNINGHAM 115KV' | 110 | -0.21033 | SPS | 'JONES 230KV' | 486 | -0.00544 | -0.20489 | 124
SPS | 'CUNNINGHAM 230KV' | 110 | -0.16699 | SPS | 'PLANTX 230KV' | 189 | 0.00956 | -0.17655 | 143
SPS | 'CUNNINGHAM 230KV' | 110 | -0.16699 | SPS | 'TOLK 230KV' | 1027.989 | 0.00826 | -0.17525 | 144
SPS | 'MADOX 115KV' | 75 | -0.21295 | SPS | 'SAN JUAN 230KV' | 119.9727 | -0.03772 | -0.17523 | 144
SPS | 'CUNNINGHAM 115KV' | 71 | -0.21033 | SPS | 'SAN JUAN 230KV' | 119.9727 | -0.03772 | -0.17261 | 147
SPS | 'CUNNINGHAM 115KV' | 110 | -0.21033 | SPS | 'SAN JUAN 230KV' | 119.9727 | -0.03772 | -0.17261 | 147
SPS | 'CUNNINGHAM 230KV' | 110 | -0.16699 | SPS | 'PLANTX 115KV' | 163.5259 | 0.00502 | -0.17201 | 147
SPS | 'CUNNINGHAM 230KV' | 110 | -0.16699 | SPS | 'WILWIND 230KV' | 159.9636 | 0.00395 | -0.17094 | 148
SPS | 'CUNNINGHAM 230KV' | 110 | -0.16699 | SPS | 'BLACKHAWK 115KV' | 220 | 0.00288 | -0.16987 | 149
SPS | 'CUNNINGHAM 230KV' | 110 | -0.16699 | SPS | 'HARRINGTON 230KV' | 1066 | 0.00292 | -0.16991 | 149
SPS | 'CUNNINGHAM 230KV' | 110 | -0.16699 | SPS | 'NICHOLS 115KV' | 82 | 0.0028 | -0.16979 | 149
SPS | 'CUNNINGHAM 230KV' | 110 | -0.16699 | SPS | 'STEER WATER 115KV' | 79.9818 | 0.00271 | -0.1697 | 149
SPS | 'CUNNINGHAM 230KV' | 110 | -0.16699 | SPS | 'CAPROCK 115KV' | 79.9818 | -0.00481 | -0.16218 | 156
SPS | 'CUNNINGHAM 230KV' | 110 | -0.16699 | SPS | 'JONES 230KV' | 486 | -0.00544 | -0.16155 | 157
SPS | 'CUNNINGHAM 230KV' | 110 | -0.16699 | SPS | 'SAN JUAN 230KV' | 119.9727 | -0.03772 | -0.12927 | 196
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | MUSTANG STATION 230/115KV TRANSFORMER CKT 1
Limiting Facility: | MUSTANG STATION 230/115KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | LEA COUNTY INTERCHANGE - YOAKUM COUNTY INTERCHANGE 230KV CKT 1
Flowgate: | 51966519691522055189111407AP
Date Redispatch Needed: | Starting 2007 4/1 - 6/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 April Minimum
Reservation | Relief Amount | Aggregate Relief Amount
1090487 | 41.781 | 41.781
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
SPS | 'MUSTANG 115KV' | 150 | -0.38901 | SPS | 'MUSTG5 118.0 230KV' | 125 | 0.257 | -0.64601 | 65
SPS | 'CUNNINGHAM 115KV' | 71 | -0.21033 | SPS | 'MUSTG5 118.0 230KV' | 125 | 0.257 | -0.46733 | 89
SPS | 'CUNNINGHAM 115KV' | 110 | -0.21033 | SPS | 'MUSTG5 118.0 230KV' | 125 | 0.257 | -0.46733 | 89
SPS | 'MADOX 115KV' | 193 | -0.21295 | SPS | 'MUSTG5 118.0 230KV' | 125 | 0.257 | -0.46995 | 89
SPS | 'CUNNINGHAM 230KV' | 250 | -0.16699 | SPS | 'MUSTG5 118.0 230KV' | 125 | 0.257 | -0.42399 | 99
SPS | 'MUSTANG 115KV' | 150 | -0.38901 | SPS | 'TOLK 230KV' | 1014.384 | 0.00827 | -0.39728 | 105
SPS | 'MUSTANG 115KV' | 150 | -0.38901 | SPS | 'WILWIND 230KV' | 72 | 0.00396 | -0.39297 | 106
SPS | 'MUSTANG 115KV' | 150 | -0.38901 | SPS | 'BLACKHAWK 115KV' | 220 | 0.00288 | -0.39189 | 107
SPS | 'MUSTANG 115KV' | 150 | -0.38901 | SPS | 'HARRINGTON 230KV' | 706 | 0.00292 | -0.39193 | 107
SPS | 'MUSTANG 115KV' | 150 | -0.38901 | SPS | 'STEER WATER 115KV' | 36 | 0.00271 | -0.39172 | 107
SPS | 'MUSTANG 115KV' | 150 | -0.38901 | SPS | 'JONES 230KV' | 104 | -0.00544 | -0.38357 | 109
SPS | 'MUSTANG 115KV' | 150 | -0.38901 | SPS | 'LP-BRND2 69KV' | 49.5386 | -0.00604 | -0.38297 | 109
SPS | 'MUSTANG 115KV' | 150 | -0.38901 | SPS | 'SAN JUAN 230KV' | 54 | -0.03772 | -0.35129 | 119
SPS | 'JONES 230KV' | 382 | -0.00544 | SPS | 'MUSTG5 118.0 230KV' | 125 | 0.257 | -0.26244 | 159
SPS | 'LP-BRND2 69KV' | 182.4614 | -0.00604 | SPS | 'MUSTG5 118.0 230KV' | 125 | 0.257 | -0.26304 | 159
SPS | 'PLANTX 115KV' | 253 | 0.00502 | SPS | 'MUSTG5 118.0 230KV' | 125 | 0.257 | -0.25198 | 166
SPS | 'TOLK 230KV' | 65.6158 | 0.00827 | SPS | 'MUSTG5 118.0 230KV' | 125 | 0.257 | -0.24873 | 168
SPS | 'PLANTX 230KV' | 189 | 0.00957 | SPS | 'MUSTG5 118.0 230KV' | 125 | 0.257 | -0.24743 | 169
SPS | 'MADOX 115KV' | 193 | -0.21295 | SPS | 'TOLK 230KV' | 1014.384 | 0.00827 | -0.22122 | 189
SPS | 'CUNNINGHAM 115KV' | 71 | -0.21033 | SPS | 'TOLK 230KV' | 1014.384 | 0.00827 | -0.2186 | 191
SPS | 'CUNNINGHAM 115KV' | 110 | -0.21033 | SPS | 'TOLK 230KV' | 1014.384 | 0.00827 | -0.2186 | 191
SPS | 'MADOX 115KV' | 193 | -0.21295 | SPS | 'WILWIND 230KV' | 72 | 0.00396 | -0.21691 | 193
SPS | 'MADOX 115KV' | 193 | -0.21295 | SPS | 'HARRINGTON 230KV' | 706 | 0.00292 | -0.21587 | 194
SPS | 'CUNNINGHAM 115KV' | 71 | -0.21033 | SPS | 'WILWIND 230KV' | 72 | 0.00396 | -0.21429 | 195
SPS | 'CUNNINGHAM 115KV' | 110 | -0.21033 | SPS | 'WILWIND 230KV' | 72 | 0.00396 | -0.21429 | 195
SPS | 'CUNNINGHAM 115KV' | 71 | -0.21033 | SPS | 'BLACKHAWK 115KV' | 220 | 0.00288 | -0.21321 | 196
SPS | 'CUNNINGHAM 115KV' | 110 | -0.21033 | SPS | 'BLACKHAWK 115KV' | 220 | 0.00288 | -0.21321 | 196
SPS | 'CUNNINGHAM 115KV' | 71 | -0.21033 | SPS | 'HARRINGTON 230KV' | 706 | 0.00292 | -0.21325 | 196
SPS | 'CUNNINGHAM 115KV' | 110 | -0.21033 | SPS | 'HARRINGTON 230KV' | 706 | 0.00292 | -0.21325 | 196
SPS | 'MADOX 115KV' | 193 | -0.21295 | SPS | 'JONES 230KV' | 104 | -0.00544 | -0.20751 | 201
SPS | 'CUNNINGHAM 115KV' | 71 | -0.21033 | SPS | 'JONES 230KV' | 104 | -0.00544 | -0.20489 | 204
SPS | 'CUNNINGHAM 115KV' | 110 | -0.21033 | SPS | 'JONES 230KV' | 104 | -0.00544 | -0.20489 | 204
SPS | 'CUNNINGHAM 230KV' | 250 | -0.16699 | SPS | 'TOLK 230KV' | 1014.384 | 0.00827 | -0.17526 | 238
SPS | 'CUNNINGHAM 230KV' | 250 | -0.16699 | SPS | 'HARRINGTON 230KV' | 706 | 0.00292 | -0.16991 | 246
SPS | 'CUNNINGHAM 230KV' | 250 | -0.16699 | SPS | 'JONES 230KV' | 104 | -0.00544 | -0.16155 | 259
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | MUSTANG STATION 230/115KV TRANSFORMER CKT 1
Limiting Facility: | MUSTANG STATION 230/115KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | LEA COUNTY INTERCHANGE - YOAKUM COUNTY INTERCHANGE 230KV CKT 1
Flowgate: | 51966519691522055189111407WP
Date Redispatch Needed: | 12/1/07 - 4/1/08
Season Flowgate Identified: | 2007 Winter Peak
Reservation | Relief Amount | Aggregate Relief Amount
1090487 | 15.208 | 15.208
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
SPS | 'MUSTANG 115KV' | 29 | -0.38898 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.25703 | -0.64601 | 24
SPS | 'MADOX 115KV' | 88.3945 | -0.21294 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.25703 | -0.46997 | 32
SPS | 'CUNNINGHAM 115KV' | 71 | -0.21032 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.25703 | -0.46735 | 33
SPS | 'CUNNINGHAM 115KV' | 110 | -0.21032 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.25703 | -0.46735 | 33
SPS | 'CUNNINGHAM 230KV' | 110 | -0.16698 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.25703 | -0.42401 | 36
SPS | 'MUSTANG 115KV' | 29 | -0.38898 | SPS | 'TOLK 230KV' | 1019.563 | 0.00822 | -0.3972 | 38
SPS | 'CARLSBAD 69KV' | 18 | -0.1354 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.25703 | -0.39243 | 39
SPS | 'MUSTANG 115KV' | 29 | -0.38898 | SPS | 'BLACKHAWK 115KV' | 220 | 0.0028 | -0.39178 | 39
SPS | 'MUSTANG 115KV' | 29 | -0.38898 | SPS | 'CZ 69KV' | 35 | 0.00253 | -0.39151 | 39
SPS | 'MUSTANG 115KV' | 29 | -0.38898 | SPS | 'HARRINGTON 230KV' | 1066 | 0.00284 | -0.39182 | 39
SPS | 'MUSTANG 115KV' | 29 | -0.38898 | SPS | 'SIDRCH 69KV' | 14 | 0.0028 | -0.39178 | 39
SPS | 'MUSTANG 115KV' | 29 | -0.38898 | SPS | 'STEER WATER 115KV' | 24 | 0.00262 | -0.3916 | 39
SPS | 'MUSTANG 115KV' | 29 | -0.38898 | SPS | 'WILWIND 230KV' | 48 | 0.00387 | -0.39285 | 39
SPS | 'MUSTANG 115KV' | 29 | -0.38898 | SPS | 'CAPROCK 115KV' | 24 | -0.00486 | -0.38412 | 40
SPS | 'MUSTANG 115KV' | 29 | -0.38898 | SPS | 'JONES 230KV' | 243 | -0.00528 | -0.3837 | 40
SPS | 'MUSTANG 115KV' | 29 | -0.38898 | SPS | 'LP-BRND2 69KV' | 60 | -0.00588 | -0.3831 | 40
SPS | 'MUSTANG 115KV' | 29 | -0.38898 | SPS | 'SAN JUAN 230KV' | 36 | -0.03776 | -0.35122 | 43
SPS | 'JONES 230KV' | 243 | -0.00528 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.25703 | -0.26231 | 58
SPS | 'LP-BRND2 69KV' | 172 | -0.00588 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.25703 | -0.26291 | 58
SPS | 'MOORE COUNTY 115KV' | 48 | 0.00296 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.25703 | -0.25407 | 60
SPS | 'NICHOLS 115KV' | 213 | 0.00271 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.25703 | -0.25432 | 60
SPS | 'NICHOLS 230KV' | 244 | 0.0028 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.25703 | -0.25423 | 60
SPS | 'PLANTX 115KV' | 253 | 0.0048 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.25703 | -0.25223 | 60
SPS | 'RIVERVIEW 69KV' | 23 | 0.0028 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.25703 | -0.25423 | 60
SPS | 'PLANTX 230KV' | 189 | 0.0095 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.25703 | -0.24753 | 61
SPS | 'TOLK 230KV' | 60.4367 | 0.00822 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.25703 | -0.24881 | 61
SPS | 'MADOX 115KV' | 88.3945 | -0.21294 | SPS | 'TOLK 230KV' | 1019.563 | 0.00822 | -0.22116 | 69
SPS | 'MUSTANG 115KV' | 29 | -0.38898 | SPS | 'CUNNINGHAM 230KV' | 196 | -0.16698 | -0.222 | 69
SPS | 'CUNNINGHAM 115KV' | 71 | -0.21032 | SPS | 'TOLK 230KV' | 1019.563 | 0.00822 | -0.21854 | 70
SPS | 'CUNNINGHAM 115KV' | 110 | -0.21032 | SPS | 'TOLK 230KV' | 1019.563 | 0.00822 | -0.21854 | 70
SPS | 'MADOX 115KV' | 88.3945 | -0.21294 | SPS | 'BLACKHAWK 115KV' | 220 | 0.0028 | -0.21574 | 70
SPS | 'MADOX 115KV' | 88.3945 | -0.21294 | SPS | 'HARRINGTON 230KV' | 1066 | 0.00284 | -0.21578 | 70
SPS | 'MADOX 115KV' | 88.3945 | -0.21294 | SPS | 'WILWIND 230KV' | 48 | 0.00387 | -0.21681 | 70
SPS | 'CUNNINGHAM 115KV' | 71 | -0.21032 | SPS | 'BLACKHAWK 115KV' | 220 | 0.0028 | -0.21312 | 71
SPS | 'CUNNINGHAM 115KV' | 110 | -0.21032 | SPS | 'BLACKHAWK 115KV' | 220 | 0.0028 | -0.21312 | 71
SPS | 'CUNNINGHAM 115KV' | 71 | -0.21032 | SPS | 'CZ 69KV' | 35 | 0.00253 | -0.21285 | 71
SPS | 'CUNNINGHAM 115KV' | 110 | -0.21032 | SPS | 'CZ 69KV' | 35 | 0.00253 | -0.21285 | 71
SPS | 'CUNNINGHAM 115KV' | 71 | -0.21032 | SPS | 'HARRINGTON 230KV' | 1066 | 0.00284 | -0.21316 | 71
SPS | 'CUNNINGHAM 115KV' | 110 | -0.21032 | SPS | 'HARRINGTON 230KV' | 1066 | 0.00284 | -0.21316 | 71
SPS | 'CUNNINGHAM 115KV' | 71 | -0.21032 | SPS | 'STEER WATER 115KV' | 24 | 0.00262 | -0.21294 | 71
SPS | 'CUNNINGHAM 115KV' | 110 | -0.21032 | SPS | 'STEER WATER 115KV' | 24 | 0.00262 | -0.21294 | 71
SPS | 'CUNNINGHAM 115KV' | 71 | -0.21032 | SPS | 'WILWIND 230KV' | 48 | 0.00387 | -0.21419 | 71
SPS | 'CUNNINGHAM 115KV' | 110 | -0.21032 | SPS | 'WILWIND 230KV' | 48 | 0.00387 | -0.21419 | 71
SPS | 'MADOX 115KV' | 88.3945 | -0.21294 | SPS | 'CZ 69KV' | 35 | 0.00253 | -0.21547 | 71
SPS | 'MADOX 115KV' | 88.3945 | -0.21294 | SPS | 'STEER WATER 115KV' | 24 | 0.00262 | -0.21556 | 71
SPS | 'MADOX 115KV' | 88.3945 | -0.21294 | SPS | 'JONES 230KV' | 243 | -0.00528 | -0.20766 | 73
SPS | 'MADOX 115KV' | 88.3945 | -0.21294 | SPS | 'LP-BRND2 69KV' | 60 | -0.00588 | -0.20706 | 73
SPS | 'CUNNINGHAM 115KV' | 71 | -0.21032 | SPS | 'JONES 230KV' | 243 | -0.00528 | -0.20504 | 74
SPS | 'CUNNINGHAM 115KV' | 110 | -0.21032 | SPS | 'JONES 230KV' | 243 | -0.00528 | -0.20504 | 74
SPS | 'CUNNINGHAM 115KV' | 71 | -0.21032 | SPS | 'LP-BRND2 69KV' | 60 | -0.00588 | -0.20444 | 74
SPS | 'CUNNINGHAM 115KV' | 110 | -0.21032 | SPS | 'LP-BRND2 69KV' | 60 | -0.00588 | -0.20444 | 74
SPS | 'MUSTANG 115KV' | 29 | -0.38898 | SPS | 'MADOX 115KV' | 104.6055 | -0.21294 | -0.17604 | 86
SPS | 'CUNNINGHAM 230KV' | 110 | -0.16698 | SPS | 'TOLK 230KV' | 1019.563 | 0.00822 | -0.1752 | 87
SPS | 'MADOX 115KV' | 88.3945 | -0.21294 | SPS | 'SAN JUAN 230KV' | 36 | -0.03776 | -0.17518 | 87
SPS | 'CUNNINGHAM 115KV' | 71 | -0.21032 | SPS | 'SAN JUAN 230KV' | 36 | -0.03776 | -0.17256 | 88
SPS | 'CUNNINGHAM 115KV' | 110 | -0.21032 | SPS | 'SAN JUAN 230KV' | 36 | -0.03776 | -0.17256 | 88
SPS | 'CUNNINGHAM 230KV' | 110 | -0.16698 | SPS | 'WILWIND 230KV' | 48 | 0.00387 | -0.17085 | 89
SPS | 'CUNNINGHAM 230KV' | 110 | -0.16698 | SPS | 'BLACKHAWK 115KV' | 220 | 0.0028 | -0.16978 | 90
SPS | 'CUNNINGHAM 230KV' | 110 | -0.16698 | SPS | 'CZ 69KV' | 35 | 0.00253 | -0.16951 | 90
SPS | 'CUNNINGHAM 230KV' | 110 | -0.16698 | SPS | 'HARRINGTON 230KV' | 1066 | 0.00284 | -0.16982 | 90
SPS | 'CUNNINGHAM 230KV' | 110 | -0.16698 | SPS | 'JONES 230KV' | 243 | -0.00528 | -0.1617 | 94
SPS | 'CUNNINGHAM 230KV' | 110 | -0.16698 | SPS | 'LP-BRND2 69KV' | 60 | -0.00588 | -0.1611 | 94
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | MUSTANG STATION 230/115KV TRANSFORMER CKT 1
Limiting Facility: | MUSTANG STATION 230/115KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | GEN:51971 1
Flowgate: | 51966519691GEN5197111107AP
Date Redispatch Needed: | Starting 2007 4/1 - 6/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 April Minimum
Reservation | Relief Amount | Aggregate Relief Amount
1090487 | 15.2393 | 15.2393
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
SPS | 'MUSTANG 115KV' | 114.3489 | -0.39792 | SPS | 'MUSTG5 118.0 230KV' | 125 | 0.21119 | -0.60911 | 25
SPS | 'MUSTANG 115KV' | 114.3489 | -0.39792 | SPS | 'TOLK 230KV' | 1020.232 | 0.01159 | -0.40951 | 37
SPS | 'MUSTANG 115KV' | 114.3489 | -0.39792 | SPS | 'BLACKHAWK 115KV' | 220 | 0.00359 | -0.40151 | 38
SPS | 'MUSTANG 115KV' | 114.3489 | -0.39792 | SPS | 'CAPROCK 115KV' | 79.9818 | 0.00665 | -0.40457 | 38
SPS | 'MUSTANG 115KV' | 114.3489 | -0.39792 | SPS | 'CZ 69KV' | 35 | 0.00326 | -0.40118 | 38
SPS | 'MUSTANG 115KV' | 114.3489 | -0.39792 | SPS | 'HARRINGTON 230KV' | 706 | 0.00363 | -0.40155 | 38
SPS | 'MUSTANG 115KV' | 114.3489 | -0.39792 | SPS | 'SIDRCH 69KV' | 14 | 0.00358 | -0.4015 | 38
SPS | 'MUSTANG 115KV' | 114.3489 | -0.39792 | SPS | 'STEER WATER 115KV' | 79.9818 | 0.00338 | -0.4013 | 38
SPS | 'MUSTANG 115KV' | 114.3489 | -0.39792 | SPS | 'WILWIND 230KV' | 159.9636 | 0.00497 | -0.40289 | 38
SPS | 'MUSTANG 115KV' | 114.3489 | -0.39792 | SPS | 'JONES 230KV' | 104 | -0.0077 | -0.39022 | 39
SPS | 'MUSTANG 115KV' | 114.3489 | -0.39792 | SPS | 'LP-BRND2 69KV' | 60 | -0.00853 | -0.38939 | 39
SPS | 'MUSTANG 115KV' | 114.3489 | -0.39792 | SPS | 'SAN JUAN 230KV' | 119.9727 | -0.00356 | -0.39436 | 39
SPS | 'MUSTANG 115KV' | 114.3489 | -0.39792 | SPS | 'CUNNINGHAM 230KV' | 56 | -0.03607 | -0.36185 | 42
SPS | 'MADOX 115KV' | 193 | -0.11872 | SPS | 'MUSTG5 118.0 230KV' | 125 | 0.21119 | -0.32991 | 46
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11614 | SPS | 'MUSTG5 118.0 230KV' | 125 | 0.21119 | -0.32733 | 47
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11614 | SPS | 'MUSTG5 118.0 230KV' | 125 | 0.21119 | -0.32733 | 47
SPS | 'CUNNINGHAM 230KV' | 250 | -0.03607 | SPS | 'MUSTG5 118.0 230KV' | 125 | 0.21119 | -0.24726 | 62
SPS | 'LP-BRND2 69KV' | 172 | -0.00853 | SPS | 'MUSTG5 118.0 230KV' | 125 | 0.21119 | -0.21972 | 69
SPS | 'JONES 230KV' | 382 | -0.0077 | SPS | 'MUSTG5 118.0 230KV' | 125 | 0.21119 | -0.21889 | 70
SPS | 'MOORE COUNTY 115KV' | 48 | 0.00378 | SPS | 'MUSTG5 118.0 230KV' | 125 | 0.21119 | -0.20741 | 73
SPS | 'PLANTX 115KV' | 253 | 0.00555 | SPS | 'MUSTG5 118.0 230KV' | 125 | 0.21119 | -0.20564 | 74
SPS | 'PLANTX 230KV' | 189 | 0.01083 | SPS | 'MUSTG5 118.0 230KV' | 125 | 0.21119 | -0.20036 | 76
SPS | 'TOLK 230KV' | 59.7683 | 0.01159 | SPS | 'MUSTG5 118.0 230KV' | 125 | 0.21119 | -0.1996 | 76
SPS | 'MADOX 115KV' | 193 | -0.11872 | SPS | 'TOLK 230KV' | 1020.232 | 0.01159 | -0.13031 | 117
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11614 | SPS | 'TOLK 230KV' | 1020.232 | 0.01159 | -0.12773 | 119
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11614 | SPS | 'TOLK 230KV' | 1020.232 | 0.01159 | -0.12773 | 119
SPS | 'MADOX 115KV' | 193 | -0.11872 | SPS | 'CAPROCK 115KV' | 79.9818 | 0.00665 | -0.12537 | 122
SPS | 'MADOX 115KV' | 193 | -0.11872 | SPS | 'WILWIND 230KV' | 159.9636 | 0.00497 | -0.12369 | 123
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11614 | SPS | 'CAPROCK 115KV' | 79.9818 | 0.00665 | -0.12279 | 124
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11614 | SPS | 'CAPROCK 115KV' | 79.9818 | 0.00665 | -0.12279 | 124
SPS | 'MADOX 115KV' | 193 | -0.11872 | SPS | 'BLACKHAWK 115KV' | 220 | 0.00359 | -0.12231 | 125
SPS | 'MADOX 115KV' | 193 | -0.11872 | SPS | 'HARRINGTON 230KV' | 706 | 0.00363 | -0.12235 | 125
SPS | 'MADOX 115KV' | 193 | -0.11872 | SPS | 'STEER WATER 115KV' | 79.9818 | 0.00338 | -0.1221 | 125
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11614 | SPS | 'WILWIND 230KV' | 159.9636 | 0.00497 | -0.12111 | 126
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11614 | SPS | 'WILWIND 230KV' | 159.9636 | 0.00497 | -0.12111 | 126
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11614 | SPS | 'BLACKHAWK 115KV' | 220 | 0.00359 | -0.11973 | 127
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11614 | SPS | 'BLACKHAWK 115KV' | 220 | 0.00359 | -0.11973 | 127
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11614 | SPS | 'HARRINGTON 230KV' | 706 | 0.00363 | -0.11977 | 127
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11614 | SPS | 'HARRINGTON 230KV' | 706 | 0.00363 | -0.11977 | 127
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11614 | SPS | 'STEER WATER 115KV' | 79.9818 | 0.00338 | -0.11952 | 128
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11614 | SPS | 'STEER WATER 115KV' | 79.9818 | 0.00338 | -0.11952 | 128
SPS | 'MADOX 115KV' | 193 | -0.11872 | SPS | 'SAN JUAN 230KV' | 119.9727 | -0.00356 | -0.11516 | 132
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11614 | SPS | 'SAN JUAN 230KV' | 119.9727 | -0.00356 | -0.11258 | 135
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11614 | SPS | 'SAN JUAN 230KV' | 119.9727 | -0.00356 | -0.11258 | 135
SPS | 'MADOX 115KV' | 193 | -0.11872 | SPS | 'JONES 230KV' | 104 | -0.0077 | -0.11102 | 137
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11614 | SPS | 'JONES 230KV' | 104 | -0.0077 | -0.10844 | 141
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11614 | SPS | 'JONES 230KV' | 104 | -0.0077 | -0.10844 | 141
SPS | 'CUNNINGHAM 230KV' | 250 | -0.03607 | SPS | 'TOLK 230KV' | 1020.232 | 0.01159 | -0.04766 | 320
SPS | 'CUNNINGHAM 230KV' | 250 | -0.03607 | SPS | 'WILWIND 230KV' | 159.9636 | 0.00497 | -0.04104 | 371
SPS | 'CUNNINGHAM 230KV' | 250 | -0.03607 | SPS | 'HARRINGTON 230KV' | 706 | 0.00363 | -0.0397 | 384
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | MUSTANG STATION 230/115KV TRANSFORMER CKT 1
Limiting Facility: | MUSTANG STATION 230/115KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | GEN:51971 1
Flowgate: | 51966519691GEN5197111107FA
Date Redispatch Needed: | Starting 2007 10/1 - 12/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 Fall Peak
Reservation | Relief Amount | Aggregate Relief Amount
1090487 | 32.5005 | 32.5005
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11612 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.32733 | 99
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11612 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.32733 | 99
SPS | 'MADOX 115KV' | 102.3579 | -0.1187 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.32991 | 99
SPS | 'CUNNINGHAM 230KV' | 306 | -0.03606 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.24727 | 131
SPS | 'NICHOLS 115KV' | 213 | 0.00339 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.20782 | 156
SPS | 'NICHOLS 230KV' | 244 | 0.00348 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.20773 | 156
SPS | 'PLANTX 115KV' | 253 | 0.00527 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.20594 | 158
SPS | 'PLANTX 230KV' | 189 | 0.01075 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.20046 | 162
SPS | 'TOLK 230KV' | 60.2673 | 0.01153 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.19968 | 163
SPS | 'MADOX 115KV' | 102.3579 | -0.1187 | SPS | 'TOLK 230KV' | 1019.733 | 0.01153 | -0.13023 | 250
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11612 | SPS | 'TOLK 230KV' | 1019.733 | 0.01153 | -0.12765 | 255
SPS | 'MADOX 115KV' | 102.3579 | -0.1187 | SPS | 'WILWIND 230KV' | 160 | 0.00487 | -0.12357 | 263
SPS | 'MADOX 115KV' | 102.3579 | -0.1187 | SPS | 'BLACKHAWK 115KV' | 220 | 0.00348 | -0.12218 | 266
SPS | 'MADOX 115KV' | 102.3579 | -0.1187 | SPS | 'HARRINGTON 230KV' | 1066 | 0.00352 | -0.12222 | 266
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11612 | SPS | 'WILWIND 230KV' | 160 | 0.00487 | -0.12099 | 269
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11612 | SPS | 'BLACKHAWK 115KV' | 220 | 0.00348 | -0.1196 | 272
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11612 | SPS | 'HARRINGTON 230KV' | 1066 | 0.00352 | -0.11964 | 272
SPS | 'MADOX 115KV' | 102.3579 | -0.1187 | SPS | 'SAN JUAN 230KV' | 120 | -0.0036 | -0.1151 | 282
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11612 | SPS | 'SAN JUAN 230KV' | 120 | -0.0036 | -0.11252 | 289
SPS | 'MADOX 115KV' | 102.3579 | -0.1187 | SPS | 'JONES 230KV' | 486 | -0.00751 | -0.11119 | 292
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11612 | SPS | 'JONES 230KV' | 486 | -0.00751 | -0.10861 | 299
SPS | 'CUNNINGHAM 230KV' | 306 | -0.03606 | SPS | 'TOLK 230KV' | 1019.733 | 0.01153 | -0.04759 | 683
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | MUSTANG STATION 230/115KV TRANSFORMER CKT 1
Limiting Facility: | MUSTANG STATION 230/115KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | GEN:51971 1
Flowgate: | 51966519691GEN5197111107SH
Date Redispatch Needed: | 6/1 - 10/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 Summer Shoulder
Reservation | Relief Amount | Aggregate Relief Amount
1090487 | 29.1781 | 29.1781
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
SPS | 'MADOX 115KV' | 75 | -0.11872 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21119 | -0.32991 | 88
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11614 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21119 | -0.32733 | 89
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11614 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21119 | -0.32733 | 89
SPS | 'CUNNINGHAM 230KV' | 110 | -0.03607 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21119 | -0.24726 | 118
SPS | 'NICHOLS 115KV' | 131 | 0.0035 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21119 | -0.20769 | 140
SPS | 'MOORE COUNTY 115KV' | 48 | 0.00378 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21119 | -0.20741 | 141
SPS | 'NICHOLS 230KV' | 244 | 0.00359 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21119 | -0.2076 | 141
SPS | 'PLANTX 115KV' | 89.4741 | 0.00555 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21119 | -0.20564 | 142
SPS | 'TOLK 230KV' | 52.0113 | 0.01159 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21119 | -0.1996 | 146
SPS | 'MADOX 115KV' | 75 | -0.11872 | SPS | 'TOLK 230KV' | 1027.989 | 0.01159 | -0.13031 | 224
SPS | 'MADOX 115KV' | 75 | -0.11872 | SPS | 'PLANTX 230KV' | 189 | 0.01083 | -0.12955 | 225
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11614 | SPS | 'TOLK 230KV' | 1027.989 | 0.01159 | -0.12773 | 228
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11614 | SPS | 'PLANTX 230KV' | 189 | 0.01083 | -0.12697 | 230
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11614 | SPS | 'WILWIND 230KV' | 159.9636 | 0.00497 | -0.12111 | 241
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11614 | SPS | 'BLACKHAWK 115KV' | 220 | 0.00358 | -0.11972 | 244
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11614 | SPS | 'HARRINGTON 230KV' | 1066 | 0.00363 | -0.11977 | 244
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11614 | SPS | 'NICHOLS 115KV' | 82 | 0.0035 | -0.11964 | 244
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11614 | SPS | 'SAN JUAN 230KV' | 119.9727 | -0.00356 | -0.11258 | 259
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11614 | SPS | 'JONES 230KV' | 486 | -0.0077 | -0.10844 | 269
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | MUSTANG STATION 230/115KV TRANSFORMER CKT 1
Limiting Facility: | MUSTANG STATION 230/115KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | GEN:51971 1
Flowgate: | 51966519691GEN5197111107SP
Date Redispatch Needed: | 6/1/07 - 10/1/07
Season Flowgate Identified: | 2007 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1090487 | 35.577 | 35.577
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
SPS | 'MADOX 115KV' | 75 | -0.11872 | SPS | 'MUSTG5 118.0 230KV' | 360 | 0.21119 | -0.32991 | 108
SPS | 'CUNNINGHAM 115KV' | 50.0098 | -0.11614 | SPS | 'MUSTG5 118.0 230KV' | 360 | 0.21119 | -0.32733 | 109
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | MUSTANG STATION 230/115KV TRANSFORMER CKT 1
Limiting Facility: | MUSTANG STATION 230/115KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | GEN:51971 1
Flowgate: | 51966519691GEN5197111107WP
Date Redispatch Needed: | 12/1/07 - 4/1/08
Season Flowgate Identified: | 2007 Winter Peak
Reservation | Relief Amount | Aggregate Relief Amount
1090487 | 22.3598 | 22.3598
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
SPS | 'MUSTANG 115KV' | 29 | -0.39789 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.6091 | 37
SPS | 'MUSTANG 115KV' | 29 | -0.39789 | SPS | 'CAPROCK 115KV' | 79.9818 | 0.00659 | -0.40448 | 55
SPS | 'MUSTANG 115KV' | 29 | -0.39789 | SPS | 'TOLK 230KV' | 1019.542 | 0.01154 | -0.40943 | 55
SPS | 'MUSTANG 115KV' | 29 | -0.39789 | SPS | 'BLACKHAWK 115KV' | 220 | 0.00348 | -0.40137 | 56
SPS | 'MUSTANG 115KV' | 29 | -0.39789 | SPS | 'CZ 69KV' | 35 | 0.00316 | -0.40105 | 56
SPS | 'MUSTANG 115KV' | 29 | -0.39789 | SPS | 'HARRINGTON 230KV' | 1066 | 0.00353 | -0.40142 | 56
SPS | 'MUSTANG 115KV' | 29 | -0.39789 | SPS | 'STEER WATER 115KV' | 79.9818 | 0.00328 | -0.40117 | 56
SPS | 'MUSTANG 115KV' | 29 | -0.39789 | SPS | 'WILWIND 230KV' | 159.9636 | 0.00487 | -0.40276 | 56
SPS | 'MUSTANG 115KV' | 29 | -0.39789 | SPS | 'JONES 230KV' | 243 | -0.00751 | -0.39038 | 57
SPS | 'MUSTANG 115KV' | 29 | -0.39789 | SPS | 'LP-BRND2 69KV' | 60 | -0.00834 | -0.38955 | 57
SPS | 'MUSTANG 115KV' | 29 | -0.39789 | SPS | 'SAN JUAN 230KV' | 119.9727 | -0.0036 | -0.39429 | 57
SPS | 'MUSTANG 115KV' | 29 | -0.39789 | SPS | 'CUNNINGHAM 230KV' | 196 | -0.03606 | -0.36183 | 62
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11611 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.32732 | 68
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11611 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.32732 | 68
SPS | 'MADOX 115KV' | 100.0889 | -0.1187 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.32991 | 68
SPS | 'MUSTANG 115KV' | 29 | -0.39789 | SPS | 'MADOX 115KV' | 92.9111 | -0.1187 | -0.27919 | 80
SPS | 'CUNNINGHAM 230KV' | 110 | -0.03606 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.24727 | 90
SPS | 'JONES 230KV' | 243 | -0.00751 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.21872 | 102
SPS | 'LP-BRND2 69KV' | 172 | -0.00834 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.21955 | 102
SPS | 'MOORE COUNTY 115KV' | 48 | 0.00368 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.20753 | 108
SPS | 'NICHOLS 115KV' | 213 | 0.00339 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.20782 | 108
SPS | 'NICHOLS 230KV' | 244 | 0.00349 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.20772 | 108
SPS | 'PLANTX 115KV' | 253 | 0.00528 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.20593 | 109
SPS | 'PLANTX 230KV' | 189 | 0.01076 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.20045 | 112
SPS | 'TOLK 230KV' | 60.4575 | 0.01154 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.19967 | 112
SPS | 'MADOX 115KV' | 100.0889 | -0.1187 | SPS | 'TOLK 230KV' | 1019.542 | 0.01154 | -0.13024 | 172
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11611 | SPS | 'TOLK 230KV' | 1019.542 | 0.01154 | -0.12765 | 175
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11611 | SPS | 'TOLK 230KV' | 1019.542 | 0.01154 | -0.12765 | 175
SPS | 'MADOX 115KV' | 100.0889 | -0.1187 | SPS | 'CAPROCK 115KV' | 79.9818 | 0.00659 | -0.12529 | 178
SPS | 'MADOX 115KV' | 100.0889 | -0.1187 | SPS | 'WILWIND 230KV' | 159.9636 | 0.00487 | -0.12357 | 181
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11611 | SPS | 'CAPROCK 115KV' | 79.9818 | 0.00659 | -0.1227 | 182
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11611 | SPS | 'CAPROCK 115KV' | 79.9818 | 0.00659 | -0.1227 | 182
SPS | 'MADOX 115KV' | 100.0889 | -0.1187 | SPS | 'BLACKHAWK 115KV' | 220 | 0.00348 | -0.12218 | 183
SPS | 'MADOX 115KV' | 100.0889 | -0.1187 | SPS | 'HARRINGTON 230KV' | 1066 | 0.00353 | -0.12223 | 183
SPS | 'MADOX 115KV' | 100.0889 | -0.1187 | SPS | 'STEER WATER 115KV' | 79.9818 | 0.00328 | -0.12198 | 183
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11611 | SPS | 'WILWIND 230KV' | 159.9636 | 0.00487 | -0.12098 | 185
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11611 | SPS | 'WILWIND 230KV' | 159.9636 | 0.00487 | -0.12098 | 185
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11611 | SPS | 'BLACKHAWK 115KV' | 220 | 0.00348 | -0.11959 | 187
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11611 | SPS | 'BLACKHAWK 115KV' | 220 | 0.00348 | -0.11959 | 187
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11611 | SPS | 'HARRINGTON 230KV' | 1066 | 0.00353 | -0.11964 | 187
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11611 | SPS | 'HARRINGTON 230KV' | 1066 | 0.00353 | -0.11964 | 187
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11611 | SPS | 'STEER WATER 115KV' | 79.9818 | 0.00328 | -0.11939 | 187
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11611 | SPS | 'STEER WATER 115KV' | 79.9818 | 0.00328 | -0.11939 | 187
SPS | 'MADOX 115KV' | 100.0889 | -0.1187 | SPS | 'SAN JUAN 230KV' | 119.9727 | -0.0036 | -0.1151 | 194
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11611 | SPS | 'SAN JUAN 230KV' | 119.9727 | -0.0036 | -0.11251 | 199
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11611 | SPS | 'SAN JUAN 230KV' | 119.9727 | -0.0036 | -0.11251 | 199
SPS | 'MADOX 115KV' | 100.0889 | -0.1187 | SPS | 'JONES 230KV' | 243 | -0.00751 | -0.11119 | 201
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11611 | SPS | 'JONES 230KV' | 243 | -0.00751 | -0.1086 | 206
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11611 | SPS | 'JONES 230KV' | 243 | -0.00751 | -0.1086 | 206
SPS | 'MADOX 115KV' | 100.0889 | -0.1187 | SPS | 'CUNNINGHAM 230KV' | 196 | -0.03606 | -0.08264 | 271
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11611 | SPS | 'CUNNINGHAM 230KV' | 196 | -0.03606 | -0.08005 | 279
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | MUSTANG STATION 230/115KV TRANSFORMER CKT 1
Limiting Facility: | MUSTANG STATION 230/115KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | GEN:51971 1
Flowgate: | 51966519691GEN5197114107G
Date Redispatch Needed: | Starting 2007 4/1 - 6/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 Spring Peak
Reservation | Relief Amount | Aggregate Relief Amount
1090487 | 17.0367 | 17.0367
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11614 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21119 | -0.32733 | 52
SPS | 'MADOX 115KV' | 75 | -0.11872 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21119 | -0.32991 | 52
SPS | 'LP-BRND2 69KV' | 152 | -0.00854 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21119 | -0.21973 | 78
SPS | 'HARRINGTON 230KV' | 360 | 0.00363 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21119 | -0.20756 | 82
SPS | 'MOORE COUNTY 115KV' | 48 | 0.00378 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21119 | -0.20741 | 82
SPS | 'NICHOLS 115KV' | 107 | 0.0035 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21119 | -0.20769 | 82
SPS | 'NICHOLS 230KV' | 113.3726 | 0.00359 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21119 | -0.2076 | 82
SPS | 'PLANTX 115KV' | 48 | 0.00555 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21119 | -0.20564 | 83
SPS | 'TOLK 230KV' | 65.2912 | 0.01159 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21119 | -0.1996 | 85
SPS | 'MADOX 115KV' | 75 | -0.11872 | SPS | 'TOLK 230KV' | 1014.709 | 0.01159 | -0.13031 | 131
SPS | 'MADOX 115KV' | 75 | -0.11872 | SPS | 'PLANTX 230KV' | 189 | 0.01083 | -0.12955 | 132
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11614 | SPS | 'TOLK 230KV' | 1014.709 | 0.01159 | -0.12773 | 133
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11614 | SPS | 'PLANTX 230KV' | 189 | 0.01083 | -0.12697 | 134
SPS | 'MADOX 115KV' | 75 | -0.11872 | SPS | 'CAPROCK 115KV' | 80 | 0.00665 | -0.12537 | 136
SPS | 'MADOX 115KV' | 75 | -0.11872 | SPS | 'PLANTX 115KV' | 205 | 0.00555 | -0.12427 | 137
SPS | 'MADOX 115KV' | 75 | -0.11872 | SPS | 'WILWIND 230KV' | 159.9999 | 0.00497 | -0.12369 | 138
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11614 | SPS | 'CAPROCK 115KV' | 80 | 0.00665 | -0.12279 | 139
SPS | 'MADOX 115KV' | 75 | -0.11872 | SPS | 'HARRINGTON 230KV' | 706 | 0.00363 | -0.12235 | 139
SPS | 'MADOX 115KV' | 75 | -0.11872 | SPS | 'NICHOLS 230KV' | 130.6274 | 0.00359 | -0.12231 | 139
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11614 | SPS | 'PLANTX 115KV' | 205 | 0.00555 | -0.12169 | 140
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11614 | SPS | 'WILWIND 230KV' | 159.9999 | 0.00497 | -0.12111 | 141
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11614 | SPS | 'HARRINGTON 230KV' | 706 | 0.00363 | -0.11977 | 142
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11614 | SPS | 'NICHOLS 230KV' | 130.6274 | 0.00359 | -0.11973 | 142
SPS | 'MADOX 115KV' | 75 | -0.11872 | SPS | 'SAN JUAN 230KV' | 119.9999 | -0.00356 | -0.11516 | 148
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11614 | SPS | 'SAN JUAN 230KV' | 119.9999 | -0.00356 | -0.11258 | 151
SPS | 'MADOX 115KV' | 75 | -0.11872 | SPS | 'JONES 230KV' | 486 | -0.0077 | -0.11102 | 153
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11614 | SPS | 'JONES 230KV' | 486 | -0.0077 | -0.10844 | 157
SPS | 'MADOX 115KV' | 75 | -0.11872 | SPS | 'CUNNINGHAM 230KV' | 306 | -0.03607 | -0.08265 | 206
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11614 | SPS | 'CUNNINGHAM 230KV' | 306 | -0.03607 | -0.08007 | 213
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | MUSTANG STATION 230/115KV TRANSFORMER CKT 1
Limiting Facility: | MUSTANG STATION 230/115KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | GEN:51972 1
Flowgate: | 51966519691GEN5197211107FA
Date Redispatch Needed: | Starting 2007 10/1 - 12/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 Fall Peak
Reservation | Relief Amount | Aggregate Relief Amount
1090487 | 31.7888 | 31.7888
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
SPS | 'MADOX 115KV' | 102.3579 | -0.1187 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.32991 | 96
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11612 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.32733 | 97
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11612 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.32733 | 97
SPS | 'CUNNINGHAM 230KV' | 306 | -0.03606 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.24727 | 129
SPS | 'NICHOLS 115KV' | 213 | 0.00339 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.20782 | 153
SPS | 'NICHOLS 230KV' | 244 | 0.00348 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.20773 | 153
SPS | 'PLANTX 115KV' | 253 | 0.00527 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.20594 | 154
SPS | 'PLANTX 230KV' | 189 | 0.01075 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.20046 | 159
SPS | 'TOLK 230KV' | 60.2673 | 0.01153 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.19968 | 159
SPS | 'MADOX 115KV' | 102.3579 | -0.1187 | SPS | 'TOLK 230KV' | 1019.733 | 0.01153 | -0.13023 | 244
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11612 | SPS | 'TOLK 230KV' | 1019.733 | 0.01153 | -0.12765 | 249
SPS | 'MADOX 115KV' | 102.3579 | -0.1187 | SPS | 'WILWIND 230KV' | 160 | 0.00487 | -0.12357 | 257
SPS | 'MADOX 115KV' | 102.3579 | -0.1187 | SPS | 'BLACKHAWK 115KV' | 220 | 0.00348 | -0.12218 | 260
SPS | 'MADOX 115KV' | 102.3579 | -0.1187 | SPS | 'HARRINGTON 230KV' | 1066 | 0.00352 | -0.12222 | 260
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11612 | SPS | 'WILWIND 230KV' | 160 | 0.00487 | -0.12099 | 263
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11612 | SPS | 'BLACKHAWK 115KV' | 220 | 0.00348 | -0.1196 | 266
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11612 | SPS | 'HARRINGTON 230KV' | 1066 | 0.00352 | -0.11964 | 266
SPS | 'MADOX 115KV' | 102.3579 | -0.1187 | SPS | 'SAN JUAN 230KV' | 120 | -0.0036 | -0.1151 | 276
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11612 | SPS | 'SAN JUAN 230KV' | 120 | -0.0036 | -0.11252 | 283
SPS | 'MADOX 115KV' | 102.3579 | -0.1187 | SPS | 'JONES 230KV' | 486 | -0.00751 | -0.11119 | 286
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11612 | SPS | 'JONES 230KV' | 486 | -0.00751 | -0.10861 | 293
SPS | 'CUNNINGHAM 230KV' | 306 | -0.03606 | SPS | 'TOLK 230KV' | 1019.733 | 0.01153 | -0.04759 | 668
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | MUSTANG STATION 230/115KV TRANSFORMER CKT 1
Limiting Facility: | MUSTANG STATION 230/115KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | GEN:51972 1
Flowgate: | 51966519691GEN5197211107SH
Date Redispatch Needed: | 6/1 - 10/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 Summer Shoulder
Reservation | Relief Amount | Aggregate Relief Amount
1090487 | 28.4664 | 28.4664
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
SPS | 'MADOX 115KV' | 75 | -0.11872 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21119 | -0.32991 | 86
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11614 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21119 | -0.32733 | 87
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11614 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21119 | -0.32733 | 87
SPS | 'CUNNINGHAM 230KV' | 110 | -0.03607 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21119 | -0.24726 | 115
SPS | 'MOORE COUNTY 115KV' | 48 | 0.00378 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21119 | -0.20741 | 137
SPS | 'NICHOLS 115KV' | 131 | 0.0035 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21119 | -0.20769 | 137
SPS | 'NICHOLS 230KV' | 244 | 0.00359 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21119 | -0.2076 | 137
SPS | 'PLANTX 115KV' | 89.4741 | 0.00555 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21119 | -0.20564 | 138
SPS | 'TOLK 230KV' | 52.0113 | 0.01159 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21119 | -0.1996 | 143
SPS | 'MADOX 115KV' | 75 | -0.11872 | SPS | 'TOLK 230KV' | 1027.989 | 0.01159 | -0.13031 | 218
SPS | 'MADOX 115KV' | 75 | -0.11872 | SPS | 'PLANTX 230KV' | 189 | 0.01083 | -0.12955 | 220
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11614 | SPS | 'TOLK 230KV' | 1027.989 | 0.01159 | -0.12773 | 223
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11614 | SPS | 'PLANTX 230KV' | 189 | 0.01083 | -0.12697 | 224
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11614 | SPS | 'PLANTX 115KV' | 163.5259 | 0.00555 | -0.12169 | 234
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11614 | SPS | 'WILWIND 230KV' | 159.9636 | 0.00497 | -0.12111 | 235
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11614 | SPS | 'BLACKHAWK 115KV' | 220 | 0.00358 | -0.11972 | 238
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11614 | SPS | 'HARRINGTON 230KV' | 1066 | 0.00363 | -0.11977 | 238
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11614 | SPS | 'NICHOLS 115KV' | 82 | 0.0035 | -0.11964 | 238
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11614 | SPS | 'STEER WATER 115KV' | 79.9818 | 0.00338 | -0.11952 | 238
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11614 | SPS | 'SAN JUAN 230KV' | 119.9727 | -0.00356 | -0.11258 | 253
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11614 | SPS | 'JONES 230KV' | 486 | -0.0077 | -0.10844 | 263
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | MUSTANG STATION 230/115KV TRANSFORMER CKT 1
Limiting Facility: | MUSTANG STATION 230/115KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | GEN:51972 1
Flowgate: | 51966519691GEN5197211107SP
Date Redispatch Needed: | 6/1/07 - 10/1/07
Season Flowgate Identified: | 2007 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1090487 | 35.577 | 35.577
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
SPS | 'MADOX 115KV' | 75 | -0.11872 | SPS | 'MUSTG5 118.0 230KV' | 360 | 0.21119 | -0.32991 | 108
SPS | 'CUNNINGHAM 115KV' | 50.0098 | -0.11614 | SPS | 'MUSTG5 118.0 230KV' | 360 | 0.21119 | -0.32733 | 109
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | MUSTANG STATION 230/115KV TRANSFORMER CKT 1
Limiting Facility: | MUSTANG STATION 230/115KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | GEN:51972 1
Flowgate: | 51966519691GEN5197211107WP
Date Redispatch Needed: | 12/1/07 - 4/1/08
Season Flowgate Identified: | 2007 Winter Peak
Reservation | Relief Amount | Aggregate Relief Amount
1090487 | 21.884 | 21.884
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
SPS | 'MUSTANG 115KV' | 29 | -0.39789 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.6091 | 36
SPS | 'MUSTANG 115KV' | 29 | -0.39789 | SPS | 'TOLK 230KV' | 1019.542 | 0.01154 | -0.40943 | 53
SPS | 'MUSTANG 115KV' | 29 | -0.39789 | SPS | 'CAPROCK 115KV' | 79.9818 | 0.00659 | -0.40448 | 54
SPS | 'MUSTANG 115KV' | 29 | -0.39789 | SPS | 'WILWIND 230KV' | 159.9636 | 0.00487 | -0.40276 | 54
SPS | 'MUSTANG 115KV' | 29 | -0.39789 | SPS | 'BLACKHAWK 115KV' | 220 | 0.00348 | -0.40137 | 55
SPS | 'MUSTANG 115KV' | 29 | -0.39789 | SPS | 'CZ 69KV' | 35 | 0.00316 | -0.40105 | 55
SPS | 'MUSTANG 115KV' | 29 | -0.39789 | SPS | 'HARRINGTON 230KV' | 1066 | 0.00353 | -0.40142 | 55
SPS | 'MUSTANG 115KV' | 29 | -0.39789 | SPS | 'STEER WATER 115KV' | 79.9818 | 0.00328 | -0.40117 | 55
SPS | 'MUSTANG 115KV' | 29 | -0.39789 | SPS | 'JONES 230KV' | 243 | -0.00751 | -0.39038 | 56
SPS | 'MUSTANG 115KV' | 29 | -0.39789 | SPS | 'LP-BRND2 69KV' | 60 | -0.00834 | -0.38955 | 56
SPS | 'MUSTANG 115KV' | 29 | -0.39789 | SPS | 'SAN JUAN 230KV' | 119.9727 | -0.0036 | -0.39429 | 56
SPS | 'MUSTANG 115KV' | 29 | -0.39789 | SPS | 'CUNNINGHAM 230KV' | 196 | -0.03606 | -0.36183 | 60
SPS | 'MADOX 115KV' | 100.0889 | -0.1187 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.32991 | 66
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11611 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.32732 | 67
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11611 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.32732 | 67
SPS | 'MUSTANG 115KV' | 29 | -0.39789 | SPS | 'MADOX 115KV' | 92.9111 | -0.1187 | -0.27919 | 78
SPS | 'CUNNINGHAM 230KV' | 110 | -0.03606 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.24727 | 89
SPS | 'JONES 230KV' | 243 | -0.00751 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.21872 | 100
SPS | 'LP-BRND2 69KV' | 172 | -0.00834 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.21955 | 100
SPS | 'MOORE COUNTY 115KV' | 48 | 0.00368 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.20753 | 105
SPS | 'NICHOLS 115KV' | 213 | 0.00339 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.20782 | 105
SPS | 'NICHOLS 230KV' | 244 | 0.00349 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.20772 | 105
SPS | 'PLANTX 115KV' | 253 | 0.00528 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.20593 | 106
SPS | 'PLANTX 230KV' | 189 | 0.01076 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.20045 | 109
SPS | 'TOLK 230KV' | 60.4575 | 0.01154 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21121 | -0.19967 | 110
SPS | 'MADOX 115KV' | 100.0889 | -0.1187 | SPS | 'TOLK 230KV' | 1019.542 | 0.01154 | -0.13024 | 168
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11611 | SPS | 'TOLK 230KV' | 1019.542 | 0.01154 | -0.12765 | 171
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11611 | SPS | 'TOLK 230KV' | 1019.542 | 0.01154 | -0.12765 | 171
SPS | 'MADOX 115KV' | 100.0889 | -0.1187 | SPS | 'CAPROCK 115KV' | 79.9818 | 0.00659 | -0.12529 | 175
SPS | 'MADOX 115KV' | 100.0889 | -0.1187 | SPS | 'WILWIND 230KV' | 159.9636 | 0.00487 | -0.12357 | 177
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11611 | SPS | 'CAPROCK 115KV' | 79.9818 | 0.00659 | -0.1227 | 178
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11611 | SPS | 'CAPROCK 115KV' | 79.9818 | 0.00659 | -0.1227 | 178
SPS | 'MADOX 115KV' | 100.0889 | -0.1187 | SPS | 'BLACKHAWK 115KV' | 220 | 0.00348 | -0.12218 | 179
SPS | 'MADOX 115KV' | 100.0889 | -0.1187 | SPS | 'HARRINGTON 230KV' | 1066 | 0.00353 | -0.12223 | 179
SPS | 'MADOX 115KV' | 100.0889 | -0.1187 | SPS | 'STEER WATER 115KV' | 79.9818 | 0.00328 | -0.12198 | 179
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11611 | SPS | 'WILWIND 230KV' | 159.9636 | 0.00487 | -0.12098 | 181
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11611 | SPS | 'WILWIND 230KV' | 159.9636 | 0.00487 | -0.12098 | 181
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11611 | SPS | 'BLACKHAWK 115KV' | 220 | 0.00348 | -0.11959 | 183
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11611 | SPS | 'BLACKHAWK 115KV' | 220 | 0.00348 | -0.11959 | 183
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11611 | SPS | 'HARRINGTON 230KV' | 1066 | 0.00353 | -0.11964 | 183
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11611 | SPS | 'HARRINGTON 230KV' | 1066 | 0.00353 | -0.11964 | 183
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11611 | SPS | 'STEER WATER 115KV' | 79.9818 | 0.00328 | -0.11939 | 183
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11611 | SPS | 'STEER WATER 115KV' | 79.9818 | 0.00328 | -0.11939 | 183
SPS | 'MADOX 115KV' | 100.0889 | -0.1187 | SPS | 'SAN JUAN 230KV' | 119.9727 | -0.0036 | -0.1151 | 190
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11611 | SPS | 'SAN JUAN 230KV' | 119.9727 | -0.0036 | -0.11251 | 195
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11611 | SPS | 'SAN JUAN 230KV' | 119.9727 | -0.0036 | -0.11251 | 195
SPS | 'MADOX 115KV' | 100.0889 | -0.1187 | SPS | 'JONES 230KV' | 243 | -0.00751 | -0.11119 | 197
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11611 | SPS | 'JONES 230KV' | 243 | -0.00751 | -0.1086 | 202
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11611 | SPS | 'JONES 230KV' | 243 | -0.00751 | -0.1086 | 202
SPS | 'MADOX 115KV' | 100.0889 | -0.1187 | SPS | 'CUNNINGHAM 230KV' | 196 | -0.03606 | -0.08264 | 265
SPS | 'CUNNINGHAM 115KV' | 110 | -0.11611 | SPS | 'CUNNINGHAM 230KV' | 196 | -0.03606 | -0.08005 | 273
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | MUSTANG STATION 230/115KV TRANSFORMER CKT 1
Limiting Facility: | MUSTANG STATION 230/115KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | GEN:51972 1
Flowgate: | 51966519691GEN5197214107G
Date Redispatch Needed: | Starting 2007 4/1 - 6/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 Spring Peak
Reservation | Relief Amount | Aggregate Relief Amount
1090487 | 16.1032 | 16.1032
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11614 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21119 | -0.32733 | 49
SPS | 'MADOX 115KV' | 75 | -0.11872 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21119 | -0.32991 | 49
SPS | 'LP-BRND2 69KV' | 152 | -0.00854 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21119 | -0.21973 | 73
SPS | 'HARRINGTON 230KV' | 360 | 0.00363 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21119 | -0.20756 | 78
SPS | 'MOORE COUNTY 115KV' | 48 | 0.00378 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21119 | -0.20741 | 78
SPS | 'NICHOLS 115KV' | 107 | 0.0035 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21119 | -0.20769 | 78
SPS | 'NICHOLS 230KV' | 113.3726 | 0.00359 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21119 | -0.2076 | 78
SPS | 'PLANTX 115KV' | 48 | 0.00555 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21119 | -0.20564 | 78
SPS | 'TOLK 230KV' | 65.2912 | 0.01159 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.21119 | -0.1996 | 81
SPS | 'MADOX 115KV' | 75 | -0.11872 | SPS | 'PLANTX 230KV' | 189 | 0.01083 | -0.12955 | 124
SPS | 'MADOX 115KV' | 75 | -0.11872 | SPS | 'TOLK 230KV' | 1014.709 | 0.01159 | -0.13031 | 124
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11614 | SPS | 'TOLK 230KV' | 1014.709 | 0.01159 | -0.12773 | 126
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11614 | SPS | 'PLANTX 230KV' | 189 | 0.01083 | -0.12697 | 127
SPS | 'MADOX 115KV' | 75 | -0.11872 | SPS | 'CAPROCK 115KV' | 80 | 0.00665 | -0.12537 | 128
SPS | 'MADOX 115KV' | 75 | -0.11872 | SPS | 'PLANTX 115KV' | 205 | 0.00555 | -0.12427 | 130
SPS | 'MADOX 115KV' | 75 | -0.11872 | SPS | 'WILWIND 230KV' | 159.9999 | 0.00497 | -0.12369 | 130
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11614 | SPS | 'CAPROCK 115KV' | 80 | 0.00665 | -0.12279 | 131
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11614 | SPS | 'PLANTX 115KV' | 205 | 0.00555 | -0.12169 | 132
SPS | 'MADOX 115KV' | 75 | -0.11872 | SPS | 'HARRINGTON 230KV' | 706 | 0.00363 | -0.12235 | 132
SPS | 'MADOX 115KV' | 75 | -0.11872 | SPS | 'NICHOLS 230KV' | 130.6274 | 0.00359 | -0.12231 | 132
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11614 | SPS | 'WILWIND 230KV' | 159.9999 | 0.00497 | -0.12111 | 133
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11614 | SPS | 'HARRINGTON 230KV' | 706 | 0.00363 | -0.11977 | 134
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11614 | SPS | 'NICHOLS 230KV' | 130.6274 | 0.00359 | -0.11973 | 134
SPS | 'MADOX 115KV' | 75 | -0.11872 | SPS | 'SAN JUAN 230KV' | 119.9999 | -0.00356 | -0.11516 | 140
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11614 | SPS | 'SAN JUAN 230KV' | 119.9999 | -0.00356 | -0.11258 | 143
SPS | 'MADOX 115KV' | 75 | -0.11872 | SPS | 'JONES 230KV' | 486 | -0.0077 | -0.11102 | 145
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11614 | SPS | 'JONES 230KV' | 486 | -0.0077 | -0.10844 | 148
SPS | 'MADOX 115KV' | 75 | -0.11872 | SPS | 'CUNNINGHAM 230KV' | 306 | -0.03607 | -0.08265 | 195
SPS | 'CUNNINGHAM 115KV' | 71 | -0.11614 | SPS | 'CUNNINGHAM 230KV' | 306 | -0.03607 | -0.08007 | 201
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | Mustang-San Andr-Amerada Hess 115KV Displacement
Limiting Facility: | DENVER CITY INTERCHANGE N - MUSTANG STATION 115KV CKT 1
Direction: | To->From
Line Outage: | DENVER CITY INTERCHANGE S - MUSTANG STATION 115KV CKT 1
Flowgate: | 51960519661519625196811107SH
Date Redispatch Needed: | 6/1 - 10/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 Summer Shoulder
Reservation | Relief Amount | Aggregate Relief Amount
1090487 | 13.34 | 13.34
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
SPS | 'MADOX 115KV' | 75 | -0.16452 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.15058 | -0.3151 | 42
SPS | 'CUNNINGHAM 115KV' | 71 | -0.16155 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.15058 | -0.31213 | 43
SPS | 'CUNNINGHAM 115KV' | 110 | -0.16155 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.15058 | -0.31213 | 43
SPS | 'CUNNINGHAM 230KV' | 110 | -0.07301 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.15058 | -0.22359 | 60
SPS | 'MADOX 115KV' | 75 | -0.16452 | SPS | 'PLANTX 230KV' | 189 | 0.00438 | -0.1689 | 79
SPS | 'MADOX 115KV' | 75 | -0.16452 | SPS | 'TOLK 230KV' | 1027.989 | 0.00375 | -0.16827 | 79
SPS | 'CUNNINGHAM 115KV' | 71 | -0.16155 | SPS | 'PLANTX 230KV' | 189 | 0.00438 | -0.16593 | 80
SPS | 'CUNNINGHAM 115KV' | 110 | -0.16155 | SPS | 'PLANTX 230KV' | 189 | 0.00438 | -0.16593 | 80
SPS | 'MADOX 115KV' | 75 | -0.16452 | SPS | 'BLACKHAWK 115KV' | 220 | 0.0013 | -0.16582 | 80
SPS | 'MADOX 115KV' | 75 | -0.16452 | SPS | 'HARRINGTON 230KV' | 1066 | 0.00132 | -0.16584 | 80
SPS | 'MADOX 115KV' | 75 | -0.16452 | SPS | 'NICHOLS 115KV' | 82 | 0.00126 | -0.16578 | 80
SPS | 'MADOX 115KV' | 75 | -0.16452 | SPS | 'PLANTX 115KV' | 163.5259 | 0.0022 | -0.16672 | 80
SPS | 'MADOX 115KV' | 75 | -0.16452 | SPS | 'STEER WATER 115KV' | 79.9818 | 0.00122 | -0.16574 | 80
SPS | 'MADOX 115KV' | 75 | -0.16452 | SPS | 'WILWIND 230KV' | 159.9636 | 0.00178 | -0.1663 | 80
SPS | 'CUNNINGHAM 115KV' | 71 | -0.16155 | SPS | 'PLANTX 115KV' | 163.5259 | 0.0022 | -0.16375 | 81
SPS | 'CUNNINGHAM 115KV' | 110 | -0.16155 | SPS | 'PLANTX 115KV' | 163.5259 | 0.0022 | -0.16375 | 81
SPS | 'CUNNINGHAM 115KV' | 71 | -0.16155 | SPS | 'TOLK 230KV' | 1027.989 | 0.00375 | -0.1653 | 81
SPS | 'CUNNINGHAM 115KV' | 110 | -0.16155 | SPS | 'TOLK 230KV' | 1027.989 | 0.00375 | -0.1653 | 81
SPS | 'CUNNINGHAM 115KV' | 71 | -0.16155 | SPS | 'BLACKHAWK 115KV' | 220 | 0.0013 | -0.16285 | 82
SPS | 'CUNNINGHAM 115KV' | 110 | -0.16155 | SPS | 'BLACKHAWK 115KV' | 220 | 0.0013 | -0.16285 | 82
SPS | 'CUNNINGHAM 115KV' | 71 | -0.16155 | SPS | 'HARRINGTON 230KV' | 1066 | 0.00132 | -0.16287 | 82
SPS | 'CUNNINGHAM 115KV' | 110 | -0.16155 | SPS | 'HARRINGTON 230KV' | 1066 | 0.00132 | -0.16287 | 82
SPS | 'CUNNINGHAM 115KV' | 71 | -0.16155 | SPS | 'NICHOLS 115KV' | 82 | 0.00126 | -0.16281 | 82
SPS | 'CUNNINGHAM 115KV' | 110 | -0.16155 | SPS | 'NICHOLS 115KV' | 82 | 0.00126 | -0.16281 | 82
SPS | 'CUNNINGHAM 115KV' | 71 | -0.16155 | SPS | 'STEER WATER 115KV' | 79.9818 | 0.00122 | -0.16277 | 82
SPS | 'CUNNINGHAM 115KV' | 110 | -0.16155 | SPS | 'STEER WATER 115KV' | 79.9818 | 0.00122 | -0.16277 | 82
SPS | 'CUNNINGHAM 115KV' | 71 | -0.16155 | SPS | 'WILWIND 230KV' | 159.9636 | 0.00178 | -0.16333 | 82
SPS | 'CUNNINGHAM 115KV' | 110 | -0.16155 | SPS | 'WILWIND 230KV' | 159.9636 | 0.00178 | -0.16333 | 82
SPS | 'MADOX 115KV' | 75 | -0.16452 | SPS | 'CAPROCK 115KV' | 79.9818 | -0.00267 | -0.16185 | 82
SPS | 'MADOX 115KV' | 75 | -0.16452 | SPS | 'JONES 230KV' | 486 | -0.00223 | -0.16229 | 82
SPS | 'MADOX 115KV' | 75 | -0.16452 | SPS | 'LP-BRND2 69KV' | 80 | -0.00258 | -0.16194 | 82
SPS | 'CUNNINGHAM 115KV' | 71 | -0.16155 | SPS | 'CAPROCK 115KV' | 79.9818 | -0.00267 | -0.15888 | 84
SPS | 'CUNNINGHAM 115KV' | 110 | -0.16155 | SPS | 'CAPROCK 115KV' | 79.9818 | -0.00267 | -0.15888 | 84
SPS | 'CUNNINGHAM 115KV' | 71 | -0.16155 | SPS | 'JONES 230KV' | 486 | -0.00223 | -0.15932 | 84
SPS | 'CUNNINGHAM 115KV' | 110 | -0.16155 | SPS | 'JONES 230KV' | 486 | -0.00223 | -0.15932 | 84
SPS | 'CUNNINGHAM 115KV' | 71 | -0.16155 | SPS | 'LP-BRND2 69KV' | 80 | -0.00258 | -0.15897 | 84
SPS | 'LP-BRND2 69KV' | 152 | -0.00258 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.15058 | -0.15316 | 87
SPS | 'MOORE COUNTY 115KV' | 48 | 0.00138 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.15058 | -0.1492 | 89
SPS | 'NICHOLS 115KV' | 131 | 0.00126 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.15058 | -0.14932 | 89
SPS | 'NICHOLS 230KV' | 244 | 0.0013 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.15058 | -0.14928 | 89
SPS | 'PLANTX 115KV' | 89.4741 | 0.0022 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.15058 | -0.14838 | 90
SPS | 'TOLK 230KV' | 52.0113 | 0.00375 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.15058 | -0.14683 | 91
SPS | 'MADOX 115KV' | 75 | -0.16452 | SPS | 'SAN JUAN 230KV' | 119.9727 | -0.01887 | -0.14565 | 92
SPS | 'CUNNINGHAM 115KV' | 71 | -0.16155 | SPS | 'SAN JUAN 230KV' | 119.9727 | -0.01887 | -0.14268 | 93
SPS | 'CUNNINGHAM 115KV' | 110 | -0.16155 | SPS | 'SAN JUAN 230KV' | 119.9727 | -0.01887 | -0.14268 | 93
SPS | 'MADOX 115KV' | 75 | -0.16452 | SPS | 'CUNNINGHAM 230KV' | 196 | -0.07301 | -0.09151 | 146
SPS | 'CUNNINGHAM 115KV' | 71 | -0.16155 | SPS | 'CUNNINGHAM 230KV' | 196 | -0.07301 | -0.08854 | 151
SPS | 'CUNNINGHAM 115KV' | 110 | -0.16155 | SPS | 'CUNNINGHAM 230KV' | 196 | -0.07301 | -0.08854 | 151
SPS | 'CUNNINGHAM 230KV' | 110 | -0.07301 | SPS | 'PLANTX 230KV' | 189 | 0.00438 | -0.07739 | 172
SPS | 'CUNNINGHAM 230KV' | 110 | -0.07301 | SPS | 'TOLK 230KV' | 1027.989 | 0.00375 | -0.07676 | 174
SPS | 'CUNNINGHAM 230KV' | 110 | -0.07301 | SPS | 'PLANTX 115KV' | 163.5259 | 0.0022 | -0.07521 | 177
SPS | 'CUNNINGHAM 230KV' | 110 | -0.07301 | SPS | 'WILWIND 230KV' | 159.9636 | 0.00178 | -0.07479 | 178
SPS | 'CUNNINGHAM 230KV' | 110 | -0.07301 | SPS | 'HARRINGTON 230KV' | 1066 | 0.00132 | -0.07433 | 179
SPS | 'CUNNINGHAM 230KV' | 110 | -0.07301 | SPS | 'BLACKHAWK 115KV' | 220 | 0.0013 | -0.07431 | 180
SPS | 'CUNNINGHAM 230KV' | 110 | -0.07301 | SPS | 'NICHOLS 115KV' | 82 | 0.00126 | -0.07427 | 180
SPS | 'CUNNINGHAM 230KV' | 110 | -0.07301 | SPS | 'STEER WATER 115KV' | 79.9818 | 0.00122 | -0.07423 | 180
SPS | 'CUNNINGHAM 230KV' | 110 | -0.07301 | SPS | 'JONES 230KV' | 486 | -0.00223 | -0.07078 | 188
SPS | 'CUNNINGHAM 230KV' | 110 | -0.07301 | SPS | 'CAPROCK 115KV' | 79.9818 | -0.00267 | -0.07034 | 190
SPS | 'CUNNINGHAM 230KV' | 110 | -0.07301 | SPS | 'SAN JUAN 230KV' | 119.9727 | -0.01887 | -0.05414 | 246
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | Mustang-San Andr-Amerada Hess 115KV Displacement
Limiting Facility: | DENVER CITY INTERCHANGE N - MUSTANG STATION 115KV CKT 1
Direction: | To->From
Line Outage: | DENVER CITY INTERCHANGE S - MUSTANG STATION 115KV CKT 1
Flowgate: | 51960519661519625196811107SP
Date Redispatch Needed: | 6/1/07 - 10/1/07
Season Flowgate Identified: | 2007 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1090487 | 23.82 | 23.82
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
SPS | 'CUNNINGHAM 115KV' | 50.0098 | -0.16155 | SPS | 'MUSTG5 118.0 230KV' | 360 | 0.15058 | -0.31213 | 76
SPS | 'MADOX 115KV' | 75 | -0.16452 | SPS | 'MUSTG5 118.0 230KV' | 360 | 0.15058 | -0.3151 | 76
SPS | 'MADOX 115KV' | 75 | -0.16452 | SPS | 'PLANTX 230KV' | 189 | 0.00438 | -0.1689 | 141
SPS | 'MADOX 115KV' | 75 | -0.16452 | SPS | 'TOLK 230KV' | 1024.722 | 0.00375 | -0.16827 | 142
SPS | 'MADOX 115KV' | 75 | -0.16452 | SPS | 'PLANTX 115KV' | 205 | 0.0022 | -0.16672 | 143
SPS | 'MADOX 115KV' | 75 | -0.16452 | SPS | 'WILWIND 230KV' | 159.9636 | 0.00178 | -0.1663 | 143
SPS | 'CUNNINGHAM 115KV' | 50.0098 | -0.16155 | SPS | 'PLANTX 230KV' | 189 | 0.00438 | -0.16593 | 144
SPS | 'CUNNINGHAM 115KV' | 50.0098 | -0.16155 | SPS | 'TOLK 230KV' | 1024.722 | 0.00375 | -0.1653 | 144
SPS | 'MADOX 115KV' | 75 | -0.16452 | SPS | 'BLACKHAWK 115KV' | 220 | 0.0013 | -0.16582 | 144
SPS | 'MADOX 115KV' | 75 | -0.16452 | SPS | 'HARRINGTON 230KV' | 1066 | 0.00132 | -0.16584 | 144
SPS | 'MADOX 115KV' | 75 | -0.16452 | SPS | 'NICHOLS 115KV' | 147 | 0.00126 | -0.16578 | 144
SPS | 'MADOX 115KV' | 75 | -0.16452 | SPS | 'NICHOLS 230KV' | 147 | 0.0013 | -0.16582 | 144
SPS | 'MADOX 115KV' | 75 | -0.16452 | SPS | 'STEER WATER 115KV' | 79.9818 | 0.00122 | -0.16574 | 144
SPS | 'CUNNINGHAM 115KV' | 50.0098 | -0.16155 | SPS | 'PLANTX 115KV' | 205 | 0.0022 | -0.16375 | 145
SPS | 'CUNNINGHAM 115KV' | 50.0098 | -0.16155 | SPS | 'BLACKHAWK 115KV' | 220 | 0.0013 | -0.16285 | 146
SPS | 'CUNNINGHAM 115KV' | 50.0098 | -0.16155 | SPS | 'HARRINGTON 230KV' | 1066 | 0.00132 | -0.16287 | 146
SPS | 'CUNNINGHAM 115KV' | 50.0098 | -0.16155 | SPS | 'NICHOLS 115KV' | 147 | 0.00126 | -0.16281 | 146
SPS | 'CUNNINGHAM 115KV' | 50.0098 | -0.16155 | SPS | 'NICHOLS 230KV' | 147 | 0.0013 | -0.16285 | 146
SPS | 'CUNNINGHAM 115KV' | 50.0098 | -0.16155 | SPS | 'STEER WATER 115KV' | 79.9818 | 0.00122 | -0.16277 | 146
SPS | 'CUNNINGHAM 115KV' | 50.0098 | -0.16155 | SPS | 'WILWIND 230KV' | 159.9636 | 0.00178 | -0.16333 | 146
SPS | 'MADOX 115KV' | 75 | -0.16452 | SPS | 'CAPROCK 115KV' | 79.9818 | -0.00267 | -0.16185 | 147
SPS | 'MADOX 115KV' | 75 | -0.16452 | SPS | 'JONES 230KV' | 486 | -0.00223 | -0.16229 | 147
SPS | 'CUNNINGHAM 115KV' | 50.0098 | -0.16155 | SPS | 'CAPROCK 115KV' | 79.9818 | -0.00267 | -0.15888 | 150
SPS | 'CUNNINGHAM 115KV' | 50.0098 | -0.16155 | SPS | 'JONES 230KV' | 486 | -0.00223 | -0.15932 | 150
SPS | 'TOLK 230KV' | 55.2779 | 0.00375 | SPS | 'MUSTG5 118.0 230KV' | 360 | 0.15058 | -0.14683 | 162
SPS | 'MADOX 115KV' | 75 | -0.16452 | SPS | 'SAN JUAN 230KV' | 119.9727 | -0.01887 | -0.14565 | 164
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | Mustang-San Andr-Amerada Hess 115KV Displacement
Limiting Facility: | DENVER CITY INTERCHANGE N - MUSTANG STATION 115KV CKT 1
Direction: | To->From
Line Outage: | DENVER CITY INTERCHANGE S - MUSTANG STATION 115KV CKT 1
Flowgate: | 51960519661519625196811407G
Date Redispatch Needed: | Starting 2007 4/1 - 6/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 Spring Peak
Reservation | Relief Amount | Aggregate Relief Amount
1090487 | 1.8935 | 1.8935
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
SPS | 'CUNNINGHAM 115KV' | 71 | -0.16155 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.15058 | -0.31213 | 6
SPS | 'MADOX 115KV' | 75 | -0.16452 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.15058 | -0.3151 | 6
SPS | 'CARLSBAD 69KV' | 18 | -0.07652 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.15058 | -0.2271 | 8
SPS | 'CUNNINGHAM 115KV' | 71 | -0.16155 | SPS | 'PLANTX 230KV' | 189 | 0.00438 | -0.16593 | 11
SPS | 'CUNNINGHAM 115KV' | 71 | -0.16155 | SPS | 'TOLK 230KV' | 1012.904 | 0.00374 | -0.16529 | 11
SPS | 'MADOX 115KV' | 75 | -0.16452 | SPS | 'HARRINGTON 230KV' | 706 | 0.00132 | -0.16584 | 11
SPS | 'MADOX 115KV' | 75 | -0.16452 | SPS | 'PLANTX 115KV' | 205 | 0.0022 | -0.16672 | 11
SPS | 'MADOX 115KV' | 75 | -0.16452 | SPS | 'PLANTX 230KV' | 189 | 0.00438 | -0.1689 | 11
SPS | 'MADOX 115KV' | 75 | -0.16452 | SPS | 'TOLK 230KV' | 1012.904 | 0.00374 | -0.16826 | 11
SPS | 'MADOX 115KV' | 75 | -0.16452 | SPS | 'WILWIND 230KV' | 72 | 0.00178 | -0.1663 | 11
SPS | 'CUNNINGHAM 115KV' | 71 | -0.16155 | SPS | 'CAPROCK 115KV' | 36 | -0.00267 | -0.15888 | 12
SPS | 'CUNNINGHAM 115KV' | 71 | -0.16155 | SPS | 'HARRINGTON 230KV' | 706 | 0.00132 | -0.16287 | 12
SPS | 'CUNNINGHAM 115KV' | 71 | -0.16155 | SPS | 'JONES 230KV' | 486 | -0.00223 | -0.15932 | 12
SPS | 'CUNNINGHAM 115KV' | 71 | -0.16155 | SPS | 'LP-BRND2 69KV' | 80 | -0.00258 | -0.15897 | 12
SPS | 'CUNNINGHAM 115KV' | 71 | -0.16155 | SPS | 'PLANTX 115KV' | 205 | 0.0022 | -0.16375 | 12
SPS | 'CUNNINGHAM 115KV' | 71 | -0.16155 | SPS | 'WILWIND 230KV' | 72 | 0.00178 | -0.16333 | 12
SPS | 'LP-BRND2 69KV' | 152 | -0.00258 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.15058 | -0.15316 | 12
SPS | 'MADOX 115KV' | 75 | -0.16452 | SPS | 'CAPROCK 115KV' | 36 | -0.00267 | -0.16185 | 12
SPS | 'MADOX 115KV' | 75 | -0.16452 | SPS | 'JONES 230KV' | 486 | -0.00223 | -0.16229 | 12
SPS | 'MADOX 115KV' | 75 | -0.16452 | SPS | 'LP-BRND2 69KV' | 80 | -0.00258 | -0.16194 | 12
SPS | 'TUCUMCARI 115KV' | 15 | -0.00267 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.15058 | -0.15325 | 12
SPS | 'CUNNINGHAM 115KV' | 71 | -0.16155 | SPS | 'SAN JUAN 230KV' | 54 | -0.01887 | -0.14268 | 13
SPS | 'HARRINGTON 230KV' | 360 | 0.00132 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.15058 | -0.14926 | 13
SPS | 'HUBRCO2 69KV' | 6 | 0.0013 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.15058 | -0.14928 | 13
SPS | 'MADOX 115KV' | 75 | -0.16452 | SPS | 'SAN JUAN 230KV' | 54 | -0.01887 | -0.14565 | 13
SPS | 'MOORE COUNTY 115KV' | 48 | 0.00138 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.15058 | -0.1492 | 13
SPS | 'NICHOLS 115KV' | 132.2241 | 0.00126 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.15058 | -0.14932 | 13
SPS | 'NICHOLS 230KV' | 244 | 0.0013 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.15058 | -0.14928 | 13
SPS | 'PLANTX 115KV' | 48 | 0.0022 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.15058 | -0.14838 | 13
SPS | 'RIVERVIEW 69KV' | 23 | 0.0013 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.15058 | -0.14928 | 13
SPS | 'SIDRCH 69KV' | 6 | 0.0013 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.15058 | -0.14928 | 13
SPS | 'TOLK 230KV' | 67.0959 | 0.00374 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.15058 | -0.14684 | 13
SPS | 'CUNNINGHAM 115KV' | 71 | -0.16155 | SPS | 'CUNNINGHAM 230KV' | 306 | -0.07301 | -0.08854 | 21
SPS | 'MADOX 115KV' | 75 | -0.16452 | SPS | 'CUNNINGHAM 230KV' | 306 | -0.07301 | -0.09151 | 21
SPS | 'CARLSBAD 69KV' | 18 | -0.07652 | SPS | 'PLANTX 230KV' | 189 | 0.00438 | -0.0809 | 23
SPS | 'CARLSBAD 69KV' | 18 | -0.07652 | SPS | 'HARRINGTON 230KV' | 706 | 0.00132 | -0.07784 | 24
SPS | 'CARLSBAD 69KV' | 18 | -0.07652 | SPS | 'PLANTX 115KV' | 205 | 0.0022 | -0.07872 | 24
SPS | 'CARLSBAD 69KV' | 18 | -0.07652 | SPS | 'TOLK 230KV' | 1012.904 | 0.00374 | -0.08026 | 24
SPS | 'CARLSBAD 69KV' | 18 | -0.07652 | SPS | 'WILWIND 230KV' | 72 | 0.00178 | -0.0783 | 24
SPS | 'CARLSBAD 69KV' | 18 | -0.07652 | SPS | 'JONES 230KV' | 486 | -0.00223 | -0.07429 | 25
SPS | 'CARLSBAD 69KV' | 18 | -0.07652 | SPS | 'CAPROCK 115KV' | 36 | -0.00267 | -0.07385 | 26
SPS | 'CARLSBAD 69KV' | 18 | -0.07652 | SPS | 'LP-BRND2 69KV' | 80 | -0.00258 | -0.07394 | 26
SPS | 'CARLSBAD 69KV' | 18 | -0.07652 | SPS | 'SAN JUAN 230KV' | 54 | -0.01887 | -0.05765 | 33
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | Mustang-San Andr-Amerada Hess 115KV Displacement
Limiting Facility: | DENVER CITY INTERCHANGE S - MUSTANG STATION 115KV CKT 1
Direction: | To->From
Line Outage: | DENVER CITY INTERCHANGE N - MUSTANG STATION 115KV CKT 1
Flowgate: | 51962519681519605196611107SH
Date Redispatch Needed: | 6/1 - 10/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 Summer Shoulder
Reservation | Relief Amount | Aggregate Relief Amount
1090487 | 9.4818 | 9.4818
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
SPS | 'MADOX 115KV' | 75 | -0.16383 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.14753 | -0.31136 | 30
SPS | 'CUNNINGHAM 115KV' | 71 | -0.16067 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.14753 | -0.3082 | 31
SPS | 'CUNNINGHAM 115KV' | 110 | -0.16067 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.14753 | -0.3082 | 31
SPS | 'CARLSBAD 69KV' | 18 | -0.07637 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.14753 | -0.2239 | 42
SPS | 'CUNNINGHAM 230KV' | 110 | -0.07304 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.14753 | -0.22057 | 43
SPS | 'MADOX 115KV' | 75 | -0.16383 | SPS | 'PLANTX 230KV' | 189 | 0.00419 | -0.16802 | 56
SPS | 'MADOX 115KV' | 75 | -0.16383 | SPS | 'BLACKHAWK 115KV' | 220 | 0.00124 | -0.16507 | 57
SPS | 'MADOX 115KV' | 75 | -0.16383 | SPS | 'HARRINGTON 230KV' | 1066 | 0.00125 | -0.16508 | 57
SPS | 'MADOX 115KV' | 75 | -0.16383 | SPS | 'NICHOLS 115KV' | 82 | 0.0012 | -0.16503 | 57
SPS | 'MADOX 115KV' | 75 | -0.16383 | SPS | 'PLANTX 115KV' | 163.5259 | 0.0021 | -0.16593 | 57
SPS | 'MADOX 115KV' | 75 | -0.16383 | SPS | 'STEER WATER 115KV' | 79.9818 | 0.00116 | -0.16499 | 57
SPS | 'MADOX 115KV' | 75 | -0.16383 | SPS | 'TOLK 230KV' | 1027.989 | 0.00353 | -0.16736 | 57
SPS | 'MADOX 115KV' | 75 | -0.16383 | SPS | 'WILWIND 230KV' | 159.9636 | 0.00169 | -0.16552 | 57
SPS | 'CUNNINGHAM 115KV' | 71 | -0.16067 | SPS | 'PLANTX 115KV' | 163.5259 | 0.0021 | -0.16277 | 58
SPS | 'CUNNINGHAM 115KV' | 110 | -0.16067 | SPS | 'PLANTX 115KV' | 163.5259 | 0.0021 | -0.16277 | 58
SPS | 'CUNNINGHAM 115KV' | 71 | -0.16067 | SPS | 'PLANTX 230KV' | 189 | 0.00419 | -0.16486 | 58
SPS | 'CUNNINGHAM 115KV' | 110 | -0.16067 | SPS | 'PLANTX 230KV' | 189 | 0.00419 | -0.16486 | 58
SPS | 'CUNNINGHAM 115KV' | 71 | -0.16067 | SPS | 'TOLK 230KV' | 1027.989 | 0.00353 | -0.1642 | 58
SPS | 'CUNNINGHAM 115KV' | 110 | -0.16067 | SPS | 'TOLK 230KV' | 1027.989 | 0.00353 | -0.1642 | 58
SPS | 'CUNNINGHAM 115KV' | 71 | -0.16067 | SPS | 'WILWIND 230KV' | 159.9636 | 0.00169 | -0.16236 | 58
SPS | 'CUNNINGHAM 115KV' | 110 | -0.16067 | SPS | 'WILWIND 230KV' | 159.9636 | 0.00169 | -0.16236 | 58
SPS | 'CUNNINGHAM 115KV' | 71 | -0.16067 | SPS | 'BLACKHAWK 115KV' | 220 | 0.00124 | -0.16191 | 59
SPS | 'CUNNINGHAM 115KV' | 110 | -0.16067 | SPS | 'BLACKHAWK 115KV' | 220 | 0.00124 | -0.16191 | 59
SPS | 'CUNNINGHAM 115KV' | 71 | -0.16067 | SPS | 'HARRINGTON 230KV' | 1066 | 0.00125 | -0.16192 | 59
SPS | 'CUNNINGHAM 115KV' | 110 | -0.16067 | SPS | 'HARRINGTON 230KV' | 1066 | 0.00125 | -0.16192 | 59
SPS | 'CUNNINGHAM 115KV' | 71 | -0.16067 | SPS | 'NICHOLS 115KV' | 82 | 0.0012 | -0.16187 | 59
SPS | 'CUNNINGHAM 115KV' | 110 | -0.16067 | SPS | 'NICHOLS 115KV' | 82 | 0.0012 | -0.16187 | 59
SPS | 'CUNNINGHAM 115KV' | 71 | -0.16067 | SPS | 'STEER WATER 115KV' | 79.9818 | 0.00116 | -0.16183 | 59
SPS | 'CUNNINGHAM 115KV' | 110 | -0.16067 | SPS | 'STEER WATER 115KV' | 79.9818 | 0.00116 | -0.16183 | 59
SPS | 'MADOX 115KV' | 75 | -0.16383 | SPS | 'CAPROCK 115KV' | 79.9818 | -0.00285 | -0.16098 | 59
SPS | 'MADOX 115KV' | 75 | -0.16383 | SPS | 'JONES 230KV' | 486 | -0.00208 | -0.16175 | 59
SPS | 'MADOX 115KV' | 75 | -0.16383 | SPS | 'LP-BRND2 69KV' | 80 | -0.00242 | -0.16141 | 59
SPS | 'CUNNINGHAM 115KV' | 71 | -0.16067 | SPS | 'CAPROCK 115KV' | 79.9818 | -0.00285 | -0.15782 | 60
SPS | 'CUNNINGHAM 115KV' | 110 | -0.16067 | SPS | 'CAPROCK 115KV' | 79.9818 | -0.00285 | -0.15782 | 60
SPS | 'CUNNINGHAM 115KV' | 71 | -0.16067 | SPS | 'JONES 230KV' | 486 | -0.00208 | -0.15859 | 60
SPS | 'CUNNINGHAM 115KV' | 110 | -0.16067 | SPS | 'JONES 230KV' | 486 | -0.00208 | -0.15859 | 60
SPS | 'CUNNINGHAM 115KV' | 71 | -0.16067 | SPS | 'LP-BRND2 69KV' | 80 | -0.00242 | -0.15825 | 60
SPS | 'CUNNINGHAM 115KV' | 110 | -0.16067 | SPS | 'LP-BRND2 69KV' | 80 | -0.00242 | -0.15825 | 60
SPS | 'LP-BRND2 69KV' | 152 | -0.00242 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.14753 | -0.14995 | 63
SPS | 'MADOX 115KV' | 75 | -0.16383 | SPS | 'SAN JUAN 230KV' | 119.9727 | -0.019 | -0.14483 | 65
SPS | 'MOORE COUNTY 115KV' | 48 | 0.00131 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.14753 | -0.14622 | 65
SPS | 'NICHOLS 115KV' | 131 | 0.0012 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.14753 | -0.14633 | 65
SPS | 'NICHOLS 230KV' | 244 | 0.00124 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.14753 | -0.14629 | 65
SPS | 'PLANTX 115KV' | 89.4741 | 0.0021 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.14753 | -0.14543 | 65
SPS | 'RIVERVIEW 69KV' | 23 | 0.00123 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.14753 | -0.1463 | 65
SPS | 'TOLK 230KV' | 52.0113 | 0.00353 | SPS | 'MUSTG5 118.0 230KV' | 210 | 0.14753 | -0.144 | 66
SPS | 'CUNNINGHAM 115KV' | 71 | -0.16067 | SPS | 'SAN JUAN 230KV' | 119.9727 | -0.019 | -0.14167 | 67
SPS | 'CUNNINGHAM 115KV' | 110 | -0.16067 | SPS | 'SAN JUAN 230KV' | 119.9727 | -0.019 | -0.14167 | 67
SPS | 'MADOX 115KV' | 75 | -0.16383 | SPS | 'CUNNINGHAM 230KV' | 196 | -0.07304 | -0.09079 | 104
SPS | 'CUNNINGHAM 115KV' | 71 | -0.16067 | SPS | 'CUNNINGHAM 230KV' | 196 | -0.07304 | -0.08763 | 108
SPS | 'CUNNINGHAM 115KV' | 110 | -0.16067 | SPS | 'CUNNINGHAM 230KV' | 196 | -0.07304 | -0.08763 | 108
SPS | 'CUNNINGHAM 230KV' | 110 | -0.07304 | SPS | 'PLANTX 230KV' | 189 | 0.00419 | -0.07723 | 123
SPS | 'CUNNINGHAM 230KV' | 110 | -0.07304 | SPS | 'TOLK 230KV' | 1027.989 | 0.00353 | -0.07657 | 124
SPS | 'CUNNINGHAM 230KV' | 110 | -0.07304 | SPS | 'PLANTX 115KV' | 163.5259 | 0.0021 | -0.07514 | 126
SPS | 'CUNNINGHAM 230KV' | 110 | -0.07304 | SPS | 'WILWIND 230KV' | 159.9636 | 0.00169 | -0.07473 | 127
SPS | 'CUNNINGHAM 230KV' | 110 | -0.07304 | SPS | 'BLACKHAWK 115KV' | 220 | 0.00124 | -0.07428 | 128
SPS | 'CUNNINGHAM 230KV' | 110 | -0.07304 | SPS | 'HARRINGTON 230KV' | 1066 | 0.00125 | -0.07429 | 128
SPS | 'CUNNINGHAM 230KV' | 110 | -0.07304 | SPS | 'NICHOLS 115KV' | 82 | 0.0012 | -0.07424 | 128
SPS | 'CUNNINGHAM 230KV' | 110 | -0.07304 | SPS | 'STEER WATER 115KV' | 79.9818 | 0.00116 | -0.0742 | 128
SPS | 'CUNNINGHAM 230KV' | 110 | -0.07304 | SPS | 'JONES 230KV' | 486 | -0.00208 | -0.07096 | 134
SPS | 'CUNNINGHAM 230KV' | 110 | -0.07304 | SPS | 'CAPROCK 115KV' | 79.9818 | -0.00285 | -0.07019 | 135
SPS | 'CUNNINGHAM 230KV' | 110 | -0.07304 | SPS | 'SAN JUAN 230KV' | 119.9727 | -0.019 | -0.05404 | 175
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | Mustang-San Andr-Amerada Hess 115KV Displacement
Limiting Facility: | DENVER CITY INTERCHANGE S - MUSTANG STATION 115KV CKT 1
Direction: | To->From
Line Outage: | DENVER CITY INTERCHANGE N - MUSTANG STATION 115KV CKT 1
Flowgate: | 51962519681519605196611107SP
Date Redispatch Needed: | 6/1/07 - 10/1/07
Season Flowgate Identified: | 2007 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1090487 | 23.3145 | 23.3145
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
SPS | 'MADOX 115KV' | 75 | -0.16383 | SPS | 'MUSTG5 118.0 230KV' | 360 | 0.14753 | -0.31136 | 75
SPS | 'CUNNINGHAM 115KV' | 50.0098 | -0.16067 | SPS | 'MUSTG5 118.0 230KV' | 360 | 0.14753 | -0.3082 | 76
SPS | 'MADOX 115KV' | 75 | -0.16383 | SPS | 'PLANTX 230KV' | 189 | 0.00419 | -0.16802 | 139
SPS | 'MADOX 115KV' | 75 | -0.16383 | SPS | 'TOLK 230KV' | 1024.722 | 0.00353 | -0.16736 | 139
SPS | 'CUNNINGHAM 115KV' | 50.0098 | -0.16067 | SPS | 'PLANTX 230KV' | 189 | 0.00419 | -0.16486 | 141
SPS | 'MADOX 115KV' | 75 | -0.16383 | SPS | 'BLACKHAWK 115KV' | 220 | 0.00124 | -0.16507 | 141
SPS | 'MADOX 115KV' | 75 | -0.16383 | SPS | 'HARRINGTON 230KV' | 1066 | 0.00125 | -0.16508 | 141
SPS | 'MADOX 115KV' | 75 | -0.16383 | SPS | 'NICHOLS 115KV' | 147 | 0.0012 | -0.16503 | 141
SPS | 'MADOX 115KV' | 75 | -0.16383 | SPS | 'NICHOLS 230KV' | 147 | 0.00124 | -0.16507 | 141
SPS | 'MADOX 115KV' | 75 | -0.16383 | SPS | 'PLANTX 115KV' | 205 | 0.0021 | -0.16593 | 141
SPS | 'MADOX 115KV' | 75 | -0.16383 | SPS | 'STEER WATER 115KV' | 79.9818 | 0.00116 | -0.16499 | 141
SPS | 'MADOX 115KV' | 75 | -0.16383 | SPS | 'WILWIND 230KV' | 159.9636 | 0.00169 | -0.16552 | 141
SPS | 'CUNNINGHAM 115KV' | 50.0098 | -0.16067 | SPS | 'TOLK 230KV' | 1024.722 | 0.00353 | -0.1642 | 142
SPS | 'CUNNINGHAM 115KV' | 50.0098 | -0.16067 | SPS | 'PLANTX 115KV' | 205 | 0.0021 | -0.16277 | 143
SPS | 'CUNNINGHAM 115KV' | 50.0098 | -0.16067 | SPS | 'BLACKHAWK 115KV' | 220 | 0.00124 | -0.16191 | 144
SPS | 'CUNNINGHAM 115KV' | 50.0098 | -0.16067 | SPS | 'HARRINGTON 230KV' | 1066 | 0.00125 | -0.16192 | 144
SPS | 'CUNNINGHAM 115KV' | 50.0098 | -0.16067 | SPS | 'NICHOLS 115KV' | 147 | 0.0012 | -0.16187 | 144
SPS | 'CUNNINGHAM 115KV' | 50.0098 | -0.16067 | SPS | 'NICHOLS 230KV' | 147 | 0.00124 | -0.16191 | 144
SPS | 'CUNNINGHAM 115KV' | 50.0098 | -0.16067 | SPS | 'STEER WATER 115KV' | 79.9818 | 0.00116 | -0.16183 | 144
SPS | 'CUNNINGHAM 115KV' | 50.0098 | -0.16067 | SPS | 'WILWIND 230KV' | 159.9636 | 0.00169 | -0.16236 | 144
SPS | 'MADOX 115KV' | 75 | -0.16383 | SPS | 'JONES 230KV' | 486 | -0.00208 | -0.16175 | 144
SPS | 'MADOX 115KV' | 75 | -0.16383 | SPS | 'CAPROCK 115KV' | 79.9818 | -0.00285 | -0.16098 | 145
SPS | 'CUNNINGHAM 115KV' | 50.0098 | -0.16067 | SPS | 'JONES 230KV' | 486 | -0.00208 | -0.15859 | 147
SPS | 'CUNNINGHAM 115KV' | 50.0098 | -0.16067 | SPS | 'CAPROCK 115KV' | 79.9818 | -0.00285 | -0.15782 | 148
SPS | 'MADOX 115KV' | 75 | -0.16383 | SPS | 'SAN JUAN 230KV' | 119.9727 | -0.019 | -0.14483 | 161
SPS | 'TOLK 230KV' | 55.2779 | 0.00353 | SPS | 'MUSTG5 118.0 230KV' | 360 | 0.14753 | -0.144 | 162
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | Seven Rivers to Pecos to Potash Junction 230kV
Limiting Facility: | CARLSBAD PLANT - POTASH JUNCTION INTERCHANGE 115KV CKT 1
Direction: | To->From
Line Outage: | CUNNINGHAM STATION - EDDY COUNTY INTERCHANGE 230KV CKT 1
Flowgate: | 52310522521522095218512407SP
Date Redispatch Needed: | 6/1/07 - 10/1/07
Season Flowgate Identified: | 2007 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1090487 | 3.2643 | 3.2643
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
SPS | 'CARLSBAD 69KV' | 18 | -0.26531 | SPS | 'MUSTG5 118.0 230KV' | 360 | 0.0485 | -0.31381 | 10
SPS | 'CARLSBAD 69KV' | 18 | -0.26531 | SPS | 'BLACKHAWK 115KV' | 220 | -0.00367 | -0.26164 | 12
SPS | 'CARLSBAD 69KV' | 18 | -0.26531 | SPS | 'CZ 69KV' | 39 | -0.00335 | -0.26196 | 12
SPS | 'CARLSBAD 69KV' | 18 | -0.26531 | SPS | 'HARRINGTON 230KV' | 1066 | -0.0037 | -0.26161 | 12
SPS | 'CARLSBAD 69KV' | 18 | -0.26531 | SPS | 'HUBRCO2 69KV' | 11 | -0.00367 | -0.26164 | 12
SPS | 'CARLSBAD 69KV' | 18 | -0.26531 | SPS | 'JONES 230KV' | 486 | 0.01395 | -0.27926 | 12
SPS | 'CARLSBAD 69KV' | 18 | -0.26531 | SPS | 'LP-BRND2 69KV' | 80 | 0.01302 | -0.27833 | 12
SPS | 'CARLSBAD 69KV' | 18 | -0.26531 | SPS | 'MOORE COUNTY 115KV' | 48 | -0.00385 | -0.26146 | 12
SPS | 'CARLSBAD 69KV' | 18 | -0.26531 | SPS | 'NICHOLS 115KV' | 147 | -0.00362 | -0.26169 | 12
SPS | 'CARLSBAD 69KV' | 18 | -0.26531 | SPS | 'NICHOLS 230KV' | 147 | -0.00366 | -0.26165 | 12
SPS | 'CARLSBAD 69KV' | 18 | -0.26531 | SPS | 'SIDRCH 69KV' | 20 | -0.00367 | -0.26164 | 12
SPS | 'CARLSBAD 69KV' | 18 | -0.26531 | SPS | 'STEER WATER 115KV' | 8 | -0.00349 | -0.26182 | 12
SPS | 'CARLSBAD 69KV' | 18 | -0.26531 | SPS | 'PLANTX 115KV' | 205 | -0.00587 | -0.25944 | 13
SPS | 'CARLSBAD 69KV' | 18 | -0.26531 | SPS | 'PLANTX 230KV' | 189 | -0.00909 | -0.25622 | 13
SPS | 'CARLSBAD 69KV' | 18 | -0.26531 | SPS | 'TOLK 230KV' | 1018.154 | -0.01292 | -0.25239 | 13
SPS | 'CARLSBAD 69KV' | 18 | -0.26531 | SPS | 'WILWIND 230KV' | 16 | -0.00514 | -0.26017 | 13
SPS | 'CARLSBAD 69KV' | 18 | -0.26531 | SPS | 'CAPROCK 115KV' | 8 | -0.02602 | -0.23929 | 14
SPS | 'CARLSBAD 69KV' | 18 | -0.26531 | SPS | 'SAN JUAN 230KV' | 12 | -0.06421 | -0.2011 | 16
SPS | 'TUCUMCARI 115KV' | 15 | -0.02602 | SPS | 'MUSTG5 118.0 230KV' | 360 | 0.0485 | -0.07452 | 44
SPS | 'TOLK 230KV' | 61.8458 | -0.01292 | SPS | 'MUSTG5 118.0 230KV' | 360 | 0.0485 | -0.06142 | 53
SPS | 'PLANTX 115KV' | 48 | -0.00587 | SPS | 'MUSTG5 118.0 230KV' | 360 | 0.0485 | -0.05437 | 60
SPS | 'RIVERVIEW 69KV' | 23 | -0.00367 | SPS | 'MUSTG5 118.0 230KV' | 360 | 0.0485 | -0.05217 | 63
SPS | 'LP-BRND2 69KV' | 152 | 0.01302 | SPS | 'MUSTG5 118.0 230KV' | 360 | 0.0485 | -0.03548 | 92
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | WICHITA - RENO 345KV
Limiting Facility: | EXIDE JUNCTION - SUMMIT 115KV CKT 1
Direction: | To->From
Line Outage: | EAST MCPHERSON - SUMMIT 230KV CKT 1
Flowgate: | 57368573811568725687312206WP
Date Redispatch Needed: | 12/1/06 - 4/1/07
Season Flowgate Identified: | 2006 Winter Peak
Reservation | Relief Amount | Aggregate Relief Amount
1086655 | 1.5186 | 2.5877
1090964 | 0.77752 | 2.5877
1090965 | 0.29157 | 2.5877
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29594 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01746 | -0.3134 | 8
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29594 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02327 | -0.31921 | 8
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29594 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 130.0238 | 0.00966 | -0.3056 | 8
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29594 | WERE | 'CHANUTE 69KV' | 35.344 | 0.00148 | -0.29742 | 9
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29594 | WERE | 'CITY OF AUGUSTA 69KV' | 17.252 | 0.00019 | -0.29613 | 9
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29594 | WERE | 'CITY OF BURLINGTON 69KV' | 4.8 | 0.00281 | -0.29875 | 9
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29594 | WERE | 'CITY OF IOLA 69KV' | 13.978 | 0.00175 | -0.29769 | 9
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29594 | WERE | 'CITY OF MULVANE 69KV' | 3.694 | -0.00102 | -0.29492 | 9
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29594 | WERE | 'CITY OF WELLINGTON 69KV' | 24 | -0.00179 | -0.29415 | 9
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29594 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.00281 | -0.29875 | 9
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29594 | WERE | 'EVANS ENERGY CENTER 138KV' | 25.8875 | 2e-05 | -0.29596 | 9
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29594 | WERE | 'WACO 138KV' | 17.953 | -0.003 | -0.29294 | 9
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29594 | WERE | 'COLBY 115KV' | 6.2809 | -0.03582 | -0.26012 | 10
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.23852 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01746 | -0.25598 | 10
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.23852 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02327 | -0.26179 | 10
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.23852 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 130.0238 | 0.00966 | -0.24818 | 10
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.23841 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01746 | -0.25587 | 10
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.23841 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02327 | -0.26168 | 10
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.23841 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 130.0238 | 0.00966 | -0.24807 | 10
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.23852 | WERE | 'CHANUTE 69KV' | 35.344 | 0.00148 | -0.24 | 11
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.23852 | WERE | 'CITY OF AUGUSTA 69KV' | 17.252 | 0.00019 | -0.23871 | 11
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.23852 | WERE | 'CITY OF BURLINGTON 69KV' | 4.8 | 0.00281 | -0.24133 | 11
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.23852 | WERE | 'CITY OF IOLA 69KV' | 13.978 | 0.00175 | -0.24027 | 11
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.23852 | WERE | 'CITY OF MULVANE 69KV' | 3.694 | -0.00102 | -0.2375 | 11
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.23852 | WERE | 'CITY OF WELLINGTON 69KV' | 24 | -0.00179 | -0.23673 | 11
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.23852 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.00281 | -0.24133 | 11
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.23852 | WERE | 'EVANS ENERGY CENTER 138KV' | 25.8875 | 2e-05 | -0.23854 | 11
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.23852 | WERE | 'WACO 138KV' | 17.953 | -0.003 | -0.23552 | 11
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.23841 | WERE | 'CHANUTE 69KV' | 35.344 | 0.00148 | -0.23989 | 11
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.23841 | WERE | 'CITY OF AUGUSTA 69KV' | 17.252 | 0.00019 | -0.2386 | 11
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.23841 | WERE | 'CITY OF BURLINGTON 69KV' | 4.8 | 0.00281 | -0.24122 | 11
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.23841 | WERE | 'CITY OF IOLA 69KV' | 13.978 | 0.00175 | -0.24016 | 11
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.23841 | WERE | 'CITY OF MULVANE 69KV' | 3.694 | -0.00102 | -0.23739 | 11
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.23841 | WERE | 'CITY OF WELLINGTON 69KV' | 24 | -0.00179 | -0.23662 | 11
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.23841 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.00281 | -0.24122 | 11
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.23841 | WERE | 'EVANS ENERGY CENTER 138KV' | 25.8875 | 2e-05 | -0.23843 | 11
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.23841 | WERE | 'WACO 138KV' | 17.953 | -0.003 | -0.23541 | 11
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.23852 | WERE | 'COLBY 115KV' | 6.2809 | -0.03582 | -0.2027 | 13
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.23841 | WERE | 'COLBY 115KV' | 6.2809 | -0.03582 | -0.20259 | 13
WERE | 'PAWNEE 115KV' | 999 | -0.13502 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02327 | -0.15829 | 16
WERE | 'RICE 115KV' | 999 | -0.13502 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02327 | -0.15829 | 16
WERE | 'ST JOHN 115KV' | 7.5 | -0.13502 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02327 | -0.15829 | 16
WERE | 'PAWNEE 115KV' | 999 | -0.13502 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01746 | -0.15248 | 17
WERE | 'RICE 115KV' | 999 | -0.13502 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01746 | -0.15248 | 17
WERE | 'ST JOHN 115KV' | 7.5 | -0.13502 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01746 | -0.15248 | 17
WERE | 'PAWNEE 115KV' | 999 | -0.13502 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 130.0238 | 0.00966 | -0.14468 | 18
WERE | 'RICE 115KV' | 999 | -0.13502 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 130.0238 | 0.00966 | -0.14468 | 18
WERE | 'ST JOHN 115KV' | 7.5 | -0.13502 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 130.0238 | 0.00966 | -0.14468 | 18
WERE | 'PAWNEE 115KV' | 999 | -0.13502 | WERE | 'CHANUTE 69KV' | 35.344 | 0.00148 | -0.1365 | 19
WERE | 'PAWNEE 115KV' | 999 | -0.13502 | WERE | 'CITY OF AUGUSTA 69KV' | 17.252 | 0.00019 | -0.13521 | 19
WERE | 'PAWNEE 115KV' | 999 | -0.13502 | WERE | 'CITY OF IOLA 69KV' | 13.978 | 0.00175 | -0.13677 | 19
WERE | 'PAWNEE 115KV' | 999 | -0.13502 | WERE | 'CITY OF WELLINGTON 69KV' | 24 | -0.00179 | -0.13323 | 19
WERE | 'PAWNEE 115KV' | 999 | -0.13502 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.00281 | -0.13783 | 19
WERE | 'PAWNEE 115KV' | 999 | -0.13502 | WERE | 'EVANS ENERGY CENTER 138KV' | 25.8875 | 2e-05 | -0.13504 | 19
WERE | 'RICE 115KV' | 999 | -0.13502 | WERE | 'CHANUTE 69KV' | 35.344 | 0.00148 | -0.1365 | 19
WERE | 'RICE 115KV' | 999 | -0.13502 | WERE | 'CITY OF AUGUSTA 69KV' | 17.252 | 0.00019 | -0.13521 | 19
WERE | 'RICE 115KV' | 999 | -0.13502 | WERE | 'CITY OF IOLA 69KV' | 13.978 | 0.00175 | -0.13677 | 19
WERE | 'RICE 115KV' | 999 | -0.13502 | WERE | 'CITY OF WELLINGTON 69KV' | 24 | -0.00179 | -0.13323 | 19
WERE | 'RICE 115KV' | 999 | -0.13502 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.00281 | -0.13783 | 19
WERE | 'RICE 115KV' | 999 | -0.13502 | WERE | 'EVANS ENERGY CENTER 138KV' | 25.8875 | 2e-05 | -0.13504 | 19
WERE | 'ST JOHN 115KV' | 7.5 | -0.13502 | WERE | 'CHANUTE 69KV' | 35.344 | 0.00148 | -0.1365 | 19
WERE | 'ST JOHN 115KV' | 7.5 | -0.13502 | WERE | 'CITY OF AUGUSTA 69KV' | 17.252 | 0.00019 | -0.13521 | 19
WERE | 'ST JOHN 115KV' | 7.5 | -0.13502 | WERE | 'CITY OF IOLA 69KV' | 13.978 | 0.00175 | -0.13677 | 19
WERE | 'ST JOHN 115KV' | 7.5 | -0.13502 | WERE | 'CITY OF WELLINGTON 69KV' | 24 | -0.00179 | -0.13323 | 19
WERE | 'ST JOHN 115KV' | 7.5 | -0.13502 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.00281 | -0.13783 | 19
WERE | 'ST JOHN 115KV' | 7.5 | -0.13502 | WERE | 'EVANS ENERGY CENTER 138KV' | 25.8875 | 2e-05 | -0.13504 | 19
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.10743 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02327 | -0.1307 | 20
WERE | 'PAWNEE 115KV' | 999 | -0.13502 | WERE | 'WACO 138KV' | 17.953 | -0.003 | -0.13202 | 20
WERE | 'RICE 115KV' | 999 | -0.13502 | WERE | 'WACO 138KV' | 17.953 | -0.003 | -0.13202 | 20
WERE | 'ST JOHN 115KV' | 7.5 | -0.13502 | WERE | 'WACO 138KV' | 17.953 | -0.003 | -0.13202 | 20
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.10743 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01746 | -0.12489 | 21
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.10743 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 130.0238 | 0.00966 | -0.11709 | 22
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.10743 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.00281 | -0.11024 | 23
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.10743 | WERE | 'CHANUTE 69KV' | 35.344 | 0.00148 | -0.10891 | 24
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.10743 | WERE | 'CITY OF AUGUSTA 69KV' | 17.252 | 0.00019 | -0.10762 | 24
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.10743 | WERE | 'CITY OF IOLA 69KV' | 13.978 | 0.00175 | -0.10918 | 24
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.10743 | WERE | 'CITY OF WELLINGTON 69KV' | 24 | -0.00179 | -0.10564 | 24
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.10743 | WERE | 'EVANS ENERGY CENTER 138KV' | 25.8875 | 2e-05 | -0.10745 | 24
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.10743 | WERE | 'WACO 138KV' | 17.953 | -0.003 | -0.10443 | 25
WEPL | 'A. M. MULLERGREN GENERATOR 115KV' | 63 | -0.12041 | WEPL | 'GRAY COUNTY WIND FARM 115KV' | 73 | -0.07564 | -0.04477 | 58
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | WICHITA - RENO 345KV
Limiting Facility: | EXIDE JUNCTION - SUMMIT 115KV CKT 1
Direction: | To->From
Line Outage: | EAST MCPHERSON - SUMMIT 230KV CKT 1
Flowgate: | 57368573811568725687312207SH
Date Redispatch Needed: | 6/1 - 10/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 Summer Shoulder
Reservation | Relief Amount | Aggregate Relief Amount
1086655 | 2.9872 | 5.0267
1090817 | 0.72369 | 5.0267
1090964 | 0.98685 | 5.0267
1090965 | 0.32895 | 5.0267
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29562 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01718 | -0.3128 | 16
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29562 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02299 | -0.31861 | 16
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29562 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 230.2191 | 0.00919 | -0.30481 | 16
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29562 | WERE | 'CHANUTE 69KV' | 46.617 | 0.00149 | -0.29711 | 17
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29562 | WERE | 'CITY OF ERIE 69KV' | 23.258 | 0.00149 | -0.29711 | 17
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29562 | WERE | 'CITY OF IOLA 69KV' | 19.865 | 0.00174 | -0.29736 | 17
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29562 | WERE | 'CITY OF MULVANE 69KV' | 6.189 | -0.00086 | -0.29476 | 17
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29562 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.96 | 0.00282 | -0.29844 | 17
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29562 | WERE | 'EVANS ENERGY CENTER 138KV' | 305 | 0.00013 | -0.29575 | 17
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29562 | WERE | 'GILL ENERGY CENTER 138KV' | 77 | -0.00316 | -0.29246 | 17
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29562 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.0088 | -0.30442 | 17
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29562 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00844 | -0.30406 | 17
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29562 | WERE | 'WACO 138KV' | 17.947 | -0.00282 | -0.2928 | 17
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.23794 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02299 | -0.26093 | 19
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.23783 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02299 | -0.26082 | 19
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.23794 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01718 | -0.25512 | 20
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.23794 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.0088 | -0.24674 | 20
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.23794 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 230.2191 | 0.00919 | -0.24713 | 20
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.23794 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00844 | -0.24638 | 20
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.23783 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01718 | -0.25501 | 20
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.23783 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.0088 | -0.24663 | 20
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.23783 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 230.2191 | 0.00919 | -0.24702 | 20
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.23783 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00844 | -0.24627 | 20
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.23794 | WERE | 'CHANUTE 69KV' | 46.617 | 0.00149 | -0.23943 | 21
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.23794 | WERE | 'CITY OF ERIE 69KV' | 23.258 | 0.00149 | -0.23943 | 21
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.23794 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.96 | 0.00282 | -0.24076 | 21
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.23794 | WERE | 'EVANS ENERGY CENTER 138KV' | 305 | 0.00013 | -0.23807 | 21
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.23794 | WERE | 'GILL ENERGY CENTER 138KV' | 77 | -0.00316 | -0.23478 | 21
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.23794 | WERE | 'WACO 138KV' | 17.947 | -0.00282 | -0.23512 | 21
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.23783 | WERE | 'CHANUTE 69KV' | 46.617 | 0.00149 | -0.23932 | 21
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.23783 | WERE | 'CITY OF ERIE 69KV' | 23.258 | 0.00149 | -0.23932 | 21
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.23783 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.96 | 0.00282 | -0.24065 | 21
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.23783 | WERE | 'EVANS ENERGY CENTER 138KV' | 305 | 0.00013 | -0.23796 | 21
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.23783 | WERE | 'GILL ENERGY CENTER 138KV' | 77 | -0.00316 | -0.23467 | 21
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.23783 | WERE | 'WACO 138KV' | 17.947 | -0.00282 | -0.23501 | 21
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29562 | WERE | 'CLAY CENTER JUNCTION 115KV' | 11.825 | -0.09835 | -0.19727 | 25
WERE | 'PAWNEE 115KV' | 999 | -0.13182 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02299 | -0.15481 | 32
WERE | 'RICE 115KV' | 999 | -0.13182 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02299 | -0.15481 | 32
WERE | 'PAWNEE 115KV' | 999 | -0.13182 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01718 | -0.149 | 34
WERE | 'RICE 115KV' | 999 | -0.13182 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01718 | -0.149 | 34
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29562 | WERE | 'ABILENE ENERGY CENTER 115KV' | 18.2344 | -0.15727 | -0.13835 | 36
WERE | 'PAWNEE 115KV' | 999 | -0.13182 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.0088 | -0.14062 | 36
WERE | 'PAWNEE 115KV' | 999 | -0.13182 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 230.2191 | 0.00919 | -0.14101 | 36
WERE | 'PAWNEE 115KV' | 999 | -0.13182 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00844 | -0.14026 | 36
WERE | 'RICE 115KV' | 999 | -0.13182 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.0088 | -0.14062 | 36
WERE | 'RICE 115KV' | 999 | -0.13182 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 230.2191 | 0.00919 | -0.14101 | 36
WERE | 'RICE 115KV' | 999 | -0.13182 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00844 | -0.14026 | 36
WERE | 'PAWNEE 115KV' | 999 | -0.13182 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.96 | 0.00282 | -0.13464 | 37
WERE | 'RICE 115KV' | 999 | -0.13182 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.96 | 0.00282 | -0.13464 | 37
WERE | 'PAWNEE 115KV' | 999 | -0.13182 | WERE | 'CITY OF ERIE 69KV' | 23.258 | 0.00149 | -0.13331 | 38
WERE | 'PAWNEE 115KV' | 999 | -0.13182 | WERE | 'EVANS ENERGY CENTER 138KV' | 305 | 0.00013 | -0.13195 | 38
WERE | 'RICE 115KV' | 999 | -0.13182 | WERE | 'CITY OF ERIE 69KV' | 23.258 | 0.00149 | -0.13331 | 38
WERE | 'RICE 115KV' | 999 | -0.13182 | WERE | 'EVANS ENERGY CENTER 138KV' | 305 | 0.00013 | -0.13195 | 38
WERE | 'PAWNEE 115KV' | 999 | -0.13182 | WERE | 'GILL ENERGY CENTER 138KV' | 77 | -0.00316 | -0.12866 | 39
WERE | 'PAWNEE 115KV' | 999 | -0.13182 | WERE | 'WACO 138KV' | 17.947 | -0.00282 | -0.129 | 39
WERE | 'RICE 115KV' | 999 | -0.13182 | WERE | 'GILL ENERGY CENTER 138KV' | 77 | -0.00316 | -0.12866 | 39
WERE | 'RICE 115KV' | 999 | -0.13182 | WERE | 'WACO 138KV' | 17.947 | -0.00282 | -0.129 | 39
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29562 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 80 | -0.23794 | -0.05768 | 87
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | WICHITA - RENO 345KV
Limiting Facility: | NORTH AMERICAN PHILIPS - NORTH AMERICAN PHILIPS JUNCTION (SOUTH) 115KV CKT 1
Direction: | From->To
Line Outage: | EAST MCPHERSON - SUMMIT 230KV CKT 1
Flowgate: | 57372573741568725687312206WP
Date Redispatch Needed: | 12/1/06 - 4/1/07
Season Flowgate Identified: | 2006 Winter Peak
Reservation | Relief Amount | Aggregate Relief Amount
1090964 | 6.9107 | 8.8852
1090965 | 1.9745 | 8.8852
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.52229 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.03388 | -0.55617 | 16
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.52229 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.0352 | -0.55749 | 16
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.52229 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 130.0238 | 0.02211 | -0.5444 | 16
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.52229 | WERE | 'CHANUTE 69KV' | 35.344 | 0.00308 | -0.52537 | 17
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.52229 | WERE | 'CITY OF AUGUSTA 69KV' | 17.252 | 0.00096 | -0.52325 | 17
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.52229 | WERE | 'CITY OF IOLA 69KV' | 13.978 | 0.00357 | -0.52586 | 17
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.52229 | WERE | 'CITY OF WELLINGTON 69KV' | 24 | -0.00277 | -0.51952 | 17
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.52229 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.00573 | -0.52802 | 17
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.52229 | WERE | 'EVANS ENERGY CENTER 138KV' | 25.8875 | 0.00069 | -0.52298 | 17
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.52229 | WERE | 'WACO 138KV' | 17.953 | -0.00487 | -0.51742 | 17
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.42301 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.03388 | -0.45689 | 19
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.42301 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.0352 | -0.45821 | 19
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.42282 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.03388 | -0.4567 | 19
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.42282 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.0352 | -0.45802 | 19
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.42301 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 130.0238 | 0.02211 | -0.44512 | 20
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.42282 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 130.0238 | 0.02211 | -0.44493 | 20
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.42301 | WERE | 'CHANUTE 69KV' | 35.344 | 0.00308 | -0.42609 | 21
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.42301 | WERE | 'CITY OF AUGUSTA 69KV' | 17.252 | 0.00096 | -0.42397 | 21
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.42301 | WERE | 'CITY OF IOLA 69KV' | 13.978 | 0.00357 | -0.42658 | 21
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.42301 | WERE | 'CITY OF WELLINGTON 69KV' | 24 | -0.00277 | -0.42024 | 21
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.42301 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.00573 | -0.42874 | 21
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.42301 | WERE | 'EVANS ENERGY CENTER 138KV' | 25.8875 | 0.00069 | -0.4237 | 21
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.42301 | WERE | 'WACO 138KV' | 17.953 | -0.00487 | -0.41814 | 21
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.42282 | WERE | 'CHANUTE 69KV' | 35.344 | 0.00308 | -0.4259 | 21
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.42282 | WERE | 'CITY OF AUGUSTA 69KV' | 17.252 | 0.00096 | -0.42378 | 21
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.42282 | WERE | 'CITY OF IOLA 69KV' | 13.978 | 0.00357 | -0.42639 | 21
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.42282 | WERE | 'CITY OF WELLINGTON 69KV' | 24 | -0.00277 | -0.42005 | 21
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.42282 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.00573 | -0.42855 | 21
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.42282 | WERE | 'EVANS ENERGY CENTER 138KV' | 25.8875 | 0.00069 | -0.42351 | 21
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.42282 | WERE | 'WACO 138KV' | 17.953 | -0.00487 | -0.41795 | 21
WERE | 'PAWNEE 115KV' | 999 | -0.24493 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.03388 | -0.27881 | 32
WERE | 'PAWNEE 115KV' | 999 | -0.24493 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.0352 | -0.28013 | 32
WERE | 'RICE 115KV' | 999 | -0.24493 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.03388 | -0.27881 | 32
WERE | 'RICE 115KV' | 999 | -0.24493 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.0352 | -0.28013 | 32
WERE | 'PAWNEE 115KV' | 999 | -0.24493 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 130.0238 | 0.02211 | -0.26704 | 33
WERE | 'RICE 115KV' | 999 | -0.24493 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 130.0238 | 0.02211 | -0.26704 | 33
WERE | 'PAWNEE 115KV' | 999 | -0.24493 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.00573 | -0.25066 | 35
WERE | 'RICE 115KV' | 999 | -0.24493 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.00573 | -0.25066 | 35
WERE | 'PAWNEE 115KV' | 999 | -0.24493 | WERE | 'CITY OF AUGUSTA 69KV' | 17.252 | 0.00096 | -0.24589 | 36
WERE | 'PAWNEE 115KV' | 999 | -0.24493 | WERE | 'EVANS ENERGY CENTER 138KV' | 25.8875 | 0.00069 | -0.24562 | 36
WERE | 'RICE 115KV' | 999 | -0.24493 | WERE | 'CITY OF AUGUSTA 69KV' | 17.252 | 0.00096 | -0.24589 | 36
WERE | 'RICE 115KV' | 999 | -0.24493 | WERE | 'EVANS ENERGY CENTER 138KV' | 25.8875 | 0.00069 | -0.24562 | 36
WERE | 'PAWNEE 115KV' | 999 | -0.24493 | WERE | 'CITY OF WELLINGTON 69KV' | 24 | -0.00277 | -0.24216 | 37
WERE | 'PAWNEE 115KV' | 999 | -0.24493 | WERE | 'WACO 138KV' | 17.953 | -0.00487 | -0.24006 | 37
WERE | 'RICE 115KV' | 999 | -0.24493 | WERE | 'CITY OF WELLINGTON 69KV' | 24 | -0.00277 | -0.24216 | 37
WERE | 'RICE 115KV' | 999 | -0.24493 | WERE | 'WACO 138KV' | 17.953 | -0.00487 | -0.24006 | 37
WEPL | 'A. M. MULLERGREN GENERATOR 115KV' | 63 | -0.22151 | WEPL | 'GRAY COUNTY WIND FARM 115KV' | 73 | -0.14083 | -0.08068 | 110
WERE | 'KNOLL 3 115 115KV' | 75 | -0.04003 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.0352 | -0.07523 | 118
WERE | 'KNOLL 3 115 115KV' | 75 | -0.04003 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.03388 | -0.07391 | 120
WERE | 'KNOLL 3 115 115KV' | 75 | -0.04003 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 130.0238 | 0.02211 | -0.06214 | 143
WERE | 'GILL ENERGY CENTER 138KV' | 218 | -0.0055 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.0352 | -0.0407 | 218
WERE | 'GILL ENERGY CENTER 138KV' | 218 | -0.0055 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.03388 | -0.03938 | 226
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.00393 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.0352 | -0.03913 | 227
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.00393 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.03388 | -0.03781 | 235
WERE | 'EVANS ENERGY CENTER 138KV' | 767.1125 | 0.00069 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.0352 | -0.03451 | 257
WERE | 'EVANS ENERGY CENTER 138KV' | 767.1125 | 0.00069 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.03388 | -0.03319 | 268
WERE | 'LATHAM1234.0 345KV' | 150 | 0.00276 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.0352 | -0.03244 | 274
WERE | 'LATHAM1234.0 345KV' | 150 | 0.00276 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.03388 | -0.03112 | 286
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | WICHITA - RENO 345KV
Limiting Facility: | NORTH AMERICAN PHILIPS - NORTH AMERICAN PHILIPS JUNCTION (SOUTH) 115KV CKT 1
Direction: | From->To
Line Outage: | EAST MCPHERSON - SUMMIT 230KV CKT 1
Flowgate: | 57372573741568725687312207FA
Date Redispatch Needed: | Starting 2007 10/1 - 12/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 Fall Peak
Reservation | Relief Amount | Aggregate Relief Amount
1090817 | 1.884 | 5.2752
1090964 | 2.6376 | 5.2752
1090965 | 0.7536 | 5.2752
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50621 | WERE | 'CHANUTE 69KV' | 56.296 | 0.00259 | -0.5088 | 10
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50621 | WERE | 'CITY OF AUGUSTA 69KV' | 19.636 | 0.00123 | -0.50744 | 10
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50621 | WERE | 'CITY OF BURLINGTON 69KV' | 4.8 | 0.00472 | -0.51093 | 10
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50621 | WERE | 'CITY OF IOLA 69KV' | 24.256 | 0.00297 | -0.50918 | 10
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50621 | WERE | 'CITY OF MULVANE 69KV' | 4.891 | -0.00107 | -0.50514 | 10
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50621 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00235 | -0.50386 | 10
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50621 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.96 | 0.00472 | -0.51093 | 10
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50621 | WERE | 'EVANS ENERGY CENTER 138KV' | 187.8892 | 0.0005 | -0.50671 | 10
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50621 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.02831 | -0.53452 | 10
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50621 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02952 | -0.53573 | 10
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50621 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 230.3248 | 0.01814 | -0.52435 | 10
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50621 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.01953 | -0.52574 | 10
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50621 | WERE | 'WACO 138KV' | 17.946 | -0.00425 | -0.50196 | 11
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50621 | WERE | 'COLBY 115KV' | 6.3622 | -0.07624 | -0.42997 | 12
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 343 | -0.40086 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.02831 | -0.42917 | 12
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 343 | -0.40086 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02952 | -0.43038 | 12
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40067 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.02831 | -0.42898 | 12
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40067 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02952 | -0.43019 | 12
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 343 | -0.40086 | WERE | 'CHANUTE 69KV' | 56.296 | 0.00259 | -0.40345 | 13
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 343 | -0.40086 | WERE | 'CITY OF AUGUSTA 69KV' | 19.636 | 0.00123 | -0.40209 | 13
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 343 | -0.40086 | WERE | 'CITY OF BURLINGTON 69KV' | 4.8 | 0.00472 | -0.40558 | 13
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 343 | -0.40086 | WERE | 'CITY OF IOLA 69KV' | 24.256 | 0.00297 | -0.40383 | 13
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 343 | -0.40086 | WERE | 'CITY OF MULVANE 69KV' | 4.891 | -0.00107 | -0.39979 | 13
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 343 | -0.40086 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00235 | -0.39851 | 13
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 343 | -0.40086 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.96 | 0.00472 | -0.40558 | 13
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 343 | -0.40086 | WERE | 'EVANS ENERGY CENTER 138KV' | 187.8892 | 0.0005 | -0.40136 | 13
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 343 | -0.40086 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 230.3248 | 0.01814 | -0.419 | 13
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 343 | -0.40086 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.01953 | -0.42039 | 13
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 343 | -0.40086 | WERE | 'WACO 138KV' | 17.946 | -0.00425 | -0.39661 | 13
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40067 | WERE | 'CHANUTE 69KV' | 56.296 | 0.00259 | -0.40326 | 13
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40067 | WERE | 'CITY OF AUGUSTA 69KV' | 19.636 | 0.00123 | -0.4019 | 13
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40067 | WERE | 'CITY OF BURLINGTON 69KV' | 4.8 | 0.00472 | -0.40539 | 13
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40067 | WERE | 'CITY OF IOLA 69KV' | 24.256 | 0.00297 | -0.40364 | 13
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40067 | WERE | 'CITY OF MULVANE 69KV' | 4.891 | -0.00107 | -0.3996 | 13
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40067 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00235 | -0.39832 | 13
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40067 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.96 | 0.00472 | -0.40539 | 13
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40067 | WERE | 'EVANS ENERGY CENTER 138KV' | 187.8892 | 0.0005 | -0.40117 | 13
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40067 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 230.3248 | 0.01814 | -0.41881 | 13
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40067 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.01953 | -0.4202 | 13
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40067 | WERE | 'WACO 138KV' | 17.946 | -0.00425 | -0.39642 | 13
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 343 | -0.40086 | WERE | 'COLBY 115KV' | 6.3622 | -0.07624 | -0.32462 | 16
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40067 | WERE | 'COLBY 115KV' | 6.3622 | -0.07624 | -0.32443 | 16
WERE | 'PAWNEE 115KV' | 999 | -0.21561 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.02831 | -0.24392 | 22
WERE | 'PAWNEE 115KV' | 999 | -0.21561 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02952 | -0.24513 | 22
WERE | 'PAWNEE 115KV' | 999 | -0.21561 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.01953 | -0.23514 | 22
WERE | 'RICE 115KV' | 999 | -0.21561 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.02831 | -0.24392 | 22
WERE | 'RICE 115KV' | 999 | -0.21561 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02952 | -0.24513 | 22
WERE | 'RICE 115KV' | 999 | -0.21561 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.01953 | -0.23514 | 22
WERE | 'ST JOHN 115KV' | 7.5 | -0.21561 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.02831 | -0.24392 | 22
WERE | 'ST JOHN 115KV' | 7.5 | -0.21561 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02952 | -0.24513 | 22
WERE | 'ST JOHN 115KV' | 7.5 | -0.21561 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.01953 | -0.23514 | 22
WERE | 'PAWNEE 115KV' | 999 | -0.21561 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 230.3248 | 0.01814 | -0.23375 | 23
WERE | 'RICE 115KV' | 999 | -0.21561 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 230.3248 | 0.01814 | -0.23375 | 23
WERE | 'PAWNEE 115KV' | 999 | -0.21561 | WERE | 'CHANUTE 69KV' | 56.296 | 0.00259 | -0.2182 | 24
WERE | 'PAWNEE 115KV' | 999 | -0.21561 | WERE | 'CITY OF AUGUSTA 69KV' | 19.636 | 0.00123 | -0.21684 | 24
WERE | 'PAWNEE 115KV' | 999 | -0.21561 | WERE | 'CITY OF IOLA 69KV' | 24.256 | 0.00297 | -0.21858 | 24
WERE | 'PAWNEE 115KV' | 999 | -0.21561 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.96 | 0.00472 | -0.22033 | 24
WERE | 'PAWNEE 115KV' | 999 | -0.21561 | WERE | 'EVANS ENERGY CENTER 138KV' | 187.8892 | 0.0005 | -0.21611 | 24
WERE | 'RICE 115KV' | 999 | -0.21561 | WERE | 'CHANUTE 69KV' | 56.296 | 0.00259 | -0.2182 | 24
WERE | 'RICE 115KV' | 999 | -0.21561 | WERE | 'CITY OF AUGUSTA 69KV' | 19.636 | 0.00123 | -0.21684 | 24
WERE | 'RICE 115KV' | 999 | -0.21561 | WERE | 'CITY OF IOLA 69KV' | 24.256 | 0.00297 | -0.21858 | 24
WERE | 'RICE 115KV' | 999 | -0.21561 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.96 | 0.00472 | -0.22033 | 24
WERE | 'RICE 115KV' | 999 | -0.21561 | WERE | 'EVANS ENERGY CENTER 138KV' | 187.8892 | 0.0005 | -0.21611 | 24
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.17964 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.02831 | -0.20795 | 25
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.17964 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02952 | -0.20916 | 25
WERE | 'PAWNEE 115KV' | 999 | -0.21561 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00235 | -0.21326 | 25
WERE | 'PAWNEE 115KV' | 999 | -0.21561 | WERE | 'WACO 138KV' | 17.946 | -0.00425 | -0.21136 | 25
WERE | 'RICE 115KV' | 999 | -0.21561 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00235 | -0.21326 | 25
WERE | 'RICE 115KV' | 999 | -0.21561 | WERE | 'WACO 138KV' | 17.946 | -0.00425 | -0.21136 | 25
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.17964 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.01953 | -0.19917 | 26
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.17964 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 230.3248 | 0.01814 | -0.19778 | 27
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.17964 | WERE | 'CHANUTE 69KV' | 56.296 | 0.00259 | -0.18223 | 29
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.17964 | WERE | 'CITY OF AUGUSTA 69KV' | 19.636 | 0.00123 | -0.18087 | 29
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.17964 | WERE | 'CITY OF IOLA 69KV' | 24.256 | 0.00297 | -0.18261 | 29
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.17964 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.96 | 0.00472 | -0.18436 | 29
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.17964 | WERE | 'EVANS ENERGY CENTER 138KV' | 187.8892 | 0.0005 | -0.18014 | 29
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.17964 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00235 | -0.17729 | 30
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.17964 | WERE | 'WACO 138KV' | 17.946 | -0.00425 | -0.17539 | 30
WERE | 'KNOLL 3 115 115KV' | 75 | -0.09268 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02952 | -0.1222 | 43
WERE | 'KNOLL 3 115 115KV' | 75 | -0.09268 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.02831 | -0.12099 | 44
WERE | 'KNOLL 3 115 115KV' | 75 | -0.09268 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.01953 | -0.11221 | 47
WERE | 'KNOLL 3 115 115KV' | 75 | -0.09268 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 230.3248 | 0.01814 | -0.11082 | 48
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50621 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 40 | -0.40086 | -0.10535 | 50
WERE | 'KNOLL 3 115 115KV' | 75 | -0.09268 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.96 | 0.00472 | -0.0974 | 54
WERE | 'KNOLL 3 115 115KV' | 75 | -0.09268 | WERE | 'CITY OF AUGUSTA 69KV' | 19.636 | 0.00123 | -0.09391 | 56
WERE | 'KNOLL 3 115 115KV' | 75 | -0.09268 | WERE | 'EVANS ENERGY CENTER 138KV' | 187.8892 | 0.0005 | -0.09318 | 57
WEPL | 'A. M. MULLERGREN GENERATOR 115KV' | 63 | -0.17717 | WEPL | 'GRAY COUNTY WIND FARM 115KV' | 60 | -0.11561 | -0.06156 | 86
WERE | 'GILL ENERGY CENTER 138KV' | 218 | -0.00479 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02952 | -0.03431 | 154
WERE | 'GILL ENERGY CENTER 138KV' | 218 | -0.00479 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.02831 | -0.0331 | 159
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.00342 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02952 | -0.03294 | 160
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.00342 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.02831 | -0.03173 | 166
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | WICHITA - RENO 345KV
Limiting Facility: | NORTH AMERICAN PHILIPS - NORTH AMERICAN PHILIPS JUNCTION (SOUTH) 115KV CKT 1
Direction: | From->To
Line Outage: | EAST MCPHERSON - SUMMIT 230KV CKT 1
Flowgate: | 57372573741568725687312207SH
Date Redispatch Needed: | 6/1 - 10/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 Summer Shoulder
Reservation | Relief Amount | Aggregate Relief Amount
1090817 | 2.8547 | 8.0883
1090964 | 4.0441 | 8.0883
1090965 | 1.1894 | 8.0883
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.52215 | WERE | 'ABILENE ENERGY CENTER 115KV' | 18.2344 | 0.12191 | -0.64406 | 13
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.52215 | WERE | 'CLAY CENTER JUNCTION 115KV' | 11.825 | 0.09097 | -0.61312 | 13
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.52215 | WERE | 'CHANUTE 69KV' | 46.617 | 0.0031 | -0.52525 | 15
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.52215 | WERE | 'CITY OF ERIE 69KV' | 23.258 | 0.0031 | -0.52525 | 15
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.52215 | WERE | 'CITY OF IOLA 69KV' | 19.865 | 0.00354 | -0.52569 | 15
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.52215 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.96 | 0.00569 | -0.52784 | 15
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.52215 | WERE | 'EVANS ENERGY CENTER 138KV' | 305 | 0.00086 | -0.52301 | 15
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.52215 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.033 | -0.55515 | 15
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.52215 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.03435 | -0.5565 | 15
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.52215 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.02019 | -0.54234 | 15
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.52215 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 230.2191 | 0.02119 | -0.54334 | 15
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.52215 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.0228 | -0.54495 | 15
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.42248 | WERE | 'ABILENE ENERGY CENTER 115KV' | 18.2344 | 0.12191 | -0.54439 | 15
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.42229 | WERE | 'ABILENE ENERGY CENTER 115KV' | 18.2344 | 0.12191 | -0.5442 | 15
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.52215 | WERE | 'CITY OF MULVANE 69KV' | 6.189 | -0.00096 | -0.52119 | 16
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.52215 | WERE | 'CITY OF WELLINGTON 69KV' | 31.07 | -0.00251 | -0.51964 | 16
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.52215 | WERE | 'GILL ENERGY CENTER 138KV' | 77 | -0.00519 | -0.51696 | 16
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.52215 | WERE | 'WACO 138KV' | 17.947 | -0.00458 | -0.51757 | 16
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.42248 | WERE | 'CLAY CENTER JUNCTION 115KV' | 11.825 | 0.09097 | -0.51345 | 16
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.42229 | WERE | 'CLAY CENTER JUNCTION 115KV' | 11.825 | 0.09097 | -0.51326 | 16
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.42248 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.033 | -0.45548 | 18
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.42248 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.03435 | -0.45683 | 18
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.42248 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.02019 | -0.44267 | 18
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.42248 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 230.2191 | 0.02119 | -0.44367 | 18
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.42248 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.0228 | -0.44528 | 18
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.42229 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.033 | -0.45529 | 18
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.42229 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.03435 | -0.45664 | 18
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.42229 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.02019 | -0.44248 | 18
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.42229 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 230.2191 | 0.02119 | -0.44348 | 18
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.42229 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.0228 | -0.44509 | 18
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.42248 | WERE | 'CHANUTE 69KV' | 46.617 | 0.0031 | -0.42558 | 19
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.42248 | WERE | 'CITY OF ERIE 69KV' | 23.258 | 0.0031 | -0.42558 | 19
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.42248 | WERE | 'CITY OF IOLA 69KV' | 19.865 | 0.00354 | -0.42602 | 19
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.42248 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.96 | 0.00569 | -0.42817 | 19
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.42248 | WERE | 'EVANS ENERGY CENTER 138KV' | 305 | 0.00086 | -0.42334 | 19
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.42248 | WERE | 'GILL ENERGY CENTER 138KV' | 77 | -0.00519 | -0.41729 | 19
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.42248 | WERE | 'WACO 138KV' | 17.947 | -0.00458 | -0.4179 | 19
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.42229 | WERE | 'CHANUTE 69KV' | 46.617 | 0.0031 | -0.42539 | 19
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.42229 | WERE | 'CITY OF ERIE 69KV' | 23.258 | 0.0031 | -0.42539 | 19
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.42229 | WERE | 'CITY OF IOLA 69KV' | 19.865 | 0.00354 | -0.42583 | 19
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.42229 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.96 | 0.00569 | -0.42798 | 19
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.42229 | WERE | 'EVANS ENERGY CENTER 138KV' | 305 | 0.00086 | -0.42315 | 19
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.42229 | WERE | 'GILL ENERGY CENTER 138KV' | 77 | -0.00519 | -0.4171 | 19
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.42229 | WERE | 'WACO 138KV' | 17.947 | -0.00458 | -0.41771 | 19
WERE | 'PAWNEE 115KV' | 999 | -0.24056 | WERE | 'ABILENE ENERGY CENTER 115KV' | 18.2344 | 0.12191 | -0.36247 | 22
WERE | 'RICE 115KV' | 999 | -0.24056 | WERE | 'ABILENE ENERGY CENTER 115KV' | 18.2344 | 0.12191 | -0.36247 | 22
WERE | 'ST JOHN 115KV' | 7.5 | -0.24056 | WERE | 'ABILENE ENERGY CENTER 115KV' | 18.2344 | 0.12191 | -0.36247 | 22
WERE | 'PAWNEE 115KV' | 999 | -0.24056 | WERE | 'CLAY CENTER JUNCTION 115KV' | 11.825 | 0.09097 | -0.33153 | 24
WERE | 'RICE 115KV' | 999 | -0.24056 | WERE | 'CLAY CENTER JUNCTION 115KV' | 11.825 | 0.09097 | -0.33153 | 24
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.20969 | WERE | 'CLAY CENTER JUNCTION 115KV' | 11.825 | 0.09097 | -0.30066 | 27
WERE | 'PAWNEE 115KV' | 999 | -0.24056 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.03435 | -0.27491 | 29
WERE | 'RICE 115KV' | 999 | -0.24056 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.03435 | -0.27491 | 29
WERE | 'PAWNEE 115KV' | 999 | -0.24056 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.033 | -0.27356 | 30
WERE | 'RICE 115KV' | 999 | -0.24056 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.033 | -0.27356 | 30
WERE | 'PAWNEE 115KV' | 999 | -0.24056 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.02019 | -0.26075 | 31
WERE | 'PAWNEE 115KV' | 999 | -0.24056 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 230.2191 | 0.02119 | -0.26175 | 31
WERE | 'PAWNEE 115KV' | 999 | -0.24056 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.0228 | -0.26336 | 31
WERE | 'RICE 115KV' | 999 | -0.24056 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.02019 | -0.26075 | 31
WERE | 'RICE 115KV' | 999 | -0.24056 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 230.2191 | 0.02119 | -0.26175 | 31
WERE | 'RICE 115KV' | 999 | -0.24056 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.0228 | -0.26336 | 31
WERE | 'PAWNEE 115KV' | 999 | -0.24056 | WERE | 'CITY OF ERIE 69KV' | 23.258 | 0.0031 | -0.24366 | 33
WERE | 'PAWNEE 115KV' | 999 | -0.24056 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.96 | 0.00569 | -0.24625 | 33
WERE | 'RICE 115KV' | 999 | -0.24056 | WERE | 'CITY OF ERIE 69KV' | 23.258 | 0.0031 | -0.24366 | 33
WERE | 'RICE 115KV' | 999 | -0.24056 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.96 | 0.00569 | -0.24625 | 33
WERE | 'PAWNEE 115KV' | 999 | -0.24056 | WERE | 'EVANS ENERGY CENTER 138KV' | 305 | 0.00086 | -0.24142 | 34
WERE | 'PAWNEE 115KV' | 999 | -0.24056 | WERE | 'GILL ENERGY CENTER 138KV' | 77 | -0.00519 | -0.23537 | 34
WERE | 'PAWNEE 115KV' | 999 | -0.24056 | WERE | 'WACO 138KV' | 17.947 | -0.00458 | -0.23598 | 34
WERE | 'RICE 115KV' | 999 | -0.24056 | WERE | 'EVANS ENERGY CENTER 138KV' | 305 | 0.00086 | -0.24142 | 34
WERE | 'RICE 115KV' | 999 | -0.24056 | WERE | 'GILL ENERGY CENTER 138KV' | 77 | -0.00519 | -0.23537 | 34
WERE | 'RICE 115KV' | 999 | -0.24056 | WERE | 'WACO 138KV' | 17.947 | -0.00458 | -0.23598 | 34
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.52215 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 80 | -0.42248 | -0.09967 | 81
WERE | 'KNOLL 3 115 115KV' | 75 | -0.04377 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.03435 | -0.07812 | 104
WERE | 'KNOLL 3 115 115KV' | 75 | -0.04377 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.033 | -0.07677 | 105
WERE | 'KNOLL 3 115 115KV' | 75 | -0.04377 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.0228 | -0.06657 | 122
WERE | 'KNOLL 3 115 115KV' | 75 | -0.04377 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 230.2191 | 0.02119 | -0.06496 | 125
WERE | 'KNOLL 3 115 115KV' | 75 | -0.04377 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.02019 | -0.06396 | 126
WERE | 'KNOLL 3 115 115KV' | 75 | -0.04377 | WERE | 'EVANS ENERGY CENTER 138KV' | 305 | 0.00086 | -0.04463 | 181
WERE | 'GILL ENERGY CENTER 138KV' | 118 | -0.00519 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.03435 | -0.03954 | 205
WERE | 'KNOLL 3 115 115KV' | 75 | -0.04377 | WERE | 'GILL ENERGY CENTER 138KV' | 77 | -0.00519 | -0.03858 | 210
WERE | 'GILL ENERGY CENTER 138KV' | 118 | -0.00519 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.033 | -0.03819 | 212
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.00364 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.03435 | -0.03799 | 213
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.00364 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.033 | -0.03664 | 221
WERE | 'EVANS ENERGY CENTER 138KV' | 488 | 0.00086 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.03435 | -0.03349 | 242
WERE | 'EVANS ENERGY CENTER 138KV' | 488 | 0.00086 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.033 | -0.03214 | 252
WERE | 'LATHAM1234.0 345KV' | 150 | 0.00285 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.03435 | -0.0315 | 257
WERE | 'LATHAM1234.0 345KV' | 150 | 0.00285 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.033 | -0.03015 | 268
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | WICHITA - RENO 345KV
Limiting Facility: | NORTH AMERICAN PHILIPS - NORTH AMERICAN PHILIPS JUNCTION (SOUTH) 115KV CKT 1
Direction: | From->To
Line Outage: | EAST MCPHERSON - SUMMIT 230KV CKT 1
Flowgate: | 57372573741568725687312207WP
Date Redispatch Needed: | 12/1/07 - 4/1/08
Season Flowgate Identified: | 2007 Winter Peak
Reservation | Relief Amount | Aggregate Relief Amount
1090817 | 5.0297 | 14.0833
1090964 | 7.0417 | 14.0833
1090965 | 2.0119 | 14.0833
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50615 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.02836 | -0.53451 | 26
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50615 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02957 | -0.53572 | 26
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50615 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 169.36 | 0.01819 | -0.52434 | 27
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50615 | WERE | 'CHANUTE 69KV' | 34.818 | 0.00263 | -0.50878 | 28
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50615 | WERE | 'CITY OF AUGUSTA 69KV' | 14.628 | 0.00127 | -0.50742 | 28
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50615 | WERE | 'CITY OF IOLA 69KV' | 14.565 | 0.00301 | -0.50916 | 28
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50615 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00231 | -0.50384 | 28
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50615 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.95 | 0.00476 | -0.51091 | 28
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50615 | WERE | 'EVANS ENERGY CENTER 138KV' | 55 | 0.00054 | -0.50669 | 28
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50615 | WERE | 'WACO 138KV' | 17.93 | -0.00421 | -0.50194 | 28
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.40081 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.02836 | -0.42917 | 33
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.40081 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02957 | -0.43038 | 33
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40061 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.02836 | -0.42897 | 33
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40061 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02957 | -0.43018 | 33
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.40081 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 169.36 | 0.01819 | -0.419 | 34
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40061 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 169.36 | 0.01819 | -0.4188 | 34
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.40081 | WERE | 'CITY OF AUGUSTA 69KV' | 14.628 | 0.00127 | -0.40208 | 35
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.40081 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00231 | -0.3985 | 35
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.40081 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.95 | 0.00476 | -0.40557 | 35
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.40081 | WERE | 'EVANS ENERGY CENTER 138KV' | 55 | 0.00054 | -0.40135 | 35
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40061 | WERE | 'CITY OF AUGUSTA 69KV' | 14.628 | 0.00127 | -0.40188 | 35
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40061 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00231 | -0.3983 | 35
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40061 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.95 | 0.00476 | -0.40537 | 35
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40061 | WERE | 'EVANS ENERGY CENTER 138KV' | 55 | 0.00054 | -0.40115 | 35
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.40081 | WERE | 'WACO 138KV' | 17.93 | -0.00421 | -0.3966 | 36
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40061 | WERE | 'WACO 138KV' | 17.93 | -0.00421 | -0.3964 | 36
WERE | 'PAWNEE 115KV' | 999 | -0.21556 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02957 | -0.24513 | 57
WERE | 'RICE 115KV' | 999 | -0.21556 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02957 | -0.24513 | 57
WERE | 'PAWNEE 115KV' | 999 | -0.21556 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.02836 | -0.24392 | 58
WERE | 'RICE 115KV' | 999 | -0.21556 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.02836 | -0.24392 | 58
WERE | 'PAWNEE 115KV' | 999 | -0.21556 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 169.36 | 0.01819 | -0.23375 | 60
WERE | 'RICE 115KV' | 999 | -0.21556 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 169.36 | 0.01819 | -0.23375 | 60
WERE | 'PAWNEE 115KV' | 999 | -0.21556 | WERE | 'EVANS ENERGY CENTER 138KV' | 55 | 0.00054 | -0.2161 | 65
WERE | 'RICE 115KV' | 999 | -0.21556 | WERE | 'EVANS ENERGY CENTER 138KV' | 55 | 0.00054 | -0.2161 | 65
WERE | 'KNOLL 3 115 115KV' | 75 | -0.09262 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02957 | -0.12219 | 115
WERE | 'KNOLL 3 115 115KV' | 75 | -0.09262 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.02836 | -0.12098 | 116
WERE | 'KNOLL 3 115 115KV' | 75 | -0.09262 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 169.36 | 0.01819 | -0.11081 | 127
WERE | 'KNOLL 3 115 115KV' | 75 | -0.09262 | WERE | 'EVANS ENERGY CENTER 138KV' | 55 | 0.00054 | -0.09316 | 151
WERE | 'GILL ENERGY CENTER 138KV' | 218 | -0.00475 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02957 | -0.03432 | 410
WERE | 'GILL ENERGY CENTER 138KV' | 218 | -0.00475 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.02836 | -0.03311 | 425
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | WICHITA - RENO 345KV
Limiting Facility: | NORTH AMERICAN PHILIPS - NORTH AMERICAN PHILIPS JUNCTION (SOUTH) 115KV CKT 1
Direction: | From->To
Line Outage: | EAST MCPHERSON - SUMMIT 230KV CKT 1
Flowgate: | 57372573741568725687314208WP
Date Redispatch Needed: | Starting 2008 12/1 - 4/1 Until EOC
Season Flowgate Identified: | 2008 Winter Peak
Reservation | Relief Amount | Aggregate Relief Amount
1090817 | 0.75208 | 4.4485
1090829 | 0.56406 | 4.4485
1090917 | 0.35776 | 4.4485
1090919 | 0.08944 | 4.4485
1090920 | 0.62608 | 4.4485
1090921 | 0.17888 | 4.4485
1090964 | 1.1281 | 4.4485
1090965 | 0.37604 | 4.4485
1091057 | 0.37604 | 4.4485
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50615 | WERE | 'CLAY CENTER JUNCTION 115KV' | 6.7 | 0.08529 | -0.59144 | 7.5215
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50615 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.02825 | -0.5344 | 8.3243
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50615 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02949 | -0.53564 | 8.305
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50615 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 193.727 | 0.01813 | -0.52428 | 8.485
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50615 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.01951 | -0.52566 | 8.4627
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50615 | WERE | 'CHANUTE 69KV' | 34.903 | 0.00262 | -0.50877 | 8.7436
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50615 | WERE | 'CITY OF AUGUSTA 69KV' | 15.285 | 0.0012 | -0.50735 | 8.7681
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50615 | WERE | 'CITY OF BURLINGTON 69KV' | 4.8 | 0.00467 | -0.51082 | 8.7085
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50615 | WERE | 'CITY OF IOLA 69KV' | 19.902 | 0.00302 | -0.50917 | 8.7368
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50615 | WERE | 'CITY OF MULVANE 69KV' | 3.921 | -0.0011 | -0.50505 | 8.808
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50615 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00237 | -0.50378 | 8.8302
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50615 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.61 | 0.00467 | -0.51082 | 8.7085
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50615 | WERE | 'EVANS ENERGY CENTER 138KV' | 110 | 0.00047 | -0.50662 | 8.7807
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50615 | WERE | 'WACO 138KV' | 17.414 | -0.00428 | -0.50187 | 8.8638
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 383 | -0.4008 | WERE | 'CLAY CENTER JUNCTION 115KV' | 6.7 | 0.08529 | -0.48609 | 9.1516
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40041 | WERE | 'CLAY CENTER JUNCTION 115KV' | 6.7 | 0.08529 | -0.4857 | 9.1589
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50615 | WERE | 'COLBY 115KV' | 5.652 | -0.07459 | -0.43156 | 10.308
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50615 | WERE | 'KNOLL 3 115 115KV' | 75 | -0.0925 | -0.41365 | 10.7543
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 383 | -0.4008 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.02825 | -0.42905 | 10.3683
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 383 | -0.4008 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02949 | -0.43029 | 10.3384
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 383 | -0.4008 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 193.727 | 0.01813 | -0.41893 | 10.6187
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 383 | -0.4008 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.01951 | -0.42031 | 10.5839
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40041 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.02825 | -0.42866 | 10.3777
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40041 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02949 | -0.4299 | 10.3478
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40041 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 193.727 | 0.01813 | -0.41854 | 10.6286
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40041 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.01951 | -0.41992 | 10.5937
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 383 | -0.4008 | WERE | 'CHANUTE 69KV' | 34.903 | 0.00262 | -0.40342 | 11.027
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 383 | -0.4008 | WERE | 'CITY OF AUGUSTA 69KV' | 15.285 | 0.0012 | -0.402 | 11.0659
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 383 | -0.4008 | WERE | 'CITY OF BURLINGTON 69KV' | 4.8 | 0.00467 | -0.40547 | 10.9712
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 383 | -0.4008 | WERE | 'CITY OF IOLA 69KV' | 19.902 | 0.00302 | -0.40382 | 11.016
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 383 | -0.4008 | WERE | 'CITY OF MULVANE 69KV' | 3.921 | -0.0011 | -0.3997 | 11.1296
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 383 | -0.4008 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00237 | -0.39843 | 11.1651
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 383 | -0.4008 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.61 | 0.00467 | -0.40547 | 10.9712
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 383 | -0.4008 | WERE | 'EVANS ENERGY CENTER 138KV' | 110 | 0.00047 | -0.40127 | 11.0861
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 383 | -0.4008 | WERE | 'WACO 138KV' | 17.414 | -0.00428 | -0.39652 | 11.2189
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40041 | WERE | 'CHANUTE 69KV' | 34.903 | 0.00262 | -0.40303 | 11.0376
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40041 | WERE | 'CITY OF AUGUSTA 69KV' | 15.285 | 0.0012 | -0.40161 | 11.0767
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40041 | WERE | 'CITY OF BURLINGTON 69KV' | 4.8 | 0.00467 | -0.40508 | 10.9818
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40041 | WERE | 'CITY OF IOLA 69KV' | 19.902 | 0.00302 | -0.40343 | 11.0267
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40041 | WERE | 'CITY OF MULVANE 69KV' | 3.921 | -0.0011 | -0.39931 | 11.1405
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40041 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00237 | -0.39804 | 11.176
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40041 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.61 | 0.00467 | -0.40508 | 10.9818
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40041 | WERE | 'EVANS ENERGY CENTER 138KV' | 110 | 0.00047 | -0.40088 | 11.0968
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40041 | WERE | 'WACO 138KV' | 17.414 | -0.00428 | -0.39613 | 11.2299
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 383 | -0.4008 | WERE | 'COLBY 115KV' | 5.652 | -0.07459 | -0.32621 | 13.6369
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40041 | WERE | 'COLBY 115KV' | 5.652 | -0.07459 | -0.32582 | 13.6532
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 383 | -0.4008 | WERE | 'KNOLL 3 115 115KV' | 75 | -0.0925 | -0.3083 | 14.4291
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40041 | WERE | 'KNOLL 3 115 115KV' | 75 | -0.0925 | -0.30791 | 14.4474
WERE | 'PAWNEE 115KV' | 999 | -0.2156 | WERE | 'CLAY CENTER JUNCTION 115KV' | 6.7 | 0.08529 | -0.30089 | 14.7845
WERE | 'RICE 115KV' | 999 | -0.2156 | WERE | 'CLAY CENTER JUNCTION 115KV' | 6.7 | 0.08529 | -0.30089 | 14.7845
WERE | 'ST JOHN 115KV' | 7.5 | -0.2156 | WERE | 'CLAY CENTER JUNCTION 115KV' | 6.7 | 0.08529 | -0.30089 | 14.7845
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.17956 | WERE | 'CLAY CENTER JUNCTION 115KV' | 6.7 | 0.08529 | -0.26485 | 16.7963
WERE | 'PAWNEE 115KV' | 999 | -0.2156 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.02825 | -0.24385 | 18.2428
WERE | 'PAWNEE 115KV' | 999 | -0.2156 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02949 | -0.24509 | 18.1505
WERE | 'RICE 115KV' | 999 | -0.2156 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.02825 | -0.24385 | 18.2428
WERE | 'RICE 115KV' | 999 | -0.2156 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02949 | -0.24509 | 18.1505
WERE | 'ST JOHN 115KV' | 7.5 | -0.2156 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.02825 | -0.24385 | 18.2428
WERE | 'ST JOHN 115KV' | 7.5 | -0.2156 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02949 | -0.24509 | 18.1505
WERE | 'PAWNEE 115KV' | 999 | -0.2156 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 193.727 | 0.01813 | -0.23373 | 19.0326
WERE | 'PAWNEE 115KV' | 999 | -0.2156 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.01951 | -0.23511 | 18.9209
WERE | 'RICE 115KV' | 999 | -0.2156 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 193.727 | 0.01813 | -0.23373 | 19.0326
WERE | 'RICE 115KV' | 999 | -0.2156 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.01951 | -0.23511 | 18.9209
WERE | 'ST JOHN 115KV' | 7.5 | -0.2156 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 193.727 | 0.01813 | -0.23373 | 19.0326
WERE | 'ST JOHN 115KV' | 7.5 | -0.2156 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.01951 | -0.23511 | 18.9209
WERE | 'PAWNEE 115KV' | 999 | -0.2156 | WERE | 'CHANUTE 69KV' | 34.903 | 0.00262 | -0.21822 | 20.3854
WERE | 'PAWNEE 115KV' | 999 | -0.2156 | WERE | 'CITY OF AUGUSTA 69KV' | 15.285 | 0.0012 | -0.2168 | 20.5189
WERE | 'PAWNEE 115KV' | 999 | -0.2156 | WERE | 'CITY OF IOLA 69KV' | 19.902 | 0.00302 | -0.21862 | 20.3481
WERE | 'PAWNEE 115KV' | 999 | -0.2156 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00237 | -0.21323 | 20.8624
WERE | 'PAWNEE 115KV' | 999 | -0.2156 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.61 | 0.00467 | -0.22027 | 20.1957
WERE | 'PAWNEE 115KV' | 999 | -0.2156 | WERE | 'EVANS ENERGY CENTER 138KV' | 110 | 0.00047 | -0.21607 | 20.5882
WERE | 'PAWNEE 115KV' | 999 | -0.2156 | WERE | 'WACO 138KV' | 17.414 | -0.00428 | -0.21132 | 21.051
WERE | 'RICE 115KV' | 999 | -0.2156 | WERE | 'CHANUTE 69KV' | 34.903 | 0.00262 | -0.21822 | 20.3854
WERE | 'RICE 115KV' | 999 | -0.2156 | WERE | 'CITY OF AUGUSTA 69KV' | 15.285 | 0.0012 | -0.2168 | 20.5189
WERE | 'RICE 115KV' | 999 | -0.2156 | WERE | 'CITY OF IOLA 69KV' | 19.902 | 0.00302 | -0.21862 | 20.3481
WERE | 'RICE 115KV' | 999 | -0.2156 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00237 | -0.21323 | 20.8624
WERE | 'RICE 115KV' | 999 | -0.2156 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.61 | 0.00467 | -0.22027 | 20.1957
WERE | 'RICE 115KV' | 999 | -0.2156 | WERE | 'EVANS ENERGY CENTER 138KV' | 110 | 0.00047 | -0.21607 | 20.5882
WERE | 'RICE 115KV' | 999 | -0.2156 | WERE | 'WACO 138KV' | 17.414 | -0.00428 | -0.21132 | 21.051
WERE | 'ST JOHN 115KV' | 7.5 | -0.2156 | WERE | 'CHANUTE 69KV' | 34.903 | 0.00262 | -0.21822 | 20.3854
WERE | 'ST JOHN 115KV' | 7.5 | -0.2156 | WERE | 'CITY OF AUGUSTA 69KV' | 15.285 | 0.0012 | -0.2168 | 20.5189
WERE | 'ST JOHN 115KV' | 7.5 | -0.2156 | WERE | 'CITY OF IOLA 69KV' | 19.902 | 0.00302 | -0.21862 | 20.3481
WERE | 'ST JOHN 115KV' | 7.5 | -0.2156 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00237 | -0.21323 | 20.8624
WERE | 'ST JOHN 115KV' | 7.5 | -0.2156 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.61 | 0.00467 | -0.22027 | 20.1957
WERE | 'ST JOHN 115KV' | 7.5 | -0.2156 | WERE | 'EVANS ENERGY CENTER 138KV' | 110 | 0.00047 | -0.21607 | 20.5882
WERE | 'ST JOHN 115KV' | 7.5 | -0.2156 | WERE | 'WACO 138KV' | 17.414 | -0.00428 | -0.21132 | 21.051
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.17956 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.02825 | -0.20781 | 21.4066
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.17956 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02949 | -0.20905 | 21.2796
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.17956 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 193.727 | 0.01813 | -0.19769 | 22.5024
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.17956 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.01951 | -0.19907 | 22.3464
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.17956 | WERE | 'CHANUTE 69KV' | 34.903 | 0.00262 | -0.18218 | 24.4182
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.17956 | WERE | 'CITY OF AUGUSTA 69KV' | 15.285 | 0.0012 | -0.18076 | 24.61
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.17956 | WERE | 'CITY OF IOLA 69KV' | 19.902 | 0.00302 | -0.18258 | 24.3647
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.17956 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.61 | 0.00467 | -0.18423 | 24.1464
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.17956 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00237 | -0.17719 | 25.1058
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.17956 | WERE | 'EVANS ENERGY CENTER 138KV' | 110 | 0.00047 | -0.18003 | 24.7098
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.17956 | WERE | 'WACO 138KV' | 17.414 | -0.00428 | -0.17528 | 25.3794
WERE | 'PAWNEE 115KV' | 999 | -0.2156 | WERE | 'KNOLL 3 115 115KV' | 75 | -0.0925 | -0.1231 | 36.1373
WERE | 'RICE 115KV' | 999 | -0.2156 | WERE | 'KNOLL 3 115 115KV' | 75 | -0.0925 | -0.1231 | 36.1373
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | WICHITA - RENO 345KV
Limiting Facility: | NORTH AMERICAN PHILIPS JUNCTION (SOUTH) - WEST MCPHERSON 115KV CKT 1
Direction: | From->To
Line Outage: | EAST MCPHERSON - SUMMIT 230KV CKT 1
Flowgate: | 57374574381568725687312206WP
Date Redispatch Needed: | 12/1/06 - 4/1/07
Season Flowgate Identified: | 2006 Winter Peak
Reservation | Relief Amount | Aggregate Relief Amount
1090964 | 3.2137 | 4.1319
1090965 | 0.9182 | 4.1319
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.24288 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01575 | -0.25863 | 16
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.24288 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01637 | -0.25925 | 16
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.24288 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 130.0238 | 0.01028 | -0.25316 | 16
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.24288 | WERE | 'CHANUTE 69KV' | 35.344 | 0.00143 | -0.24431 | 17
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.24288 | WERE | 'CITY OF AUGUSTA 69KV' | 17.252 | 0.00045 | -0.24333 | 17
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.24288 | WERE | 'CITY OF IOLA 69KV' | 13.978 | 0.00166 | -0.24454 | 17
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.24288 | WERE | 'CITY OF WELLINGTON 69KV' | 24 | -0.00129 | -0.24159 | 17
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.24288 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.00266 | -0.24554 | 17
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.24288 | WERE | 'EVANS ENERGY CENTER 138KV' | 25.8875 | 0.00032 | -0.2432 | 17
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.24288 | WERE | 'WACO 138KV' | 17.953 | -0.00227 | -0.24061 | 17
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.19671 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01575 | -0.21246 | 19
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.19671 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01637 | -0.21308 | 19
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.19662 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01575 | -0.21237 | 19
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.19662 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01637 | -0.21299 | 19
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.19671 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 130.0238 | 0.01028 | -0.20699 | 20
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.19662 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 130.0238 | 0.01028 | -0.2069 | 20
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.19671 | WERE | 'CHANUTE 69KV' | 35.344 | 0.00143 | -0.19814 | 21
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.19671 | WERE | 'CITY OF AUGUSTA 69KV' | 17.252 | 0.00045 | -0.19716 | 21
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.19671 | WERE | 'CITY OF IOLA 69KV' | 13.978 | 0.00166 | -0.19837 | 21
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.19671 | WERE | 'CITY OF WELLINGTON 69KV' | 24 | -0.00129 | -0.19542 | 21
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.19671 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.00266 | -0.19937 | 21
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.19671 | WERE | 'EVANS ENERGY CENTER 138KV' | 25.8875 | 0.00032 | -0.19703 | 21
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.19671 | WERE | 'WACO 138KV' | 17.953 | -0.00227 | -0.19444 | 21
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.19662 | WERE | 'CHANUTE 69KV' | 35.344 | 0.00143 | -0.19805 | 21
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.19662 | WERE | 'CITY OF AUGUSTA 69KV' | 17.252 | 0.00045 | -0.19707 | 21
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.19662 | WERE | 'CITY OF IOLA 69KV' | 13.978 | 0.00166 | -0.19828 | 21
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.19662 | WERE | 'CITY OF WELLINGTON 69KV' | 24 | -0.00129 | -0.19533 | 21
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.19662 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.00266 | -0.19928 | 21
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.19662 | WERE | 'EVANS ENERGY CENTER 138KV' | 25.8875 | 0.00032 | -0.19694 | 21
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.19662 | WERE | 'WACO 138KV' | 17.953 | -0.00227 | -0.19435 | 21
WERE | 'PAWNEE 115KV' | 999 | -0.1139 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01575 | -0.12965 | 32
WERE | 'PAWNEE 115KV' | 999 | -0.1139 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01637 | -0.13027 | 32
WERE | 'RICE 115KV' | 999 | -0.1139 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01575 | -0.12965 | 32
WERE | 'RICE 115KV' | 999 | -0.1139 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01637 | -0.13027 | 32
WERE | 'PAWNEE 115KV' | 999 | -0.1139 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 130.0238 | 0.01028 | -0.12418 | 33
WERE | 'RICE 115KV' | 999 | -0.1139 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 130.0238 | 0.01028 | -0.12418 | 33
WERE | 'PAWNEE 115KV' | 999 | -0.1139 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.00266 | -0.11656 | 35
WERE | 'RICE 115KV' | 999 | -0.1139 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.00266 | -0.11656 | 35
WERE | 'PAWNEE 115KV' | 999 | -0.1139 | WERE | 'CITY OF AUGUSTA 69KV' | 17.252 | 0.00045 | -0.11435 | 36
WERE | 'PAWNEE 115KV' | 999 | -0.1139 | WERE | 'EVANS ENERGY CENTER 138KV' | 25.8875 | 0.00032 | -0.11422 | 36
WERE | 'RICE 115KV' | 999 | -0.1139 | WERE | 'CITY OF AUGUSTA 69KV' | 17.252 | 0.00045 | -0.11435 | 36
WERE | 'RICE 115KV' | 999 | -0.1139 | WERE | 'EVANS ENERGY CENTER 138KV' | 25.8875 | 0.00032 | -0.11422 | 36
WERE | 'PAWNEE 115KV' | 999 | -0.1139 | WERE | 'CITY OF WELLINGTON 69KV' | 24 | -0.00129 | -0.11261 | 37
WERE | 'PAWNEE 115KV' | 999 | -0.1139 | WERE | 'WACO 138KV' | 17.953 | -0.00227 | -0.11163 | 37
WERE | 'RICE 115KV' | 999 | -0.1139 | WERE | 'CITY OF WELLINGTON 69KV' | 24 | -0.00129 | -0.11261 | 37
WERE | 'RICE 115KV' | 999 | -0.1139 | WERE | 'WACO 138KV' | 17.953 | -0.00227 | -0.11163 | 37
WEPL | 'A. M. MULLERGREN GENERATOR 115KV' | 63 | -0.10301 | WEPL | 'GRAY COUNTY WIND FARM 115KV' | 73 | -0.06549 | -0.03752 | 110
WERE | 'KNOLL 3 115 115KV' | 75 | -0.01862 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01637 | -0.03499 | 118
WERE | 'KNOLL 3 115 115KV' | 75 | -0.01862 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01575 | -0.03437 | 120
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | WICHITA - RENO 345KV
Limiting Facility: | NORTH AMERICAN PHILIPS JUNCTION (SOUTH) - WEST MCPHERSON 115KV CKT 1
Direction: | From->To
Line Outage: | EAST MCPHERSON - SUMMIT 230KV CKT 1
Flowgate: | 57374574381568725687312207FA
Date Redispatch Needed: | Starting 2007 10/1 - 12/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 Fall Peak
Reservation | Relief Amount | Aggregate Relief Amount
1090817 | 2.1902 | 6.1327
1090964 | 3.0663 | 6.1327
1090965 | 0.8761 | 6.1327
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.2354 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01317 | -0.24857 | 25
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.2354 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01373 | -0.24913 | 25
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.2354 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 230.3248 | 0.00844 | -0.24384 | 25
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.2354 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00908 | -0.24448 | 25
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.2354 | WERE | 'CHANUTE 69KV' | 56.296 | 0.0012 | -0.2366 | 26
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.2354 | WERE | 'CITY OF AUGUSTA 69KV' | 19.636 | 0.00057 | -0.23597 | 26
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.2354 | WERE | 'CITY OF IOLA 69KV' | 24.256 | 0.00138 | -0.23678 | 26
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.2354 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00109 | -0.23431 | 26
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.2354 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.96 | 0.0022 | -0.2376 | 26
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.2354 | WERE | 'EVANS ENERGY CENTER 138KV' | 187.8892 | 0.00023 | -0.23563 | 26
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.2354 | WERE | 'WACO 138KV' | 17.946 | -0.00198 | -0.23342 | 26
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 343 | -0.18641 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01317 | -0.19958 | 31
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 343 | -0.18641 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01373 | -0.20014 | 31
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 343 | -0.18641 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 230.3248 | 0.00844 | -0.19485 | 31
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 343 | -0.18641 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00908 | -0.19549 | 31
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.18632 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01317 | -0.19949 | 31
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.18632 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01373 | -0.20005 | 31
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.18632 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 230.3248 | 0.00844 | -0.19476 | 31
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.18632 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00908 | -0.1954 | 31
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 343 | -0.18641 | WERE | 'CITY OF AUGUSTA 69KV' | 19.636 | 0.00057 | -0.18698 | 33
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 343 | -0.18641 | WERE | 'CITY OF IOLA 69KV' | 24.256 | 0.00138 | -0.18779 | 33
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 343 | -0.18641 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00109 | -0.18532 | 33
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 343 | -0.18641 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.96 | 0.0022 | -0.18861 | 33
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 343 | -0.18641 | WERE | 'EVANS ENERGY CENTER 138KV' | 187.8892 | 0.00023 | -0.18664 | 33
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 343 | -0.18641 | WERE | 'WACO 138KV' | 17.946 | -0.00198 | -0.18443 | 33
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.18632 | WERE | 'CITY OF AUGUSTA 69KV' | 19.636 | 0.00057 | -0.18689 | 33
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.18632 | WERE | 'CITY OF IOLA 69KV' | 24.256 | 0.00138 | -0.1877 | 33
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.18632 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00109 | -0.18523 | 33
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.18632 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.96 | 0.0022 | -0.18852 | 33
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.18632 | WERE | 'EVANS ENERGY CENTER 138KV' | 187.8892 | 0.00023 | -0.18655 | 33
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.18632 | WERE | 'WACO 138KV' | 17.946 | -0.00198 | -0.18434 | 33
WERE | 'PAWNEE 115KV' | 999 | -0.10027 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01317 | -0.11344 | 54
WERE | 'PAWNEE 115KV' | 999 | -0.10027 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01373 | -0.114 | 54
WERE | 'RICE 115KV' | 999 | -0.10027 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01317 | -0.11344 | 54
WERE | 'RICE 115KV' | 999 | -0.10027 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01373 | -0.114 | 54
WERE | 'PAWNEE 115KV' | 999 | -0.10027 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 230.3248 | 0.00844 | -0.10871 | 56
WERE | 'PAWNEE 115KV' | 999 | -0.10027 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00908 | -0.10935 | 56
WERE | 'RICE 115KV' | 999 | -0.10027 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 230.3248 | 0.00844 | -0.10871 | 56
WERE | 'RICE 115KV' | 999 | -0.10027 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00908 | -0.10935 | 56
WERE | 'PAWNEE 115KV' | 999 | -0.10027 | WERE | 'EVANS ENERGY CENTER 138KV' | 187.8892 | 0.00023 | -0.1005 | 61
WERE | 'RICE 115KV' | 999 | -0.10027 | WERE | 'EVANS ENERGY CENTER 138KV' | 187.8892 | 0.00023 | -0.1005 | 61
WERE | 'KNOLL 3 115 115KV' | 75 | -0.0431 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01373 | -0.05683 | 108
WERE | 'KNOLL 3 115 115KV' | 75 | -0.0431 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01317 | -0.05627 | 109
WERE | 'KNOLL 3 115 115KV' | 75 | -0.0431 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00908 | -0.05218 | 118
WERE | 'KNOLL 3 115 115KV' | 75 | -0.0431 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 230.3248 | 0.00844 | -0.05154 | 119
WERE | 'KNOLL 3 115 115KV' | 75 | -0.0431 | WERE | 'EVANS ENERGY CENTER 138KV' | 187.8892 | 0.00023 | -0.04333 | 142
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | WICHITA - RENO 345KV
Limiting Facility: | NORTH AMERICAN PHILIPS JUNCTION (SOUTH) - WEST MCPHERSON 115KV CKT 1
Direction: | From->To
Line Outage: | EAST MCPHERSON - SUMMIT 230KV CKT 1
Flowgate: | 57374574381568725687312207SH
Date Redispatch Needed: | 6/1 - 10/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 Summer Shoulder
Reservation | Relief Amount | Aggregate Relief Amount
1090817 | 2.7658 | 7.7441
1090964 | 3.8721 | 7.7441
1090965 | 1.1063 | 7.7441
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.24281 | WERE | 'ABILENE ENERGY CENTER 115KV' | 18.2344 | 0.05669 | -0.2995 | 26
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.24281 | WERE | 'CLAY CENTER JUNCTION 115KV' | 11.825 | 0.0423 | -0.28511 | 27
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.24281 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01534 | -0.25815 | 30
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.24281 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01597 | -0.25878 | 30
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.24281 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.00939 | -0.2522 | 31
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.24281 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 230.2191 | 0.00986 | -0.25267 | 31
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.24281 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.0106 | -0.25341 | 31
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.19647 | WERE | 'ABILENE ENERGY CENTER 115KV' | 18.2344 | 0.05669 | -0.25316 | 31
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.19638 | WERE | 'ABILENE ENERGY CENTER 115KV' | 18.2344 | 0.05669 | -0.25307 | 31
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.24281 | WERE | 'CHANUTE 69KV' | 46.617 | 0.00144 | -0.24425 | 32
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.24281 | WERE | 'CITY OF ERIE 69KV' | 23.258 | 0.00144 | -0.24425 | 32
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.24281 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.96 | 0.00264 | -0.24545 | 32
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.24281 | WERE | 'EVANS ENERGY CENTER 138KV' | 305 | 0.0004 | -0.24321 | 32
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.24281 | WERE | 'GILL ENERGY CENTER 138KV' | 77 | -0.00241 | -0.2404 | 32
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.24281 | WERE | 'WACO 138KV' | 17.947 | -0.00213 | -0.24068 | 32
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.19647 | WERE | 'CLAY CENTER JUNCTION 115KV' | 11.825 | 0.0423 | -0.23877 | 32
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.19638 | WERE | 'CLAY CENTER JUNCTION 115KV' | 11.825 | 0.0423 | -0.23868 | 32
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.19647 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01597 | -0.21244 | 36
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.19638 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01597 | -0.21235 | 36
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.19647 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01534 | -0.21181 | 37
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.19647 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.0106 | -0.20707 | 37
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.19638 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01534 | -0.21172 | 37
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.19638 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.0106 | -0.20698 | 37
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.19647 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.00939 | -0.20586 | 38
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.19647 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 230.2191 | 0.00986 | -0.20633 | 38
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.19638 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.00939 | -0.20577 | 38
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.19638 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 230.2191 | 0.00986 | -0.20624 | 38
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.19647 | WERE | 'CITY OF ERIE 69KV' | 23.258 | 0.00144 | -0.19791 | 39
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.19647 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.96 | 0.00264 | -0.19911 | 39
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.19647 | WERE | 'EVANS ENERGY CENTER 138KV' | 305 | 0.0004 | -0.19687 | 39
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.19638 | WERE | 'CITY OF ERIE 69KV' | 23.258 | 0.00144 | -0.19782 | 39
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.19638 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.96 | 0.00264 | -0.19902 | 39
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.19638 | WERE | 'EVANS ENERGY CENTER 138KV' | 305 | 0.0004 | -0.19678 | 39
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.19647 | WERE | 'GILL ENERGY CENTER 138KV' | 77 | -0.00241 | -0.19406 | 40
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.19647 | WERE | 'WACO 138KV' | 17.947 | -0.00213 | -0.19434 | 40
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.19638 | WERE | 'GILL ENERGY CENTER 138KV' | 77 | -0.00241 | -0.19397 | 40
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.19638 | WERE | 'WACO 138KV' | 17.947 | -0.00213 | -0.19425 | 40
WERE | 'PAWNEE 115KV' | 999 | -0.11187 | WERE | 'ABILENE ENERGY CENTER 115KV' | 18.2344 | 0.05669 | -0.16856 | 46
WERE | 'RICE 115KV' | 999 | -0.11187 | WERE | 'ABILENE ENERGY CENTER 115KV' | 18.2344 | 0.05669 | -0.16856 | 46
WERE | 'PAWNEE 115KV' | 999 | -0.11187 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01534 | -0.12721 | 61
WERE | 'PAWNEE 115KV' | 999 | -0.11187 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01597 | -0.12784 | 61
WERE | 'RICE 115KV' | 999 | -0.11187 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01534 | -0.12721 | 61
WERE | 'RICE 115KV' | 999 | -0.11187 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01597 | -0.12784 | 61
WERE | 'PAWNEE 115KV' | 999 | -0.11187 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.0106 | -0.12247 | 63
WERE | 'RICE 115KV' | 999 | -0.11187 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.0106 | -0.12247 | 63
WERE | 'PAWNEE 115KV' | 999 | -0.11187 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.00939 | -0.12126 | 64
WERE | 'PAWNEE 115KV' | 999 | -0.11187 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 230.2191 | 0.00986 | -0.12173 | 64
WERE | 'RICE 115KV' | 999 | -0.11187 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.00939 | -0.12126 | 64
WERE | 'RICE 115KV' | 999 | -0.11187 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 230.2191 | 0.00986 | -0.12173 | 64
WERE | 'PAWNEE 115KV' | 999 | -0.11187 | WERE | 'CITY OF ERIE 69KV' | 23.258 | 0.00144 | -0.11331 | 68
WERE | 'RICE 115KV' | 999 | -0.11187 | WERE | 'CITY OF ERIE 69KV' | 23.258 | 0.00144 | -0.11331 | 68
WERE | 'PAWNEE 115KV' | 999 | -0.11187 | WERE | 'EVANS ENERGY CENTER 138KV' | 305 | 0.0004 | -0.11227 | 69
WERE | 'RICE 115KV' | 999 | -0.11187 | WERE | 'EVANS ENERGY CENTER 138KV' | 305 | 0.0004 | -0.11227 | 69
WERE | 'PAWNEE 115KV' | 999 | -0.11187 | WERE | 'GILL ENERGY CENTER 138KV' | 77 | -0.00241 | -0.10946 | 71
WERE | 'RICE 115KV' | 999 | -0.11187 | WERE | 'GILL ENERGY CENTER 138KV' | 77 | -0.00241 | -0.10946 | 71
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.24281 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 80 | -0.19647 | -0.04634 | 167
WERE | 'KNOLL 3 115 115KV' | 75 | -0.02035 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01597 | -0.03632 | 213
WERE | 'KNOLL 3 115 115KV' | 75 | -0.02035 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01534 | -0.03569 | 217
WERE | 'KNOLL 3 115 115KV' | 75 | -0.02035 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.0106 | -0.03095 | 250
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | WICHITA - RENO 345KV
Limiting Facility: | NORTH AMERICAN PHILIPS JUNCTION (SOUTH) - WEST MCPHERSON 115KV CKT 1
Direction: | From->To
Line Outage: | EAST MCPHERSON - SUMMIT 230KV CKT 1
Flowgate: | 57374574381568725687312207WP
Date Redispatch Needed: | 12/1/07 - 4/1/08
Season Flowgate Identified: | 2007 Winter Peak
Reservation | Relief Amount | Aggregate Relief Amount
1090817 | 2.339 | 6.5492
1090964 | 3.2746 | 6.5492
1090965 | 0.9356 | 6.5492
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.23538 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01319 | -0.24857 | 26
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.23538 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01375 | -0.24913 | 26
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.23538 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 169.36 | 0.00846 | -0.24384 | 27
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.23538 | WERE | 'CHANUTE 69KV' | 34.818 | 0.00122 | -0.2366 | 28
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.23538 | WERE | 'CITY OF AUGUSTA 69KV' | 14.628 | 0.00059 | -0.23597 | 28
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.23538 | WERE | 'CITY OF IOLA 69KV' | 14.565 | 0.0014 | -0.23678 | 28
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.23538 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00108 | -0.2343 | 28
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.23538 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.95 | 0.00222 | -0.2376 | 28
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.23538 | WERE | 'EVANS ENERGY CENTER 138KV' | 55 | 0.00025 | -0.23563 | 28
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.23538 | WERE | 'WACO 138KV' | 17.93 | -0.00196 | -0.23342 | 28
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.18639 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01319 | -0.19958 | 33
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.18639 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01375 | -0.20014 | 33
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.1863 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01319 | -0.19949 | 33
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.1863 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01375 | -0.20005 | 33
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.18639 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 169.36 | 0.00846 | -0.19485 | 34
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.1863 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 169.36 | 0.00846 | -0.19476 | 34
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.18639 | WERE | 'CITY OF AUGUSTA 69KV' | 14.628 | 0.00059 | -0.18698 | 35
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.18639 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00108 | -0.18531 | 35
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.18639 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.95 | 0.00222 | -0.18861 | 35
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.18639 | WERE | 'EVANS ENERGY CENTER 138KV' | 55 | 0.00025 | -0.18664 | 35
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.1863 | WERE | 'CITY OF AUGUSTA 69KV' | 14.628 | 0.00059 | -0.18689 | 35
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.1863 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00108 | -0.18522 | 35
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.1863 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.95 | 0.00222 | -0.18852 | 35
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.1863 | WERE | 'EVANS ENERGY CENTER 138KV' | 55 | 0.00025 | -0.18655 | 35
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.18639 | WERE | 'WACO 138KV' | 17.93 | -0.00196 | -0.18443 | 36
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.1863 | WERE | 'WACO 138KV' | 17.93 | -0.00196 | -0.18434 | 36
WERE | 'PAWNEE 115KV' | 999 | -0.10024 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01375 | -0.11399 | 57
WERE | 'RICE 115KV' | 999 | -0.10024 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01375 | -0.11399 | 57
WERE | 'PAWNEE 115KV' | 999 | -0.10024 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01319 | -0.11343 | 58
WERE | 'RICE 115KV' | 999 | -0.10024 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01319 | -0.11343 | 58
WERE | 'PAWNEE 115KV' | 999 | -0.10024 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 169.36 | 0.00846 | -0.1087 | 60
WERE | 'RICE 115KV' | 999 | -0.10024 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 169.36 | 0.00846 | -0.1087 | 60
WERE | 'PAWNEE 115KV' | 999 | -0.10024 | WERE | 'EVANS ENERGY CENTER 138KV' | 55 | 0.00025 | -0.10049 | 65
WERE | 'RICE 115KV' | 999 | -0.10024 | WERE | 'EVANS ENERGY CENTER 138KV' | 55 | 0.00025 | -0.10049 | 65
WERE | 'KNOLL 3 115 115KV' | 75 | -0.04307 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01375 | -0.05682 | 115
WERE | 'KNOLL 3 115 115KV' | 75 | -0.04307 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01319 | -0.05626 | 116
WERE | 'KNOLL 3 115 115KV' | 75 | -0.04307 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 169.36 | 0.00846 | -0.05153 | 127
WERE | 'KNOLL 3 115 115KV' | 75 | -0.04307 | WERE | 'EVANS ENERGY CENTER 138KV' | 55 | 0.00025 | -0.04332 | 151
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | WICHITA - RENO 345KV
Limiting Facility: | NORTH AMERICAN PHILIPS JUNCTION (SOUTH) - WEST MCPHERSON 115KV CKT 1
Direction: | From->To
Line Outage: | EAST MCPHERSON - SUMMIT 230KV CKT 1
Flowgate: | 57374574381568725687314207G
Date Redispatch Needed: | Starting 2007 4/1 - 6/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 Spring Peak
Reservation | Relief Amount | Aggregate Relief Amount
1090964 | 1.8576 | 2.4039
1090965 | 0.54635 | 2.4039
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.2428 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | 0.05672 | -0.29952 | 8
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.2428 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01537 | -0.25817 | 9
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.2428 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.016 | -0.2588 | 9
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.2428 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 68 | 0.01063 | -0.25343 | 9
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 300.5205 | -0.19645 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | 0.05672 | -0.25317 | 9
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.19636 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | 0.05672 | -0.25308 | 9
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.2428 | WERE | 'CHANUTE 69KV' | 40.39 | 0.00148 | -0.24428 | 10
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.2428 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | 0.0008 | -0.2436 | 10
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.2428 | WERE | 'CITY OF BURLINGTON 69KV' | 4.8 | 0.00267 | -0.24547 | 10
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.2428 | WERE | 'CITY OF IOLA 69KV' | 17.08 | 0.00168 | -0.24448 | 10
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.2428 | WERE | 'CITY OF MULVANE 69KV' | 4.922 | -0.00042 | -0.24238 | 10
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.2428 | WERE | 'CITY OF WELLINGTON 69KV' | 40.503 | -0.00115 | -0.24165 | 10
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.2428 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 20.09 | 0.00267 | -0.24547 | 10
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.2428 | WERE | 'EVANS ENERGY CENTER 138KV' | 305 | 0.00042 | -0.24322 | 10
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.2428 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00239 | -0.24041 | 10
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.2428 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.00942 | -0.25222 | 10
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.2428 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 227.1991 | 0.00988 | -0.25268 | 10
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.2428 | WERE | 'WACO 138KV' | 18 | -0.00211 | -0.24069 | 10
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 300.5205 | -0.19645 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01537 | -0.21182 | 11
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 300.5205 | -0.19645 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.016 | -0.21245 | 11
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.19636 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01537 | -0.21173 | 11
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.19636 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.016 | -0.21236 | 11
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.2428 | WERE | 'COLBY 115KV' | 6.1302 | -0.03655 | -0.20625 | 12
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 300.5205 | -0.19645 | WERE | 'CHANUTE 69KV' | 40.39 | 0.00148 | -0.19793 | 12
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 300.5205 | -0.19645 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | 0.0008 | -0.19725 | 12
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 300.5205 | -0.19645 | WERE | 'CITY OF BURLINGTON 69KV' | 4.8 | 0.00267 | -0.19912 | 12
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 300.5205 | -0.19645 | WERE | 'CITY OF IOLA 69KV' | 17.08 | 0.00168 | -0.19813 | 12
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 300.5205 | -0.19645 | WERE | 'CITY OF MULVANE 69KV' | 4.922 | -0.00042 | -0.19603 | 12
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 300.5205 | -0.19645 | WERE | 'CITY OF WELLINGTON 69KV' | 40.503 | -0.00115 | -0.1953 | 12
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 300.5205 | -0.19645 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 20.09 | 0.00267 | -0.19912 | 12
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 300.5205 | -0.19645 | WERE | 'EVANS ENERGY CENTER 138KV' | 305 | 0.00042 | -0.19687 | 12
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 300.5205 | -0.19645 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00239 | -0.19406 | 12
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 300.5205 | -0.19645 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.00942 | -0.20587 | 12
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 300.5205 | -0.19645 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 227.1991 | 0.00988 | -0.20633 | 12
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 300.5205 | -0.19645 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 68 | 0.01063 | -0.20708 | 12
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 300.5205 | -0.19645 | WERE | 'WACO 138KV' | 18 | -0.00211 | -0.19434 | 12
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.19636 | WERE | 'CHANUTE 69KV' | 40.39 | 0.00148 | -0.19784 | 12
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.19636 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | 0.0008 | -0.19716 | 12
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.19636 | WERE | 'CITY OF BURLINGTON 69KV' | 4.8 | 0.00267 | -0.19903 | 12
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.19636 | WERE | 'CITY OF IOLA 69KV' | 17.08 | 0.00168 | -0.19804 | 12
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.19636 | WERE | 'CITY OF MULVANE 69KV' | 4.922 | -0.00042 | -0.19594 | 12
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.19636 | WERE | 'CITY OF WELLINGTON 69KV' | 40.503 | -0.00115 | -0.19521 | 12
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.19636 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 20.09 | 0.00267 | -0.19903 | 12
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.19636 | WERE | 'EVANS ENERGY CENTER 138KV' | 305 | 0.00042 | -0.19678 | 12
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.19636 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00239 | -0.19397 | 12
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.19636 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.00942 | -0.20578 | 12
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.19636 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 227.1991 | 0.00988 | -0.20624 | 12
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.19636 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 68 | 0.01063 | -0.20699 | 12
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.19636 | WERE | 'WACO 138KV' | 18 | -0.00211 | -0.19425 | 12
WERE | 'PAWNEE 115KV' | 999 | -0.11186 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | 0.05672 | -0.16858 | 14
WERE | 'RICE 115KV' | 999 | -0.11186 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | 0.05672 | -0.16858 | 14
WERE | 'ST JOHN 115KV' | 7.5 | -0.11186 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | 0.05672 | -0.16858 | 14
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 300.5205 | -0.19645 | WERE | 'COLBY 115KV' | 6.1302 | -0.03655 | -0.1599 | 15
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.19636 | WERE | 'COLBY 115KV' | 6.1302 | -0.03655 | -0.15981 | 15
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.0975 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | 0.05672 | -0.15422 | 16
WERE | 'PAWNEE 115KV' | 999 | -0.11186 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01537 | -0.12723 | 19
WERE | 'PAWNEE 115KV' | 999 | -0.11186 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.016 | -0.12786 | 19
WERE | 'RICE 115KV' | 999 | -0.11186 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01537 | -0.12723 | 19
WERE | 'RICE 115KV' | 999 | -0.11186 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.016 | -0.12786 | 19
WERE | 'ST JOHN 115KV' | 7.5 | -0.11186 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01537 | -0.12723 | 19
WERE | 'ST JOHN 115KV' | 7.5 | -0.11186 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.016 | -0.12786 | 19
WERE | 'PAWNEE 115KV' | 999 | -0.11186 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.00942 | -0.12128 | 20
WERE | 'PAWNEE 115KV' | 999 | -0.11186 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 227.1991 | 0.00988 | -0.12174 | 20
WERE | 'PAWNEE 115KV' | 999 | -0.11186 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 68 | 0.01063 | -0.12249 | 20
WERE | 'RICE 115KV' | 999 | -0.11186 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.00942 | -0.12128 | 20
WERE | 'RICE 115KV' | 999 | -0.11186 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 227.1991 | 0.00988 | -0.12174 | 20
WERE | 'RICE 115KV' | 999 | -0.11186 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 68 | 0.01063 | -0.12249 | 20
WERE | 'ST JOHN 115KV' | 7.5 | -0.11186 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.00942 | -0.12128 | 20
WERE | 'ST JOHN 115KV' | 7.5 | -0.11186 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 227.1991 | 0.00988 | -0.12174 | 20
WERE | 'ST JOHN 115KV' | 7.5 | -0.11186 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 68 | 0.01063 | -0.12249 | 20
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.0975 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01537 | -0.11287 | 21
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.0975 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.016 | -0.1135 | 21
WERE | 'PAWNEE 115KV' | 999 | -0.11186 | WERE | 'CHANUTE 69KV' | 40.39 | 0.00148 | -0.11334 | 21
WERE | 'PAWNEE 115KV' | 999 | -0.11186 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | 0.0008 | -0.11266 | 21
WERE | 'PAWNEE 115KV' | 999 | -0.11186 | WERE | 'CITY OF IOLA 69KV' | 17.08 | 0.00168 | -0.11354 | 21
WERE | 'PAWNEE 115KV' | 999 | -0.11186 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 20.09 | 0.00267 | -0.11453 | 21
WERE | 'PAWNEE 115KV' | 999 | -0.11186 | WERE | 'EVANS ENERGY CENTER 138KV' | 305 | 0.00042 | -0.11228 | 21
WERE | 'RICE 115KV' | 999 | -0.11186 | WERE | 'CHANUTE 69KV' | 40.39 | 0.00148 | -0.11334 | 21
WERE | 'RICE 115KV' | 999 | -0.11186 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | 0.0008 | -0.11266 | 21
WERE | 'RICE 115KV' | 999 | -0.11186 | WERE | 'CITY OF IOLA 69KV' | 17.08 | 0.00168 | -0.11354 | 21
WERE | 'RICE 115KV' | 999 | -0.11186 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 20.09 | 0.00267 | -0.11453 | 21
WERE | 'RICE 115KV' | 999 | -0.11186 | WERE | 'EVANS ENERGY CENTER 138KV' | 305 | 0.00042 | -0.11228 | 21
WERE | 'ST JOHN 115KV' | 7.5 | -0.11186 | WERE | 'CHANUTE 69KV' | 40.39 | 0.00148 | -0.11334 | 21
WERE | 'ST JOHN 115KV' | 7.5 | -0.11186 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | 0.0008 | -0.11266 | 21
WERE | 'ST JOHN 115KV' | 7.5 | -0.11186 | WERE | 'CITY OF IOLA 69KV' | 17.08 | 0.00168 | -0.11354 | 21
WERE | 'ST JOHN 115KV' | 7.5 | -0.11186 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 20.09 | 0.00267 | -0.11453 | 21
WERE | 'ST JOHN 115KV' | 7.5 | -0.11186 | WERE | 'EVANS ENERGY CENTER 138KV' | 305 | 0.00042 | -0.11228 | 21
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.0975 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.00942 | -0.10692 | 22
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.0975 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 227.1991 | 0.00988 | -0.10738 | 22
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.0975 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 68 | 0.01063 | -0.10813 | 22
WERE | 'PAWNEE 115KV' | 999 | -0.11186 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00239 | -0.10947 | 22
WERE | 'PAWNEE 115KV' | 999 | -0.11186 | WERE | 'WACO 138KV' | 18 | -0.00211 | -0.10975 | 22
WERE | 'RICE 115KV' | 999 | -0.11186 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00239 | -0.10947 | 22
WERE | 'RICE 115KV' | 999 | -0.11186 | WERE | 'WACO 138KV' | 18 | -0.00211 | -0.10975 | 22
WERE | 'ST JOHN 115KV' | 7.5 | -0.11186 | WERE | 'CITY OF WELLINGTON 69KV' | 40.503 | -0.00115 | -0.11071 | 22
WERE | 'ST JOHN 115KV' | 7.5 | -0.11186 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00239 | -0.10947 | 22
WERE | 'ST JOHN 115KV' | 7.5 | -0.11186 | WERE | 'WACO 138KV' | 18 | -0.00211 | -0.10975 | 22
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.0975 | WERE | 'CHANUTE 69KV' | 40.39 | 0.00148 | -0.09898 | 24
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.0975 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | 0.0008 | -0.0983 | 24
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.0975 | WERE | 'CITY OF IOLA 69KV' | 17.08 | 0.00168 | -0.09918 | 24
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | WICHITA - RENO 345KV
Limiting Facility: | NORTH AMERICAN PHILIPS JUNCTION (SOUTH) - WEST MCPHERSON 115KV CKT 1
Direction: | From->To
Line Outage: | EAST MCPHERSON - SUMMIT 230KV CKT 1
Flowgate: | 57374574381568725687314208WP
Date Redispatch Needed: | Starting 2008 12/1 - 4/1 Until EOC
Season Flowgate Identified: | 2008 Winter Peak
Reservation | Relief Amount | Aggregate Relief Amount
1090817 | 1.5739 | 8.019
1090829 | 0.91812 | 8.019
1090917 | 0.58226 | 8.019
1090919 | 0.16636 | 8.019
1090920 | 1.1645 | 8.019
1090921 | 0.29113 | 8.019
1090964 | 2.0986 | 8.019
1090965 | 0.61208 | 8.019
1091057 | 0.61208 | 8.019
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.23538 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01314 | -0.24852 | 32.2671
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.23538 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01371 | -0.24909 | 32.1933
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.23538 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 193.727 | 0.00843 | -0.24381 | 32.8905
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.23538 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.00907 | -0.24445 | 32.8044
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.23538 | WERE | 'CHANUTE 69KV' | 34.903 | 0.00122 | -0.2366 | 33.8928
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.23538 | WERE | 'CITY OF AUGUSTA 69KV' | 15.285 | 0.00056 | -0.23594 | 33.9876
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.23538 | WERE | 'CITY OF IOLA 69KV' | 19.902 | 0.00141 | -0.23679 | 33.8656
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.23538 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.0011 | -0.23428 | 34.2284
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.23538 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.61 | 0.00217 | -0.23755 | 33.7572
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.23538 | WERE | 'EVANS ENERGY CENTER 138KV' | 110 | 0.00022 | -0.2356 | 34.0366
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.23538 | WERE | 'WACO 138KV' | 17.414 | -0.00199 | -0.23339 | 34.3589
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 383 | -0.18638 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01371 | -0.20009 | 40.0771
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 383 | -0.18638 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01314 | -0.19952 | 40.1916
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 383 | -0.18638 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 193.727 | 0.00843 | -0.19481 | 41.1633
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 383 | -0.18638 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.00907 | -0.19545 | 41.0285
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.1862 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01314 | -0.19934 | 40.2279
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.1862 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01371 | -0.19991 | 40.1132
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.1862 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 193.727 | 0.00843 | -0.19463 | 41.2014
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.1862 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.00907 | -0.19527 | 41.0664
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.23538 | WERE | 'KNOLL 3 115 115KV' | 75 | -0.04301 | -0.19237 | 41.6854
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 383 | -0.18638 | WERE | 'CITY OF AUGUSTA 69KV' | 15.285 | 0.00056 | -0.18694 | 42.8963
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 383 | -0.18638 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.0011 | -0.18528 | 43.2806
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 383 | -0.18638 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.61 | 0.00217 | -0.18855 | 42.53
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 383 | -0.18638 | WERE | 'EVANS ENERGY CENTER 138KV' | 110 | 0.00022 | -0.1866 | 42.9744
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.1862 | WERE | 'CITY OF AUGUSTA 69KV' | 15.285 | 0.00056 | -0.18676 | 42.9376
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.1862 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.0011 | -0.1851 | 43.3227
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.1862 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.61 | 0.00217 | -0.18837 | 42.5706
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.1862 | WERE | 'EVANS ENERGY CENTER 138KV' | 110 | 0.00022 | -0.18642 | 43.0159
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 383 | -0.18638 | WERE | 'WACO 138KV' | 17.414 | -0.00199 | -0.18439 | 43.4895
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.1862 | WERE | 'WACO 138KV' | 17.414 | -0.00199 | -0.18421 | 43.532
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 383 | -0.18638 | WERE | 'KNOLL 3 115 115KV' | 75 | -0.04301 | -0.14337 | 55.9324
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.1862 | WERE | 'KNOLL 3 115 115KV' | 75 | -0.04301 | -0.14319 | 56.0027
WERE | 'PAWNEE 115KV' | 999 | -0.10026 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01371 | -0.11397 | 70.3609
WERE | 'RICE 115KV' | 999 | -0.10026 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01371 | -0.11397 | 70.3609
WERE | 'PAWNEE 115KV' | 999 | -0.10026 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01314 | -0.1134 | 70.7146
WERE | 'RICE 115KV' | 999 | -0.10026 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01314 | -0.1134 | 70.7146
WERE | 'PAWNEE 115KV' | 999 | -0.10026 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 193.727 | 0.00843 | -0.10869 | 73.7789
WERE | 'PAWNEE 115KV' | 999 | -0.10026 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.00907 | -0.10933 | 73.347
WERE | 'RICE 115KV' | 999 | -0.10026 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 193.727 | 0.00843 | -0.10869 | 73.7789
WERE | 'RICE 115KV' | 999 | -0.10026 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 48 | 0.00907 | -0.10933 | 73.347
WERE | 'PAWNEE 115KV' | 999 | -0.10026 | WERE | 'EVANS ENERGY CENTER 138KV' | 110 | 0.00022 | -0.10048 | 79.8072
WERE | 'RICE 115KV' | 999 | -0.10026 | WERE | 'EVANS ENERGY CENTER 138KV' | 110 | 0.00022 | -0.10048 | 79.8072
WERE | 'PAWNEE 115KV' | 999 | -0.10026 | WERE | 'KNOLL 3 115 115KV' | 75 | -0.04301 | -0.05725 | 140.0704
WERE | 'RICE 115KV' | 999 | -0.10026 | WERE | 'KNOLL 3 115 115KV' | 75 | -0.04301 | -0.05725 | 140.0704
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | WICHITA - RENO 345KV
Limiting Facility: | NORTH AMERICAN PHILIPS JUNCTION (SOUTH) - WEST MCPHERSON 115KV CKT 2
Direction: | From->To
Line Outage: | EAST MCPHERSON - SUMMIT 230KV CKT 1
Flowgate: | 57374574382568725687312206WP
Date Redispatch Needed: | 12/1/06 - 4/1/07
Season Flowgate Identified: | 2006 Winter Peak
Reservation | Relief Amount | Aggregate Relief Amount
1090964 | 3.697 | 4.7534
1090965 | 1.0563 | 4.7534
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.27941 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01812 | -0.29753 | 16
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.27941 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01883 | -0.29824 | 16
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.27941 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 130.0238 | 0.01183 | -0.29124 | 16
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.27941 | WERE | 'CHANUTE 69KV' | 35.344 | 0.00165 | -0.28106 | 17
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.27941 | WERE | 'CITY OF AUGUSTA 69KV' | 17.252 | 0.00051 | -0.27992 | 17
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.27941 | WERE | 'CITY OF IOLA 69KV' | 13.978 | 0.00191 | -0.28132 | 17
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.27941 | WERE | 'CITY OF WELLINGTON 69KV' | 24 | -0.00148 | -0.27793 | 17
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.27941 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.00306 | -0.28247 | 17
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.27941 | WERE | 'EVANS ENERGY CENTER 138KV' | 25.8875 | 0.00037 | -0.27978 | 17
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.27941 | WERE | 'WACO 138KV' | 17.953 | -0.00261 | -0.2768 | 17
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.2263 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01812 | -0.24442 | 19
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.2263 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01883 | -0.24513 | 19
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.2262 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01812 | -0.24432 | 19
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.2262 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01883 | -0.24503 | 19
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.2263 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 130.0238 | 0.01183 | -0.23813 | 20
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.2262 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 130.0238 | 0.01183 | -0.23803 | 20
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.2263 | WERE | 'CHANUTE 69KV' | 35.344 | 0.00165 | -0.22795 | 21
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.2263 | WERE | 'CITY OF AUGUSTA 69KV' | 17.252 | 0.00051 | -0.22681 | 21
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.2263 | WERE | 'CITY OF IOLA 69KV' | 13.978 | 0.00191 | -0.22821 | 21
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.2263 | WERE | 'CITY OF WELLINGTON 69KV' | 24 | -0.00148 | -0.22482 | 21
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.2263 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.00306 | -0.22936 | 21
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.2263 | WERE | 'EVANS ENERGY CENTER 138KV' | 25.8875 | 0.00037 | -0.22667 | 21
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.2263 | WERE | 'WACO 138KV' | 17.953 | -0.00261 | -0.22369 | 21
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.2262 | WERE | 'CHANUTE 69KV' | 35.344 | 0.00165 | -0.22785 | 21
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.2262 | WERE | 'CITY OF AUGUSTA 69KV' | 17.252 | 0.00051 | -0.22671 | 21
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.2262 | WERE | 'CITY OF IOLA 69KV' | 13.978 | 0.00191 | -0.22811 | 21
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.2262 | WERE | 'CITY OF WELLINGTON 69KV' | 24 | -0.00148 | -0.22472 | 21
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.2262 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.00306 | -0.22926 | 21
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.2262 | WERE | 'EVANS ENERGY CENTER 138KV' | 25.8875 | 0.00037 | -0.22657 | 21
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.2262 | WERE | 'WACO 138KV' | 17.953 | -0.00261 | -0.22359 | 21
WERE | 'PAWNEE 115KV' | 999 | -0.13103 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01812 | -0.14915 | 32
WERE | 'PAWNEE 115KV' | 999 | -0.13103 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01883 | -0.14986 | 32
WERE | 'RICE 115KV' | 999 | -0.13103 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01812 | -0.14915 | 32
WERE | 'RICE 115KV' | 999 | -0.13103 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01883 | -0.14986 | 32
WERE | 'PAWNEE 115KV' | 999 | -0.13103 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 130.0238 | 0.01183 | -0.14286 | 33
WERE | 'RICE 115KV' | 999 | -0.13103 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 130.0238 | 0.01183 | -0.14286 | 33
WERE | 'PAWNEE 115KV' | 999 | -0.13103 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.00306 | -0.13409 | 35
WERE | 'RICE 115KV' | 999 | -0.13103 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.00306 | -0.13409 | 35
WERE | 'PAWNEE 115KV' | 999 | -0.13103 | WERE | 'CITY OF AUGUSTA 69KV' | 17.252 | 0.00051 | -0.13154 | 36
WERE | 'PAWNEE 115KV' | 999 | -0.13103 | WERE | 'EVANS ENERGY CENTER 138KV' | 25.8875 | 0.00037 | -0.1314 | 36
WERE | 'RICE 115KV' | 999 | -0.13103 | WERE | 'CITY OF AUGUSTA 69KV' | 17.252 | 0.00051 | -0.13154 | 36
WERE | 'RICE 115KV' | 999 | -0.13103 | WERE | 'EVANS ENERGY CENTER 138KV' | 25.8875 | 0.00037 | -0.1314 | 36
WERE | 'PAWNEE 115KV' | 999 | -0.13103 | WERE | 'CITY OF WELLINGTON 69KV' | 24 | -0.00148 | -0.12955 | 37
WERE | 'PAWNEE 115KV' | 999 | -0.13103 | WERE | 'WACO 138KV' | 17.953 | -0.00261 | -0.12842 | 37
WERE | 'RICE 115KV' | 999 | -0.13103 | WERE | 'CITY OF WELLINGTON 69KV' | 24 | -0.00148 | -0.12955 | 37
WERE | 'RICE 115KV' | 999 | -0.13103 | WERE | 'WACO 138KV' | 17.953 | -0.00261 | -0.12842 | 37
WEPL | 'A. M. MULLERGREN GENERATOR 115KV' | 63 | -0.1185 | WEPL | 'GRAY COUNTY WIND FARM 115KV' | 73 | -0.07534 | -0.04316 | 110
WERE | 'KNOLL 3 115 115KV' | 75 | -0.02141 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01883 | -0.04024 | 118
WERE | 'KNOLL 3 115 115KV' | 75 | -0.02141 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01812 | -0.03953 | 120
WERE | 'KNOLL 3 115 115KV' | 75 | -0.02141 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 130.0238 | 0.01183 | -0.03324 | 143
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | WICHITA - RENO 345KV
Limiting Facility: | NORTH AMERICAN PHILIPS JUNCTION (SOUTH) - WEST MCPHERSON 115KV CKT 2
Direction: | From->To
Line Outage: | EAST MCPHERSON - SUMMIT 230KV CKT 1
Flowgate: | 57374574382568725687312207WP
Date Redispatch Needed: | 12/1/07 - 4/1/08
Season Flowgate Identified: | 2007 Winter Peak
Reservation | Relief Amount | Aggregate Relief Amount
1090817 | 1.2916 | 3.5518
1090964 | 1.7221 | 3.5518
1090965 | 0.53815 | 3.5518
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.27078 | WERE | 'CLAY CENTER JUNCTION 115KV' | 6.7 | 0.04568 | -0.31646 | 11
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.27078 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01517 | -0.28595 | 12
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.27078 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01582 | -0.2866 | 12
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.27078 | WERE | 'CHANUTE 69KV' | 34.818 | 0.00141 | -0.27219 | 13
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.27078 | WERE | 'CITY OF AUGUSTA 69KV' | 14.628 | 0.00068 | -0.27146 | 13
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.27078 | WERE | 'CITY OF BURLINGTON 69KV' | 4.8 | 0.00255 | -0.27333 | 13
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.27078 | WERE | 'CITY OF IOLA 69KV' | 14.565 | 0.00161 | -0.27239 | 13
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.27078 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00124 | -0.26954 | 13
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.27078 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.95 | 0.00255 | -0.27333 | 13
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.27078 | WERE | 'EVANS ENERGY CENTER 138KV' | 55 | 0.00029 | -0.27107 | 13
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.27078 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 169.36 | 0.00973 | -0.28051 | 13
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.27078 | WERE | 'WACO 138KV' | 17.93 | -0.00225 | -0.26853 | 13
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.21442 | WERE | 'CLAY CENTER JUNCTION 115KV' | 6.7 | 0.04568 | -0.2601 | 14
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.21432 | WERE | 'CLAY CENTER JUNCTION 115KV' | 6.7 | 0.04568 | -0.26 | 14
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.27078 | WERE | 'COLBY 115KV' | 6.2479 | -0.04074 | -0.23004 | 15
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.21442 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01517 | -0.22959 | 15
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.21442 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01582 | -0.23024 | 15
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.21432 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01517 | -0.22949 | 15
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.21432 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01582 | -0.23014 | 15
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.21442 | WERE | 'CHANUTE 69KV' | 34.818 | 0.00141 | -0.21583 | 16
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.21442 | WERE | 'CITY OF IOLA 69KV' | 14.565 | 0.00161 | -0.21603 | 16
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.21442 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.95 | 0.00255 | -0.21697 | 16
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.21442 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 169.36 | 0.00973 | -0.22415 | 16
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.21432 | WERE | 'CHANUTE 69KV' | 34.818 | 0.00141 | -0.21573 | 16
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.21432 | WERE | 'CITY OF IOLA 69KV' | 14.565 | 0.00161 | -0.21593 | 16
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.21432 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.95 | 0.00255 | -0.21687 | 16
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.21432 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 169.36 | 0.00973 | -0.22405 | 16
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.21442 | WERE | 'CITY OF AUGUSTA 69KV' | 14.628 | 0.00068 | -0.2151 | 17
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.21442 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00124 | -0.21318 | 17
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.21442 | WERE | 'EVANS ENERGY CENTER 138KV' | 55 | 0.00029 | -0.21471 | 17
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.21442 | WERE | 'WACO 138KV' | 17.93 | -0.00225 | -0.21217 | 17
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.21432 | WERE | 'CITY OF AUGUSTA 69KV' | 14.628 | 0.00068 | -0.215 | 17
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.21432 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00124 | -0.21308 | 17
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.21432 | WERE | 'EVANS ENERGY CENTER 138KV' | 55 | 0.00029 | -0.21461 | 17
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.21432 | WERE | 'WACO 138KV' | 17.93 | -0.00225 | -0.21207 | 17
WERE | 'PAWNEE 115KV' | 999 | -0.11532 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01517 | -0.13049 | 27
WERE | 'PAWNEE 115KV' | 999 | -0.11532 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01582 | -0.13114 | 27
WERE | 'RICE 115KV' | 999 | -0.11532 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01517 | -0.13049 | 27
WERE | 'RICE 115KV' | 999 | -0.11532 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01582 | -0.13114 | 27
WERE | 'PAWNEE 115KV' | 999 | -0.11532 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 169.36 | 0.00973 | -0.12505 | 28
WERE | 'RICE 115KV' | 999 | -0.11532 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 169.36 | 0.00973 | -0.12505 | 28
WERE | 'PAWNEE 115KV' | 999 | -0.11532 | WERE | 'CHANUTE 69KV' | 34.818 | 0.00141 | -0.11673 | 30
WERE | 'PAWNEE 115KV' | 999 | -0.11532 | WERE | 'CITY OF IOLA 69KV' | 14.565 | 0.00161 | -0.11693 | 30
WERE | 'PAWNEE 115KV' | 999 | -0.11532 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.95 | 0.00255 | -0.11787 | 30
WERE | 'RICE 115KV' | 999 | -0.11532 | WERE | 'CHANUTE 69KV' | 34.818 | 0.00141 | -0.11673 | 30
WERE | 'RICE 115KV' | 999 | -0.11532 | WERE | 'CITY OF IOLA 69KV' | 14.565 | 0.00161 | -0.11693 | 30
WERE | 'RICE 115KV' | 999 | -0.11532 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.95 | 0.00255 | -0.11787 | 30
WERE | 'PAWNEE 115KV' | 999 | -0.11532 | WERE | 'CITY OF AUGUSTA 69KV' | 14.628 | 0.00068 | -0.116 | 31
WERE | 'PAWNEE 115KV' | 999 | -0.11532 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00124 | -0.11408 | 31
WERE | 'PAWNEE 115KV' | 999 | -0.11532 | WERE | 'EVANS ENERGY CENTER 138KV' | 55 | 0.00029 | -0.11561 | 31
WERE | 'PAWNEE 115KV' | 999 | -0.11532 | WERE | 'WACO 138KV' | 17.93 | -0.00225 | -0.11307 | 31
WERE | 'RICE 115KV' | 999 | -0.11532 | WERE | 'CITY OF AUGUSTA 69KV' | 14.628 | 0.00068 | -0.116 | 31
WERE | 'RICE 115KV' | 999 | -0.11532 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00124 | -0.11408 | 31
WERE | 'RICE 115KV' | 999 | -0.11532 | WERE | 'EVANS ENERGY CENTER 138KV' | 55 | 0.00029 | -0.11561 | 31
WERE | 'RICE 115KV' | 999 | -0.11532 | WERE | 'WACO 138KV' | 17.93 | -0.00225 | -0.11307 | 31
WERE | 'KNOLL 3 115 115KV' | 75 | -0.04955 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01582 | -0.06537 | 54
WERE | 'KNOLL 3 115 115KV' | 75 | -0.04955 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01517 | -0.06472 | 55
WERE | 'KNOLL 3 115 115KV' | 75 | -0.04955 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 169.36 | 0.00973 | -0.05928 | 60
WERE | 'KNOLL 3 115 115KV' | 75 | -0.04955 | WERE | 'EVANS ENERGY CENTER 138KV' | 55 | 0.00029 | -0.04984 | 71
WEPL | 'A. M. MULLERGREN GENERATOR 115KV' | 63 | -0.09475 | WEPL | 'GRAY COUNTY WIND FARM 115KV' | 60 | -0.06181 | -0.03294 | 108
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | YOAKUM COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 1 Displacement
Limiting Facility: | YOAKUM COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 1
Direction: | To->From
Line Outage: | MUSTANG STATION 230/115KV TRANSFORMER CKT 1
Flowgate: | 51890518911519695196611107SP
Date Redispatch Needed: | 6/1/07 - 10/1/07
Season Flowgate Identified: | 2007 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1090487 | 22.8133 | 22.8133
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
SPS | 'MADOX 115KV' | 75 | -0.06195 | SPS | 'MUSTG5 118.0 230KV' | 360 | 0.15538 | -0.21733 | 105
SPS | 'CUNNINGHAM 115KV' | 50.0098 | -0.06007 | SPS | 'MUSTG5 118.0 230KV' | 360 | 0.15538 | -0.21545 | 106
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor

## Table 7
Transmission Owner | Upgrade | Solution | Deferred Group | Assigned Upgrade E & C | Date Upgrade needed per AG study. | Date Upgrade Needed per Expansion Plan | Expansion Plan E & C Cost
OKGE | CONTINENTAL BLACKS - OSAGE 69KV CKT 1 Deferred | Rebuild & Reconductor 0.57 Miles of 477AS33 to 477 ACCC/TW | 1 | 0 | 2016-06-01 | 2016-06-01 | 200000
OKGE | Sooner to Rose Hill 345 kV OKGE | New 345 kV line from Sooner to Oklahoma/Kansas | 1 | 27500000 | 2016-06-01
WERE | Sooner to Rose Hill 345 kV WERE | New 345 kV line from Oklahoma/Kansas Stateline to Rose Hill | 1 | 27500000 | 2016-06-01
Note: Within a deferral group, the expansion plan upgrade(s) that were deferred as a result of a requested upgrade are so noted.