## Table 1
Customer | Study Number | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date without interim redispatch | Deferred Stop Date without interim redispatch | Start Date with interim redispatch | Stop Date with interim redispatch |  | Mimimum Allocated ATC (MW) within reservation period | Season of Minimum Allocated ATC within reservation period
AECC | AG3-2006-001 | 1161209 | CSWS | CSWS | 70 | 2011-06-01 | 2031-06-01 | [5 empty] | 0 | 12SP
AEPM | AG3-2006-039 | 1158760 | CSWS | CSWS | 160 | 2007-07-01 | 2012-07-01 | 2011-06-01 | 2016-06-01 | 2008-06-01 | 2013-06-01 | 2 | 0 | 12SP
AEPM | AG3-2006-040 | 1158761 | CSWS | CSWS | 160 | 2007-11-01 | 2012-11-01 | 2011-06-01 | 2016-06-01 | 2008-06-01 | 2013-06-01 | 2 | 0 | 12SP
AEPM | AG3-2006-044 | 1162214 | CSWS | CSWS | 455 | 2011-06-01 | 2031-06-01 | [5 empty] | 0 | 12SP
AEPM | AG3-2006-094 | 1163062 | CSWS | CSWS | 550 | 2010-06-01 | 2015-06-01 | [5 empty] | 0 | 12SP
NTEC | AG3-2006-035 | 1161974 | CSWS | CSWS | 52 | 2011-06-01 | 2031-06-01 | [5 empty] | 0 | 12SP
OMPA | AG3-2006-028 | 1159596 | CSWS | CSWS | 41 | 2011-06-01 | 2031-06-01 | [5 empty] | 0 | 12SP
1488
Note 1: Disregard Redispatch shown in Table 6 for limitations identified earlier than the start date with redispatch with the exception of limitations identified in the 2007 Summer Shoulder, and 2007 Fall Peak
Note 2: Start and Stop Dates with interim redispatch are determined based on customers choosing option to pursue redispatch to start service at Requested Start and Stop Dates or earliest date possible.

## Table 2
Customer | Study Number | Reservation | Engineering and Construction Cost of Upgrades Allocated to Customer for Revenue Requirements | 1Letter of Credit Amount Required | 2Potential Base Plan Engineering and Construction Funding Allowable | Notes | 4Additional Engineering and Construction Cost for 3rd Party Upgrades | 3 Total Revenue Requirements for Assigned Upgrades over term of reservation without potential base plan funding allocation | 3 5 Total Revenue Requirements for Assigned Upgrades over term of reservation WITH potential base plan funding allocation | Point-to-Point Base Rate over reservation period | 4Total Cost of Reservation Assignable to Customer contingent upon base plan funding
AECC | AG3-2006-001 | 1161209 | 28413543.6618 | 0 | 28413543.6618 |  | Indeterminate | 93671667.9857 | 0 | 0 | Schedule 9 charges
AEPM | AG3-2006-039 | 1158760 | 13335822.5559 | 0 | 13335822.5559 |  |  | 22803021.8427 | 0 | 0 | Schedule 9 charges
AEPM | AG3-2006-040 | 1158761 | 13335822.5559 | 0 | 13335822.5559 |  |  | 22803021.8427 | 0 | 0 | Schedule 9 charges
AEPM | AG3-2006-044 | 1162214 | 104319779.6885 | 0 | 104319779.6885 |  | Indeterminate | 366609201.062 | 0 | 0 | Schedule 9 charges
AEPM | AG3-2006-094 | 1163062 | 49966693.3666 | 0 | 49966693.3666 |  | Indeterminate | 95541059.4914 | 0 | 0 | Schedule 9 charges
NTEC | AG3-2006-035 | 1161974 | 10606764.0002 | 1246764.0002 | 9360000 |  |  | 36052653.3742 | 4237781.7026 | 0 | 4237781.7026
OMPA | AG3-2006-028 | 1159596 | 16416663.6495 | 0 | 16416663.6495 |  | Indeterminate | 55648248.8897 | 0 | 0 | Schedule 9 charges
Totals |  |  | 236395089.4784 |  |  |  |  | 693128874.4883 | 4237781.7026
Note 1: Letter of Credit required for financial security for transmission owner for network upgrades is determined by allocated engineering and construction costs less engineering and construction costs for upgrades when network customer is the transmission owner less the E & C allocation of expedited projects. Letter of Credit is not required for base plan funded upgrades. The LOC listed is based on meeting OATT Attachment J requirements for base plan funding.
Note 2. If potential base plan funding is applicable, this value is the lesser of the Engineering and Construction costs of assignable upgrades or the value of base plan funding calculated pursuant to Attachment J, Section III B criteria. Allocation of base plan funding is contingent upon verification of customer agreements meeting Attachment J, Section II B criteria. Not applicable if PTP base rate exceeds revenue requirements.
Note 3: Revenue Requirements (RR) are based upon deferred end dates if applicable. Deferred dates are based upon customer's choice to pursue redispatch. Achievable Base Plan Avoided RR in the case of a Base Plan upgrade being displaced or deferred by an earlier in service date for a Requested Upgrade shall be determined per Attachment J, Section VII.C methodology. Assumption of a 40 year service life is utilized for Base Plan funded projects. A present worth analysis of RR on a common year basis between the Base Plan and Requested Upgrades was performed to determine avoided Base Plan RR due to the displacement or deferral of the Base Plan upgrade by the Requested Upgrade. The incremental increase in present worth of a Requested Upgrade on a common year basis as a Base Plan upgrade is assigned to the transmission requests impacting the upgrade based on the displacement or deferral. If the displacement analysis results in lower RR due to the shorter amortization period of the requested upgrade when compared to a base plan amortization period, then no direct assignment of the upgrade cost is made due to the displacement to an earlier start date.
Note 4. For PTP requests, total cost is based on the higher of the base rate or assigned upgrade revenue requirements. For Network requests, the total cost is based on the assigned upgrade revenue requirement. Allocation of base plan funding will be determined after verification of designated resource meeting Attachment J, Section II B Criteria. Additionally E & C of 3rd Party upgrades is assignable to Customer. This includes prepayments required for any SWPA upgrades. Revenue requirements for 3rd Party facilities are not calculated. Total cost to customer is based on assumption of Revenue Requirements with confirmation of base plan funding. Customer is responsible for negotiating redispatch costs if applicable. Customer is also responsible to pay credits for previously assigned upgrades that are impacted by their request. Credits can be paid from base plan funding if applicable.
Note 5: RR with base plan funding may increase or decrease even if no base plan funding is applicable to a particular request if another request that shares the upgrade is now full base plan funded resulting in a different amortization period for the upgrade and thus different RR.
Note on E1: jbr0903: Equated to allocated E & C less upgrades where TO = CUST less base plan funding

## Table3
Customer | Study Number
AECC | AG3-2006-001
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AECC | 1161209 | CSWS | CSWS | 70 | 2011-06-01 | 1931-06-01 |  |  | 28413544 | 0 | 28413544 | 93671667.9703
[9 empty] | 28413544 | 0 | 28413544 | 93671667.9703
Reservation | Upgrade Name | COD | EOC | Earliest Service Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1161209 | ARDMORE - ROCKY POINT 69KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 149920 | 1627500 | 632268.69
| DILLARD4 - HEALDTON TAP 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 27959 | 300000 | 117913.55
| DYESS - ELM SPRINGS REC 161KV CKT 1 #1 | 2008-06-01 | 2008-06-01 |  |  | 5302 | 100000 | 21828.21
| DYESS - ELM SPRINGS REC 161KV CKT 1 #2 | 2010-06-01 | 2010-06-01 |  |  | 253074 | 4800000 | 923407.3
| DYESS - TONTITOWN 161KV CKT 1 | 2010-06-01 | 2010-06-01 |  |  | 60318 | 500000 | 227821.86
| FT SMITH 500 (FTSMITH3) 500/161/13.8KV TRANSFORMER CKT 3 | 2017-06-01 | 2017-06-01 |  |  | 7212152 | 9750000 | 19466602.71
| FULTON - HOPE 115KV CKT 1 AECC | 2011-06-01 | 2011-06-01 |  |  | 252732 | 2090000 | 750984.31
| HEMPSTEAD - HOPE 115KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 1085764 | 9000000 | 3726661.86
| HEMPSTEAD - NW TEXARKANA 345KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 6181819 | 57530000 | 21785206.47
| Hugo - SunnySide 345kV OKGE | 2008-04-01 | 2011-06-01 |  |  | 4681683 | 66000000 | 19744407.48
| Hugo - SunnySide 345kV WFEC | 2008-04-01 | 2011-06-01 |  |  | 3192057 | 45000000 | 7676835.3003
| MAGAZINE REC - NORTH MAGAZINE 161KV CKT 1 # 2 | 2012-06-01 | 2012-06-01 |  |  | 14665 | 100000 | 48472.66
| OKAY - TOLLETTE 69KV CKT 1 Displacement | 2011-06-01 | 2011-06-01 |  |  | 2081 | 19364 | 7141.44
| SE TEXARKANA - TEXARKANA PLANT 69KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 4359 | 35000 | 15163.01
| SOUTH TEXARKANA REC - TEXARKANA PLANT 69KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 4750000 | 4750000 | 16304653.49
| SUNNYSIDE - UNIROYAL 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 3584 | 40000 | 15394.39
| SUNNYSIDE (SUNNYSD3) 345/138/13.8KV TRANSFORMER CKT 1 | 2008-04-01 | 2011-06-01 |  |  | 461075 | 6500000 | 2001599.43
| VBI - VBI NORTH 69KV CKT 1 | 2017-06-01 | 2017-06-01 |  |  | 75000 | 75000 | 205305.81
[5 empty] | Total | 28413544 | 208216864 | 93671667.9703
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Date | Redispatch Available
1161209 | 412SUB - KANSAS TAP 161KV CKT 1 | 2012-06-01 | 2012-06-01
| 412SUB - KERR 161KV CKT 1 | 2012-06-01 | 2012-06-01
| BONANZA - BONANZA TAP 161KV CKT 1 | 2011-06-01 | 2011-06-01
| BONANZA - EXCELSIOR 161KV CKT 1 | 2014-06-01 | 2014-06-01
| BULL SHOALS - BULL SHOALS 161KV CKT 1 | 2012-06-01 | 2012-06-01
| CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | 2017-06-01 | 2017-06-01
| CLARKSVILLE - DARDANELLE 161KV CKT 1 | 2012-06-01 | 2012-06-01
| DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 AEPW | 2011-06-01 | 2011-06-01
| DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 OKGE | 2012-06-01 | 2011-06-01
| DARDANELLE - RUSSELLVILLE SOUTH 161KV CKT 1 SWPA | 2012-06-01 | 2012-06-01
| Device - Cox Cap | 2013-06-01 | 2013-06-01
| Device - Main Cap | 2013-06-01 | 2013-06-01
| Device - Mill Cap | 2013-06-01 | 2013-06-01
| Device - Norton Cap | 2013-06-01 | 2013-06-01
| EAST CENTERTON - FLINT CREEK 161 KV CKT 1 | 2014-06-01 | 2014-06-01
| ELM SPRINGS REC - TONTITOWN 161KV CKT 1 | 2016-06-01 | 2016-06-01
| FLINT CREEK - GENTRY REC 161KV CKT 1 | 2017-06-01 | 2017-06-01
| KANSAS TAP - WEST SILOAM SPRINGS 161KV CKT 1 | 2012-06-01 | 2012-06-01
| MAGAZINE REC - NORTH MAGAZINE 161KV CKT 1 AEPW | 2012-06-01 | 2011-06-01
| MAGAZINE REC - NORTH MAGAZINE 161KV CKT 1 OKGE | 2012-06-01 | 2011-06-01
| MUSKOGEE - PECAN CREEK 345KV CKT 1 | 2012-06-01 | 2012-06-01
| SILOAM CITY - WEST SILOAM SPRINGS 161KV CKT 1 | 2012-06-01 | 2012-06-01
| SUB 124 - AURORA H.T. 161KV | 2014-06-01 | 2014-06-01
| SUB 438 - RIVERSIDE 161KV | 2014-06-01 | 2014-06-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Date | Redispatch Available
1161209 | Device - Sunset | 2013-06-01 | 2013-06-01
Third Party Limitations.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost
1161209 | ARKANSAS NUCLEAR ONE 161 - RUSSELLVILLE NORTH 161KV CKT 1 | 2012-06-01 | 2012-06-01 |  |  | 0 | 0
| DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 ENTR | 2012-06-01 | 2011-06-01 |  |  | 0 | 0
| MAGAZINE REC - NORTH MAGAZINE 161KV CKT 1 ENTR | 2012-06-01 | 2011-06-01 |  |  | 0 | 0
| RUSSELLVILLE EAST - RUSSELLVILLE NORTH 161KV CKT 1 | 2012-06-01 | 2012-06-01 |  |  | 0 | 0
| RUSSELLVILLE EAST - RUSSELLVILLE SOUTH 161KV CKT 1 | 2012-06-01 | 2012-06-01 |  |  | 0 | 0
[5 empty] | Total | 0 | 0
Customer | Study Number
AEPM | AG3-2006-039
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AEPM | 1158760 | CSWS | CSWS | 160 | 2007-07-01 | 2012-07-01 | 2011-06-01 | 2016-06-01 | 13335823 | 0 | 13335822 | 22803021.8413
[9 empty] | 13335823 | 0 | 13335822 | 22803021.8413
Reservation | Upgrade Name | COD | EOC | Earliest Service Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1158760 | ARSENAL HILL - FORT HUMBUG 138KV CKT 1 Displacement | 2010-06-01 | 2010-06-01 |  |  | 27603 | 1782291 | 38246.07
| ARSENAL HILL - MCWILLIE STREET 138KV CKT 1 Displacement | 2010-06-01 | 2010-06-01 |  |  | 508 | 32833 | 729.96
| AVOCA - EAST ROGERS 161KV CKT 1 | 2008-06-01 | 2008-06-01 |  |  | 450000 | 900000 | 728444.55
| DYESS - EAST ROGERS 161KV CKT 1 | 2008-06-01 | 2008-06-01 |  |  | 230950 | 461900 | 373853.93
| DYESS - ELM SPRINGS REC 161KV CKT 1 #1 | 2008-06-01 | 2008-06-01 |  |  | 47349 | 100000 | 91041.48
| DYESS - ELM SPRINGS REC 161KV CKT 1 #2 | 2010-06-01 | 2010-06-01 |  |  | 2273463 | 4800000 | 3874214.7
| DYESS - TONTITOWN 161KV CKT 1 | 2010-06-01 | 2010-06-01 |  |  | 219841 | 500000 | 387799.43
| Hugo - SunnySide 345kV OKGE | 2008-04-01 | 2011-06-01 |  | Yes | 4491629 | 66000000 | 8227763.24
| Hugo - SunnySide 345kV WFEC | 2008-04-01 | 2011-06-01 |  | Yes | 3062474 | 45000000 | 4821605.9713
| LAWTON EASTSIDE (LES 4) 345/138/13.8KV TRANSFORMER CKT 1 | 2012-12-01 | 2012-12-01 |  |  | 435803 | 4560000 | 636467.58
| LINWOOD - MCWILLIE STREET 138KV CKT 1 #2 | 2009-06-01 | 2009-06-01 |  |  | 62500 | 125000 | 95682
| LINWOOD - POWELL STREET 138KV CKT 1 | 2012-06-01 | 2012-06-01 |  |  | 94930 | 456000 | 143035.24
| LONGWOOD (LONGWOOD) 345/138/13.2KV TRANSFORMER CKT 1 | 2008-06-01 | 2010-06-01 |  | Yes | 1496415 | 5700000 | 2550045.02
| SUNNYSIDE (SUNNYSD3) 345/138/13.8KV TRANSFORMER CKT 1 | 2008-04-01 | 2011-06-01 |  | Yes | 442357 | 6500000 | 834092.67
[5 empty] | Total | 13335822 | 136918024 | 22803021.8413
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Date | Redispatch Available
1158760 | FULTON - HOPE 115KV CKT 1 AEPW | 2012-06-01 | 2012-06-01
| LIEBERMAN - LONGWOOD 138KV CKT 1 | 2008-06-01 | 2010-06-01 |  | Yes
| LIEBERMAN - NORTH BENTON 138KV CKT 1 | 2010-06-01 | 2010-06-01
| LINWOOD - MCWILLIE STREET 138KV CKT 1 #1 | 2008-04-01 | 2008-06-01 |  | Yes
| SOUTHWEST SHREVEPORT - SOUTHWEST SHREVEPORT TAP 138KV CKT 1 | 2008-06-01 | 2010-06-01 |  | Yes
| SOUTHWEST SHREVEPORT (SW SHV 1) 345/138/13.8KV TRANSFORMER CKT 1 | 2008-04-01 | 2009-06-01 |  | Yes
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Date | Redispatch Available
1158760 | HUGO POWER PLANT - VALLIANT 345 KV AEPW | 2010-05-01 | 2010-05-01
| HUGO POWER PLANT - VALLIANT 345 KV WFEC | 2010-05-01 | 2010-05-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Date | Redispatch Available
1158760 | ALUMAX TAP - NORTHWEST TEXARKANA 138KV CKT 1 | 2008-04-01 | 2008-06-01 |  | Yes
| BANN - NW TEXARKANA-BANN T 138KV CKT 1 | 2008-04-01 | 2008-06-01 |  | Yes
| SOUTHWEST SHREVEPORT (SW SHV 1) 345/138/13.8KV TRANSFORMER CKT 2 | 2008-04-01 | 2009-06-01 |  | Yes
Customer | Study Number
AEPM | AG3-2006-040
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AEPM | 1158761 | CSWS | CSWS | 160 | 2007-11-01 | 2012-11-01 | 2011-06-01 | 2016-06-01 | 13335823 | 0 | 13335822 | 22803021.8413
[9 empty] | 13335823 | 0 | 13335822 | 22803021.8413
Reservation | Upgrade Name | COD | EOC | Earliest Service Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1158761 | ARSENAL HILL - FORT HUMBUG 138KV CKT 1 Displacement | 2010-06-01 | 2010-06-01 |  |  | 27603 | 1782291 | 38246.07
| ARSENAL HILL - MCWILLIE STREET 138KV CKT 1 Displacement | 2010-06-01 | 2010-06-01 |  |  | 508 | 32833 | 729.96
| AVOCA - EAST ROGERS 161KV CKT 1 | 2008-06-01 | 2008-06-01 |  |  | 450000 | 900000 | 728444.55
| DYESS - EAST ROGERS 161KV CKT 1 | 2008-06-01 | 2008-06-01 |  |  | 230950 | 461900 | 373853.93
| DYESS - ELM SPRINGS REC 161KV CKT 1 #1 | 2008-06-01 | 2008-06-01 |  |  | 47349 | 100000 | 91041.48
| DYESS - ELM SPRINGS REC 161KV CKT 1 #2 | 2010-06-01 | 2010-06-01 |  |  | 2273463 | 4800000 | 3874214.7
| DYESS - TONTITOWN 161KV CKT 1 | 2010-06-01 | 2010-06-01 |  |  | 219841 | 500000 | 387799.43
| Hugo - SunnySide 345kV OKGE | 2008-04-01 | 2011-06-01 |  | Yes | 4491629 | 66000000 | 8227763.24
| Hugo - SunnySide 345kV WFEC | 2008-04-01 | 2011-06-01 |  | Yes | 3062474 | 45000000 | 4821605.9713
| LAWTON EASTSIDE (LES 4) 345/138/13.8KV TRANSFORMER CKT 1 | 2012-12-01 | 2012-12-01 |  |  | 435803 | 4560000 | 636467.58
| LINWOOD - MCWILLIE STREET 138KV CKT 1 #2 | 2009-06-01 | 2009-06-01 |  |  | 62500 | 125000 | 95682
| LINWOOD - POWELL STREET 138KV CKT 1 | 2012-06-01 | 2012-06-01 |  |  | 94930 | 456000 | 143035.24
| LONGWOOD (LONGWOOD) 345/138/13.2KV TRANSFORMER CKT 1 | 2008-06-01 | 2010-06-01 |  | Yes | 1496415 | 5700000 | 2550045.02
| SUNNYSIDE (SUNNYSD3) 345/138/13.8KV TRANSFORMER CKT 1 | 2008-04-01 | 2011-06-01 |  | Yes | 442357 | 6500000 | 834092.67
[5 empty] | Total | 13335822 | 136918024 | 22803021.8413
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Date | Redispatch Available
1158761 | FULTON - HOPE 115KV CKT 1 AEPW | 2012-06-01 | 2012-06-01
| LIEBERMAN - LONGWOOD 138KV CKT 1 | 2008-06-01 | 2010-06-01 |  | Yes
| LIEBERMAN - NORTH BENTON 138KV CKT 1 | 2010-06-01 | 2010-06-01
| LINWOOD - MCWILLIE STREET 138KV CKT 1 #1 | 2008-04-01 | 2008-06-01 |  | Yes
| SOUTHWEST SHREVEPORT - SOUTHWEST SHREVEPORT TAP 138KV CKT 1 | 2008-06-01 | 2010-06-01 |  | Yes
| SOUTHWEST SHREVEPORT (SW SHV 1) 345/138/13.8KV TRANSFORMER CKT 1 | 2008-04-01 | 2009-06-01 |  | Yes
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Date | Redispatch Available
1158761 | HUGO POWER PLANT - VALLIANT 345 KV AEPW | 2010-05-01 | 2010-05-01
| HUGO POWER PLANT - VALLIANT 345 KV WFEC | 2010-05-01 | 2010-05-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Date | Redispatch Available
1158761 | ALUMAX TAP - NORTHWEST TEXARKANA 138KV CKT 1 | 2008-04-01 | 2008-06-01 |  | Yes
| BANN - NW TEXARKANA-BANN T 138KV CKT 1 | 2008-04-01 | 2008-06-01 |  | Yes
| SOUTHWEST SHREVEPORT (SW SHV 1) 345/138/13.8KV TRANSFORMER CKT 2 | 2008-04-01 | 2009-06-01 |  | Yes
Customer | Study Number
AEPM | AG3-2006-044
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AEPM | 1162214 | CSWS | CSWS | 455 | 2011-06-01 | 1931-06-01 |  |  | 104319780 | 0 | 104319780 | 366609201.0584
[9 empty] | 104319780 | 0 | 104319780 | 366609201.0584
Reservation | Upgrade Name | COD | EOC | Earliest Service Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1162214 | ARDMORE - ROCKY POINT 69KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 764916 | 1627500 | 3225936.73
| DILLARD4 - HEALDTON TAP 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 141602 | 300000 | 597188.56
| FULTON - HOPE 115KV CKT 1 AECC | 2011-06-01 | 2011-06-01 |  |  | 1540361 | 2090000 | 4577128.93
| HEMPSTEAD - HOPE 115KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 6711928 | 9000000 | 23037313.89
| HEMPSTEAD - NW TEXARKANA 345KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 42406792 | 57530000 | 149444802.48
| Hugo - SunnySide 345kV OKGE | 2008-04-01 | 2011-06-01 |  |  | 27293577 | 66000000 | 115107218.07
| Hugo - SunnySide 345kV WFEC | 2008-04-01 | 2011-06-01 |  |  | 18609257 | 45000000 | 44754902.8884
| LAWTON EASTSIDE (LES 4) 345/138/13.8KV TRANSFORMER CKT 1 | 2012-12-01 | 2012-12-01 |  |  | 1701079 | 4560000 | 5319374.13
| LINWOOD - POWELL STREET 138KV CKT 1 | 2012-06-01 | 2012-06-01 |  |  | 266140 | 456000 | 858617.43
| LONGWOOD (LONGWOOD) 345/138/13.2KV TRANSFORMER CKT 1 | 2008-06-01 | 2010-06-01 |  |  | 2136789 | 5700000 | 7796638.82
| OKAY - TOLLETTE 69KV CKT 1 Displacement | 2011-06-01 | 2011-06-01 |  |  | 14274 | 19364 | 48991.5
| SE TEXARKANA - TEXARKANA PLANT 69KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 26340 | 35000 | 91625.05
| SUNNYSIDE - UNIROYAL 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 18721 | 40000 | 80412.5
| SUNNYSIDE (SUNNYSD3) 345/138/13.8KV TRANSFORMER CKT 1 | 2008-04-01 | 2011-06-01 |  |  | 2688004 | 6500000 | 11669050.08
[5 empty] | Total | 104319780 | 198857864 | 366609201.0584
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Date | Redispatch Available
1162214 | BONANZA - EXCELSIOR 161KV CKT 1 | 2014-06-01 | 2014-06-01
| DARDANELLE - RUSSELLVILLE SOUTH 161KV CKT 1 SWPA | 2012-06-01 | 2012-06-01
| LONGWOOD - OAK PAN-HARR REC 138KV CKT 1 | 2017-06-01 | 2017-06-01
| MUSKOGEE - PECAN CREEK 345KV CKT 1 | 2012-06-01 | 2012-06-01
| SOUTHWEST SHREVEPORT - WESTERN ELECTRIC T 138KV CKT 1 | 2017-06-01 | 2017-06-01
| SUB 124 - AURORA H.T. 161KV | 2014-06-01 | 2014-06-01
| SUB 438 - RIVERSIDE 161KV | 2014-06-01 | 2014-06-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Date | Redispatch Available
1162214 | SOUTHWEST SHREVEPORT (SW SHV 1) 345/138/13.8KV TRANSFORMER CKT 2 | 2008-04-01 | 2009-06-01
Third Party Limitations.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost
1162214 | ARKANSAS NUCLEAR ONE 161 - RUSSELLVILLE NORTH 161KV CKT 1 | 2012-06-01 | 2012-06-01 |  |  | 0 | 0
| RUSSELLVILLE EAST - RUSSELLVILLE NORTH 161KV CKT 1 | 2012-06-01 | 2012-06-01 |  |  | 0 | 0
| RUSSELLVILLE EAST - RUSSELLVILLE SOUTH 161KV CKT 1 | 2012-06-01 | 2012-06-01 |  |  | 0 | 0
[5 empty] | Total | 0 | 0
Customer | Study Number
AEPM | AG3-2006-094
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AEPM | 1163062 | CSWS | CSWS | 550 | 2010-06-01 | 2015-06-01 |  |  | 49966693 | 0 | 49966693 | 95541059.4871
[9 empty] | 49966693 | 0 | 49966693 | 95541059.4871
Reservation | Upgrade Name | COD | EOC | Earliest Service Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1163062 | ARDMORE - ROCKY POINT 69KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 565829 | 1627500 | 1244659.39
| ARSENAL HILL - FORT HUMBUG 138KV CKT 1 Displacement | 2010-06-01 | 2010-06-01 |  |  | 1727085 | 1782291 | 2821470.03
| ARSENAL HILL - MCWILLIE STREET 138KV CKT 1 Displacement | 2010-06-01 | 2010-06-01 |  |  | 31816 | 32833 | 53840.96
| ARSENAL HILL - WATERWORKS 69KV CKT 1 | 2010-06-01 | 2010-06-01 |  |  | 3898800 | 3898800 | 6196458.81
| ARSENAL HILL (ARSHILL1) 138/69/12.47KV TRANSFORMER CKT 1 | 2010-06-01 | 2010-06-01 |  |  | 3005700 | 3005700 | 4777032.99
| ARSENAL HILL (ARSHILL2) 138/69/14.5KV TRANSFORMER CKT 2 | 2010-06-01 | 2010-06-01 |  |  | 3005700 | 3005700 | 4777032.99
| DILLARD4 - HEALDTON TAP 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 100335 | 300000 | 220707.84
| Hugo - SunnySide 345kV OKGE | 2008-04-01 | 2011-06-01 |  |  | 20173923 | 66000000 | 44376768.94
| Hugo - SunnySide 345kV WFEC | 2008-04-01 | 2011-06-01 |  |  | 13754948 | 45000000 | 23604974.7371
| LAWTON EASTSIDE (LES 4) 345/138/13.8KV TRANSFORMER CKT 1 | 2012-12-01 | 2012-12-01 |  |  | 1623622 | 4560000 | 2795771.49
| MAGAZINE REC - NORTH MAGAZINE 161KV CKT 1 # 2 | 2012-06-01 | 2012-06-01 |  |  | 77887 | 100000 | 141762.21
| SUNNYSIDE - UNIROYAL 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 14222 | 40000 | 31862.39
| SUNNYSIDE (SUNNYSD3) 345/138/13.8KV TRANSFORMER CKT 1 | 2008-04-01 | 2011-06-01 |  |  | 1986826 | 6500000 | 4498716.71
[5 empty] | Total | 49966693 | 135852824 | 95541059.4871
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Date | Redispatch Available
1163062 | ARSENAL HILL - NORTH MARKET 69KV CKT 1 | 2010-06-01 | 2010-06-01
| BONANZA - EXCELSIOR 161KV CKT 1 | 2014-06-01 | 2014-06-01
| CLARKSVILLE - DARDANELLE 161KV CKT 1 | 2012-06-01 | 2012-06-01
| DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 AEPW | 2011-06-01 | 2011-06-01
| DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 OKGE | 2012-06-01 | 2011-06-01
| DARDANELLE - RUSSELLVILLE SOUTH 161KV CKT 1 SWPA | 2012-06-01 | 2012-06-01
| LIEBERMAN - NORTH BENTON 138KV CKT 1 | 2010-06-01 | 2010-06-01
| MAGAZINE REC - NORTH MAGAZINE 161KV CKT 1 AEPW | 2012-06-01 | 2011-06-01
| MAGAZINE REC - NORTH MAGAZINE 161KV CKT 1 OKGE | 2012-06-01 | 2011-06-01
| MUSKOGEE - PECAN CREEK 345KV CKT 1 | 2012-06-01 | 2012-06-01
| PORT ROBSON - REDPOINT 138kV | 2012-06-01 | 2012-06-01
| SUB 124 - AURORA H.T. 161KV | 2014-06-01 | 2014-06-01
| SUB 438 - RIVERSIDE 161KV | 2014-06-01 | 2014-06-01
Third Party Limitations.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost
1163062 | ARKANSAS NUCLEAR ONE 161 - RUSSELLVILLE NORTH 161KV CKT 1 | 2012-06-01 | 2012-06-01 |  |  | 0 | 0
| DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 ENTR | 2012-06-01 | 2011-06-01 |  |  | 0 | 0
| MAGAZINE REC - NORTH MAGAZINE 161KV CKT 1 ENTR | 2012-06-01 | 2011-06-01 |  |  | 0 | 0
| RUSSELLVILLE EAST - RUSSELLVILLE NORTH 161KV CKT 1 | 2012-06-01 | 2012-06-01 |  |  | 0 | 0
| RUSSELLVILLE EAST - RUSSELLVILLE SOUTH 161KV CKT 1 | 2012-06-01 | 2012-06-01 |  |  | 0 | 0
[5 empty] | Total | 0 | 0
Customer | Study Number
NTEC | AG3-2006-035
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
NTEC | 1161974 | CSWS | CSWS | 52 | 2011-06-01 | 1931-06-01 |  |  | 9360000 | 0 | 10606764 | 36052653.374
[9 empty] | 9360000 | 0 | 10606764 | 36052653.374
Reservation | Upgrade Name | COD | EOC | Earliest Service Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1161974 | BANN - LONESTAR ORDINANCE TAP 69KV CKT 1 #2 | 2012-06-01 | 2012-06-01 |  |  | 4250000 | 4250000 | 13711295.02
| FULTON - HOPE 115KV CKT 1 AECC | 2011-06-01 | 2011-06-01 |  |  | 141961 | 2090000 | 421832.16
| HEMPSTEAD - HOPE 115KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 574865 | 9000000 | 1973106.01
| HEMPSTEAD - NW TEXARKANA 345KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 5065246 | 57530000 | 17850317.19
| LONGWOOD (LONGWOOD) 345/138/13.2KV TRANSFORMER CKT 1 | 2008-06-01 | 2010-06-01 |  |  | 570382 | 5700000 | 2081189.32
| OKAY - TOLLETTE 69KV CKT 1 Displacement | 2011-06-01 | 2011-06-01 |  |  | 1705 | 19364 | 5852.06
| SE TEXARKANA - TEXARKANA PLANT 69KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 2605 | 35000 | 9061.63
[5 empty] | Total | 10606764 | 78624364 | 36052653.37
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Date | Redispatch Available
1161974 | BANN - LONESTAR ORDINANCE TAP 69KV CKT 1 #1 | 2012-06-01 | 2012-06-01
| BIG SANDY - HAWKINS 69KV CKT 1 | 2014-06-01 | 2014-06-01
| BIG SANDY - PERDUE 69KV CKT 1 | 2014-06-01 | 2014-06-01
| CARTHAGE REC POD - ROCK HILL 138KV CKT 1 | 2017-06-01 | 2017-06-01
| FOREST HILLS REC - MAGNOLIA TAP 69KV CKT 1 | 2010-06-01 | 2010-06-01
| FOREST HILLS REC - QUITMAN 69KV CKT 1 | 2010-06-01 | 2010-06-01
| GEORGIA-PACIFIC - KEATCHIE REC 138KV CKT 1 | 2015-06-01 | 2015-06-01
| LONE STAR SOUTH - PITTSBURG 138KV CKT 1 | 2015-06-01 | 2015-06-01
| LONGWOOD - OAK PAN-HARR REC 138KV CKT 1 | 2017-06-01 | 2017-06-01
| MAGNOLIA TAP - WINNSBORO 69KV CKT 1 | 2010-06-01 | 2010-06-01
| NORTH MINEOLA - QUITMAN 69KV CKT 1 | 2016-06-01 | 2016-06-01
| SOUTHWEST SHREVEPORT - SOUTHWEST SHREVEPORT TAP 138KV CKT 1 | 2008-06-01 | 2010-06-01
| SOUTHWEST SHREVEPORT - WESTERN ELECTRIC T 138KV CKT 1 | 2017-06-01 | 2017-06-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Date | Redispatch Available
1161974 | SOUTHWEST SHREVEPORT (SW SHV 1) 345/138/13.8KV TRANSFORMER CKT 2 | 2008-04-01 | 2009-06-01
Customer | Study Number
OMPA | AG3-2006-028
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
OMPA | 1159596 | CSWS | CSWS | 41 | 2011-06-01 | 1931-06-01 |  |  | 16416664 | 0 | 16416664 | 55648248.9022
[9 empty] | 16416664 | 0 | 16416664 | 55648248.9022
Reservation | Upgrade Name | COD | EOC | Earliest Service Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1159596 | ARDMORE - ROCKY POINT 69KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 146834 | 1627500 | 619253.87
| DILLARD4 - HEALDTON TAP 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 30104 | 300000 | 126959.82
| FT SMITH 500 (FTSMITH3) 500/161/13.8KV TRANSFORMER CKT 3 | 2017-06-01 | 2017-06-01 |  |  | 2537848 | 9750000 | 6850005.21
| FULTON - HOPE 115KV CKT 1 AECC | 2011-06-01 | 2011-06-01 |  |  | 154945 | 2090000 | 460413.66
| HEMPSTEAD - HOPE 115KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 627443 | 9000000 | 2153569.19
| HEMPSTEAD - NW TEXARKANA 345KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 3876143 | 57530000 | 13659826.59
| Hugo - SunnySide 345kV OKGE | 2008-04-01 | 2011-06-01 |  |  | 4867559 | 66000000 | 20528316.07
| Hugo - SunnySide 345kV WFEC | 2008-04-01 | 2011-06-01 |  |  | 3318790 | 45000000 | 7981625.7122
| LAWTON EASTSIDE (LES 4) 345/138/13.8KV TRANSFORMER CKT 1 | 2012-12-01 | 2012-12-01 |  |  | 363694 | 4560000 | 1137292.54
| MAGAZINE REC - NORTH MAGAZINE 161KV CKT 1 # 2 | 2012-06-01 | 2012-06-01 |  |  | 7448 | 100000 | 24618.1
| OKAY - TOLLETTE 69KV CKT 1 Displacement | 2011-06-01 | 2011-06-01 |  |  | 1305 | 19364 | 4477.94
| SE TEXARKANA - TEXARKANA PLANT 69KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 1696 | 35000 | 5899.62
| SUNNYSIDE - UNIROYAL 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 3474 | 40000 | 14921.91
| SUNNYSIDE (SUNNYSD3) 345/138/13.8KV TRANSFORMER CKT 1 | 2008-04-01 | 2011-06-01 |  |  | 479381 | 6500000 | 2081068.67
[5 empty] | Total | 16416664 | 202551864 | 55648248.9022
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Date | Redispatch Available
1159596 | BONANZA - EXCELSIOR 161KV CKT 1 | 2014-06-01 | 2014-06-01
| BROWN - RUSSETT 138KV CKT 1 SWPA | 2011-06-01 | 2011-06-01
| BROWN - RUSSETT 138KV CKT 1 WFEC | 2011-06-01 | 2011-06-01
| CLARKSVILLE - DARDANELLE 161KV CKT 1 | 2012-06-01 | 2012-06-01
| DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 AEPW | 2011-06-01 | 2011-06-01
| DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 OKGE | 2012-06-01 | 2011-06-01
| DARDANELLE - RUSSELLVILLE SOUTH 161KV CKT 1 SWPA | 2012-06-01 | 2012-06-01
| MAGAZINE REC - NORTH MAGAZINE 161KV CKT 1 AEPW | 2012-06-01 | 2011-06-01
| MAGAZINE REC - NORTH MAGAZINE 161KV CKT 1 OKGE | 2012-06-01 | 2011-06-01
| MUSKOGEE - PECAN CREEK 345KV CKT 1 | 2012-06-01 | 2012-06-01
| RUSSETT - RUSSETT 138KV CKT 1 OKGE | 2012-12-01 | 2012-12-01
| RUSSETT - RUSSETT 138KV CKT 1 WFEC | 2012-12-01 | 2012-12-01
| SUB 124 - AURORA H.T. 161KV | 2014-06-01 | 2014-06-01
| SUB 438 - RIVERSIDE 161KV | 2014-06-01 | 2014-06-01
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Date | Redispatch Available
1159596 | LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01
Third Party Limitations.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost
1159596 | ARKANSAS NUCLEAR ONE 161 - RUSSELLVILLE NORTH 161KV CKT 1 | 2012-06-01 | 2012-06-01 |  |  | 0 | 0
| DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 ENTR | 2012-06-01 | 2011-06-01 |  |  | 0 | 0
| MAGAZINE REC - NORTH MAGAZINE 161KV CKT 1 ENTR | 2012-06-01 | 2011-06-01 |  |  | 0 | 0
| RUSSELLVILLE EAST - RUSSELLVILLE NORTH 161KV CKT 1 | 2012-06-01 | 2012-06-01 |  |  | 0 | 0
| RUSSELLVILLE EAST - RUSSELLVILLE SOUTH 161KV CKT 1 | 2012-06-01 | 2012-06-01 |  |  | 0 | 0
[5 empty] | Total | 0 | 0

## Table4
Transmission Owner | Upgrade | Solution | Earliest Data Upgrade Required (COD) | Estimated Date of Upgrade Completion (EOC) | Estimated Engineering & Construction Cost
AECC | FULTON - HOPE 115KV CKT 1 AECC | Upgrades to Fulton Switching Station, Reconductor the Fulton to Hope 115/138kV Line, Upgrades to McNab Substation | 2011-06-01 | 2011-06-01 | 2090000
AEPW | ARSENAL HILL - FORT HUMBUG 138KV CKT 1 Displacement | Rebuild 3.24 miles of 1272 AAC with 2156 ACSR. Replace 3 switches, breaker jumpers, and reset CTs @ Arsenal Hill. Replace 2 switches and jumpers @ Fort Humbug | 2010-06-01 | 2010-06-01 | 1782291
AEPW | ARSENAL HILL - MCWILLIE STREET 138KV CKT 1 Displacement | Replace Arsenal Hill switches and jumpers | 2010-06-01 | 2010-06-01 | 32833
AEPW | ARSENAL HILL - WATERWORKS 69KV CKT 1 | Rebuild 2.55 miles of 666 ACSR with 1272 ACSR | 2010-06-01 | 2010-06-01 | 3898800
AEPW | ARSENAL HILL (ARSHILL1) 138/69/12.47KV TRANSFORMER CKT 1 | Replace auto & 69 kV breaker and switches | 2010-06-01 | 2010-06-01 | 3005700
AEPW | ARSENAL HILL (ARSHILL2) 138/69/14.5KV TRANSFORMER CKT 2 | Replace auto & 69 kV breaker and switches | 2010-06-01 | 2010-06-01 | 3005700
AEPW | AVOCA - EAST ROGERS 161KV CKT 1 | Install 3% impedance reactor set at East Rogers on 161 kV line to Avoca REC. | 2008-06-01 | 2008-06-01 | 900000
AEPW | BANN - LONESTAR ORDINANCE TAP 69KV CKT 1 #2 | Reset relays @ Bann and replace switch @ Lone Star Ordinance Tap. Rebuild 4.14 miles of 397 ACSR with 795 ACSR. | 2012-06-01 | 2012-06-01 | 4250000
AEPW | DYESS - EAST ROGERS 161KV CKT 1 | Relocate 2% impedance reactor set from Chamber Springs to East Rogers and install on 161 kV line to Dyess. | 2008-06-01 | 2008-06-01 | 461900
AEPW | DYESS - ELM SPRINGS REC 161KV CKT 1 #1 | Replace Elm Springs switch. | 2008-06-01 | 2008-06-01 | 100000
AEPW | DYESS - ELM SPRINGS REC 161KV CKT 1 #2 | Rebuild 5.17 miles of line. | 2010-06-01 | 2010-06-01 | 4800000
AEPW | DYESS - TONTITOWN 161KV CKT 1 | Replace Dyess Breaker, Switches, & wavetrap | 2010-06-01 | 2010-06-01 | 500000
AEPW | HEMPSTEAD - HOPE 115KV CKT 1 | Reconductor from Hempstead to Hope 666 ACSR with 1590 ACSR, replace jumpers, circuit switcher, one span of conductor at Hope | 2011-06-01 | 2011-06-01 | 9000000
AEPW | HEMPSTEAD - NW TEXARKANA 345KV CKT 1 | Build 33 miles of 2-795MCM ACSR from Turk NW Texarkana, Add 345kV terminal at NW Texarkana, Add 345kV terminal at Turk | 2011-06-01 | 2011-06-01 | 57530000
AEPW | LAWTON EASTSIDE (LES 4) 345/138/13.8KV TRANSFORMER CKT 1 | Replace Auto with new 450 MVA auto | 2012-12-01 | 2012-12-01 | 4560000
AEPW | LINWOOD - MCWILLIE STREET 138KV CKT 1 #2 | Replace Linwood Switches 10872 & 10873 and replace breaker jumpers | 2009-06-01 | 2009-06-01 | 125000
AEPW | LINWOOD - POWELL STREET 138KV CKT 1 | Replace Breaker, Switches, & Jumpers @ Linwood. Replace circuit switcher @ Powell Street | 2012-06-01 | 2012-06-01 | 456000
AEPW | LONGWOOD (LONGWOOD) 345/138/13.2KV TRANSFORMER CKT 1 | Replace Longwood Autotransformer | 2008-06-01 | 2010-06-01 | 5700000
AEPW | MAGAZINE REC - NORTH MAGAZINE 161KV CKT 1 # 2 | Replace Jumpers @ N. Magazine | 2012-06-01 | 2012-06-01 | 100000
AEPW | OKAY - TOLLETTE 69KV CKT 1 Displacement | Replace switches | 2011-06-01 | 2011-06-01 | 19364
AEPW | SE TEXARKANA - TEXARKANA PLANT 69KV CKT 1 | Change out the 500 CU jumpers @ Texarkana Plant | 2011-06-01 | 2011-06-01 | 35000
AEPW | SOUTH TEXARKANA REC - TEXARKANA PLANT 69KV CKT 1 | Rebuild 5.92 miles of 266 ACSR with 795 ACSR. Replace switches, jumpers, and reset CTs & relays @ Texarkana Plant | 2011-06-01 | 2011-06-01 | 4750000
OKGE | ARDMORE - ROCKY POINT 69KV CKT 1 | Replace 4.65 miles of line w/477AS33 | 2011-06-01 | 2011-06-01 | 1627500
OKGE | DILLARD4 - HEALDTON TAP 138KV CKT 1 | Replace Differential Relaying | 2011-06-01 | 2011-06-01 | 300000
OKGE | FT SMITH 500 (FTSMITH3) 500/161/13.8KV TRANSFORMER CKT 3 | Convert Ft. Smith 161kv to 1-1/2 breaker design and install 3rd 500-161kV transformer bank. | 2017-06-01 | 2017-06-01 | 9750000
OKGE | Hugo - SunnySide 345kV OKGE | Add 345 line from Hugo to SunnySide, Install breaker, switches, and relays | 2008-04-01 | 2011-06-01 | 66000000
OKGE | SUNNYSIDE - UNIROYAL 138KV CKT 1 | Replace wavetrap 800A at Uniroyal | 2011-06-01 | 2011-06-01 | 40000
OKGE | SUNNYSIDE (SUNNYSD3) 345/138/13.8KV TRANSFORMER CKT 1 | Add 2nd 345/138KV Auto | 2008-04-01 | 2011-06-01 | 6500000
OKGE | VBI - VBI NORTH 69KV CKT 1 | Upgrade CT | 2017-06-01 | 2017-06-01 | 75000
WFEC | Hugo - SunnySide 345kV WFEC | Add 345 line from Hugo to SunnySide | 2008-04-01 | 2011-06-01 | 45000000
Construction Pending Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Transmission Owner | Upgrade | Solution | Earliest Data Upgrade Required (COD) | Estimated Date of Upgrade Completion (EOC)
AEPW | ALUMAX TAP - NORTHWEST TEXARKANA 138KV CKT 1 | Rebuild 1.68 miles of 1024 ACAR with 2156 ACSR, Replace wavetrap & jumpers with 2156 ACSR. Replace Switch 2285 @ Alumax Tap. | 2008-04-01 | 2008-06-01
AEPW | BANN - NW TEXARKANA-BANN T 138KV CKT 1 | Rebuild 3.4 miles of 2-477 ACSR with 2156 ACSR. Reset Bann Relay | 2008-04-01 | 2008-06-01
AEPW | SOUTHWEST SHREVEPORT (SW SHV 1) 345/138/13.8KV TRANSFORMER CKT 2 | Replace Auto, two 138 kV breakers and five 138 kV switches. Reset relays and CTs | 2008-04-01 | 2009-06-01
SPRM | Device - Sunset | 30 Mvar Capacitor Bank at Sunset | 2013-06-01 | 2013-06-01
Expansion Plan Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Transmission Owner | Upgrade | Solution | Earliest Data Upgrade Required (COD) | Estimated Date of Upgrade Completion (EOC)
AEPW | ARSENAL HILL - NORTH MARKET 69KV CKT 1 | Rebuild 2.3 miles of 666 ACSR with 1272 ACSR | 2010-06-01 | 2010-06-01
AEPW | BANN - LONESTAR ORDINANCE TAP 69KV CKT 1 #1 | Relay at Bann New limits will be 65/72 MVA summer (line conductor/Lone Star switch) and 72/72 MVA winter (Lone Star Switch) | 2012-06-01 | 2012-06-01
AEPW | BIG SANDY - HAWKINS 69KV CKT 1 | Rebuild 5.5 miles of 477 ACSR with 1272 ACSR. | 2014-06-01 | 2014-06-01
AEPW | BIG SANDY - PERDUE 69KV CKT 1 | Rebuild 5.4 miles of 477 ACSR with 1272 ACSR. | 2014-06-01 | 2014-06-01
AEPW | BONANZA - BONANZA TAP 161KV CKT 1 | Rebuild 0.06 miles of 397 ACSR with 1272 ACSR & reset relay @ Bonanza or Bonanza T-Excelsior-Midland-N. Huntington 161 kV loop | 2011-06-01 | 2011-06-01
AEPW | BONANZA - EXCELSIOR 161KV CKT 1 | New 161 kV from Bonanza to Excelsior (includes Bonanza station) | 2014-06-01 | 2014-06-01
AEPW | CARTHAGE REC POD - ROCK HILL 138KV CKT 1 | Replace transformer differential relay and reset cts | 2017-06-01 | 2017-06-01
AEPW | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | Rebuild / reconductor 10.24 miles of line with 2156 ACSR. | 2017-06-01 | 2017-06-01
AEPW | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 AEPW | Rebuild 17.96 miles of 250 Copperweld with 1272 ACSR. | 2011-06-01 | 2011-06-01
AEPW | EAST CENTERTON - FLINT CREEK 161 KV CKT 1 | Reconductor Flint Creek-East Centerton 161 kV with 2156 conductor | 2014-06-01 | 2014-06-01
AEPW | ELM SPRINGS REC - TONTITOWN 161KV CKT 1 | Replace Wavetrap and switch jumpers | 2016-06-01 | 2016-06-01
AEPW | FLINT CREEK - GENTRY REC 161KV CKT 1 | Rebuild 1.09 miles of 2-397.5 ACSR with 2156 ACSR. Replace Flint Creek wavetrap & jumpers | 2017-06-01 | 2017-06-01
AEPW | FOREST HILLS REC - MAGNOLIA TAP 69KV CKT 1 | Rebuild 7.91 miles of 477 ACSR with 1272 ACSR & replace switch 9116 | 2010-06-01 | 2010-06-01
AEPW | FOREST HILLS REC - QUITMAN 69KV CKT 1 | Replace Quitman bus, switches & jumpers. Change CT & relay settings @ Quitman | 2010-06-01 | 2010-06-01
AEPW | FULTON - HOPE 115KV CKT 1 AEPW | Replace strain bus in Hope Substation | 2012-06-01 | 2012-06-01
AEPW | GEORGIA-PACIFIC - KEATCHIE REC 138KV CKT 1 | Rebuild 12.63 miles of 795 ACSR with 1272 ACSR | 2015-06-01 | 2015-06-01
AEPW | LIEBERMAN - LONGWOOD 138KV CKT 1 | Rebuild 7.8 miles with 2156 ACSR. Replace Longwood wavetrap jumpers | 2008-06-01 | 2010-06-01
AEPW | LIEBERMAN - NORTH BENTON 138KV CKT 1 | Rebuild 14.15 miles with 1590 ACSR. Replace wavetrap & breaker jumpers @ Lieberman. Reset CT @ Lieberman | 2010-06-01 | 2010-06-01
AEPW | LINWOOD - MCWILLIE STREET 138KV CKT 1 #1 | Rebuild 2.09 miles of 666 ACSR with 1272 ACSR | 2008-04-01 | 2008-06-01
AEPW | LONE STAR SOUTH - PITTSBURG 138KV CKT 1 | Replace wavetraps at both ends. Reset CTs @ Lone Star South. Replace switches & reset relays @ Pittsburg | 2015-06-01 | 2015-06-01
AEPW | LONGWOOD - OAK PAN-HARR REC 138KV CKT 1 | Reconductor 1.8 miles of 666 ACSR with 1272 ACSR | 2017-06-01 | 2017-06-01
AEPW | MAGAZINE REC - NORTH MAGAZINE 161KV CKT 1 AEPW | Rebuild 7.43 miles of 250 CWC with 795 ACSR | 2012-06-01 | 2011-06-01
AEPW | MAGNOLIA TAP - WINNSBORO 69KV CKT 1 | Replace switch # 9114 @. Replace switches @ Winnsboro. Reset Cts and relay settings at Winnsboro. | 2010-06-01 | 2010-06-01
AEPW | NORTH MINEOLA - QUITMAN 69KV CKT 1 | Mineola to Quipman 69 kV up grade switches and sub conductor N Mineola and Quipman subs | 2016-06-01 | 2016-06-01
AEPW | PORT ROBSON - REDPOINT 138kV | New 138 kV line from Port Robson - Red Point via McDade & Haughton. Convert McDade & Haughton to 138 kV. | 2012-06-01 | 2012-06-01
AEPW | SOUTHWEST SHREVEPORT - SOUTHWEST SHREVEPORT TAP 138KV CKT 1 | Rebuild 2.29 miles of 2-397.5 ACSR with 2-795 ACSR. Double Circuit the line and add terminal @ SW Shreveport to eliminate three terminal line. | 2008-06-01 | 2010-06-01
AEPW | SOUTHWEST SHREVEPORT - WESTERN ELECTRIC T 138KV CKT 1 | Rebuild 2.9 miles of 2-795 ACSR with 2156 ACSR. Replace switch 1647 @ Western Electric "T". Replace switch 10237 & reset relays @ SW Shreveport. | 2017-06-01 | 2017-06-01
AEPW | SOUTHWEST SHREVEPORT (SW SHV 1) 345/138/13.8KV TRANSFORMER CKT 1 | Using IEEE Guide for Loading of Mineral-Oil Immersed Power Transformers (C57.91-2000) Re-rate the autos. Replace .two 138 kV breakers and five 138 kV switches. Reset relays and CTs | 2008-04-01 | 2009-06-01
EMDE | SUB 124 - AURORA H.T. 161KV | Install 3 - stages of 22 MVAR each for total of 66 MVAR capacitor bank at Aurora Sub #124 bus# 547537 | 2014-06-01 | 2014-06-01
EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | 2014-06-01 | 2014-06-01
GRDA | 412SUB - KANSAS TAP 161KV CKT 1 | Reconductor 9.7 miles with 1590MCM ACSR. | 2012-06-01 | 2012-06-01
GRDA | 412SUB - KERR 161KV CKT 1 | Reconductor 8/10ths of mile out of Kerr Dam | 2012-06-01 | 2012-06-01
GRDA | KANSAS TAP - WEST SILOAM SPRINGS 161KV CKT 1 | Rebuild line to 1590 ACSR | 2012-06-01 | 2012-06-01
GRDA | SILOAM CITY - WEST SILOAM SPRINGS 161KV CKT 1 | Rebuild line to 1590 ACSR | 2012-06-01 | 2012-06-01
OKGE | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 OKGE | Rebuild 17.96 miles of 250 Copperweld with 1272 ACSR. | 2012-06-01 | 2011-06-01
OKGE | MAGAZINE REC - NORTH MAGAZINE 161KV CKT 1 OKGE | Rebuild 7.43 miles of 250 CWC with 795 ACSR | 2012-06-01 | 2011-06-01
OKGE | MUSKOGEE - PECAN CREEK 345KV CKT 1 | Increase CT ration at Pecan Creek from 800-5 to 2000-5 to allow a 1500 amp rating of line section. | 2012-06-01 | 2012-06-01
OKGE | RUSSETT - RUSSETT 138KV CKT 1 OKGE | Replace trap and increase CTR. Pending verification of relays. | 2012-12-01 | 2012-12-01
SPRM | Device - Cox Cap | Install 30 Mvar capacitor at Cox 69 kV bus | 2013-06-01 | 2013-06-01
SPRM | Device - Main Cap | Install 30 Mvar capacitor at Main 161 kv bus | 2013-06-01 | 2013-06-01
SPRM | Device - Mill Cap | Install 30 Mvar capacitor at Mill 161 kV bus | 2013-06-01 | 2013-06-01
SPRM | Device - Norton Cap | Install 30 Mvar capacitor at Norton 161 kV bus | 2013-06-01 | 2013-06-01
SWPA | BROWN - RUSSETT 138KV CKT 1 SWPA | Upgrade Terminal Equipment at Brown- Switches/Wavetraps | 2011-06-01 | 2011-06-01
SWPA | BULL SHOALS - BULL SHOALS 161KV CKT 1 | Replace buswork in Bull Shoals switchyard. | 2012-06-01 | 2012-06-01
SWPA | CLARKSVILLE - DARDANELLE 161KV CKT 1 | Reconductor Clarksville-Dardanelle line | 2012-06-01 | 2012-06-01
SWPA | DARDANELLE - RUSSELLVILLE SOUTH 161KV CKT 1 SWPA | Replace wave trap, disconnect switches, current transformers, and breaker. Bus will limit rating to 1340 amps. | 2012-06-01 | 2012-06-01
WFEC | BROWN - RUSSETT 138KV CKT 1 WFEC |  | 2011-06-01 | 2011-06-01
WFEC | RUSSETT - RUSSETT 138KV CKT 1 WFEC | Upgrade Terminal Equip CTs at Russett | 2012-12-01 | 2012-12-01
Previously Assigned Aggregate Study Upgrades requiring credits to Previous Aggregate Study Customers.
Transmission Owner | Upgrade | Solution | Earliest Data Upgrade Required (COD) | Estimated Date of Upgrade Completion (EOC)
AEPW | HUGO POWER PLANT - VALLIANT 345 KV AEPW | Vallient 345 KV line terminal | 2010-05-01 | 2010-05-01
KACP | LACYGNE - WEST GARDNER 345KV CKT 1 | KCPL Sponsored Project to Reconductor Line to be In-Service by 6/1/2006 | 2006-06-01 | 2006-06-01
OKGE | ARCADIA - REDBUD 345 KV CKT 1 | Sponsored Project to Uprate Terninal Equipment | 2006-06-01 | 2006-06-01
OKGE | ARCADIA - REDBUD 345 KV CKT 2 | Sponsored Project to Uprate Terninal Equipment | 2006-06-01 | 2006-06-01
WFEC | HUGO POWER PLANT - VALLIANT 345 KV WFEC | New 345/138 kv Auto, and 19 miles 345 KV | 2010-05-01 | 2010-05-01

## Table5
Transmission Owner | UpgradeName | Solution | Earliest Data Upgrade Required (COD) | Estimated Date of Upgrade Completion (EOC) | Estimated Engineering & Construction Cost
ENTR | ARKANSAS NUCLEAR ONE 161 - RUSSELLVILLE NORTH 161KV CKT 1 | Indeterminate | 2012-06-01 | 2012-06-01 | 0
ENTR | RUSSELLVILLE EAST - RUSSELLVILLE NORTH 161KV CKT 1 | Indeterminate | 2012-06-01 | 2012-06-01 | 0
ENTR | RUSSELLVILLE EAST - RUSSELLVILLE SOUTH 161KV CKT 1 | Indeterminate | 2012-06-01 | 2012-06-01 | 0
ENTR | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 ENTR | Rebuild 17.96 miles of 250 Copperweld with 1272 ACSR. | 2012-06-01 | 2011-06-01 | 0
ENTR | MAGAZINE REC - NORTH MAGAZINE 161KV CKT 1 ENTR | Rebuild 7.43 miles of 250 CWC with 795 ACSR | 2012-06-01 | 2011-06-01 | 0