## Table 1
Customer | Study Number | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date without interim redispatch | Deferred Stop Date without interim redispatch | Start Date with interim redispatch | Stop Date with interim redispatch | Mimimum Allocated ATC (MW) within reservation period | Season of Minimum Allocated ATC within reservation period
AECC | AG3-2006-003 | 1161131 | WR | EES | 50 | 2007-12-01 | 2027-12-01 | 2008-10-01 | 2028-10-01 | 2008-10-01 | 2028-10-01 | 24 | 08SP
AECC | AG3-2006-002 | 1161136 | WR | CSWS | 50 | 2007-12-01 | 2027-12-01 | 2009-03-01 | 2029-03-01 | 2009-03-01 | 2029-03-01 | 0 | 07WP
AECC | AG3-2006-001 | 1161209 | CSWS | CSWS | 70 | 2011-06-01 | 2031-06-01 |  |  |  |  | 0 | 11SP
AEPM | AG3-2006-039 | 1158760 | CSWS | CSWS | 160 | 2007-07-01 | 2012-07-01 | 2009-04-01 | 2014-04-01 06:00 | 2007-07-01 | 2012-07-01 | 0 | 07SP
AEPM | AG3-2006-040 | 1158761 | CSWS | CSWS | 160 | 2007-11-01 | 2012-11-01 | 2009-04-01 | 2014-04-01 06:00 | 2007-11-01 | 2012-11-01 | 0 | 08SP
AEPM | AG3-2006-043 | 1162211 | OKGE | CSWS | 457 | 2011-06-01 | 2031-06-01 |  |  |  |  | 0 | 11SP
AEPM | AG3-2006-044 | 1162214 | CSWS | CSWS | 455 | 2011-06-01 | 2031-06-01 |  |  |  |  | 0 | 16SP
AEPM | AG3-2006-045 | 1162223 | CSWS | WFEC | 15 | 2007-08-01 | 2012-08-01 |  |  |  |  | 0 | 11SP
AEPM | AG3-2006-072 | 1162484 | CSWS | EES | 11 | 2009-01-01 | 2014-01-01 |  |  |  |  | 0 | 11SP
AEPM | AG3-2006-073 | 1162486 | CSWS | EES | 25 | 2009-01-01 | 2014-01-01 |  |  |  |  | 0 | 11SP
AEPM | AG3-2006-074 | 1162487 | CSWS | EES | 20 | 2009-01-01 | 2014-01-01 |  |  |  |  | 0 | 11SP
AEPM | AG3-2006-075 | 1162491 | CSWS | EES | 19 | 2009-01-01 | 2014-01-01 |  |  |  |  | 0 | 11SP
AEPM | AG3-2006-076 | 1162492 | CSWS | EES | 9 | 2009-01-01 | 2014-01-01 |  |  |  |  | 0 | 11SP
AEPM | AG3-2006-077 | 1162494 | CSWS | EES | 17 | 2009-01-01 | 2014-01-01 |  |  |  |  | 0 | 11SP
AEPM | AG3-2006-092 | 1162763 | CSWS | CSWS | 100 | 2007-06-01 | 2008-06-01 | 2009-06-01 | 2010-06-01 06:00 | 2007-06-01 | 2008-06-01 | 12 | 07SP
AEPM | AG3-2006-091 | 1162766 | CSWS | CSWS | 100 | 2007-06-01 | 2008-06-01 | 2009-06-01 | 2010-06-01 06:00 | 2007-06-01 | 2008-06-01 | 12 | 07SP
AEPM | AG3-2006-095 | 1162768 | OKGE | CSWS | 100 | 2007-06-01 | 2008-06-01 |  |  |  |  | 100 | N/A
AEPM | AG3-2006-094 | 1163062 | CSWS | CSWS | 550 | 2010-06-01 | 2015-06-01 |  |  |  |  | 0 | 11SP
GRDX | AG3-2006-032 | 1161666 | CSWS | GRDA | 150 | 2007-02-01 | 2008-02-01 | 2009-06-01 | 2010-06-01 06:00 | 2009-06-01 | 2010-06-01 06:00 | 0 | 06WP
GRDX | AG3-2006-033 | 1161667 | OKGE | GRDA | 150 | 2007-02-01 | 2008-02-01 | 2009-06-01 | 2010-06-01 06:00 | 2009-06-01 | 2010-06-01 06:00 | 0 | 07AP
GSEC | AG3-2006-100 | 1162688 | SPS | SPS | 10 | 2007-03-01 | 2037-03-01 | 2009-04-01 | 2039-04-01 12:00 | 2009-04-01 | 2039-04-01 12:00 | 0 | 07SP
KCPS | AG3-2006-106 | 1162649 | KCPL | KCPL | 101 | 2007-02-01 | 2037-02-01 | 2010-01-01 | 2040-01-01 12:00 | 2009-01-01 | 2039-01-01 12:00 | 0 | 06WP
KCPS | AG3-2006-103 | 1162650 | KCPL | CLEC | 52 | 2007-02-01 | 2008-02-01 | 2008-06-01 | 2009-06-01 06:00 | 2007-06-01 | 2008-06-01 | 0 | 07SH
KCPS | AG3-2006-103 | 1162651 | KCPL | CLEC | 51 | 2007-02-01 | 2008-02-01 | 2008-06-01 | 2009-06-01 06:00 | 2007-06-01 | 2008-06-01 | 0 | 07SH
KCPS | AG3-2006-104 | 1162654 | KCPL | SPA | 16 | 2007-02-01 | 2008-02-01 | 2009-06-01 | 2010-06-01 06:00 | 2007-06-01 | 2008-06-01 | 0 | 07SH
KCPS | AG3-2006-101 | 1162685 | AECI | KCPL | 50 | 2007-06-01 | 2008-06-01 | 2008-06-01 | 2009-06-01 06:00 | 2007-06-01 | 2008-06-01 | 0 | 07SH
KCPS | AG3-2006-101 | 1162686 | AECI | KCPL | 50 | 2007-06-01 | 2008-06-01 | 2008-06-01 | 2009-06-01 06:00 | 2007-06-01 | 2008-06-01 | 0 | 07SH
MIDW | AG3-2006-086 | 1162102 | WR | WR | 25 | 2007-06-01 | 2017-06-01 | 2009-07-01 | 2019-07-01 12:00 | 2009-07-01 | 2019-07-01 12:00 | 0 | 07SH
MIDW | AG3-2006-087 | 1162109 | WR | WR | 10 | 2008-06-01 | 2018-06-01 | 2009-07-01 | 2019-07-01 12:00 | 2009-07-01 | 2019-07-01 12:00 | 0 | 08SP
MIDW | AG3-2006-087 | 1162122 | WR | WR | 10 | 2008-06-01 | 2018-06-01 | 2009-07-01 | 2019-07-01 12:00 | 2009-07-01 | 2019-07-01 12:00 | 0 | 08SP
MIDW | AG3-2006-087 | 1162123 | WR | WR | 19 | 2008-06-01 | 2018-06-01 | 2009-07-01 | 2019-07-01 12:00 | 2009-07-01 | 2019-07-01 12:00 | 0 | 08SP
MIDW | AG3-2006-087 | 1162130 | WR | WR | 6 | 2008-06-01 | 2018-06-01 | 2009-07-01 | 2019-07-01 12:00 | 2009-07-01 | 2019-07-01 12:00 | 0 | 08SP
MIDW | AG3-2006-058 | 1162131 | WR | WR | 40 | 2010-06-01 | 2020-06-01 |  |  |  |  | 0 | 11SP
MIDW | AG3-2006-058 | 1162136 | WR | WR | 10 | 2010-06-01 | 2020-06-01 |  |  |  |  | 0 | 11SP
MIDW | AG3-2006-062 | 1162137 | WR | WR | 20 | 2008-06-01 | 2038-06-01 | 2009-07-01 | 2039-07-01 12:00 | 2009-07-01 | 2039-07-01 12:00 | 0 | 11SP
MIDW | AG3-2006-062 | 1162141 | WR | WR | 5 | 2008-06-01 | 2038-06-01 | 2009-07-01 | 2039-07-01 12:00 | 2009-07-01 | 2039-07-01 12:00 | 0 | 08SP
MIDW | AG3-2006-062 | 1162142 | WR | WR | 40 | 2008-06-01 | 2038-06-01 | 2009-07-01 | 2039-07-01 12:00 | 2009-07-01 | 2039-07-01 12:00 | 0 | 11SP
MIDW | AG3-2006-062 | 1162143 | WR | WR | 10 | 2008-06-01 | 2038-06-01 | 2009-07-01 | 2039-07-01 12:00 | 2009-07-01 | 2039-07-01 12:00 | 0 | 11SP
MIDW | AG3-2006-058 | 1162175 | WR | WR | 68 | 2008-06-01 | 2038-06-01 | 2009-07-01 | 2039-07-01 12:00 | 2009-07-01 | 2039-07-01 12:00 | 0 | 08SP
MIDW | AG3-2006-058 | 1162176 | WR | WR | 16 | 2008-06-01 | 2038-06-01 | 2009-07-01 | 2039-07-01 12:00 | 2009-07-01 | 2039-07-01 12:00 | 0 | 08SP
MIDW | AG3-2006-058 | 1162183 | WR | WR | 40 | 2010-06-01 | 2030-06-01 |  |  |  |  | 0 | 11SP
MIDW | AG3-2006-058 | 1162190 | WR | WR | 10 | 2010-06-01 | 2030-06-01 |  |  |  |  | 0 | 11SP
MIDW | AG3-2006-058 | 1162191 | WR | WR | 40 | 2010-06-01 | 2030-06-01 |  |  |  |  | 0 | 11SP
MIDW | AG3-2006-058 | 1162192 | WR | WR | 10 | 2010-06-01 | 2030-06-01 |  |  |  |  | 0 | 11SP
MIDW | AG3-2006-058 | 1162193 | WR | WR | 20 | 2010-06-01 | 2030-06-01 |  |  |  |  | 0 | 11SP
MIDW | AG3-2006-058 | 1162194 | WR | WR | 5 | 2010-06-01 | 2030-06-01 |  |  |  |  | 0 | 11SP
MIDW | AG3-2006-121 | 1167662 | WR | WR | 35 | 2007-02-01 | 2012-02-01 | 2009-07-01 | 2014-07-01 06:00 | 2009-07-01 | 2014-07-01 06:00 | 0 | 06WP
MIDW | AG3-2006-121 | 1167664 | WR | WR | 10 | 2007-02-01 | 2012-02-01 | 2009-07-01 | 2014-07-01 06:00 | 2009-07-01 | 2014-07-01 06:00 | 0 | 06WP
NTEC | AG3-2006-035 | 1161974 | CSWS | CSWS | 52 | 2011-06-01 | 2031-06-01 |  |  |  |  | 0 | 11SP
OGE | AG3-2006-034 | 1161665 | OKGE | SPA | 20 | 2007-02-01 | 2012-02-01 | 2009-06-01 | 2014-06-01 06:00 | 2007-06-01 | 2012-06-01 | 0 | 08SP
OGE | AG3-2006-049 | 1162077 | OKGE | OKGE | 384 | 2011-06-01 | 2031-06-01 |  |  |  |  | 0 | 11SP
OMPA | AG3-2006-028 | 1159596 | CSWS | CSWS | 41 | 2011-06-01 | 2031-06-01 |  |  |  |  | 0 | 11SP
OMPA | AG3-2006-050 | 1162095 | OKGE | OKGE | 73 | 2011-06-01 | 2031-06-01 |  |  |  |  | 0 | 11SP
SEPC | AG3-2006-113 | 1162670 | WR | SECI | 51 | 2007-12-01 | 2027-12-01 | 2009-07-01 | 2029-07-01 | 2009-07-01 | 2029-07-01 | 0 | 07WP
SPSM | AG3-2006-115 | 1162675 | OKGE | SPS | 100 | 2007-02-01 | 2008-02-01 | 2010-06-01 | 2011-06-01 06:00 | 2010-06-01 | 2011-06-01 06:00 | 0 | 06WP
UCU | AG3-2006-025D | 1152228 | MPS | MPS | 585 | 2007-02-01 | 2027-02-01 | 2008-10-01 | 2028-10-01 | 2008-10-01 | 2028-10-01 | 266 | 16SP
UCU | AG3-2006-052D | 1162075 | WR | MPS | 51 | 2008-01-01 | 2028-01-01 | 2009-07-01 | 2029-07-01 | 2009-07-01 | 2029-07-01 | 0 | 08SP
UCU | AG3-2006-088D | 1162678 | WR | MPS | 25 | 2008-01-01 | 2028-01-01 | 2009-07-01 | 2029-07-01 | 2009-07-01 | 2029-07-01 | 0 | 08SP
UCU | AG3-2006-088D | 1162681 | WR | MPS | 25 | 2008-01-01 | 2028-01-01 | 2009-07-01 | 2029-07-01 | 2009-07-01 | 2029-07-01 | 0 | 08SP
WRGS | AG3-2006-025 | 1140120 | WR | WR | 360 | 2009-05-01 | 2015-05-01 | 2009-07-01 | 2015-07-01 | 2009-05-01 | 2015-05-01 | 0 | 11SP
WRGS | AG3-2006-024D | 1161506 | WR | WR | 380 | 2008-05-01 | 2014-05-01 | 2009-07-01 | 2015-07-01 12:00 | 2008-05-01 | 2014-05-01 | 0 | 11SP
WRGS | AG3-2006-036D | 1161997 | MPS | WR | 300 | 2007-06-01 | 2014-06-01 | 2009-07-01 | 2016-07-01 | 2007-06-01 | 2014-06-01 | 0 | 07SH
Note 1: Disregard Redispatch shown in Table 6 for limitations identified earlier than the start date with redispatch with the exception of limitations identified in the 2007 Spring Peak, 2007 April Minimum, 2007 Summer Shoulder, and 2007 Fall Peak.
Note 2: Start and Stop Dates are determined based on customers choosing option to pursue redispatch to start service at Requested Start and Stop Dates or earliest date possible.

## Table 2
Customer | Study Number | Reservation | 11 12 Engineering and Construction Cost of Upgrades Allocated to Customer for Revenue Requirements | 1Letter of Credit Amount Required | 2Potential Base Plan Engineering and Construction Funding Allowable | Notes | 4Additional Engineering and Construction Cost for 3rd Party Upgrades | 3 Total Revenue Requirements for Assigned Upgrades over term of reservation without potential base plan funding allocation | 3 7 Total Revenue Requirements for Assigned Upgrades over term of reservation WITH potential base plan funding allocation | Point-to-Point Base Rate over reservation period | 4Total Cost of Reservation Assignable to Customer contingent upon base plan funding
AECC | AG3-2006-003 | 1161131 | 1193934 | 1193934 | 0 |  | 0 | 4023653.199 | 4023653.1938 | 10800000 | 10800000
AECC | AG3-2006-002 | 1161136 | 1602781 | 1602781 | 900000 |  | 0 | 5324317.8235 | 2334585.5775 | 0 | 2334585.5775
AECC | AG3-2006-001 | 1161209 | 16025758 | 16025758 | 12600000 |  | Indeterminate | 48715775.6075 | 10413763.7715 | 0 | 10413763.7715
AEPM | AG3-2006-039 | 1158760 | 2929914 | 0 | 2929914 |  | 0 | 4970982.104 | 0 | 0 | Sch 9 charges
AEPM | AG3-2006-040 | 1158761 | 2929914 | 0 | 2929914 |  | 0 | 5110867.5717 | 0 | 0 | Sch 9 charges
AEPM | AG3-2006-043 | 1162211 | 33746343 | 32731470 | 33746343 |  | 0 | 142923594.7475 | 0 | 0 | Sch 9 charges
AEPM | AG3-2006-044 | 1162214 | 65804529 | 24585845 | 65804529 |  | Indeterminate | 209754477.0601 | 0 | 0 | Sch 9 charges
AEPM | AG3-2006-045 | 1162223 | 12753734 | 12747809 | 2700000 |  | 0 | 21896250.0474 | 17258572.8113 | 0 | 17258572.8113
AEPM | AG3-2006-072 | 1162484 | 94131 | 15572 | 94131 |  | 699631 | 129329.3614 | 0 | 0 | 699631
AEPM | AG3-2006-073 | 1162486 | 217664 | 35043 | 217664 |  | 1648402 | 297164.2035 | 0 | 0 | 1648402
AEPM | AG3-2006-074 | 1162487 | 164867 | 25895 | 164867 |  | 4781159 | 224558.8836 | 0 | 0 | 4781159
AEPM | AG3-2006-075 | 1162491 | 172001 | 27734 | 172001 |  | 368115 | 234732.3645 | 0 | 0 | 368115
AEPM | AG3-2006-076 | 1162492 | 74619 | 12065 | 74619 |  | 1274547 | 102411.2738 | 0 | 0 | 1274547
AEPM | AG3-2006-077 | 1162494 | 142745 | 21628 | 142745 |  | 923922 | 194374.7958 | 0 | 0 | 923922
AEPM | AG3-2006-092 | 1162763 | 412771 | 423497 | 0 |  | 9695776 | 796369.401 | 626271.1282 | 1260000 | 10955776
AEPM | AG3-2006-091 | 1162766 | 708552 | 369057 | 0 |  | 0 | 1440733.9374 | 1067726.5115 | 1260000 | 1260000
AEPM | AG3-2006-095 | 1162768 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1260000 | 1260000
AEPM | AG3-2006-094 | 1163062 | 41165604 | 22337329 | 41165604 |  | Indeterminate | 74814620.3672 | 0 | 0 | Sch 9 charges
GRDX | AG3-2006-032 | 1161666 | 2100194 | 939442 | 0 |  | 0 | 3865347.609 | 3412176.2681 | 0 | 3412176.2681
GRDX | AG3-2006-033 | 1161667 | 1586545 | 483331 | 0 |  | 0 | 2733549.8488 | 2500398.841 | 0 | 2500398.841
GSEC | AG3-2006-100 | 1162688 | 245825 | 315825 | 0 |  | 200000 | 1197199.5052 | 1197199.5013 | 0 | 1397199.5013
KCPS | AG3-2006-106 | 1162649 | 2412312 | 1712312 | 1800000 |  | 0 | 10671156.757 | 2708636.9196 | 0 | 2708636.9196
KCPS | AG3-2006-103 | 1162650 | 0 | 0 | 0 |  | 0 | 0 | 0 | 655200 | 655200
KCPS | AG3-2006-103 | 1162651 | 0 | 0 | 0 |  | 0 | 0 | 0 | 642600 | 642600
KCPS | AG3-2006-104 | 1162654 | 60661 | 62237 | 0 |  | Indeterminate | 140558.6712 | 110536.4389 | 172800 | 172800
KCPS | AG3-2006-101 | 1162685 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | Sch 9 charges
KCPS | AG3-2006-101 | 1162686 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | Sch 9 charges
MIDW | AG3-2006-086 | 1162102 | 254918 | 249393 | 0 | 5 | 0 | 647141.9815 | 647141.9799 | 0 | 647141.9799
MIDW | AG3-2006-087 | 1162109 | 101982 | 99772 | 0 | 5 | 0 | 258894.0257 | 258894.0251 | 0 | 258894.0251
MIDW | AG3-2006-087 | 1162122 | 101982 | 99772 | 0 | 5 | 0 | 258894.0257 | 258894.0251 | 0 | 258894.0251
MIDW | AG3-2006-087 | 1162123 | 193707 | 189508 | 0 | 5 | 0 | 491749.1401 | 491749.1389 | 0 | 491749.1389
MIDW | AG3-2006-087 | 1162130 | 61175 | 59849 | 0 | 5 | 0 | 155302.3797 | 155302.3793 | 0 | 155302.3793
MIDW | AG3-2006-058 | 1162131 | 109856 | 103235 | 0 | 6 | 0 | 319683.5767 | 319683.5753 | 0 | 319683.5753
MIDW | AG3-2006-058 | 1162136 | 27450 | 25795 | 0 | 6 | 0 | 79879.8299 | 79879.8295 | 0 | 79879.8295
MIDW | AG3-2006-062 | 1162137 | 41184 | 34425 | 0 | 5 | 0 | 193951.5244 | 193951.5229 | 0 | 193951.5229
MIDW | AG3-2006-062 | 1162141 | 10295 | 8605 | 0 | 5 | 0 | 48483.0126 | 48483.0122 | 0 | 48483.0122
MIDW | AG3-2006-062 | 1162142 | 82370 | 68852 | 0 | 5 | 0 | 387912.7541 | 387912.751 | 0 | 387912.751
MIDW | AG3-2006-062 | 1162143 | 20598 | 17218 | 0 | 5 | 0 | 97004.6073 | 97004.6065 | 0 | 97004.6065
MIDW | AG3-2006-058 | 1162175 | 188374 | 175503 | 0 | 5 | 0 | 909305.6988 | 909305.6945 | 0 | 909305.6945
MIDW | AG3-2006-058 | 1162176 | 44330 | 41301 | 0 | 5 | 0 | 213987.1335 | 213987.1325 | 0 | 213987.1325
MIDW | AG3-2006-058 | 1162183 | 109856 | 103235 | 0 | 6 | 0 | 436064.0272 | 436064.0253 | 0 | 436064.0253
MIDW | AG3-2006-058 | 1162190 | 27450 | 25795 | 0 | 6 | 0 | 108959.6876 | 108959.6871 | 0 | 108959.6871
MIDW | AG3-2006-058 | 1162191 | 109856 | 103235 | 0 | 6 | 0 | 436064.0272 | 436064.0253 | 0 | 436064.0253
MIDW | AG3-2006-058 | 1162192 | 27450 | 25795 | 0 | 6 | 0 | 108959.6876 | 108959.6871 | 0 | 108959.6871
MIDW | AG3-2006-058 | 1162193 | 54927 | 51617 | 0 | 6 | 0 | 218028.3398 | 218028.3388 | 0 | 218028.3388
MIDW | AG3-2006-058 | 1162194 | 13724 | 12897 | 0 | 6 | 0 | 54476.2227 | 54476.2225 | 0 | 54476.2225
MIDW | AG3-2006-121 | 1167662 | 356864 | 349129 | 0 | 5 | 0 | 742588.8213 | 742588.8194 | 0 | 742588.8194
MIDW | AG3-2006-121 | 1167664 | 101982 | 99772 | 0 | 5 | 0 | 212211.0512 | 212211.0507 | 0 | 212211.0507
NTEC | AG3-2006-035 | 1161974 | 6121447 | 6221447 | 6121447 |  | 0 | 20861245.8471 | 0 | 0 | Sch 9 charges
OGE | AG3-2006-034 | 1161665 | 223609 | 201071 | 0 | 10 | 558304 | 286390.8379 | 272306.6855 | 1080000 | 1638304
OGE | AG3-2006-049 | 1162077 | 37225529 | 996162 | 37225529 |  | 0 | 157102840.8133 | 0 | 0 | Sch 9 charges
OMPA | AG3-2006-028 | 1159596 | 28376454 | 28376454 | 7380000 |  | Indeterminate | 111895824.9816 | 82794543.0374 | 0 | 82794543.0374
OMPA | AG3-2006-050 | 1162095 | 5848818 | 5859066 | 5848818 |  | 0 | 24947918.3034 | 0 | 0 | Sch 9 charges
SEPC | AG3-2006-113 | 1162670 | 307835 | 307835 | 0 | 8 | 0 | 1158971.1793 | 1158971.1778 | 0 | 1158971.1778
SPSM | AG3-2006-115 | 1162675 | 9809510 | 1041803 | 0 |  | 0 | 20360374.6139 | 20038225.3446 | 1741200 | 20038225.3446
UCU | AG3-2006-025D | 1152228 | 2100000 | 0 | 0 | 8 | 0 | 7147507.8291 | 7147507.8291 | 0 | 7147507.8291
UCU | AG3-2006-052D | 1162075 | 343378 | 343378 | 0 | 8 | 0 | 1293873.1512 | 1293873.1507 | 19718640 | 19718640
UCU | AG3-2006-088D | 1162678 | 168314 | 168314 | 0 | 8 | 0 | 634219.6626 | 634219.6624 | 9666000 | 9666000
UCU | AG3-2006-088D | 1162681 | 168314 | 168314 | 0 | 8 | 0 | 634219.6626 | 634219.6624 | 9666000 | 9666000
WRGS | AG3-2006-025 | 1140120 | 1044255 | 209792 | 0 | 9 | 0 | 2324972.3554 | 2156950.0549 | 0 | 2156950.0549
WRGS | AG3-2006-024D | 1161506 | 1531041 | 216788 | 1531041 | 9 | 0 | 3572237.2046 | 0 | 0 | Sch 9 charges
WRGS | AG3-2006-036D | 1161997 | 2315803 | 642483 | 2315803 | 9 | 0 | 5423927.5583 | 0 | 0 | Sch 9 charges
Totals |  | 72028207 | 284170035 |  | 225864969 |  |  | 903586090.6952 | 168163879.0965
Note 1: Letter of Credit required for financial security for transmission owner for network upgrades is determined by allocated engineering and construction costs less engineering and construction costs for upgrades when network customer is the transmission owner less the E & C allocation of expedited projects plus network upgrades for assigned upgrades less that $100,000 which are base plan funded but still require a letter of credit.
Note 2. If potential base plan funding is applicable, this value is the lesser of the Engineering and Construction costs of assignable upgrades or the value of base plan funding calculated pursuant to Attachment J, Section III B criteria. Allocation of base plan funding is contingent upon verification of customer agreements meeting Attachment J, Section II B criteria. Not applicable if PTP base rate exceeds revenue requirements.
Note 3: Revenue Requirements (RR) are based upon deferred end dates if applicable. Deferred dates are based upon customer's choice to pursue redispatch. Achievable Base Plan Avoided RR in the case of a Base Plan upgrade being displaced or deferred by an earlier in service date for a Requested Upgrade shall be determined per Attachment J, Section VII.C methodology. Assumption of a 40 year service life is utilized for Base Plan funded projects. A present worth analysis of RR on a common year basis between the Base Plan and Requested Upgrades was performed to determine avoided Base Plan RR due to the displacement or deferral of the Base Plan upgrade by the Requested Upgrade. The incremental increase in present worth of a Requested Upgrade on a common year basis as a Base Plan upgrade is assigned to the transmission requests impacting the upgrade based on the displacement or deferral. If the displacement analysis results in lower RR due to the shorter amortization period of the requested upgrade when compared to a base plan amortization period, then no direct assignment of the upgrade cost is made due to the displacement to an earlier start date.
Note 4. For PTP requests, total cost is based on the higher of the base rate or assigned upgrade revenue requirements. For Network requests, the total cost is based on the assigned upgrade revenue requirement. Allocation of base plan funding will be determined after verification of designated resource meeting Attachment J, Section II B Criteria. Additionally E & C of 3rd Party upgrades is assignable to Customer. This includes prepayments required for any SWPA upgrades. Revenue requirements for 3rd Party facilities are not calculated. Total cost to customer is based on assumption of Revenue Requirements with confirmation of base plan funding. Customer is responsible for negotiating redispatch costs if applicable. Customer is also responsible to pay credits for previously assigned upgrades that are impacted by their request. Credits required will be determined at a later date.
Note 5: Midwest has a maximum of 385MW total resources for 2007 or 2008 for base plan funding consideration.
Note 6: Midwest has a maximum of 391MW total resources for 2010 for base plan funding consideration.
Note 7: RR with base plan funding may increase or decrease even if no base plan funding is applicable to a particular request if another request that shares the upgrade is now full base plan funded resulting in a different amortization period for the upgrade and thus different RR.
Note 8: Resource ratio exceeds 125% load criteria for base plan funding.
Note 9: Westar has a maximum of 7160MW total resources for 2009 base plan consideration. Thus a cap of 920MW new resouces eligible for base plan funding with no base funding for 1140120 if 1161506 and 1161997 confirmed.
Note 10: Requires a SWPA prepayment of $2000 for the Jones-Jonesboro 161kV upgrade.
Note 11: E & C for an expedited project was assigned to previous AG customer or a Transmission Owner planned project thus not included in this total.
Note 12: E & C allocation for determination of allocated revenue requirements does not include those upgrades estimated at $100,000 or less as these are base plan funded. Thus this number sets the cap for base plan funding allowable for remaining assigned upgrades. Allocated E & C in Table 3 does include those upgrades less than $100,000 in order to establish the allocation per request per upgrade detail which is required for Letter of Credit determination.

## Table 3
Customer | Study Number
AECC | AG3-2006-001
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AECC | 1161209 | CSWS | CSWS | 70 | 2011-06-01 | 2031-06-01 |  |  | 12600000 | 0 | 16025758 | 48715775.61
[9 empty] | 12600000 | 0 | 16025758 | 48715775.61
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1161209 | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 AEPW | 2011-06-01 | 2011-06-01 |  |  | 1355299 | 9000000 | 4898494.84
| DYESS - ELM SPRINGS REC 161KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 281517 | 5000000 | 981288.49
| DYESS - TONTITOWN 161KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 28152 | 500000 | 98129.89
| HEMPSTEAD - NW TEXARKANA 345 kV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 5742721 | 56000000 | 20099552.15
| Hugo - SunnySide 345kV | 2011-06-01 | 2011-06-01 |  |  | 3720121 | 50000000 | 9125094.34
| SOUTH TEXARKANA REC - TEXARKANA PLANT 69KV CKT 1 | 2016-06-01 | 2016-06-01 |  |  | 4000000 | 4000000 | 9928811.3
| SUGAR HILL (SUGAR HL) 138/69/12.47KV TRANSFORMER CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 330480 | 2500000 | 1150614.03
| SUNNYSIDE 345/138KV TRANSFORMER CKT 2 | 2011-06-01 | 2011-06-01 |  |  | 567468 | 6500000 | 2433790.55
[5 empty] | Total | 16025758 | 133500000 | 48715775.59
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1161209 | BEN WHEELER - BARTONS CHAPEL | 2016-06-01 | 2016-06-01
| BONANZA - BONANZA TAP 161KV CKT 1 Displacement | 2015-06-01 | 2015-06-01
| BULL SHOALS - BULL SHOALS 161KV CKT 1 | 2010-06-01 | 2010-06-01
| Siloam Springs - South Fayetteville 161 kV | 2014-06-01 | 2014-06-01
| WALDRON CAPACITOR | 2016-06-01 | 2016-06-01
Third Party Limitations.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1161209 | 5FLIPN - BULL SHOALS HES 161KV CKT 1 | 2011-06-01 | 2011-06-01
| 5HILLTOP 161 - 5ST_JOE 161 161KV CKT 1 | 2011-06-01 | 2011-06-01
| 5ST_JOE 161 - EVERTON 161KV CKT 1 | 2011-06-01 | 2011-06-01
| ARKANSAS NUCLEAR ONE 161 - RUSSELLVILLE NORTH 161KV CKT 1 | 2007-06-01 | 2007-06-01
| DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 ENTR | 2011-06-01 | 2011-06-01
| EVERTON - HARRISON-EAST 161KV CKT 1 | 2011-06-01 | 2011-06-01
| HARRISON-EAST - SUMMIT 161KV CKT 1 | 2016-06-01 | 2016-06-01
| RUSSELLVILLE EAST - RUSSELLVILLE NORTH 161KV CKT 1 | 2011-06-01 | 2011-06-01
Customer | Study Number
AECC | AG3-2006-002
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AECC | 1161136 | WR | CSWS | 50 | 2007-12-01 | 2027-12-01 | 2009-03-01 | 2029-03-01 | 900000 | 0 | 1602781 | 5324317.82
[9 empty] | 900000 | 0 | 1602781 | 5324317.82
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1161136 | ARCADIA - SOONER 345kV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 1062061 | 65000000 | 3697315.36
| DYESS - ELM SPRINGS REC 161KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 202594 | 5000000 | 586642.01
| DYESS - TONTITOWN 161KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 20259 | 500000 | 58663.04
| HEMPSTEAD - NW TEXARKANA 345 kV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 251992 | 56000000 | 732672.55
| ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER Displacement | 2007-06-01 | 2009-06-01 | 2008-10-01 |  | 65875 | 1132688 | 249024.87
[5 empty] | Total | 1602781 | 127632688 | 5324317.83
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1161136 | ALUMAX TAP - NORTHWEST TEXARKANA 138KV CKT 1 | 2008-06-01 | 2008-06-01
| BONANZA - BONANZA TAP 161KV CKT 1 Displacement | 2015-06-01 | 2015-06-01
| BROKEN BOW - CRAIG JUNCTION 138KV CKT 1 AEPW | 2007-12-01 | 2009-03-01 |  | No
| Siloam Springs - South Fayetteville 161 kV | 2014-06-01 | 2014-06-01
| WALDRON CAPACITOR | 2016-06-01 | 2016-06-01
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1161136 | HUGO POWER PLANT - VALLIANT 345 KV AEPW | 2010-05-01 | 2010-05-01
| HUGO POWER PLANT - VALLIANT 345 KV WFEC | 2010-05-01 | 2010-05-01
| LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01
| ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 Displacement | 2011-06-01 | 2011-06-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1161136 | CHAMBER SPRINGS - TONTITOWN 161KV CKT 1 | 2006-12-01 | 2007-06-01 |  | No
| Chamber Springs - Tontitown 345 kV | 2008-06-01 | 2008-06-01
| Flint Creek - East Centerton 345 kV | 2008-06-01 | 2008-06-01
| WICHITA - RENO 345KV | 2007-02-01 | 2009-07-01 |  | No
Customer | Study Number
AECC | AG3-2006-003
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AECC | 1161131 | WR | EES | 50 | 2007-12-01 | 2027-12-01 | 2008-10-01 | 2028-10-01 | 0 | 10800000 | 1193934 | 4023653.2
[9 empty] | 0 | 10800000 | 1193934 | 4023653.2
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1161131 | ARCADIA - SOONER 345kV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 1125484 | 65000000 | 3772545.11
| ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER Displacement | 2007-06-01 | 2009-06-01 | 2008-10-01 | No | 68450 | 1132688 | 251108.08
[5 empty] | Total | 1193934 | 66132688 | 4023653.19
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1161131 | BEN WHEELER - BARTONS CHAPEL | 2016-06-01 | 2016-06-01
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1161131 | HUGO POWER PLANT - VALLIANT 345 KV AEPW | 2010-05-01 | 2010-05-01
| HUGO POWER PLANT - VALLIANT 345 KV WFEC | 2010-05-01 | 2010-05-01
| IATAN - NASHUA 345KV CKT 1 | 2010-06-01 | 2010-06-01
| LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01
| ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 Displacement | 2011-06-01 | 2011-06-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1161131 | WICHITA - RENO 345KV | 2007-02-01 | 2009-07-01 |  | No
Customer | Study Number
AEPM | AG3-2006-039
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AEPM | 1158760 | CSWS | CSWS | 160 | 2007-07-01 | 2012-07-01 | 2009-04-01 | 2014-04-01 | 2929914 | 0 | 2931360 | 4970982.1
[9 empty] | 2929914 | 0 | 2931360 | 4970982.1
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1158760 | ARSENAL HILL - FORT HUMBUG 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 39774 | 2750000 | 60294.52
| ARSENAL HILL - MCWILLIE STREET 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 1446 | 100000 | 0
| ARSENAL HILL - WATERWORKS 69KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 28926 | 2000000 | 43611.21
| DYESS - ELM SPRINGS REC 161KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 2257944 | 5000000 | 3407357.8
| DYESS - TONTITOWN 161KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 225794 | 500000 | 340735.17
| SOUTHWEST SHREVEPORT - SOUTHWEST SHREVEPORT TAP 138KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 377476 | 2500000 | 657075.62
| SOUTHWEST SHREVEPORT (SW SHV 1) 345/138/13.8KV TRANSFORMER CKT 1 Expedite | 2008-06-01 | 2009-04-01 |  | Yes | 0 | 1500000 | 230953.89
| SOUTHWEST SHREVEPORT (SW SHV 1) 345/138/13.8KV TRANSFORMER CKT 2 Expedite | 2008-06-01 | 2009-04-01 |  | Yes | 0 | 1500000 | 230953.89
[5 empty] | Total | 2931360 | 15850000 | 4970982.1
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1158760 | LINWOOD - MCWILLIE STREET 138KV CKT 1 | 2007-06-01 | 2008-01-01 |  | Yes
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1158760 | HUGO POWER PLANT - VALLIANT 345 KV AEPW | 2010-05-01 | 2010-05-01
| HUGO POWER PLANT - VALLIANT 345 KV WFEC | 2010-05-01 | 2010-05-01
| SOUTHWEST SHREVEPORT (SW SHV 1) 345/138/13.8KV TRANSFORMER CKT 1 | 2010-06-01 | 2010-06-01
| SOUTHWEST SHREVEPORT (SW SHV 2) 345/138/13.8KV TRANSFORMER CKT 2 | 2010-06-01 | 2010-06-01
Customer | Study Number
AEPM | AG3-2006-040
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AEPM | 1158761 | CSWS | CSWS | 160 | 2007-11-01 | 2012-11-01 | 2009-04-01 | 2014-04-01 | 2929914 | 0 | 2931360 | 5110867.57
[9 empty] | 2929914 | 0 | 2931360 | 5110867.57
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1158761 | ARSENAL HILL - FORT HUMBUG 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 39774 | 2750000 | 61991.23
| ARSENAL HILL - MCWILLIE STREET 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 1446 | 100000 | 0
| ARSENAL HILL - WATERWORKS 69KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 28926 | 2000000 | 44838.45
| DYESS - ELM SPRINGS REC 161KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 2257944 | 5000000 | 3503242.24
| DYESS - TONTITOWN 161KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 225794 | 500000 | 350323.6
| SOUTHWEST SHREVEPORT - SOUTHWEST SHREVEPORT TAP 138KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 377476 | 2500000 | 675566
| SOUTHWEST SHREVEPORT (SW SHV 1) 345/138/13.8KV TRANSFORMER CKT 1 Expedite | 2008-06-01 | 2009-04-01 |  | Yes | 0 | 1500000 | 237453.03
| SOUTHWEST SHREVEPORT (SW SHV 1) 345/138/13.8KV TRANSFORMER CKT 2 Expedite | 2008-06-01 | 2009-04-01 |  | Yes | 0 | 1500000 | 237453.03
[5 empty] | Total | 2931360 | 15850000 | 5110867.58
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1158761 | LINWOOD - MCWILLIE STREET 138KV CKT 1 | 2007-06-01 | 2008-01-01
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1158761 | HUGO POWER PLANT - VALLIANT 345 KV AEPW | 2010-05-01 | 2010-05-01
| HUGO POWER PLANT - VALLIANT 345 KV WFEC | 2010-05-01 | 2010-05-01
| SOUTHWEST SHREVEPORT (SW SHV 1) 345/138/13.8KV TRANSFORMER CKT 1 | 2010-06-01 | 2010-06-01
| SOUTHWEST SHREVEPORT (SW SHV 2) 345/138/13.8KV TRANSFORMER CKT 2 | 2010-06-01 | 2010-06-01
Customer | Study Number
AEPM | AG3-2006-043
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AEPM | 1162211 | OKGE | CSWS | 457 | 2011-06-01 | 2031-06-01 |  |  | 33746343 | 0 | 33956125 | 142923594.75
[9 empty] | 33746343 | 0 | 33956125 | 142923594.75
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1162211 | ARCADIA - SOONER 345kV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 27983186 | 65000000 | 119712415.57
| ARSENAL HILL - FORT HUMBUG 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 112124 | 2750000 | 392612.97
| ARSENAL HILL - MCWILLIE STREET 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 4077 | 100000 | 0
| ARSENAL HILL - WATERWORKS 69KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 81544 | 2000000 | 283981.01
| FRANKLIN SW - MIDWEST TAP 138KV CKT 1 OKGE Displacement | 2014-06-01 | 2014-06-01 |  |  | 12503 | 14588 | 42669.42
| FRANKLIN SW - MIDWEST TAP 138KV CKT 1 WFEC Displacement | 2014-06-01 | 2014-06-01 |  |  | 85705 | 100000 | 0
| MILLER - WHITE EAGLE 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 107417 | 300000 | 462164.55
| ROSEHILL - SOONER 345KV CKT 1 OKGE Displacement | 2011-06-01 | 2011-06-01 |  |  | 2796310 | 6322628 | 12064838.63
| ROSEHILL - SOONER 345KV CKT 1 WERE Displacement | 2011-06-01 | 2011-06-01 |  |  | 1626349 | 3677275 | 5835902.92
| RUSSETT - RUSSETT 138KV CKT 1 OKGE | 2016-06-01 | 2016-06-01 |  |  | 45000 | 45000 | 0
| RUSSETT - RUSSETT 138KV CKT 1 WFEC | 2016-06-01 | 2016-06-01 |  |  | 75000 | 75000 | 0
| SOUTHWEST SHREVEPORT - SOUTHWEST SHREVEPORT TAP 138KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 1026910 | 2500000 | 4129009.69
[5 empty] | Total | 33956125 | 82884491 | 142923594.76
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162211 | ALUMAX TAP - NORTHWEST TEXARKANA 138KV CKT 1 | 2008-06-01 | 2008-06-01
| BROKEN BOW - CRAIG JUNCTION 138KV CKT 1 AEPW | 2007-12-01 | 2009-03-01
| LINWOOD - MCWILLIE STREET 138KV CKT 1 | 2007-06-01 | 2008-01-01
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162211 | HUGO POWER PLANT - VALLIANT 345 KV AEPW | 2010-05-01 | 2010-05-01
| HUGO POWER PLANT - VALLIANT 345 KV WFEC | 2010-05-01 | 2010-05-01
| SOUTHWEST SHREVEPORT (SW SHV 1) 345/138/13.8KV TRANSFORMER CKT 1 | 2010-06-01 | 2010-06-01
| SOUTHWEST SHREVEPORT (SW SHV 2) 345/138/13.8KV TRANSFORMER CKT 2 | 2010-06-01 | 2010-06-01
Customer | Study Number
AEPM | AG3-2006-044
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AEPM | 1162214 | CSWS | CSWS | 455 | 2011-06-01 | 2031-06-01 |  |  | 65804529 | 0 | 65804529 | 209754477.06
[9 empty] | 65804529 | 0 | 65804529 | 209754477.06
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1162214 | HEMPSTEAD - NW TEXARKANA 345 kV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 39367878 | 56000000 | 137787769.41
| Hugo - SunnySide 345kV | 2011-06-01 | 2011-06-01 |  |  | 21744724 | 50000000 | 53337689.28
| SUGAR HILL (SUGAR HL) 138/69/12.47KV TRANSFORMER CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 1850806 | 2500000 | 6443849.42
| SUNNYSIDE 345/138KV TRANSFORMER CKT 2 | 2011-06-01 | 2011-06-01 |  |  | 2841121 | 6500000 | 12185168.95
[5 empty] | Total | 65804529 | 115000000 | 209754477.06
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162214 | SOUTHWEST SHREVEPORT (SW SHV 1) 345/138/13.8KV TRANSFORMER CKT 1 | 2010-06-01 | 2010-06-01
| SOUTHWEST SHREVEPORT (SW SHV 2) 345/138/13.8KV TRANSFORMER CKT 2 | 2010-06-01 | 2010-06-01
Third Party Limitations.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162214 | ARKANSAS NUCLEAR ONE 161 - RUSSELLVILLE NORTH 161KV CKT 1 | 2007-06-01 | 2007-06-01
| RUSSELLVILLE EAST - RUSSELLVILLE NORTH 161KV CKT 1 | 2011-06-01 | 2011-06-01
Customer | Study Number
AEPM | AG3-2006-045
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AEPM | 1162223 | CSWS | WFEC | 15 | 2007-08-01 | 2012-08-01 |  |  | 2700000 | 0 | 12753859 | 21896250.05
[9 empty] | 2700000 | 0 | 12753859 | 21896250.05
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1162223 | ARCADIA - SOONER 345kV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 309975 | 65000000 | 533561.97
| ARSENAL HILL - FORT HUMBUG 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 3430 | 2750000 | 5236.13
| ARSENAL HILL - MCWILLIE STREET 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 125 | 100000 | 0
| ARSENAL HILL - WATERWORKS 69KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 2495 | 2000000 | 3788.07
| CANEY CREEK 345/138 kV | 2011-06-01 | 2011-06-01 |  |  | 11294125 | 31000000 | 19552052.89
| CURRY COUNTY INTERCHANGE - ROOSEVELT COUNTY INTERCHANGE 115KV CKT 2 Displacement | 2007-06-01 | 2010-06-01 |  |  | 6099 | 344362 | 11902.43
| Hugo - SunnySide 345kV | 2011-06-01 | 2011-06-01 |  |  | 1033108 | 50000000 | 1600156.32
| Potter - Roosevelt 345KV Displacement | 2007-06-01 | 2010-06-01 |  |  | 41040 | 10372158 | 80037.72
| SUNNYSIDE 345/138KV TRANSFORMER CKT 2 | 2011-06-01 | 2011-06-01 |  |  | 63462 | 6500000 | 109514.53
[5 empty] | Total | 12753859 | 168066520 | 21896250.06
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162223 | ANADARKO - CYRIL 69KV CKT 1 | 2011-06-01 | 2011-06-01
| ANADARKO - GEORGIA 138KV CKT 1 | 2011-06-01 | 2011-06-01
| CYRIL - MEDICINE PARK JCT 69KV CKT 1 | 2011-06-01 | 2011-06-01
| DUNCAN (DUNCAN) 138/69/13.8KV TRANSFORMER CKT 1 | 2011-06-01 | 2011-06-01
| FLETCHER - MEDICINE PARK JCT 69KV CKT 1 | 2011-06-01 | 2011-06-01
| FRANKLIN SW 138/69KV TRANSFORMER CKT 1 | 2011-06-01 | 2011-06-01
| LINWOOD - MCWILLIE STREET 138KV CKT 1 | 2007-06-01 | 2008-01-01
| Sayre interconnect | 2011-06-01 | 2011-06-01
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162223 | ANADARKO 138/69KV TRANSFORMER CKT 1 | 2011-06-01 | 2011-06-01
| ARCADIA - REDBUD 345 KV CKT 1 | 2006-06-01 | 2006-06-01
| ARCADIA - REDBUD 345 KV CKT 2 | 2006-06-01 | 2006-06-01
| BEELINE - EXPLORER GLENPOOL 138KV CKT 1 | 2009-06-01 | 2009-06-01
| BROWN - EXPLORER TAP 138KV CKT 1 | 2008-06-01 | 2008-06-01
| EXPLORER GLENPOOL - RIVERSIDE STATION 138KV CKT 1 AEPW | 2009-06-01 | 2009-06-01
| EXPLORER GLENPOOL - RIVERSIDE STATION 138KV CKT 1 OKGE | 2009-06-01 | 2009-06-01
| SOUTHWEST SHREVEPORT (SW SHV 1) 345/138/13.8KV TRANSFORMER CKT 1 | 2010-06-01 | 2010-06-01
| SOUTHWEST SHREVEPORT (SW SHV 2) 345/138/13.8KV TRANSFORMER CKT 2 | 2010-06-01 | 2010-06-01
Potential reservation deferral and redispatch requirement on the following upgrades due to positive MW Impact on limitations that require upgrade. No cost assignment due to negative MW impact on defined upgrade.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162223 | ROOSEVELT COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 1 Displacement | 2007-06-01 | 2010-06-01
Customer | Study Number
AEPM | AG3-2006-072
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AEPM | 1162484 | CSWS | EES | 11 | 2009-01-01 | 2014-01-01 |  |  | 94131 | 0 | 794332 | 129329.36
[9 empty] | 94131 | 0 | 794332 | 129329.36
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1162484 | 5 TRIBES - HANCOCK 161KV CKT 1 Displacement | 2007-06-01 | 2009-06-01 |  |  | 394 | 100000 | 0
| 5 TRIBES - PECAN CREEK 161KV CKT 1 Displacement | 2007-06-01 | 2009-06-01 |  |  | 1840 | 466473 | 4912.61
| ARSENAL HILL - FORT HUMBUG 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 4848 | 2750000 | 8319.33
| ARSENAL HILL - MCWILLIE STREET 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 176 | 100000 | 0
| ARSENAL HILL - WATERWORKS 69KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 3526 | 2000000 | 6017.82
| BEAVER - EUREKA SPRINGS 161KV CKT 1 AEPW | 2013-06-01 | 2013-06-01 |  |  | 70579 | 850000 | 74662.23
| BEAVER - EUREKA SPRINGS 161KV CKT 1 SWPA | 2013-06-01 | 2013-06-01 |  |  | 199283 | 2400000 | 0
| COCODRIE 230/138KV TRANSFORMER CKT 1 | 2011-12-01 | 2011-12-01 |  |  | 500348 | 6000000 | 0
| PECAN CREEK (PECANCK1) 345/161/13.8KV TRANSFORMER CKT 1 Displacement | 2007-06-01 | 2009-06-01 |  |  | 13338 | 3381928 | 35417.37
[5 empty] | Total | 794332 | 18048401 | 129329.36
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162484 | LINWOOD - MCWILLIE STREET 138KV CKT 1 | 2007-06-01 | 2008-01-01
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162484 | BEELINE - EXPLORER GLENPOOL 138KV CKT 1 | 2009-06-01 | 2009-06-01
| COFFEYVILLE TAP - DEARING 138KV CKT 1 AEPW Displacement | 2011-06-01 | 2011-06-01
| COFFEYVILLE TAP - DEARING 138KV CKT 1 WERE Displacement | 2011-06-01 | 2011-06-01
| EXPLORER GLENPOOL - RIVERSIDE STATION 138KV CKT 1 AEPW | 2009-06-01 | 2009-06-01
| EXPLORER GLENPOOL - RIVERSIDE STATION 138KV CKT 1 OKGE | 2009-06-01 | 2009-06-01
| SOUTHWEST SHREVEPORT (SW SHV 1) 345/138/13.8KV TRANSFORMER CKT 1 | 2010-06-01 | 2010-06-01
| SOUTHWEST SHREVEPORT (SW SHV 2) 345/138/13.8KV TRANSFORMER CKT 2 | 2010-06-01 | 2010-06-01
Customer | Study Number
AEPM | AG3-2006-073
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AEPM | 1162486 | CSWS | EES | 25 | 2009-01-01 | 2014-01-01 |  |  | 217664 | 0 | 1867349 | 297164.2
[9 empty] | 217664 | 0 | 1867349 | 297164.2
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1162486 | 5 TRIBES - HANCOCK 161KV CKT 1 Displacement | 2007-06-01 | 2009-06-01 |  |  | 888 | 100000 | 0
| 5 TRIBES - PECAN CREEK 161KV CKT 1 Displacement | 2007-06-01 | 2009-06-01 |  |  | 4140 | 466473 | 11053.37
| ARSENAL HILL - FORT HUMBUG 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 10870 | 2750000 | 18653.29
| ARSENAL HILL - MCWILLIE STREET 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 395 | 100000 | 0
| ARSENAL HILL - WATERWORKS 69KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 7906 | 2000000 | 13493.17
| BEAVER - EUREKA SPRINGS 161KV CKT 1 AEPW | 2013-06-01 | 2013-06-01 |  |  | 164733 | 850000 | 174263.35
| BEAVER - EUREKA SPRINGS 161KV CKT 1 SWPA | 2013-06-01 | 2013-06-01 |  |  | 465127 | 2400000 | 0
| COCODRIE 230/138KV TRANSFORMER CKT 1 | 2011-12-01 | 2011-12-01 |  |  | 1183275 | 6000000 | 0
| PECAN CREEK (PECANCK1) 345/161/13.8KV TRANSFORMER CKT 1 Displacement | 2007-06-01 | 2009-06-01 |  |  | 30015 | 3381928 | 79701.02
[5 empty] | Total | 1867349 | 18048401 | 297164.2
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162486 | LINWOOD - MCWILLIE STREET 138KV CKT 1 | 2007-06-01 | 2008-01-01
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162486 | BEELINE - EXPLORER GLENPOOL 138KV CKT 1 | 2009-06-01 | 2009-06-01
| COFFEYVILLE TAP - DEARING 138KV CKT 1 AEPW Displacement | 2011-06-01 | 2011-06-01
| COFFEYVILLE TAP - DEARING 138KV CKT 1 WERE Displacement | 2011-06-01 | 2011-06-01
| EXPLORER GLENPOOL - RIVERSIDE STATION 138KV CKT 1 AEPW | 2009-06-01 | 2009-06-01
| EXPLORER GLENPOOL - RIVERSIDE STATION 138KV CKT 1 OKGE | 2009-06-01 | 2009-06-01
| SOUTHWEST SHREVEPORT (SW SHV 1) 345/138/13.8KV TRANSFORMER CKT 1 | 2010-06-01 | 2010-06-01
| SOUTHWEST SHREVEPORT (SW SHV 2) 345/138/13.8KV TRANSFORMER CKT 2 | 2010-06-01 | 2010-06-01
Customer | Study Number
AEPM | AG3-2006-074
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AEPM | 1162487 | CSWS | EES | 20 | 2009-01-01 | 2014-01-01 |  |  | 164867 | 0 | 4946997 | 224558.88
[9 empty] | 164867 | 0 | 4946997 | 224558.88
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1162487 | 5 TRIBES - HANCOCK 161KV CKT 1 Displacement | 2007-06-01 | 2009-06-01 |  |  | 656 | 100000 | 0
| 5 TRIBES - PECAN CREEK 161KV CKT 1 Displacement | 2007-06-01 | 2009-06-01 |  |  | 3059 | 466473 | 8167.21
| ARSENAL HILL - FORT HUMBUG 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 8663 | 2750000 | 14866
| ARSENAL HILL - MCWILLIE STREET 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 315 | 100000 | 0
| ARSENAL HILL - WATERWORKS 69KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 6300 | 2000000 | 10752.21
| BAYOU RAPIDES - TWIN BRIDGES 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 1230000 | 1230000 | 0
| BEAVER - EUREKA SPRINGS 161KV CKT 1 AEPW | 2013-06-01 | 2013-06-01 |  |  | 124665 | 850000 | 131877.28
| BEAVER - EUREKA SPRINGS 161KV CKT 1 SWPA | 2013-06-01 | 2013-06-01 |  |  | 351995 | 2400000 | 0
| COCODRIE 230/138KV TRANSFORMER CKT 1 | 2011-12-01 | 2011-12-01 |  |  | 3199164 | 6000000 | 0
| PECAN CREEK (PECANCK1) 345/161/13.8KV TRANSFORMER CKT 1 Displacement | 2007-06-01 | 2009-06-01 |  |  | 22180 | 3381928 | 58896.18
[5 empty] | Total | 4946997 | 19278401 | 224558.88
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162487 | LINWOOD - MCWILLIE STREET 138KV CKT 1 | 2007-06-01 | 2008-01-01
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162487 | BEELINE - EXPLORER GLENPOOL 138KV CKT 1 | 2009-06-01 | 2009-06-01
| COFFEYVILLE TAP - DEARING 138KV CKT 1 AEPW Displacement | 2011-06-01 | 2011-06-01
| COFFEYVILLE TAP - DEARING 138KV CKT 1 WERE Displacement | 2011-06-01 | 2011-06-01
| EXPLORER GLENPOOL - RIVERSIDE STATION 138KV CKT 1 AEPW | 2009-06-01 | 2009-06-01
| EXPLORER GLENPOOL - RIVERSIDE STATION 138KV CKT 1 OKGE | 2009-06-01 | 2009-06-01
| HUGO POWER PLANT - VALLIANT 345 KV AEPW | 2010-05-01 | 2010-05-01
| HUGO POWER PLANT - VALLIANT 345 KV WFEC | 2010-05-01 | 2010-05-01
| SOUTHWEST SHREVEPORT (SW SHV 1) 345/138/13.8KV TRANSFORMER CKT 1 | 2010-06-01 | 2010-06-01
| SOUTHWEST SHREVEPORT (SW SHV 2) 345/138/13.8KV TRANSFORMER CKT 2 | 2010-06-01 | 2010-06-01
Customer | Study Number
AEPM | AG3-2006-075
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AEPM | 1162491 | CSWS | EES | 19 | 2009-01-01 | 2014-01-01 |  |  | 172001 | 0 | 541125 | 234732.36
[9 empty] | 172001 | 0 | 541125 | 234732.36
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1162491 | 5 TRIBES - HANCOCK 161KV CKT 1 Displacement | 2007-06-01 | 2009-06-01 |  |  | 702 | 100000 | 0
| 5 TRIBES - PECAN CREEK 161KV CKT 1 Displacement | 2007-06-01 | 2009-06-01 |  |  | 3277 | 466473 | 8749.25
| ARSENAL HILL - FORT HUMBUG 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 8450 | 2750000 | 14500.49
| ARSENAL HILL - MCWILLIE STREET 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 307 | 100000 | 0
| ARSENAL HILL - WATERWORKS 69KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 6145 | 2000000 | 10487.67
| BEAVER - EUREKA SPRINGS 161KV CKT 1 AEPW | 2013-06-01 | 2013-06-01 |  |  | 130374 | 850000 | 137916.57
| BEAVER - EUREKA SPRINGS 161KV CKT 1 SWPA | 2013-06-01 | 2013-06-01 |  |  | 368115 | 2400000 | 0
| PECAN CREEK (PECANCK1) 345/161/13.8KV TRANSFORMER CKT 1 Displacement | 2007-06-01 | 2009-06-01 |  |  | 23755 | 3381928 | 63078.39
[5 empty] | Total | 541125 | 12048401 | 234732.37
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162491 | LINWOOD - MCWILLIE STREET 138KV CKT 1 | 2007-06-01 | 2008-01-01
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162491 | BEELINE - EXPLORER GLENPOOL 138KV CKT 1 | 2009-06-01 | 2009-06-01
| COFFEYVILLE TAP - DEARING 138KV CKT 1 AEPW Displacement | 2011-06-01 | 2011-06-01
| COFFEYVILLE TAP - DEARING 138KV CKT 1 WERE Displacement | 2011-06-01 | 2011-06-01
| EXPLORER GLENPOOL - RIVERSIDE STATION 138KV CKT 1 AEPW | 2009-06-01 | 2009-06-01
| EXPLORER GLENPOOL - RIVERSIDE STATION 138KV CKT 1 OKGE | 2009-06-01 | 2009-06-01
| SOUTHWEST SHREVEPORT (SW SHV 1) 345/138/13.8KV TRANSFORMER CKT 1 | 2010-06-01 | 2010-06-01
| SOUTHWEST SHREVEPORT (SW SHV 2) 345/138/13.8KV TRANSFORMER CKT 2 | 2010-06-01 | 2010-06-01
Customer | Study Number
AEPM | AG3-2006-076
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AEPM | 1162492 | CSWS | EES | 9 | 2009-01-01 | 2014-01-01 |  |  | 74619 | 0 | 1349622 | 102411.27
[9 empty] | 74619 | 0 | 1349622 | 102411.27
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1162492 | 5 TRIBES - HANCOCK 161KV CKT 1 Displacement | 2007-06-01 | 2009-06-01 |  |  | 306 | 100000 | 0
| 5 TRIBES - PECAN CREEK 161KV CKT 1 Displacement | 2007-06-01 | 2009-06-01 |  |  | 1425 | 466473 | 3804.6
| ARSENAL HILL - FORT HUMBUG 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 4132 | 2750000 | 7090.65
| ARSENAL HILL - MCWILLIE STREET 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 150 | 100000 | 0
| ARSENAL HILL - WATERWORKS 69KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 3005 | 2000000 | 5128.63
| BEAVER - EUREKA SPRINGS 161KV CKT 1 AEPW | 2013-06-01 | 2013-06-01 |  |  | 55723 | 850000 | 58946.76
| BEAVER - EUREKA SPRINGS 161KV CKT 1 SWPA | 2013-06-01 | 2013-06-01 |  |  | 157334 | 2400000 | 0
| COCODRIE 230/138KV TRANSFORMER CKT 1 | 2011-12-01 | 2011-12-01 |  |  | 1117213 | 6000000 | 0
| PECAN CREEK (PECANCK1) 345/161/13.8KV TRANSFORMER CKT 1 Displacement | 2007-06-01 | 2009-06-01 |  |  | 10334 | 3381928 | 27440.63
[5 empty] | Total | 1349622 | 18048401 | 102411.27
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162492 | LINWOOD - MCWILLIE STREET 138KV CKT 1 | 2007-06-01 | 2008-01-01
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162492 | BEELINE - EXPLORER GLENPOOL 138KV CKT 1 | 2009-06-01 | 2009-06-01
| COFFEYVILLE TAP - DEARING 138KV CKT 1 AEPW Displacement | 2011-06-01 | 2011-06-01
| COFFEYVILLE TAP - DEARING 138KV CKT 1 WERE Displacement | 2011-06-01 | 2011-06-01
| EXPLORER GLENPOOL - RIVERSIDE STATION 138KV CKT 1 AEPW | 2009-06-01 | 2009-06-01
| EXPLORER GLENPOOL - RIVERSIDE STATION 138KV CKT 1 OKGE | 2009-06-01 | 2009-06-01
| HUGO POWER PLANT - VALLIANT 345 KV AEPW | 2010-05-01 | 2010-05-01
| HUGO POWER PLANT - VALLIANT 345 KV WFEC | 2010-05-01 | 2010-05-01
| SOUTHWEST SHREVEPORT (SW SHV 1) 345/138/13.8KV TRANSFORMER CKT 1 | 2010-06-01 | 2010-06-01
| SOUTHWEST SHREVEPORT (SW SHV 2) 345/138/13.8KV TRANSFORMER CKT 2 | 2010-06-01 | 2010-06-01
Customer | Study Number
AEPM | AG3-2006-077
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AEPM | 1162494 | CSWS | EES | 17 | 2009-01-01 | 2014-01-01 |  |  | 142745 | 0 | 1067526 | 194374.8
[9 empty] | 142745 | 0 | 1067526 | 194374.8
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1162494 | 5 TRIBES - HANCOCK 161KV CKT 1 Displacement | 2007-06-01 | 2009-06-01 |  |  | 548 | 100000 | 0
| 5 TRIBES - PECAN CREEK 161KV CKT 1 Displacement | 2007-06-01 | 2009-06-01 |  |  | 2555 | 466473 | 6821.58
| ARSENAL HILL - FORT HUMBUG 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 8547 | 2750000 | 14666.94
| ARSENAL HILL - MCWILLIE STREET 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 311 | 100000 | 0
| ARSENAL HILL - WATERWORKS 69KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 6216 | 2000000 | 10608.85
| BEAVER - EUREKA SPRINGS 161KV CKT 1 AEPW | 2013-06-01 | 2013-06-01 |  |  | 106902 | 850000 | 113086.64
| BEAVER - EUREKA SPRINGS 161KV CKT 1 SWPA | 2013-06-01 | 2013-06-01 |  |  | 301842 | 2400000 | 0
| Natchitoches Capacitor | 2011-06-01 | 2011-06-01 |  |  | 622080 | 622080 | 0
| PECAN CREEK (PECANCK1) 345/161/13.8KV TRANSFORMER CKT 1 Displacement | 2007-06-01 | 2009-06-01 |  |  | 18525 | 3381928 | 49190.79
[5 empty] | Total | 1067526 | 12670481 | 194374.8
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162494 | LINWOOD - MCWILLIE STREET 138KV CKT 1 | 2007-06-01 | 2008-01-01
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162494 | BEELINE - EXPLORER GLENPOOL 138KV CKT 1 | 2009-06-01 | 2009-06-01
| COFFEYVILLE TAP - DEARING 138KV CKT 1 AEPW Displacement | 2011-06-01 | 2011-06-01
| COFFEYVILLE TAP - DEARING 138KV CKT 1 WERE Displacement | 2011-06-01 | 2011-06-01
| EXPLORER GLENPOOL - RIVERSIDE STATION 138KV CKT 1 AEPW | 2009-06-01 | 2009-06-01
| EXPLORER GLENPOOL - RIVERSIDE STATION 138KV CKT 1 OKGE | 2009-06-01 | 2009-06-01
| HUGO POWER PLANT - VALLIANT 345 KV AEPW | 2010-05-01 | 2010-05-01
| HUGO POWER PLANT - VALLIANT 345 KV WFEC | 2010-05-01 | 2010-05-01
| SOUTHWEST SHREVEPORT (SW SHV 1) 345/138/13.8KV TRANSFORMER CKT 1 | 2010-06-01 | 2010-06-01
| SOUTHWEST SHREVEPORT (SW SHV 2) 345/138/13.8KV TRANSFORMER CKT 2 | 2010-06-01 | 2010-06-01
Customer | Study Number
AEPM | AG3-2006-091
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AEPM | 1162766 | CSWS | CSWS | 100 | 2007-06-01 | 2008-06-01 | 2009-06-01 | 2010-06-01 | 0 | 1260000 | 717899 | 1440733.94
[9 empty] | 0 | 1260000 | 717899 | 1440733.94
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1162766 | 5 TRIBES - HANCOCK 161KV CKT 1 Displacement | 2007-06-01 | 2009-06-01 |  | Yes | 9347 | 100000 | 0
| 5 TRIBES - PECAN CREEK 161KV CKT 1 Displacement | 2007-06-01 | 2009-06-01 |  | Yes | 43601 | 466473 | 101513.89
| PECAN CREEK (PECANCK1) 345/161/13.8KV TRANSFORMER CKT 1 Displacement | 2007-06-01 | 2009-06-01 |  | Yes | 316109 | 3381928 | 731976.47
| SOUTHWEST SHREVEPORT - SOUTHWEST SHREVEPORT TAP 138KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 348842 | 2500000 | 607243.58
[5 empty] | Total | 717899 | 6448401 | 1440733.94
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162766 | BROKEN BOW - CRAIG JUNCTION 138KV CKT 1 AEPW | 2007-12-01 | 2009-03-01
| LINWOOD - MCWILLIE STREET 138KV CKT 1 | 2007-06-01 | 2008-01-01
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162766 | ARCADIA - REDBUD 345 KV CKT 1 | 2006-06-01 | 2006-06-01
| ARCADIA - REDBUD 345 KV CKT 2 | 2006-06-01 | 2006-06-01
Customer | Study Number
AEPM | AG3-2006-092
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AEPM | 1162763 | CSWS | CSWS | 100 | 2007-06-01 | 2008-06-01 | 2009-06-01 | 2010-06-01 | 0 | 1260000 | 423497 | 796369.4
[9 empty] | 0 | 1260000 | 423497 | 796369.4
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1162763 | 5 TRIBES - HANCOCK 161KV CKT 1 Displacement | 2007-06-01 | 2009-06-01 |  | Yes | 10726 | 100000 | 0
| 5 TRIBES - PECAN CREEK 161KV CKT 1 Displacement | 2007-06-01 | 2009-06-01 |  | Yes | 50033 | 466473 | 96993.56
| PECAN CREEK (PECANCK1) 345/161/13.8KV TRANSFORMER CKT 1 Displacement | 2007-06-01 | 2009-06-01 |  | Yes | 362738 | 3381928 | 699375.84
[5 empty] | Total | 423497 | 3948401 | 796369.4
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162763 | BROKEN BOW - CRAIG JUNCTION 138KV CKT 1 AEPW | 2007-12-01 | 2009-03-01
| LINWOOD - MCWILLIE STREET 138KV CKT 1 | 2007-06-01 | 2008-01-01
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162763 | ARCADIA - REDBUD 345 KV CKT 1 | 2006-06-01 | 2006-06-01
| ARCADIA - REDBUD 345 KV CKT 2 | 2006-06-01 | 2006-06-01
| HUGO POWER PLANT - VALLIANT 345 KV AEPW | 2010-05-01 | 2010-05-01
| HUGO POWER PLANT - VALLIANT 345 KV WFEC | 2010-05-01 | 2010-05-01
| SOUTHWEST SHREVEPORT (SW SHV 1) 345/138/13.8KV TRANSFORMER CKT 1 | 2010-06-01 | 2010-06-01
| SOUTHWEST SHREVEPORT (SW SHV 2) 345/138/13.8KV TRANSFORMER CKT 2 | 2010-06-01 | 2010-06-01
Customer | Study Number
AEPM | AG3-2006-094
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AEPM | 1163062 | CSWS | CSWS | 550 | 2010-06-01 | 2015-06-01 |  |  | 41165604 | 0 | 41256854 | 74814620.37
[9 empty] | 41165604 | 0 | 41256854 | 74814620.37
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1163062 | ARSENAL HILL - FORT HUMBUG 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 2509388 | 2750000 | 4837880.25
| ARSENAL HILL - MCWILLIE STREET 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 91250 | 100000 | 0
| ARSENAL HILL - WATERWORKS 69KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 1825009 | 2000000 | 3499318.96
| ARSENAL HILL (ARSHILL1) 138/69/12.47KV TRANSFORMER CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 2500000 | 2500000 | 3702088.17
| ARSENAL HILL (ARSHILL2) 138/69/14.5KV TRANSFORMER CKT 2 | 2011-06-01 | 2011-06-01 |  |  | 2500000 | 2500000 | 3702088.17
| DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 AEPW | 2011-06-01 | 2011-06-01 |  |  | 7102862 | 9000000 | 14134555.3
| HEMPSTEAD - NW TEXARKANA 345 kV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 2391016 | 56000000 | 4607574.66
| Hugo - SunnySide 345kV | 2011-06-01 | 2011-06-01 |  |  | 19790467 | 50000000 | 34634576.84
| SUNNYSIDE 345/138KV TRANSFORMER CKT 2 | 2011-06-01 | 2011-06-01 |  |  | 2546862 | 6500000 | 5696538.02
[5 empty] | Total | 41256854 | 131350000 | 74814620.37
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1163062 | ARSENAL HILL - NORTH MARKET 69KV CKT 1 | 2011-06-01 | 2011-06-01
| LINWOOD - MCWILLIE STREET 138KV CKT 1 | 2007-06-01 | 2008-01-01
| PORT ROBSON - REDPOINT 138kV | 2011-06-01 | 2011-06-01
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1163062 | SOUTHWEST SHREVEPORT (SW SHV 1) 345/138/13.8KV TRANSFORMER CKT 1 | 2010-06-01 | 2010-06-01
| SOUTHWEST SHREVEPORT (SW SHV 2) 345/138/13.8KV TRANSFORMER CKT 2 | 2010-06-01 | 2010-06-01
Third Party Limitations.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1163062 | ARKANSAS NUCLEAR ONE 161 - RUSSELLVILLE NORTH 161KV CKT 1 | 2007-06-01 | 2007-06-01
| DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 ENTR | 2011-06-01 | 2011-06-01
| RUSSELLVILLE EAST - RUSSELLVILLE NORTH 161KV CKT 1 | 2011-06-01 | 2011-06-01
Customer | Study Number
AEPM | AG3-2006-095
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AEPM | 1162768 | OKGE | CSWS | 100 | 2007-06-01 | 2008-06-01 |  |  | 0 | 1260000 | 0 | 0
[9 empty] | 0 | 1260000 | 0 | 0
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1162768 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162768 | ARCADIA - REDBUD 345 KV CKT 1 | 2006-06-01 | 2006-06-01
| ARCADIA - REDBUD 345 KV CKT 2 | 2006-06-01 | 2006-06-01
Customer | Study Number
GRDX | AG3-2006-032
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
GRDX | 1161666 | CSWS | GRDA | 150 | 2007-02-01 | 2008-02-01 | 2009-06-01 | 2010-06-01 | 0 | 0 | 2123987 | 3865347.61
[9 empty] | 0 | 0 | 2123987 | 3865347.61
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1161666 | 5 TRIBES - HANCOCK 161KV CKT 1 Displacement | 2007-06-01 | 2009-06-01 |  | No | 23793 | 100000 | 0
| 5 TRIBES - PECAN CREEK 161KV CKT 1 Displacement | 2007-06-01 | 2009-06-01 |  | No | 110988 | 466473 | 258407.47
| CLAREMORE (CLRAUTO3) 161/69/13.8KV TRANSFORMER CKT 3 | 2007-06-01 | 2009-06-01 |  | No | 1184545 | 2300000 | 1743681.21
| PECAN CREEK (PECANCK1) 345/161/13.8KV TRANSFORMER CKT 1 Displacement | 2007-06-01 | 2009-06-01 |  | No | 804661 | 3381928 | 1863258.93
[5 empty] | Total | 2123987 | 6248401 | 3865347.61
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1161666 | Kansas 7.2MVAR Cap | 2007-06-01 | 2009-06-01 |  | No
| SCoffeyville Capacitor | 2008-06-01 | 2008-06-01
| Turkey Ford 7.2MVAR Cap | 2007-06-01 | 2009-06-01 |  | No
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1161666 | ARCADIA - REDBUD 345 KV CKT 1 | 2006-06-01 | 2006-06-01
| ARCADIA - REDBUD 345 KV CKT 2 | 2006-06-01 | 2006-06-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1161666 | CHAMBER SPRINGS - TONTITOWN 161KV CKT 1 | 2006-12-01 | 2007-06-01 |  | No
| TALLANT - RAMONA 161kV CKT 1 | 2007-04-01 | 2008-10-01 |  | No
Customer | Study Number
GRDX | AG3-2006-033
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
GRDX | 1161667 | OKGE | GRDA | 150 | 2007-02-01 | 2008-02-01 | 2009-06-01 | 2010-06-01 | 0 | 0 | 1598786 | 2733549.85
[9 empty] | 0 | 0 | 1598786 | 2733549.85
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1161667 | 5 TRIBES - HANCOCK 161KV CKT 1 Displacement | 2007-06-01 | 2009-06-01 |  | No | 12241 | 100000 | 0
| 5 TRIBES - PECAN CREEK 161KV CKT 1 Displacement | 2007-06-01 | 2009-06-01 |  | No | 57102 | 466473 | 132947.56
| CLAREMORE (CLRAUTO3) 161/69/13.8KV TRANSFORMER CKT 3 | 2007-06-01 | 2009-06-01 |  | No | 1115455 | 2300000 | 1641978.93
| PECAN CREEK (PECANCK1) 345/161/13.8KV TRANSFORMER CKT 1 Displacement | 2007-06-01 | 2009-06-01 |  | No | 413988 | 3381928 | 958623.37
[5 empty] | Total | 1598786 | 6248401 | 2733549.86
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1161667 | Kansas 7.2MVAR Cap | 2007-06-01 | 2009-06-01 |  | No
| SCoffeyville Capacitor | 2008-06-01 | 2008-06-01
| Turkey Ford 7.2MVAR Cap | 2007-06-01 | 2009-06-01 |  | No
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1161667 | ARCADIA - REDBUD 345 KV CKT 1 | 2006-06-01 | 2006-06-01
| ARCADIA - REDBUD 345 KV CKT 2 | 2006-06-01 | 2006-06-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1161667 | TALLANT - RAMONA 161kV CKT 1 | 2007-04-01 | 2008-10-01 |  | No
Customer | Study Number
GSEC | AG3-2006-100
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
GSEC | 1162688 | SPS | SPS | 10 | 2007-03-01 | 2037-03-01 | 2009-04-01 | 2039-04-01 | 0 | 0 | 515825 | 1197199.51
[9 empty] | 0 | 0 | 515825 | 1197199.51
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1162688 | CURRY COUNTY INTERCHANGE - ROOSEVELT COUNTY INTERCHANGE 115KV CKT 2 Displacement | 2007-06-01 | 2010-06-01 |  | No | 10545 | 344362 | 51322.94
| GSEC Midway Interconnection #1 | 2007-06-01 | 2007-06-01 |  | No | 70000 | 70000 | 0
| GSEC Midway Interconnection #2 | 2011-06-01 | 2011-06-01 |  | No | 200000 | 200000 | 0
| ROOSEVELT COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 1 Displacement | 2007-06-01 | 2010-06-01 |  | No | 235280 | 858753 | 1145876.57
[5 empty] | Total | 515825 | 1473115 | 1197199.51
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162688 | ELK CITY - ELK CITY 69KV CKT 1 AEPW | 2008-12-01 | 2009-04-01 |  | No
| Hitchland 345 and 115 kV Interchange | 2010-06-01 | 2010-06-01
| Mooreland - Potter 345 kV SPS | 2016-06-01 | 2016-06-01
| Mooreland - Potter 345 kV WFEC | 2016-06-01 | 2016-06-01
| Mooreland 345/138 kV Transformer | 2016-06-01 | 2016-06-01
| POTTER COUNTY INTERCHANGE (POTTR CO) 345/230/13.2KV TRANSFORMER CKT 2 | 2016-06-01 | 2016-06-01
| Pringle - Etter 115 kV | 2010-06-01 | 2010-06-01
| Sayre interconnect | 2011-06-01 | 2011-06-01
| SNYDER - SNYDER INTERCONNECTION | 2016-06-01 | 2016-06-01
| Spearville - Mooreland 345 kV SUNC | 2016-06-01 | 2016-06-01
| Spearville - Mooreland 345 kV WFEC | 2016-06-01 | 2016-06-01
| Tex-Hitchland-Sherman Tap 115 kV ckt | 2010-06-01 | 2010-06-01
| TUCO INTERCHANGE 345/115KV TRANSFORMER CKT 1 | 2016-06-01 | 2016-06-01
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162688 | CACHE - SNYDER 138KV CKT 1 | 2008-06-01 | 2008-06-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162688 | ALTUS JCT TAP - RUSSELL 138KV CKT 1 | 2015-06-01 | 2008-06-01
Potential reservation deferral and redispatch requirement on the following upgrades due to positive MW Impact on limitations that require upgrade. No cost assignment due to negative MW impact on defined upgrade.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162688 | Potter - Roosevelt 345KV Displacement | 2007-06-01 | 2010-06-01 |  | No
Customer | Study Number
KCPS | AG3-2006-101
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
KCPS | 1162685 | AECI | KCPL | 50 | 2007-06-01 | 2008-06-01 | 2008-06-01 | 2009-06-01 | 0 | 0 | 0 | 0
KCPS | 1162686 | AECI | KCPL | 50 | 2007-06-01 | 2008-06-01 | 2008-06-01 | 2009-06-01 | 0 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0 | 0
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1162685 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
1162686 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162685 | ARCADIA - REDBUD 345 KV CKT 1 | 2006-06-01 | 2006-06-01
| ARCADIA - REDBUD 345 KV CKT 2 | 2006-06-01 | 2006-06-01
| LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01
1162686 | ARCADIA - REDBUD 345 KV CKT 1 | 2006-06-01 | 2006-06-01
| ARCADIA - REDBUD 345 KV CKT 2 | 2006-06-01 | 2006-06-01
| LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162685 | LACYGNE-PAOLA-WEST GARDER 345KV | 2007-06-01 | 2008-06-01 |  | Yes
1162686 | LACYGNE-PAOLA-WEST GARDER 345KV | 2007-06-01 | 2008-06-01 |  | Yes
Customer | Study Number
KCPS | AG3-2006-103
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
KCPS | 1162650 | KCPL | CLEC | 52 | 2007-02-01 | 2008-02-01 | 2008-06-01 | 2009-06-01 | 0 | 655200 | 0 | 0
KCPS | 1162651 | KCPL | CLEC | 51 | 2007-02-01 | 2008-02-01 | 2008-06-01 | 2009-06-01 | 0 | 642600 | 0 | 0
[9 empty] | 0 | 1297800 | 0 | 0
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1162650 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
1162651 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162650 | BROKEN BOW - CRAIG JUNCTION 138KV CKT 1 AEPW | 2007-12-01 | 2009-03-01
1162651 | BROKEN BOW - CRAIG JUNCTION 138KV CKT 1 AEPW | 2007-12-01 | 2009-03-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162650 | LACYGNE-PAOLA-WEST GARDER 345KV | 2007-06-01 | 2008-06-01 |  | Yes
1162651 | LACYGNE-PAOLA-WEST GARDER 345KV | 2007-06-01 | 2008-06-01 |  | Yes
Customer | Study Number
KCPS | AG3-2006-104
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
KCPS | 1162654 | KCPL | SPA | 16 | 2007-02-01 | 2008-02-01 | 2009-06-01 | 2010-06-01 | 0 | 172800 | 62237 | 140558.67
[9 empty] | 0 | 172800 | 62237 | 140558.67
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1162654 | 5 TRIBES - HANCOCK 161KV CKT 1 Displacement | 2007-06-01 | 2009-06-01 |  | Yes | 1576 | 100000 | 0
| 5 TRIBES - PECAN CREEK 161KV CKT 1 Displacement | 2007-06-01 | 2009-06-01 |  | Yes | 7353 | 466473 | 17119.6
| PECAN CREEK (PECANCK1) 345/161/13.8KV TRANSFORMER CKT 1 Displacement | 2007-06-01 | 2009-06-01 |  | Yes | 53308 | 3381928 | 123439.07
[5 empty] | Total | 62237 | 3948401 | 140558.67
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162654 | IATAN - NASHUA 345KV CKT 1 | 2010-06-01 | 2010-06-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162654 | LACYGNE-PAOLA-WEST GARDER 345KV | 2007-06-01 | 2008-06-01 |  | Yes
Third Party Limitations.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162654 | ARKANSAS NUCLEAR ONE 161 - RUSSELLVILLE NORTH 161KV CKT 1 | 2007-06-01 | 2007-06-01
Customer | Study Number
KCPS | AG3-2006-106
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
KCPS | 1162649 | WPEK | KCPL | 101 | 2007-02-01 | 2037-02-01 | 2010-01-01 | 2040-01-01 | 1800000 | 0 | 2412312 | 10671156.76
[9 empty] | 1800000 | 0 | 2412312 | 10671156.76
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1162649 | COLLEGE - CRAIG 161KV CKT 1 | 2016-06-01 | 2016-06-01 |  |  | 700000 | 700000 | 2415301.93
| CURRY COUNTY INTERCHANGE - ROOSEVELT COUNTY INTERCHANGE 115KV CKT 2 Displacement | 2007-06-01 | 2010-06-01 |  |  | 101791 | 344362 | 485704.9
| MEDICINE LODGE - SUN CITY 115KV CKT 1 | 2007-06-01 | 2008-01-01 |  | Yes | 150000 | 150000 | 822787.94
| Potter - Roosevelt 345KV Displacement | 2007-06-01 | 2010-06-01 |  |  | 1441958 | 10372158 | 6875842.75
| SPS MUST RUN GENERATION #1 | 2007-04-01 | 2007-04-01 |  |  | 0 | 0 | 0
| ST JOHN CAPACITOR Displacement | 2008-06-01 | 2008-06-01 |  |  | 18563 | 114189 | 71519.24
[5 empty] | Total | 2412312 | 11680709 | 10671156.76
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162649 | AVONDALE - GLADSTONE 161KV CKT 1 | 2016-06-01 | 2016-06-01
| CROSSTOWN - NEAST 161KV CKT 1 | 2015-06-01 | 2015-06-01
| GREENSBURG - JUDSON LARGE 115KV CKT 1 | 2006-12-01 | 2007-09-01 |  | Yes
| KINSLEY CAPACITOR | 2007-06-01 | 2009-01-01 |  | No
| MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | 2006-12-01 | 2010-01-01 |  | Yes
| Sayre interconnect | 2011-06-01 | 2011-06-01
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162649 | IATAN - NASHUA 345KV CKT 1 | 2010-06-01 | 2010-06-01
| LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162649 | LACYGNE-PAOLA-WEST GARDER 345KV | 2007-06-01 | 2008-06-01 |  | Yes
| RENO - SUMMIT 345KV | 2011-01-01 | 2011-01-01
Potential reservation deferral and redispatch requirement on the following upgrades due to positive MW Impact on limitations that require upgrade. No cost assignment due to negative MW impact on defined upgrade.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162649 | ROOSEVELT COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 1 Displacement | 2007-06-01 | 2010-06-01
Customer | Study Number
MIDW | AG3-2006-058
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
MIDW | 1162131 | WR | WR | 40 | 2010-06-01 | 2020-06-01 |  |  | 0 | 0 | 109856 | 319683.58
MIDW | 1162136 | WR | WR | 10 | 2010-06-01 | 2020-06-01 |  |  | 0 | 0 | 27450 | 79879.83
MIDW | 1162175 | WR | WR | 68 | 2008-06-01 | 2038-06-01 | 2009-07-01 | 2039-07-01 | 0 | 0 | 188374 | 909305.7
MIDW | 1162176 | WR | WR | 16 | 2008-06-01 | 2038-06-01 | 2009-07-01 | 2039-07-01 | 0 | 0 | 44330 | 213987.13
MIDW | 1162183 | WR | WR | 40 | 2010-06-01 | 2030-06-01 |  |  | 0 | 0 | 109856 | 436064.03
MIDW | 1162190 | WR | WR | 10 | 2010-06-01 | 2030-06-01 |  |  | 0 | 0 | 27450 | 108959.69
MIDW | 1162191 | WR | WR | 40 | 2010-06-01 | 2030-06-01 |  |  | 0 | 0 | 109856 | 436064.03
MIDW | 1162192 | WR | WR | 10 | 2010-06-01 | 2030-06-01 |  |  | 0 | 0 | 27450 | 108959.69
MIDW | 1162193 | WR | WR | 20 | 2010-06-01 | 2030-06-01 |  |  | 0 | 0 | 54927 | 218028.34
MIDW | 1162194 | WR | WR | 5 | 2010-06-01 | 2030-06-01 |  |  | 0 | 0 | 13724 | 54476.22
[9 empty] | 0 | 0 | 713273 | 2885408.24
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1162131 | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 7548 | 300000 | 22696.48
| EXIDE JUNCTION - SUMMIT 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 45080 | 2000000 | 132258.26
| ROOSEVELT COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 1 Displacement | 2007-06-01 | 2010-06-01 |  |  | 50607 | 858753 | 148712.03
| ST JOHN CAPACITOR Displacement | 2008-06-01 | 2008-06-01 |  |  | 6621 | 114189 | 16016.81
[5 empty] | Total | 109856 | 3272942 | 319683.58
1162136 | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 1886 | 300000 | 5671.11
| EXIDE JUNCTION - SUMMIT 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 11267 | 2000000 | 33055.76
| ROOSEVELT COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 1 Displacement | 2007-06-01 | 2010-06-01 |  |  | 12642 | 858753 | 37149.36
| ST JOHN CAPACITOR Displacement | 2008-06-01 | 2008-06-01 |  |  | 1655 | 114189 | 4003.6
[5 empty] | Total | 27450 | 3272942 | 79879.83
1162175 | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 12831 | 300000 | 63030.02
| EXIDE JUNCTION - SUMMIT 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 76637 | 2000000 | 367314.21
| ROOSEVELT COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 1 Displacement | 2007-06-01 | 2010-06-01 |  |  | 86035 | 858753 | 427489.44
| ST JOHN CAPACITOR Displacement | 2008-06-01 | 2008-06-01 |  |  | 12871 | 114189 | 51472.02
[5 empty] | Total | 188374 | 3272942 | 909305.69
1162176 | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 3019 | 300000 | 14830.3
| EXIDE JUNCTION - SUMMIT 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 18032 | 2000000 | 86425.75
| ROOSEVELT COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 1 Displacement | 2007-06-01 | 2010-06-01 |  |  | 20250 | 858753 | 100617.9
| ST JOHN CAPACITOR Displacement | 2008-06-01 | 2008-06-01 |  |  | 3029 | 114189 | 12113.18
[5 empty] | Total | 44330 | 3272942 | 213987.13
1162183 | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 7548 | 300000 | 30590.17
| EXIDE JUNCTION - SUMMIT 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 45080 | 2000000 | 178256.82
| ROOSEVELT COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 1 Displacement | 2007-06-01 | 2010-06-01 |  |  | 50607 | 858753 | 205447.5
| ST JOHN CAPACITOR Displacement | 2008-06-01 | 2008-06-01 |  |  | 6621 | 114189 | 21769.54
[5 empty] | Total | 109856 | 3272942 | 436064.03
1162190 | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 1886 | 300000 | 7643.49
| EXIDE JUNCTION - SUMMIT 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 11267 | 2000000 | 44552.34
| ROOSEVELT COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 1 Displacement | 2007-06-01 | 2010-06-01 |  |  | 12642 | 858753 | 51322.29
| ST JOHN CAPACITOR Displacement | 2008-06-01 | 2008-06-01 |  |  | 1655 | 114189 | 5441.56
[5 empty] | Total | 27450 | 3272942 | 108959.68
1162191 | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 7548 | 300000 | 30590.17
| EXIDE JUNCTION - SUMMIT 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 45080 | 2000000 | 178256.82
| ROOSEVELT COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 1 Displacement | 2007-06-01 | 2010-06-01 |  |  | 50607 | 858753 | 205447.5
| ST JOHN CAPACITOR Displacement | 2008-06-01 | 2008-06-01 |  |  | 6621 | 114189 | 21769.54
[5 empty] | Total | 109856 | 3272942 | 436064.03
1162192 | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 1886 | 300000 | 7643.49
| EXIDE JUNCTION - SUMMIT 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 11267 | 2000000 | 44552.34
| ROOSEVELT COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 1 Displacement | 2007-06-01 | 2010-06-01 |  |  | 12642 | 858753 | 51322.29
| ST JOHN CAPACITOR Displacement | 2008-06-01 | 2008-06-01 |  |  | 1655 | 114189 | 5441.56
[5 empty] | Total | 27450 | 3272942 | 108959.68
1162193 | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 3774 | 300000 | 15295.08
| EXIDE JUNCTION - SUMMIT 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 22540 | 2000000 | 89128.41
| ROOSEVELT COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 1 Displacement | 2007-06-01 | 2010-06-01 |  |  | 25303 | 858753 | 102721.72
| ST JOHN CAPACITOR Displacement | 2008-06-01 | 2008-06-01 |  |  | 3310 | 114189 | 10883.12
[5 empty] | Total | 54927 | 3272942 | 218028.33
1162194 | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 943 | 300000 | 3821.74
| EXIDE JUNCTION - SUMMIT 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 5633 | 2000000 | 22274.19
| ROOSEVELT COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 1 Displacement | 2007-06-01 | 2010-06-01 |  |  | 6321 | 858753 | 25661.15
| ST JOHN CAPACITOR Displacement | 2008-06-01 | 2008-06-01 |  |  | 827 | 114189 | 2719.14
[5 empty] | Total | 13724 | 3272942 | 54476.22
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162131 | HAYS PLANT - SOUTH HAYS 115KV CKT 1 | 2008-06-01 | 2009-06-01 |  | No
| HAYS PLANT - VINE STREET 115KV CKT 1 | 2008-06-01 | 2009-06-01 |  | No
| HEIZER 115/69KV TRANSFORMER CKT 1 | 2016-06-01 | 2016-06-01
| HEIZER 115/69KV TRANSFORMER CKT 2 | 2016-06-01 | 2016-06-01
| KINSLEY CAPACITOR | 2007-06-01 | 2009-01-01 |  | No
| Mooreland - Potter 345 kV SPS | 2016-06-01 | 2016-06-01
| Mooreland - Potter 345 kV WFEC | 2016-06-01 | 2016-06-01
| Mooreland 345/138 kV Transformer | 2016-06-01 | 2016-06-01
| POTTER COUNTY INTERCHANGE (POTTR CO) 345/230/13.2KV TRANSFORMER CKT 2 | 2016-06-01 | 2016-06-01
| Spearville - Mooreland 345 kV SUNC | 2016-06-01 | 2016-06-01
| Spearville - Mooreland 345 kV WFEC | 2016-06-01 | 2016-06-01
| TUCO INTERCHANGE 345/115KV TRANSFORMER CKT 1 | 2016-06-01 | 2016-06-01
1162136 | HAYS PLANT - SOUTH HAYS 115KV CKT 1 | 2008-06-01 | 2009-06-01 |  | No
| HAYS PLANT - VINE STREET 115KV CKT 1 | 2008-06-01 | 2009-06-01 |  | No
| HEIZER 115/69KV TRANSFORMER CKT 1 | 2016-06-01 | 2016-06-01
| HEIZER 115/69KV TRANSFORMER CKT 2 | 2016-06-01 | 2016-06-01
| KINSLEY CAPACITOR | 2007-06-01 | 2009-01-01 |  | No
| Mooreland - Potter 345 kV SPS | 2016-06-01 | 2016-06-01
| Mooreland - Potter 345 kV WFEC | 2016-06-01 | 2016-06-01
| Mooreland 345/138 kV Transformer | 2016-06-01 | 2016-06-01
| POTTER COUNTY INTERCHANGE (POTTR CO) 345/230/13.2KV TRANSFORMER CKT 2 | 2016-06-01 | 2016-06-01
| Spearville - Mooreland 345 kV SUNC | 2016-06-01 | 2016-06-01
| Spearville - Mooreland 345 kV WFEC | 2016-06-01 | 2016-06-01
| TUCO INTERCHANGE 345/115KV TRANSFORMER CKT 1 | 2016-06-01 | 2016-06-01
1162175 | HAYS PLANT - SOUTH HAYS 115KV CKT 1 | 2008-06-01 | 2009-06-01 |  | No
| HAYS PLANT - VINE STREET 115KV CKT 1 | 2008-06-01 | 2009-06-01 |  | No
| HEIZER 115/69KV TRANSFORMER CKT 1 | 2016-06-01 | 2016-06-01
| HEIZER 115/69KV TRANSFORMER CKT 2 | 2016-06-01 | 2016-06-01
| KINSLEY CAPACITOR | 2007-06-01 | 2009-01-01 |  | No
| Mooreland - Potter 345 kV SPS | 2016-06-01 | 2016-06-01
| Mooreland - Potter 345 kV WFEC | 2016-06-01 | 2016-06-01
| Mooreland 345/138 kV Transformer | 2016-06-01 | 2016-06-01
| POTTER COUNTY INTERCHANGE (POTTR CO) 345/230/13.2KV TRANSFORMER CKT 2 | 2016-06-01 | 2016-06-01
| Spearville - Mooreland 345 kV SUNC | 2016-06-01 | 2016-06-01
| Spearville - Mooreland 345 kV WFEC | 2016-06-01 | 2016-06-01
| TUCO INTERCHANGE 345/115KV TRANSFORMER CKT 1 | 2016-06-01 | 2016-06-01
1162176 | HAYS PLANT - SOUTH HAYS 115KV CKT 1 | 2008-06-01 | 2009-06-01 |  | No
| HAYS PLANT - VINE STREET 115KV CKT 1 | 2008-06-01 | 2009-06-01 |  | No
| HEIZER 115/69KV TRANSFORMER CKT 1 | 2016-06-01 | 2016-06-01
| HEIZER 115/69KV TRANSFORMER CKT 2 | 2016-06-01 | 2016-06-01
| KINSLEY CAPACITOR | 2007-06-01 | 2009-01-01 |  | No
| Mooreland - Potter 345 kV SPS | 2016-06-01 | 2016-06-01
| Mooreland - Potter 345 kV WFEC | 2016-06-01 | 2016-06-01
| Mooreland 345/138 kV Transformer | 2016-06-01 | 2016-06-01
| POTTER COUNTY INTERCHANGE (POTTR CO) 345/230/13.2KV TRANSFORMER CKT 2 | 2016-06-01 | 2016-06-01
| Spearville - Mooreland 345 kV SUNC | 2016-06-01 | 2016-06-01
| Spearville - Mooreland 345 kV WFEC | 2016-06-01 | 2016-06-01
| TUCO INTERCHANGE 345/115KV TRANSFORMER CKT 1 | 2016-06-01 | 2016-06-01
1162183 | HAYS PLANT - SOUTH HAYS 115KV CKT 1 | 2008-06-01 | 2009-06-01 |  | No
| HAYS PLANT - VINE STREET 115KV CKT 1 | 2008-06-01 | 2009-06-01 |  | No
| HEIZER 115/69KV TRANSFORMER CKT 1 | 2016-06-01 | 2016-06-01
| HEIZER 115/69KV TRANSFORMER CKT 2 | 2016-06-01 | 2016-06-01
| KINSLEY CAPACITOR | 2007-06-01 | 2009-01-01 |  | No
| Mooreland - Potter 345 kV SPS | 2016-06-01 | 2016-06-01
| Mooreland - Potter 345 kV WFEC | 2016-06-01 | 2016-06-01
| Mooreland 345/138 kV Transformer | 2016-06-01 | 2016-06-01
| POTTER COUNTY INTERCHANGE (POTTR CO) 345/230/13.2KV TRANSFORMER CKT 2 | 2016-06-01 | 2016-06-01
| Spearville - Mooreland 345 kV SUNC | 2016-06-01 | 2016-06-01
| Spearville - Mooreland 345 kV WFEC | 2016-06-01 | 2016-06-01
| TUCO INTERCHANGE 345/115KV TRANSFORMER CKT 1 | 2016-06-01 | 2016-06-01
1162190 | HAYS PLANT - SOUTH HAYS 115KV CKT 1 | 2008-06-01 | 2009-06-01 |  | No
| HAYS PLANT - VINE STREET 115KV CKT 1 | 2008-06-01 | 2009-06-01 |  | No
| HEIZER 115/69KV TRANSFORMER CKT 1 | 2016-06-01 | 2016-06-01
| HEIZER 115/69KV TRANSFORMER CKT 2 | 2016-06-01 | 2016-06-01
| KINSLEY CAPACITOR | 2007-06-01 | 2009-01-01 |  | No
| Mooreland - Potter 345 kV SPS | 2016-06-01 | 2016-06-01
| Mooreland - Potter 345 kV WFEC | 2016-06-01 | 2016-06-01
| Mooreland 345/138 kV Transformer | 2016-06-01 | 2016-06-01
| POTTER COUNTY INTERCHANGE (POTTR CO) 345/230/13.2KV TRANSFORMER CKT 2 | 2016-06-01 | 2016-06-01
| Spearville - Mooreland 345 kV SUNC | 2016-06-01 | 2016-06-01
| Spearville - Mooreland 345 kV WFEC | 2016-06-01 | 2016-06-01
| TUCO INTERCHANGE 345/115KV TRANSFORMER CKT 1 | 2016-06-01 | 2016-06-01
1162191 | HAYS PLANT - SOUTH HAYS 115KV CKT 1 | 2008-06-01 | 2009-06-01 |  | No
| HAYS PLANT - VINE STREET 115KV CKT 1 | 2008-06-01 | 2009-06-01 |  | No
| HEIZER 115/69KV TRANSFORMER CKT 1 | 2016-06-01 | 2016-06-01
| HEIZER 115/69KV TRANSFORMER CKT 2 | 2016-06-01 | 2016-06-01
| KINSLEY CAPACITOR | 2007-06-01 | 2009-01-01 |  | No
| Mooreland - Potter 345 kV SPS | 2016-06-01 | 2016-06-01
| Mooreland - Potter 345 kV WFEC | 2016-06-01 | 2016-06-01
| Mooreland 345/138 kV Transformer | 2016-06-01 | 2016-06-01
| POTTER COUNTY INTERCHANGE (POTTR CO) 345/230/13.2KV TRANSFORMER CKT 2 | 2016-06-01 | 2016-06-01
| Spearville - Mooreland 345 kV SUNC | 2016-06-01 | 2016-06-01
| Spearville - Mooreland 345 kV WFEC | 2016-06-01 | 2016-06-01
| TUCO INTERCHANGE 345/115KV TRANSFORMER CKT 1 | 2016-06-01 | 2016-06-01
1162192 | HAYS PLANT - SOUTH HAYS 115KV CKT 1 | 2008-06-01 | 2009-06-01 |  | No
| HAYS PLANT - VINE STREET 115KV CKT 1 | 2008-06-01 | 2009-06-01 |  | No
| HEIZER 115/69KV TRANSFORMER CKT 1 | 2016-06-01 | 2016-06-01
| HEIZER 115/69KV TRANSFORMER CKT 2 | 2016-06-01 | 2016-06-01
| KINSLEY CAPACITOR | 2007-06-01 | 2009-01-01 |  | No
| Mooreland - Potter 345 kV SPS | 2016-06-01 | 2016-06-01
| Mooreland - Potter 345 kV WFEC | 2016-06-01 | 2016-06-01
| Mooreland 345/138 kV Transformer | 2016-06-01 | 2016-06-01
| POTTER COUNTY INTERCHANGE (POTTR CO) 345/230/13.2KV TRANSFORMER CKT 2 | 2016-06-01 | 2016-06-01
| Spearville - Mooreland 345 kV SUNC | 2016-06-01 | 2016-06-01
| Spearville - Mooreland 345 kV WFEC | 2016-06-01 | 2016-06-01
| TUCO INTERCHANGE 345/115KV TRANSFORMER CKT 1 | 2016-06-01 | 2016-06-01
1162193 | HAYS PLANT - SOUTH HAYS 115KV CKT 1 | 2008-06-01 | 2009-06-01 |  | No
| HAYS PLANT - VINE STREET 115KV CKT 1 | 2008-06-01 | 2009-06-01 |  | No
| HEIZER 115/69KV TRANSFORMER CKT 1 | 2016-06-01 | 2016-06-01
| HEIZER 115/69KV TRANSFORMER CKT 2 | 2016-06-01 | 2016-06-01
| KINSLEY CAPACITOR | 2007-06-01 | 2009-01-01 |  | No
| Mooreland - Potter 345 kV SPS | 2016-06-01 | 2016-06-01
| Mooreland - Potter 345 kV WFEC | 2016-06-01 | 2016-06-01
| Mooreland 345/138 kV Transformer | 2016-06-01 | 2016-06-01
| POTTER COUNTY INTERCHANGE (POTTR CO) 345/230/13.2KV TRANSFORMER CKT 2 | 2016-06-01 | 2016-06-01
| Spearville - Mooreland 345 kV SUNC | 2016-06-01 | 2016-06-01
| Spearville - Mooreland 345 kV WFEC | 2016-06-01 | 2016-06-01
| TUCO INTERCHANGE 345/115KV TRANSFORMER CKT 1 | 2016-06-01 | 2016-06-01
1162194 | HAYS PLANT - SOUTH HAYS 115KV CKT 1 | 2008-06-01 | 2009-06-01 |  | No
| HAYS PLANT - VINE STREET 115KV CKT 1 | 2008-06-01 | 2009-06-01 |  | No
| HEIZER 115/69KV TRANSFORMER CKT 1 | 2016-06-01 | 2016-06-01
| HEIZER 115/69KV TRANSFORMER CKT 2 | 2016-06-01 | 2016-06-01
| KINSLEY CAPACITOR | 2007-06-01 | 2009-01-01 |  | No
| Mooreland - Potter 345 kV SPS | 2016-06-01 | 2016-06-01
| Mooreland - Potter 345 kV WFEC | 2016-06-01 | 2016-06-01
| Mooreland 345/138 kV Transformer | 2016-06-01 | 2016-06-01
| POTTER COUNTY INTERCHANGE (POTTR CO) 345/230/13.2KV TRANSFORMER CKT 2 | 2016-06-01 | 2016-06-01
| Spearville - Mooreland 345 kV SUNC | 2016-06-01 | 2016-06-01
| Spearville - Mooreland 345 kV WFEC | 2016-06-01 | 2016-06-01
| TUCO INTERCHANGE 345/115KV TRANSFORMER CKT 1 | 2016-06-01 | 2016-06-01
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162131 | IATAN - NASHUA 345KV CKT 1 | 2010-06-01 | 2010-06-01
1162136 | IATAN - NASHUA 345KV CKT 1 | 2010-06-01 | 2010-06-01
1162175 | IATAN - NASHUA 345KV CKT 1 | 2010-06-01 | 2010-06-01
1162176 | IATAN - NASHUA 345KV CKT 1 | 2010-06-01 | 2010-06-01
1162183 | IATAN - NASHUA 345KV CKT 1 | 2010-06-01 | 2010-06-01
1162190 | IATAN - NASHUA 345KV CKT 1 | 2010-06-01 | 2010-06-01
1162191 | IATAN - NASHUA 345KV CKT 1 | 2010-06-01 | 2010-06-01
1162192 | IATAN - NASHUA 345KV CKT 1 | 2010-06-01 | 2010-06-01
1162193 | IATAN - NASHUA 345KV CKT 1 | 2010-06-01 | 2010-06-01
1162194 | IATAN - NASHUA 345KV CKT 1 | 2010-06-01 | 2010-06-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162131 | RENO - SUMMIT 345KV | 2011-01-01 | 2011-01-01
| WICHITA - RENO 345KV | 2007-02-01 | 2009-07-01 |  | No
1162136 | RENO - SUMMIT 345KV | 2011-01-01 | 2011-01-01
| WICHITA - RENO 345KV | 2007-02-01 | 2009-07-01 |  | No
1162175 | RENO - SUMMIT 345KV | 2011-01-01 | 2011-01-01
| WICHITA - RENO 345KV | 2007-02-01 | 2009-07-01 |  | No
1162176 | RENO - SUMMIT 345KV | 2011-01-01 | 2011-01-01
| WICHITA - RENO 345KV | 2007-02-01 | 2009-07-01 |  | No
1162183 | RENO - SUMMIT 345KV | 2011-01-01 | 2011-01-01
| WICHITA - RENO 345KV | 2007-02-01 | 2009-07-01 |  | No
1162190 | RENO - SUMMIT 345KV | 2011-01-01 | 2011-01-01
| WICHITA - RENO 345KV | 2007-02-01 | 2009-07-01 |  | No
1162191 | RENO - SUMMIT 345KV | 2011-01-01 | 2011-01-01
| WICHITA - RENO 345KV | 2007-02-01 | 2009-07-01 |  | No
1162192 | RENO - SUMMIT 345KV | 2011-01-01 | 2011-01-01
| WICHITA - RENO 345KV | 2007-02-01 | 2009-07-01 |  | No
1162193 | RENO - SUMMIT 345KV | 2011-01-01 | 2011-01-01
| WICHITA - RENO 345KV | 2007-02-01 | 2009-07-01 |  | No
1162194 | RENO - SUMMIT 345KV | 2011-01-01 | 2011-01-01
| WICHITA - RENO 345KV | 2007-02-01 | 2009-07-01 |  | No
Potential reservation deferral and redispatch requirement on the following upgrades due to positive MW Impact on limitations that require upgrade. No cost assignment due to negative MW impact on defined upgrade.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162131 | CURRY COUNTY INTERCHANGE - ROOSEVELT COUNTY INTERCHANGE 115KV CKT 2 Displacement | 2007-06-01 | 2010-06-01
| Potter - Roosevelt 345KV Displacement | 2007-06-01 | 2010-06-01
1162136 | CURRY COUNTY INTERCHANGE - ROOSEVELT COUNTY INTERCHANGE 115KV CKT 2 Displacement | 2007-06-01 | 2010-06-01
| Potter - Roosevelt 345KV Displacement | 2007-06-01 | 2010-06-01
1162175 | CURRY COUNTY INTERCHANGE - ROOSEVELT COUNTY INTERCHANGE 115KV CKT 2 Displacement | 2007-06-01 | 2010-06-01
| Potter - Roosevelt 345KV Displacement | 2007-06-01 | 2010-06-01
1162176 | CURRY COUNTY INTERCHANGE - ROOSEVELT COUNTY INTERCHANGE 115KV CKT 2 Displacement | 2007-06-01 | 2010-06-01
| Potter - Roosevelt 345KV Displacement | 2007-06-01 | 2010-06-01
1162183 | CURRY COUNTY INTERCHANGE - ROOSEVELT COUNTY INTERCHANGE 115KV CKT 2 Displacement | 2007-06-01 | 2010-06-01
| Potter - Roosevelt 345KV Displacement | 2007-06-01 | 2010-06-01
1162190 | CURRY COUNTY INTERCHANGE - ROOSEVELT COUNTY INTERCHANGE 115KV CKT 2 Displacement | 2007-06-01 | 2010-06-01
| Potter - Roosevelt 345KV Displacement | 2007-06-01 | 2010-06-01
1162191 | CURRY COUNTY INTERCHANGE - ROOSEVELT COUNTY INTERCHANGE 115KV CKT 2 Displacement | 2007-06-01 | 2010-06-01
| Potter - Roosevelt 345KV Displacement | 2007-06-01 | 2010-06-01
1162192 | CURRY COUNTY INTERCHANGE - ROOSEVELT COUNTY INTERCHANGE 115KV CKT 2 Displacement | 2007-06-01 | 2010-06-01
| Potter - Roosevelt 345KV Displacement | 2007-06-01 | 2010-06-01
1162193 | CURRY COUNTY INTERCHANGE - ROOSEVELT COUNTY INTERCHANGE 115KV CKT 2 Displacement | 2007-06-01 | 2010-06-01
| Potter - Roosevelt 345KV Displacement | 2007-06-01 | 2010-06-01
1162194 | CURRY COUNTY INTERCHANGE - ROOSEVELT COUNTY INTERCHANGE 115KV CKT 2 Displacement | 2007-06-01 | 2010-06-01
| Potter - Roosevelt 345KV Displacement | 2007-06-01 | 2010-06-01
Customer | Study Number
MIDW | AG3-2006-062
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
MIDW | 1162137 | WR | WR | 20 | 2008-06-01 | 2038-06-01 | 2009-07-01 | 2039-07-01 | 0 | 0 | 41184 | 193951.52
MIDW | 1162141 | WR | WR | 5 | 2008-06-01 | 2038-06-01 | 2009-07-01 | 2039-07-01 | 0 | 0 | 10295 | 48483.01
MIDW | 1162142 | WR | WR | 40 | 2008-06-01 | 2038-06-01 | 2009-07-01 | 2039-07-01 | 0 | 0 | 82370 | 387912.75
MIDW | 1162143 | WR | WR | 10 | 2008-06-01 | 2038-06-01 | 2009-07-01 | 2039-07-01 | 0 | 0 | 20598 | 97004.61
[9 empty] | 0 | 0 | 154447 | 727351.89
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1162137 | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 4090 | 300000 | 20091.4
| EXIDE JUNCTION - SUMMIT 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 24430 | 2000000 | 117090.78
| NORTHVIEW - SUMMIT 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 5905 | 610000 | 29739.63
| ST JOHN CAPACITOR Displacement | 2008-06-01 | 2008-06-01 |  |  | 6759 | 114189 | 27029.71
[5 empty] | Total | 41184 | 3024189 | 193951.52
1162141 | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 1022 | 300000 | 5020.39
| EXIDE JUNCTION - SUMMIT 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 6106 | 2000000 | 29265.51
| NORTHVIEW - SUMMIT 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 1477 | 610000 | 7438.68
| ST JOHN CAPACITOR Displacement | 2008-06-01 | 2008-06-01 |  |  | 1690 | 114189 | 6758.43
[5 empty] | Total | 10295 | 3024189 | 48483.01
1162142 | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 8181 | 300000 | 40187.72
| EXIDE JUNCTION - SUMMIT 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 48861 | 2000000 | 234186.36
| NORTHVIEW - SUMMIT 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 11810 | 610000 | 59479.26
| ST JOHN CAPACITOR Displacement | 2008-06-01 | 2008-06-01 |  |  | 13518 | 114189 | 54059.42
[5 empty] | Total | 82370 | 3024189 | 387912.76
1162143 | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 2046 | 300000 | 10050.61
| EXIDE JUNCTION - SUMMIT 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 12218 | 2000000 | 58559.77
| NORTHVIEW - SUMMIT 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 2954 | 610000 | 14877.37
| ST JOHN CAPACITOR Displacement | 2008-06-01 | 2008-06-01 |  |  | 3380 | 114189 | 13516.86
[5 empty] | Total | 20598 | 3024189 | 97004.61
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162137 | HEIZER 115/69KV TRANSFORMER CKT 1 | 2016-06-01 | 2016-06-01
| HEIZER 115/69KV TRANSFORMER CKT 2 | 2016-06-01 | 2016-06-01
| KINSLEY CAPACITOR | 2007-06-01 | 2009-01-01 |  | No
1162141 | HEIZER 115/69KV TRANSFORMER CKT 1 | 2016-06-01 | 2016-06-01
| HEIZER 115/69KV TRANSFORMER CKT 2 | 2016-06-01 | 2016-06-01
| KINSLEY CAPACITOR | 2007-06-01 | 2009-01-01 |  | No
1162142 | HEIZER 115/69KV TRANSFORMER CKT 1 | 2016-06-01 | 2016-06-01
| HEIZER 115/69KV TRANSFORMER CKT 2 | 2016-06-01 | 2016-06-01
| KINSLEY CAPACITOR | 2007-06-01 | 2009-01-01 |  | No
1162143 | HEIZER 115/69KV TRANSFORMER CKT 1 | 2016-06-01 | 2016-06-01
| HEIZER 115/69KV TRANSFORMER CKT 2 | 2016-06-01 | 2016-06-01
| KINSLEY CAPACITOR | 2007-06-01 | 2009-01-01 |  | No
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162137 | RENO - SUMMIT 345KV | 2011-01-01 | 2011-01-01
| WICHITA - RENO 345KV | 2007-02-01 | 2009-07-01 |  | No
1162141 | RENO - SUMMIT 345KV | 2011-01-01 | 2011-01-01
| WICHITA - RENO 345KV | 2007-02-01 | 2009-07-01 |  | No
1162142 | RENO - SUMMIT 345KV | 2011-01-01 | 2011-01-01
| WICHITA - RENO 345KV | 2007-02-01 | 2009-07-01 |  | No
1162143 | RENO - SUMMIT 345KV | 2011-01-01 | 2011-01-01
| WICHITA - RENO 345KV | 2007-02-01 | 2009-07-01 |  | No
Customer | Study Number
MIDW | AG3-2006-086
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
MIDW | 1162102 | WR | WR | 25 | 2007-06-01 | 2017-06-01 | 2009-07-01 | 2019-07-01 | 0 | 0 | 254918 | 647141.98
[9 empty] | 0 | 0 | 254918 | 647141.98
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1162102 | ARCADIA - SOONER 345kV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 212521 | 65000000 | 534027.89
| ROOSEVELT COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 1 Displacement | 2007-06-01 | 2010-06-01 |  |  | 36872 | 858753 | 100640.51
| ST JOHN CAPACITOR Displacement | 2008-06-01 | 2008-06-01 |  |  | 5525 | 114189 | 12473.58
[5 empty] | Total | 254918 | 65972942 | 647141.98
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162102 | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | 2007-06-01 | 2009-06-01 |  | No
| CLAY CENTER - GREENLEAF 115KV CKT 1 | 2007-06-01 | 2009-06-01 |  | No
| Evans - Grant - Chisolm Rebuild and Conversion Project | 2007-06-01 | 2009-06-01 |  | No
| GILL ENERGY CENTER EAST - GILLJCT269.0 69KV CKT 1 | 2007-06-01 | 2008-06-01 | 2007-10-01 | No
| GILL ENERGY CENTER EAST - MACARTHUR 69KV CKT 1 | 2007-06-01 | 2007-07-01 |  | No
| HAYS PLANT - SOUTH HAYS 115KV CKT 1 | 2008-06-01 | 2009-06-01 |  | No
| HAYS PLANT - VINE STREET 115KV CKT 1 | 2008-06-01 | 2009-06-01 |  | No
| HEIZER 115/69KV TRANSFORMER CKT 1 | 2016-06-01 | 2016-06-01
| HEIZER 115/69KV TRANSFORMER CKT 2 | 2016-06-01 | 2016-06-01
| KINSLEY CAPACITOR | 2007-06-01 | 2009-01-01 |  | No
| Mooreland - Potter 345 kV SPS | 2016-06-01 | 2016-06-01
| Mooreland - Potter 345 kV WFEC | 2016-06-01 | 2016-06-01
| Mooreland 345/138 kV Transformer | 2016-06-01 | 2016-06-01
| POTTER COUNTY INTERCHANGE (POTTR CO) 345/230/13.2KV TRANSFORMER CKT 2 | 2016-06-01 | 2016-06-01
| Spearville - Mooreland 345 kV SUNC | 2016-06-01 | 2016-06-01
| Spearville - Mooreland 345 kV WFEC | 2016-06-01 | 2016-06-01
| STRANGER CREEK TRANSFORMER CKT 2 | 2009-06-01 | 2009-06-01
| TUCO INTERCHANGE 345/115KV TRANSFORMER CKT 1 | 2016-06-01 | 2016-06-01
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162102 | LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162102 | HEIZER TO KNOLL 230KV | 2007-06-01 | 2008-06-01 |  | No
| LACYGNE-PAOLA-WEST GARDER 345KV | 2007-06-01 | 2008-06-01 |  | No
| PHILLIPSBURG - RHOADES | 2007-06-01 | 2008-10-01 |  | No
| RENO - SUMMIT 345KV | 2011-01-01 | 2011-01-01
| WICHITA - RENO 345KV | 2007-02-01 | 2009-07-01 |  | No
Potential reservation deferral and redispatch requirement on the following upgrades due to positive MW Impact on limitations that require upgrade. No cost assignment due to negative MW impact on defined upgrade.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162102 | CURRY COUNTY INTERCHANGE - ROOSEVELT COUNTY INTERCHANGE 115KV CKT 2 Displacement | 2007-06-01 | 2010-06-01
| Potter - Roosevelt 345KV Displacement | 2007-06-01 | 2010-06-01
Customer | Study Number
MIDW | AG3-2006-087
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
MIDW | 1162109 | WR | WR | 10 | 2008-06-01 | 2018-06-01 | 2009-07-01 | 2019-07-01 | 0 | 0 | 101982 | 258894.03
MIDW | 1162122 | WR | WR | 10 | 2008-06-01 | 2018-06-01 | 2009-07-01 | 2019-07-01 | 0 | 0 | 101982 | 258894.03
MIDW | 1162123 | WR | WR | 19 | 2008-06-01 | 2018-06-01 | 2009-07-01 | 2019-07-01 | 0 | 0 | 193707 | 491749.14
MIDW | 1162130 | WR | WR | 6 | 2008-06-01 | 2018-06-01 | 2009-07-01 | 2019-07-01 | 0 | 0 | 61175 | 155302.38
[9 empty] | 0 | 0 | 458846 | 1164839.58
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1162109 | ARCADIA - SOONER 345kV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 85023 | 65000000 | 213647.84
| ROOSEVELT COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 1 Displacement | 2007-06-01 | 2010-06-01 |  |  | 14749 | 858753 | 40256.75
| ST JOHN CAPACITOR Displacement | 2008-06-01 | 2008-06-01 |  |  | 2210 | 114189 | 4989.43
[5 empty] | Total | 101982 | 65972942 | 258894.02
1162122 | ARCADIA - SOONER 345kV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 85023 | 65000000 | 213647.84
| ROOSEVELT COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 1 Displacement | 2007-06-01 | 2010-06-01 |  |  | 14749 | 858753 | 40256.75
| ST JOHN CAPACITOR Displacement | 2008-06-01 | 2008-06-01 |  |  | 2210 | 114189 | 4989.43
[5 empty] | Total | 101982 | 65972942 | 258894.02
1162123 | ARCADIA - SOONER 345kV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 161493 | 65000000 | 405803.5
| ROOSEVELT COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 1 Displacement | 2007-06-01 | 2010-06-01 |  |  | 28015 | 858753 | 76465.72
| ST JOHN CAPACITOR Displacement | 2008-06-01 | 2008-06-01 |  |  | 4199 | 114189 | 9479.92
[5 empty] | Total | 193707 | 65972942 | 491749.14
1162130 | ARCADIA - SOONER 345kV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 50992 | 65000000 | 128133.93
| ROOSEVELT COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 1 Displacement | 2007-06-01 | 2010-06-01 |  |  | 8857 | 858753 | 24174.79
| ST JOHN CAPACITOR Displacement | 2008-06-01 | 2008-06-01 |  |  | 1326 | 114189 | 2993.66
[5 empty] | Total | 61175 | 65972942 | 155302.38
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162109 | Evans - Grant - Chisolm Rebuild and Conversion Project | 2007-06-01 | 2009-06-01 |  | No
| GILL ENERGY CENTER EAST - MACARTHUR 69KV CKT 1 | 2007-06-01 | 2007-07-01 |  | No
| HAYS PLANT - SOUTH HAYS 115KV CKT 1 | 2008-06-01 | 2009-06-01 |  | No
| HAYS PLANT - VINE STREET 115KV CKT 1 | 2008-06-01 | 2009-06-01 |  | No
| HEIZER 115/69KV TRANSFORMER CKT 1 | 2016-06-01 | 2016-06-01
| HEIZER 115/69KV TRANSFORMER CKT 2 | 2016-06-01 | 2016-06-01
| KINSLEY CAPACITOR | 2007-06-01 | 2009-01-01 |  | No
| Mooreland - Potter 345 kV SPS | 2016-06-01 | 2016-06-01
| Mooreland - Potter 345 kV WFEC | 2016-06-01 | 2016-06-01
| Mooreland 345/138 kV Transformer | 2016-06-01 | 2016-06-01
| POTTER COUNTY INTERCHANGE (POTTR CO) 345/230/13.2KV TRANSFORMER CKT 2 | 2016-06-01 | 2016-06-01
| Spearville - Mooreland 345 kV SUNC | 2016-06-01 | 2016-06-01
| Spearville - Mooreland 345 kV WFEC | 2016-06-01 | 2016-06-01
| STRANGER CREEK TRANSFORMER CKT 2 | 2009-06-01 | 2009-06-01
| TUCO INTERCHANGE 345/115KV TRANSFORMER CKT 1 | 2016-06-01 | 2016-06-01
1162122 | Evans - Grant - Chisolm Rebuild and Conversion Project | 2007-06-01 | 2009-06-01 |  | No
| GILL ENERGY CENTER EAST - MACARTHUR 69KV CKT 1 | 2007-06-01 | 2007-07-01 |  | No
| HAYS PLANT - SOUTH HAYS 115KV CKT 1 | 2008-06-01 | 2009-06-01 |  | No
| HAYS PLANT - VINE STREET 115KV CKT 1 | 2008-06-01 | 2009-06-01 |  | No
| HEIZER 115/69KV TRANSFORMER CKT 1 | 2016-06-01 | 2016-06-01
| HEIZER 115/69KV TRANSFORMER CKT 2 | 2016-06-01 | 2016-06-01
| KINSLEY CAPACITOR | 2007-06-01 | 2009-01-01 |  | No
| Mooreland - Potter 345 kV SPS | 2016-06-01 | 2016-06-01
| Mooreland - Potter 345 kV WFEC | 2016-06-01 | 2016-06-01
| Mooreland 345/138 kV Transformer | 2016-06-01 | 2016-06-01
| POTTER COUNTY INTERCHANGE (POTTR CO) 345/230/13.2KV TRANSFORMER CKT 2 | 2016-06-01 | 2016-06-01
| Spearville - Mooreland 345 kV SUNC | 2016-06-01 | 2016-06-01
| Spearville - Mooreland 345 kV WFEC | 2016-06-01 | 2016-06-01
| STRANGER CREEK TRANSFORMER CKT 2 | 2009-06-01 | 2009-06-01
| TUCO INTERCHANGE 345/115KV TRANSFORMER CKT 1 | 2016-06-01 | 2016-06-01
1162123 | Evans - Grant - Chisolm Rebuild and Conversion Project | 2007-06-01 | 2009-06-01 |  | No
| GILL ENERGY CENTER EAST - MACARTHUR 69KV CKT 1 | 2007-06-01 | 2007-07-01 |  | No
| HAYS PLANT - SOUTH HAYS 115KV CKT 1 | 2008-06-01 | 2009-06-01 |  | No
| HAYS PLANT - VINE STREET 115KV CKT 1 | 2008-06-01 | 2009-06-01 |  | No
| HEIZER 115/69KV TRANSFORMER CKT 1 | 2016-06-01 | 2016-06-01
| HEIZER 115/69KV TRANSFORMER CKT 2 | 2016-06-01 | 2016-06-01
| KINSLEY CAPACITOR | 2007-06-01 | 2009-01-01 |  | No
| Mooreland - Potter 345 kV SPS | 2016-06-01 | 2016-06-01
| Mooreland - Potter 345 kV WFEC | 2016-06-01 | 2016-06-01
| Mooreland 345/138 kV Transformer | 2016-06-01 | 2016-06-01
| POTTER COUNTY INTERCHANGE (POTTR CO) 345/230/13.2KV TRANSFORMER CKT 2 | 2016-06-01 | 2016-06-01
| Spearville - Mooreland 345 kV SUNC | 2016-06-01 | 2016-06-01
| Spearville - Mooreland 345 kV WFEC | 2016-06-01 | 2016-06-01
| STRANGER CREEK TRANSFORMER CKT 2 | 2009-06-01 | 2009-06-01
| TUCO INTERCHANGE 345/115KV TRANSFORMER CKT 1 | 2016-06-01 | 2016-06-01
1162130 | Evans - Grant - Chisolm Rebuild and Conversion Project | 2007-06-01 | 2009-06-01 |  | No
| GILL ENERGY CENTER EAST - MACARTHUR 69KV CKT 1 | 2007-06-01 | 2007-07-01 |  | No
| HAYS PLANT - SOUTH HAYS 115KV CKT 1 | 2008-06-01 | 2009-06-01 |  | No
| HAYS PLANT - VINE STREET 115KV CKT 1 | 2008-06-01 | 2009-06-01 |  | No
| HEIZER 115/69KV TRANSFORMER CKT 1 | 2016-06-01 | 2016-06-01
| HEIZER 115/69KV TRANSFORMER CKT 2 | 2016-06-01 | 2016-06-01
| KINSLEY CAPACITOR | 2007-06-01 | 2009-01-01 |  | No
| Mooreland - Potter 345 kV SPS | 2016-06-01 | 2016-06-01
| Mooreland - Potter 345 kV WFEC | 2016-06-01 | 2016-06-01
| Mooreland 345/138 kV Transformer | 2016-06-01 | 2016-06-01
| POTTER COUNTY INTERCHANGE (POTTR CO) 345/230/13.2KV TRANSFORMER CKT 2 | 2016-06-01 | 2016-06-01
| Spearville - Mooreland 345 kV SUNC | 2016-06-01 | 2016-06-01
| Spearville - Mooreland 345 kV WFEC | 2016-06-01 | 2016-06-01
| STRANGER CREEK TRANSFORMER CKT 2 | 2009-06-01 | 2009-06-01
| TUCO INTERCHANGE 345/115KV TRANSFORMER CKT 1 | 2016-06-01 | 2016-06-01
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162109 | LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01
1162122 | LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01
1162123 | LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01
1162130 | LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162109 | RENO - SUMMIT 345KV | 2011-01-01 | 2011-01-01
| WICHITA - RENO 345KV | 2007-02-01 | 2009-07-01 |  | No
1162122 | RENO - SUMMIT 345KV | 2011-01-01 | 2011-01-01
| WICHITA - RENO 345KV | 2007-02-01 | 2009-07-01 |  | No
1162123 | RENO - SUMMIT 345KV | 2011-01-01 | 2011-01-01
| WICHITA - RENO 345KV | 2007-02-01 | 2009-07-01 |  | No
1162130 | RENO - SUMMIT 345KV | 2011-01-01 | 2011-01-01
| WICHITA - RENO 345KV | 2007-02-01 | 2009-07-01 |  | No
Potential reservation deferral and redispatch requirement on the following upgrades due to positive MW Impact on limitations that require upgrade. No cost assignment due to negative MW impact on defined upgrade.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162109 | CURRY COUNTY INTERCHANGE - ROOSEVELT COUNTY INTERCHANGE 115KV CKT 2 Displacement | 2007-06-01 | 2010-06-01
| Potter - Roosevelt 345KV Displacement | 2007-06-01 | 2010-06-01
1162122 | CURRY COUNTY INTERCHANGE - ROOSEVELT COUNTY INTERCHANGE 115KV CKT 2 Displacement | 2007-06-01 | 2010-06-01
| Potter - Roosevelt 345KV Displacement | 2007-06-01 | 2010-06-01
1162123 | CURRY COUNTY INTERCHANGE - ROOSEVELT COUNTY INTERCHANGE 115KV CKT 2 Displacement | 2007-06-01 | 2010-06-01
| Potter - Roosevelt 345KV Displacement | 2007-06-01 | 2010-06-01
1162130 | CURRY COUNTY INTERCHANGE - ROOSEVELT COUNTY INTERCHANGE 115KV CKT 2 Displacement | 2007-06-01 | 2010-06-01
| Potter - Roosevelt 345KV Displacement | 2007-06-01 | 2010-06-01
Customer | Study Number
MIDW | AG3-2006-121
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
MIDW | 1167662 | WR | WR | 35 | 2007-02-01 | 2012-02-01 | 2009-07-01 | 2014-07-01 | 0 | 0 | 356864 | 742588.82
MIDW | 1167664 | WR | WR | 10 | 2007-02-01 | 2012-02-01 | 2009-07-01 | 2014-07-01 | 0 | 0 | 101982 | 212211.05
[9 empty] | 0 | 0 | 458846 | 954799.87
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1167662 | ARCADIA - SOONER 345kV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 297508 | 65000000 | 610277.48
| ROOSEVELT COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 1 Displacement | 2007-06-01 | 2010-06-01 |  |  | 51621 | 858753 | 117584.45
| ST JOHN CAPACITOR Displacement | 2008-06-01 | 2008-06-01 |  |  | 7735 | 114189 | 14726.88
[5 empty] | Total | 356864 | 65972942 | 742588.81
1167664 | ARCADIA - SOONER 345kV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 85023 | 65000000 | 174407.49
| ROOSEVELT COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 1 Displacement | 2007-06-01 | 2010-06-01 |  |  | 14749 | 858753 | 33595.88
| ST JOHN CAPACITOR Displacement | 2008-06-01 | 2008-06-01 |  |  | 2210 | 114189 | 4207.68
[5 empty] | Total | 101982 | 65972942 | 212211.05
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1167662 | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | 2007-06-01 | 2009-06-01 |  | No
| CLAY CENTER - GREENLEAF 115KV CKT 1 | 2007-06-01 | 2009-06-01 |  | No
| Evans - Grant - Chisolm Rebuild and Conversion Project | 2007-06-01 | 2009-06-01 |  | No
| GILL ENERGY CENTER EAST - GILLJCT269.0 69KV CKT 1 | 2007-06-01 | 2008-06-01 | 2007-10-01 | No
| GILL ENERGY CENTER EAST - MACARTHUR 69KV CKT 1 | 2007-06-01 | 2007-07-01 |  | No
| HAYS PLANT - SOUTH HAYS 115KV CKT 1 | 2008-06-01 | 2009-06-01 |  | No
| HAYS PLANT - VINE STREET 115KV CKT 1 | 2008-06-01 | 2009-06-01 |  | No
| KINSLEY CAPACITOR | 2007-06-01 | 2009-01-01 |  | No
| STRANGER CREEK TRANSFORMER CKT 2 | 2009-06-01 | 2009-06-01
1167664 | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | 2007-06-01 | 2009-06-01 |  | No
| CLAY CENTER - GREENLEAF 115KV CKT 1 | 2007-06-01 | 2009-06-01 |  | No
| Evans - Grant - Chisolm Rebuild and Conversion Project | 2007-06-01 | 2009-06-01 |  | No
| GILL ENERGY CENTER EAST - GILLJCT269.0 69KV CKT 1 | 2007-06-01 | 2008-06-01 | 2007-10-01 | No
| GILL ENERGY CENTER EAST - MACARTHUR 69KV CKT 1 | 2007-06-01 | 2007-07-01 |  | No
| HAYS PLANT - SOUTH HAYS 115KV CKT 1 | 2008-06-01 | 2009-06-01 |  | No
| HAYS PLANT - VINE STREET 115KV CKT 1 | 2008-06-01 | 2009-06-01 |  | No
| KINSLEY CAPACITOR | 2007-06-01 | 2009-01-01 |  | No
| STRANGER CREEK TRANSFORMER CKT 2 | 2009-06-01 | 2009-06-01
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1167662 | LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01
1167664 | LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1167662 | HEIZER TO KNOLL 230KV | 2007-06-01 | 2008-06-01 |  | No
| LACYGNE-PAOLA-WEST GARDER 345KV | 2007-06-01 | 2008-06-01 |  | No
| PHILLIPSBURG - RHOADES | 2007-06-01 | 2008-10-01 |  | No
| RENO - SUMMIT 345KV | 2011-01-01 | 2011-01-01
| WICHITA - RENO 345KV | 2007-02-01 | 2009-07-01 |  | No
1167664 | HEIZER TO KNOLL 230KV | 2007-06-01 | 2008-06-01 |  | No
| LACYGNE-PAOLA-WEST GARDER 345KV | 2007-06-01 | 2008-06-01 |  | No
| PHILLIPSBURG - RHOADES | 2007-06-01 | 2008-10-01 |  | No
| RENO - SUMMIT 345KV | 2011-01-01 | 2011-01-01
| WICHITA - RENO 345KV | 2007-02-01 | 2009-07-01 |  | No
Potential reservation deferral and redispatch requirement on the following upgrades due to positive MW Impact on limitations that require upgrade. No cost assignment due to negative MW impact on defined upgrade.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1167662 | CURRY COUNTY INTERCHANGE - ROOSEVELT COUNTY INTERCHANGE 115KV CKT 2 Displacement | 2007-06-01 | 2010-06-01
| Potter - Roosevelt 345KV Displacement | 2007-06-01 | 2010-06-01
1167664 | CURRY COUNTY INTERCHANGE - ROOSEVELT COUNTY INTERCHANGE 115KV CKT 2 Displacement | 2007-06-01 | 2010-06-01
| Potter - Roosevelt 345KV Displacement | 2007-06-01 | 2010-06-01
Customer | Study Number
NTEC | AG3-2006-035
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
NTEC | 1161974 | CSWS | CSWS | 52 | 2011-06-01 | 2031-06-01 |  |  | 6121447 | 0 | 6221447 | 20861245.85
[9 empty] | 6121447 | 0 | 6221447 | 20861245.85
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1161974 | DIANA - PERDUE 138KV CKT 1 | 2016-06-01 | 2016-06-01 |  |  | 750000 | 750000 | 1872198.55
| HEMPSTEAD - NW TEXARKANA 345 kV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 4684037 | 56000000 | 16394152.87
| HOOKS - LONESTAR ORDINANCE TAP 69KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 125000 | 125000 | 437671.1
| NEW BOSTON - NORTH NEW BOSTON 69KV CKT 1 Displacement | 2011-06-01 | 2011-06-01 |  |  | 100000 | 100000 | 0
| SOUTHWEST SHREVEPORT - SOUTHWEST SHREVEPORT TAP 138KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 369296 | 2500000 | 1484868.94
| SUGAR HILL (SUGAR HL) 138/69/12.47KV TRANSFORMER CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 193114 | 2500000 | 672354.39
[5 empty] | Total | 6221447 | 61975000 | 20861245.85
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1161974 | BANN - LONESTAR ORDINANCE TAP 69KV CKT 1 | 2011-06-01 | 2011-06-01
| BEN WHEELER - BARTONS CHAPEL | 2016-06-01 | 2016-06-01
| BIG SANDY - HAWKINS 69KV CKT 1 | 2016-06-01 | 2016-06-01
| BIG SANDY - PERDUE 69KV CKT 1 | 2016-06-01 | 2016-06-01
| DAINGERFIELD - JENKINS REC T 69KV CKT 1 | 2011-06-01 | 2011-06-01
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1161974 | SOUTHWEST SHREVEPORT (SW SHV 1) 345/138/13.8KV TRANSFORMER CKT 1 | 2010-06-01 | 2010-06-01
| SOUTHWEST SHREVEPORT (SW SHV 2) 345/138/13.8KV TRANSFORMER CKT 2 | 2010-06-01 | 2010-06-01
Customer | Study Number
OGE | AG3-2006-034
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
OGE | 1161665 | OKGE | SPA | 20 | 2007-02-01 | 2012-02-01 | 2009-06-01 | 2014-06-01 | 0 | 1080000 | 786564 | 286390.84
[9 empty] | 0 | 1080000 | 786564 | 286390.84
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1161665 | 5 TRIBES - HANCOCK 161KV CKT 1 Displacement | 2007-06-01 | 2009-06-01 |  | Yes | 604 | 100000 | 0
| 5 TRIBES - PECAN CREEK 161KV CKT 1 Displacement | 2007-06-01 | 2009-06-01 |  | Yes | 2819 | 466473 | 7816.84
| BEAVER - EUREKA SPRINGS 161KV CKT 1 AEPW | 2013-06-01 | 2013-06-01 |  |  | 197024 | 850000 | 215645.63
| BEAVER - EUREKA SPRINGS 161KV CKT 1 SWPA | 2013-06-01 | 2013-06-01 |  |  | 556304 | 2400000 | 0
| FRANKLIN SW - MIDWEST TAP 138KV CKT 1 OKGE Displacement | 2014-06-01 | 2014-06-01 |  |  | 590 | 14588 | 958.24
| FRANKLIN SW - MIDWEST TAP 138KV CKT 1 WFEC Displacement | 2014-06-01 | 2014-06-01 |  |  | 4047 | 100000 | 0
| JONES - JONESBORO 161KV CKT 1 SWPA | 2007-06-01 | 2008-06-01 | 2008-02-01 | Yes | 2000 | 2000 | 0
| MILLER - WHITE EAGLE 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 2739 | 300000 | 5608.36
| PECAN CREEK (PECANCK1) 345/161/13.8KV TRANSFORMER CKT 1 Displacement | 2007-06-01 | 2009-06-01 |  | Yes | 20437 | 3381928 | 56361.77
[5 empty] | Total | 786564 | 7614989 | 286390.84
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1161665 | ARCADIA - REDBUD 345 KV CKT 1 | 2006-06-01 | 2006-06-01
| ARCADIA - REDBUD 345 KV CKT 2 | 2006-06-01 | 2006-06-01
| FPL SWITCH - MOORELAND 138KV CKT 1 OKGE | 2006-06-01 | 2008-04-01
| FPL SWITCH - MOORELAND 138KV CKT 1 WFEC | 2006-06-01 | 2008-04-01
| HUGO POWER PLANT - VALLIANT 345 KV AEPW | 2010-05-01 | 2010-05-01
| HUGO POWER PLANT - VALLIANT 345 KV WFEC | 2010-05-01 | 2010-05-01
| LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01
Third Party Limitations.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1161665 | 5TRUMAN - HARISBURG TAP 161KV CKT 1 | 2011-06-01 | 2011-06-01
| JONES - JONESBORO 161KV CKT 1 ENTR | 2007-06-01 | 2007-06-01
| JONESBORO - JONESBORO NORTH (AECC) 161KV CKT 1 | 2011-06-01 | 2011-06-01
| JONESBORO NORTH (AECC) - PARAGOULD SOUTH (AECC) 161KV CKT 1 | 2011-06-01 | 2011-06-01
Customer | Study Number
OGE | AG3-2006-049
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
OGE | 1162077 | OKGE | OKGE | 384 | 2011-06-01 | 2031-06-01 |  |  | 37225529 | 0 | 37263748 | 157102840.81
[9 empty] | 37225529 | 0 | 37263748 | 157102840.81
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1162077 | 5 TRIBES - HANCOCK 161KV CKT 1 Displacement | 2007-06-01 | 2009-06-01 |  |  | 38219 | 100000 | 0
| 5 TRIBES - PECAN CREEK 161KV CKT 1 Displacement | 2007-06-01 | 2009-06-01 |  |  | 178281 | 466473 | 1038774.44
| ARCADIA - SOONER 345kV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 28557652 | 65000000 | 122169988.22
| ARKOMA - FT SMITHW 161KV CKT 1 | 2016-06-01 | 2016-06-01 |  |  | 2900000 | 2900000 | 8506967.77
| FAIRMONT TAP - WOODRING 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 576681 | 850000 | 2519827.41
| MILLER - WHITE EAGLE 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 101995 | 300000 | 438836.25
| PECAN CREEK (PECANCK1) 345/161/13.8KV TRANSFORMER CKT 1 Displacement | 2007-06-01 | 2009-06-01 |  |  | 1292540 | 3381928 | 7490165.43
| ROSEHILL - SOONER 345KV CKT 1 OKGE Displacement | 2011-06-01 | 2011-06-01 |  |  | 1712779 | 6322628 | 7389882.47
| ROSEHILL - SOONER 345KV CKT 1 WERE Displacement | 2011-06-01 | 2011-06-01 |  |  | 996162 | 3677275 | 3574573.92
| WAUKOMIS TAP - WOODRING 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 909439 | 1500000 | 3973824.9
[5 empty] | Total | 37263748 | 84498304 | 157102840.81
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162077 | COLONY - FT SMITH 161KV CKT 1 | 2011-06-01 | 2011-06-01
Customer | Study Number
OMPA | AG3-2006-028
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
OMPA | 1159596 | CSWS | CSWS | 41 | 2011-06-01 | 2031-06-01 |  |  | 7380000 | 0 | 28376454 | 111895824.98
[9 empty] | 7380000 | 0 | 28376454 | 111895824.98
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1159596 | ARCADIA - SOONER 345kV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 40156 | 65000000 | 171787.86
| CANEY CREEK 345/138 kV | 2011-06-01 | 2011-06-01 |  |  | 19705875 | 31000000 | 84785060.82
| CURRY COUNTY INTERCHANGE - ROOSEVELT COUNTY INTERCHANGE 115KV CKT 2 Displacement | 2007-06-01 | 2010-06-01 |  |  | 5569 | 344362 | 24483.01
| DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 AEPW | 2011-06-01 | 2011-06-01 |  |  | 541839 | 9000000 | 1958383.76
| FAIRMONT TAP - WOODRING 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 57388 | 850000 | 250758.83
| HEMPSTEAD - NW TEXARKANA 345 kV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 3562356 | 56000000 | 12468263.77
| Hugo - SunnySide 345kV | 2011-06-01 | 2011-06-01 |  |  | 3711580 | 50000000 | 9104144.1
| MILLER - WHITE EAGLE 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 25689 | 300000 | 110527.62
| Potter - Roosevelt 345KV Displacement | 2007-06-01 | 2010-06-01 |  |  | 15529 | 10372158 | 68224.64
| ROOSEVELT COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 1 Displacement | 2007-06-01 | 2010-06-01 |  |  | 2887 | 858753 | 12700.54
| SUGAR HILL (SUGAR HL) 138/69/12.47KV TRANSFORMER CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 125601 | 2500000 | 437298.09
| SUNNYSIDE 345/138KV TRANSFORMER CKT 2 | 2011-06-01 | 2011-06-01 |  |  | 481086 | 6500000 | 2063310.29
| WAUKOMIS TAP - WOODRING 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 100899 | 1500000 | 440881.64
[5 empty] | Total | 28376454 | 234225273 | 111895824.97
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1159596 | BEN WHEELER - BARTONS CHAPEL | 2016-06-01 | 2016-06-01
| Mooreland - Potter 345 kV SPS | 2016-06-01 | 2016-06-01
| Mooreland - Potter 345 kV WFEC | 2016-06-01 | 2016-06-01
| Mooreland 345/138 kV Transformer | 2016-06-01 | 2016-06-01
| POTTER COUNTY INTERCHANGE (POTTR CO) 345/230/13.2KV TRANSFORMER CKT 2 | 2016-06-01 | 2016-06-01
| Sayre interconnect | 2011-06-01 | 2011-06-01
| SNYDER - SNYDER INTERCONNECTION | 2016-06-01 | 2016-06-01
| Spearville - Mooreland 345 kV SUNC | 2016-06-01 | 2016-06-01
| Spearville - Mooreland 345 kV WFEC | 2016-06-01 | 2016-06-01
| TUCO INTERCHANGE 345/115KV TRANSFORMER CKT 1 | 2016-06-01 | 2016-06-01
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1159596 | ARCADIA - REDBUD 345 KV CKT 1 | 2006-06-01 | 2006-06-01
| ARCADIA - REDBUD 345 KV CKT 2 | 2006-06-01 | 2006-06-01
| CACHE - SNYDER 138KV CKT 1 | 2008-06-01 | 2008-06-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1159596 | RENO - SUMMIT 345KV | 2011-01-01 | 2011-01-01
| WICHITA - RENO 345KV | 2007-02-01 | 2009-07-01
Third Party Limitations.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1159596 | ARKANSAS NUCLEAR ONE 161 - RUSSELLVILLE NORTH 161KV CKT 1 | 2007-06-01 | 2007-06-01
| DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 ENTR | 2011-06-01 | 2011-06-01
| EVERTON - HARRISON-EAST 161KV CKT 1 | 2011-06-01 | 2011-06-01
| RUSSELLVILLE EAST - RUSSELLVILLE NORTH 161KV CKT 1 | 2011-06-01 | 2011-06-01
Customer | Study Number
OMPA | AG3-2006-050
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
OMPA | 1162095 | OKGE | OKGE | 73 | 2011-06-01 | 2031-06-01 |  |  | 5848818 | 0 | 5859066 | 24947918.3
[9 empty] | 5848818 | 0 | 5859066 | 24947918.3
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1162095 | ARCADIA - SOONER 345kV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 4943904 | 65000000 | 21150082.42
| FAIRMONT TAP - WOODRING 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 119068 | 850000 | 520271.71
| FRANKLIN SW - MIDWEST TAP 138KV CKT 1 OKGE Displacement | 2014-06-01 | 2014-06-01 |  |  | 1495 | 14588 | 5102.04
| FRANKLIN SW - MIDWEST TAP 138KV CKT 1 WFEC Displacement | 2014-06-01 | 2014-06-01 |  |  | 10248 | 100000 | 0
| MILLER - WHITE EAGLE 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 62160 | 300000 | 267445.08
| ROSEHILL - SOONER 345KV CKT 1 OKGE Displacement | 2011-06-01 | 2011-06-01 |  |  | 295730 | 6322628 | 1275943.91
| ROSEHILL - SOONER 345KV CKT 1 WERE Displacement | 2011-06-01 | 2011-06-01 |  |  | 171998 | 3677275 | 617188.33
| WAUKOMIS TAP - WOODRING 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 254463 | 1500000 | 1111884.81
[5 empty] | Total | 5859066 | 77764491 | 24947918.3
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162095 | Mooreland - Potter 345 kV SPS | 2016-06-01 | 2016-06-01
| Mooreland - Potter 345 kV WFEC | 2016-06-01 | 2016-06-01
| Mooreland 345/138 kV Transformer | 2016-06-01 | 2016-06-01
| POTTER COUNTY INTERCHANGE (POTTR CO) 345/230/13.2KV TRANSFORMER CKT 2 | 2016-06-01 | 2016-06-01
| Sayre interconnect | 2011-06-01 | 2011-06-01
| SNYDER - SNYDER INTERCONNECTION | 2016-06-01 | 2016-06-01
| Spearville - Mooreland 345 kV SUNC | 2016-06-01 | 2016-06-01
| Spearville - Mooreland 345 kV WFEC | 2016-06-01 | 2016-06-01
| TUCO INTERCHANGE 345/115KV TRANSFORMER CKT 1 | 2016-06-01 | 2016-06-01
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162095 | CACHE - SNYDER 138KV CKT 1 | 2008-06-01 | 2008-06-01
Customer | Study Number
SEPC | AG3-2006-113
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
SEPC | 1162670 | WR | SECI | 51 | 2007-12-01 | 2027-12-01 | 2009-07-01 | 2029-07-01 | 0 | 0 | 307835 | 1158971.18
[9 empty] | 0 | 0 | 307835 | 1158971.18
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1162670 | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 19188 | 300000 | 72754.74
| EXIDE JUNCTION - SUMMIT 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 114604 | 2000000 | 423978.34
| NORTHVIEW - SUMMIT 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 50726 | 610000 | 197192.74
| ROOSEVELT COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 1 Displacement | 2007-06-01 | 2010-06-01 |  |  | 123317 | 858753 | 465045.36
[5 empty] | Total | 307835 | 3768753 | 1158971.18
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162670 | HAYS PLANT - SOUTH HAYS 115KV CKT 1 | 2008-06-01 | 2009-06-01 |  | No
| HAYS PLANT - VINE STREET 115KV CKT 1 | 2008-06-01 | 2009-06-01 |  | No
| Mooreland - Potter 345 kV SPS | 2016-06-01 | 2016-06-01
| Mooreland - Potter 345 kV WFEC | 2016-06-01 | 2016-06-01
| Mooreland 345/138 kV Transformer | 2016-06-01 | 2016-06-01
| POTTER COUNTY INTERCHANGE (POTTR CO) 345/230/13.2KV TRANSFORMER CKT 2 | 2016-06-01 | 2016-06-01
| Spearville - Mooreland 345 kV SUNC | 2016-06-01 | 2016-06-01
| Spearville - Mooreland 345 kV WFEC | 2016-06-01 | 2016-06-01
| TUCO INTERCHANGE 345/115KV TRANSFORMER CKT 1 | 2016-06-01 | 2016-06-01
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162670 | IATAN - NASHUA 345KV CKT 1 | 2010-06-01 | 2010-06-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162670 | PHILLIPSBURG - RHOADES | 2007-06-01 | 2008-10-01 |  | No
| RENO - SUMMIT 345KV | 2011-01-01 | 2011-01-01
| WICHITA - RENO 345KV | 2007-02-01 | 2009-07-01 |  | No
Potential reservation deferral and redispatch requirement on the following upgrades due to positive MW Impact on limitations that require upgrade. No cost assignment due to negative MW impact on defined upgrade.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162670 | CURRY COUNTY INTERCHANGE - ROOSEVELT COUNTY INTERCHANGE 115KV CKT 2 Displacement | 2007-06-01 | 2010-06-01
| Potter - Roosevelt 345KV Displacement | 2007-06-01 | 2010-06-01
Customer | Study Number
SPSM | AG3-2006-115
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
SPSM | 1162675 | OKGE | SPS | 100 | 2007-02-01 | 2008-02-01 | 2010-06-01 | 2011-06-01 | 0 | 1741200 | 9809510 | 20360374.61
[9 empty] | 0 | 1741200 | 9809510 | 20360374.61
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1162675 | CURRY COUNTY INTERCHANGE - ROOSEVELT COUNTY INTERCHANGE 115KV CKT 2 Displacement | 2007-06-01 | 2010-06-01 |  | No | 199148 | 344362 | 418227.68
| FAIRMONT TAP - WOODRING 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 96864 | 850000 | 185333.57
| Potter - Roosevelt 345KV Displacement | 2007-06-01 | 2010-06-01 |  | No | 8568559 | 10372158 | 17982697.64
| ROSEHILL - SOONER 345KV CKT 1 OKGE Displacement | 2011-06-01 | 2011-06-01 |  |  | 448746 | 6322628 | 847799.85
| ROSEHILL - SOONER 345KV CKT 1 WERE Displacement | 2011-06-01 | 2011-06-01 |  |  | 260993 | 3677275 | 476298.77
| SPS MUST RUN GENERATION #1 | 2007-04-01 | 2007-04-01 |  |  | 0 | 0 | 0
| SPS MUST RUN GENERATION #2 | 2007-10-01 | 2007-10-01 |  |  | 0 | 0 | 0
| SPS MUST RUN GENERATION #3 | 2007-06-01 | 2007-06-01 |  |  | 0 | 0 | 0
| SPS MUST RUN GENERATION #4 | 2007-12-01 | 2007-12-01 |  |  | 0 | 0 | 0
| SPS MUST RUN GENERATION #5 | 2007-10-01 | 2007-10-01 |  |  | 0 | 0 | 0
| WAUKOMIS TAP - WOODRING 138KV CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 235200 | 1500000 | 450017.1
[5 empty] | Total | 9809510 | 23066423 | 20360374.61
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162675 | CARLSBAD PLANT 115/69KV TRANSFORMERS | 2007-06-01 | 2008-06-01 |  | No
| MUSTANG STATION 230/115KV TRANSFORMER CKT 1 | 2007-04-01 | 2008-06-01 |  | No
| Sayre interconnect | 2011-06-01 | 2011-06-01
| Seven Rivers to Pecos to Potash Junction 230kV | 2007-06-01 | 2008-06-01 | 2007-10-01 | No
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162675 | ARCADIA - REDBUD 345 KV CKT 1 | 2006-06-01 | 2006-06-01
| ARCADIA - REDBUD 345 KV CKT 2 | 2006-06-01 | 2006-06-01
| CACHE - SNYDER 138KV CKT 1 | 2008-06-01 | 2008-06-01
| LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162675 | HOBBS 115 KV Lines | 2007-10-01 | 2008-06-01 | 2008-04-01 | No
| HOBBS 230/115KV TRANSFORMER CKT 2 | 2007-10-01 | 2008-06-01 | 2008-04-01 | No
| HOBBS Substation and Lines | 2007-10-01 | 2008-06-01 | 2008-04-01 | No
| Mustang-San Andr-Amerada Hess 115KV Displacement | 2007-04-01 | 2008-06-01 |  | No
| RENO - SUMMIT 345KV | 2011-01-01 | 2011-01-01
| TUCO INTERCHANGE 230KV #1 | 2007-06-01 | 2007-06-01
| TUCO INTERCHANGE 230KV #2 | 2008-06-01 | 2008-06-01
| WICHITA - RENO 345KV | 2007-02-01 | 2009-07-01 |  | No
| YOAKUM COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 1 Displacement | 2007-06-01 | 2008-06-01 | 2007-10-01 | No
Potential reservation deferral and redispatch requirement on the following upgrades due to positive MW Impact on limitations that require upgrade. No cost assignment due to negative MW impact on defined upgrade.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162675 | ROOSEVELT COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 1 Displacement | 2007-06-01 | 2010-06-01 |  | No
* The existing firm reservations offered for curtailment provided no interim mitigation on the limitations requiring the upgrades for the requested service.
Customer | Study Number
UCU | AG3-2006-025D
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
UCU | 1152228 | MPS | MPS | 585 | 2007-02-01 | 2027-02-01 | 2008-10-01 | 2028-10-01 | 0 | 0 | 2100000 | 7147507.83
[9 empty] | 0 | 0 | 2100000 | 7147507.83
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1152228 | HARRISONVILLE 161/69KV TRANSFORMER CKT 1 | 2007-06-01 | 2009-06-01 | 2008-10-01 | No | 2100000 | 2100000 | 7147507.83
| MPS MUST RUN GENERATION #1 | 2006-12-01 | 2006-12-01 |  |  | 0 | 0 | 0
[5 empty] | Total | 2100000 | 2100000 | 7147507.83
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1152228 | EAST 40MVAR CAPACITOR | 2009-01-01 | 2009-01-01
| INDUSTRIAL PARK - LAKE ROAD 161KV CKT 1 | 2007-06-01 | 2008-06-01 |  | No
| RALPH GREEN 14.4MVAR CAPACITOR | 2011-06-01 | 2011-06-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1152228 | CLINTON - CLINTON GREEN STREET 69KV CKT 1 | 2016-06-01 | 2011-06-01
| CLINTON - CLINTON PLANT 69KV CKT 1 | 2011-06-01 | 2011-06-01
Customer | Study Number
UCU | AG3-2006-052D
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
UCU | 1162075 | WR | MPS | 51 | 2008-01-01 | 2028-01-01 | 2009-07-01 | 2029-07-01 | 0 | 19718640 | 343378 | 1293873.15
[9 empty] | 0 | 19718640 | 343378 | 1293873.15
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1162075 | CURRY COUNTY INTERCHANGE - ROOSEVELT COUNTY INTERCHANGE 115KV CKT 2 Displacement | 2007-06-01 | 2010-06-01 |  |  | 10711 | 344362 | 40365.89
| EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 17259 | 300000 | 65440.59
| EXIDE JUNCTION - SUMMIT 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 103082 | 2000000 | 381352.62
| MPS MUST RUN GENERATION #1 | 2006-12-01 | 2006-12-01 |  |  | 0 | 0 | 0
| NORTHVIEW - SUMMIT 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 58275 | 610000 | 226538.79
| Potter - Roosevelt 345KV Displacement | 2007-06-01 | 2010-06-01 |  |  | 154051 | 10372158 | 580175.26
[5 empty] | Total | 343378 | 13626520 | 1293873.15
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162075 | EAST 40MVAR CAPACITOR | 2009-01-01 | 2009-01-01
| HAYS PLANT - SOUTH HAYS 115KV CKT 1 | 2008-06-01 | 2009-06-01 |  | No
| HAYS PLANT - VINE STREET 115KV CKT 1 | 2008-06-01 | 2009-06-01 |  | No
| INDUSTRIAL PARK - LAKE ROAD 161KV CKT 1 | 2007-06-01 | 2008-06-01 |  | No
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162075 | IATAN - NASHUA 345KV CKT 1 | 2010-06-01 | 2010-06-01
| LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162075 | CLINTON - CLINTON GREEN STREET 69KV CKT 1 | 2016-06-01 | 2011-06-01
| CLINTON - CLINTON PLANT 69KV CKT 1 | 2011-06-01 | 2011-06-01
| RENO - SUMMIT 345KV | 2011-01-01 | 2011-01-01
| WICHITA - RENO 345KV | 2007-02-01 | 2009-07-01 |  | No
Potential reservation deferral and redispatch requirement on the following upgrades due to positive MW Impact on limitations that require upgrade. No cost assignment due to negative MW impact on defined upgrade.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162075 | ROOSEVELT COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 1 Displacement | 2007-06-01 | 2010-06-01
Customer | Study Number
UCU | AG3-2006-088D
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
UCU | 1162678 | WR | MPS | 25 | 2008-01-01 | 2028-01-01 | 2009-07-01 | 2029-07-01 | 0 | 9666000 | 168314 | 634219.66
UCU | 1162681 | WR | MPS | 25 | 2008-01-01 | 2028-01-01 | 2009-07-01 | 2029-07-01 | 0 | 9666000 | 168314 | 634219.66
[9 empty] | 0 | 19332000 | 336628 | 1268439.32
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1162678 | CURRY COUNTY INTERCHANGE - ROOSEVELT COUNTY INTERCHANGE 115KV CKT 2 Displacement | 2007-06-01 | 2010-06-01 |  |  | 5249 | 344362 | 19781.58
| EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 8460 | 300000 | 32077.61
| EXIDE JUNCTION - SUMMIT 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 50527 | 2000000 | 186925.01
| MPS MUST RUN GENERATION #1 | 2006-12-01 | 2006-12-01 |  |  | 0 | 0 | 0
| NORTHVIEW - SUMMIT 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 28567 | 610000 | 111051.63
| Potter - Roosevelt 345KV Displacement | 2007-06-01 | 2010-06-01 |  |  | 75511 | 10372158 | 284383.83
[5 empty] | Total | 168314 | 13626520 | 634219.66
1162681 | CURRY COUNTY INTERCHANGE - ROOSEVELT COUNTY INTERCHANGE 115KV CKT 2 Displacement | 2007-06-01 | 2010-06-01 |  |  | 5249 | 344362 | 19781.58
| EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 8460 | 300000 | 32077.61
| EXIDE JUNCTION - SUMMIT 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 50527 | 2000000 | 186925.01
| MPS MUST RUN GENERATION #1 | 2006-12-01 | 2006-12-01 |  |  | 0 | 0 | 0
| NORTHVIEW - SUMMIT 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 28567 | 610000 | 111051.63
| Potter - Roosevelt 345KV Displacement | 2007-06-01 | 2010-06-01 |  |  | 75511 | 10372158 | 284383.83
[5 empty] | Total | 168314 | 13626520 | 634219.66
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162678 | EAST 40MVAR CAPACITOR | 2009-01-01 | 2009-01-01
| HAYS PLANT - SOUTH HAYS 115KV CKT 1 | 2008-06-01 | 2009-06-01 |  | No
| HAYS PLANT - VINE STREET 115KV CKT 1 | 2008-06-01 | 2009-06-01 |  | No
| INDUSTRIAL PARK - LAKE ROAD 161KV CKT 1 | 2007-06-01 | 2008-06-01 |  | No
1162681 | EAST 40MVAR CAPACITOR | 2009-01-01 | 2009-01-01
| HAYS PLANT - SOUTH HAYS 115KV CKT 1 | 2008-06-01 | 2009-06-01 |  | No
| HAYS PLANT - VINE STREET 115KV CKT 1 | 2008-06-01 | 2009-06-01 |  | No
| INDUSTRIAL PARK - LAKE ROAD 161KV CKT 1 | 2007-06-01 | 2008-06-01 |  | No
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162678 | IATAN - NASHUA 345KV CKT 1 | 2010-06-01 | 2010-06-01
| LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01
1162681 | IATAN - NASHUA 345KV CKT 1 | 2010-06-01 | 2010-06-01
| LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162678 | CLINTON - CLINTON GREEN STREET 69KV CKT 1 | 2016-06-01 | 2011-06-01
| CLINTON - CLINTON PLANT 69KV CKT 1 | 2011-06-01 | 2011-06-01
| RENO - SUMMIT 345KV | 2011-01-01 | 2011-01-01
| WICHITA - RENO 345KV | 2007-02-01 | 2009-07-01 |  | No
1162681 | CLINTON - CLINTON GREEN STREET 69KV CKT 1 | 2016-06-01 | 2011-06-01
| CLINTON - CLINTON PLANT 69KV CKT 1 | 2011-06-01 | 2011-06-01
| RENO - SUMMIT 345KV | 2011-01-01 | 2011-01-01
| WICHITA - RENO 345KV | 2007-02-01 | 2009-07-01 |  | No
Potential reservation deferral and redispatch requirement on the following upgrades due to positive MW Impact on limitations that require upgrade. No cost assignment due to negative MW impact on defined upgrade.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1162678 | ROOSEVELT COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 1 Displacement | 2007-06-01 | 2010-06-01
1162681 | ROOSEVELT COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 1 Displacement | 2007-06-01 | 2010-06-01
Customer | Study Number
WRGS | AG3-2006-024D
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
WRGS | 1161506 | WR | WR | 380 | 2008-05-01 | 2014-05-01 | 2009-07-01 | 2015-07-01 | 1531041 | 0 | 1531041 | 3572237.2
[9 empty] | 1531041 | 0 | 1531041 | 3572237.2
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1161506 | BOEING - STEARMAN 138KV CKT 1 | 2012-06-01 | 2012-06-01 |  |  | 87449 | 300000 | 126882.78
| EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 62692 | 300000 | 154664.29
| EXIDE JUNCTION - SUMMIT 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 445369 | 2000000 | 1072038.07
| NORTHVIEW - SUMMIT 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 140688 | 610000 | 355847.31
| ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER Displacement | 2007-06-01 | 2009-06-01 | 2008-10-01 | Yes | 451970 | 1132688 | 1138962.66
| ROSEHILL - SOONER 345KV CKT 1 OKGE Displacement | 2011-06-01 | 2011-06-01 |  |  | 216788 | 6322628 | 467701.97
| ROSEHILL - SOONER 345KV CKT 1 WERE Displacement | 2011-06-01 | 2011-06-01 |  |  | 126085 | 3677275 | 256140.14
[5 empty] | Total | 1531041 | 14342591 | 3572237.22
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1161506 | ALTAMONT 138KV | 2011-06-01 | 2011-06-01
| DEARING (DEARIN1X) 138/69/13.2KV TRANSFORMER CKT 1 | 2011-12-01 | 2011-12-01
| Evans - Grant - Chisolm Rebuild and Conversion Project | 2007-06-01 | 2009-06-01 |  | Yes
| STRANGER CREEK TRANSFORMER CKT 2 | 2009-06-01 | 2009-06-01
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1161506 | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 Displacement | 2011-06-01 | 2011-06-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1161506 | RENO - SUMMIT 345KV | 2011-01-01 | 2011-01-01
| WICHITA - RENO 345KV | 2007-02-01 | 2009-07-01 |  | Yes
Customer | Study Number
WRGS | AG3-2006-025
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
WRGS | 1140120 | WR | WR | 360 | 2009-05-01 | 2015-05-01 | 2009-07-01 | 2015-07-01 | 0 | 0 | 1044255 | 2324972.36
[9 empty] | 0 | 0 | 1044255 | 2324972.36
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1140120 | BOEING - STEARMAN 138KV CKT 1 | 2012-06-01 | 2012-06-01 |  |  | 84628 | 300000 | 121309.88
| EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 60669 | 300000 | 147869.65
| EXIDE JUNCTION - SUMMIT 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 430999 | 2000000 | 1024945.46
| NORTHVIEW - SUMMIT 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 136151 | 610000 | 340221.48
| ROSEHILL - SOONER 345KV CKT 1 OKGE Displacement | 2011-06-01 | 2011-06-01 |  |  | 209792 | 6322628 | 445739.15
| ROSEHILL - SOONER 345KV CKT 1 WERE Displacement | 2011-06-01 | 2011-06-01 |  |  | 122016 | 3677275 | 244886.74
[5 empty] | Total | 1044255 | 13209903 | 2324972.36
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1140120 | ALTAMONT 138KV | 2011-06-01 | 2011-06-01
| DEARING (DEARIN1X) 138/69/13.2KV TRANSFORMER CKT 1 | 2011-12-01 | 2011-12-01
| Evans - Grant - Chisolm Rebuild and Conversion Project | 2007-06-01 | 2009-06-01
| STRANGER CREEK TRANSFORMER CKT 2 | 2009-06-01 | 2009-06-01
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1140120 | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 Displacement | 2011-06-01 | 2011-06-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1140120 | RENO - SUMMIT 345KV | 2011-01-01 | 2011-01-01
| WICHITA - RENO 345KV | 2007-02-01 | 2009-07-01 |  | Yes
Customer | Study Number
WRGS | AG3-2006-036D
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
WRGS | 1161997 | MPS | WR | 300 | 2007-06-01 | 2014-06-01 | 2009-07-01 | 2016-07-01 | 2315803 | 0 | 2315803 | 5423927.56
[9 empty] | 2315803 | 0 | 2315803 | 5423927.56
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1161997 | BOEING - STEARMAN 138KV CKT 1 | 2012-06-01 | 2012-06-01 |  |  | 127922 | 300000 | 191934.26
| EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 59061 | 300000 | 150673.94
| EXIDE JUNCTION - SUMMIT 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 421392 | 2000000 | 1048904.48
| NORTHVIEW - SUMMIT 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 144880 | 610000 | 378943.53
| ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER Displacement | 2007-06-01 | 2009-06-01 | 2008-10-01 | Yes | 546393 | 1132688 | 1423850.63
| ROSEHILL - SOONER 345KV CKT 1 OKGE Displacement | 2011-06-01 | 2011-06-01 |  |  | 642483 | 6322628 | 1444630.59
| ROSEHILL - SOONER 345KV CKT 1 WERE Displacement | 2011-06-01 | 2011-06-01 |  |  | 373672 | 3677275 | 784990.13
[5 empty] | Total | 2315803 | 14342591 | 5423927.56
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1161997 | ALTAMONT 138KV | 2011-06-01 | 2011-06-01
| CROSSTOWN - NEAST 161KV CKT 1 | 2015-06-01 | 2015-06-01
| DEARING (DEARIN1X) 138/69/13.2KV TRANSFORMER CKT 1 | 2011-12-01 | 2011-12-01
| Evans - Grant - Chisolm Rebuild and Conversion Project | 2007-06-01 | 2009-06-01 |  | Yes
| GILL ENERGY CENTER EAST - INTERSTATE 138KV CKT 1 | 2016-06-01 | 2016-06-01
| STRANGER CREEK TRANSFORMER CKT 2 | 2009-06-01 | 2009-06-01
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1161997 | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 Displacement | 2011-06-01 | 2011-06-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1161997 | RENO - SUMMIT 345KV | 2011-01-01 | 2011-01-01
| WICHITA - RENO 345KV | 2007-02-01 | 2009-07-01 |  | Yes

## Table4
Transmission Owner | Upgrade | Solution | Earliest Data Upgrade Required (COD) | Estimated Date of Upgrade Completion (EOC) | Estimated Engineering & Construction Cost
AEPW | ARSENAL HILL - FORT HUMBUG 138KV CKT 1 | Rebuild 3.24 miles of 1272 AAC with 2156 ACSR. Replace 3 switches, breaker jumpers, and reset CTs @ Arsenal Hill. Replace 2 switches and jumpers @ Fort Humbug | 2011-06-01 | 2011-06-01 | 2750000
AEPW | ARSENAL HILL - MCWILLIE STREET 138KV CKT 1 | Replace Arsenal Hill switches and jumpers | 2011-06-01 | 2011-06-01 | 100000
AEPW | ARSENAL HILL - WATERWORKS 69KV CKT 1 | Rebuild 2.55 miles of 666 ACSR with 1272 ACSR | 2011-06-01 | 2011-06-01 | 2000000
AEPW | ARSENAL HILL (ARSHILL1) 138/69/12.47KV TRANSFORMER CKT 1 | Replace auto & 69 kV breaker and switches | 2011-06-01 | 2011-06-01 | 2500000
AEPW | ARSENAL HILL (ARSHILL2) 138/69/14.5KV TRANSFORMER CKT 2 | Replace auto & 69 kV breaker and switches | 2011-06-01 | 2011-06-01 | 2500000
AEPW | BEAVER - EUREKA SPRINGS 161KV CKT 1 AEPW | Reconductor 1.25 miles of 795 ACSR with 1590 ACSR. | 2013-06-01 | 2013-06-01 | 850000
AEPW | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 AEPW | Rebuild 17.96 miles of 250 Copperweld with 795 ACSR. | 2011-06-01 | 2011-06-01 | 9000000
AEPW | DIANA - PERDUE 138KV CKT 1 | Replace Breakers 9310 & 10080 & five switches @ Perdue. Replace switch 12798 @ Diana | 2016-06-01 | 2016-06-01 | 750000
AEPW | DYESS - ELM SPRINGS REC 161KV CKT 1 | Replace Elm Springs switch. Rebuild 5.17 miles of line. | 2011-06-01 | 2011-06-01 | 5000000
AEPW | DYESS - TONTITOWN 161KV CKT 1 | Replace Dyess Breaker, Switches, & wavetrap | 2011-06-01 | 2011-06-01 | 500000
AEPW | HEMPSTEAD - NW TEXARKANA 345 kV CKT 1 | Build 33 miles of 2-795MCM ACSR from Turk NW Texarkana, Add 345kV terminal at NW Texarkana, Add 345kV terminal at Turk | 2011-06-01 | 2011-06-01 | 56000000
AEPW | HOOKS - LONESTAR ORDINANCE TAP 69KV CKT 1 | Replace Lone Star Ordinance Tap switch | 2011-06-01 | 2011-06-01 | 125000
AEPW | NEW BOSTON - NORTH NEW BOSTON 69KV CKT 1 Displacement | Replace New Boston switches | 2011-06-01 | 2011-06-01 | 100000
AEPW | SOUTH TEXARKANA REC - TEXARKANA PLANT 69KV CKT 1 | Rebuild 5.92 miles of 266 ACSR with 795 ACSR. Replace switches, jumpers, and reset CTs & relays @ Texarkana Plant | 2016-06-01 | 2016-06-01 | 4000000
AEPW | SOUTHWEST SHREVEPORT - SOUTHWEST SHREVEPORT TAP 138KV CKT 1 | Rebuild 2.29 miles of 2-397.5 ACSR with 1590 ACSR. | 2009-06-01 | 2009-06-01 | 2500000
AEPW | SOUTHWEST SHREVEPORT (SW SHV 1) 345/138/13.8KV TRANSFORMER CKT 1 Expedite | Using IEEE Guide for Loading of Mineral-Oil Immersed Power Transformers (C57.91-2000) Re-rate the autos. Replace .two 138 kV breakers and five 138 kV switches. Reset relays and CTs | 2008-06-01 | 2009-04-01 | 1500000
AEPW | SOUTHWEST SHREVEPORT (SW SHV 1) 345/138/13.8KV TRANSFORMER CKT 2 Expedite | Using IEEE Guide for Loading of Mineral-Oil Immersed Power Transformers (C57.91-2000) Re-rate the autos. Replace .two 138 kV breakers and five 138 kV switches. Reset relays and CTs | 2008-06-01 | 2009-04-01 | 1500000
AEPW | SUGAR HILL (SUGAR HL) 138/69/12.47KV TRANSFORMER CKT 1 | Replace auto & 69 kV breaker and switches or Add 2nd Auto | 2011-06-01 | 2011-06-01 | 2500000
GRDA | CLAREMORE (CLRAUTO3) 161/69/13.8KV TRANSFORMER CKT 3 | Add 3rd 161/69 KV Transformer | 2007-06-01 | 2009-06-01 | 2300000
KACP | COLLEGE - CRAIG 161KV CKT 1 | Reconductor 4 miles with 1192.5 ACSS, 558 normal/emergency rating and upgrade breaker. | 2016-06-01 | 2016-06-01 | 700000
MIDW | ST JOHN CAPACITOR Displacement | 20MVar capacitor at ST John | 2008-06-01 | 2008-06-01 | 114189
MIPU | HARRISONVILLE 161/69KV TRANSFORMER CKT 1 | Transformer Upgrade | 2007-06-01 | 2009-06-01 | 2100000
MIPU | MPS MUST RUN GENERATION #1 | MPS Voltage Instability due to EAST - WOODBINE 161KV CKT 1 and ST JOE - WOODBINE 161KV CKT 1 contingencies in the 2006/07 Winter Peak, 2007 Spring Peak, 2007 Summer Peak, 2007Summer Shoulder, 2007/08 Winter Peak, 2008 Summer Peak, 2008/09 Winter Peak. Must Run Lake Road Generation. | 2006-12-01 | 2006-12-01 | 0
OKGE | 5 TRIBES - HANCOCK 161KV CKT 1 Displacement | Replace 800A Wave Trap, increase Relay CTR to 1200-5A. | 2007-06-01 | 2009-06-01 | 100000
OKGE | 5 TRIBES - PECAN CREEK 161KV CKT 1 Displacement | replace 636AS33 conductor with 795AS33 | 2007-06-01 | 2009-06-01 | 466473
OKGE | ARCADIA - SOONER 345kV CKT 1 | Build 65 miles of 345kV line from Sooner to Arcadia. Add Terminal equipment at each end | 2011-06-01 | 2011-06-01 | 65000000
OKGE | ARKOMA - FT SMITHW 161KV CKT 1 | Replace 1200A terminal equipment at Arkoma to 2000A and rebuild 4.47 miles of line to 1590AS52. | 2016-06-01 | 2016-06-01 | 2900000
OKGE | CANEY CREEK 345/138 kV | Tap Sunnyside - Pittsburg 345kV and build new substation between Russett and Mills Creek. Build 25 miles of 138kV from new substation to Caney Creek | 2011-06-01 | 2011-06-01 | 31000000
OKGE | FAIRMONT TAP - WOODRING 138KV CKT 1 | Reconductor .75 with ACCC conductor. Increase CTRs to at least 1600-5 ratio. Line relays will need to check to determine if replacement is needed. | 2011-06-01 | 2011-06-01 | 850000
OKGE | FRANKLIN SW - MIDWEST TAP 138KV CKT 1 OKGE Displacement | Reconductor 1.27 miles of line to 1590AS52. WFEC will have to provide upgrade solution also for their Franklin (WFEC). | 2014-06-01 | 2014-06-01 | 14588
OKGE | MILLER - WHITE EAGLE 138KV CKT 1 | Replace line relay at White Eagle & Cont. Empire | 2011-06-01 | 2011-06-01 | 300000
OKGE | PECAN CREEK (PECANCK1) 345/161/13.8KV TRANSFORMER CKT 1 Displacement | Add a 345/161 kV 369MVA transformer | 2007-06-01 | 2009-06-01 | 3381928
OKGE | ROSEHILL - SOONER 345KV CKT 1 OKGE Displacement | New 345 kV line from Sooner to Oklahoma/Kansas | 2011-06-01 | 2011-06-01 | 6322628
OKGE | RUSSETT - RUSSETT 138KV CKT 1 OKGE | Replace trap and increase CTR. Pending verification of relays. | 2016-06-01 | 2016-06-01 | 45000
OKGE | RUSSETT - RUSSETT 138KV CKT 1 WFEC | Upgrade Terminal Equip CTs at Russett | 2016-06-01 | 2016-06-01 | 75000
OKGE | SUNNYSIDE 345/138KV TRANSFORMER CKT 2 | Add 2nd 345/138KV Auto | 2011-06-01 | 2011-06-01 | 6500000
OKGE | WAUKOMIS TAP - WOODRING 138KV CKT 1 | Reconductor 2.75 miles of line with Drake ACCC conductor and increase CTR. | 2011-06-01 | 2011-06-01 | 1500000
SPS | CURRY COUNTY INTERCHANGE - ROOSEVELT COUNTY INTERCHANGE 115KV CKT 2 Displacement | Upgrade Roosevelt to Curry 115 kV circuit w/795 ACSR | 2007-06-01 | 2010-06-01 | 344362
SPS | GSEC Midway Interconnection #1 | New Delivery Point tapping 69 kV Tie Line from AEPW Shamrock to SPS Magic City | 2007-06-01 | 2007-06-01 | 70000
SPS | Potter - Roosevelt 345KV Displacement | New 345 kV circuit from Potter - Roosevelt 2-795 ACSR & 345/230 kV 560 MVA transformer | 2007-06-01 | 2010-06-01 | 10372158
SPS | ROOSEVELT COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 1 Displacement | Add 2nd transformer 230/115 kV 252 MVA | 2007-06-01 | 2010-06-01 | 858753
SPS | SPS MUST RUN GENERATION #1 | SPS Voltage Instability for Forced Harrington or Tolk Outages due to High Wind Generation Level, Import Level, and Scheduled Harrington Outage in 2007 Spring Peak MUST Run Nichols Generation no less than 300 MW | 2007-04-01 | 2007-04-01 | 0
SPS | SPS MUST RUN GENERATION #2 | SPS Voltage Instability for Tolk to Eddy 345 kV outage due to Scheduled Cunningham Outage and either High Wind Generation Level or Import Level in 2007 Fall Peak MUST Run Cunningham and Maddox Generation in order to not exceed approximately 225 MW of Flow | 2007-10-01 | 2007-10-01 | 0
SPS | SPS MUST RUN GENERATION #3 | SPS Voltage Instability for Tolk to Eddy 345 kV outage due to Scheduled Cunningham Outage and either High Wind Generation Level or Import Level in 2007 Summer Shoulder MUST Run Cunningham and Maddox Generation in order to not exceed approximately 225 MW o | 2007-06-01 | 2007-06-01 | 0
SPS | SPS MUST RUN GENERATION #4 | SPS Voltage Instability for Tolk to Eddy 345 kV outage due to Scheduled Cunningham Outage and either High Wind Generation Level or Import Level in 2007/08 Winter Peak MUST Run Cunningham and Maddox Generation in order to not exceed approximately 225 MW of | 2007-12-01 | 2007-12-01 | 0
SPS | SPS MUST RUN GENERATION #5 | Must Run Requirement of Cunningham #2 and Maddox #1 to prevent Voltage Collapse in 2007 Fall Peak for the DENVER CITY INTERCHANGE S - SHELC23 115KV CKT 1 line outage | 2007-10-01 | 2007-10-01 | 0
WEPL | MEDICINE LODGE - SUN CITY 115KV CKT 1 | Replace relaying from Sun City to Medicine Lodge | 2007-06-01 | 2008-01-01 | 150000
WERE | BOEING - STEARMAN 138KV CKT 1 | Uprate 1.95 mile Boeing-Stearman 138 kV line. | 2012-06-01 | 2012-06-01 | 300000
WERE | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | Rebuild and reconductor 0.34 miles with 1192 ACSR and rebuild substations. | 2009-06-01 | 2009-06-01 | 300000
WERE | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | Rebuild 4.94-mile Summit-Exide Jct 115 kV, 1192.5 ACSR | 2009-06-01 | 2009-06-01 | 2000000
WERE | NORTHVIEW - SUMMIT 115KV CKT 1 | Uprate line to 100oC and replace wave trap | 2009-06-01 | 2009-06-01 | 610000
WERE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER Displacement | Add third 345-138 kV transformer at Rose Hill | 2007-06-01 | 2009-06-01 | 1132688
WERE | ROSEHILL - SOONER 345KV CKT 1 WERE Displacement | New 345 kV line from Oklahoma/Kansas Stateline to Rose Hill | 2011-06-01 | 2011-06-01 | 3677275
WFEC | FRANKLIN SW - MIDWEST TAP 138KV CKT 1 WFEC Displacement | Replace switches and wavetrap at Franklin Switch to 2000A | 2014-06-01 | 2014-06-01 | 100000
WFEC | Hugo - SunnySide 345kV | Add 345 line from Hugo to SunnySide | 2011-06-01 | 2011-06-01 | 50000000
Construction Pending Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Transmission Owner | Upgrade | Solution | Earliest Data Upgrade Required (COD) | Estimated Date of Upgrade Completion (EOC)
AEPW | CHAMBER SPRINGS - TONTITOWN 161KV CKT 1 | Reconductor 666 ACSR (11.6 mies)and 1272 ACSR (.1 mile) to Drake ACCC (2156 ACSR section 0.6 miles is not replaced) and remove the series reactors at Chamber Springs on the Chamber Springs to Tontitown 161 kV line | 2006-12-01 | 2007-06-01
AEPW | Chamber Springs - Tontitown 345 kV | New 345 kV Line and Tontitown 345/161 kV Transformer | 2008-06-01 | 2008-06-01
AEPW | Flint Creek - East Centerton 345 kV | New 345 kV Line and East Centerton 345/161 kV Transformer | 2008-06-01 | 2008-06-01
GRDA | TALLANT - RAMONA 161kV CKT 1 | Tap the Tallant-Ramona(PSO) 69 kV line 10.62 miles from Tallant, 2.01 miles from Ramona. There is a 138/69 kV transformer at South Fork, and then a 9 mile 138 kV line to Skiatook East. | 2007-04-01 | 2008-10-01
KACP | LACYGNE-PAOLA-WEST GARDER 345KV | New 345/161kV transformer and 345kV line tapping LaCyne - West Gardner 345kV | 2007-06-01 | 2008-06-01
MIDW | HEIZER TO KNOLL 230KV | Convert 115 kV to 230kV | 2007-06-01 | 2008-06-01
MIPU | CLINTON - CLINTON GREEN STREET 69KV CKT 1 | Upgrade line to 795 26/7 ACSR conductor | 2016-06-01 | 2011-06-01
MIPU | CLINTON - CLINTON PLANT 69KV CKT 1 | Upgrade line to 795 26/7 ACSR conductor | 2011-06-01 | 2011-06-01
SPS | HOBBS 115 KV Lines | Reroute two lines into New Hobbs Substation (Cunningham to Millen 115 kV line and Cunningham to Russell 115 kV line) | 2007-10-01 | 2008-06-01
SPS | HOBBS 230/115KV TRANSFORMER CKT 2 | Add 2nd 150 MVA transformer at Hobbs | 2007-10-01 | 2008-06-01
SPS | HOBBS Substation and Lines | New 230/115 kV Substation on Lea Co to Midland 230 kV line with reroute of the Maddox to Lea Co 115 kV line | 2007-10-01 | 2008-06-01
SPS | Mustang-San Andr-Amerada Hess 115KV Displacement | Terminate V53 at Mustang instead of Denver City - 3 mi of new 115 kV circuit. Mustang-San Andr-Amerada Hess 115 kV ckt | 2007-04-01 | 2008-06-01
SPS | TUCO INTERCHANGE 230KV #1 | SPS Plan to add 2 50 MVAR Shunt Capacitors at TUCO 230 kV, a 50 MVAR Shunt Capacitor at Swisher 230 kV, a 50 MVAR Shunt Capacitor at Lubbock South 230 kV, and a 50 MVAR Shunt Capacitor at Carlisle 230 kV | 2007-06-01 | 2007-06-01
SPS | TUCO INTERCHANGE 230KV #2 | SPS Plan to Add +150/-50 SVC at TUCO 230 kV | 2008-06-01 | 2008-06-01
SPS | YOAKUM COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 1 Displacement | Upgrade Transformer 230/115 kV 252 MVA | 2007-06-01 | 2008-06-01
SUNC | PHILLIPSBURG - RHOADES | New line between Phillipsburg and Rhoades scheduled to be in service by 6/1/2008 | 2007-06-01 | 2008-10-01
WERE | RENO - SUMMIT 345KV | Install new 50.55-mile 345 kV line from Reno county to Summit; 31 miles of 115 kV line between Circle and S Philips would be rebuilt as double circuit with the 345 kV line to minimize ROW impacts; Substation work required at Summit for new 345 kV terminal | 2011-01-01 | 2011-01-01
WERE | WICHITA - RENO 345KV | Build 345kV from Wichita to Reno Co | 2007-02-01 | 2009-07-01
WFEC | ALTUS JCT TAP - RUSSELL 138KV CKT 1 | WFEC has plans to Increase CT Rating. Project should be inservce by 6/1/2008 | 2015-06-01 | 2008-06-01
Expansion Plan Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Transmission Owner | Upgrade | Solution | Earliest Data Upgrade Required (COD) | Estimated Date of Upgrade Completion (EOC)
AEPW | ALUMAX TAP - NORTHWEST TEXARKANA 138KV CKT 1 | Rebuild 1.68 miles of 1024 ACAR with 2156 ACSR, Replace wavetrap & jumpers with 2156 ACSR. Replace Switch 2285 @ Alumax Tap. | 2008-06-01 | 2008-06-01
AEPW | ARSENAL HILL - NORTH MARKET 69KV CKT 1 | Rebuild 2.3 miles of 666 ACSR with 1272 ACSR | 2011-06-01 | 2011-06-01
AEPW | BANN - LONESTAR ORDINANCE TAP 69KV CKT 1 | Reset relays @ Bann and replace switch @ Lone Star Ordinance Tap. Rebuild 4.14 miles of 397 ACSR with 795 ACSR. | 2011-06-01 | 2011-06-01
AEPW | BIG SANDY - HAWKINS 69KV CKT 1 | Rebuild 5.5 miles of 477 ACSR with 1272 ACSR. | 2016-06-01 | 2016-06-01
AEPW | BIG SANDY - PERDUE 69KV CKT 1 | Rebuild 5.4 miles of 477 ACSR with 1272 ACSR. | 2016-06-01 | 2016-06-01
AEPW | BROKEN BOW - CRAIG JUNCTION 138KV CKT 1 AEPW | Rebuild 7.66 miles of 3/0 CW CU with 795 ACSR | 2007-12-01 | 2009-03-01
AEPW | DAINGERFIELD - JENKINS REC T 69KV CKT 1 | Replace Daingerfield Breaker # 1M90 & reset relays | 2011-06-01 | 2011-06-01
AEPW | DUNCAN (DUNCAN) 138/69/13.8KV TRANSFORMER CKT 1 | Replace Duncan Autotransformer | 2011-06-01 | 2011-06-01
AEPW | ELK CITY - ELK CITY 69KV CKT 1 AEPW | Replace metering CTs & Jumpers and reset relay Cts | 2008-12-01 | 2009-04-01
AEPW | LINWOOD - MCWILLIE STREET 138KV CKT 1 | Rebuild 2.09 miles of 666 ACSR with 1272 ACSR | 2007-06-01 | 2008-01-01
AEPW | PORT ROBSON - REDPOINT 138kV | New 138 kV line from Port Robson - Red Point via McDade & Haughton. Convert McDade & Haughton to 138 kV. | 2011-06-01 | 2011-06-01
AEPW | Siloam Springs - South Fayetteville 161 kV | Convert Existing 69 kV Line to 161 kV Operation | 2014-06-01 | 2014-06-01
AEPW | WALDRON CAPACITOR | Install additional cap bank at Waldron | 2016-06-01 | 2016-06-01
AEPW/WFEC | SNYDER - SNYDER INTERCONNECTION | New Tie line between AEPW's Snyder and WFEC's Snyder | 2016-06-01 | 2016-06-01
GRDA | Kansas 7.2MVAR Cap | Add 7.2MVAr at Kansas area | 2007-06-01 | 2009-06-01
GRDA | SCoffeyville Capacitor | Increase to a 14.4MVAr at South Coffeyville Bus 97001 | 2008-06-01 | 2008-06-01
GRDA | Turkey Ford 7.2MVAR Cap | Install 7.2MVAR capacitors at Turkey Ford 69 kV bus | 2007-06-01 | 2009-06-01
KACP | AVONDALE - GLADSTONE 161KV CKT 1 | Replace 800 amp wavetrap at Gladstone with 1200 amp wavetrap | 2016-06-01 | 2016-06-01
KACP | CROSSTOWN - NEAST 161KV CKT 1 | Add series reactor at Crosstown | 2015-06-01 | 2015-06-01
MIDW | HAYS PLANT - SOUTH HAYS 115KV CKT 1 | Reconductor Line | 2008-06-01 | 2009-06-01
MIDW | HAYS PLANT - VINE STREET 115KV CKT 1 | Reconductor Line | 2008-06-01 | 2009-06-01
MIDW | HEIZER 115/69KV TRANSFORMER CKT 1 | Replace auto | 2016-06-01 | 2016-06-01
MIDW | HEIZER 115/69KV TRANSFORMER CKT 2 | Replace auto | 2016-06-01 | 2016-06-01
MIDW | KINSLEY CAPACITOR | Install 12mvar capacitor at Kinsley | 2007-06-01 | 2009-01-01
MIPU | EAST 40MVAR CAPACITOR | Add 40MVAR capacitor at East 161kV | 2009-01-01 | 2009-01-01
MIPU | INDUSTRIAL PARK - LAKE ROAD 161KV CKT 1 | Structure replacement - Higher line rating | 2007-06-01 | 2008-06-01
MIPU | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | Replace Wavetrap at Martin City | 2006-12-01 | 2010-01-01
MIPU | RALPH GREEN 14.4MVAR CAPACITOR | 14.4MVAR at Ralph Green | 2011-06-01 | 2011-06-01
OKGE | BONANZA - BONANZA TAP 161KV CKT 1 Displacement | Rebuild 0.06 miles of 397 ACSR with 1272 ACSR & reset relay @ Bonanza or Bonanza T-Excelsior-Midland-N. Huntington 161 kV loop | 2015-06-01 | 2015-06-01
OKGE | COLONY - FT SMITH 161KV CKT 1 | Reconductor 2.2 miles to Drake ACCC/TW and change terminal equipment at Ft. Smith & Colony to 2000A. | 2011-06-01 | 2011-06-01
SPS | CARLSBAD PLANT 115/69KV TRANSFORMERS | Upgrade to 75 MVA transformers | 2007-06-01 | 2008-06-01
SPS | Hitchland 345 and 115 kV Interchange | New 345/115 kV Substation on Potter to Finney 345 kV line near the Texas Oklahoma border with tap of Spearman to Texas Co 115 kV line (Three breaker 345 kV bus, 345/115 Kv transformer, five 115 kV breakers) | 2010-06-01 | 2010-06-01
SPS | Mooreland - Potter 345 kV SPS | New 345 kV line from Potter to Mooreland on wooden h-frame structures. | 2016-06-01 | 2016-06-01
SPS | MUSTANG STATION 230/115KV TRANSFORMER CKT 1 | Install 252 MVA Transformer | 2007-04-01 | 2008-06-01
SPS | POTTER COUNTY INTERCHANGE (POTTR CO) 345/230/13.2KV TRANSFORMER CKT 2 | New 345/230 kV 560 MVA transformer | 2016-06-01 | 2016-06-01
SPS | Seven Rivers to Pecos to Potash Junction 230kV | Seven Rivers to Pecos to Potash Junction 230kV | 2007-06-01 | 2008-06-01
SPS | Tex-Hitchland-Sherman Tap 115 kV ckt | Route Sherman Tap to Texas Co in/out of New Hitchland Interchange | 2010-06-01 | 2010-06-01
SPS | TUCO INTERCHANGE 345/115KV TRANSFORMER CKT 1 | Install 345/115 kV Transformer at Tuco | 2016-06-01 | 2016-06-01
SUNC | Spearville - Mooreland 345 kV SUNC | New 345 kV line from Spearville to Kansas/Oklahoma Stateline | 2016-06-01 | 2016-06-01
SWPA | BULL SHOALS - BULL SHOALS 161KV CKT 1 | Replace buswork in Bull Shoals switchyard. | 2010-06-01 | 2010-06-01
WEPL | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 2007-06-01 | 2009-06-01
WEPL | GREENSBURG - JUDSON LARGE 115KV CKT 1 | Replace relaying from Judson Large to Greensgirg | 2006-12-01 | 2007-09-01
WERE | ALTAMONT 138KV | Install 30 Mvar cap at Altamont 138 kV (bus # 57000) | 2011-06-01 | 2011-06-01
WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 2007-06-01 | 2009-06-01
WERE | DEARING (DEARIN1X) 138/69/13.2KV TRANSFORMER CKT 1 | 2nd Dearing 138-69 kV Transformer | 2011-12-01 | 2011-12-01
WERE | Evans - Grant - Chisolm Rebuild and Conversion Project | Build Evans - Grant 138 kV line, Convert Grant - Chisolm 69 kV line to 138 kV, Install New Grant 138/69 kV XFMR. And Rebuild Grant - Grant Jct. 69 kV line. | 2007-06-01 | 2009-06-01
WERE | GILL ENERGY CENTER EAST - GILLJCT269.0 69KV CKT 1 | Rebuild Gill-Gill Jct | 2007-06-01 | 2008-06-01
WERE | GILL ENERGY CENTER EAST - INTERSTATE 138KV CKT 1 | Replace wave trap | 2016-06-01 | 2016-06-01
WERE | GILL ENERGY CENTER EAST - MACARTHUR 69KV CKT 1 | Replace bus, jumpers and disconnect switches at MacArthur 69 kV substation to increase line capacity to conductor rating | 2007-06-01 | 2007-07-01
WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 2009-06-01 | 2009-06-01
WFEC | ANADARKO - CYRIL 69KV CKT 1 | Anadarko-Cyril 336>795 Reconductor 13 miles from 336 to 795 ACSR | 2011-06-01 | 2011-06-01
WFEC | ANADARKO - GEORGIA 138KV CKT 1 | Replace Terminal Equipment | 2011-06-01 | 2011-06-01
WFEC | CYRIL - MEDICINE PARK JCT 69KV CKT 1 | Cyril >MedparkJct 336>795: Reconductor 12.9 miles from 336 to 795 ACSR | 2011-06-01 | 2011-06-01
WFEC | FLETCHER - MEDICINE PARK JCT 69KV CKT 1 | Reconductor 4 miles from 336 to 795 ACSR | 2011-06-01 | 2011-06-01
WFEC | FRANKLIN SW 138/69KV TRANSFORMER CKT 1 | Replace 70 MVA Auto with 112 MVA autotranformer (100 MVA base Rating), Upgrade 138 and 69 KV buswork and switches. | 2011-06-01 | 2011-06-01
WFEC | Mooreland - Potter 345 kV WFEC | 345 kV line Terminal | 2016-06-01 | 2016-06-01
WFEC | Mooreland 345/138 kV Transformer | New Mooreland 345/138 kV Transformer | 2016-06-01 | 2016-06-01
WFEC | Sayre interconnect | Convert Sayre to Sweetwater>Durham>Brantley>MorewoodSw convert to 138 KV | 2011-06-01 | 2011-06-01
WFEC | Spearville - Mooreland 345 kV WFEC | New 345 kV line from Kansas/Oklahoma Stateline to Mooreland | 2016-06-01 | 2016-06-01
Previously Assigned Aggregate Study Upgrades requiring credits to Previous Aggregate Study Customers
Transmission Owner | Upgrade | Solution | Earliest Data Upgrade Required (COD) | Estimated Date of Upgrade Completion (EOC)
AEPW | CACHE - SNYDER 138KV CKT 1 | Replace Snyder wavetrap | 2008-06-01 | 2008-06-01
AEPW | COFFEYVILLE TAP - DEARING 138KV CKT 1 AEPW Displacement | Rebuild 1.09 miles of line using 1590 ACSR | 2011-06-01 | 2011-06-01
AEPW | EXPLORER GLENPOOL - RIVERSIDE STATION 138KV CKT 1 AEPW | Reconductor 1.9 miles with ACCC. Replace wave trap jumpers at Riverside. | 2009-06-01 | 2009-06-01
AEPW | HUGO POWER PLANT - VALLIANT 345 KV AEPW | Vallient 345 KV line terminal | 2010-05-01 | 2010-05-01
AEPW | SOUTHWEST SHREVEPORT (SW SHV 1) 345/138/13.8KV TRANSFORMER CKT 1 | Using IEEE Guide for Loading of Mineral-Oil Immersed Power Transformers (C57.91-2000) Re-rate the autos. Replace .two 138 kV breakers and five 138 kV switches. Reset relays and CTs | 2010-06-01 | 2010-06-01
AEPW | SOUTHWEST SHREVEPORT (SW SHV 2) 345/138/13.8KV TRANSFORMER CKT 2 | Using IEEE Guide for Loading of Mineral-Oil Immersed Power Transformers (C57.91-2000) Re-rate the autos. Replace .two 138 kV breakers and five 138 kV switches. Reset relays and CTs | 2010-06-01 | 2010-06-01
KACP | IATAN - NASHUA 345KV CKT 1 | New Iatan-Nashua line (27.5 mi.) and Nashua substation work and 345/161kV transformer | 2010-06-01 | 2010-06-01
KACP | LACYGNE - WEST GARDNER 345KV CKT 1 | KCPL Sponsored Project to Reconductor Line to be In-Service by 6/1/2006 | 2006-06-01 | 2006-06-01
OKGE | ARCADIA - REDBUD 345 KV CKT 1 | Sponsored Project to Uprate Terninal Equipment | 2006-06-01 | 2006-06-01
OKGE | ARCADIA - REDBUD 345 KV CKT 2 | Sponsored Project to Uprate Terninal Equipment | 2006-06-01 | 2006-06-01
OKGE | BEELINE - EXPLORER GLENPOOL 138KV CKT 1 | Reconductor .92miles of line with Drake ACCC/TW. | 2009-06-01 | 2009-06-01
OKGE | BROWN - EXPLORER TAP 138KV CKT 1 | Upgrade CT to 800A at Brown. | 2008-06-01 | 2008-06-01
OKGE | EXPLORER GLENPOOL - RIVERSIDE STATION 138KV CKT 1 OKGE | Reconductor 1.82 miles line with Drake ACCC/TW. | 2009-06-01 | 2009-06-01
OKGE | FPL SWITCH - MOORELAND 138KV CKT 1 OKGE | OGE would rebuild .18 miles of 267AS33 with 795AS33. This would raise OGE's summer and winter Rate B to 287MVA. The limit will still be at WFEC's Mooreland at 390A & 600A. | 2006-06-01 | 2008-04-01
WERE | COFFEYVILLE TAP - DEARING 138KV CKT 1 WERE Displacement | Tie Line, Rebuild 3.93 miles of 795 ACSR with 1590 ACSR. | 2011-06-01 | 2011-06-01
WERE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 Displacement | Add third 345-138 kV transformer at Rose Hill | 2011-06-01 | 2011-06-01
WFEC | ANADARKO 138/69KV TRANSFORMER CKT 1 | Install 2nd 112 MVA auto in parallel with existing Unit | 2011-06-01 | 2011-06-01
WFEC | FPL SWITCH - MOORELAND 138KV CKT 1 WFEC | Upgrade terminal equipment FPL Sw & Mooreland | 2006-06-01 | 2008-04-01
WFEC | HUGO POWER PLANT - VALLIANT 345 KV WFEC | New 345/138 kv Auto, and 19 miles 345 KV | 2010-05-01 | 2010-05-01

## Table 5
Transmission Owner | Upgrade | Solution | Earliest Date Upgrade Required (COD) | Estimated Date of Upgrade Completion (EOC) | Estimated Engineering & Construction Cost
SWPA | JONES - JONESBORO 161KV CKT 1 SWPA | Change the ratio on the metering CTs to 1200/5 and adjust the meters | 2007-06-01 | 2008-02-01 | 2000
CELE | BAYOU RAPIDES - TWIN BRIDGES 138KV CKT 1 | Reconductor Bayou Rapides to Twin Bridges 138 kV | 2011-06-01 | 2011-06-01 | 1230000
CELE | COCODRIE 230/138KV TRANSFORMER CKT 1 | Replace Cocodrie 230/138 kV Auto XFMR | 2011-12-01 | 2011-12-01 | 6000000
CELE | Natchitoches Capacitor | Install 28.8 MVAr capacitor bank at Natchitoches Bus 50131 | 2011-06-01 | 2011-06-01 | 622080
ENTR | 5FLIPN - BULL SHOALS HES 161KV CKT 1 |  | 2011-06-01 | 2011-06-01 | Indeterminate
ENTR | 5HILLTOP 161 - 5ST_JOE 161 161KV CKT 1 |  | 2011-06-01 | 2011-06-01 | Indeterminate
ENTR | 5ST_JOE 161 - EVERTON 161KV CKT 1 |  | 2011-06-01 | 2011-06-01 | Indeterminate
ENTR | 5TRUMAN - HARISBURG TAP 161KV CKT 1 |  | 2011-06-01 | 2011-06-01 | Indeterminate
ENTR | ARKANSAS NUCLEAR ONE 161 - RUSSELLVILLE NORTH 161KV CKT 1 |  | 2007-06-01 | 2007-06-01 | Indeterminate
ENTR | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 ENTR |  | 2011-06-01 | 2011-06-01 | Indeterminate
ENTR | EVERTON - HARRISON-EAST 161KV CKT 1 |  | 2011-06-01 | 2011-06-01 | Indeterminate
ENTR | HARRISON-EAST - SUMMIT 161KV CKT 1 |  | 2016-06-01 | 2016-06-01 | Indeterminate
ENTR | JONES - JONESBORO 161KV CKT 1 ENTR |  | 2007-06-01 | 2007-06-01 | Indeterminate
ENTR | JONESBORO - JONESBORO NORTH (AECC) 161KV CKT 1 |  | 2011-06-01 | 2011-06-01 | Indeterminate
ENTR | JONESBORO NORTH (AECC) - PARAGOULD SOUTH (AECC) 161KV CKT 1 |  | 2011-06-01 | 2011-06-01 | Indeterminate
ENTR | RUSSELLVILLE EAST - RUSSELLVILLE NORTH 161KV CKT 1 |  | 2011-06-01 | 2011-06-01 | Indeterminate
GSEC | GSEC Midway Interconnection #2 | Install 7.2 MVAR Capacitor at GSEC Midway 69 kV | 2011-06-01 | 2011-06-01 | 200000
RAYBURN | BEN WHEELER - BARTONS CHAPEL | Diana - Bartons Chapel & Ben Wheeler - Bartons Chapel | 2016-06-01 | 2016-06-01 | Indeterminate
SWPA | BEAVER - EUREKA SPRINGS 161KV CKT 1 SWPA | Reconductor 6 miles of 795 ACSR with 1590 ACSR. Reconnect CT's to 1000:5 Tap on Bkrs 42, 32, & half or 22. Replace metering & reset relays for Line 2 & Line 3. Conduct Environmental Impact Study. | 2013-06-01 | 2013-06-01 | 2400000
SWPA | JONES - JONESBORO 161KV CKT 1 SWPA | Change the ratio on the metering CTs to 1200/5 and adjust the meters | 2007-06-01 | 2008-06-01 | 2000

## Table6
Upgrade: | 5 TRIBES - HANCOCK 161KV CKT 1 Displacement, 5 TRIBES - PECAN CREEK 161KV CKT 1 Displacement, PECAN CREEK (PECANCK1) 345/161/13.8KV TRANSFORMER CKT 1 Displacement
Limiting Facility: | PECAN CREEK (PECANCK1) 345/161/13.8KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | FT SMITH - MUSKOGEE 345KV CKT 1
Flowgate: | PECCANCK12751553025522413107SP
Date Redispatch Needed: | 6/1/07 - 10/1/07
Season Flowgate Identified: | 2007 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1161665 | 0.60444 | 8.0286
1162654 | 0.5091 | 8.0286
1162763 | 3.6432 | 8.0286
1162766 | 3.2718 | 8.0286
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
OKGE | 'MUSKOGEE 161KV' | 166 | -0.29781 | OKGE | 'MUSKOGEE 345KV' | 1516 | 0.14393 | -0.44174 | 18
OKGE | 'MUSKOGEE 161KV' | 31 | -0.29781 | OKGE | 'MUSKOGEE 345KV' | 1516 | 0.14393 | -0.44174 | 18
OKGE | 'MUSKOGEE 161KV' | 166 | -0.29781 | OKGE | 'FPLWND2 34KV' | 102 | 0.03611 | -0.33392 | 24
OKGE | 'MUSKOGEE 161KV' | 31 | -0.29781 | OKGE | 'FPLWND2 34KV' | 102 | 0.03611 | -0.33392 | 24
OKGE | 'MUSKOGEE 161KV' | 166 | -0.29781 | OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.03326 | -0.33107 | 24
OKGE | 'MUSKOGEE 161KV' | 166 | -0.29781 | OKGE | 'HORSESHOE LAKE 138KV' | 111.835 | 0.03326 | -0.33107 | 24
OKGE | 'MUSKOGEE 161KV' | 166 | -0.29781 | OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.03326 | -0.33107 | 24
OKGE | 'MUSKOGEE 161KV' | 31 | -0.29781 | OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.03326 | -0.33107 | 24
OKGE | 'MUSKOGEE 161KV' | 31 | -0.29781 | OKGE | 'HORSESHOE LAKE 138KV' | 111.835 | 0.03326 | -0.33107 | 24
OKGE | 'MUSKOGEE 161KV' | 31 | -0.29781 | OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.03326 | -0.33107 | 24
OKGE | 'MUSKOGEE 161KV' | 166 | -0.29781 | OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.03033 | -0.32814 | 24
OKGE | 'MUSKOGEE 161KV' | 31 | -0.29781 | OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.03033 | -0.32814 | 24
OKGE | 'MUSKOGEE 161KV' | 166 | -0.29781 | OKGE | 'MCCLAIN 138KV' | 478 | 0.03728 | -0.33509 | 24
OKGE | 'MUSKOGEE 161KV' | 31 | -0.29781 | OKGE | 'MCCLAIN 138KV' | 478 | 0.03728 | -0.33509 | 24
OKGE | 'MUSKOGEE 161KV' | 166 | -0.29781 | OKGE | 'MUSTANG 138KV' | 365.5 | 0.03707 | -0.33488 | 24
OKGE | 'MUSKOGEE 161KV' | 31 | -0.29781 | OKGE | 'MUSTANG 138KV' | 365.5 | 0.03707 | -0.33488 | 24
OKGE | 'MUSKOGEE 161KV' | 166 | -0.29781 | OKGE | 'MUSTANG 69KV' | 106 | 0.03687 | -0.33468 | 24
OKGE | 'MUSKOGEE 161KV' | 31 | -0.29781 | OKGE | 'MUSTANG 69KV' | 106 | 0.03687 | -0.33468 | 24
OKGE | 'MUSKOGEE 161KV' | 166 | -0.29781 | OKGE | 'OMPA-KINGFISHER BOWMAN 69KV' | 19.7 | 0.03652 | -0.33433 | 24
OKGE | 'MUSKOGEE 161KV' | 31 | -0.29781 | OKGE | 'OMPA-KINGFISHER BOWMAN 69KV' | 19.7 | 0.03652 | -0.33433 | 24
OKGE | 'MUSKOGEE 161KV' | 166 | -0.29781 | OKGE | 'OMPA-PONCA CITY 69KV' | 76.3593 | 0.03382 | -0.33163 | 24
OKGE | 'MUSKOGEE 161KV' | 31 | -0.29781 | OKGE | 'OMPA-PONCA CITY 69KV' | 76.3593 | 0.03382 | -0.33163 | 24
OKGE | 'MUSKOGEE 161KV' | 166 | -0.29781 | OKGE | 'ONE OAK 345KV' | 132 | 0.03901 | -0.33682 | 24
OKGE | 'MUSKOGEE 161KV' | 31 | -0.29781 | OKGE | 'ONE OAK 345KV' | 132 | 0.03901 | -0.33682 | 24
OKGE | 'MUSKOGEE 161KV' | 166 | -0.29781 | OKGE | 'REDBUD 345KV' | 250 | 0.04319 | -0.341 | 24
OKGE | 'MUSKOGEE 161KV' | 31 | -0.29781 | OKGE | 'REDBUD 345KV' | 250 | 0.04319 | -0.341 | 24
OKGE | 'MUSKOGEE 161KV' | 166 | -0.29781 | OKGE | 'SEMINOLE 138KV' | 476.3899 | 0.03935 | -0.33716 | 24
OKGE | 'MUSKOGEE 161KV' | 31 | -0.29781 | OKGE | 'SEMINOLE 138KV' | 476.3899 | 0.03935 | -0.33716 | 24
OKGE | 'MUSKOGEE 161KV' | 166 | -0.29781 | OKGE | 'SEMINOLE 345KV' | 996 | 0.04283 | -0.34064 | 24
OKGE | 'MUSKOGEE 161KV' | 31 | -0.29781 | OKGE | 'SEMINOLE 345KV' | 996 | 0.04283 | -0.34064 | 24
OKGE | 'MUSKOGEE 161KV' | 166 | -0.29781 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.03617 | -0.33398 | 24
OKGE | 'MUSKOGEE 161KV' | 31 | -0.29781 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.03617 | -0.33398 | 24
OKGE | 'MUSKOGEE 161KV' | 166 | -0.29781 | OKGE | 'SMITH COGEN 138KV' | 120 | 0.03697 | -0.33478 | 24
OKGE | 'MUSKOGEE 161KV' | 31 | -0.29781 | OKGE | 'SMITH COGEN 138KV' | 120 | 0.03697 | -0.33478 | 24
OKGE | 'MUSKOGEE 161KV' | 166 | -0.29781 | OKGE | 'SOONER 138KV' | 505 | 0.03471 | -0.33252 | 24
OKGE | 'MUSKOGEE 161KV' | 31 | -0.29781 | OKGE | 'SOONER 138KV' | 505 | 0.03471 | -0.33252 | 24
OKGE | 'MUSKOGEE 161KV' | 166 | -0.29781 | OKGE | 'SOONER 345KV' | 513 | 0.03624 | -0.33405 | 24
OKGE | 'MUSKOGEE 161KV' | 31 | -0.29781 | OKGE | 'SOONER 345KV' | 513 | 0.03624 | -0.33405 | 24
OKGE | 'MUSKOGEE 161KV' | 166 | -0.29781 | OKGE | 'AES 161KV' | 320 | -0.06234 | -0.23547 | 34
OKGE | 'MUSKOGEE 161KV' | 31 | -0.29781 | OKGE | 'AES 161KV' | 320 | -0.06234 | -0.23547 | 34
OKGE | 'SHADY2 345 69KV' | 600 | -0.05853 | OKGE | 'MUSKOGEE 345KV' | 1516 | 0.14393 | -0.20246 | 40
SWPA | 'TENKILLER FERRY 161KV' | 26 | -0.14959 | SWPA | 'KEYSTONE DAM 161KV' | 59.4 | 0.04152 | -0.19111 | 42
SWPA | 'WEBBERS FALLS 161KV' | 30 | -0.14959 | SWPA | 'KEYSTONE DAM 161KV' | 59.4 | 0.04152 | -0.19111 | 42
SWPA | 'TENKILLER FERRY 161KV' | 26 | -0.14959 | SWPA | 'DENISON 138KV' | 59.4 | 0.03206 | -0.18165 | 44
SWPA | 'WEBBERS FALLS 161KV' | 30 | -0.14959 | SWPA | 'DENISON 138KV' | 59.4 | 0.03206 | -0.18165 | 44
SWPA | 'TENKILLER FERRY 161KV' | 26 | -0.14959 | SWPA | 'BROKEN BOW 138KV' | 93.4 | 0.02151 | -0.1711 | 47
SWPA | 'WEBBERS FALLS 161KV' | 30 | -0.14959 | SWPA | 'BROKEN BOW 138KV' | 93.4 | 0.02151 | -0.1711 | 47
SWPA | 'TENKILLER FERRY 161KV' | 26 | -0.14959 | SWPA | 'BEAVER 161KV' | 100.7001 | 0.01932 | -0.16891 | 48
SWPA | 'TENKILLER FERRY 161KV' | 26 | -0.14959 | SWPA | 'CARTHAGE 69KV' | 30 | 0.0182 | -0.16779 | 48
SWPA | 'TENKILLER FERRY 161KV' | 26 | -0.14959 | SWPA | 'STOCKTON 161KV' | 44.1 | 0.01713 | -0.16672 | 48
SWPA | 'WEBBERS FALLS 161KV' | 30 | -0.14959 | SWPA | 'BEAVER 161KV' | 100.7001 | 0.01932 | -0.16891 | 48
SWPA | 'WEBBERS FALLS 161KV' | 30 | -0.14959 | SWPA | 'CARTHAGE 69KV' | 30 | 0.0182 | -0.16779 | 48
SWPA | 'WEBBERS FALLS 161KV' | 30 | -0.14959 | SWPA | 'STOCKTON 161KV' | 44.1 | 0.01713 | -0.16672 | 48
SWPA | 'TENKILLER FERRY 161KV' | 26 | -0.14959 | SWPA | 'JAMES RIVER 161KV' | 159 | 0.01587 | -0.16546 | 49
SWPA | 'TENKILLER FERRY 161KV' | 26 | -0.14959 | SWPA | 'JAMES RIVER 69KV' | 233.8672 | 0.01587 | -0.16546 | 49
SWPA | 'TENKILLER FERRY 161KV' | 26 | -0.14959 | SWPA | 'MCCARTNEY 161KV' | 322.3152 | 0.01551 | -0.1651 | 49
SWPA | 'TENKILLER FERRY 161KV' | 26 | -0.14959 | SWPA | 'TABLE ROCK 161KV' | 186.8 | 0.01339 | -0.16298 | 49
SWPA | 'TENKILLER FERRY 161KV' | 26 | -0.14959 | SWPA | 'TRUMAN 161KV' | 102 | 0.01573 | -0.16532 | 49
SWPA | 'WEBBERS FALLS 161KV' | 30 | -0.14959 | SWPA | 'JAMES RIVER 161KV' | 159 | 0.01587 | -0.16546 | 49
SWPA | 'WEBBERS FALLS 161KV' | 30 | -0.14959 | SWPA | 'JAMES RIVER 69KV' | 233.8672 | 0.01587 | -0.16546 | 49
SWPA | 'WEBBERS FALLS 161KV' | 30 | -0.14959 | SWPA | 'MCCARTNEY 161KV' | 322.3152 | 0.01551 | -0.1651 | 49
SWPA | 'WEBBERS FALLS 161KV' | 30 | -0.14959 | SWPA | 'TABLE ROCK 161KV' | 186.8 | 0.01339 | -0.16298 | 49
SWPA | 'WEBBERS FALLS 161KV' | 30 | -0.14959 | SWPA | 'TRUMAN 161KV' | 102 | 0.01573 | -0.16532 | 49
SWPA | 'TENKILLER FERRY 161KV' | 26 | -0.14959 | SWPA | 'CLARENCE CANNON DAM 69KV' | 39.2 | 0.01136 | -0.16095 | 50
SWPA | 'WEBBERS FALLS 161KV' | 30 | -0.14959 | SWPA | 'CLARENCE CANNON DAM 69KV' | 39.2 | 0.01136 | -0.16095 | 50
SWPA | 'TENKILLER FERRY 161KV' | 26 | -0.14959 | SWPA | 'BULL SHOALS 161KV' | 293.2 | 0.00487 | -0.15446 | 52
SWPA | 'WEBBERS FALLS 161KV' | 30 | -0.14959 | SWPA | 'BULL SHOALS 161KV' | 293.2 | 0.00487 | -0.15446 | 52
SWPA | 'TENKILLER FERRY 161KV' | 26 | -0.14959 | SWPA | 'NORFORK 161KV' | 20 | 0.00313 | -0.15272 | 53
SWPA | 'TENKILLER FERRY 161KV' | 26 | -0.14959 | SWPA | 'SIKESTON 161KV' | 235 | 0.00178 | -0.15137 | 53
SWPA | 'WEBBERS FALLS 161KV' | 30 | -0.14959 | SWPA | 'NORFORK 161KV' | 20 | 0.00313 | -0.15272 | 53
SWPA | 'WEBBERS FALLS 161KV' | 30 | -0.14959 | SWPA | 'SIKESTON 161KV' | 235 | 0.00178 | -0.15137 | 53
SWPA | 'TENKILLER FERRY 161KV' | 26 | -0.14959 | SWPA | 'JONESBORO 161KV' | 43 | -0.00246 | -0.14713 | 55
SWPA | 'WEBBERS FALLS 161KV' | 30 | -0.14959 | SWPA | 'JONESBORO 161KV' | 43 | -0.00246 | -0.14713 | 55
SWPA | 'TENKILLER FERRY 161KV' | 26 | -0.14959 | SWPA | 'GREERS FERRY 161KV' | 93.4 | -0.01034 | -0.13925 | 58
SWPA | 'WEBBERS FALLS 161KV' | 30 | -0.14959 | SWPA | 'GREERS FERRY 161KV' | 93.4 | -0.01034 | -0.13925 | 58
AEPW | 'FITZHUGH 161KV' | 95 | -0.05708 | AEPW | 'OEC 345KV' | 506 | 0.07008 | -0.12716 | 63
AEPW | 'FITZHUGH 161KV' | 95 | -0.05708 | AEPW | 'COGENTRIX 345KV' | 765 | 0.06587 | -0.12295 | 65
SWPA | 'TENKILLER FERRY 161KV' | 26 | -0.14959 | SWPA | 'DARDANELLE 161KV' | 105.2 | -0.02727 | -0.12232 | 66
SWPA | 'WEBBERS FALLS 161KV' | 30 | -0.14959 | SWPA | 'DARDANELLE 161KV' | 105.2 | -0.02727 | -0.12232 | 66
OKGE | 'HORSESHOE LAKE 138KV' | 268.665 | 0.03326 | OKGE | 'MUSKOGEE 345KV' | 1516 | 0.14393 | -0.11067 | 73
OKGE | 'OMPA-PONCA CITY 69KV' | 80.2407 | 0.03382 | OKGE | 'MUSKOGEE 345KV' | 1516 | 0.14393 | -0.11011 | 73
AEPW | 'FITZHUGH 161KV' | 95 | -0.05708 | AEPW | 'RIVERSIDE STATION 138KV' | 646 | 0.05171 | -0.10879 | 74
OKGE | 'SOONER 138KV' | 25 | 0.03471 | OKGE | 'MUSKOGEE 345KV' | 1516 | 0.14393 | -0.10922 | 74
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | 0.03536 | OKGE | 'MUSKOGEE 345KV' | 1516 | 0.14393 | -0.10857 | 74
AEPW | 'FITZHUGH 161KV' | 95 | -0.05708 | AEPW | 'TULSA POWER STATION 138KV' | 112 | 0.04943 | -0.10651 | 75
AEPW | 'FITZHUGH 161KV' | 95 | -0.05708 | AEPW | 'TULSA POWER STATION 138KV' | 147 | 0.04943 | -0.10651 | 75
OKGE | 'MCCLAIN 138KV' | 42 | 0.03728 | OKGE | 'MUSKOGEE 345KV' | 1516 | 0.14393 | -0.10665 | 75
OKGE | 'SOONER 7 345 345KV' | 1050 | 0.03624 | OKGE | 'MUSKOGEE 345KV' | 1516 | 0.14393 | -0.10769 | 75
OKGE | 'TINKER 5G 138KV' | 62 | 0.03663 | OKGE | 'MUSKOGEE 345KV' | 1516 | 0.14393 | -0.1073 | 75
AEPW | 'FITZHUGH 161KV' | 95 | -0.05708 | AEPW | 'NORTHEASTERN STATION 345KV' | 645 | 0.04737 | -0.10445 | 77
OKGE | 'ONE OAK 345KV' | 204 | 0.03901 | OKGE | 'MUSKOGEE 345KV' | 1516 | 0.14393 | -0.10492 | 77
OKGE | 'SEMINOLE 138KV' | 28.6101 | 0.03935 | OKGE | 'MUSKOGEE 345KV' | 1516 | 0.14393 | -0.10458 | 77
OKGE | 'SHADY2 345 69KV' | 600 | -0.05853 | OKGE | 'REDBUD 345KV' | 250 | 0.04319 | -0.10172 | 79
OKGE | 'SHADY2 345 69KV' | 600 | -0.05853 | OKGE | 'SEMINOLE 345KV' | 996 | 0.04283 | -0.10136 | 79
OKGE | 'REDBUD 345KV' | 650 | 0.04319 | OKGE | 'MUSKOGEE 345KV' | 1516 | 0.14393 | -0.10074 | 80
OKGE | 'REDBUD 345KV' | 300 | 0.04319 | OKGE | 'MUSKOGEE 345KV' | 1516 | 0.14393 | -0.10074 | 80
SWPA | 'OZARK 161KV' | 37 | -0.05701 | SWPA | 'KEYSTONE DAM 161KV' | 59.4 | 0.04152 | -0.09853 | 81
OKGE | 'SHADY2 345 69KV' | 600 | -0.05853 | OKGE | 'ONE OAK 345KV' | 132 | 0.03901 | -0.09754 | 82
OKGE | 'SHADY2 345 69KV' | 600 | -0.05853 | OKGE | 'SEMINOLE 138KV' | 476.3899 | 0.03935 | -0.09788 | 82
AEPW | 'FITZHUGH 161KV' | 95 | -0.05708 | AEPW | 'COMANCHE 138KV' | 160 | 0.03989 | -0.09697 | 83
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | 5 TRIBES - HANCOCK 161KV CKT 1 Displacement, 5 TRIBES - PECAN CREEK 161KV CKT 1 Displacement, PECAN CREEK (PECANCK1) 345/161/13.8KV TRANSFORMER CKT 1 Displacement
Limiting Facility: | PECAN CREEK (PECANCK1) 345/161/13.8KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | FT SMITH - MUSKOGEE 345KV CKT 1
Flowgate: | PECCANCK12751553025522413108SP
Date Redispatch Needed: | Starting 2008 6/1 - 10/1 Until EOC of Upgrade
Season Flowgate Identified: | 2008 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1161665 | 0.677 | 8.7685
1162654 | 0.55248 | 8.7685
1162763 | 3.982 | 8.7685
1162766 | 3.557 | 8.7685
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
OKGE | 'MUSKOGEE 161KV' | 166 | -0.29784 | OKGE | 'MUSKOGEE 345KV' | 1516 | 0.1439 | -0.44174 | 20
OKGE | 'MUSKOGEE 161KV' | 31 | -0.29784 | OKGE | 'MUSKOGEE 345KV' | 1516 | 0.1439 | -0.44174 | 20
OKGE | 'MUSKOGEE 161KV' | 166 | -0.29784 | OKGE | 'FPLWND2 34KV' | 102 | 0.03613 | -0.33397 | 26
OKGE | 'MUSKOGEE 161KV' | 31 | -0.29784 | OKGE | 'FPLWND2 34KV' | 102 | 0.03613 | -0.33397 | 26
OKGE | 'MUSKOGEE 161KV' | 166 | -0.29784 | OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.03324 | -0.33108 | 26
OKGE | 'MUSKOGEE 161KV' | 166 | -0.29784 | OKGE | 'HORSESHOE LAKE 138KV' | 212.7954 | 0.03324 | -0.33108 | 26
OKGE | 'MUSKOGEE 161KV' | 166 | -0.29784 | OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.03324 | -0.33108 | 26
OKGE | 'MUSKOGEE 161KV' | 31 | -0.29784 | OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.03324 | -0.33108 | 26
OKGE | 'MUSKOGEE 161KV' | 31 | -0.29784 | OKGE | 'HORSESHOE LAKE 138KV' | 212.7954 | 0.03324 | -0.33108 | 26
OKGE | 'MUSKOGEE 161KV' | 31 | -0.29784 | OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.03324 | -0.33108 | 26
OKGE | 'MUSKOGEE 161KV' | 166 | -0.29784 | OKGE | 'MCCLAIN 138KV' | 478 | 0.03713 | -0.33497 | 26
OKGE | 'MUSKOGEE 161KV' | 31 | -0.29784 | OKGE | 'MCCLAIN 138KV' | 478 | 0.03713 | -0.33497 | 26
OKGE | 'MUSKOGEE 161KV' | 166 | -0.29784 | OKGE | 'MUSTANG 138KV' | 365.5 | 0.03706 | -0.3349 | 26
OKGE | 'MUSKOGEE 161KV' | 31 | -0.29784 | OKGE | 'MUSTANG 138KV' | 365.5 | 0.03706 | -0.3349 | 26
OKGE | 'MUSKOGEE 161KV' | 166 | -0.29784 | OKGE | 'MUSTANG 69KV' | 106 | 0.03687 | -0.33471 | 26
OKGE | 'MUSKOGEE 161KV' | 31 | -0.29784 | OKGE | 'MUSTANG 69KV' | 106 | 0.03687 | -0.33471 | 26
OKGE | 'MUSKOGEE 161KV' | 166 | -0.29784 | OKGE | 'OMPA-KINGFISHER BOWMAN 69KV' | 19.7 | 0.03651 | -0.33435 | 26
OKGE | 'MUSKOGEE 161KV' | 31 | -0.29784 | OKGE | 'OMPA-KINGFISHER BOWMAN 69KV' | 19.7 | 0.03651 | -0.33435 | 26
OKGE | 'MUSKOGEE 161KV' | 166 | -0.29784 | OKGE | 'OMPA-PONCA CITY 69KV' | 78.0781 | 0.03381 | -0.33165 | 26
OKGE | 'MUSKOGEE 161KV' | 31 | -0.29784 | OKGE | 'OMPA-PONCA CITY 69KV' | 78.0781 | 0.03381 | -0.33165 | 26
OKGE | 'MUSKOGEE 161KV' | 166 | -0.29784 | OKGE | 'ONE OAK 345KV' | 136 | 0.03899 | -0.33683 | 26
OKGE | 'MUSKOGEE 161KV' | 31 | -0.29784 | OKGE | 'ONE OAK 345KV' | 136 | 0.03899 | -0.33683 | 26
OKGE | 'MUSKOGEE 161KV' | 166 | -0.29784 | OKGE | 'REDBUD 345KV' | 250 | 0.04317 | -0.34101 | 26
OKGE | 'MUSKOGEE 161KV' | 31 | -0.29784 | OKGE | 'REDBUD 345KV' | 250 | 0.04317 | -0.34101 | 26
OKGE | 'MUSKOGEE 161KV' | 166 | -0.29784 | OKGE | 'SEMINOLE 138KV' | 476.6378 | 0.03933 | -0.33717 | 26
OKGE | 'MUSKOGEE 161KV' | 31 | -0.29784 | OKGE | 'SEMINOLE 138KV' | 476.6378 | 0.03933 | -0.33717 | 26
OKGE | 'MUSKOGEE 161KV' | 166 | -0.29784 | OKGE | 'SEMINOLE 345KV' | 996 | 0.0428 | -0.34064 | 26
OKGE | 'MUSKOGEE 161KV' | 31 | -0.29784 | OKGE | 'SEMINOLE 345KV' | 996 | 0.0428 | -0.34064 | 26
OKGE | 'MUSKOGEE 161KV' | 166 | -0.29784 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.03619 | -0.33403 | 26
OKGE | 'MUSKOGEE 161KV' | 31 | -0.29784 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.03619 | -0.33403 | 26
OKGE | 'MUSKOGEE 161KV' | 166 | -0.29784 | OKGE | 'SMITH COGEN 138KV' | 120 | 0.03698 | -0.33482 | 26
OKGE | 'MUSKOGEE 161KV' | 31 | -0.29784 | OKGE | 'SMITH COGEN 138KV' | 120 | 0.03698 | -0.33482 | 26
OKGE | 'MUSKOGEE 161KV' | 166 | -0.29784 | OKGE | 'SOONER 138KV' | 505 | 0.03469 | -0.33253 | 26
OKGE | 'MUSKOGEE 161KV' | 31 | -0.29784 | OKGE | 'SOONER 138KV' | 505 | 0.03469 | -0.33253 | 26
OKGE | 'MUSKOGEE 161KV' | 166 | -0.29784 | OKGE | 'SOONER 345KV' | 513 | 0.03623 | -0.33407 | 26
OKGE | 'MUSKOGEE 161KV' | 31 | -0.29784 | OKGE | 'SOONER 345KV' | 513 | 0.03623 | -0.33407 | 26
OKGE | 'MUSKOGEE 161KV' | 166 | -0.29784 | OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.03031 | -0.32815 | 27
OKGE | 'MUSKOGEE 161KV' | 31 | -0.29784 | OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.03031 | -0.32815 | 27
OKGE | 'MUSKOGEE 161KV' | 166 | -0.29784 | OKGE | 'AES 161KV' | 320 | -0.06239 | -0.23545 | 37
OKGE | 'MUSKOGEE 161KV' | 31 | -0.29784 | OKGE | 'AES 161KV' | 320 | -0.06239 | -0.23545 | 37
OKGE | 'SHADY2 345 69KV' | 600 | -0.05857 | OKGE | 'MUSKOGEE 345KV' | 1516 | 0.1439 | -0.20247 | 43
SWPA | 'TENKILLER FERRY 161KV' | 26 | -0.14963 | SWPA | 'KEYSTONE DAM 161KV' | 59.6 | 0.0415 | -0.19113 | 46
SWPA | 'WEBBERS FALLS 161KV' | 29.8 | -0.14963 | SWPA | 'KEYSTONE DAM 161KV' | 59.6 | 0.0415 | -0.19113 | 46
SWPA | 'TENKILLER FERRY 161KV' | 26 | -0.14963 | SWPA | 'DENISON 138KV' | 59.6 | 0.03204 | -0.18167 | 48
SWPA | 'WEBBERS FALLS 161KV' | 29.8 | -0.14963 | SWPA | 'DENISON 138KV' | 59.6 | 0.03204 | -0.18167 | 48
SWPA | 'TENKILLER FERRY 161KV' | 26 | -0.14963 | SWPA | 'BROKEN BOW 138KV' | 93.6 | 0.02149 | -0.17112 | 51
SWPA | 'WEBBERS FALLS 161KV' | 29.8 | -0.14963 | SWPA | 'BROKEN BOW 138KV' | 93.6 | 0.02149 | -0.17112 | 51
SWPA | 'TENKILLER FERRY 161KV' | 26 | -0.14963 | SWPA | 'BEAVER 161KV' | 104.1233 | 0.01954 | -0.16917 | 52
SWPA | 'TENKILLER FERRY 161KV' | 26 | -0.14963 | SWPA | 'CARTHAGE 69KV' | 32 | 0.01828 | -0.16791 | 52
SWPA | 'WEBBERS FALLS 161KV' | 29.8 | -0.14963 | SWPA | 'BEAVER 161KV' | 104.1233 | 0.01954 | -0.16917 | 52
SWPA | 'WEBBERS FALLS 161KV' | 29.8 | -0.14963 | SWPA | 'CARTHAGE 69KV' | 32 | 0.01828 | -0.16791 | 52
SWPA | 'TENKILLER FERRY 161KV' | 26 | -0.14963 | SWPA | 'JAMES RIVER 161KV' | 159 | 0.01593 | -0.16556 | 53
SWPA | 'TENKILLER FERRY 161KV' | 26 | -0.14963 | SWPA | 'JAMES RIVER 69KV' | 233.6668 | 0.01592 | -0.16555 | 53
SWPA | 'TENKILLER FERRY 161KV' | 26 | -0.14963 | SWPA | 'MCCARTNEY 161KV' | 342.4351 | 0.01557 | -0.1652 | 53
SWPA | 'TENKILLER FERRY 161KV' | 26 | -0.14963 | SWPA | 'STOCKTON 161KV' | 44.3 | 0.01717 | -0.1668 | 53
SWPA | 'TENKILLER FERRY 161KV' | 26 | -0.14963 | SWPA | 'TRUMAN 161KV' | 102 | 0.01575 | -0.16538 | 53
SWPA | 'WEBBERS FALLS 161KV' | 29.8 | -0.14963 | SWPA | 'JAMES RIVER 161KV' | 159 | 0.01593 | -0.16556 | 53
SWPA | 'WEBBERS FALLS 161KV' | 29.8 | -0.14963 | SWPA | 'JAMES RIVER 69KV' | 233.6668 | 0.01592 | -0.16555 | 53
SWPA | 'WEBBERS FALLS 161KV' | 29.8 | -0.14963 | SWPA | 'MCCARTNEY 161KV' | 342.4351 | 0.01557 | -0.1652 | 53
SWPA | 'WEBBERS FALLS 161KV' | 29.8 | -0.14963 | SWPA | 'STOCKTON 161KV' | 44.3 | 0.01717 | -0.1668 | 53
SWPA | 'WEBBERS FALLS 161KV' | 29.8 | -0.14963 | SWPA | 'TRUMAN 161KV' | 102 | 0.01575 | -0.16538 | 53
SWPA | 'TENKILLER FERRY 161KV' | 26 | -0.14963 | SWPA | 'CLARENCE CANNON DAM 69KV' | 39.4 | 0.01137 | -0.161 | 54
SWPA | 'TENKILLER FERRY 161KV' | 26 | -0.14963 | SWPA | 'TABLE ROCK 161KV' | 187.2 | 0.01348 | -0.16311 | 54
SWPA | 'WEBBERS FALLS 161KV' | 29.8 | -0.14963 | SWPA | 'CLARENCE CANNON DAM 69KV' | 39.4 | 0.01137 | -0.161 | 54
SWPA | 'WEBBERS FALLS 161KV' | 29.8 | -0.14963 | SWPA | 'TABLE ROCK 161KV' | 187.2 | 0.01348 | -0.16311 | 54
SWPA | 'TENKILLER FERRY 161KV' | 26 | -0.14963 | SWPA | 'BULL SHOALS 161KV' | 294 | 0.00492 | -0.15455 | 57
SWPA | 'TENKILLER FERRY 161KV' | 26 | -0.14963 | SWPA | 'NORFORK 161KV' | 20 | 0.00317 | -0.1528 | 57
SWPA | 'WEBBERS FALLS 161KV' | 29.8 | -0.14963 | SWPA | 'BULL SHOALS 161KV' | 294 | 0.00492 | -0.15455 | 57
SWPA | 'WEBBERS FALLS 161KV' | 29.8 | -0.14963 | SWPA | 'NORFORK 161KV' | 20 | 0.00317 | -0.1528 | 57
SWPA | 'TENKILLER FERRY 161KV' | 26 | -0.14963 | SWPA | 'SIKESTON 161KV' | 235 | 0.00178 | -0.15141 | 58
SWPA | 'WEBBERS FALLS 161KV' | 29.8 | -0.14963 | SWPA | 'SIKESTON 161KV' | 235 | 0.00178 | -0.15141 | 58
SWPA | 'TENKILLER FERRY 161KV' | 26 | -0.14963 | SWPA | 'JONESBORO 161KV' | 43 | -0.00245 | -0.14718 | 60
SWPA | 'WEBBERS FALLS 161KV' | 29.8 | -0.14963 | SWPA | 'JONESBORO 161KV' | 43 | -0.00245 | -0.14718 | 60
SWPA | 'TENKILLER FERRY 161KV' | 26 | -0.14963 | SWPA | 'GREERS FERRY 161KV' | 93.6 | -0.01034 | -0.13929 | 63
SWPA | 'WEBBERS FALLS 161KV' | 29.8 | -0.14963 | SWPA | 'GREERS FERRY 161KV' | 93.6 | -0.01034 | -0.13929 | 63
SWPA | 'TENKILLER FERRY 161KV' | 26 | -0.14963 | SWPA | 'DARDANELLE 161KV' | 105.2 | -0.02728 | -0.12235 | 72
SWPA | 'WEBBERS FALLS 161KV' | 29.8 | -0.14963 | SWPA | 'DARDANELLE 161KV' | 105.2 | -0.02728 | -0.12235 | 72
OKGE | 'HORSESHOE LAKE 138KV' | 167.7046 | 0.03324 | OKGE | 'MUSKOGEE 345KV' | 1516 | 0.1439 | -0.11066 | 79
OKGE | 'CONTINENTAL EMPIRE 138KV' | 32 | 0.03469 | OKGE | 'MUSKOGEE 345KV' | 1516 | 0.1439 | -0.10921 | 80
OKGE | 'OMPA-PONCA CITY 69KV' | 78.5219 | 0.03381 | OKGE | 'MUSKOGEE 345KV' | 1516 | 0.1439 | -0.11009 | 80
OKGE | 'SOONER 7 345 345KV' | 1050 | 0.03623 | OKGE | 'MUSKOGEE 345KV' | 1516 | 0.1439 | -0.10767 | 81
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | 0.03535 | OKGE | 'MUSKOGEE 345KV' | 1516 | 0.1439 | -0.10855 | 81
OKGE | 'MCCLAIN 138KV' | 42 | 0.03713 | OKGE | 'MUSKOGEE 345KV' | 1516 | 0.1439 | -0.10677 | 82
OKGE | 'TINKER 5G 138KV' | 62 | 0.03661 | OKGE | 'MUSKOGEE 345KV' | 1516 | 0.1439 | -0.10729 | 82
OKGE | 'ONE OAK 345KV' | 200 | 0.03899 | OKGE | 'MUSKOGEE 345KV' | 1516 | 0.1439 | -0.10491 | 84
OKGE | 'SEMINOLE 138KV' | 28.3622 | 0.03933 | OKGE | 'MUSKOGEE 345KV' | 1516 | 0.1439 | -0.10457 | 84
OKGE | 'SHADY2 345 69KV' | 600 | -0.05857 | OKGE | 'REDBUD 345KV' | 250 | 0.04317 | -0.10174 | 86
OKGE | 'SHADY2 345 69KV' | 600 | -0.05857 | OKGE | 'SEMINOLE 345KV' | 996 | 0.0428 | -0.10137 | 86
OKGE | 'REDBUD 345KV' | 650 | 0.04317 | OKGE | 'MUSKOGEE 345KV' | 1516 | 0.1439 | -0.10073 | 87
OKGE | 'REDBUD 345KV' | 300 | 0.04317 | OKGE | 'MUSKOGEE 345KV' | 1516 | 0.1439 | -0.10073 | 87
OKGE | 'SHADY2 345 69KV' | 600 | -0.05857 | OKGE | 'ONE OAK 345KV' | 136 | 0.03899 | -0.09756 | 90
OKGE | 'SHADY2 345 69KV' | 600 | -0.05857 | OKGE | 'SEMINOLE 138KV' | 476.6378 | 0.03933 | -0.0979 | 90
OKGE | 'SHADY2 345 69KV' | 600 | -0.05857 | OKGE | 'MCCLAIN 138KV' | 478 | 0.03713 | -0.0957 | 92
OKGE | 'SHADY2 345 69KV' | 600 | -0.05857 | OKGE | 'MUSTANG 138KV' | 365.5 | 0.03706 | -0.09563 | 92
OKGE | 'SHADY2 345 69KV' | 600 | -0.05857 | OKGE | 'MUSTANG 69KV' | 106 | 0.03687 | -0.09544 | 92
OKGE | 'SHADY2 345 69KV' | 600 | -0.05857 | OKGE | 'SMITH COGEN 138KV' | 120 | 0.03698 | -0.09555 | 92
OKGE | 'SHADY2 345 69KV' | 600 | -0.05857 | OKGE | 'SOONER 345KV' | 513 | 0.03623 | -0.0948 | 92
OKGE | 'SHADY2 345 69KV' | 600 | -0.05857 | OKGE | 'FPLWND2 34KV' | 102 | 0.03613 | -0.0947 | 93
OKGE | 'SHADY2 345 69KV' | 600 | -0.05857 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.03619 | -0.09476 | 93
OKGE | 'SHADY2 345 69KV' | 600 | -0.05857 | OKGE | 'SOONER 138KV' | 505 | 0.03469 | -0.09326 | 94
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | Evans - Grant - Chisolm Rebuild and Conversion Project
Limiting Facility: | 17TH STREET (17TH 4X) 138/69/11.295KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | CHISHOLM (CHISLM1X) 138/69/13.2KV TRANSFORMER CKT 1
Flowgate: | 17TTH4X1421CHISISLM1X4212208SP
Date Redispatch Needed: | Starting 2008 6/1 - 10/1 Until EOC of Upgrade
Season Flowgate Identified: | 2008 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1161506 | 0.24192 | 0.4949
1161997 | 0.25298 | 0.4949
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.09189 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | -0.00188 | -0.09001 | 5
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.09189 | WERE | 'CHANUTE 69KV' | 55.637 | 0.00235 | -0.09424 | 5
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.09189 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | 0.00766 | -0.09955 | 5
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.09189 | WERE | 'CITY OF BURLINGTON 69KV' | 7.8 | 0.00372 | -0.09561 | 5
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.09189 | WERE | 'CITY OF ERIE 69KV' | 23.374 | 0.00235 | -0.09424 | 5
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.09189 | WERE | 'CITY OF FREDONIA 69KV' | 3.596 | 0.00275 | -0.09464 | 5
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.09189 | WERE | 'CITY OF GIRARD 69KV' | 4.592 | 0.00139 | -0.09328 | 5
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.09189 | WERE | 'CITY OF IOLA 69KV' | 24.471 | 0.00203 | -0.09392 | 5
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.09189 | WERE | 'CLAY CENTER JUNCTION 115KV' | 21.056 | -0.00155 | -0.09034 | 5
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.09189 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.98 | 0.00372 | -0.09561 | 5
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.09189 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | -0.00081 | -0.09108 | 5
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.09189 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | -0.00081 | -0.09108 | 5
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.09189 | WERE | 'LANG 7 345 345KV' | 310 | -0.00112 | -0.09077 | 5
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.09189 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | -0.00015 | -0.09174 | 5
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.09189 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 274.2987 | -0.00025 | -0.09164 | 5
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.09189 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | -0.00018 | -0.09171 | 5
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.09189 | WERE | 'COLBY 115KV' | 2.6903 | -0.00359 | -0.0883 | 6
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.09189 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 120 | -0.00405 | -0.08784 | 6
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.09189 | WERE | 'KNOLL 3 115 115KV' | 75 | -0.00408 | -0.08781 | 6
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.09189 | WERE | 'SMOKEY HILLS 34KV' | 152 | -0.00291 | -0.08898 | 6
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.06368 | WERE | 'CHANUTE 69KV' | 55.637 | 0.00235 | -0.06603 | 7
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.06368 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | 0.00766 | -0.07134 | 7
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.06368 | WERE | 'CITY OF BURLINGTON 69KV' | 7.8 | 0.00372 | -0.0674 | 7
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.06368 | WERE | 'CITY OF ERIE 69KV' | 23.374 | 0.00235 | -0.06603 | 7
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.06368 | WERE | 'CITY OF FREDONIA 69KV' | 3.596 | 0.00275 | -0.06643 | 7
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.06368 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.98 | 0.00372 | -0.0674 | 7
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.09189 | WERE | 'EVANS ENERGY CENTER 138KV' | 320.8022 | -0.01706 | -0.07483 | 7
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.06368 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | -0.00188 | -0.0618 | 8
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.06368 | WERE | 'CITY OF GIRARD 69KV' | 4.592 | 0.00139 | -0.06507 | 8
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.06368 | WERE | 'CITY OF IOLA 69KV' | 24.471 | 0.00203 | -0.06571 | 8
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.06368 | WERE | 'CLAY CENTER JUNCTION 115KV' | 21.056 | -0.00155 | -0.06213 | 8
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.06368 | WERE | 'COLBY 115KV' | 2.6903 | -0.00359 | -0.06009 | 8
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.06368 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 120 | -0.00405 | -0.05963 | 8
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.06368 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | -0.00081 | -0.06287 | 8
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.06368 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | -0.00081 | -0.06287 | 8
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.06368 | WERE | 'KNOLL 3 115 115KV' | 75 | -0.00408 | -0.0596 | 8
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.06368 | WERE | 'LANG 7 345 345KV' | 310 | -0.00112 | -0.06256 | 8
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.06368 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | -0.00015 | -0.06353 | 8
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.06368 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 274.2987 | -0.00025 | -0.06343 | 8
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.06368 | WERE | 'SMOKEY HILLS 34KV' | 152 | -0.00291 | -0.06077 | 8
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.06368 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | -0.00018 | -0.0635 | 8
WERE | 'CITY OF MULVANE 69KV' | 7.5 | -0.0489 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | 0.00766 | -0.05656 | 9
WERE | 'CITY OF MULVANE 69KV' | 7.5 | -0.0489 | WERE | 'CITY OF BURLINGTON 69KV' | 7.8 | 0.00372 | -0.05262 | 9
WERE | 'CITY OF MULVANE 69KV' | 7.5 | -0.0489 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.98 | 0.00372 | -0.05262 | 9
WERE | 'CITY OF MULVANE 69KV' | 7.5 | -0.0489 | WERE | 'CHANUTE 69KV' | 55.637 | 0.00235 | -0.05125 | 10
WERE | 'CITY OF MULVANE 69KV' | 7.5 | -0.0489 | WERE | 'CITY OF ERIE 69KV' | 23.374 | 0.00235 | -0.05125 | 10
WERE | 'CITY OF MULVANE 69KV' | 7.5 | -0.0489 | WERE | 'CITY OF FREDONIA 69KV' | 3.596 | 0.00275 | -0.05165 | 10
WERE | 'CITY OF MULVANE 69KV' | 7.5 | -0.0489 | WERE | 'CITY OF GIRARD 69KV' | 4.592 | 0.00139 | -0.05029 | 10
WERE | 'CITY OF MULVANE 69KV' | 7.5 | -0.0489 | WERE | 'CITY OF IOLA 69KV' | 24.471 | 0.00203 | -0.05093 | 10
WERE | 'CITY OF MULVANE 69KV' | 7.5 | -0.0489 | WERE | 'CLAY CENTER JUNCTION 115KV' | 21.056 | -0.00155 | -0.04735 | 10
WERE | 'CITY OF MULVANE 69KV' | 7.5 | -0.0489 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | -0.00081 | -0.04809 | 10
WERE | 'CITY OF MULVANE 69KV' | 7.5 | -0.0489 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | -0.00081 | -0.04809 | 10
WERE | 'CITY OF MULVANE 69KV' | 7.5 | -0.0489 | WERE | 'LANG 7 345 345KV' | 310 | -0.00112 | -0.04778 | 10
WERE | 'CITY OF MULVANE 69KV' | 7.5 | -0.0489 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | -0.00015 | -0.04875 | 10
WERE | 'CITY OF MULVANE 69KV' | 7.5 | -0.0489 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 274.2987 | -0.00025 | -0.04865 | 10
WERE | 'CITY OF MULVANE 69KV' | 7.5 | -0.0489 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | -0.00018 | -0.04872 | 10
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.09189 | WERE | 'CITY OF WELLINGTON 69KV' | 41.45 | -0.04432 | -0.04757 | 10
WERE | 'CITY OF MULVANE 69KV' | 7.5 | -0.0489 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | -0.00188 | -0.04702 | 11
WERE | 'CITY OF MULVANE 69KV' | 7.5 | -0.0489 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 120 | -0.00405 | -0.04485 | 11
WERE | 'CITY OF MULVANE 69KV' | 7.5 | -0.0489 | WERE | 'KNOLL 3 115 115KV' | 75 | -0.00408 | -0.04482 | 11
WERE | 'CITY OF MULVANE 69KV' | 7.5 | -0.0489 | WERE | 'SMOKEY HILLS 34KV' | 152 | -0.00291 | -0.04599 | 11
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.06368 | WERE | 'EVANS ENERGY CENTER 138KV' | 320.8022 | -0.01706 | -0.04662 | 11
WEPL | 'HARPER 138KV' | 15.06 | -0.04694 | WEPL | 'BELOIT 115KV' | 9.25 | -0.00211 | -0.04483 | 11
WEPL | 'HARPER 138KV' | 15.06 | -0.04694 | WEPL | 'CLIFTON 115KV' | 41.8109 | -0.00132 | -0.04562 | 11
WEPL | 'HARPER 138KV' | 15.06 | -0.04694 | WEPL | 'GREENLEAF 115KV' | 6.744 | -0.00108 | -0.04586 | 11
WEPL | 'HARPER 138KV' | 15.06 | -0.04694 | WEPL | 'PLAINVILLE 115KV' | 5.25 | -0.00379 | -0.04315 | 11
WEPL | 'HARPER 138KV' | 15.06 | -0.04694 | WEPL | 'SMITH CENTER 115KV' | 3.813 | -0.00293 | -0.04401 | 11
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.09189 | WERE | 'CITY OF MULVANE 69KV' | 8.29 | -0.0489 | -0.04299 | 12
WEPL | 'HARPER 138KV' | 15.06 | -0.04694 | WEPL | 'A. M. MULLERGREN GENERATOR 115KV' | 63 | -0.00576 | -0.04118 | 12
WEPL | 'HARPER 138KV' | 15.06 | -0.04694 | WEPL | 'NORTH WEST GREAT BEND 115KV' | 12.243 | -0.00576 | -0.04118 | 12
WEPL | 'HARPER 138KV' | 15.06 | -0.04694 | WEPL | 'RUSSELL 115KV' | 25.25 | -0.00471 | -0.04223 | 12
WEPL | 'HARPER 138KV' | 15.06 | -0.04694 | WEPL | 'GRAY COUNTY WIND FARM 115KV' | 60 | -0.00939 | -0.03755 | 13
WEPL | 'HARPER 138KV' | 15.06 | -0.04694 | WEPL | 'JUDSON LARGE 115KV' | 104.1272 | -0.00945 | -0.03749 | 13
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.09189 | WERE | 'WACO 138KV' | 17.967 | -0.05894 | -0.03295 | 15
WERE | 'CITY OF MULVANE 69KV' | 7.5 | -0.0489 | WERE | 'EVANS ENERGY CENTER 138KV' | 320.8022 | -0.01706 | -0.03184 | 16
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | Evans - Grant - Chisolm Rebuild and Conversion Project
Limiting Facility: | CHISHOLM (CHISLM1X) 138/69/13.2KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | EVANS ENERGY CENTER NORTH - SEDGWICK COUNTY NO. 12 COLWICH 138KV CKT 1
Flowgate: | CHIISLM1X1421570405706512207SP
Date Redispatch Needed: | 6/1/07 - 10/1/07
Season Flowgate Identified: | 2007 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1161997 | 0.1601 | 0.1601
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.05046 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | -0.00048 | -0.04998 | 3
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.05046 | WERE | 'BPU - CITY OF MCPHERSON 115KV' | 135 | -0.00136 | -0.0491 | 3
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.05046 | WERE | 'CHANUTE 69KV' | 56.723 | 0.00083 | -0.05129 | 3
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.05046 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | 0.00103 | -0.05149 | 3
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.05046 | WERE | 'CITY OF BURLINGTON 69KV' | 7.8 | 0.00168 | -0.05214 | 3
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.05046 | WERE | 'CITY OF ERIE 69KV' | 23.27 | 0.00083 | -0.05129 | 3
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.05046 | WERE | 'CITY OF FREDONIA 69KV' | 3.895 | 0.00099 | -0.05145 | 3
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.05046 | WERE | 'CITY OF GIRARD 69KV' | 4.789 | 0.00042 | -0.05088 | 3
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.05046 | WERE | 'CITY OF IOLA 69KV' | 24.267 | 0.00071 | -0.05117 | 3
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.05046 | WERE | 'CLAY CENTER JUNCTION 115KV' | 22.939 | -0.00029 | -0.05017 | 3
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.05046 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.00168 | -0.05214 | 3
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.05046 | WERE | 'COLBY 115KV' | 4.0926 | -0.00179 | -0.04867 | 3
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.05046 | WERE | 'EVANS ENERGY CENTER 138KV' | 340 | -0.003 | -0.04746 | 3
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.05046 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 120 | -0.00187 | -0.04859 | 3
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.05046 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 9e-05 | -0.05055 | 3
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.05046 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 9e-05 | -0.05055 | 3
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.05046 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | 0.00033 | -0.05079 | 3
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.05046 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 235.4582 | 0.00032 | -0.05078 | 3
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.05046 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 122.7222 | 0.00037 | -0.05083 | 3
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.03703 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | -0.00048 | -0.03655 | 4
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.03703 | WERE | 'BPU - CITY OF MCPHERSON 115KV' | 135 | -0.00136 | -0.03567 | 4
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.03703 | WERE | 'CHANUTE 69KV' | 56.723 | 0.00083 | -0.03786 | 4
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.03703 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | 0.00103 | -0.03806 | 4
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.03703 | WERE | 'CITY OF BURLINGTON 69KV' | 7.8 | 0.00168 | -0.03871 | 4
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.03703 | WERE | 'CITY OF ERIE 69KV' | 23.27 | 0.00083 | -0.03786 | 4
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.03703 | WERE | 'CITY OF FREDONIA 69KV' | 3.895 | 0.00099 | -0.03802 | 4
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.03703 | WERE | 'CITY OF GIRARD 69KV' | 4.789 | 0.00042 | -0.03745 | 4
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.03703 | WERE | 'CITY OF IOLA 69KV' | 24.267 | 0.00071 | -0.03774 | 4
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.03703 | WERE | 'CLAY CENTER JUNCTION 115KV' | 22.939 | -0.00029 | -0.03674 | 4
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.03703 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.00168 | -0.03871 | 4
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.03703 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 9e-05 | -0.03712 | 4
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.03703 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 9e-05 | -0.03712 | 4
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.03703 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | 0.00033 | -0.03736 | 4
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.03703 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 235.4582 | 0.00032 | -0.03735 | 4
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.03703 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 122.7222 | 0.00037 | -0.0374 | 4
WERE | 'CITY OF MULVANE 69KV' | 7.502 | -0.03281 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | -0.00048 | -0.03233 | 5
WERE | 'CITY OF MULVANE 69KV' | 7.502 | -0.03281 | WERE | 'BPU - CITY OF MCPHERSON 115KV' | 135 | -0.00136 | -0.03145 | 5
WERE | 'CITY OF MULVANE 69KV' | 7.502 | -0.03281 | WERE | 'CHANUTE 69KV' | 56.723 | 0.00083 | -0.03364 | 5
WERE | 'CITY OF MULVANE 69KV' | 7.502 | -0.03281 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | 0.00103 | -0.03384 | 5
WERE | 'CITY OF MULVANE 69KV' | 7.502 | -0.03281 | WERE | 'CITY OF BURLINGTON 69KV' | 7.8 | 0.00168 | -0.03449 | 5
WERE | 'CITY OF MULVANE 69KV' | 7.502 | -0.03281 | WERE | 'CITY OF ERIE 69KV' | 23.27 | 0.00083 | -0.03364 | 5
WERE | 'CITY OF MULVANE 69KV' | 7.502 | -0.03281 | WERE | 'CITY OF FREDONIA 69KV' | 3.895 | 0.00099 | -0.0338 | 5
WERE | 'CITY OF MULVANE 69KV' | 7.502 | -0.03281 | WERE | 'CITY OF GIRARD 69KV' | 4.789 | 0.00042 | -0.03323 | 5
WERE | 'CITY OF MULVANE 69KV' | 7.502 | -0.03281 | WERE | 'CITY OF IOLA 69KV' | 24.267 | 0.00071 | -0.03352 | 5
WERE | 'CITY OF MULVANE 69KV' | 7.502 | -0.03281 | WERE | 'CLAY CENTER JUNCTION 115KV' | 22.939 | -0.00029 | -0.03252 | 5
WERE | 'CITY OF MULVANE 69KV' | 7.502 | -0.03281 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.00168 | -0.03449 | 5
WERE | 'CITY OF MULVANE 69KV' | 7.502 | -0.03281 | WERE | 'COLBY 115KV' | 4.0926 | -0.00179 | -0.03102 | 5
WERE | 'CITY OF MULVANE 69KV' | 7.502 | -0.03281 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 120 | -0.00187 | -0.03094 | 5
WERE | 'CITY OF MULVANE 69KV' | 7.502 | -0.03281 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 9e-05 | -0.0329 | 5
WERE | 'CITY OF MULVANE 69KV' | 7.502 | -0.03281 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 9e-05 | -0.0329 | 5
WERE | 'CITY OF MULVANE 69KV' | 7.502 | -0.03281 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | 0.00033 | -0.03314 | 5
WERE | 'CITY OF MULVANE 69KV' | 7.502 | -0.03281 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 235.4582 | 0.00032 | -0.03313 | 5
WERE | 'CITY OF MULVANE 69KV' | 7.502 | -0.03281 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 122.7222 | 0.00037 | -0.03318 | 5
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.03703 | WERE | 'COLBY 115KV' | 4.0926 | -0.00179 | -0.03524 | 5
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.03703 | WERE | 'EVANS ENERGY CENTER 138KV' | 340 | -0.003 | -0.03403 | 5
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.03703 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 120 | -0.00187 | -0.03516 | 5
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | Evans - Grant - Chisolm Rebuild and Conversion Project
Limiting Facility: | CHISHOLM (CHISLM1X) 138/69/13.2KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | EVANS ENERGY CENTER NORTH - SEDGWICK COUNTY NO. 12 COLWICH 138KV CKT 1
Flowgate: | CHIISLM1X1421570405706512208SP
Date Redispatch Needed: | Starting 2008 6/1 - 10/1 Until EOC of Upgrade
Season Flowgate Identified: | 2008 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1161506 | 2.7348 | 5.3784
1161997 | 2.6436 | 5.3784
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.05046 | WERE | 'CHANUTE 69KV' | 55.637 | 0.00084 | -0.0513 | 105
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.05046 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | 6e-05 | -0.05052 | 106
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.05046 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | 6e-05 | -0.05052 | 106
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.05046 | WERE | 'LANG 7 345 345KV' | 310 | 0.00033 | -0.05079 | 106
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.05046 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | 0.00031 | -0.05077 | 106
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.05046 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 274.2987 | 0.0003 | -0.05076 | 106
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.05046 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00035 | -0.05081 | 106
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.05046 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | -0.00052 | -0.04994 | 108
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.05046 | WERE | 'SMOKEY HILLS 34KV' | 152 | -0.00117 | -0.04929 | 109
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.05046 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 120 | -0.00183 | -0.04863 | 111
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.05046 | WERE | 'KNOLL 3 115 115KV' | 75 | -0.00192 | -0.04854 | 111
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.05046 | WERE | 'EVANS ENERGY CENTER 138KV' | 320.8022 | -0.00301 | -0.04745 | 113
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | GREENSBURG - JUDSON LARGE 115KV CKT 1
Limiting Facility: | GREENSBURG - JUDSON LARGE 115KV CKT 1
Direction: | To->From
Line Outage: | '58779 MULGREN6 230 58795 SPEARVL6 230 1'
Flowgate: | 58764587711587795879511106WP
Date Redispatch Needed: | 12/1/06 - 4/1/07
Season Flowgate Identified: | 2006 Winter Peak
Reservation | Relief Amount | Aggregate Relief Amount
1162649 | 13.2623 | 13.2623
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WEPL | 'HARPER 138KV' | 17.21 | -0.12721 | WEPL | 'GRAY COUNTY WIND FARM 115KV' | 63 | 0.23722 | -0.36443 | 36
WEPL | 'HARPER 138KV' | 17.21 | -0.12721 | WEPL | 'JUDSON LARGE 115KV' | 53.7604 | 0.23887 | -0.36608 | 36
WEPL | 'A. M. MULLERGREN GENERATOR 115KV' | 46.0158 | -0.04038 | WEPL | 'JUDSON LARGE 115KV' | 53.7604 | 0.23887 | -0.27925 | 47
WEPL | 'A. M. MULLERGREN GENERATOR 115KV' | 46.0158 | -0.04038 | WEPL | 'GRAY COUNTY WIND FARM 115KV' | 63 | 0.23722 | -0.2776 | 48
WEPL | 'RUSSELL 115KV' | 27.9 | -0.03155 | WEPL | 'GRAY COUNTY WIND FARM 115KV' | 63 | 0.23722 | -0.26877 | 49
WEPL | 'RUSSELL 115KV' | 27.9 | -0.03155 | WEPL | 'JUDSON LARGE 115KV' | 53.7604 | 0.23887 | -0.27042 | 49
WEPL | 'CLIFTON 115KV' | 70 | -0.00966 | WEPL | 'JUDSON LARGE 115KV' | 53.7604 | 0.23887 | -0.24853 | 53
WEPL | 'CLIFTON 115KV' | 70 | -0.00966 | WEPL | 'GRAY COUNTY WIND FARM 115KV' | 63 | 0.23722 | -0.24688 | 54
KACP | 'BULL CREEK 161KV' | 308 | -0.00494 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12719 | -0.13213 | 100
KACP | 'PAOLA COMBUSTION TURBINES 161KV' | 77 | -0.00489 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12719 | -0.13208 | 100
KACP | 'GRAND AVENUE 161KV' | 65 | -0.00372 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12719 | -0.13091 | 101
KACP | 'HAWTHORN 161KV' | 423 | -0.00353 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12719 | -0.13072 | 101
KACP | 'MONTROSE 161KV' | 118.3993 | -0.0038 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12719 | -0.13099 | 101
KACP | 'NORTHEAST 13KV' | 56 | -0.00368 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12719 | -0.13087 | 101
KACP | 'NORTHEAST 13KV' | 56 | -0.00368 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12719 | -0.13087 | 101
KACP | 'NORTHEAST 13KV' | 58 | -0.00368 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12719 | -0.13087 | 101
KACP | 'NORTHEAST 13KV' | 59 | -0.00368 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12719 | -0.13087 | 101
KACP | 'NORTHEAST 161KV' | 55 | -0.00368 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12719 | -0.13087 | 101
KACP | 'NORTHEAST 161KV' | 58 | -0.00368 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12719 | -0.13087 | 101
KACP | 'NORTHEAST 161KV' | 58 | -0.00368 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12719 | -0.13087 | 101
KACP | 'NORTHEAST 161KV' | 58 | -0.00368 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12719 | -0.13087 | 101
KACP | 'CITY OF HIGGINSVILLE 69KV' | 36 | -0.00303 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12719 | -0.13022 | 102
KACP | 'MARSHALL 161KV' | 54.1 | -0.00195 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12719 | -0.12914 | 103
WEPL | 'CIMARRON RIVER 115KV' | 72 | 0.14655 | WEPL | 'JUDSON LARGE 115KV' | 53.7604 | 0.23887 | -0.09232 | 144
WEPL | 'CIMARRON RIVER 115KV' | 72 | 0.14655 | WEPL | 'GRAY COUNTY WIND FARM 115KV' | 63 | 0.23722 | -0.09067 | 146
WERE | 'PAWNEE 115KV' | 999 | -0.09442 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | -0.00683 | -0.08759 | 151
WERE | 'RICE 115KV' | 999 | -0.09442 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | -0.00683 | -0.08759 | 151
WERE | 'PAWNEE 115KV' | 999 | -0.09442 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 220.265 | -0.00723 | -0.08719 | 152
WERE | 'RICE 115KV' | 999 | -0.09442 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 220.265 | -0.00723 | -0.08719 | 152
WERE | 'PAWNEE 115KV' | 999 | -0.09442 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 61.0684 | -0.00789 | -0.08653 | 153
WERE | 'RICE 115KV' | 999 | -0.09442 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 61.0684 | -0.00789 | -0.08653 | 153
WERE | 'PAWNEE 115KV' | 999 | -0.09442 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | -0.00893 | -0.08549 | 155
WERE | 'PAWNEE 115KV' | 999 | -0.09442 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | -0.00882 | -0.0856 | 155
WERE | 'RICE 115KV' | 999 | -0.09442 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | -0.00893 | -0.08549 | 155
WERE | 'RICE 115KV' | 999 | -0.09442 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | -0.00882 | -0.0856 | 155
WERE | 'PAWNEE 115KV' | 999 | -0.09442 | WERE | 'EVANS ENERGY CENTER 138KV' | 165 | -0.01573 | -0.07869 | 169
WERE | 'RICE 115KV' | 999 | -0.09442 | WERE | 'EVANS ENERGY CENTER 138KV' | 165 | -0.01573 | -0.07869 | 169
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | GREENSBURG - JUDSON LARGE 115KV CKT 1
Limiting Facility: | GREENSBURG - JUDSON LARGE 115KV CKT 1
Direction: | To->From
Line Outage: | '58779 MULGREN6 230 58795 SPEARVL6 230 1'
Flowgate: | 58764587711587795879511107G
Date Redispatch Needed: | Starting 2007 4/1 - 6/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 Spring Peak
Reservation | Relief Amount | Aggregate Relief Amount
1162649 | 13.2098 | 13.2098
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WEPL | 'HARPER 138KV' | 17.21 | -0.12652 | WEPL | 'GRAY COUNTY WIND FARM 115KV' | 63 | 0.23707 | -0.36359 | 36
WEPL | 'HARPER 138KV' | 17.21 | -0.12652 | WEPL | 'JUDSON LARGE 115KV' | 87.1589 | 0.23872 | -0.36524 | 36
WEPL | 'A. M. MULLERGREN GENERATOR 115KV' | 19.7129 | -0.03192 | WEPL | 'GRAY COUNTY WIND FARM 115KV' | 63 | 0.23707 | -0.26899 | 49
WEPL | 'A. M. MULLERGREN GENERATOR 115KV' | 19.7129 | -0.03192 | WEPL | 'JUDSON LARGE 115KV' | 87.1589 | 0.23872 | -0.27064 | 49
WEPL | 'RUSSELL 115KV' | 27.9 | -0.02558 | WEPL | 'GRAY COUNTY WIND FARM 115KV' | 63 | 0.23707 | -0.26265 | 50
WEPL | 'RUSSELL 115KV' | 27.9 | -0.02558 | WEPL | 'JUDSON LARGE 115KV' | 87.1589 | 0.23872 | -0.2643 | 50
WEPL | 'CLIFTON 115KV' | 70 | -0.0091 | WEPL | 'JUDSON LARGE 115KV' | 87.1589 | 0.23872 | -0.24782 | 53
WEPL | 'CLIFTON 115KV' | 70 | -0.0091 | WEPL | 'GRAY COUNTY WIND FARM 115KV' | 63 | 0.23707 | -0.24617 | 54
KACP | 'LACYGNE UNIT 345KV' | 736 | -0.00607 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12673 | -0.1328 | 99
KACP | 'BULL CREEK 161KV' | 80.22 | -0.00483 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12673 | -0.13156 | 100
KACP | 'PAOLA COMBUSTION TURBINES 161KV' | 77 | -0.00479 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12673 | -0.13152 | 100
KACP | 'GRAND AVENUE 161KV' | 65 | -0.00363 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12673 | -0.13036 | 101
KACP | 'NORTHEAST 13KV' | 56 | -0.00359 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12673 | -0.13032 | 101
KACP | 'NORTHEAST 13KV' | 56 | -0.00359 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12673 | -0.13032 | 101
KACP | 'NORTHEAST 13KV' | 58 | -0.00359 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12673 | -0.13032 | 101
KACP | 'NORTHEAST 13KV' | 59 | -0.00359 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12673 | -0.13032 | 101
KACP | 'NORTHEAST 161KV' | 55 | -0.00359 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12673 | -0.13032 | 101
KACP | 'NORTHEAST 161KV' | 58 | -0.00359 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12673 | -0.13032 | 101
KACP | 'NORTHEAST 161KV' | 58 | -0.00359 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12673 | -0.13032 | 101
KACP | 'NORTHEAST 161KV' | 58 | -0.00359 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12673 | -0.13032 | 101
KACP | 'CITY OF HIGGINSVILLE 69KV' | 36 | -0.00297 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12673 | -0.1297 | 102
KACP | 'MARSHALL 161KV' | 54.1 | -0.00192 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12673 | -0.12865 | 103
WEPL | 'CIMARRON RIVER 115KV' | 72 | 0.14611 | WEPL | 'JUDSON LARGE 115KV' | 87.1589 | 0.23872 | -0.09261 | 143
WEPL | 'CIMARRON RIVER 115KV' | 72 | 0.14611 | WEPL | 'GRAY COUNTY WIND FARM 115KV' | 63 | 0.23707 | -0.09096 | 145
WERE | 'PAWNEE 115KV' | 999 | -0.09134 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | -0.00665 | -0.08469 | 156
WERE | 'RICE 115KV' | 999 | -0.09134 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | -0.00665 | -0.08469 | 156
WERE | 'PAWNEE 115KV' | 999 | -0.09134 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 230.0213 | -0.00703 | -0.08431 | 157
WERE | 'PAWNEE 115KV' | 999 | -0.09134 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 78.1487 | -0.00735 | -0.08399 | 157
WERE | 'RICE 115KV' | 999 | -0.09134 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 230.0213 | -0.00703 | -0.08431 | 157
WERE | 'RICE 115KV' | 999 | -0.09134 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 78.1487 | -0.00735 | -0.08399 | 157
WERE | 'PAWNEE 115KV' | 999 | -0.09134 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | -0.00864 | -0.0827 | 160
WERE | 'PAWNEE 115KV' | 999 | -0.09134 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | -0.00857 | -0.08277 | 160
WERE | 'RICE 115KV' | 999 | -0.09134 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | -0.00864 | -0.0827 | 160
WERE | 'RICE 115KV' | 999 | -0.09134 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | -0.00857 | -0.08277 | 160
WERE | 'PAWNEE 115KV' | 999 | -0.09134 | WERE | 'EVANS ENERGY CENTER 138KV' | 340 | -0.01562 | -0.07572 | 174
WERE | 'RICE 115KV' | 999 | -0.09134 | WERE | 'EVANS ENERGY CENTER 138KV' | 340 | -0.01562 | -0.07572 | 174
WERE | 'PAWNEE 115KV' | 999 | -0.09134 | WERE | 'BPU - CITY OF MCPHERSON 115KV' | 135 | -0.02187 | -0.06947 | 190
WERE | 'RICE 115KV' | 999 | -0.09134 | WERE | 'BPU - CITY OF MCPHERSON 115KV' | 135 | -0.02187 | -0.06947 | 190
WERE | 'PAWNEE 115KV' | 999 | -0.09134 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.02485 | -0.06649 | 199
WERE | 'RICE 115KV' | 999 | -0.09134 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.02485 | -0.06649 | 199
WERE | 'PAWNEE 115KV' | 999 | -0.09134 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 120 | -0.02786 | -0.06348 | 208
WERE | 'RICE 115KV' | 999 | -0.09134 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 120 | -0.02786 | -0.06348 | 208
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | JONES - JONESBORO 161KV CKT 1 SWPA
Limiting Facility: | JONES - JONESBORO 161KV CKT 1
Direction: | From->To
Line Outage: | KENNETT - NEW MADRID 161KV CKT 1
Flowgate: | 99755526181526105260013207SP
Date Redispatch Needed: | 6/1/07 - 10/1/07
Season Flowgate Identified: | 2007 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1161665 | 3.6139 | 3.6139
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
SWPA | 'JONESBORO 161KV' | 20 | -0.65617 | SWPA | 'BEAVER 161KV' | 100.2468 | -0.02684 | -0.62933 | 6
SWPA | 'JONESBORO 161KV' | 20 | -0.65617 | SWPA | 'BROKEN BOW 138KV' | 93.4 | -0.01199 | -0.64418 | 6
SWPA | 'JONESBORO 161KV' | 20 | -0.65617 | SWPA | 'BULL SHOALS 161KV' | 293.2 | -0.04995 | -0.60622 | 6
SWPA | 'JONESBORO 161KV' | 20 | -0.65617 | SWPA | 'CARTHAGE 69KV' | 30 | -0.02225 | -0.63392 | 6
SWPA | 'JONESBORO 161KV' | 20 | -0.65617 | SWPA | 'CLARENCE CANNON DAM 69KV' | 39.2 | -0.01434 | -0.64183 | 6
SWPA | 'JONESBORO 161KV' | 20 | -0.65617 | SWPA | 'DARDANELLE 161KV' | 105.2 | -0.02441 | -0.63176 | 6
SWPA | 'JONESBORO 161KV' | 20 | -0.65617 | SWPA | 'DENISON 138KV' | 59.4 | -0.01524 | -0.64093 | 6
SWPA | 'JONESBORO 161KV' | 20 | -0.65617 | SWPA | 'EUFAULA 138KV' | 51 | -0.01734 | -0.63883 | 6
SWPA | 'JONESBORO 161KV' | 20 | -0.65617 | SWPA | 'EUFAULA 161KV' | 25.5 | -0.01734 | -0.63883 | 6
SWPA | 'JONESBORO 161KV' | 20 | -0.65617 | SWPA | 'FORT GIBSON 161KV' | 42.4 | -0.01825 | -0.63792 | 6
SWPA | 'JONESBORO 161KV' | 20 | -0.65617 | SWPA | 'JAMES RIVER 161KV' | 159 | -0.02453 | -0.63164 | 6
SWPA | 'JONESBORO 161KV' | 20 | -0.65617 | SWPA | 'JAMES RIVER 69KV' | 232.999 | -0.02456 | -0.63161 | 6
SWPA | 'JONESBORO 161KV' | 20 | -0.65617 | SWPA | 'KEYSTONE DAM 161KV' | 59.4 | -0.01818 | -0.63799 | 6
SWPA | 'JONESBORO 161KV' | 20 | -0.65617 | SWPA | 'MCCARTNEY 161KV' | 322.3152 | -0.02405 | -0.63212 | 6
SWPA | 'JONESBORO 161KV' | 20 | -0.65617 | SWPA | 'NORFORK 161KV' | 20 | -0.06277 | -0.5934 | 6
SWPA | 'JONESBORO 161KV' | 20 | -0.65617 | SWPA | 'OZARK 161KV' | 78 | -0.0195 | -0.63667 | 6
SWPA | 'JONESBORO 161KV' | 20 | -0.65617 | SWPA | 'POPLAR BLUFF 69KV' | 6 | -0.05741 | -0.59876 | 6
SWPA | 'JONESBORO 161KV' | 20 | -0.65617 | SWPA | 'ROBERT S. KERR 161KV' | 107.2 | -0.01729 | -0.63888 | 6
SWPA | 'JONESBORO 161KV' | 20 | -0.65617 | SWPA | 'SIKESTON 161KV' | 235 | -0.01452 | -0.64165 | 6
SWPA | 'JONESBORO 161KV' | 20 | -0.65617 | SWPA | 'STOCKTON 161KV' | 44.1 | -0.02111 | -0.63506 | 6
SWPA | 'JONESBORO 161KV' | 20 | -0.65617 | SWPA | 'TABLE ROCK 161KV' | 186.8 | -0.03159 | -0.62458 | 6
SWPA | 'JONESBORO 161KV' | 20 | -0.65617 | SWPA | 'TENKILLER FERRY 161KV' | 16 | -0.01768 | -0.63849 | 6
SWPA | 'JONESBORO 161KV' | 20 | -0.65617 | SWPA | 'TRUMAN 161KV' | 102 | -0.01767 | -0.6385 | 6
SWPA | 'JONESBORO 161KV' | 20 | -0.65617 | SWPA | 'WEBBERS FALLS 161KV' | 39 | -0.01768 | -0.63849 | 6
SWPA | 'PARAGOULD 69KV' | 12 | -0.62004 | SWPA | 'BEAVER 161KV' | 100.2468 | -0.02684 | -0.5932 | 6
SWPA | 'PARAGOULD 69KV' | 12 | -0.62004 | SWPA | 'BROKEN BOW 138KV' | 93.4 | -0.01199 | -0.60805 | 6
SWPA | 'PARAGOULD 69KV' | 12 | -0.62004 | SWPA | 'BULL SHOALS 161KV' | 293.2 | -0.04995 | -0.57009 | 6
SWPA | 'PARAGOULD 69KV' | 12 | -0.62004 | SWPA | 'CARTHAGE 69KV' | 30 | -0.02225 | -0.59779 | 6
SWPA | 'PARAGOULD 69KV' | 12 | -0.62004 | SWPA | 'CLARENCE CANNON DAM 69KV' | 39.2 | -0.01434 | -0.6057 | 6
SWPA | 'PARAGOULD 69KV' | 12 | -0.62004 | SWPA | 'DARDANELLE 161KV' | 105.2 | -0.02441 | -0.59563 | 6
SWPA | 'PARAGOULD 69KV' | 12 | -0.62004 | SWPA | 'DENISON 138KV' | 59.4 | -0.01524 | -0.6048 | 6
SWPA | 'PARAGOULD 69KV' | 12 | -0.62004 | SWPA | 'EUFAULA 138KV' | 51 | -0.01734 | -0.6027 | 6
SWPA | 'PARAGOULD 69KV' | 12 | -0.62004 | SWPA | 'EUFAULA 161KV' | 25.5 | -0.01734 | -0.6027 | 6
SWPA | 'PARAGOULD 69KV' | 12 | -0.62004 | SWPA | 'FORT GIBSON 161KV' | 42.4 | -0.01825 | -0.60179 | 6
SWPA | 'PARAGOULD 69KV' | 12 | -0.62004 | SWPA | 'JAMES RIVER 161KV' | 159 | -0.02453 | -0.59551 | 6
SWPA | 'PARAGOULD 69KV' | 12 | -0.62004 | SWPA | 'JAMES RIVER 69KV' | 232.999 | -0.02456 | -0.59548 | 6
SWPA | 'PARAGOULD 69KV' | 12 | -0.62004 | SWPA | 'KEYSTONE DAM 161KV' | 59.4 | -0.01818 | -0.60186 | 6
SWPA | 'PARAGOULD 69KV' | 12 | -0.62004 | SWPA | 'MCCARTNEY 161KV' | 322.3152 | -0.02405 | -0.59599 | 6
SWPA | 'PARAGOULD 69KV' | 12 | -0.62004 | SWPA | 'NORFORK 161KV' | 20 | -0.06277 | -0.55727 | 6
SWPA | 'PARAGOULD 69KV' | 12 | -0.62004 | SWPA | 'OZARK 161KV' | 78 | -0.0195 | -0.60054 | 6
SWPA | 'PARAGOULD 69KV' | 12 | -0.62004 | SWPA | 'POPLAR BLUFF 69KV' | 6 | -0.05741 | -0.56263 | 6
SWPA | 'PARAGOULD 69KV' | 12 | -0.62004 | SWPA | 'ROBERT S. KERR 161KV' | 107.2 | -0.01729 | -0.60275 | 6
SWPA | 'PARAGOULD 69KV' | 12 | -0.62004 | SWPA | 'SIKESTON 161KV' | 235 | -0.01452 | -0.60552 | 6
SWPA | 'PARAGOULD 69KV' | 12 | -0.62004 | SWPA | 'STOCKTON 161KV' | 44.1 | -0.02111 | -0.59893 | 6
SWPA | 'PARAGOULD 69KV' | 12 | -0.62004 | SWPA | 'TABLE ROCK 161KV' | 186.8 | -0.03159 | -0.58845 | 6
SWPA | 'PARAGOULD 69KV' | 12 | -0.62004 | SWPA | 'TENKILLER FERRY 161KV' | 16 | -0.01768 | -0.60236 | 6
SWPA | 'PARAGOULD 69KV' | 12 | -0.62004 | SWPA | 'TRUMAN 161KV' | 102 | -0.01767 | -0.60237 | 6
SWPA | 'PARAGOULD 69KV' | 12 | -0.62004 | SWPA | 'WEBBERS FALLS 161KV' | 39 | -0.01768 | -0.60236 | 6
SWPA | 'KENNETT 69KV' | 21.8 | -0.53283 | SWPA | 'BEAVER 161KV' | 100.2468 | -0.02684 | -0.50599 | 7
SWPA | 'KENNETT 69KV' | 21.8 | -0.53283 | SWPA | 'BROKEN BOW 138KV' | 93.4 | -0.01199 | -0.52084 | 7
SWPA | 'KENNETT 69KV' | 21.8 | -0.53283 | SWPA | 'BULL SHOALS 161KV' | 293.2 | -0.04995 | -0.48288 | 7
SWPA | 'KENNETT 69KV' | 21.8 | -0.53283 | SWPA | 'CARTHAGE 69KV' | 30 | -0.02225 | -0.51058 | 7
SWPA | 'KENNETT 69KV' | 21.8 | -0.53283 | SWPA | 'CLARENCE CANNON DAM 69KV' | 39.2 | -0.01434 | -0.51849 | 7
SWPA | 'KENNETT 69KV' | 21.8 | -0.53283 | SWPA | 'DARDANELLE 161KV' | 105.2 | -0.02441 | -0.50842 | 7
SWPA | 'KENNETT 69KV' | 21.8 | -0.53283 | SWPA | 'DENISON 138KV' | 59.4 | -0.01524 | -0.51759 | 7
SWPA | 'KENNETT 69KV' | 21.8 | -0.53283 | SWPA | 'EUFAULA 138KV' | 51 | -0.01734 | -0.51549 | 7
SWPA | 'KENNETT 69KV' | 21.8 | -0.53283 | SWPA | 'EUFAULA 161KV' | 25.5 | -0.01734 | -0.51549 | 7
SWPA | 'KENNETT 69KV' | 21.8 | -0.53283 | SWPA | 'FORT GIBSON 161KV' | 42.4 | -0.01825 | -0.51458 | 7
SWPA | 'KENNETT 69KV' | 21.8 | -0.53283 | SWPA | 'JAMES RIVER 161KV' | 159 | -0.02453 | -0.5083 | 7
SWPA | 'KENNETT 69KV' | 21.8 | -0.53283 | SWPA | 'JAMES RIVER 69KV' | 232.999 | -0.02456 | -0.50827 | 7
SWPA | 'KENNETT 69KV' | 21.8 | -0.53283 | SWPA | 'KEYSTONE DAM 161KV' | 59.4 | -0.01818 | -0.51465 | 7
SWPA | 'KENNETT 69KV' | 21.8 | -0.53283 | SWPA | 'MCCARTNEY 161KV' | 322.3152 | -0.02405 | -0.50878 | 7
SWPA | 'KENNETT 69KV' | 21.8 | -0.53283 | SWPA | 'OZARK 161KV' | 78 | -0.0195 | -0.51333 | 7
SWPA | 'KENNETT 69KV' | 21.8 | -0.53283 | SWPA | 'ROBERT S. KERR 161KV' | 107.2 | -0.01729 | -0.51554 | 7
SWPA | 'KENNETT 69KV' | 21.8 | -0.53283 | SWPA | 'SIKESTON 161KV' | 235 | -0.01452 | -0.51831 | 7
SWPA | 'KENNETT 69KV' | 21.8 | -0.53283 | SWPA | 'STOCKTON 161KV' | 44.1 | -0.02111 | -0.51172 | 7
SWPA | 'KENNETT 69KV' | 21.8 | -0.53283 | SWPA | 'TABLE ROCK 161KV' | 186.8 | -0.03159 | -0.50124 | 7
SWPA | 'KENNETT 69KV' | 21.8 | -0.53283 | SWPA | 'TENKILLER FERRY 161KV' | 16 | -0.01768 | -0.51515 | 7
SWPA | 'KENNETT 69KV' | 21.8 | -0.53283 | SWPA | 'TRUMAN 161KV' | 102 | -0.01767 | -0.51516 | 7
SWPA | 'KENNETT 69KV' | 21.8 | -0.53283 | SWPA | 'WEBBERS FALLS 161KV' | 39 | -0.01768 | -0.51515 | 7
SWPA | 'JONESBORO 161KV' | 20 | -0.65617 | SWPA | 'GREERS FERRY 161KV' | 93.4 | -0.20712 | -0.44905 | 8
SWPA | 'KENNETT 69KV' | 21.8 | -0.53283 | SWPA | 'NORFORK 161KV' | 20 | -0.06277 | -0.47006 | 8
SWPA | 'KENNETT 69KV' | 21.8 | -0.53283 | SWPA | 'POPLAR BLUFF 69KV' | 6 | -0.05741 | -0.47542 | 8
SWPA | 'JONESBORO 161KV' | 20 | -0.65617 | SWPA | 'MALDEN 69KV' | 7 | -0.24774 | -0.40843 | 9
SWPA | 'PARAGOULD 69KV' | 12 | -0.62004 | SWPA | 'GREERS FERRY 161KV' | 93.4 | -0.20712 | -0.41292 | 9
SWPA | 'PIGGOTT 69KV' | 7.5 | -0.43128 | SWPA | 'BEAVER 161KV' | 100.2468 | -0.02684 | -0.40444 | 9
SWPA | 'PIGGOTT 69KV' | 7.5 | -0.43128 | SWPA | 'BROKEN BOW 138KV' | 93.4 | -0.01199 | -0.41929 | 9
SWPA | 'PIGGOTT 69KV' | 7.5 | -0.43128 | SWPA | 'BULL SHOALS 161KV' | 293.2 | -0.04995 | -0.38133 | 9
SWPA | 'PIGGOTT 69KV' | 7.5 | -0.43128 | SWPA | 'CARTHAGE 69KV' | 30 | -0.02225 | -0.40903 | 9
SWPA | 'PIGGOTT 69KV' | 7.5 | -0.43128 | SWPA | 'CLARENCE CANNON DAM 69KV' | 39.2 | -0.01434 | -0.41694 | 9
SWPA | 'PIGGOTT 69KV' | 7.5 | -0.43128 | SWPA | 'DARDANELLE 161KV' | 105.2 | -0.02441 | -0.40687 | 9
SWPA | 'PIGGOTT 69KV' | 7.5 | -0.43128 | SWPA | 'DENISON 138KV' | 59.4 | -0.01524 | -0.41604 | 9
SWPA | 'PIGGOTT 69KV' | 7.5 | -0.43128 | SWPA | 'EUFAULA 138KV' | 51 | -0.01734 | -0.41394 | 9
SWPA | 'PIGGOTT 69KV' | 7.5 | -0.43128 | SWPA | 'EUFAULA 161KV' | 25.5 | -0.01734 | -0.41394 | 9
SWPA | 'PIGGOTT 69KV' | 7.5 | -0.43128 | SWPA | 'FORT GIBSON 161KV' | 42.4 | -0.01825 | -0.41303 | 9
SWPA | 'PIGGOTT 69KV' | 7.5 | -0.43128 | SWPA | 'JAMES RIVER 161KV' | 159 | -0.02453 | -0.40675 | 9
SWPA | 'PIGGOTT 69KV' | 7.5 | -0.43128 | SWPA | 'JAMES RIVER 69KV' | 232.999 | -0.02456 | -0.40672 | 9
SWPA | 'PIGGOTT 69KV' | 7.5 | -0.43128 | SWPA | 'KEYSTONE DAM 161KV' | 59.4 | -0.01818 | -0.4131 | 9
SWPA | 'PIGGOTT 69KV' | 7.5 | -0.43128 | SWPA | 'MCCARTNEY 161KV' | 322.3152 | -0.02405 | -0.40723 | 9
SWPA | 'PIGGOTT 69KV' | 7.5 | -0.43128 | SWPA | 'OZARK 161KV' | 78 | -0.0195 | -0.41178 | 9
SWPA | 'PIGGOTT 69KV' | 7.5 | -0.43128 | SWPA | 'ROBERT S. KERR 161KV' | 107.2 | -0.01729 | -0.41399 | 9
SWPA | 'PIGGOTT 69KV' | 7.5 | -0.43128 | SWPA | 'SIKESTON 161KV' | 235 | -0.01452 | -0.41676 | 9
SWPA | 'PIGGOTT 69KV' | 7.5 | -0.43128 | SWPA | 'STOCKTON 161KV' | 44.1 | -0.02111 | -0.41017 | 9
SWPA | 'PIGGOTT 69KV' | 7.5 | -0.43128 | SWPA | 'TABLE ROCK 161KV' | 186.8 | -0.03159 | -0.39969 | 9
SWPA | 'PIGGOTT 69KV' | 7.5 | -0.43128 | SWPA | 'TENKILLER FERRY 161KV' | 16 | -0.01768 | -0.4136 | 9
SWPA | 'PIGGOTT 69KV' | 7.5 | -0.43128 | SWPA | 'TRUMAN 161KV' | 102 | -0.01767 | -0.41361 | 9
SWPA | 'PIGGOTT 69KV' | 7.5 | -0.43128 | SWPA | 'WEBBERS FALLS 161KV' | 39 | -0.01768 | -0.4136 | 9
SWPA | 'PARAGOULD 69KV' | 12 | -0.62004 | SWPA | 'MALDEN 69KV' | 7 | -0.24774 | -0.3723 | 10
SWPA | 'PIGGOTT 69KV' | 7.5 | -0.43128 | SWPA | 'NORFORK 161KV' | 20 | -0.06277 | -0.36851 | 10
SWPA | 'PIGGOTT 69KV' | 7.5 | -0.43128 | SWPA | 'POPLAR BLUFF 69KV' | 6 | -0.05741 | -0.37387 | 10
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | LACYGNE-PAOLA-WEST GARDER 345KV
Limiting Facility: | WEST GARDNER (WGARD 11) 345/161/13.8KV TRANSFORMER CKT 11
Direction: | From->To
Line Outage: | '57965 W.GRDNR7 345 57977 CRAIG 7 345 1'
Flowgate: | WGAARD1117511579775796513307SP
Date Redispatch Needed: | 6/1/07 - 10/1/07
Season Flowgate Identified: | 2007 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1162650 | 14.8164 | 33.9667
1162651 | 14.5314 | 33.9667
1162654 | 4.6189 | 33.9667
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
KACP | 'MARSHALL 161KV' | 54.1 | 0.02209 | KACP | 'BULL CREEK 161KV' | 119.6306 | 0.35437 | -0.33228 | 102
KACP | 'GRAND AVENUE 161KV' | 65 | 0.06491 | KACP | 'BULL CREEK 161KV' | 119.6306 | 0.35437 | -0.28946 | 117
KACP | 'NORTHEAST 13KV' | 56 | 0.06338 | KACP | 'BULL CREEK 161KV' | 119.6306 | 0.35437 | -0.29099 | 117
KACP | 'NORTHEAST 13KV' | 56 | 0.06338 | KACP | 'BULL CREEK 161KV' | 119.6306 | 0.35437 | -0.29099 | 117
KACP | 'NORTHEAST 13KV' | 58 | 0.06338 | KACP | 'BULL CREEK 161KV' | 119.6306 | 0.35437 | -0.29099 | 117
KACP | 'NORTHEAST 13KV' | 59 | 0.06338 | KACP | 'BULL CREEK 161KV' | 119.6306 | 0.35437 | -0.29099 | 117
KACP | 'NORTHEAST 161KV' | 55 | 0.06338 | KACP | 'BULL CREEK 161KV' | 119.6306 | 0.35437 | -0.29099 | 117
KACP | 'NORTHEAST 161KV' | 58 | 0.06338 | KACP | 'BULL CREEK 161KV' | 119.6306 | 0.35437 | -0.29099 | 117
KACP | 'NORTHEAST 161KV' | 58 | 0.06338 | KACP | 'BULL CREEK 161KV' | 119.6306 | 0.35437 | -0.29099 | 117
KACP | 'NORTHEAST 161KV' | 58 | 0.06338 | KACP | 'BULL CREEK 161KV' | 119.6306 | 0.35437 | -0.29099 | 117
KACP | 'PAOLA COMBUSTION TURBINES 161KV' | 77 | 0.10111 | KACP | 'BULL CREEK 161KV' | 119.6306 | 0.35437 | -0.25326 | 134
WERE | 'CLR_3 .575 34KV' | 300 | -0.0501 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.03101 | -0.08111 | 419
WERE | 'LATHAM1234.0 345KV' | 150 | -0.0501 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.03101 | -0.08111 | 419
WERE | 'CLR_3 .575 34KV' | 300 | -0.0501 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 225.3871 | 0.0297 | -0.0798 | 426
WERE | 'LATHAM1234.0 345KV' | 150 | -0.0501 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 225.3871 | 0.0297 | -0.0798 | 426
WERE | 'CLR_3 .575 34KV' | 300 | -0.0501 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.02895 | -0.07905 | 430
WERE | 'LATHAM1234.0 345KV' | 150 | -0.0501 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.02895 | -0.07905 | 430
WERE | 'EVANS ENERGY CENTER 138KV' | 174.7754 | -0.04048 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.03101 | -0.07149 | 475
WERE | 'EVANS N4 138 16KV' | 360 | -0.04047 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.03101 | -0.07148 | 475
WERE | 'EVANS ENERGY CENTER 138KV' | 174.7754 | -0.04048 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 225.3871 | 0.0297 | -0.07018 | 484
WERE | 'EVANS N4 138 16KV' | 360 | -0.04047 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 225.3871 | 0.0297 | -0.07017 | 484
WERE | 'EVANS ENERGY CENTER 138KV' | 174.7754 | -0.04048 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.02895 | -0.06943 | 489
WERE | 'EVANS N4 138 16KV' | 360 | -0.04047 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.02895 | -0.06942 | 489
WERE | 'LYONS 115KV' | 999 | -0.01311 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.03101 | -0.04412 | 770
WERE | 'LYONS 115KV' | 999 | -0.01311 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.02895 | -0.04206 | 808
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | LACYGNE-PAOLA-WEST GARDER 345KV
Limiting Facility: | WEST GARDNER (WGARD 11) 345/161/13.8KV TRANSFORMER CKT 11
Direction: | From->To
Line Outage: | '57965 W.GRDNR7 345 57977 CRAIG 7 345 1'
Flowgate: | WGAARD1127511579775796511307SH
Date Redispatch Needed: | 6/1 - 10/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 Summer Shoulder
Reservation | Relief Amount | Aggregate Relief Amount
1162649 | 7.0033 | 14.7433
1162685 | 3.87 | 14.7433
1162686 | 3.87 | 14.7433
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
KACP | 'BULL CREEK 161KV' | 308 | -0.35437 | KACP | 'LACYGNE UNIT 345KV' | 958 | 0.1266 | -0.48097 | 31
KACP | 'BULL CREEK 161KV' | 308 | -0.35437 | KACP | 'SPEARVILLE WIND 34KV' | 101 | -0.01118 | -0.34319 | 43
KACP | 'BULL CREEK 161KV' | 308 | -0.35437 | KACP | 'MONTROSE 161KV' | 355.9788 | -0.03298 | -0.32139 | 46
KACP | 'BULL CREEK 161KV' | 308 | -0.35437 | KACP | 'HAWTHORN 161KV' | 45.4241 | -0.05555 | -0.29882 | 49
KACP | 'BULL CREEK 161KV' | 308 | -0.35437 | KACP | 'HAWTHORN 161KV' | 455 | -0.05555 | -0.29882 | 49
KACP | 'BULL CREEK 161KV' | 308 | -0.35437 | KACP | 'IATAN 345KV' | 396 | -0.0586 | -0.29577 | 50
KACP | 'PAOLA COMBUSTION TURBINES 161KV' | 77 | -0.10111 | KACP | 'LACYGNE UNIT 345KV' | 958 | 0.1266 | -0.22771 | 65
KACP | 'GRAND AVENUE 161KV' | 65 | -0.06491 | KACP | 'LACYGNE UNIT 345KV' | 958 | 0.1266 | -0.19151 | 77
KACP | 'NORTHEAST 13KV' | 56 | -0.06338 | KACP | 'LACYGNE UNIT 345KV' | 958 | 0.1266 | -0.18998 | 78
KACP | 'NORTHEAST 13KV' | 56 | -0.06338 | KACP | 'LACYGNE UNIT 345KV' | 958 | 0.1266 | -0.18998 | 78
KACP | 'NORTHEAST 13KV' | 58 | -0.06338 | KACP | 'LACYGNE UNIT 345KV' | 958 | 0.1266 | -0.18998 | 78
KACP | 'NORTHEAST 13KV' | 59 | -0.06338 | KACP | 'LACYGNE UNIT 345KV' | 958 | 0.1266 | -0.18998 | 78
KACP | 'NORTHEAST 161KV' | 55 | -0.06338 | KACP | 'LACYGNE UNIT 345KV' | 958 | 0.1266 | -0.18998 | 78
KACP | 'NORTHEAST 161KV' | 58 | -0.06338 | KACP | 'LACYGNE UNIT 345KV' | 958 | 0.1266 | -0.18998 | 78
KACP | 'NORTHEAST 161KV' | 58 | -0.06338 | KACP | 'LACYGNE UNIT 345KV' | 958 | 0.1266 | -0.18998 | 78
KACP | 'NORTHEAST 161KV' | 58 | -0.06338 | KACP | 'LACYGNE UNIT 345KV' | 958 | 0.1266 | -0.18998 | 78
KACP | 'HAWTHORN 161KV' | 268.5759 | -0.05555 | KACP | 'LACYGNE UNIT 345KV' | 958 | 0.1266 | -0.18215 | 81
KACP | 'CITY OF HIGGINSVILLE 69KV' | 36 | -0.02828 | KACP | 'LACYGNE UNIT 345KV' | 958 | 0.1266 | -0.15488 | 95
KACP | 'MARSHALL 161KV' | 54.1 | -0.02207 | KACP | 'LACYGNE UNIT 345KV' | 958 | 0.1266 | -0.14867 | 99
KACP | 'PAOLA COMBUSTION TURBINES 161KV' | 77 | -0.10111 | KACP | 'SPEARVILLE WIND 34KV' | 101 | -0.01118 | -0.08993 | 164
WERE | 'LAWRENCE ENERGY CENTER 115KV' | 78 | -0.03527 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | 0.04133 | -0.0766 | 192
WERE | 'LAWRENCE ENERGY CENTER 115KV' | 78 | -0.03527 | WERE | 'EVANS ENERGY CENTER 138KV' | 305 | 0.04047 | -0.07574 | 195
KACP | 'PAOLA COMBUSTION TURBINES 161KV' | 77 | -0.10111 | KACP | 'MONTROSE 161KV' | 355.9788 | -0.03298 | -0.06813 | 216
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.01905 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | 0.04133 | -0.06038 | 244
WERE | 'KNOLL 3 115 115KV' | 84.36 | -0.01845 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | 0.04133 | -0.05978 | 247
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.01905 | WERE | 'EVANS ENERGY CENTER 138KV' | 305 | 0.04047 | -0.05952 | 248
WERE | 'KNOLL 3 115 115KV' | 84.36 | -0.01845 | WERE | 'EVANS ENERGY CENTER 138KV' | 305 | 0.04047 | -0.05892 | 250
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 275.2344 | -0.01721 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | 0.04133 | -0.05854 | 252
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 275.2344 | -0.01721 | WERE | 'EVANS ENERGY CENTER 138KV' | 305 | 0.04047 | -0.05768 | 256
WERE | 'PAWNEE 115KV' | 999 | -0.00886 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | 0.04133 | -0.05019 | 294
WERE | 'RICE 115KV' | 999 | -0.00886 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | 0.04133 | -0.05019 | 294
WERE | 'PAWNEE 115KV' | 999 | -0.00886 | WERE | 'EVANS ENERGY CENTER 138KV' | 305 | 0.04047 | -0.04933 | 299
WERE | 'RICE 115KV' | 999 | -0.00886 | WERE | 'EVANS ENERGY CENTER 138KV' | 305 | 0.04047 | -0.04933 | 299
WERE | 'LANG 7 345 345KV' | 828 | -0.0039 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | 0.04133 | -0.04523 | 326
WERE | 'LANG 7 345 345KV' | 828 | -0.0039 | WERE | 'EVANS ENERGY CENTER 138KV' | 305 | 0.04047 | -0.04437 | 332
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | LINWOOD - MCWILLIE STREET 138KV CKT 1
Limiting Facility: | LINWOOD - MCWILLIE STREET 138KV CKT 1
Direction: | From->To
Line Outage: | HARTS ISLAND - SOUTH SHREVEPORT 138KV CKT 1
Flowgate: | 53422534281534145344611407SP
Date Redispatch Needed: | 6/1/07 - 10/1/07
Season Flowgate Identified: | 2007 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1158760 | 5.8368 | 5.8368
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.50272 | AEPW | 'AEP-CT0613.8 161KV' | 160 | -0.00343 | -0.49929 | 12
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.50272 | AEPW | 'COGENTRIX 345KV' | 300 | -0.00416 | -0.49856 | 12
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.50272 | AEPW | 'COMANCHE 138KV' | 160 | -0.00553 | -0.49719 | 12
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.50272 | AEPW | 'COMANCHE 69KV' | 63 | -0.00554 | -0.49718 | 12
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.50272 | AEPW | 'EASTMAN 138KV' | 355 | -0.0127 | -0.49002 | 12
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.50272 | AEPW | 'FITZHUGH 161KV' | 31 | -0.00241 | -0.50031 | 12
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.50272 | AEPW | 'FLINT CREEK 161KV' | 420 | -0.00346 | -0.49926 | 12
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.50272 | AEPW | 'KNOXLEE 138KV' | 164 | -0.00881 | -0.49391 | 12
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.50272 | AEPW | 'L&D13 69KV' | 11 | -0.00278 | -0.49994 | 12
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.50272 | AEPW | 'LEBROCK 345KV' | 515 | -0.0179 | -0.48482 | 12
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.50272 | AEPW | 'NARROWS 69KV' | 22 | -0.01482 | -0.4879 | 12
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.50272 | AEPW | 'NORTHEASTERN STATION 138KV' | 95 | -0.00386 | -0.49886 | 12
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.50272 | AEPW | 'NORTHEASTERN STATION 138KV' | 405 | -0.00386 | -0.49886 | 12
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.50272 | AEPW | 'NORTHEASTERN STATION 345KV' | 645 | -0.00384 | -0.49888 | 12
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.50272 | AEPW | 'OEC 345KV' | 369 | -0.00404 | -0.49868 | 12
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.50272 | AEPW | 'PIRKEY GENERATION 138KV' | 475 | -0.02418 | -0.47854 | 12
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.50272 | AEPW | 'RIVERSIDE STATION 138KV' | 495.5 | -0.00417 | -0.49855 | 12
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.50272 | AEPW | 'SOUTHWESTERN STATION 138KV' | 257 | -0.00547 | -0.49725 | 12
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.50272 | AEPW | 'TULSA POWER STATION 138KV' | 77 | -0.00413 | -0.49859 | 12
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.50272 | AEPW | 'TULSA POWER STATION 138KV' | 75 | -0.00413 | -0.49859 | 12
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.50272 | AEPW | 'WEATHERFORD 34KV' | 148 | -0.00519 | -0.49753 | 12
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.50272 | AEPW | 'WELEETKA 138KV' | 70 | -0.00504 | -0.49768 | 12
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.50272 | AEPW | 'WELSH 345KV' | 990 | -0.01226 | -0.49046 | 12
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.50272 | AEPW | 'WILKES 138KV' | 189.1239 | -0.02818 | -0.47454 | 12
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.50272 | AEPW | 'WILKES 345KV' | 286.3495 | -0.01614 | -0.48658 | 12
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.36037 | AEPW | 'AEP-CT0613.8 161KV' | 160 | -0.00343 | -0.35694 | 16
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.36037 | AEPW | 'COGENTRIX 345KV' | 300 | -0.00416 | -0.35621 | 16
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.36037 | AEPW | 'COMANCHE 138KV' | 160 | -0.00553 | -0.35484 | 16
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.36037 | AEPW | 'COMANCHE 69KV' | 63 | -0.00554 | -0.35483 | 16
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.36037 | AEPW | 'FITZHUGH 161KV' | 31 | -0.00241 | -0.35796 | 16
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.36037 | AEPW | 'FLINT CREEK 161KV' | 420 | -0.00346 | -0.35691 | 16
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.36037 | AEPW | 'L&D13 69KV' | 11 | -0.00278 | -0.35759 | 16
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.36037 | AEPW | 'NORTHEASTERN STATION 138KV' | 95 | -0.00386 | -0.35651 | 16
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.36037 | AEPW | 'NORTHEASTERN STATION 138KV' | 405 | -0.00386 | -0.35651 | 16
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.36037 | AEPW | 'NORTHEASTERN STATION 345KV' | 645 | -0.00384 | -0.35653 | 16
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.36037 | AEPW | 'OEC 345KV' | 369 | -0.00404 | -0.35633 | 16
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.36037 | AEPW | 'RIVERSIDE STATION 138KV' | 495.5 | -0.00417 | -0.3562 | 16
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.36037 | AEPW | 'SOUTHWESTERN STATION 138KV' | 257 | -0.00547 | -0.3549 | 16
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.36037 | AEPW | 'TULSA POWER STATION 138KV' | 77 | -0.00413 | -0.35624 | 16
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.36037 | AEPW | 'TULSA POWER STATION 138KV' | 75 | -0.00413 | -0.35624 | 16
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.36037 | AEPW | 'WEATHERFORD 34KV' | 148 | -0.00519 | -0.35518 | 16
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.36037 | AEPW | 'WELEETKA 138KV' | 70 | -0.00504 | -0.35533 | 16
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.36037 | AEPW | 'EASTMAN 138KV' | 355 | -0.0127 | -0.34767 | 17
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.36037 | AEPW | 'KNOXLEE 138KV' | 164 | -0.00881 | -0.35156 | 17
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.36037 | AEPW | 'LEBROCK 345KV' | 515 | -0.0179 | -0.34247 | 17
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.36037 | AEPW | 'NARROWS 69KV' | 22 | -0.01482 | -0.34555 | 17
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.36037 | AEPW | 'PIRKEY GENERATION 138KV' | 475 | -0.02418 | -0.33619 | 17
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.36037 | AEPW | 'WELSH 345KV' | 990 | -0.01226 | -0.34811 | 17
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.36037 | AEPW | 'WILKES 345KV' | 286.3495 | -0.01614 | -0.34423 | 17
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.36037 | AEPW | 'WILKES 138KV' | 189.1239 | -0.02818 | -0.33219 | 18
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.50272 | AEPW | 'LIEBERMAN 138KV' | 74 | -0.21155 | -0.29117 | 20
AEPW | 'LIEBERMAN 138KV' | 154 | -0.21155 | AEPW | 'AEP-CT0613.8 161KV' | 160 | -0.00343 | -0.20812 | 28
AEPW | 'LIEBERMAN 138KV' | 154 | -0.21155 | AEPW | 'COGENTRIX 345KV' | 300 | -0.00416 | -0.20739 | 28
AEPW | 'LIEBERMAN 138KV' | 154 | -0.21155 | AEPW | 'COMANCHE 138KV' | 160 | -0.00553 | -0.20602 | 28
AEPW | 'LIEBERMAN 138KV' | 154 | -0.21155 | AEPW | 'COMANCHE 69KV' | 63 | -0.00554 | -0.20601 | 28
AEPW | 'LIEBERMAN 138KV' | 154 | -0.21155 | AEPW | 'FITZHUGH 161KV' | 31 | -0.00241 | -0.20914 | 28
AEPW | 'LIEBERMAN 138KV' | 154 | -0.21155 | AEPW | 'FLINT CREEK 161KV' | 420 | -0.00346 | -0.20809 | 28
AEPW | 'LIEBERMAN 138KV' | 154 | -0.21155 | AEPW | 'L&D13 69KV' | 11 | -0.00278 | -0.20877 | 28
AEPW | 'LIEBERMAN 138KV' | 154 | -0.21155 | AEPW | 'NORTHEASTERN STATION 138KV' | 95 | -0.00386 | -0.20769 | 28
AEPW | 'LIEBERMAN 138KV' | 154 | -0.21155 | AEPW | 'NORTHEASTERN STATION 138KV' | 405 | -0.00386 | -0.20769 | 28
AEPW | 'LIEBERMAN 138KV' | 154 | -0.21155 | AEPW | 'NORTHEASTERN STATION 345KV' | 645 | -0.00384 | -0.20771 | 28
AEPW | 'LIEBERMAN 138KV' | 154 | -0.21155 | AEPW | 'OEC 345KV' | 369 | -0.00404 | -0.20751 | 28
AEPW | 'LIEBERMAN 138KV' | 154 | -0.21155 | AEPW | 'RIVERSIDE STATION 138KV' | 495.5 | -0.00417 | -0.20738 | 28
AEPW | 'LIEBERMAN 138KV' | 154 | -0.21155 | AEPW | 'SOUTHWESTERN STATION 138KV' | 257 | -0.00547 | -0.20608 | 28
AEPW | 'LIEBERMAN 138KV' | 154 | -0.21155 | AEPW | 'TULSA POWER STATION 138KV' | 75 | -0.00413 | -0.20742 | 28
AEPW | 'LIEBERMAN 138KV' | 154 | -0.21155 | AEPW | 'TULSA POWER STATION 138KV' | 77 | -0.00413 | -0.20742 | 28
AEPW | 'LIEBERMAN 138KV' | 154 | -0.21155 | AEPW | 'WEATHERFORD 34KV' | 148 | -0.00519 | -0.20636 | 28
AEPW | 'LIEBERMAN 138KV' | 154 | -0.21155 | AEPW | 'WELEETKA 138KV' | 70 | -0.00504 | -0.20651 | 28
AEPW | 'LIEBERMAN 138KV' | 154 | -0.21155 | AEPW | 'EASTMAN 138KV' | 355 | -0.0127 | -0.19885 | 29
AEPW | 'LIEBERMAN 138KV' | 154 | -0.21155 | AEPW | 'KNOXLEE 138KV' | 164 | -0.00881 | -0.20274 | 29
AEPW | 'LIEBERMAN 138KV' | 154 | -0.21155 | AEPW | 'WELSH 345KV' | 990 | -0.01226 | -0.19929 | 29
AEPW | 'LIEBERMAN 138KV' | 154 | -0.21155 | AEPW | 'LEBROCK 345KV' | 515 | -0.0179 | -0.19365 | 30
AEPW | 'LIEBERMAN 138KV' | 154 | -0.21155 | AEPW | 'NARROWS 69KV' | 22 | -0.01482 | -0.19673 | 30
AEPW | 'LIEBERMAN 138KV' | 154 | -0.21155 | AEPW | 'WILKES 345KV' | 286.3495 | -0.01614 | -0.19541 | 30
AEPW | 'LIEBERMAN 138KV' | 154 | -0.21155 | AEPW | 'PIRKEY GENERATION 138KV' | 475 | -0.02418 | -0.18737 | 31
AEPW | 'LIEBERMAN 138KV' | 154 | -0.21155 | AEPW | 'WILKES 138KV' | 189.1239 | -0.02818 | -0.18337 | 32
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.36037 | AEPW | 'LIEBERMAN 138KV' | 74 | -0.21155 | -0.14882 | 39
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1
Limiting Facility: | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1
Direction: | To->From
Line Outage: | '59198 PECULR 7 345 59200 PHILL 7 345 1'
Flowgate: | 59210592591591985920013107SP
Date Redispatch Needed: | 6/1/07 - 10/1/07
Season Flowgate Identified: | 2007 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1162649 | 4.2612 | 4.2612
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
MIPU | 'ARIES 161KV' | 295 | -0.0451 | MIPU | 'SOUTH HARPER 161KV' | 315 | 0.39783 | -0.44293 | 10
MIPU | 'GREENWOOD 161KV' | 218.4158 | -0.04811 | MIPU | 'SOUTH HARPER 161KV' | 315 | 0.39783 | -0.44594 | 10
MIPU | 'LAKE ROAD 161KV' | 91 | -0.01573 | MIPU | 'SOUTH HARPER 161KV' | 315 | 0.39783 | -0.41356 | 10
MIPU | 'NEVADA 69KV' | 20.3 | -0.01068 | MIPU | 'SOUTH HARPER 161KV' | 315 | 0.39783 | -0.40851 | 10
MIPU | 'SIBLEY 161KV' | 15.2387 | -0.0335 | MIPU | 'SOUTH HARPER 161KV' | 315 | 0.39783 | -0.43133 | 10
MIPU | 'TWA 161KV' | 32.1 | -0.02448 | MIPU | 'SOUTH HARPER 161KV' | 315 | 0.39783 | -0.42231 | 10
MIPU | 'RALPH GREEN 69KV' | 73.7 | 0.07367 | MIPU | 'SOUTH HARPER 161KV' | 315 | 0.39783 | -0.32416 | 13
KACP | 'NORTHEAST 13KV' | 33.1631 | -0.02906 | KACP | 'LACYGNE UNIT 345KV' | 958 | 0.04156 | -0.07062 | 60
KACP | 'NORTHEAST 13KV' | 58 | -0.02906 | KACP | 'LACYGNE UNIT 345KV' | 958 | 0.04156 | -0.07062 | 60
KACP | 'NORTHEAST 13KV' | 59 | -0.02906 | KACP | 'LACYGNE UNIT 345KV' | 958 | 0.04156 | -0.07062 | 60
KACP | 'NORTHEAST 161KV' | 58 | -0.02906 | KACP | 'LACYGNE UNIT 345KV' | 958 | 0.04156 | -0.07062 | 60
KACP | 'NORTHEAST 161KV' | 58 | -0.02906 | KACP | 'LACYGNE UNIT 345KV' | 958 | 0.04156 | -0.07062 | 60
KACP | 'NORTHEAST 161KV' | 58 | -0.02906 | KACP | 'LACYGNE UNIT 345KV' | 958 | 0.04156 | -0.07062 | 60
KACP | 'GRAND AVENUE 161KV' | 65 | -0.02871 | KACP | 'LACYGNE UNIT 345KV' | 958 | 0.04156 | -0.07027 | 61
KACP | 'MONTROSE 161KV' | 23.8539 | -0.02083 | KACP | 'LACYGNE UNIT 345KV' | 958 | 0.04156 | -0.06239 | 68
KACP | 'MARSHALL 161KV' | 54.1 | -0.01571 | KACP | 'LACYGNE UNIT 345KV' | 958 | 0.04156 | -0.05727 | 74
KACP | 'NORTHEAST 13KV' | 58 | -0.02906 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.0113 | -0.04036 | 106
KACP | 'NORTHEAST 13KV' | 59 | -0.02906 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.0113 | -0.04036 | 106
KACP | 'NORTHEAST 161KV' | 58 | -0.02906 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.0113 | -0.04036 | 106
KACP | 'NORTHEAST 161KV' | 58 | -0.02906 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.0113 | -0.04036 | 106
KACP | 'NORTHEAST 161KV' | 58 | -0.02906 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.0113 | -0.04036 | 106
KACP | 'GRAND AVENUE 161KV' | 65 | -0.02871 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.0113 | -0.04001 | 107
MIPU | 'GREENWOOD 161KV' | 218.4158 | -0.04811 | MIPU | 'LAKE ROAD 34KV' | 92 | -0.01573 | -0.03238 | 132
KACP | 'NORTHEAST 13KV' | 58 | -0.02906 | KACP | 'PAOLA COMBUSTION TURBINES 161KV' | 77 | 0.00149 | -0.03055 | 139
KACP | 'NORTHEAST 13KV' | 59 | -0.02906 | KACP | 'PAOLA COMBUSTION TURBINES 161KV' | 77 | 0.00149 | -0.03055 | 139
KACP | 'NORTHEAST 161KV' | 58 | -0.02906 | KACP | 'PAOLA COMBUSTION TURBINES 161KV' | 77 | 0.00149 | -0.03055 | 139
KACP | 'NORTHEAST 161KV' | 58 | -0.02906 | KACP | 'PAOLA COMBUSTION TURBINES 161KV' | 77 | 0.00149 | -0.03055 | 139
KACP | 'NORTHEAST 161KV' | 58 | -0.02906 | KACP | 'PAOLA COMBUSTION TURBINES 161KV' | 77 | 0.00149 | -0.03055 | 139
KACP | 'GRAND AVENUE 161KV' | 65 | -0.02871 | KACP | 'PAOLA COMBUSTION TURBINES 161KV' | 77 | 0.00149 | -0.0302 | 141
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1
Limiting Facility: | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1
Direction: | To->From
Line Outage: | '59198 PECULR 7 345 59200 PHILL 7 345 1'
Flowgate: | 59210592591591985920013108SP
Date Redispatch Needed: | Starting 2008 6/1 - 10/1 Until EOC of Upgrade
Season Flowgate Identified: | 2008 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1162649 | 4.2258 | 4.2258
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
MIPU | 'GREENWOOD 161KV' | 188.8042 | -0.04796 | MIPU | 'SOUTH HARPER 161KV' | 315 | 0.3981 | -0.44606 | 9
MIPU | 'ARIES 161KV' | 295 | -0.04495 | MIPU | 'SOUTH HARPER 161KV' | 315 | 0.3981 | -0.44305 | 10
MIPU | 'LAKE ROAD 161KV' | 91 | -0.01636 | MIPU | 'SOUTH HARPER 161KV' | 315 | 0.3981 | -0.41446 | 10
MIPU | 'NEVADA 69KV' | 20.3 | -0.01034 | MIPU | 'SOUTH HARPER 161KV' | 315 | 0.3981 | -0.40844 | 10
MIPU | 'SIBLEY 161KV' | 20.6431 | -0.03357 | MIPU | 'SOUTH HARPER 161KV' | 315 | 0.3981 | -0.43167 | 10
MIPU | 'TWA 161KV' | 32.1 | -0.02459 | MIPU | 'SOUTH HARPER 161KV' | 315 | 0.3981 | -0.42269 | 10
MIPU | 'RALPH GREEN 69KV' | 73.7 | 0.07389 | MIPU | 'SOUTH HARPER 161KV' | 315 | 0.3981 | -0.32421 | 13
KACP | 'NORTHEAST 13KV' | 36 | -0.02926 | KACP | 'LACYGNE UNIT 345KV' | 958 | 0.04079 | -0.07005 | 60
KACP | 'NORTHEAST 13KV' | 58 | -0.02926 | KACP | 'LACYGNE UNIT 345KV' | 958 | 0.04079 | -0.07005 | 60
KACP | 'NORTHEAST 13KV' | 59 | -0.02926 | KACP | 'LACYGNE UNIT 345KV' | 958 | 0.04079 | -0.07005 | 60
KACP | 'NORTHEAST 161KV' | 58 | -0.02926 | KACP | 'LACYGNE UNIT 345KV' | 958 | 0.04079 | -0.07005 | 60
KACP | 'NORTHEAST 161KV' | 58 | -0.02926 | KACP | 'LACYGNE UNIT 345KV' | 958 | 0.04079 | -0.07005 | 60
KACP | 'NORTHEAST 161KV' | 58 | -0.02926 | KACP | 'LACYGNE UNIT 345KV' | 958 | 0.04079 | -0.07005 | 60
KACP | 'GRAND AVENUE 161KV' | 65 | -0.02892 | KACP | 'LACYGNE UNIT 345KV' | 958 | 0.04079 | -0.06971 | 61
KACP | 'MONTROSE 161KV' | 24.8651 | -0.02053 | KACP | 'LACYGNE UNIT 345KV' | 958 | 0.04079 | -0.06132 | 69
KACP | 'MARSHALL 161KV' | 54.1 | -0.01573 | KACP | 'LACYGNE UNIT 345KV' | 958 | 0.04079 | -0.05652 | 75
KACP | 'NORTHEAST 13KV' | 36 | -0.02926 | KACP | 'PAOLA COMBUSTION TURBINES 161KV' | 77 | 0.01241 | -0.04167 | 101
KACP | 'NORTHEAST 13KV' | 58 | -0.02926 | KACP | 'PAOLA COMBUSTION TURBINES 161KV' | 77 | 0.01241 | -0.04167 | 101
KACP | 'NORTHEAST 13KV' | 59 | -0.02926 | KACP | 'PAOLA COMBUSTION TURBINES 161KV' | 77 | 0.01241 | -0.04167 | 101
KACP | 'NORTHEAST 161KV' | 58 | -0.02926 | KACP | 'PAOLA COMBUSTION TURBINES 161KV' | 77 | 0.01241 | -0.04167 | 101
KACP | 'NORTHEAST 161KV' | 58 | -0.02926 | KACP | 'PAOLA COMBUSTION TURBINES 161KV' | 77 | 0.01241 | -0.04167 | 101
KACP | 'NORTHEAST 161KV' | 58 | -0.02926 | KACP | 'PAOLA COMBUSTION TURBINES 161KV' | 77 | 0.01241 | -0.04167 | 101
KACP | 'GRAND AVENUE 161KV' | 65 | -0.02892 | KACP | 'PAOLA COMBUSTION TURBINES 161KV' | 77 | 0.01241 | -0.04133 | 102
KACP | 'GRAND AVENUE 161KV' | 65 | -0.02892 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.01116 | -0.04008 | 105
KACP | 'NORTHEAST 13KV' | 36 | -0.02926 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.01116 | -0.04042 | 105
KACP | 'NORTHEAST 13KV' | 58 | -0.02926 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.01116 | -0.04042 | 105
KACP | 'NORTHEAST 13KV' | 59 | -0.02926 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.01116 | -0.04042 | 105
KACP | 'NORTHEAST 161KV' | 58 | -0.02926 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.01116 | -0.04042 | 105
KACP | 'NORTHEAST 161KV' | 58 | -0.02926 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.01116 | -0.04042 | 105
KACP | 'NORTHEAST 161KV' | 58 | -0.02926 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.01116 | -0.04042 | 105
MIPU | 'GREENWOOD 161KV' | 188.8042 | -0.04796 | MIPU | 'LAKE ROAD 34KV' | 92 | -0.01636 | -0.0316 | 134
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1
Limiting Facility: | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1
Direction: | To->From
Line Outage: | '59198 PECULR 7 345 59200 PHILL 7 345 1'
Flowgate: | 59210592591591985920013406WP
Date Redispatch Needed: | 12/1/06 - 4/1/07
Season Flowgate Identified: | 2006 Winter Peak
Reservation | Relief Amount | Aggregate Relief Amount
1162649 | 4.2228 | 4.2228
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
MIPU | 'GREENWOOD 161KV' | 247.4621 | -0.04821 | MIPU | 'SOUTH HARPER 161KV' | 315 | 0.39791 | -0.44612 | 9
MIPU | 'ARIES 161KV' | 595 | -0.0452 | MIPU | 'SOUTH HARPER 161KV' | 315 | 0.39791 | -0.44311 | 10
MIPU | 'LAKE ROAD 161KV' | 91 | -0.01588 | MIPU | 'SOUTH HARPER 161KV' | 315 | 0.39791 | -0.41379 | 10
MIPU | 'NEVADA 69KV' | 20.3 | -0.01075 | MIPU | 'SOUTH HARPER 161KV' | 315 | 0.39791 | -0.40866 | 10
MIPU | 'SIBLEY 161KV' | 13.3699 | -0.03368 | MIPU | 'SOUTH HARPER 161KV' | 315 | 0.39791 | -0.43159 | 10
MIPU | 'TWA 161KV' | 32.1 | -0.02461 | MIPU | 'SOUTH HARPER 161KV' | 315 | 0.39791 | -0.42252 | 10
MIPU | 'RALPH GREEN 69KV' | 73.7 | 0.0736 | MIPU | 'SOUTH HARPER 161KV' | 315 | 0.39791 | -0.32431 | 13
KACP | 'HAWTHORN 161KV' | 423 | -0.03195 | KACP | 'LACYGNE UNIT 345KV' | 962 | 0.04166 | -0.07361 | 57
KACP | 'NORTHEAST 13KV' | 56 | -0.02939 | KACP | 'LACYGNE UNIT 345KV' | 962 | 0.04166 | -0.07105 | 59
KACP | 'NORTHEAST 13KV' | 56 | -0.02939 | KACP | 'LACYGNE UNIT 345KV' | 962 | 0.04166 | -0.07105 | 59
KACP | 'NORTHEAST 13KV' | 58 | -0.02939 | KACP | 'LACYGNE UNIT 345KV' | 962 | 0.04166 | -0.07105 | 59
KACP | 'NORTHEAST 13KV' | 59 | -0.02939 | KACP | 'LACYGNE UNIT 345KV' | 962 | 0.04166 | -0.07105 | 59
KACP | 'NORTHEAST 161KV' | 55 | -0.02939 | KACP | 'LACYGNE UNIT 345KV' | 962 | 0.04166 | -0.07105 | 59
KACP | 'NORTHEAST 161KV' | 58 | -0.02939 | KACP | 'LACYGNE UNIT 345KV' | 962 | 0.04166 | -0.07105 | 59
KACP | 'NORTHEAST 161KV' | 58 | -0.02939 | KACP | 'LACYGNE UNIT 345KV' | 962 | 0.04166 | -0.07105 | 59
KACP | 'NORTHEAST 161KV' | 58 | -0.02939 | KACP | 'LACYGNE UNIT 345KV' | 962 | 0.04166 | -0.07105 | 59
KACP | 'GRAND AVENUE 161KV' | 65 | -0.02898 | KACP | 'LACYGNE UNIT 345KV' | 962 | 0.04166 | -0.07064 | 60
KACP | 'MONTROSE 161KV' | 125.9585 | -0.02094 | KACP | 'LACYGNE UNIT 345KV' | 962 | 0.04166 | -0.0626 | 67
KACP | 'CITY OF HIGGINSVILLE 69KV' | 36 | -0.02043 | KACP | 'LACYGNE UNIT 345KV' | 962 | 0.04166 | -0.06209 | 68
KACP | 'MARSHALL 161KV' | 54.1 | -0.01608 | KACP | 'LACYGNE UNIT 345KV' | 962 | 0.04166 | -0.05774 | 73
KACP | 'BULL CREEK 161KV' | 308 | -0.00395 | KACP | 'LACYGNE UNIT 345KV' | 962 | 0.04166 | -0.04561 | 93
KACP | 'HAWTHORN 161KV' | 423 | -0.03195 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.01139 | -0.04334 | 97
KACP | 'NORTHEAST 13KV' | 56 | -0.02939 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.01139 | -0.04078 | 104
KACP | 'NORTHEAST 13KV' | 56 | -0.02939 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.01139 | -0.04078 | 104
KACP | 'NORTHEAST 13KV' | 58 | -0.02939 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.01139 | -0.04078 | 104
KACP | 'NORTHEAST 13KV' | 59 | -0.02939 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.01139 | -0.04078 | 104
KACP | 'NORTHEAST 161KV' | 55 | -0.02939 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.01139 | -0.04078 | 104
KACP | 'NORTHEAST 161KV' | 58 | -0.02939 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.01139 | -0.04078 | 104
KACP | 'NORTHEAST 161KV' | 58 | -0.02939 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.01139 | -0.04078 | 104
KACP | 'NORTHEAST 161KV' | 58 | -0.02939 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.01139 | -0.04078 | 104
KACP | 'GRAND AVENUE 161KV' | 65 | -0.02898 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.01139 | -0.04037 | 105
KACP | 'PAOLA COMBUSTION TURBINES 161KV' | 77 | 0.00156 | KACP | 'LACYGNE UNIT 345KV' | 962 | 0.04166 | -0.0401 | 105
MIPU | 'GREENWOOD 161KV' | 247.4621 | -0.04821 | MIPU | 'LAKE ROAD 34KV' | 92 | -0.01588 | -0.03233 | 131
KACP | 'MONTROSE 161KV' | 125.9585 | -0.02094 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.01139 | -0.03233 | 131
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | MEDICINE LODGE - SUN CITY 115KV CKT 1
Limiting Facility: | MEDICINE LODGE - SUN CITY 115KV CKT 1
Direction: | To->From
Line Outage: | '58779 MULGREN6 230 58795 SPEARVL6 230 1'
Flowgate: | 58773587971587795879511107SH
Date Redispatch Needed: | 6/1 - 10/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 Summer Shoulder
Reservation | Relief Amount | Aggregate Relief Amount
1162649 | 13.2058 | 13.2058
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WEPL | 'HARPER 138KV' | 17.21 | -0.12651 | WEPL | 'GRAY COUNTY WIND FARM 115KV' | 63 | 0.23705 | -0.36356 | 36
WEPL | 'HARPER 138KV' | 17.21 | -0.12651 | WEPL | 'JUDSON LARGE 115KV' | 115.8174 | 0.23871 | -0.36522 | 36
WEPL | 'RUSSELL 115KV' | 27.9 | -0.02558 | WEPL | 'GRAY COUNTY WIND FARM 115KV' | 63 | 0.23705 | -0.26263 | 50
WEPL | 'RUSSELL 115KV' | 27.9 | -0.02558 | WEPL | 'JUDSON LARGE 115KV' | 115.8174 | 0.23871 | -0.26429 | 50
WEPL | 'CLIFTON 115KV' | 23.5006 | -0.00909 | WEPL | 'JUDSON LARGE 115KV' | 115.8174 | 0.23871 | -0.2478 | 53
WEPL | 'CLIFTON 115KV' | 23.5006 | -0.00909 | WEPL | 'GRAY COUNTY WIND FARM 115KV' | 63 | 0.23705 | -0.24614 | 54
KACP | 'BULL CREEK 161KV' | 171.8679 | -0.0048 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12671 | -0.13151 | 100
KACP | 'PAOLA COMBUSTION TURBINES 161KV' | 77 | -0.00476 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12671 | -0.13147 | 100
KACP | 'GRAND AVENUE 161KV' | 65 | -0.00363 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12671 | -0.13034 | 101
KACP | 'NORTHEAST 13KV' | 56 | -0.00359 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12671 | -0.1303 | 101
KACP | 'NORTHEAST 13KV' | 56 | -0.00359 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12671 | -0.1303 | 101
KACP | 'NORTHEAST 13KV' | 58 | -0.00359 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12671 | -0.1303 | 101
KACP | 'NORTHEAST 13KV' | 59 | -0.00359 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12671 | -0.1303 | 101
KACP | 'NORTHEAST 161KV' | 55 | -0.00359 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12671 | -0.1303 | 101
KACP | 'NORTHEAST 161KV' | 58 | -0.00359 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12671 | -0.1303 | 101
KACP | 'NORTHEAST 161KV' | 58 | -0.00359 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12671 | -0.1303 | 101
KACP | 'NORTHEAST 161KV' | 58 | -0.00359 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12671 | -0.1303 | 101
KACP | 'CITY OF HIGGINSVILLE 69KV' | 36 | -0.00293 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12671 | -0.12964 | 102
KACP | 'MARSHALL 161KV' | 54.1 | -0.00187 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12671 | -0.12858 | 103
WEPL | 'CIMARRON RIVER 115KV' | 72 | 0.14609 | WEPL | 'JUDSON LARGE 115KV' | 115.8174 | 0.23871 | -0.09262 | 143
WEPL | 'CIMARRON RIVER 115KV' | 72 | 0.14609 | WEPL | 'GRAY COUNTY WIND FARM 115KV' | 63 | 0.23705 | -0.09096 | 145
WERE | 'PAWNEE 115KV' | 999 | -0.09134 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | -0.00663 | -0.08471 | 156
WERE | 'RICE 115KV' | 999 | -0.09134 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | -0.00663 | -0.08471 | 156
WERE | 'PAWNEE 115KV' | 999 | -0.09134 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 219.1565 | -0.00701 | -0.08433 | 157
WERE | 'PAWNEE 115KV' | 999 | -0.09134 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | -0.00734 | -0.084 | 157
WERE | 'RICE 115KV' | 999 | -0.09134 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 219.1565 | -0.00701 | -0.08433 | 157
WERE | 'RICE 115KV' | 999 | -0.09134 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | -0.00734 | -0.084 | 157
WERE | 'PAWNEE 115KV' | 999 | -0.09134 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | -0.00863 | -0.08271 | 160
WERE | 'PAWNEE 115KV' | 999 | -0.09134 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | -0.00856 | -0.08278 | 160
WERE | 'RICE 115KV' | 999 | -0.09134 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | -0.00863 | -0.08271 | 160
WERE | 'RICE 115KV' | 999 | -0.09134 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | -0.00856 | -0.08278 | 160
WERE | 'PAWNEE 115KV' | 999 | -0.09134 | WERE | 'EVANS ENERGY CENTER 138KV' | 340 | -0.0156 | -0.07574 | 174
WERE | 'RICE 115KV' | 999 | -0.09134 | WERE | 'EVANS ENERGY CENTER 138KV' | 340 | -0.0156 | -0.07574 | 174
WERE | 'PAWNEE 115KV' | 999 | -0.09134 | WERE | 'BPU - CITY OF MCPHERSON 115KV' | 127.7656 | -0.02186 | -0.06948 | 190
WERE | 'RICE 115KV' | 999 | -0.09134 | WERE | 'BPU - CITY OF MCPHERSON 115KV' | 127.7656 | -0.02186 | -0.06948 | 190
WERE | 'PAWNEE 115KV' | 999 | -0.09134 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.02483 | -0.06651 | 199
WERE | 'RICE 115KV' | 999 | -0.09134 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.02483 | -0.06651 | 199
WERE | 'PAWNEE 115KV' | 999 | -0.09134 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 120 | -0.02785 | -0.06349 | 208
WERE | 'RICE 115KV' | 999 | -0.09134 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 120 | -0.02785 | -0.06349 | 208
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | MEDICINE LODGE - SUN CITY 115KV CKT 1
Limiting Facility: | MEDICINE LODGE - SUN CITY 115KV CKT 1
Direction: | To->From
Line Outage: | '58779 MULGREN6 230 58795 SPEARVL6 230 1'
Flowgate: | 58773587971587795879511107SP
Date Redispatch Needed: | 6/1/07 - 10/1/07
Season Flowgate Identified: | 2007 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1162649 | 13.2058 | 13.2058
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WEPL | 'HARPER 138KV' | 17.21 | -0.12651 | WEPL | 'GRAY COUNTY WIND FARM 115KV' | 63 | 0.23705 | -0.36356 | 36
WEPL | 'HARPER 138KV' | 17.21 | -0.12651 | WEPL | 'JUDSON LARGE 115KV' | 116.5146 | 0.23871 | -0.36522 | 36
WEPL | 'HARPER 138KV' | 17.21 | -0.12651 | WEPL | 'CIMARRON RIVER 115KV' | 32.223 | 0.14609 | -0.2726 | 48
WEPL | 'RUSSELL 115KV' | 27.9 | -0.02558 | WEPL | 'GRAY COUNTY WIND FARM 115KV' | 63 | 0.23705 | -0.26263 | 50
WEPL | 'RUSSELL 115KV' | 27.9 | -0.02558 | WEPL | 'JUDSON LARGE 115KV' | 116.5146 | 0.23871 | -0.26429 | 50
WEPL | 'RUSSELL 115KV' | 27.9 | -0.02558 | WEPL | 'CIMARRON RIVER 115KV' | 32.223 | 0.14609 | -0.17167 | 77
KACP | 'GRAND AVENUE 161KV' | 65 | -0.00363 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12671 | -0.13034 | 101
KACP | 'NORTHEAST 13KV' | 59 | -0.00359 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12671 | -0.1303 | 101
KACP | 'NORTHEAST 161KV' | 58 | -0.00359 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12671 | -0.1303 | 101
KACP | 'NORTHEAST 161KV' | 58 | -0.00359 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12671 | -0.1303 | 101
KACP | 'MARSHALL 161KV' | 54.1 | -0.00187 | KACP | 'SPEARVILLE WIND 34KV' | 101 | 0.12671 | -0.12858 | 103
WERE | 'PAWNEE 115KV' | 999 | -0.09134 | WERE | 'CHANUTE 69KV' | 56.723 | -0.00543 | -0.08591 | 154
WERE | 'RICE 115KV' | 999 | -0.09134 | WERE | 'CHANUTE 69KV' | 56.723 | -0.00543 | -0.08591 | 154
WERE | 'PAWNEE 115KV' | 999 | -0.09134 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 105 | -0.00663 | -0.08471 | 156
WERE | 'RICE 115KV' | 999 | -0.09134 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 105 | -0.00663 | -0.08471 | 156
WERE | 'PAWNEE 115KV' | 999 | -0.09134 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 229.2843 | -0.00701 | -0.08433 | 157
WERE | 'PAWNEE 115KV' | 999 | -0.09134 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 158 | -0.00734 | -0.084 | 157
WERE | 'RICE 115KV' | 999 | -0.09134 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 229.2843 | -0.00701 | -0.08433 | 157
WERE | 'RICE 115KV' | 999 | -0.09134 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 158 | -0.00734 | -0.084 | 157
WERE | 'PAWNEE 115KV' | 999 | -0.09134 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | -0.00863 | -0.08271 | 160
WERE | 'PAWNEE 115KV' | 999 | -0.09134 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | -0.00856 | -0.08278 | 160
WERE | 'RICE 115KV' | 999 | -0.09134 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | -0.00863 | -0.08271 | 160
WERE | 'RICE 115KV' | 999 | -0.09134 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | -0.00856 | -0.08278 | 160
WERE | 'PAWNEE 115KV' | 999 | -0.09134 | WERE | 'EVANS ENERGY CENTER 138KV' | 565 | -0.0156 | -0.07574 | 174
WERE | 'RICE 115KV' | 999 | -0.09134 | WERE | 'EVANS ENERGY CENTER 138KV' | 565 | -0.0156 | -0.07574 | 174
WERE | 'PAWNEE 115KV' | 999 | -0.09134 | WERE | 'BPU - CITY OF MCPHERSON 115KV' | 152.9351 | -0.02186 | -0.06948 | 190
WERE | 'RICE 115KV' | 999 | -0.09134 | WERE | 'BPU - CITY OF MCPHERSON 115KV' | 152.9351 | -0.02186 | -0.06948 | 190
WERE | 'PAWNEE 115KV' | 999 | -0.09134 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | -0.02213 | -0.06921 | 191
WERE | 'RICE 115KV' | 999 | -0.09134 | WERE | 'GILL ENERGY CENTER 69KV' | 75 | -0.02213 | -0.06921 | 191
WERE | 'PAWNEE 115KV' | 999 | -0.09134 | WERE | 'GILL ENERGY CENTER 138KV' | 171 | -0.02483 | -0.06651 | 199
WERE | 'RICE 115KV' | 999 | -0.09134 | WERE | 'GILL ENERGY CENTER 138KV' | 171 | -0.02483 | -0.06651 | 199
WERE | 'PAWNEE 115KV' | 999 | -0.09134 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 210 | -0.02785 | -0.06349 | 208
WERE | 'RICE 115KV' | 999 | -0.09134 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 210 | -0.02785 | -0.06349 | 208
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER Displacement
Limiting Facility: | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | ROSE HILL (ROSEHL3X) 345/138/13.8KV TRANSFORMER CKT 1
Flowgate: | ROSEHL1X2741ROSESEHL3X7412207SP
Date Redispatch Needed: | 6/1/07 - 10/1/07
Season Flowgate Identified: | 2007 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1161997 | 6.4709 | 6.4709
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'CITY OF MULVANE 69KV' | 7.502 | -0.28341 | WERE | 'CITY OF BURLINGTON 69KV' | 7.8 | 0.045 | -0.32841 | 20
WERE | 'CITY OF MULVANE 69KV' | 7.502 | -0.28341 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.045 | -0.32841 | 20
WERE | 'CITY OF WINFIELD 69KV' | 40 | -0.21371 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.045 | -0.25871 | 25
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21103 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.045 | -0.25603 | 25
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.2085 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.045 | -0.2535 | 26
WERE | 'GETTY 69KV' | 35 | -0.18751 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.045 | -0.23251 | 28
WERE | 'CITY OF WINFIELD 69KV' | 40 | -0.21371 | WERE | 'CITY OF IOLA 69KV' | 24.267 | -0.00501 | -0.2087 | 31
WERE | 'CITY OF WINFIELD 69KV' | 40 | -0.21371 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | -0.00519 | -0.20852 | 31
WERE | 'CITY OF WINFIELD 69KV' | 40 | -0.21371 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | -0.00487 | -0.20884 | 31
WERE | 'CITY OF WINFIELD 69KV' | 40 | -0.21371 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | -0.00262 | -0.21109 | 31
WERE | 'CITY OF WINFIELD 69KV' | 40 | -0.21371 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 235.4582 | -0.00316 | -0.21055 | 31
WERE | 'CITY OF WINFIELD 69KV' | 40 | -0.21371 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 122.7222 | -0.00749 | -0.20622 | 31
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.2085 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | -0.00262 | -0.20588 | 31
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21103 | WERE | 'CITY OF IOLA 69KV' | 24.267 | -0.00501 | -0.20602 | 31
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21103 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | -0.00519 | -0.20584 | 31
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21103 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | -0.00487 | -0.20616 | 31
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21103 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | -0.00262 | -0.20841 | 31
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21103 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 235.4582 | -0.00316 | -0.20787 | 31
WERE | 'CITY OF WINFIELD 69KV' | 40 | -0.21371 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | -0.0094 | -0.20431 | 32
WERE | 'CITY OF WINFIELD 69KV' | 40 | -0.21371 | WERE | 'BPU - CITY OF MCPHERSON 115KV' | 135 | -0.01406 | -0.19965 | 32
WERE | 'CITY OF WINFIELD 69KV' | 40 | -0.21371 | WERE | 'CHANUTE 69KV' | 56.723 | -0.01105 | -0.20266 | 32
WERE | 'CITY OF WINFIELD 69KV' | 40 | -0.21371 | WERE | 'CITY OF ERIE 69KV' | 23.27 | -0.01105 | -0.20266 | 32
WERE | 'CITY OF WINFIELD 69KV' | 40 | -0.21371 | WERE | 'CLAY CENTER JUNCTION 115KV' | 22.939 | -0.00847 | -0.20524 | 32
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.2085 | WERE | 'CITY OF IOLA 69KV' | 24.267 | -0.00501 | -0.20349 | 32
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.2085 | WERE | 'CLAY CENTER JUNCTION 115KV' | 22.939 | -0.00847 | -0.20003 | 32
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.2085 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | -0.00519 | -0.20331 | 32
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.2085 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | -0.00487 | -0.20363 | 32
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.2085 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 235.4582 | -0.00316 | -0.20534 | 32
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.2085 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 122.7222 | -0.00749 | -0.20101 | 32
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21103 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | -0.0094 | -0.20163 | 32
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21103 | WERE | 'CHANUTE 69KV' | 56.723 | -0.01105 | -0.19998 | 32
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21103 | WERE | 'CITY OF ERIE 69KV' | 23.27 | -0.01105 | -0.19998 | 32
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21103 | WERE | 'CLAY CENTER JUNCTION 115KV' | 22.939 | -0.00847 | -0.20256 | 32
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21103 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 122.7222 | -0.00749 | -0.20354 | 32
WERE | 'CITY OF WINFIELD 69KV' | 40 | -0.21371 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 120 | -0.01693 | -0.19678 | 33
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.2085 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | -0.0094 | -0.1991 | 33
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.2085 | WERE | 'BPU - CITY OF MCPHERSON 115KV' | 135 | -0.01406 | -0.19444 | 33
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.2085 | WERE | 'CHANUTE 69KV' | 56.723 | -0.01105 | -0.19745 | 33
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.2085 | WERE | 'CITY OF ERIE 69KV' | 23.27 | -0.01105 | -0.19745 | 33
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21103 | WERE | 'BPU - CITY OF MCPHERSON 115KV' | 135 | -0.01406 | -0.19697 | 33
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21103 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 120 | -0.01693 | -0.1941 | 33
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.2085 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 120 | -0.01693 | -0.19157 | 34
WERE | 'GETTY 69KV' | 35 | -0.18751 | WERE | 'CITY OF IOLA 69KV' | 24.267 | -0.00501 | -0.1825 | 35
WERE | 'GETTY 69KV' | 35 | -0.18751 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | -0.00519 | -0.18232 | 35
WERE | 'GETTY 69KV' | 35 | -0.18751 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | -0.00487 | -0.18264 | 35
WERE | 'GETTY 69KV' | 35 | -0.18751 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | -0.00262 | -0.18489 | 35
WERE | 'GETTY 69KV' | 35 | -0.18751 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 235.4582 | -0.00316 | -0.18435 | 35
WERE | 'GETTY 69KV' | 35 | -0.18751 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | -0.0094 | -0.17811 | 36
WERE | 'GETTY 69KV' | 35 | -0.18751 | WERE | 'CLAY CENTER JUNCTION 115KV' | 22.939 | -0.00847 | -0.17904 | 36
WERE | 'GETTY 69KV' | 35 | -0.18751 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 122.7222 | -0.00749 | -0.18002 | 36
WERE | 'GETTY 69KV' | 35 | -0.18751 | WERE | 'BPU - CITY OF MCPHERSON 115KV' | 135 | -0.01406 | -0.17345 | 37
WERE | 'GETTY 69KV' | 35 | -0.18751 | WERE | 'CHANUTE 69KV' | 56.723 | -0.01105 | -0.17646 | 37
WERE | 'GETTY 69KV' | 35 | -0.18751 | WERE | 'CITY OF ERIE 69KV' | 23.27 | -0.01105 | -0.17646 | 37
WERE | 'GETTY 69KV' | 35 | -0.18751 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 120 | -0.01693 | -0.17058 | 38
WERE | 'EVANS ENERGY CENTER 138KV' | 233 | -0.09828 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.045 | -0.14328 | 45
WERE | 'EVANS N4 138 16KV' | 360 | -0.09763 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.045 | -0.14263 | 45
WEPL | 'HARPER 138KV' | 17.21 | -0.15495 | WEPL | 'CLIFTON 115KV' | 42.8426 | -0.00958 | -0.14537 | 45
WEPL | 'HARPER 138KV' | 17.21 | -0.15495 | WEPL | 'A. M. MULLERGREN GENERATOR 115KV' | 63 | -0.02307 | -0.13188 | 49
WERE | 'CITY OF WINFIELD 69KV' | 40 | -0.21371 | WERE | 'EVANS ENERGY CENTER 138KV' | 340 | -0.09828 | -0.11543 | 56
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21103 | WERE | 'EVANS ENERGY CENTER 138KV' | 340 | -0.09828 | -0.11275 | 57
WERE | 'EVANS ENERGY CENTER 138KV' | 233 | -0.09828 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | -0.00262 | -0.09566 | 68
WERE | 'EVANS ENERGY CENTER 138KV' | 233 | -0.09828 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 235.4582 | -0.00316 | -0.09512 | 68
WERE | 'EVANS N4 138 16KV' | 360 | -0.09763 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | -0.00262 | -0.09501 | 68
WERE | 'EVANS N4 138 16KV' | 360 | -0.09763 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 235.4582 | -0.00316 | -0.09447 | 68
WERE | 'EVANS ENERGY CENTER 138KV' | 233 | -0.09828 | WERE | 'CITY OF IOLA 69KV' | 24.267 | -0.00501 | -0.09327 | 69
WERE | 'EVANS ENERGY CENTER 138KV' | 233 | -0.09828 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | -0.00487 | -0.09341 | 69
WERE | 'EVANS ENERGY CENTER 138KV' | 233 | -0.09828 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | -0.00519 | -0.09309 | 70
WERE | 'EVANS N4 138 16KV' | 360 | -0.09763 | WERE | 'CITY OF IOLA 69KV' | 24.267 | -0.00501 | -0.09262 | 70
WERE | 'EVANS N4 138 16KV' | 360 | -0.09763 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | -0.00519 | -0.09244 | 70
WERE | 'EVANS N4 138 16KV' | 360 | -0.09763 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | -0.00487 | -0.09276 | 70
WERE | 'EVANS ENERGY CENTER 138KV' | 233 | -0.09828 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 122.7222 | -0.00749 | -0.09079 | 71
WERE | 'EVANS N4 138 16KV' | 360 | -0.09763 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 122.7222 | -0.00749 | -0.09014 | 72
WERE | 'EVANS ENERGY CENTER 138KV' | 233 | -0.09828 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | -0.0094 | -0.08888 | 73
WERE | 'EVANS N4 138 16KV' | 360 | -0.09763 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | -0.0094 | -0.08823 | 73
WERE | 'GETTY 69KV' | 35 | -0.18751 | WERE | 'EVANS ENERGY CENTER 138KV' | 340 | -0.09828 | -0.08923 | 73
WERE | 'EVANS ENERGY CENTER 138KV' | 233 | -0.09828 | WERE | 'CHANUTE 69KV' | 56.723 | -0.01105 | -0.08723 | 74
WERE | 'EVANS N4 138 16KV' | 360 | -0.09763 | WERE | 'CHANUTE 69KV' | 56.723 | -0.01105 | -0.08658 | 75
WERE | 'EVANS ENERGY CENTER 138KV' | 233 | -0.09828 | WERE | 'BPU - CITY OF MCPHERSON 115KV' | 135 | -0.01406 | -0.08422 | 77
WERE | 'EVANS N4 138 16KV' | 360 | -0.09763 | WERE | 'BPU - CITY OF MCPHERSON 115KV' | 135 | -0.01406 | -0.08357 | 77
EMDE | 'LARUSSEL 161KV' | 189.4348 | 0.00674 | EMDE | 'ELK RIVER 345KV' | 150 | 0.09044 | -0.0837 | 77
EMDE | 'RIVERTON 161KV' | 216 | 0.0071 | EMDE | 'ELK RIVER 345KV' | 150 | 0.09044 | -0.08334 | 78
EMDE | 'RIVERTON 161KV' | 34 | 0.00776 | EMDE | 'ELK RIVER 345KV' | 150 | 0.09044 | -0.08268 | 78
EMDE | 'STATE LINE 161KV' | 103 | 0.00732 | EMDE | 'ELK RIVER 345KV' | 150 | 0.09044 | -0.08312 | 78
WERE | 'EVANS ENERGY CENTER 138KV' | 233 | -0.09828 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 120 | -0.01693 | -0.08135 | 80
WERE | 'EVANS N4 138 16KV' | 360 | -0.09763 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 120 | -0.01693 | -0.0807 | 80
WERE | 'PAWNEE 115KV' | 999 | -0.04114 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | -0.00262 | -0.03852 | 168
WERE | 'RICE 115KV' | 999 | -0.04114 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | -0.00262 | -0.03852 | 168
WERE | 'PAWNEE 115KV' | 999 | -0.04114 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 235.4582 | -0.00316 | -0.03798 | 170
WERE | 'RICE 115KV' | 999 | -0.04114 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 235.4582 | -0.00316 | -0.03798 | 170
WERE | 'PAWNEE 115KV' | 999 | -0.04114 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | -0.00487 | -0.03627 | 178
WERE | 'RICE 115KV' | 999 | -0.04114 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | -0.00487 | -0.03627 | 178
WERE | 'PAWNEE 115KV' | 999 | -0.04114 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | -0.00519 | -0.03595 | 180
WERE | 'RICE 115KV' | 999 | -0.04114 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | -0.00519 | -0.03595 | 180
WERE | 'PAWNEE 115KV' | 999 | -0.04114 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 122.7222 | -0.00749 | -0.03365 | 192
WERE | 'RICE 115KV' | 999 | -0.04114 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 122.7222 | -0.00749 | -0.03365 | 192
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER Displacement
Limiting Facility: | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | ROSE HILL (ROSEHL3X) 345/138/13.8KV TRANSFORMER CKT 1
Flowgate: | ROSEHL1X2741ROSESEHL3X7414208SP
Date Redispatch Needed: | Starting 2008 6/1 - 10/1 Until EOC of Upgrade
Season Flowgate Identified: | 2008 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1161506 | 11.811 | 25.5345
1161997 | 13.7235 | 25.5345
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'CITY OF WINFIELD 69KV' | 40 | -0.21374 | WERE | 'CLR_3 .575 34KV' | 100 | 0.09039 | -0.30413 | 84
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21109 | WERE | 'CLR_3 .575 34KV' | 100 | 0.09039 | -0.30148 | 85
WERE | 'GETTY 69KV' | 35 | -0.18758 | WERE | 'CLR_3 .575 34KV' | 100 | 0.09039 | -0.27797 | 92
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21109 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | -0.00281 | -0.20828 | 123
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21109 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 264.507 | -0.00335 | -0.20774 | 123
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21109 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | -0.00545 | -0.20564 | 124
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21109 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | -0.00513 | -0.20596 | 124
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21109 | WERE | 'LANG 7 345 345KV' | 310 | -0.00846 | -0.20263 | 126
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21109 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 128 | -0.00769 | -0.2034 | 126
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21109 | WERE | 'CHANUTE 69KV' | 55.637 | -0.01078 | -0.20031 | 127
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21109 | WERE | 'SMOKEY HILLS 34KV' | 51 | -0.01294 | -0.19815 | 129
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21109 | WERE | 'BPU - CITY OF MCPHERSON 115KV' | 135 | -0.01411 | -0.19698 | 130
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21109 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 120 | -0.01678 | -0.19431 | 131
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21109 | WERE | 'KNOLL 3 115 115KV' | 75 | -0.01696 | -0.19413 | 132
WERE | 'EVANS ENERGY CENTER 138KV' | 421.6074 | -0.09836 | WERE | 'CLR_3 .575 34KV' | 100 | 0.09039 | -0.18875 | 135
WERE | 'EVANS N4 138 16KV' | 360 | -0.09771 | WERE | 'CLR_3 .575 34KV' | 100 | 0.09039 | -0.1881 | 136
WERE | 'PAWNEE 115KV' | 999 | -0.04078 | WERE | 'CLR_3 .575 34KV' | 100 | 0.09039 | -0.13117 | 195
WERE | 'RICE 115KV' | 999 | -0.04078 | WERE | 'CLR_3 .575 34KV' | 100 | 0.09039 | -0.13117 | 195
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21109 | WERE | 'EVANS ENERGY CENTER 138KV' | 355.3926 | -0.09836 | -0.11273 | 227
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.01678 | WERE | 'CLR_3 .575 34KV' | 100 | 0.09039 | -0.10717 | 238
WERE | 'LANG 7 345 345KV' | 518 | -0.00846 | WERE | 'CLR_3 .575 34KV' | 100 | 0.09039 | -0.09885 | 258
WERE | 'EVANS ENERGY CENTER 138KV' | 421.6074 | -0.09836 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 264.507 | -0.00335 | -0.09501 | 269
WERE | 'EVANS N4 138 16KV' | 360 | -0.09771 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 264.507 | -0.00335 | -0.09436 | 271
WERE | 'EVANS ENERGY CENTER 138KV' | 421.6074 | -0.09836 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | -0.00513 | -0.09323 | 274
WERE | 'EVANS ENERGY CENTER 138KV' | 421.6074 | -0.09836 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | -0.00545 | -0.09291 | 275
WERE | 'EVANS N4 138 16KV' | 360 | -0.09771 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | -0.00513 | -0.09258 | 276
WERE | 'EVANS N4 138 16KV' | 360 | -0.09771 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | -0.00545 | -0.09226 | 277
WERE | 'EVANS ENERGY CENTER 138KV' | 421.6074 | -0.09836 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 128 | -0.00769 | -0.09067 | 282
WERE | 'EVANS ENERGY CENTER 138KV' | 421.6074 | -0.09836 | WERE | 'LANG 7 345 345KV' | 310 | -0.00846 | -0.0899 | 284
WERE | 'EVANS N4 138 16KV' | 360 | -0.09771 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 128 | -0.00769 | -0.09002 | 284
WERE | 'EVANS N4 138 16KV' | 360 | -0.09771 | WERE | 'LANG 7 345 345KV' | 310 | -0.00846 | -0.08925 | 286
WERE | 'EVANS ENERGY CENTER 138KV' | 421.6074 | -0.09836 | WERE | 'BPU - CITY OF MCPHERSON 115KV' | 135 | -0.01411 | -0.08425 | 303
WERE | 'EVANS N4 138 16KV' | 360 | -0.09771 | WERE | 'BPU - CITY OF MCPHERSON 115KV' | 135 | -0.01411 | -0.0836 | 305
EMDE | 'LARUSSEL 161KV' | 180 | 0.00686 | EMDE | 'ELK RIVER 345KV' | 150 | 0.09039 | -0.08353 | 306
EMDE | 'RIVERTON 161KV' | 199.0941 | 0.00724 | EMDE | 'ELK RIVER 345KV' | 150 | 0.09039 | -0.08315 | 307
EMDE | 'STATE LINE 161KV' | 103 | 0.00746 | EMDE | 'ELK RIVER 345KV' | 150 | 0.09039 | -0.08293 | 308
WERE | 'EVANS ENERGY CENTER 138KV' | 421.6074 | -0.09836 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 120 | -0.01678 | -0.08158 | 313
WERE | 'EVANS N4 138 16KV' | 360 | -0.09771 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 120 | -0.01678 | -0.08093 | 316
WERE | 'PAWNEE 115KV' | 999 | -0.04078 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 264.507 | -0.00335 | -0.03743 | 682
WERE | 'RICE 115KV' | 999 | -0.04078 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 264.507 | -0.00335 | -0.03743 | 682
WERE | 'PAWNEE 115KV' | 999 | -0.04078 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | -0.00513 | -0.03565 | 716
WERE | 'RICE 115KV' | 999 | -0.04078 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | -0.00513 | -0.03565 | 716
WERE | 'PAWNEE 115KV' | 999 | -0.04078 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | -0.00545 | -0.03533 | 723
WERE | 'RICE 115KV' | 999 | -0.04078 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | -0.00545 | -0.03533 | 723
WERE | 'PAWNEE 115KV' | 999 | -0.04078 | WERE | 'LANG 7 345 345KV' | 310 | -0.00846 | -0.03232 | 790
WERE | 'RICE 115KV' | 999 | -0.04078 | WERE | 'LANG 7 345 345KV' | 310 | -0.00846 | -0.03232 | 790
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER Displacement
Limiting Facility: | ROSE HILL (ROSEHL3X) 345/138/13.8KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 1
Flowgate: | ROSEHL3X2741ROSESEHL1X7412207SP
Date Redispatch Needed: | 6/1/07 - 10/1/07
Season Flowgate Identified: | 2007 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1161997 | 6.7481 | 6.7481
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'CITY OF MULVANE 69KV' | 7.502 | -0.28354 | WERE | 'CITY OF BURLINGTON 69KV' | 7.8 | 0.04502 | -0.32856 | 21
WERE | 'CITY OF MULVANE 69KV' | 7.502 | -0.28354 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.04502 | -0.32856 | 21
WERE | 'CITY OF WINFIELD 69KV' | 40 | -0.2138 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.04502 | -0.25882 | 26
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21113 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.04502 | -0.25615 | 26
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.2086 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.04502 | -0.25362 | 27
WERE | 'GETTY 69KV' | 35 | -0.1876 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.04502 | -0.23262 | 29
WERE | 'CITY OF WINFIELD 69KV' | 40 | -0.2138 | WERE | 'CITY OF IOLA 69KV' | 24.267 | -0.00502 | -0.20878 | 32
WERE | 'CITY OF WINFIELD 69KV' | 40 | -0.2138 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | -0.0052 | -0.2086 | 32
WERE | 'CITY OF WINFIELD 69KV' | 40 | -0.2138 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | -0.00487 | -0.20893 | 32
WERE | 'CITY OF WINFIELD 69KV' | 40 | -0.2138 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | -0.00262 | -0.21118 | 32
WERE | 'CITY OF WINFIELD 69KV' | 40 | -0.2138 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 235.4582 | -0.00316 | -0.21064 | 32
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21113 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | -0.00262 | -0.20851 | 32
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21113 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 235.4582 | -0.00316 | -0.20797 | 32
WERE | 'CITY OF WINFIELD 69KV' | 40 | -0.2138 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | -0.00941 | -0.20439 | 33
WERE | 'CITY OF WINFIELD 69KV' | 40 | -0.2138 | WERE | 'CHANUTE 69KV' | 56.723 | -0.01106 | -0.20274 | 33
WERE | 'CITY OF WINFIELD 69KV' | 40 | -0.2138 | WERE | 'CITY OF ERIE 69KV' | 23.27 | -0.01106 | -0.20274 | 33
WERE | 'CITY OF WINFIELD 69KV' | 40 | -0.2138 | WERE | 'CLAY CENTER JUNCTION 115KV' | 22.939 | -0.00847 | -0.20533 | 33
WERE | 'CITY OF WINFIELD 69KV' | 40 | -0.2138 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 122.7222 | -0.00749 | -0.20631 | 33
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.2086 | WERE | 'CITY OF IOLA 69KV' | 24.267 | -0.00502 | -0.20358 | 33
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.2086 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | -0.0052 | -0.2034 | 33
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.2086 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | -0.00487 | -0.20373 | 33
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.2086 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | -0.00262 | -0.20598 | 33
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.2086 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 235.4582 | -0.00316 | -0.20544 | 33
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21113 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | -0.00941 | -0.20172 | 33
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21113 | WERE | 'CITY OF IOLA 69KV' | 24.267 | -0.00502 | -0.20611 | 33
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21113 | WERE | 'CLAY CENTER JUNCTION 115KV' | 22.939 | -0.00847 | -0.20266 | 33
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21113 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | -0.0052 | -0.20593 | 33
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21113 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | -0.00487 | -0.20626 | 33
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21113 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 122.7222 | -0.00749 | -0.20364 | 33
WERE | 'CITY OF WINFIELD 69KV' | 40 | -0.2138 | WERE | 'BPU - CITY OF MCPHERSON 115KV' | 135 | -0.01406 | -0.19974 | 34
WERE | 'CITY OF WINFIELD 69KV' | 40 | -0.2138 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 120 | -0.01694 | -0.19686 | 34
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.2086 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | -0.00941 | -0.19919 | 34
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.2086 | WERE | 'CHANUTE 69KV' | 56.723 | -0.01106 | -0.19754 | 34
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.2086 | WERE | 'CITY OF ERIE 69KV' | 23.27 | -0.01106 | -0.19754 | 34
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.2086 | WERE | 'CLAY CENTER JUNCTION 115KV' | 22.939 | -0.00847 | -0.20013 | 34
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.2086 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 122.7222 | -0.00749 | -0.20111 | 34
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21113 | WERE | 'BPU - CITY OF MCPHERSON 115KV' | 135 | -0.01406 | -0.19707 | 34
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21113 | WERE | 'CHANUTE 69KV' | 56.723 | -0.01106 | -0.20007 | 34
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21113 | WERE | 'CITY OF ERIE 69KV' | 23.27 | -0.01106 | -0.20007 | 34
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.2086 | WERE | 'BPU - CITY OF MCPHERSON 115KV' | 135 | -0.01406 | -0.19454 | 35
WERE | 'GILL ENERGY CENTER 138KV' | 18 | -0.2086 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 120 | -0.01694 | -0.19166 | 35
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21113 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 120 | -0.01694 | -0.19419 | 35
WERE | 'GETTY 69KV' | 35 | -0.1876 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | -0.00262 | -0.18498 | 36
WERE | 'GETTY 69KV' | 35 | -0.1876 | WERE | 'CITY OF IOLA 69KV' | 24.267 | -0.00502 | -0.18258 | 37
WERE | 'GETTY 69KV' | 35 | -0.1876 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | -0.0052 | -0.1824 | 37
WERE | 'GETTY 69KV' | 35 | -0.1876 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | -0.00487 | -0.18273 | 37
WERE | 'GETTY 69KV' | 35 | -0.1876 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 235.4582 | -0.00316 | -0.18444 | 37
WERE | 'GETTY 69KV' | 35 | -0.1876 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 122.7222 | -0.00749 | -0.18011 | 37
WERE | 'GETTY 69KV' | 35 | -0.1876 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | -0.00941 | -0.17819 | 38
WERE | 'GETTY 69KV' | 35 | -0.1876 | WERE | 'CHANUTE 69KV' | 56.723 | -0.01106 | -0.17654 | 38
WERE | 'GETTY 69KV' | 35 | -0.1876 | WERE | 'CITY OF ERIE 69KV' | 23.27 | -0.01106 | -0.17654 | 38
WERE | 'GETTY 69KV' | 35 | -0.1876 | WERE | 'CLAY CENTER JUNCTION 115KV' | 22.939 | -0.00847 | -0.17913 | 38
WERE | 'GETTY 69KV' | 35 | -0.1876 | WERE | 'BPU - CITY OF MCPHERSON 115KV' | 135 | -0.01406 | -0.17354 | 39
WERE | 'GETTY 69KV' | 35 | -0.1876 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 120 | -0.01694 | -0.17066 | 40
WEPL | 'HARPER 138KV' | 17.21 | -0.15502 | WEPL | 'CLIFTON 115KV' | 42.8426 | -0.00958 | -0.14544 | 46
WERE | 'EVANS ENERGY CENTER 138KV' | 233 | -0.09833 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.04502 | -0.14335 | 47
WERE | 'EVANS N4 138 16KV' | 360 | -0.09768 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.97 | 0.04502 | -0.1427 | 47
WEPL | 'HARPER 138KV' | 17.21 | -0.15502 | WEPL | 'A. M. MULLERGREN GENERATOR 115KV' | 63 | -0.02308 | -0.13194 | 51
WERE | 'CITY OF WINFIELD 69KV' | 40 | -0.2138 | WERE | 'EVANS ENERGY CENTER 138KV' | 340 | -0.09833 | -0.11547 | 58
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21113 | WERE | 'EVANS ENERGY CENTER 138KV' | 340 | -0.09833 | -0.1128 | 60
WERE | 'EVANS ENERGY CENTER 138KV' | 233 | -0.09833 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | -0.00262 | -0.09571 | 71
WERE | 'EVANS ENERGY CENTER 138KV' | 233 | -0.09833 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 235.4582 | -0.00316 | -0.09517 | 71
WERE | 'EVANS N4 138 16KV' | 360 | -0.09768 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | -0.00262 | -0.09506 | 71
WERE | 'EVANS N4 138 16KV' | 360 | -0.09768 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 235.4582 | -0.00316 | -0.09452 | 71
WERE | 'EVANS ENERGY CENTER 138KV' | 233 | -0.09833 | WERE | 'CITY OF IOLA 69KV' | 24.267 | -0.00502 | -0.09331 | 72
WERE | 'EVANS ENERGY CENTER 138KV' | 233 | -0.09833 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | -0.0052 | -0.09313 | 72
WERE | 'EVANS ENERGY CENTER 138KV' | 233 | -0.09833 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | -0.00487 | -0.09346 | 72
WERE | 'EVANS N4 138 16KV' | 360 | -0.09768 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | -0.0052 | -0.09248 | 73
WERE | 'EVANS N4 138 16KV' | 360 | -0.09768 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | -0.00487 | -0.09281 | 73
WERE | 'EVANS ENERGY CENTER 138KV' | 233 | -0.09833 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 122.7222 | -0.00749 | -0.09084 | 74
WERE | 'EVANS N4 138 16KV' | 360 | -0.09768 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 122.7222 | -0.00749 | -0.09019 | 75
WERE | 'EVANS ENERGY CENTER 138KV' | 233 | -0.09833 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | -0.00941 | -0.08892 | 76
WERE | 'EVANS N4 138 16KV' | 360 | -0.09768 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | -0.00941 | -0.08827 | 76
WERE | 'GETTY 69KV' | 35 | -0.1876 | WERE | 'EVANS ENERGY CENTER 138KV' | 340 | -0.09833 | -0.08927 | 76
WERE | 'EVANS ENERGY CENTER 138KV' | 233 | -0.09833 | WERE | 'CHANUTE 69KV' | 56.723 | -0.01106 | -0.08727 | 77
WERE | 'EVANS N4 138 16KV' | 360 | -0.09768 | WERE | 'CHANUTE 69KV' | 56.723 | -0.01106 | -0.08662 | 78
WERE | 'EVANS ENERGY CENTER 138KV' | 233 | -0.09833 | WERE | 'BPU - CITY OF MCPHERSON 115KV' | 135 | -0.01406 | -0.08427 | 80
WERE | 'EVANS N4 138 16KV' | 360 | -0.09768 | WERE | 'BPU - CITY OF MCPHERSON 115KV' | 135 | -0.01406 | -0.08362 | 81
EMDE | 'LARUSSEL 161KV' | 189.4348 | 0.00674 | EMDE | 'ELK RIVER 345KV' | 150 | 0.09048 | -0.08374 | 81
EMDE | 'RIVERTON 161KV' | 216 | 0.00711 | EMDE | 'ELK RIVER 345KV' | 150 | 0.09048 | -0.08337 | 81
EMDE | 'STATE LINE 161KV' | 103 | 0.00732 | EMDE | 'ELK RIVER 345KV' | 150 | 0.09048 | -0.08316 | 81
EMDE | 'RIVERTON 161KV' | 34 | 0.00776 | EMDE | 'ELK RIVER 345KV' | 150 | 0.09048 | -0.08272 | 82
WERE | 'EVANS ENERGY CENTER 138KV' | 233 | -0.09833 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 120 | -0.01694 | -0.08139 | 83
WERE | 'EVANS N4 138 16KV' | 360 | -0.09768 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 120 | -0.01694 | -0.08074 | 84
WERE | 'PAWNEE 115KV' | 999 | -0.04116 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | -0.00262 | -0.03854 | 175
WERE | 'RICE 115KV' | 999 | -0.04116 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | -0.00262 | -0.03854 | 175
WERE | 'PAWNEE 115KV' | 999 | -0.04116 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 235.4582 | -0.00316 | -0.038 | 178
WERE | 'RICE 115KV' | 999 | -0.04116 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 235.4582 | -0.00316 | -0.038 | 178
WERE | 'PAWNEE 115KV' | 999 | -0.04116 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | -0.00487 | -0.03629 | 186
WERE | 'RICE 115KV' | 999 | -0.04116 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | -0.00487 | -0.03629 | 186
WERE | 'PAWNEE 115KV' | 999 | -0.04116 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | -0.0052 | -0.03596 | 188
WERE | 'RICE 115KV' | 999 | -0.04116 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | -0.0052 | -0.03596 | 188
WERE | 'PAWNEE 115KV' | 999 | -0.04116 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 122.7222 | -0.00749 | -0.03367 | 200
WERE | 'RICE 115KV' | 999 | -0.04116 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 122.7222 | -0.00749 | -0.03367 | 200
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER Displacement
Limiting Facility: | ROSE HILL (ROSEHL3X) 345/138/13.8KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 1
Flowgate: | ROSEHL3X2741ROSESEHL1X7414208SP
Date Redispatch Needed: | Starting 2008 6/1 - 10/1 Until EOC of Upgrade
Season Flowgate Identified: | 2008 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1161506 | 11.9697 | 25.7922
1161997 | 13.8225 | 25.7922
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'CITY OF WINFIELD 69KV' | 40 | -0.21384 | WERE | 'CLR_3 .575 34KV' | 100 | 0.09043 | -0.30427 | 85
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21119 | WERE | 'CLR_3 .575 34KV' | 100 | 0.09043 | -0.30162 | 86
WERE | 'GETTY 69KV' | 35 | -0.18767 | WERE | 'CLR_3 .575 34KV' | 100 | 0.09043 | -0.2781 | 93
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21119 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | -0.00281 | -0.20838 | 124
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21119 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 264.507 | -0.00335 | -0.20784 | 124
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21119 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | -0.00545 | -0.20574 | 125
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21119 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | -0.00513 | -0.20606 | 125
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21119 | WERE | 'LANG 7 345 345KV' | 310 | -0.00847 | -0.20272 | 127
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21119 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 128 | -0.0077 | -0.20349 | 127
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21119 | WERE | 'CHANUTE 69KV' | 55.637 | -0.01078 | -0.20041 | 129
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21119 | WERE | 'SMOKEY HILLS 34KV' | 51 | -0.01295 | -0.19824 | 130
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21119 | WERE | 'BPU - CITY OF MCPHERSON 115KV' | 135 | -0.01412 | -0.19707 | 131
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21119 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 120 | -0.01679 | -0.1944 | 133
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21119 | WERE | 'KNOLL 3 115 115KV' | 75 | -0.01697 | -0.19422 | 133
WERE | 'EVANS ENERGY CENTER 138KV' | 421.6074 | -0.0984 | WERE | 'CLR_3 .575 34KV' | 100 | 0.09043 | -0.18883 | 137
WERE | 'EVANS N4 138 16KV' | 360 | -0.09775 | WERE | 'CLR_3 .575 34KV' | 100 | 0.09043 | -0.18818 | 137
WERE | 'PAWNEE 115KV' | 999 | -0.0408 | WERE | 'CLR_3 .575 34KV' | 100 | 0.09043 | -0.13123 | 197
WERE | 'RICE 115KV' | 999 | -0.0408 | WERE | 'CLR_3 .575 34KV' | 100 | 0.09043 | -0.13123 | 197
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.21119 | WERE | 'EVANS ENERGY CENTER 138KV' | 355.3926 | -0.0984 | -0.11279 | 229
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.01679 | WERE | 'CLR_3 .575 34KV' | 100 | 0.09043 | -0.10722 | 241
WERE | 'LANG 7 345 345KV' | 518 | -0.00847 | WERE | 'CLR_3 .575 34KV' | 100 | 0.09043 | -0.0989 | 261
WERE | 'EVANS ENERGY CENTER 138KV' | 421.6074 | -0.0984 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 264.507 | -0.00335 | -0.09505 | 271
WERE | 'EVANS N4 138 16KV' | 360 | -0.09775 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 264.507 | -0.00335 | -0.0944 | 273
WERE | 'EVANS ENERGY CENTER 138KV' | 421.6074 | -0.0984 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | -0.00545 | -0.09295 | 277
WERE | 'EVANS ENERGY CENTER 138KV' | 421.6074 | -0.0984 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | -0.00513 | -0.09327 | 277
WERE | 'EVANS N4 138 16KV' | 360 | -0.09775 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | -0.00513 | -0.09262 | 278
WERE | 'EVANS N4 138 16KV' | 360 | -0.09775 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | -0.00545 | -0.0923 | 279
WERE | 'EVANS ENERGY CENTER 138KV' | 421.6074 | -0.0984 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 128 | -0.0077 | -0.0907 | 284
WERE | 'EVANS N4 138 16KV' | 360 | -0.09775 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 128 | -0.0077 | -0.09005 | 286
WERE | 'EVANS ENERGY CENTER 138KV' | 421.6074 | -0.0984 | WERE | 'LANG 7 345 345KV' | 310 | -0.00847 | -0.08993 | 287
WERE | 'EVANS N4 138 16KV' | 360 | -0.09775 | WERE | 'LANG 7 345 345KV' | 310 | -0.00847 | -0.08928 | 289
WERE | 'EVANS ENERGY CENTER 138KV' | 421.6074 | -0.0984 | WERE | 'BPU - CITY OF MCPHERSON 115KV' | 135 | -0.01412 | -0.08428 | 306
WERE | 'EVANS N4 138 16KV' | 360 | -0.09775 | WERE | 'BPU - CITY OF MCPHERSON 115KV' | 135 | -0.01412 | -0.08363 | 308
EMDE | 'LARUSSEL 161KV' | 180 | 0.00686 | EMDE | 'ELK RIVER 345KV' | 150 | 0.09043 | -0.08357 | 309
EMDE | 'RIVERTON 161KV' | 199.0941 | 0.00724 | EMDE | 'ELK RIVER 345KV' | 150 | 0.09043 | -0.08319 | 310
WERE | 'EVANS ENERGY CENTER 138KV' | 421.6074 | -0.0984 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 120 | -0.01679 | -0.08161 | 316
WERE | 'EVANS N4 138 16KV' | 360 | -0.09775 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 120 | -0.01679 | -0.08096 | 319
WERE | 'PAWNEE 115KV' | 999 | -0.0408 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 264.507 | -0.00335 | -0.03745 | 689
WERE | 'RICE 115KV' | 999 | -0.0408 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 264.507 | -0.00335 | -0.03745 | 689
WERE | 'PAWNEE 115KV' | 999 | -0.0408 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | -0.00513 | -0.03567 | 723
WERE | 'RICE 115KV' | 999 | -0.0408 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | -0.00513 | -0.03567 | 723
WERE | 'PAWNEE 115KV' | 999 | -0.0408 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | -0.00545 | -0.03535 | 730
WERE | 'RICE 115KV' | 999 | -0.0408 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | -0.00545 | -0.03535 | 730
WERE | 'PAWNEE 115KV' | 999 | -0.0408 | WERE | 'LANG 7 345 345KV' | 310 | -0.00847 | -0.03233 | 798
WERE | 'RICE 115KV' | 999 | -0.0408 | WERE | 'LANG 7 345 345KV' | 310 | -0.00847 | -0.03233 | 798
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | SOUTHWEST SHREVEPORT (SW SHV 1) 345/138/13.8KV TRANSFORMER CKT 1 Expedite
Limiting Facility: | SOUTHWEST SHREVEPORT (SW SHV 1) 345/138/13.8KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | SOUTHWEST SHREVEPORT (SW SHV 2) 345/138/13.8KV TRANSFORMER CKT 2
Flowgate: | SWSHV12741SWSSHV27421408SP
Date Redispatch Needed: | Starting 2008 6/1 - 10/1 Until EOC of Upgrade
Season Flowgate Identified: | 2008 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1158760 | 4.1821 | 12.4063
1158761 | 4.1821 | 12.4063
1162763 | 1.3594 | 12.4063
1162766 | 1.3559 | 12.4063
1162768 | 1.3268 | 12.4063
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.3928 | AEPW | 'AEP-CT0613.8 161KV' | 320 | -0.00202 | -0.39078 | 32
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.3928 | AEPW | 'COGENTRIX 345KV' | 300 | -0.00261 | -0.39019 | 32
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.3928 | AEPW | 'COMANCHE 138KV' | 160 | -0.00383 | -0.38897 | 32
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.3928 | AEPW | 'COMANCHE 69KV' | 63 | -0.00384 | -0.38896 | 32
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.3928 | AEPW | 'FITZHUGH 161KV' | 101 | -0.00079 | -0.39201 | 32
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.3928 | AEPW | 'FLINT CREEK 161KV' | 428 | -0.00205 | -0.39075 | 32
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.3928 | AEPW | 'L&D13 69KV' | 11 | -0.00117 | -0.39163 | 32
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.3928 | AEPW | 'NORTHEASTERN STATION 138KV' | 377 | -0.00238 | -0.39042 | 32
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.3928 | AEPW | 'NORTHEASTERN STATION 138KV' | 95 | -0.00238 | -0.39042 | 32
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.3928 | AEPW | 'NORTHEASTERN STATION 345KV' | 645 | -0.00237 | -0.39043 | 32
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.3928 | AEPW | 'OEC 345KV' | 319 | -0.00251 | -0.39029 | 32
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.3928 | AEPW | 'RIVERSIDE STATION 138KV' | 422 | -0.00262 | -0.39018 | 32
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.3928 | AEPW | 'SLEEPING BEAR 138KV' | 80 | -0.00337 | -0.38943 | 32
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.3928 | AEPW | 'SOUTHWESTERN STATION 138KV' | 168 | -0.0038 | -0.389 | 32
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.3928 | AEPW | 'SOUTHWESTERN STATION 138KV' | 143 | -0.0038 | -0.389 | 32
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.3928 | AEPW | 'TULSA POWER STATION 138KV' | 38 | -0.00259 | -0.39021 | 32
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.3928 | AEPW | 'WEATHERFORD 34KV' | 148 | -0.00357 | -0.38923 | 32
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.3928 | AEPW | 'WELEETKA 138KV' | 84 | -0.00341 | -0.38939 | 32
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.3928 | AEPW | 'WELSH 345KV' | 1044 | -0.00825 | -0.38455 | 32
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.3928 | AEPW | 'WILKES 345KV' | 191 | -0.00103 | -0.39177 | 32
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.39134 | AEPW | 'AEP-CT0613.8 161KV' | 320 | -0.00202 | -0.38932 | 32
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.39134 | AEPW | 'COGENTRIX 345KV' | 300 | -0.00261 | -0.38873 | 32
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.39134 | AEPW | 'COMANCHE 138KV' | 160 | -0.00383 | -0.38751 | 32
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.39134 | AEPW | 'COMANCHE 69KV' | 63 | -0.00384 | -0.3875 | 32
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.39134 | AEPW | 'FITZHUGH 161KV' | 101 | -0.00079 | -0.39055 | 32
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.39134 | AEPW | 'FLINT CREEK 161KV' | 428 | -0.00205 | -0.38929 | 32
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.39134 | AEPW | 'L&D13 69KV' | 11 | -0.00117 | -0.39017 | 32
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.39134 | AEPW | 'NORTHEASTERN STATION 138KV' | 95 | -0.00238 | -0.38896 | 32
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.39134 | AEPW | 'NORTHEASTERN STATION 138KV' | 377 | -0.00238 | -0.38896 | 32
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.39134 | AEPW | 'NORTHEASTERN STATION 345KV' | 645 | -0.00237 | -0.38897 | 32
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.39134 | AEPW | 'OEC 345KV' | 319 | -0.00251 | -0.38883 | 32
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.39134 | AEPW | 'RIVERSIDE STATION 138KV' | 422 | -0.00262 | -0.38872 | 32
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.39134 | AEPW | 'SLEEPING BEAR 138KV' | 80 | -0.00337 | -0.38797 | 32
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.39134 | AEPW | 'SOUTHWESTERN STATION 138KV' | 168 | -0.0038 | -0.38754 | 32
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.39134 | AEPW | 'SOUTHWESTERN STATION 138KV' | 143 | -0.0038 | -0.38754 | 32
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.39134 | AEPW | 'TULSA POWER STATION 138KV' | 38 | -0.00259 | -0.38875 | 32
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.39134 | AEPW | 'WEATHERFORD 34KV' | 148 | -0.00357 | -0.38777 | 32
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.39134 | AEPW | 'WELEETKA 138KV' | 84 | -0.00341 | -0.38793 | 32
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.39134 | AEPW | 'WELSH 345KV' | 1044 | -0.00825 | -0.38309 | 32
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.39134 | AEPW | 'WILKES 345KV' | 191 | -0.00103 | -0.39031 | 32
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.3928 | AEPW | 'NARROWS 69KV' | 22 | -0.01354 | -0.37926 | 33
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.39134 | AEPW | 'NARROWS 69KV' | 22 | -0.01354 | -0.3778 | 33
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.3928 | AEPW | 'WILKES 138KV' | 136.2395 | -0.03012 | -0.36268 | 34
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.39134 | AEPW | 'WILKES 138KV' | 136.2395 | -0.03012 | -0.36122 | 34
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.3928 | AEPW | 'LEBROCK 345KV' | 465 | -0.0464 | -0.3464 | 36
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.39134 | AEPW | 'LEBROCK 345KV' | 465 | -0.0464 | -0.34494 | 36
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.3928 | AEPW | 'PIRKEY GENERATION 138KV' | 490 | -0.07038 | -0.32242 | 38
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.39134 | AEPW | 'PIRKEY GENERATION 138KV' | 490 | -0.07038 | -0.32096 | 39
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.3928 | AEPW | 'EASTMAN 138KV' | 355 | -0.08859 | -0.30421 | 41
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.39134 | AEPW | 'EASTMAN 138KV' | 355 | -0.08859 | -0.30275 | 41
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.3928 | AEPW | 'KNOXLEE 138KV' | 103 | -0.10873 | -0.28407 | 44
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.39134 | AEPW | 'KNOXLEE 138KV' | 103 | -0.10873 | -0.28261 | 44
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22408 | AEPW | 'AEP-CT0613.8 161KV' | 320 | -0.00202 | -0.22206 | 56
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22408 | AEPW | 'COGENTRIX 345KV' | 300 | -0.00261 | -0.22147 | 56
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22408 | AEPW | 'COMANCHE 138KV' | 160 | -0.00383 | -0.22025 | 56
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22408 | AEPW | 'COMANCHE 69KV' | 63 | -0.00384 | -0.22024 | 56
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22408 | AEPW | 'FITZHUGH 161KV' | 101 | -0.00079 | -0.22329 | 56
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22408 | AEPW | 'FLINT CREEK 161KV' | 428 | -0.00205 | -0.22203 | 56
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22408 | AEPW | 'NORTHEASTERN STATION 138KV' | 95 | -0.00238 | -0.2217 | 56
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22408 | AEPW | 'NORTHEASTERN STATION 138KV' | 377 | -0.00238 | -0.2217 | 56
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22408 | AEPW | 'NORTHEASTERN STATION 345KV' | 645 | -0.00237 | -0.22171 | 56
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22408 | AEPW | 'OEC 345KV' | 319 | -0.00251 | -0.22157 | 56
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22408 | AEPW | 'RIVERSIDE STATION 138KV' | 422 | -0.00262 | -0.22146 | 56
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22408 | AEPW | 'SLEEPING BEAR 138KV' | 80 | -0.00337 | -0.22071 | 56
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22408 | AEPW | 'SOUTHWESTERN STATION 138KV' | 168 | -0.0038 | -0.22028 | 56
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22408 | AEPW | 'SOUTHWESTERN STATION 138KV' | 143 | -0.0038 | -0.22028 | 56
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22408 | AEPW | 'TULSA POWER STATION 138KV' | 38 | -0.00259 | -0.22149 | 56
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22408 | AEPW | 'WEATHERFORD 34KV' | 148 | -0.00357 | -0.22051 | 56
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22408 | AEPW | 'WELEETKA 138KV' | 84 | -0.00341 | -0.22067 | 56
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22408 | AEPW | 'WILKES 345KV' | 191 | -0.00103 | -0.22305 | 56
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22408 | AEPW | 'WELSH 345KV' | 1044 | -0.00825 | -0.21583 | 57
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22408 | AEPW | 'NARROWS 69KV' | 22 | -0.01354 | -0.21054 | 59
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22408 | AEPW | 'WILKES 138KV' | 136.2395 | -0.03012 | -0.19396 | 64
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22408 | AEPW | 'LEBROCK 345KV' | 465 | -0.0464 | -0.17768 | 70
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.3928 | AEPW | 'LIEBERMAN 138KV' | 26.1641 | -0.22408 | -0.16872 | 74
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.39134 | AEPW | 'LIEBERMAN 138KV' | 26.1641 | -0.22408 | -0.16726 | 74
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22408 | AEPW | 'PIRKEY GENERATION 138KV' | 490 | -0.07038 | -0.1537 | 81
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22408 | AEPW | 'EASTMAN 138KV' | 355 | -0.08859 | -0.13549 | 92
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22408 | AEPW | 'KNOXLEE 138KV' | 103 | -0.10873 | -0.11535 | 108
AEPW | 'KNOXLEE 138KV' | 260 | -0.10873 | AEPW | 'FITZHUGH 161KV' | 101 | -0.00079 | -0.10794 | 115
AEPW | 'KNOXLEE 138KV' | 60 | -0.10873 | AEPW | 'FITZHUGH 161KV' | 101 | -0.00079 | -0.10794 | 115
AEPW | 'KNOXLEE 138KV' | 260 | -0.10873 | AEPW | 'WILKES 345KV' | 191 | -0.00103 | -0.1077 | 115
AEPW | 'KNOXLEE 138KV' | 60 | -0.10873 | AEPW | 'WILKES 345KV' | 191 | -0.00103 | -0.1077 | 115
AEPW | 'KNOXLEE 138KV' | 260 | -0.10873 | AEPW | 'AEP-CT0613.8 161KV' | 320 | -0.00202 | -0.10671 | 116
AEPW | 'KNOXLEE 138KV' | 60 | -0.10873 | AEPW | 'AEP-CT0613.8 161KV' | 320 | -0.00202 | -0.10671 | 116
AEPW | 'KNOXLEE 138KV' | 260 | -0.10873 | AEPW | 'FLINT CREEK 161KV' | 428 | -0.00205 | -0.10668 | 116
AEPW | 'KNOXLEE 138KV' | 60 | -0.10873 | AEPW | 'FLINT CREEK 161KV' | 428 | -0.00205 | -0.10668 | 116
AEPW | 'KNOXLEE 138KV' | 260 | -0.10873 | AEPW | 'COGENTRIX 345KV' | 300 | -0.00261 | -0.10612 | 117
AEPW | 'KNOXLEE 138KV' | 60 | -0.10873 | AEPW | 'COGENTRIX 345KV' | 300 | -0.00261 | -0.10612 | 117
AEPW | 'KNOXLEE 138KV' | 260 | -0.10873 | AEPW | 'NORTHEASTERN STATION 138KV' | 377 | -0.00238 | -0.10635 | 117
AEPW | 'KNOXLEE 138KV' | 260 | -0.10873 | AEPW | 'NORTHEASTERN STATION 138KV' | 95 | -0.00238 | -0.10635 | 117
AEPW | 'KNOXLEE 138KV' | 60 | -0.10873 | AEPW | 'NORTHEASTERN STATION 138KV' | 95 | -0.00238 | -0.10635 | 117
AEPW | 'KNOXLEE 138KV' | 60 | -0.10873 | AEPW | 'NORTHEASTERN STATION 138KV' | 377 | -0.00238 | -0.10635 | 117
AEPW | 'KNOXLEE 138KV' | 260 | -0.10873 | AEPW | 'NORTHEASTERN STATION 345KV' | 645 | -0.00237 | -0.10636 | 117
AEPW | 'KNOXLEE 138KV' | 60 | -0.10873 | AEPW | 'NORTHEASTERN STATION 345KV' | 645 | -0.00237 | -0.10636 | 117
AEPW | 'KNOXLEE 138KV' | 260 | -0.10873 | AEPW | 'OEC 345KV' | 319 | -0.00251 | -0.10622 | 117
AEPW | 'KNOXLEE 138KV' | 60 | -0.10873 | AEPW | 'OEC 345KV' | 319 | -0.00251 | -0.10622 | 117
AEPW | 'KNOXLEE 138KV' | 260 | -0.10873 | AEPW | 'RIVERSIDE STATION 138KV' | 422 | -0.00262 | -0.10611 | 117
AEPW | 'KNOXLEE 138KV' | 60 | -0.10873 | AEPW | 'RIVERSIDE STATION 138KV' | 422 | -0.00262 | -0.10611 | 117
AEPW | 'KNOXLEE 138KV' | 260 | -0.10873 | AEPW | 'COMANCHE 138KV' | 160 | -0.00383 | -0.1049 | 118
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | SOUTHWEST SHREVEPORT (SW SHV 1) 345/138/13.8KV TRANSFORMER CKT 2 Expedite
Limiting Facility: | SOUTHWEST SHREVEPORT (SW SHV 2) 345/138/13.8KV TRANSFORMER CKT 2
Direction: | From->To
Line Outage: | SOUTHWEST SHREVEPORT (SW SHV 1) 345/138/13.8KV TRANSFORMER CKT 1
Flowgate: | SWSHV22742SWSSHV17411408SP
Date Redispatch Needed: | Starting 2008 6/1 - 10/1 Until EOC of Upgrade
Season Flowgate Identified: | 2008 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1158760 | 0.14666 | 0.52012
1158761 | 0.14666 | 0.52012
1162763 | 0.07628 | 0.52012
1162766 | 0.07608 | 0.52012
1162768 | 0.07444 | 0.52012
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.38572 | AEPW | 'AEP-CT0613.8 161KV' | 320 | -0.00198 | -0.38374 | 1
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.38572 | AEPW | 'COGENTRIX 345KV' | 300 | -0.00256 | -0.38316 | 1
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.38572 | AEPW | 'COMANCHE 138KV' | 160 | -0.00376 | -0.38196 | 1
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.38572 | AEPW | 'COMANCHE 69KV' | 63 | -0.00377 | -0.38195 | 1
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.38572 | AEPW | 'FITZHUGH 161KV' | 101 | -0.00078 | -0.38494 | 1
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.38572 | AEPW | 'FLINT CREEK 161KV' | 428 | -0.00201 | -0.38371 | 1
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.38572 | AEPW | 'L&D13 69KV' | 11 | -0.00115 | -0.38457 | 1
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.38572 | AEPW | 'NARROWS 69KV' | 22 | -0.0133 | -0.37242 | 1
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.38572 | AEPW | 'NORTHEASTERN STATION 138KV' | 95 | -0.00233 | -0.38339 | 1
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.38572 | AEPW | 'NORTHEASTERN STATION 138KV' | 377 | -0.00233 | -0.38339 | 1
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.38572 | AEPW | 'NORTHEASTERN STATION 345KV' | 645 | -0.00233 | -0.38339 | 1
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.38572 | AEPW | 'OEC 345KV' | 319 | -0.00246 | -0.38326 | 1
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.38572 | AEPW | 'RIVERSIDE STATION 138KV' | 422 | -0.00258 | -0.38314 | 1
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.38572 | AEPW | 'SLEEPING BEAR 138KV' | 80 | -0.00331 | -0.38241 | 1
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.38572 | AEPW | 'SOUTHWESTERN STATION 138KV' | 168 | -0.00373 | -0.38199 | 1
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.38572 | AEPW | 'SOUTHWESTERN STATION 138KV' | 143 | -0.00373 | -0.38199 | 1
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.38572 | AEPW | 'TULSA POWER STATION 138KV' | 38 | -0.00255 | -0.38317 | 1
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.38572 | AEPW | 'WEATHERFORD 34KV' | 148 | -0.0035 | -0.38222 | 1
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.38572 | AEPW | 'WELEETKA 138KV' | 84 | -0.00334 | -0.38238 | 1
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.38572 | AEPW | 'WELSH 345KV' | 1044 | -0.0081 | -0.37762 | 1
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.38572 | AEPW | 'WILKES 138KV' | 136.2395 | -0.02958 | -0.35614 | 1
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.38572 | AEPW | 'WILKES 345KV' | 191 | -0.00102 | -0.3847 | 1
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.38429 | AEPW | 'AEP-CT0613.8 161KV' | 320 | -0.00198 | -0.38231 | 1
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.38429 | AEPW | 'COGENTRIX 345KV' | 300 | -0.00256 | -0.38173 | 1
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.38429 | AEPW | 'COMANCHE 138KV' | 160 | -0.00376 | -0.38053 | 1
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.38429 | AEPW | 'COMANCHE 69KV' | 63 | -0.00377 | -0.38052 | 1
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.38429 | AEPW | 'FITZHUGH 161KV' | 101 | -0.00078 | -0.38351 | 1
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.38429 | AEPW | 'FLINT CREEK 161KV' | 428 | -0.00201 | -0.38228 | 1
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.38429 | AEPW | 'L&D13 69KV' | 11 | -0.00115 | -0.38314 | 1
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.38429 | AEPW | 'NARROWS 69KV' | 22 | -0.0133 | -0.37099 | 1
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.38429 | AEPW | 'NORTHEASTERN STATION 138KV' | 377 | -0.00233 | -0.38196 | 1
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.38429 | AEPW | 'NORTHEASTERN STATION 138KV' | 95 | -0.00233 | -0.38196 | 1
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.38429 | AEPW | 'NORTHEASTERN STATION 345KV' | 645 | -0.00233 | -0.38196 | 1
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.38429 | AEPW | 'OEC 345KV' | 319 | -0.00246 | -0.38183 | 1
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.38429 | AEPW | 'RIVERSIDE STATION 138KV' | 422 | -0.00258 | -0.38171 | 1
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.38429 | AEPW | 'SLEEPING BEAR 138KV' | 80 | -0.00331 | -0.38098 | 1
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.38429 | AEPW | 'SOUTHWESTERN STATION 138KV' | 143 | -0.00373 | -0.38056 | 1
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.38429 | AEPW | 'SOUTHWESTERN STATION 138KV' | 168 | -0.00373 | -0.38056 | 1
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.38429 | AEPW | 'TULSA POWER STATION 138KV' | 38 | -0.00255 | -0.38174 | 1
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.38429 | AEPW | 'WEATHERFORD 34KV' | 148 | -0.0035 | -0.38079 | 1
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.38429 | AEPW | 'WELEETKA 138KV' | 84 | -0.00334 | -0.38095 | 1
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.38429 | AEPW | 'WELSH 345KV' | 1044 | -0.0081 | -0.37619 | 1
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.38429 | AEPW | 'WILKES 138KV' | 136.2395 | -0.02958 | -0.35471 | 1
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.38429 | AEPW | 'WILKES 345KV' | 191 | -0.00102 | -0.38327 | 1
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.38572 | AEPW | 'EASTMAN 138KV' | 355 | -0.08699 | -0.29873 | 2
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.38572 | AEPW | 'KNOXLEE 138KV' | 103 | -0.10677 | -0.27895 | 2
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.38572 | AEPW | 'LEBROCK 345KV' | 465 | -0.04556 | -0.34016 | 2
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.38572 | AEPW | 'PIRKEY GENERATION 138KV' | 490 | -0.06911 | -0.31661 | 2
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.38429 | AEPW | 'EASTMAN 138KV' | 355 | -0.08699 | -0.2973 | 2
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.38429 | AEPW | 'KNOXLEE 138KV' | 103 | -0.10677 | -0.27752 | 2
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.38429 | AEPW | 'LEBROCK 345KV' | 465 | -0.04556 | -0.33873 | 2
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.38429 | AEPW | 'PIRKEY GENERATION 138KV' | 490 | -0.06911 | -0.31518 | 2
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22004 | AEPW | 'AEP-CT0613.8 161KV' | 320 | -0.00198 | -0.21806 | 2
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22004 | AEPW | 'COGENTRIX 345KV' | 300 | -0.00256 | -0.21748 | 2
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22004 | AEPW | 'COMANCHE 138KV' | 160 | -0.00376 | -0.21628 | 2
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22004 | AEPW | 'COMANCHE 69KV' | 63 | -0.00377 | -0.21627 | 2
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22004 | AEPW | 'FITZHUGH 161KV' | 101 | -0.00078 | -0.21926 | 2
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22004 | AEPW | 'FLINT CREEK 161KV' | 428 | -0.00201 | -0.21803 | 2
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22004 | AEPW | 'L&D13 69KV' | 11 | -0.00115 | -0.21889 | 2
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22004 | AEPW | 'NORTHEASTERN STATION 138KV' | 95 | -0.00233 | -0.21771 | 2
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22004 | AEPW | 'NORTHEASTERN STATION 138KV' | 377 | -0.00233 | -0.21771 | 2
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22004 | AEPW | 'NORTHEASTERN STATION 345KV' | 645 | -0.00233 | -0.21771 | 2
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22004 | AEPW | 'OEC 345KV' | 319 | -0.00246 | -0.21758 | 2
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22004 | AEPW | 'RIVERSIDE STATION 138KV' | 422 | -0.00258 | -0.21746 | 2
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22004 | AEPW | 'SLEEPING BEAR 138KV' | 80 | -0.00331 | -0.21673 | 2
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22004 | AEPW | 'SOUTHWESTERN STATION 138KV' | 143 | -0.00373 | -0.21631 | 2
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22004 | AEPW | 'SOUTHWESTERN STATION 138KV' | 168 | -0.00373 | -0.21631 | 2
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22004 | AEPW | 'TULSA POWER STATION 138KV' | 38 | -0.00255 | -0.21749 | 2
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22004 | AEPW | 'WEATHERFORD 34KV' | 148 | -0.0035 | -0.21654 | 2
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22004 | AEPW | 'WELEETKA 138KV' | 84 | -0.00334 | -0.2167 | 2
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22004 | AEPW | 'WELSH 345KV' | 1044 | -0.0081 | -0.21194 | 2
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22004 | AEPW | 'WILKES 345KV' | 191 | -0.00102 | -0.21902 | 2
AEPW | 'AH-CC_ST18.0 138KV' | 550 | -0.38572 | AEPW | 'LIEBERMAN 138KV' | 26.1641 | -0.22004 | -0.16568 | 3
AEPW | 'ARSENAL HILL 69KV' | 99 | -0.38429 | AEPW | 'LIEBERMAN 138KV' | 26.1641 | -0.22004 | -0.16425 | 3
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22004 | AEPW | 'LEBROCK 345KV' | 465 | -0.04556 | -0.17448 | 3
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22004 | AEPW | 'NARROWS 69KV' | 22 | -0.0133 | -0.20674 | 3
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22004 | AEPW | 'PIRKEY GENERATION 138KV' | 490 | -0.06911 | -0.15093 | 3
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22004 | AEPW | 'WILKES 138KV' | 136.2395 | -0.02958 | -0.19046 | 3
AEPW | 'LIEBERMAN 138KV' | 201.8359 | -0.22004 | AEPW | 'EASTMAN 138KV' | 355 | -0.08699 | -0.13305 | 4
AEPW | 'NORTH MARSHALL 69KV' | 5 | -0.13591 | AEPW | 'AEP-CT0613.8 161KV' | 320 | -0.00198 | -0.13393 | 4
AEPW | 'NORTH MARSHALL 69KV' | 5 | -0.13591 | AEPW | 'COGENTRIX 345KV' | 300 | -0.00256 | -0.13335 | 4
AEPW | 'NORTH MARSHALL 69KV' | 5 | -0.13591 | AEPW | 'COMANCHE 138KV' | 160 | -0.00376 | -0.13215 | 4
AEPW | 'NORTH MARSHALL 69KV' | 5 | -0.13591 | AEPW | 'COMANCHE 69KV' | 63 | -0.00377 | -0.13214 | 4
AEPW | 'NORTH MARSHALL 69KV' | 5 | -0.13591 | AEPW | 'FITZHUGH 161KV' | 101 | -0.00078 | -0.13513 | 4
AEPW | 'NORTH MARSHALL 69KV' | 5 | -0.13591 | AEPW | 'FLINT CREEK 161KV' | 428 | -0.00201 | -0.1339 | 4
AEPW | 'NORTH MARSHALL 69KV' | 5 | -0.13591 | AEPW | 'L&D13 69KV' | 11 | -0.00115 | -0.13476 | 4
AEPW | 'NORTH MARSHALL 69KV' | 5 | -0.13591 | AEPW | 'NARROWS 69KV' | 22 | -0.0133 | -0.12261 | 4
AEPW | 'NORTH MARSHALL 69KV' | 5 | -0.13591 | AEPW | 'NORTHEASTERN STATION 138KV' | 95 | -0.00233 | -0.13358 | 4
AEPW | 'NORTH MARSHALL 69KV' | 5 | -0.13591 | AEPW | 'NORTHEASTERN STATION 138KV' | 377 | -0.00233 | -0.13358 | 4
AEPW | 'NORTH MARSHALL 69KV' | 5 | -0.13591 | AEPW | 'NORTHEASTERN STATION 345KV' | 645 | -0.00233 | -0.13358 | 4
AEPW | 'NORTH MARSHALL 69KV' | 5 | -0.13591 | AEPW | 'OEC 345KV' | 319 | -0.00246 | -0.13345 | 4
AEPW | 'NORTH MARSHALL 69KV' | 5 | -0.13591 | AEPW | 'RIVERSIDE STATION 138KV' | 422 | -0.00258 | -0.13333 | 4
AEPW | 'NORTH MARSHALL 69KV' | 5 | -0.13591 | AEPW | 'SLEEPING BEAR 138KV' | 80 | -0.00331 | -0.1326 | 4
AEPW | 'NORTH MARSHALL 69KV' | 5 | -0.13591 | AEPW | 'SOUTHWESTERN STATION 138KV' | 168 | -0.00373 | -0.13218 | 4
AEPW | 'NORTH MARSHALL 69KV' | 5 | -0.13591 | AEPW | 'SOUTHWESTERN STATION 138KV' | 143 | -0.00373 | -0.13218 | 4
AEPW | 'NORTH MARSHALL 69KV' | 5 | -0.13591 | AEPW | 'TULSA POWER STATION 138KV' | 38 | -0.00255 | -0.13336 | 4
AEPW | 'NORTH MARSHALL 69KV' | 5 | -0.13591 | AEPW | 'WEATHERFORD 34KV' | 148 | -0.0035 | -0.13241 | 4
AEPW | 'NORTH MARSHALL 69KV' | 5 | -0.13591 | AEPW | 'WELEETKA 138KV' | 84 | -0.00334 | -0.13257 | 4
AEPW | 'NORTH MARSHALL 69KV' | 5 | -0.13591 | AEPW | 'WELSH 345KV' | 1044 | -0.0081 | -0.12781 | 4
AEPW | 'NORTH MARSHALL 69KV' | 5 | -0.13591 | AEPW | 'WILKES 345KV' | 191 | -0.00102 | -0.13489 | 4
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | WICHITA - RENO 345KV
Limiting Facility: | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1
Direction: | From->To
Line Outage: | EAST MCPHERSON - SUMMIT 230KV CKT 1
Flowgate: | 57368573721568725687312208SP
Date Redispatch Needed: | Starting 2008 6/1 - 10/1 Until EOC of Upgrade
Season Flowgate Identified: | 2008 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1161506 | 3.4749 | 6.5643
1161997 | 3.0894 | 6.5643
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.28454 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06209 | -0.34663 | 19
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.28454 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | 0.01396 | -0.2985 | 22
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.28454 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | 0.01967 | -0.30421 | 22
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.28454 | WERE | 'LANG 7 345 345KV' | 310 | 0.0073 | -0.29184 | 22
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.28454 | WERE | 'CHANUTE 69KV' | 55.637 | 0.00116 | -0.2857 | 23
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.28454 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | 0.00019 | -0.28473 | 23
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.28454 | WERE | 'CITY OF BURLINGTON 69KV' | 7.8 | 0.00213 | -0.28667 | 23
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.28454 | WERE | 'CITY OF ERIE 69KV' | 23.374 | 0.00116 | -0.2857 | 23
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.28454 | WERE | 'CITY OF IOLA 69KV' | 24.471 | 0.00138 | -0.28592 | 23
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.28454 | WERE | 'CITY OF MULVANE 69KV' | 8.29 | -0.00093 | -0.28361 | 23
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.28454 | WERE | 'CITY OF WELLINGTON 69KV' | 41.45 | -0.00153 | -0.28301 | 23
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.28454 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.98 | 0.00213 | -0.28667 | 23
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.28454 | WERE | 'EVANS ENERGY CENTER 138KV' | 320.8022 | -0.00011 | -0.28443 | 23
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.28454 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00287 | -0.28167 | 23
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.28454 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | 0.00682 | -0.29136 | 23
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.28454 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 274.2987 | 0.00711 | -0.29165 | 23
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.28454 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00621 | -0.29075 | 23
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.28454 | WERE | 'WACO 138KV' | 17.967 | -0.00259 | -0.28195 | 23
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.22292 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06209 | -0.28501 | 23
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22281 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06209 | -0.2849 | 23
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.28454 | WERE | 'KNOLL 3 115 115KV' | 75 | -0.03173 | -0.25281 | 26
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.22292 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | 0.01967 | -0.24259 | 27
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22281 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | 0.01967 | -0.24248 | 27
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.22292 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | 0.01396 | -0.23688 | 28
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22281 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | 0.01396 | -0.23677 | 28
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.22292 | WERE | 'CHANUTE 69KV' | 55.637 | 0.00116 | -0.22408 | 29
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.22292 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | 0.00019 | -0.22311 | 29
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.22292 | WERE | 'CITY OF ERIE 69KV' | 23.374 | 0.00116 | -0.22408 | 29
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.22292 | WERE | 'CITY OF IOLA 69KV' | 24.471 | 0.00138 | -0.2243 | 29
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.22292 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.98 | 0.00213 | -0.22505 | 29
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.22292 | WERE | 'EVANS ENERGY CENTER 138KV' | 320.8022 | -0.00011 | -0.22281 | 29
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.22292 | WERE | 'LANG 7 345 345KV' | 310 | 0.0073 | -0.23022 | 29
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.22292 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | 0.00682 | -0.22974 | 29
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.22292 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 274.2987 | 0.00711 | -0.23003 | 29
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.22292 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00621 | -0.22913 | 29
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22281 | WERE | 'CHANUTE 69KV' | 55.637 | 0.00116 | -0.22397 | 29
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22281 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | 0.00019 | -0.223 | 29
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22281 | WERE | 'CITY OF ERIE 69KV' | 23.374 | 0.00116 | -0.22397 | 29
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22281 | WERE | 'CITY OF IOLA 69KV' | 24.471 | 0.00138 | -0.22419 | 29
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22281 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.98 | 0.00213 | -0.22494 | 29
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22281 | WERE | 'EVANS ENERGY CENTER 138KV' | 320.8022 | -0.00011 | -0.2227 | 29
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22281 | WERE | 'LANG 7 345 345KV' | 310 | 0.0073 | -0.23011 | 29
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22281 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | 0.00682 | -0.22963 | 29
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22281 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 274.2987 | 0.00711 | -0.22992 | 29
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22281 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00621 | -0.22902 | 29
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.22292 | WERE | 'CITY OF WELLINGTON 69KV' | 41.45 | -0.00153 | -0.22139 | 30
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.22292 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00287 | -0.22005 | 30
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.22292 | WERE | 'WACO 138KV' | 17.967 | -0.00259 | -0.22033 | 30
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22281 | WERE | 'CITY OF WELLINGTON 69KV' | 41.45 | -0.00153 | -0.22128 | 30
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22281 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00287 | -0.21994 | 30
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22281 | WERE | 'WACO 138KV' | 17.967 | -0.00259 | -0.22022 | 30
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.22292 | WERE | 'KNOLL 3 115 115KV' | 75 | -0.03173 | -0.19119 | 34
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22281 | WERE | 'KNOLL 3 115 115KV' | 75 | -0.03173 | -0.19108 | 34
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.28454 | WERE | 'CLAY CENTER JUNCTION 115KV' | 21.056 | -0.10223 | -0.18231 | 36
WERE | 'PAWNEE 115KV' | 999 | -0.11442 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06209 | -0.17651 | 37
WERE | 'RICE 115KV' | 999 | -0.11442 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06209 | -0.17651 | 37
WERE | 'CLAY CENTER JUNCTION 115KV' | 17.044 | -0.10223 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06209 | -0.16432 | 40
WERE | 'PAWNEE 115KV' | 999 | -0.11442 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | 0.01967 | -0.13409 | 49
WERE | 'RICE 115KV' | 999 | -0.11442 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | 0.01967 | -0.13409 | 49
WERE | 'PAWNEE 115KV' | 999 | -0.11442 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | 0.01396 | -0.12838 | 51
WERE | 'RICE 115KV' | 999 | -0.11442 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | 0.01396 | -0.12838 | 51
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.28454 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | -0.1615 | -0.12304 | 53
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.22292 | WERE | 'CLAY CENTER JUNCTION 115KV' | 21.056 | -0.10223 | -0.12069 | 54
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22281 | WERE | 'CLAY CENTER JUNCTION 115KV' | 21.056 | -0.10223 | -0.12058 | 54
WERE | 'PAWNEE 115KV' | 999 | -0.11442 | WERE | 'LANG 7 345 345KV' | 310 | 0.0073 | -0.12172 | 54
WERE | 'PAWNEE 115KV' | 999 | -0.11442 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | 0.00682 | -0.12124 | 54
WERE | 'PAWNEE 115KV' | 999 | -0.11442 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 274.2987 | 0.00711 | -0.12153 | 54
WERE | 'PAWNEE 115KV' | 999 | -0.11442 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00621 | -0.12063 | 54
WERE | 'RICE 115KV' | 999 | -0.11442 | WERE | 'LANG 7 345 345KV' | 310 | 0.0073 | -0.12172 | 54
WERE | 'RICE 115KV' | 999 | -0.11442 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | 0.00682 | -0.12124 | 54
WERE | 'RICE 115KV' | 999 | -0.11442 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 274.2987 | 0.00711 | -0.12153 | 54
WERE | 'RICE 115KV' | 999 | -0.11442 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00621 | -0.12063 | 54
WERE | 'PAWNEE 115KV' | 999 | -0.11442 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.98 | 0.00213 | -0.11655 | 56
WERE | 'RICE 115KV' | 999 | -0.11442 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.98 | 0.00213 | -0.11655 | 56
WERE | 'PAWNEE 115KV' | 999 | -0.11442 | WERE | 'CHANUTE 69KV' | 55.637 | 0.00116 | -0.11558 | 57
WERE | 'PAWNEE 115KV' | 999 | -0.11442 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | 0.00019 | -0.11461 | 57
WERE | 'PAWNEE 115KV' | 999 | -0.11442 | WERE | 'CITY OF ERIE 69KV' | 23.374 | 0.00116 | -0.11558 | 57
WERE | 'PAWNEE 115KV' | 999 | -0.11442 | WERE | 'CITY OF IOLA 69KV' | 24.471 | 0.00138 | -0.1158 | 57
WERE | 'PAWNEE 115KV' | 999 | -0.11442 | WERE | 'EVANS ENERGY CENTER 138KV' | 320.8022 | -0.00011 | -0.11431 | 57
WERE | 'RICE 115KV' | 999 | -0.11442 | WERE | 'CHANUTE 69KV' | 55.637 | 0.00116 | -0.11558 | 57
WERE | 'RICE 115KV' | 999 | -0.11442 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | 0.00019 | -0.11461 | 57
WERE | 'RICE 115KV' | 999 | -0.11442 | WERE | 'CITY OF ERIE 69KV' | 23.374 | 0.00116 | -0.11558 | 57
WERE | 'RICE 115KV' | 999 | -0.11442 | WERE | 'CITY OF IOLA 69KV' | 24.471 | 0.00138 | -0.1158 | 57
WERE | 'RICE 115KV' | 999 | -0.11442 | WERE | 'EVANS ENERGY CENTER 138KV' | 320.8022 | -0.00011 | -0.11431 | 57
WERE | 'PAWNEE 115KV' | 999 | -0.11442 | WERE | 'CITY OF WELLINGTON 69KV' | 41.45 | -0.00153 | -0.11289 | 58
WERE | 'RICE 115KV' | 999 | -0.11442 | WERE | 'CITY OF WELLINGTON 69KV' | 41.45 | -0.00153 | -0.11289 | 58
WERE | 'PAWNEE 115KV' | 999 | -0.11442 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00287 | -0.11155 | 59
WERE | 'RICE 115KV' | 999 | -0.11442 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00287 | -0.11155 | 59
WERE | 'PAWNEE 115KV' | 999 | -0.11442 | WERE | 'KNOLL 3 115 115KV' | 75 | -0.03173 | -0.08269 | 79
WERE | 'RICE 115KV' | 999 | -0.11442 | WERE | 'KNOLL 3 115 115KV' | 75 | -0.03173 | -0.08269 | 79
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.00215 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06209 | -0.06424 | 102
WERE | 'CITY OF WINFIELD 69KV' | 40 | -0.00093 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06209 | -0.06302 | 104
WERE | 'EVANS ENERGY CENTER 138KV' | 486.1978 | -0.00011 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06209 | -0.0622 | 106
WERE | 'EVANS N4 138 16KV' | 360 | -0.0001 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06209 | -0.06219 | 106
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.28454 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 120 | -0.22292 | -0.06162 | 107
WERE | 'CLR_3 .575 34KV' | 300 | 0.00089 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06209 | -0.0612 | 107
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.22292 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | -0.1615 | -0.06142 | 107
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22281 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | -0.1615 | -0.06131 | 107
WERE | 'LATHAM1234.0 345KV' | 150 | 0.00089 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06209 | -0.0612 | 107
WERE | 'LYONS 115KV' | 999 | 0.00089 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06209 | -0.0612 | 107
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | WICHITA - RENO 345KV
Limiting Facility: | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1
Direction: | From->To
Line Outage: | EAST MCPHERSON - SUMMIT 230KV CKT 1
Flowgate: | 57368573721568725687312211SP
Date Redispatch Needed: | 6/1/09 - 7/1/09
Season Flowgate Identified: | 2011 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1140120 | 7.9976 | 23.6879
1161506 | 8.2668 | 23.6879
1161997 | 7.4235 | 23.6879
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28476 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06181 | -0.34657 | 68
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28476 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01916 | -0.30392 | 78
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28476 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01349 | -0.29825 | 79
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28476 | WERE | 'LANG 7 345 345KV' | 610 | 0.007 | -0.29176 | 81
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28476 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | 0.00644 | -0.2912 | 81
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28476 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 201.5866 | 0.00674 | -0.2915 | 81
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28476 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00582 | -0.29058 | 82
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28476 | WERE | 'CHANUTE 69KV' | 58.843 | 0.00106 | -0.28582 | 83
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28476 | WERE | 'EVANS ENERGY CENTER 138KV' | 331.6143 | -0.00025 | -0.28451 | 83
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.2231 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06181 | -0.28491 | 83
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22288 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06181 | -0.28469 | 83
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28476 | WERE | 'CITY OF WELLINGTON 69KV' | 41.45 | -0.00163 | -0.28313 | 84
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28476 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00296 | -0.2818 | 84
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.2231 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01916 | -0.24226 | 98
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22288 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01916 | -0.24204 | 98
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.2231 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01349 | -0.23659 | 100
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22288 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01349 | -0.23637 | 100
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.2231 | WERE | 'LANG 7 345 345KV' | 610 | 0.007 | -0.2301 | 103
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.2231 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | 0.00644 | -0.22954 | 103
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.2231 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 201.5866 | 0.00674 | -0.22984 | 103
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.2231 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00582 | -0.22892 | 103
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22288 | WERE | 'LANG 7 345 345KV' | 610 | 0.007 | -0.22988 | 103
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22288 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | 0.00644 | -0.22932 | 103
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22288 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 201.5866 | 0.00674 | -0.22962 | 103
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22288 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00582 | -0.2287 | 104
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.2231 | WERE | 'CHANUTE 69KV' | 58.843 | 0.00106 | -0.22416 | 106
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.2231 | WERE | 'EVANS ENERGY CENTER 138KV' | 331.6143 | -0.00025 | -0.22285 | 106
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22288 | WERE | 'CHANUTE 69KV' | 58.843 | 0.00106 | -0.22394 | 106
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22288 | WERE | 'EVANS ENERGY CENTER 138KV' | 331.6143 | -0.00025 | -0.22263 | 106
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.2231 | WERE | 'CITY OF WELLINGTON 69KV' | 41.45 | -0.00163 | -0.22147 | 107
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22288 | WERE | 'CITY OF WELLINGTON 69KV' | 41.45 | -0.00163 | -0.22125 | 107
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.2231 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00296 | -0.22014 | 108
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22288 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00296 | -0.21992 | 108
WERE | 'PAWNEE 115KV' | 999 | -0.11452 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06181 | -0.17633 | 134
WERE | 'RICE 115KV' | 999 | -0.11452 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06181 | -0.17633 | 134
WERE | 'PAWNEE 115KV' | 999 | -0.11452 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01916 | -0.13368 | 177
WERE | 'RICE 115KV' | 999 | -0.11452 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01916 | -0.13368 | 177
WERE | 'PAWNEE 115KV' | 999 | -0.11452 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01349 | -0.12801 | 185
WERE | 'RICE 115KV' | 999 | -0.11452 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01349 | -0.12801 | 185
WERE | 'PAWNEE 115KV' | 999 | -0.11452 | WERE | 'LANG 7 345 345KV' | 610 | 0.007 | -0.12152 | 195
WERE | 'PAWNEE 115KV' | 999 | -0.11452 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 201.5866 | 0.00674 | -0.12126 | 195
WERE | 'RICE 115KV' | 999 | -0.11452 | WERE | 'LANG 7 345 345KV' | 610 | 0.007 | -0.12152 | 195
WERE | 'RICE 115KV' | 999 | -0.11452 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 201.5866 | 0.00674 | -0.12126 | 195
WERE | 'PAWNEE 115KV' | 999 | -0.11452 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | 0.00644 | -0.12096 | 196
WERE | 'RICE 115KV' | 999 | -0.11452 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | 0.00644 | -0.12096 | 196
WERE | 'PAWNEE 115KV' | 999 | -0.11452 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00582 | -0.12034 | 197
WERE | 'RICE 115KV' | 999 | -0.11452 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00582 | -0.12034 | 197
WERE | 'PAWNEE 115KV' | 999 | -0.11452 | WERE | 'EVANS ENERGY CENTER 138KV' | 331.6143 | -0.00025 | -0.11427 | 207
WERE | 'RICE 115KV' | 999 | -0.11452 | WERE | 'EVANS ENERGY CENTER 138KV' | 331.6143 | -0.00025 | -0.11427 | 207
WERE | 'PAWNEE 115KV' | 999 | -0.11452 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00296 | -0.11156 | 212
WERE | 'RICE 115KV' | 999 | -0.11452 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00296 | -0.11156 | 212
WERE | 'EVANS ENERGY CENTER 138KV' | 475.3857 | -0.00025 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06181 | -0.06206 | 382
WERE | 'EVANS N4 138 16KV' | 360 | -0.00024 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06181 | -0.06205 | 382
WERE | 'CLR_3 .575 34KV' | 300 | 0.00072 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06181 | -0.06109 | 388
WERE | 'LATHAM1234.0 345KV' | 150 | 0.00072 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06181 | -0.06109 | 388
WERE | 'LYONS 115KV' | 999 | 0.00084 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06181 | -0.06097 | 389
WERE | 'LANG 7 345 345KV' | 218 | 0.007 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06181 | -0.05481 | 432
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | WICHITA - RENO 345KV
Limiting Facility: | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1
Direction: | From->To
Line Outage: | NORTHVIEW - SUMMIT 115KV CKT 1
Flowgate: | 57368573721573715738112208SP
Date Redispatch Needed: | Starting 2008 6/1 - 10/1 Until EOC of Upgrade
Season Flowgate Identified: | 2008 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1161506 | 3.1979 | 6.2824
1161997 | 3.0845 | 6.2824
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.35542 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08284 | -0.43826 | 14
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.35542 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | 0.01102 | -0.36644 | 17
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.35542 | WERE | 'KNOLL 3 115 115KV' | 75 | 0.01715 | -0.37257 | 17
WERE | 'CLAY CENTER JUNCTION 115KV' | 17.044 | -0.23392 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08284 | -0.31676 | 20
WERE | 'CLAY CENTER JUNCTION 115KV' | 17.044 | -0.23392 | WERE | 'KNOLL 3 115 115KV' | 75 | 0.01715 | -0.25107 | 25
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.16261 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08284 | -0.24545 | 26
WERE | 'CLAY CENTER JUNCTION 115KV' | 17.044 | -0.23392 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | 0.01102 | -0.24494 | 26
WERE | 'CLAY CENTER JUNCTION 115KV' | 17.044 | -0.23392 | WERE | 'CHANUTE 69KV' | 55.637 | -8e-05 | -0.23384 | 27
WERE | 'CLAY CENTER JUNCTION 115KV' | 17.044 | -0.23392 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | -0.00076 | -0.23316 | 27
WERE | 'CLAY CENTER JUNCTION 115KV' | 17.044 | -0.23392 | WERE | 'CITY OF ERIE 69KV' | 23.374 | -8e-05 | -0.23384 | 27
WERE | 'CLAY CENTER JUNCTION 115KV' | 17.044 | -0.23392 | WERE | 'CITY OF IOLA 69KV' | 24.471 | 0 | -0.23392 | 27
WERE | 'CLAY CENTER JUNCTION 115KV' | 17.044 | -0.23392 | WERE | 'CITY OF WELLINGTON 69KV' | 41.45 | -0.001 | -0.23292 | 27
WERE | 'CLAY CENTER JUNCTION 115KV' | 17.044 | -0.23392 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.98 | -4e-05 | -0.23388 | 27
WERE | 'CLAY CENTER JUNCTION 115KV' | 17.044 | -0.23392 | WERE | 'EVANS ENERGY CENTER 138KV' | 320.8022 | -0.00076 | -0.23316 | 27
WERE | 'CLAY CENTER JUNCTION 115KV' | 17.044 | -0.23392 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00151 | -0.23241 | 27
WERE | 'CLAY CENTER JUNCTION 115KV' | 17.044 | -0.23392 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | 0.00237 | -0.23629 | 27
WERE | 'CLAY CENTER JUNCTION 115KV' | 17.044 | -0.23392 | WERE | 'LANG 7 345 345KV' | 310 | 0.00063 | -0.23455 | 27
WERE | 'CLAY CENTER JUNCTION 115KV' | 17.044 | -0.23392 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | -0.00152 | -0.2324 | 27
WERE | 'CLAY CENTER JUNCTION 115KV' | 17.044 | -0.23392 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 274.2987 | -0.00168 | -0.23224 | 27
WERE | 'CLAY CENTER JUNCTION 115KV' | 17.044 | -0.23392 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | -0.00421 | -0.22971 | 27
WERE | 'CLAY CENTER JUNCTION 115KV' | 17.044 | -0.23392 | WERE | 'WACO 138KV' | 17.967 | -0.00143 | -0.23249 | 27
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.16261 | WERE | 'KNOLL 3 115 115KV' | 75 | 0.01715 | -0.17976 | 35
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.09467 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08284 | -0.17751 | 35
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.09461 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08284 | -0.17745 | 35
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.16261 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | 0.01102 | -0.17363 | 36
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.16261 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | 0.00237 | -0.16498 | 38
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.16261 | WERE | 'LANG 7 345 345KV' | 310 | 0.00063 | -0.16324 | 38
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.16261 | WERE | 'CHANUTE 69KV' | 55.637 | -8e-05 | -0.16253 | 39
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.16261 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | -0.00076 | -0.16185 | 39
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.16261 | WERE | 'CITY OF ERIE 69KV' | 23.374 | -8e-05 | -0.16253 | 39
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.16261 | WERE | 'CITY OF IOLA 69KV' | 24.471 | 0 | -0.16261 | 39
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.16261 | WERE | 'CITY OF WELLINGTON 69KV' | 41.45 | -0.001 | -0.16161 | 39
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.16261 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.98 | -4e-05 | -0.16257 | 39
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.16261 | WERE | 'EVANS ENERGY CENTER 138KV' | 320.8022 | -0.00076 | -0.16185 | 39
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.16261 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00151 | -0.1611 | 39
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.16261 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | -0.00152 | -0.16109 | 39
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.16261 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 274.2987 | -0.00168 | -0.16093 | 39
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.16261 | WERE | 'WACO 138KV' | 17.967 | -0.00143 | -0.16118 | 39
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.16261 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | -0.00421 | -0.1584 | 40
WERE | 'CLAY CENTER JUNCTION 115KV' | 17.044 | -0.23392 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 120 | -0.09467 | -0.13925 | 45
WERE | 'PAWNEE 115KV' | 999 | -0.03606 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08284 | -0.1189 | 53
WERE | 'RICE 115KV' | 999 | -0.03606 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08284 | -0.1189 | 53
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.09467 | WERE | 'KNOLL 3 115 115KV' | 75 | 0.01715 | -0.11182 | 56
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.09461 | WERE | 'KNOLL 3 115 115KV' | 75 | 0.01715 | -0.11176 | 56
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.09467 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | 0.01102 | -0.10569 | 59
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.09461 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | 0.01102 | -0.10563 | 59
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.09467 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | 0.00237 | -0.09704 | 65
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.09461 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | 0.00237 | -0.09698 | 65
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.09467 | WERE | 'CHANUTE 69KV' | 55.637 | -8e-05 | -0.09459 | 66
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.09467 | WERE | 'CITY OF ERIE 69KV' | 23.374 | -8e-05 | -0.09459 | 66
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.09467 | WERE | 'CITY OF IOLA 69KV' | 24.471 | 0 | -0.09467 | 66
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.09467 | WERE | 'LANG 7 345 345KV' | 310 | 0.00063 | -0.0953 | 66
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.09461 | WERE | 'CHANUTE 69KV' | 55.637 | -8e-05 | -0.09453 | 66
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.09461 | WERE | 'CITY OF ERIE 69KV' | 23.374 | -8e-05 | -0.09453 | 66
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.09461 | WERE | 'CITY OF IOLA 69KV' | 24.471 | 0 | -0.09461 | 66
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.09461 | WERE | 'LANG 7 345 345KV' | 310 | 0.00063 | -0.09524 | 66
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.09467 | WERE | 'CITY OF WELLINGTON 69KV' | 41.45 | -0.001 | -0.09367 | 67
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.09467 | WERE | 'EVANS ENERGY CENTER 138KV' | 320.8022 | -0.00076 | -0.09391 | 67
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.09467 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00151 | -0.09316 | 67
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.09467 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | -0.00152 | -0.09315 | 67
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.09461 | WERE | 'CITY OF WELLINGTON 69KV' | 41.45 | -0.001 | -0.09361 | 67
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.09461 | WERE | 'EVANS ENERGY CENTER 138KV' | 320.8022 | -0.00076 | -0.09385 | 67
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.09461 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00151 | -0.0931 | 67
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.09461 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | -0.00152 | -0.09309 | 67
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.09467 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 274.2987 | -0.00168 | -0.09299 | 68
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.09461 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 274.2987 | -0.00168 | -0.09293 | 68
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.09467 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | -0.00421 | -0.09046 | 69
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.09461 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | -0.00421 | -0.0904 | 69
WERE | 'TECUMSEH ENERGY CENTER 115KV' | 53 | -0.00421 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08284 | -0.08705 | 72
WERE | 'TECUMSEH ENERGY CENTER 69KV' | 41 | -0.00469 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08284 | -0.08753 | 72
WERE | 'LAWRENCE ENERGY CENTER 115KV' | 28 | -0.00152 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08284 | -0.08436 | 74
WERE | 'CITY OF WINFIELD 69KV' | 40 | -0.00079 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08284 | -0.08363 | 75
WERE | 'EVANS ENERGY CENTER 138KV' | 486.1978 | -0.00076 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08284 | -0.0836 | 75
WERE | 'EVANS N4 138 16KV' | 360 | -0.00075 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08284 | -0.08359 | 75
WERE | 'GETTY 69KV' | 35 | -0.00078 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08284 | -0.08362 | 75
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.0013 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08284 | -0.08414 | 75
WERE | 'CHANUTE 69KV' | 32.163 | -8e-05 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08284 | -0.08292 | 76
WERE | 'CLR_3 .575 34KV' | 300 | -0.00035 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08284 | -0.08319 | 76
WERE | 'LANG 7 345 345KV' | 518 | 0.00063 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08284 | -0.08221 | 76
WERE | 'LATHAM1234.0 345KV' | 150 | -0.00035 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08284 | -0.08319 | 76
WERE | 'LYONS 115KV' | 999 | 5e-05 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08284 | -0.08279 | 76
WERE | 'NEOSHO ENERGY CENTER 138KV' | 67 | -6e-05 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08284 | -0.0829 | 76
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.16261 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 120 | -0.09467 | -0.06794 | 92
WERE | 'PAWNEE 115KV' | 999 | -0.03606 | WERE | 'KNOLL 3 115 115KV' | 75 | 0.01715 | -0.05321 | 118
WERE | 'RICE 115KV' | 999 | -0.03606 | WERE | 'KNOLL 3 115 115KV' | 75 | 0.01715 | -0.05321 | 118
WERE | 'PAWNEE 115KV' | 999 | -0.03606 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | 0.01102 | -0.04708 | 133
WERE | 'RICE 115KV' | 999 | -0.03606 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | 0.01102 | -0.04708 | 133
WERE | 'PAWNEE 115KV' | 999 | -0.03606 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | 0.00237 | -0.03843 | 163
WERE | 'RICE 115KV' | 999 | -0.03606 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | 0.00237 | -0.03843 | 163
WERE | 'PAWNEE 115KV' | 999 | -0.03606 | WERE | 'LANG 7 345 345KV' | 310 | 0.00063 | -0.03669 | 171
WERE | 'RICE 115KV' | 999 | -0.03606 | WERE | 'LANG 7 345 345KV' | 310 | 0.00063 | -0.03669 | 171
WERE | 'PAWNEE 115KV' | 999 | -0.03606 | WERE | 'EVANS ENERGY CENTER 138KV' | 320.8022 | -0.00076 | -0.0353 | 178
WERE | 'RICE 115KV' | 999 | -0.03606 | WERE | 'EVANS ENERGY CENTER 138KV' | 320.8022 | -0.00076 | -0.0353 | 178
WERE | 'PAWNEE 115KV' | 999 | -0.03606 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00151 | -0.03455 | 182
WERE | 'PAWNEE 115KV' | 999 | -0.03606 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | -0.00152 | -0.03454 | 182
WERE | 'RICE 115KV' | 999 | -0.03606 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00151 | -0.03455 | 182
WERE | 'RICE 115KV' | 999 | -0.03606 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | -0.00152 | -0.03454 | 182
WERE | 'PAWNEE 115KV' | 999 | -0.03606 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 274.2987 | -0.00168 | -0.03438 | 183
WERE | 'RICE 115KV' | 999 | -0.03606 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 274.2987 | -0.00168 | -0.03438 | 183
WERE | 'PAWNEE 115KV' | 999 | -0.03606 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | -0.00421 | -0.03185 | 197
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | WICHITA - RENO 345KV
Limiting Facility: | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1
Direction: | From->To
Line Outage: | NORTHVIEW - SUMMIT 115KV CKT 1
Flowgate: | 57368573721573715738112211SP
Date Redispatch Needed: | 6/1/09 - 7/1/09
Season Flowgate Identified: | 2011 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1140120 | 6.0922 | 18.4885
1161506 | 6.2814 | 18.4885
1161997 | 6.1148 | 18.4885
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.16271 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08273 | -0.24544 | 75
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.09476 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08273 | -0.17749 | 104
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.09464 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08273 | -0.17737 | 104
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.16271 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01086 | -0.17357 | 107
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.16271 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.00225 | -0.16496 | 112
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.16271 | WERE | 'LANG 7 345 345KV' | 610 | 0.00057 | -0.16328 | 113
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.16271 | WERE | 'CHANUTE 69KV' | 58.843 | -0.00011 | -0.1626 | 114
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.16271 | WERE | 'CITY OF WELLINGTON 69KV' | 41.45 | -0.00103 | -0.16168 | 114
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.16271 | WERE | 'EVANS ENERGY CENTER 138KV' | 331.6143 | -0.00079 | -0.16192 | 114
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.16271 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00153 | -0.16118 | 115
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.16271 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | -0.00148 | -0.16123 | 115
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.16271 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 201.5866 | -0.00167 | -0.16104 | 115
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.16271 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | -0.00428 | -0.15843 | 117
WERE | 'PAWNEE 115KV' | 999 | -0.03611 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08273 | -0.11884 | 156
WERE | 'RICE 115KV' | 999 | -0.03611 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08273 | -0.11884 | 156
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.09476 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01086 | -0.10562 | 175
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.09464 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01086 | -0.1055 | 175
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.09476 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.00225 | -0.09701 | 191
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.09464 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.00225 | -0.09689 | 191
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.09476 | WERE | 'LANG 7 345 345KV' | 610 | 0.00057 | -0.09533 | 194
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.09464 | WERE | 'LANG 7 345 345KV' | 610 | 0.00057 | -0.09521 | 194
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.09476 | WERE | 'EVANS ENERGY CENTER 138KV' | 331.6143 | -0.00079 | -0.09397 | 197
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.09464 | WERE | 'EVANS ENERGY CENTER 138KV' | 331.6143 | -0.00079 | -0.09385 | 197
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.09476 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00153 | -0.09323 | 198
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.09476 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | -0.00148 | -0.09328 | 198
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.09464 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | -0.00148 | -0.09316 | 198
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.09476 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 201.5866 | -0.00167 | -0.09309 | 199
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.09464 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00153 | -0.09311 | 199
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.09464 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 201.5866 | -0.00167 | -0.09297 | 199
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.09476 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | -0.00428 | -0.09048 | 204
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.00133 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08273 | -0.08406 | 220
WERE | 'EVANS ENERGY CENTER 138KV' | 475.3857 | -0.00079 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08273 | -0.08352 | 221
WERE | 'EVANS N4 138 16KV' | 360 | -0.00079 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08273 | -0.08352 | 221
WERE | 'CLR_3 .575 34KV' | 300 | -0.00039 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08273 | -0.08312 | 222
WERE | 'LATHAM1234.0 345KV' | 150 | -0.00039 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08273 | -0.08312 | 222
WERE | 'LYONS 115KV' | 999 | 4e-05 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08273 | -0.08269 | 224
WERE | 'LANG 7 345 345KV' | 218 | 0.00057 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08273 | -0.08216 | 225
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.16271 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 120 | -0.09476 | -0.06795 | 272
WERE | 'PAWNEE 115KV' | 999 | -0.03611 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01086 | -0.04697 | 394
WERE | 'RICE 115KV' | 999 | -0.03611 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01086 | -0.04697 | 394
WERE | 'PAWNEE 115KV' | 999 | -0.03611 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.00225 | -0.03836 | 482
WERE | 'RICE 115KV' | 999 | -0.03611 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.00225 | -0.03836 | 482
WERE | 'PAWNEE 115KV' | 999 | -0.03611 | WERE | 'LANG 7 345 345KV' | 610 | 0.00057 | -0.03668 | 504
WERE | 'RICE 115KV' | 999 | -0.03611 | WERE | 'LANG 7 345 345KV' | 610 | 0.00057 | -0.03668 | 504
WERE | 'PAWNEE 115KV' | 999 | -0.03611 | WERE | 'EVANS ENERGY CENTER 138KV' | 331.6143 | -0.00079 | -0.03532 | 523
WERE | 'RICE 115KV' | 999 | -0.03611 | WERE | 'EVANS ENERGY CENTER 138KV' | 331.6143 | -0.00079 | -0.03532 | 523
WERE | 'PAWNEE 115KV' | 999 | -0.03611 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 201.5866 | -0.00167 | -0.03444 | 537
WERE | 'RICE 115KV' | 999 | -0.03611 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 201.5866 | -0.00167 | -0.03444 | 537
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | WICHITA - RENO 345KV
Limiting Facility: | EXIDE JUNCTION - SUMMIT 115KV CKT 1
Direction: | To->From
Line Outage: | EAST MCPHERSON - SUMMIT 230KV CKT 1
Flowgate: | 57368573811568725687312207SH
Date Redispatch Needed: | 6/1/07 - 10/1/07 Until EOC of Upgrade
Season Flowgate Identified: | 2007 Summer Shoulder
Reservation | Relief Amount | Aggregate Relief Amount
1161997 | 12.186 | 12.186
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29562 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02299 | -0.31861 | 38
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29562 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01718 | -0.3128 | 39
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29562 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.0088 | -0.30442 | 40
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29562 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 235.3866 | 0.00919 | -0.30481 | 40
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29562 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00844 | -0.30406 | 40
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29562 | WERE | 'CHANUTE 69KV' | 46.617 | 0.00149 | -0.29711 | 41
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29562 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | 0.00049 | -0.29611 | 41
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29562 | WERE | 'CITY OF ERIE 69KV' | 23.258 | 0.00149 | -0.29711 | 41
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29562 | WERE | 'CITY OF IOLA 69KV' | 19.865 | 0.00174 | -0.29736 | 41
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29562 | WERE | 'CITY OF WELLINGTON 69KV' | 31.07 | -0.00165 | -0.29397 | 41
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29562 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.96 | 0.00282 | -0.29844 | 41
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29562 | WERE | 'EVANS ENERGY CENTER 138KV' | 269.2019 | 0.00013 | -0.29575 | 41
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29562 | WERE | 'GILL ENERGY CENTER 138KV' | 77 | -0.00315 | -0.29247 | 42
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29562 | WERE | 'WACO 138KV' | 17.947 | -0.00282 | -0.2928 | 42
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.23794 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02299 | -0.26093 | 47
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.23783 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02299 | -0.26082 | 47
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.23794 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01718 | -0.25512 | 48
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.23783 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01718 | -0.25501 | 48
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.23794 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.0088 | -0.24674 | 49
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.23794 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 235.3866 | 0.00919 | -0.24713 | 49
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.23794 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00844 | -0.24638 | 49
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.23783 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.0088 | -0.24663 | 49
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.23783 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 235.3866 | 0.00919 | -0.24702 | 49
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.23783 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00844 | -0.24627 | 49
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.23794 | WERE | 'CHANUTE 69KV' | 46.617 | 0.00149 | -0.23943 | 51
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.23794 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | 0.00049 | -0.23843 | 51
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.23794 | WERE | 'CITY OF ERIE 69KV' | 23.258 | 0.00149 | -0.23943 | 51
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.23794 | WERE | 'CITY OF IOLA 69KV' | 19.865 | 0.00174 | -0.23968 | 51
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.23794 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.96 | 0.00282 | -0.24076 | 51
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.23794 | WERE | 'EVANS ENERGY CENTER 138KV' | 269.2019 | 0.00013 | -0.23807 | 51
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.23783 | WERE | 'CHANUTE 69KV' | 46.617 | 0.00149 | -0.23932 | 51
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.23783 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | 0.00049 | -0.23832 | 51
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.23783 | WERE | 'CITY OF ERIE 69KV' | 23.258 | 0.00149 | -0.23932 | 51
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.23783 | WERE | 'CITY OF IOLA 69KV' | 19.865 | 0.00174 | -0.23957 | 51
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.23783 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.96 | 0.00282 | -0.24065 | 51
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.23783 | WERE | 'EVANS ENERGY CENTER 138KV' | 269.2019 | 0.00013 | -0.23796 | 51
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.23794 | WERE | 'CITY OF WELLINGTON 69KV' | 31.07 | -0.00165 | -0.23629 | 52
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.23794 | WERE | 'GILL ENERGY CENTER 138KV' | 77 | -0.00315 | -0.23479 | 52
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.23794 | WERE | 'WACO 138KV' | 17.947 | -0.00282 | -0.23512 | 52
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.23783 | WERE | 'CITY OF WELLINGTON 69KV' | 31.07 | -0.00165 | -0.23618 | 52
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.23783 | WERE | 'GILL ENERGY CENTER 138KV' | 77 | -0.00315 | -0.23468 | 52
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.23783 | WERE | 'WACO 138KV' | 17.947 | -0.00282 | -0.23501 | 52
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.15727 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02299 | -0.18026 | 68
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.15727 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01718 | -0.17445 | 70
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.15727 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.0088 | -0.16607 | 73
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.15727 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 235.3866 | 0.00919 | -0.16646 | 73
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.15727 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00844 | -0.16571 | 74
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.15727 | WERE | 'CHANUTE 69KV' | 46.617 | 0.00149 | -0.15876 | 77
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.15727 | WERE | 'EVANS ENERGY CENTER 138KV' | 269.2019 | 0.00013 | -0.1574 | 77
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.15727 | WERE | 'CITY OF WELLINGTON 69KV' | 31.07 | -0.00165 | -0.15562 | 78
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.15727 | WERE | 'GILL ENERGY CENTER 138KV' | 77 | -0.00315 | -0.15412 | 79
WERE | 'PAWNEE 115KV' | 999 | -0.13182 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02299 | -0.15481 | 79
WERE | 'RICE 115KV' | 999 | -0.13182 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02299 | -0.15481 | 79
WERE | 'PAWNEE 115KV' | 999 | -0.13182 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01718 | -0.149 | 82
WERE | 'RICE 115KV' | 999 | -0.13182 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01718 | -0.149 | 82
WERE | 'PAWNEE 115KV' | 999 | -0.13182 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 235.3866 | 0.00919 | -0.14101 | 86
WERE | 'RICE 115KV' | 999 | -0.13182 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 235.3866 | 0.00919 | -0.14101 | 86
WERE | 'PAWNEE 115KV' | 999 | -0.13182 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.0088 | -0.14062 | 87
WERE | 'PAWNEE 115KV' | 999 | -0.13182 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00844 | -0.14026 | 87
WERE | 'RICE 115KV' | 999 | -0.13182 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | 0.0088 | -0.14062 | 87
WERE | 'RICE 115KV' | 999 | -0.13182 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00844 | -0.14026 | 87
WERE | 'PAWNEE 115KV' | 999 | -0.13182 | WERE | 'CHANUTE 69KV' | 46.617 | 0.00149 | -0.13331 | 91
WERE | 'RICE 115KV' | 999 | -0.13182 | WERE | 'CHANUTE 69KV' | 46.617 | 0.00149 | -0.13331 | 91
WERE | 'PAWNEE 115KV' | 999 | -0.13182 | WERE | 'EVANS ENERGY CENTER 138KV' | 269.2019 | 0.00013 | -0.13195 | 92
WERE | 'RICE 115KV' | 999 | -0.13182 | WERE | 'EVANS ENERGY CENTER 138KV' | 269.2019 | 0.00013 | -0.13195 | 92
WERE | 'PAWNEE 115KV' | 999 | -0.13182 | WERE | 'GILL ENERGY CENTER 138KV' | 77 | -0.00315 | -0.12867 | 95
WERE | 'RICE 115KV' | 999 | -0.13182 | WERE | 'GILL ENERGY CENTER 138KV' | 77 | -0.00315 | -0.12867 | 95
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.29562 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 80 | -0.23794 | -0.05768 | 211
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | WICHITA - RENO 345KV
Limiting Facility: | EXIDE JUNCTION - SUMMIT 115KV CKT 1
Direction: | To->From
Line Outage: | EAST MCPHERSON - SUMMIT 230KV CKT 1
Flowgate: | 57368573811568725687312207WP
Date Redispatch Needed: | 12/1/07 - 4/1/08
Season Flowgate Identified: | 2007 Winter Peak
Reservation | Relief Amount | Aggregate Relief Amount
1161997 | 4.0249 | 4.0249
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28455 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06208 | -0.34663 | 12
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28455 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01396 | -0.29851 | 13
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28455 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01966 | -0.30421 | 13
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28455 | WERE | 'CHANUTE 69KV' | 34.818 | 0.00116 | -0.28571 | 14
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28455 | WERE | 'CITY OF AUGUSTA 69KV' | 14.628 | 0.00021 | -0.28476 | 14
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28455 | WERE | 'CITY OF BURLINGTON 69KV' | 4.8 | 0.00217 | -0.28672 | 14
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28455 | WERE | 'CITY OF IOLA 69KV' | 14.565 | 0.00137 | -0.28592 | 14
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28455 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00151 | -0.28304 | 14
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28455 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.95 | 0.00217 | -0.28672 | 14
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28455 | WERE | 'EVANS ENERGY CENTER 138KV' | 46.665 | -9e-05 | -0.28446 | 14
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28455 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 136.4686 | 0.0071 | -0.29165 | 14
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28455 | WERE | 'WACO 138KV' | 17.93 | -0.00257 | -0.28198 | 14
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.22293 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06208 | -0.28501 | 14
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22282 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06208 | -0.2849 | 14
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28455 | WERE | 'COLBY 115KV' | 7.2302 | -0.03493 | -0.24962 | 16
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.22293 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01396 | -0.23689 | 17
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.22293 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01966 | -0.24259 | 17
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.22293 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 136.4686 | 0.0071 | -0.23003 | 17
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22282 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01396 | -0.23678 | 17
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22282 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01966 | -0.24248 | 17
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.1615 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06208 | -0.22358 | 18
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.22293 | WERE | 'CHANUTE 69KV' | 34.818 | 0.00116 | -0.22409 | 18
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.22293 | WERE | 'CITY OF AUGUSTA 69KV' | 14.628 | 0.00021 | -0.22314 | 18
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.22293 | WERE | 'CITY OF IOLA 69KV' | 14.565 | 0.00137 | -0.2243 | 18
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.22293 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00151 | -0.22142 | 18
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.22293 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.95 | 0.00217 | -0.2251 | 18
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.22293 | WERE | 'EVANS ENERGY CENTER 138KV' | 46.665 | -9e-05 | -0.22284 | 18
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.22293 | WERE | 'WACO 138KV' | 17.93 | -0.00257 | -0.22036 | 18
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22282 | WERE | 'CHANUTE 69KV' | 34.818 | 0.00116 | -0.22398 | 18
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22282 | WERE | 'CITY OF AUGUSTA 69KV' | 14.628 | 0.00021 | -0.22303 | 18
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22282 | WERE | 'CITY OF IOLA 69KV' | 14.565 | 0.00137 | -0.22419 | 18
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22282 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00151 | -0.22131 | 18
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22282 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.95 | 0.00217 | -0.22499 | 18
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22282 | WERE | 'EVANS ENERGY CENTER 138KV' | 46.665 | -9e-05 | -0.22273 | 18
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22282 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 136.4686 | 0.0071 | -0.22992 | 18
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22282 | WERE | 'WACO 138KV' | 17.93 | -0.00257 | -0.22025 | 18
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.22293 | WERE | 'COLBY 115KV' | 7.2302 | -0.03493 | -0.188 | 21
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22282 | WERE | 'COLBY 115KV' | 7.2302 | -0.03493 | -0.18789 | 21
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.1615 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01966 | -0.18116 | 22
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.1615 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01396 | -0.17546 | 23
WERE | 'PAWNEE 115KV' | 999 | -0.11443 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06208 | -0.17651 | 23
WERE | 'RICE 115KV' | 999 | -0.11443 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06208 | -0.17651 | 23
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.1615 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 136.4686 | 0.0071 | -0.1686 | 24
WERE | 'CLAY CENTER JUNCTION 115KV' | 31.4 | -0.10224 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06208 | -0.16432 | 24
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.1615 | WERE | 'CHANUTE 69KV' | 34.818 | 0.00116 | -0.16266 | 25
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.1615 | WERE | 'CITY OF AUGUSTA 69KV' | 14.628 | 0.00021 | -0.16171 | 25
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.1615 | WERE | 'CITY OF IOLA 69KV' | 14.565 | 0.00137 | -0.16287 | 25
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.1615 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00151 | -0.15999 | 25
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.1615 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.95 | 0.00217 | -0.16367 | 25
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.1615 | WERE | 'EVANS ENERGY CENTER 138KV' | 46.665 | -9e-05 | -0.16141 | 25
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.1615 | WERE | 'WACO 138KV' | 17.93 | -0.00257 | -0.15893 | 25
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.09113 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06208 | -0.15321 | 26
WERE | 'PAWNEE 115KV' | 999 | -0.11443 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01966 | -0.13409 | 30
WERE | 'RICE 115KV' | 999 | -0.11443 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01966 | -0.13409 | 30
WERE | 'PAWNEE 115KV' | 999 | -0.11443 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01396 | -0.12839 | 31
WERE | 'RICE 115KV' | 999 | -0.11443 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01396 | -0.12839 | 31
WERE | 'CLAY CENTER JUNCTION 115KV' | 31.4 | -0.10224 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01966 | -0.1219 | 33
WERE | 'PAWNEE 115KV' | 999 | -0.11443 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 136.4686 | 0.0071 | -0.12153 | 33
WERE | 'RICE 115KV' | 999 | -0.11443 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 136.4686 | 0.0071 | -0.12153 | 33
WERE | 'CLAY CENTER JUNCTION 115KV' | 31.4 | -0.10224 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01396 | -0.1162 | 35
WERE | 'PAWNEE 115KV' | 999 | -0.11443 | WERE | 'CHANUTE 69KV' | 34.818 | 0.00116 | -0.11559 | 35
WERE | 'PAWNEE 115KV' | 999 | -0.11443 | WERE | 'CITY OF AUGUSTA 69KV' | 14.628 | 0.00021 | -0.11464 | 35
WERE | 'PAWNEE 115KV' | 999 | -0.11443 | WERE | 'CITY OF IOLA 69KV' | 14.565 | 0.00137 | -0.1158 | 35
WERE | 'PAWNEE 115KV' | 999 | -0.11443 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.95 | 0.00217 | -0.1166 | 35
WERE | 'PAWNEE 115KV' | 999 | -0.11443 | WERE | 'EVANS ENERGY CENTER 138KV' | 46.665 | -9e-05 | -0.11434 | 35
WERE | 'RICE 115KV' | 999 | -0.11443 | WERE | 'CHANUTE 69KV' | 34.818 | 0.00116 | -0.11559 | 35
WERE | 'RICE 115KV' | 999 | -0.11443 | WERE | 'CITY OF AUGUSTA 69KV' | 14.628 | 0.00021 | -0.11464 | 35
WERE | 'RICE 115KV' | 999 | -0.11443 | WERE | 'CITY OF IOLA 69KV' | 14.565 | 0.00137 | -0.1158 | 35
WERE | 'RICE 115KV' | 999 | -0.11443 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.95 | 0.00217 | -0.1166 | 35
WERE | 'RICE 115KV' | 999 | -0.11443 | WERE | 'EVANS ENERGY CENTER 138KV' | 46.665 | -9e-05 | -0.11434 | 35
WERE | 'PAWNEE 115KV' | 999 | -0.11443 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00151 | -0.11292 | 36
WERE | 'PAWNEE 115KV' | 999 | -0.11443 | WERE | 'WACO 138KV' | 17.93 | -0.00257 | -0.11186 | 36
WERE | 'RICE 115KV' | 999 | -0.11443 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00151 | -0.11292 | 36
WERE | 'RICE 115KV' | 999 | -0.11443 | WERE | 'WACO 138KV' | 17.93 | -0.00257 | -0.11186 | 36
WERE | 'CLAY CENTER JUNCTION 115KV' | 31.4 | -0.10224 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 136.4686 | 0.0071 | -0.10934 | 37
WERE | 'CLAY CENTER JUNCTION 115KV' | 31.4 | -0.10224 | WERE | 'CHANUTE 69KV' | 34.818 | 0.00116 | -0.1034 | 39
WERE | 'CLAY CENTER JUNCTION 115KV' | 31.4 | -0.10224 | WERE | 'CITY OF AUGUSTA 69KV' | 14.628 | 0.00021 | -0.10245 | 39
WERE | 'CLAY CENTER JUNCTION 115KV' | 31.4 | -0.10224 | WERE | 'CITY OF IOLA 69KV' | 14.565 | 0.00137 | -0.10361 | 39
WERE | 'CLAY CENTER JUNCTION 115KV' | 31.4 | -0.10224 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.95 | 0.00217 | -0.10441 | 39
WERE | 'CLAY CENTER JUNCTION 115KV' | 31.4 | -0.10224 | WERE | 'EVANS ENERGY CENTER 138KV' | 46.665 | -9e-05 | -0.10215 | 39
WERE | 'CLAY CENTER JUNCTION 115KV' | 31.4 | -0.10224 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00151 | -0.10073 | 40
WERE | 'CLAY CENTER JUNCTION 115KV' | 31.4 | -0.10224 | WERE | 'WACO 138KV' | 17.93 | -0.00257 | -0.09967 | 40
WERE | 'KNOLL 3 115 115KV' | 84.36 | -0.03174 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06208 | -0.09382 | 43
WERE | 'GILL ENERGY CENTER 138KV' | 218 | -0.00285 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06208 | -0.06493 | 62
WERE | 'CITY OF WELLINGTON 69KV' | 23.5 | -0.00151 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06208 | -0.06359 | 63
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.00213 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06208 | -0.06421 | 63
WERE | 'CITY OF WINFIELD 69KV' | 40 | -0.00091 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06208 | -0.06299 | 64
WERE | 'EVANS ENERGY CENTER 138KV' | 746.335 | -9e-05 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06208 | -0.06217 | 65
WERE | 'EVANS N4 138 16KV' | 360 | -8e-05 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06208 | -0.06216 | 65
WERE | 'GETTY 69KV' | 35 | 0.00049 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06208 | -0.06159 | 65
WERE | 'CHANUTE 69KV' | 52.982 | 0.00116 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06208 | -0.06092 | 66
WERE | 'CITY OF ERIE 69KV' | 24.535 | 0.00116 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06208 | -0.06092 | 66
WERE | 'CITY OF IOLA 69KV' | 23.063 | 0.00137 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06208 | -0.06071 | 66
WERE | 'CLR_3 .575 34KV' | 300 | 0.00091 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06208 | -0.06117 | 66
WERE | 'LATHAM1234.0 345KV' | 150 | 0.00091 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06208 | -0.06117 | 66
WERE | 'LYONS 115KV' | 999 | 0.0009 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06208 | -0.06118 | 66
WERE | 'NEOSHO ENERGY CENTER 138KV' | 67 | 0.00112 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06208 | -0.06096 | 66
WERE | 'TECUMSEH ENERGY CENTER 115KV' | 243 | 0.00621 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06208 | -0.05587 | 72
WERE | 'TECUMSEH ENERGY CENTER 69KV' | 41 | 0.00616 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06208 | -0.05592 | 72
WERE | 'LANG 7 345 345KV' | 828 | 0.0073 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06208 | -0.05478 | 73
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | WICHITA - RENO 345KV
Limiting Facility: | EXIDE JUNCTION - SUMMIT 115KV CKT 1
Direction: | To->From
Line Outage: | EAST MCPHERSON - SUMMIT 230KV CKT 1
Flowgate: | 57368573811568725687312208SP
Date Redispatch Needed: | Starting 2008 6/1 - 10/1 Until EOC of Upgrade
Season Flowgate Identified: | 2008 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1161506 | 8.1786 | 15.5268
1161997 | 7.3482 | 15.5268
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.28454 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06209 | -0.34663 | 45
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.28454 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | 0.01967 | -0.30421 | 51
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.28454 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | 0.01396 | -0.2985 | 52
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.28454 | WERE | 'LANG 7 345 345KV' | 310 | 0.0073 | -0.29184 | 53
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.28454 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | 0.00682 | -0.29136 | 53
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.28454 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 274.2987 | 0.00711 | -0.29165 | 53
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.28454 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00621 | -0.29075 | 53
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.28454 | WERE | 'CHANUTE 69KV' | 55.637 | 0.00116 | -0.2857 | 54
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.28454 | WERE | 'CITY OF ERIE 69KV' | 23.374 | 0.00116 | -0.2857 | 54
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.28454 | WERE | 'CITY OF IOLA 69KV' | 24.471 | 0.00138 | -0.28592 | 54
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.28454 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.98 | 0.00213 | -0.28667 | 54
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.22292 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06209 | -0.28501 | 54
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22281 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06209 | -0.2849 | 54
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.28454 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | 0.00019 | -0.28473 | 55
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.28454 | WERE | 'CITY OF WELLINGTON 69KV' | 41.45 | -0.00153 | -0.28301 | 55
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.28454 | WERE | 'EVANS ENERGY CENTER 138KV' | 320.8022 | -0.00011 | -0.28443 | 55
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.28454 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00287 | -0.28167 | 55
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.28454 | WERE | 'KNOLL 3 115 115KV' | 75 | -0.03173 | -0.25281 | 61
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.22292 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | 0.01967 | -0.24259 | 64
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22281 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | 0.01967 | -0.24248 | 64
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.22292 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | 0.01396 | -0.23688 | 66
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22281 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | 0.01396 | -0.23677 | 66
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.22292 | WERE | 'LANG 7 345 345KV' | 310 | 0.0073 | -0.23022 | 67
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.22292 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 274.2987 | 0.00711 | -0.23003 | 67
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22281 | WERE | 'LANG 7 345 345KV' | 310 | 0.0073 | -0.23011 | 67
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.22292 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | 0.00682 | -0.22974 | 68
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.22292 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00621 | -0.22913 | 68
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22281 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | 0.00682 | -0.22963 | 68
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22281 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 274.2987 | 0.00711 | -0.22992 | 68
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22281 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00621 | -0.22902 | 68
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.22292 | WERE | 'CHANUTE 69KV' | 55.637 | 0.00116 | -0.22408 | 69
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.22292 | WERE | 'CITY OF ERIE 69KV' | 23.374 | 0.00116 | -0.22408 | 69
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.22292 | WERE | 'CITY OF IOLA 69KV' | 24.471 | 0.00138 | -0.2243 | 69
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22281 | WERE | 'CHANUTE 69KV' | 55.637 | 0.00116 | -0.22397 | 69
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22281 | WERE | 'CITY OF ERIE 69KV' | 23.374 | 0.00116 | -0.22397 | 69
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22281 | WERE | 'CITY OF IOLA 69KV' | 24.471 | 0.00138 | -0.22419 | 69
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.22292 | WERE | 'CITY OF WELLINGTON 69KV' | 41.45 | -0.00153 | -0.22139 | 70
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.22292 | WERE | 'EVANS ENERGY CENTER 138KV' | 320.8022 | -0.00011 | -0.22281 | 70
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22281 | WERE | 'CITY OF WELLINGTON 69KV' | 41.45 | -0.00153 | -0.22128 | 70
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22281 | WERE | 'EVANS ENERGY CENTER 138KV' | 320.8022 | -0.00011 | -0.2227 | 70
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.22292 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00287 | -0.22005 | 71
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22281 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00287 | -0.21994 | 71
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.22292 | WERE | 'KNOLL 3 115 115KV' | 75 | -0.03173 | -0.19119 | 81
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22281 | WERE | 'KNOLL 3 115 115KV' | 75 | -0.03173 | -0.19108 | 81
WERE | 'PAWNEE 115KV' | 999 | -0.11442 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06209 | -0.17651 | 88
WERE | 'RICE 115KV' | 999 | -0.11442 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06209 | -0.17651 | 88
WERE | 'PAWNEE 115KV' | 999 | -0.11442 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | 0.01967 | -0.13409 | 116
WERE | 'RICE 115KV' | 999 | -0.11442 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | 0.01967 | -0.13409 | 116
WERE | 'PAWNEE 115KV' | 999 | -0.11442 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | 0.01396 | -0.12838 | 121
WERE | 'RICE 115KV' | 999 | -0.11442 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | 0.01396 | -0.12838 | 121
WERE | 'PAWNEE 115KV' | 999 | -0.11442 | WERE | 'LANG 7 345 345KV' | 310 | 0.0073 | -0.12172 | 128
WERE | 'PAWNEE 115KV' | 999 | -0.11442 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | 0.00682 | -0.12124 | 128
WERE | 'PAWNEE 115KV' | 999 | -0.11442 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 274.2987 | 0.00711 | -0.12153 | 128
WERE | 'RICE 115KV' | 999 | -0.11442 | WERE | 'LANG 7 345 345KV' | 310 | 0.0073 | -0.12172 | 128
WERE | 'RICE 115KV' | 999 | -0.11442 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | 0.00682 | -0.12124 | 128
WERE | 'RICE 115KV' | 999 | -0.11442 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 274.2987 | 0.00711 | -0.12153 | 128
WERE | 'PAWNEE 115KV' | 999 | -0.11442 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00621 | -0.12063 | 129
WERE | 'RICE 115KV' | 999 | -0.11442 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00621 | -0.12063 | 129
WERE | 'PAWNEE 115KV' | 999 | -0.11442 | WERE | 'CHANUTE 69KV' | 55.637 | 0.00116 | -0.11558 | 134
WERE | 'RICE 115KV' | 999 | -0.11442 | WERE | 'CHANUTE 69KV' | 55.637 | 0.00116 | -0.11558 | 134
WERE | 'PAWNEE 115KV' | 999 | -0.11442 | WERE | 'EVANS ENERGY CENTER 138KV' | 320.8022 | -0.00011 | -0.11431 | 136
WERE | 'RICE 115KV' | 999 | -0.11442 | WERE | 'EVANS ENERGY CENTER 138KV' | 320.8022 | -0.00011 | -0.11431 | 136
WERE | 'PAWNEE 115KV' | 999 | -0.11442 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00287 | -0.11155 | 139
WERE | 'RICE 115KV' | 999 | -0.11442 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00287 | -0.11155 | 139
WERE | 'PAWNEE 115KV' | 999 | -0.11442 | WERE | 'KNOLL 3 115 115KV' | 75 | -0.03173 | -0.08269 | 188
WERE | 'RICE 115KV' | 999 | -0.11442 | WERE | 'KNOLL 3 115 115KV' | 75 | -0.03173 | -0.08269 | 188
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.00215 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06209 | -0.06424 | 242
WERE | 'EVANS ENERGY CENTER 138KV' | 486.1978 | -0.00011 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06209 | -0.0622 | 250
WERE | 'EVANS N4 138 16KV' | 360 | -0.0001 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06209 | -0.06219 | 250
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.28454 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 120 | -0.22292 | -0.06162 | 252
WERE | 'CLR_3 .575 34KV' | 300 | 0.00089 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06209 | -0.0612 | 254
WERE | 'LATHAM1234.0 345KV' | 150 | 0.00089 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06209 | -0.0612 | 254
WERE | 'LYONS 115KV' | 999 | 0.00089 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06209 | -0.0612 | 254
WERE | 'LANG 7 345 345KV' | 518 | 0.0073 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06209 | -0.05479 | 283
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | WICHITA - RENO 345KV
Limiting Facility: | EXIDE JUNCTION - SUMMIT 115KV CKT 1
Direction: | To->From
Line Outage: | EAST MCPHERSON - SUMMIT 230KV CKT 1
Flowgate: | 57368573811568725687312211SP
Date Redispatch Needed: | 6/1/09 - 7/1/09
Season Flowgate Identified: | 2011 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1140120 | 11.7981 | 35.1743
1161506 | 12.1649 | 35.1743
1161997 | 11.2114 | 35.1743
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28476 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06181 | -0.34657 | 101
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28476 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01916 | -0.30392 | 116
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28476 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01349 | -0.29825 | 118
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28476 | WERE | 'LANG 7 345 345KV' | 610 | 0.007 | -0.29176 | 121
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28476 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | 0.00644 | -0.2912 | 121
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28476 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 201.5866 | 0.00674 | -0.2915 | 121
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28476 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00582 | -0.29058 | 121
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28476 | WERE | 'CHANUTE 69KV' | 58.843 | 0.00106 | -0.28582 | 123
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.2231 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06181 | -0.28491 | 123
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28476 | WERE | 'CITY OF WELLINGTON 69KV' | 41.45 | -0.00163 | -0.28313 | 124
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28476 | WERE | 'EVANS ENERGY CENTER 138KV' | 331.6143 | -0.00025 | -0.28451 | 124
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22288 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06181 | -0.28469 | 124
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28476 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00296 | -0.2818 | 125
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.2231 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01916 | -0.24226 | 145
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22288 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01916 | -0.24204 | 145
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.2231 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01349 | -0.23659 | 149
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22288 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01349 | -0.23637 | 149
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.2231 | WERE | 'LANG 7 345 345KV' | 610 | 0.007 | -0.2301 | 153
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.2231 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | 0.00644 | -0.22954 | 153
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.2231 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 201.5866 | 0.00674 | -0.22984 | 153
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22288 | WERE | 'LANG 7 345 345KV' | 610 | 0.007 | -0.22988 | 153
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22288 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | 0.00644 | -0.22932 | 153
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22288 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 201.5866 | 0.00674 | -0.22962 | 153
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.2231 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00582 | -0.22892 | 154
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22288 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00582 | -0.2287 | 154
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.2231 | WERE | 'CHANUTE 69KV' | 58.843 | 0.00106 | -0.22416 | 157
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22288 | WERE | 'CHANUTE 69KV' | 58.843 | 0.00106 | -0.22394 | 157
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.2231 | WERE | 'EVANS ENERGY CENTER 138KV' | 331.6143 | -0.00025 | -0.22285 | 158
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22288 | WERE | 'EVANS ENERGY CENTER 138KV' | 331.6143 | -0.00025 | -0.22263 | 158
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.2231 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00296 | -0.22014 | 160
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22288 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00296 | -0.21992 | 160
WERE | 'PAWNEE 115KV' | 999 | -0.11452 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06181 | -0.17633 | 199
WERE | 'RICE 115KV' | 999 | -0.11452 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.06181 | -0.17633 | 199
WERE | 'PAWNEE 115KV' | 999 | -0.11452 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01916 | -0.13368 | 263
WERE | 'RICE 115KV' | 999 | -0.11452 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01916 | -0.13368 | 263
WERE | 'PAWNEE 115KV' | 999 | -0.11452 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01349 | -0.12801 | 275
WERE | 'RICE 115KV' | 999 | -0.11452 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.01349 | -0.12801 | 275
WERE | 'PAWNEE 115KV' | 999 | -0.11452 | WERE | 'LANG 7 345 345KV' | 610 | 0.007 | -0.12152 | 289
WERE | 'RICE 115KV' | 999 | -0.11452 | WERE | 'LANG 7 345 345KV' | 610 | 0.007 | -0.12152 | 289
WERE | 'PAWNEE 115KV' | 999 | -0.11452 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 201.5866 | 0.00674 | -0.12126 | 290
WERE | 'RICE 115KV' | 999 | -0.11452 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 201.5866 | 0.00674 | -0.12126 | 290
WERE | 'PAWNEE 115KV' | 999 | -0.11452 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00582 | -0.12034 | 292
WERE | 'RICE 115KV' | 999 | -0.11452 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00582 | -0.12034 | 292
WERE | 'PAWNEE 115KV' | 999 | -0.11452 | WERE | 'EVANS ENERGY CENTER 138KV' | 331.6143 | -0.00025 | -0.11427 | 308
WERE | 'RICE 115KV' | 999 | -0.11452 | WERE | 'EVANS ENERGY CENTER 138KV' | 331.6143 | -0.00025 | -0.11427 | 308
WERE | 'PAWNEE 115KV' | 999 | -0.11452 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00296 | -0.11156 | 315
WERE | 'RICE 115KV' | 999 | -0.11452 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00296 | -0.11156 | 315
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | WICHITA - RENO 345KV
Limiting Facility: | EXIDE JUNCTION - SUMMIT 115KV CKT 1
Direction: | To->From
Line Outage: | EAST MCPHERSON - SUMMIT 230KV CKT 1
Flowgate: | 57368573811568725687314208WP
Date Redispatch Needed: | Starting 2008 12/1 - 4/1 Until EOC of Upgrade
Season Flowgate Identified: | 2008 Winter Peak
Reservation | Relief Amount | Aggregate Relief Amount
1161506 | 2.8169 | 4.9146
1161997 | 2.0977 | 4.9146
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28453 | WERE | 'SMOKEY HILLS 34KV' | 51 | 0.0621 | -0.34663 | 14
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28453 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 490 | 0.01395 | -0.29848 | 16
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28453 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 974.2261 | 0.01966 | -0.30419 | 16
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28453 | WERE | 'CHANUTE 69KV' | 34.903 | 0.00117 | -0.2857 | 17
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28453 | WERE | 'CITY OF AUGUSTA 69KV' | 15.285 | 0.00019 | -0.28472 | 17
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28453 | WERE | 'CITY OF IOLA 69KV' | 19.902 | 0.00139 | -0.28592 | 17
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28453 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00153 | -0.283 | 17
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28453 | WERE | 'CLR_3 .575 34KV' | 100 | 0.00089 | -0.28542 | 17
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28453 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.61 | 0.00213 | -0.28666 | 17
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28453 | WERE | 'LANG 7 345 345KV' | 380 | 0.0073 | -0.29183 | 17
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28453 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 154.9715 | 0.0071 | -0.29163 | 17
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28453 | WERE | 'WACO 138KV' | 17.414 | -0.00259 | -0.28194 | 17
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.22291 | WERE | 'SMOKEY HILLS 34KV' | 51 | 0.0621 | -0.28501 | 17
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22268 | WERE | 'SMOKEY HILLS 34KV' | 51 | 0.0621 | -0.28478 | 17
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.28453 | WERE | 'KNOLL 3 115 115KV' | 39.9 | -0.0317 | -0.25283 | 19
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.22291 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 974.2261 | 0.01966 | -0.24257 | 20
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22268 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 974.2261 | 0.01966 | -0.24234 | 20
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.22291 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 490 | 0.01395 | -0.23686 | 21
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.22291 | WERE | 'LANG 7 345 345KV' | 380 | 0.0073 | -0.23021 | 21
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.22291 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 154.9715 | 0.0071 | -0.23001 | 21
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22268 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 490 | 0.01395 | -0.23663 | 21
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22268 | WERE | 'LANG 7 345 345KV' | 380 | 0.0073 | -0.22998 | 21
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22268 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 154.9715 | 0.0071 | -0.22978 | 21
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.1615 | WERE | 'SMOKEY HILLS 34KV' | 51 | 0.0621 | -0.2236 | 22
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.22291 | WERE | 'CHANUTE 69KV' | 34.903 | 0.00117 | -0.22408 | 22
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.22291 | WERE | 'CITY OF AUGUSTA 69KV' | 15.285 | 0.00019 | -0.2231 | 22
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.22291 | WERE | 'CITY OF IOLA 69KV' | 19.902 | 0.00139 | -0.2243 | 22
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.22291 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00153 | -0.22138 | 22
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.22291 | WERE | 'CLR_3 .575 34KV' | 100 | 0.00089 | -0.2238 | 22
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.22291 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.61 | 0.00213 | -0.22504 | 22
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.22291 | WERE | 'WACO 138KV' | 17.414 | -0.00259 | -0.22032 | 22
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22268 | WERE | 'CHANUTE 69KV' | 34.903 | 0.00117 | -0.22385 | 22
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22268 | WERE | 'CITY OF AUGUSTA 69KV' | 15.285 | 0.00019 | -0.22287 | 22
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22268 | WERE | 'CITY OF IOLA 69KV' | 19.902 | 0.00139 | -0.22407 | 22
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22268 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00153 | -0.22115 | 22
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22268 | WERE | 'CLR_3 .575 34KV' | 100 | 0.00089 | -0.22357 | 22
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22268 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.61 | 0.00213 | -0.22481 | 22
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22268 | WERE | 'WACO 138KV' | 17.414 | -0.00259 | -0.22009 | 22
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.22291 | WERE | 'KNOLL 3 115 115KV' | 39.9 | -0.0317 | -0.19121 | 26
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.22268 | WERE | 'KNOLL 3 115 115KV' | 39.9 | -0.0317 | -0.19098 | 26
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.1615 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 974.2261 | 0.01966 | -0.18116 | 27
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.1615 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 490 | 0.01395 | -0.17545 | 28
WERE | 'PAWNEE 115KV' | 999 | -0.11443 | WERE | 'SMOKEY HILLS 34KV' | 51 | 0.0621 | -0.17653 | 28
WERE | 'RICE 115KV' | 999 | -0.11443 | WERE | 'SMOKEY HILLS 34KV' | 51 | 0.0621 | -0.17653 | 28
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.1615 | WERE | 'LANG 7 345 345KV' | 380 | 0.0073 | -0.1688 | 29
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.1615 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 154.9715 | 0.0071 | -0.1686 | 29
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.1615 | WERE | 'CHANUTE 69KV' | 34.903 | 0.00117 | -0.16267 | 30
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.1615 | WERE | 'CITY OF AUGUSTA 69KV' | 15.285 | 0.00019 | -0.16169 | 30
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.1615 | WERE | 'CITY OF IOLA 69KV' | 19.902 | 0.00139 | -0.16289 | 30
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.1615 | WERE | 'CLR_3 .575 34KV' | 100 | 0.00089 | -0.16239 | 30
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.1615 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.61 | 0.00213 | -0.16363 | 30
WERE | 'CLAY CENTER JUNCTION 115KV' | 31.4 | -0.10224 | WERE | 'SMOKEY HILLS 34KV' | 51 | 0.0621 | -0.16434 | 30
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.1615 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00153 | -0.15997 | 31
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.1615 | WERE | 'WACO 138KV' | 17.414 | -0.00259 | -0.15891 | 31
WERE | 'PAWNEE 115KV' | 999 | -0.11443 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 974.2261 | 0.01966 | -0.13409 | 37
WERE | 'RICE 115KV' | 999 | -0.11443 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 974.2261 | 0.01966 | -0.13409 | 37
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.1615 | WERE | 'KNOLL 3 115 115KV' | 39.9 | -0.0317 | -0.1298 | 38
WERE | 'PAWNEE 115KV' | 999 | -0.11443 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 490 | 0.01395 | -0.12838 | 38
WERE | 'RICE 115KV' | 999 | -0.11443 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 490 | 0.01395 | -0.12838 | 38
WERE | 'CLAY CENTER JUNCTION 115KV' | 31.4 | -0.10224 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 974.2261 | 0.01966 | -0.1219 | 40
WERE | 'PAWNEE 115KV' | 999 | -0.11443 | WERE | 'LANG 7 345 345KV' | 380 | 0.0073 | -0.12173 | 40
WERE | 'PAWNEE 115KV' | 999 | -0.11443 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 154.9715 | 0.0071 | -0.12153 | 40
WERE | 'RICE 115KV' | 999 | -0.11443 | WERE | 'LANG 7 345 345KV' | 380 | 0.0073 | -0.12173 | 40
WERE | 'RICE 115KV' | 999 | -0.11443 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 154.9715 | 0.0071 | -0.12153 | 40
WERE | 'CLAY CENTER JUNCTION 115KV' | 31.4 | -0.10224 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 490 | 0.01395 | -0.11619 | 42
WERE | 'PAWNEE 115KV' | 999 | -0.11443 | WERE | 'CITY OF IOLA 69KV' | 19.902 | 0.00139 | -0.11582 | 42
WERE | 'PAWNEE 115KV' | 999 | -0.11443 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.61 | 0.00213 | -0.11656 | 42
WERE | 'RICE 115KV' | 999 | -0.11443 | WERE | 'CITY OF IOLA 69KV' | 19.902 | 0.00139 | -0.11582 | 42
WERE | 'RICE 115KV' | 999 | -0.11443 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.61 | 0.00213 | -0.11656 | 42
WERE | 'PAWNEE 115KV' | 999 | -0.11443 | WERE | 'CHANUTE 69KV' | 34.903 | 0.00117 | -0.1156 | 43
WERE | 'PAWNEE 115KV' | 999 | -0.11443 | WERE | 'CITY OF AUGUSTA 69KV' | 15.285 | 0.00019 | -0.11462 | 43
WERE | 'PAWNEE 115KV' | 999 | -0.11443 | WERE | 'CLR_3 .575 34KV' | 100 | 0.00089 | -0.11532 | 43
WERE | 'RICE 115KV' | 999 | -0.11443 | WERE | 'CHANUTE 69KV' | 34.903 | 0.00117 | -0.1156 | 43
WERE | 'RICE 115KV' | 999 | -0.11443 | WERE | 'CITY OF AUGUSTA 69KV' | 15.285 | 0.00019 | -0.11462 | 43
WERE | 'RICE 115KV' | 999 | -0.11443 | WERE | 'CLR_3 .575 34KV' | 100 | 0.00089 | -0.11532 | 43
WERE | 'PAWNEE 115KV' | 999 | -0.11443 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00153 | -0.1129 | 44
WERE | 'PAWNEE 115KV' | 999 | -0.11443 | WERE | 'WACO 138KV' | 17.414 | -0.00259 | -0.11184 | 44
WERE | 'RICE 115KV' | 999 | -0.11443 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00153 | -0.1129 | 44
WERE | 'RICE 115KV' | 999 | -0.11443 | WERE | 'WACO 138KV' | 17.414 | -0.00259 | -0.11184 | 44
WERE | 'CLAY CENTER JUNCTION 115KV' | 31.4 | -0.10224 | WERE | 'LANG 7 345 345KV' | 380 | 0.0073 | -0.10954 | 45
WERE | 'CLAY CENTER JUNCTION 115KV' | 31.4 | -0.10224 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 154.9715 | 0.0071 | -0.10934 | 45
WERE | 'CLAY CENTER JUNCTION 115KV' | 31.4 | -0.10224 | WERE | 'CITY OF IOLA 69KV' | 19.902 | 0.00139 | -0.10363 | 47
WERE | 'CLAY CENTER JUNCTION 115KV' | 31.4 | -0.10224 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.61 | 0.00213 | -0.10437 | 47
WERE | 'CLAY CENTER JUNCTION 115KV' | 31.4 | -0.10224 | WERE | 'CHANUTE 69KV' | 34.903 | 0.00117 | -0.10341 | 48
WERE | 'CLAY CENTER JUNCTION 115KV' | 31.4 | -0.10224 | WERE | 'CLR_3 .575 34KV' | 100 | 0.00089 | -0.10313 | 48
WERE | 'CLAY CENTER JUNCTION 115KV' | 31.4 | -0.10224 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00153 | -0.10071 | 49
WERE | 'CLAY CENTER JUNCTION 115KV' | 31.4 | -0.10224 | WERE | 'WACO 138KV' | 17.414 | -0.00259 | -0.09965 | 49
WERE | 'KNOLL 3 115 115KV' | 44.46 | -0.0317 | WERE | 'SMOKEY HILLS 34KV' | 51 | 0.0621 | -0.0938 | 52
WERE | 'PAWNEE 115KV' | 999 | -0.11443 | WERE | 'KNOLL 3 115 115KV' | 39.9 | -0.0317 | -0.08273 | 59
WERE | 'RICE 115KV' | 999 | -0.11443 | WERE | 'KNOLL 3 115 115KV' | 39.9 | -0.0317 | -0.08273 | 59
WERE | 'CLAY CENTER JUNCTION 115KV' | 31.4 | -0.10224 | WERE | 'KNOLL 3 115 115KV' | 39.9 | -0.0317 | -0.07054 | 70
WERE | 'GILL ENERGY CENTER 138KV' | 218 | -0.00287 | WERE | 'SMOKEY HILLS 34KV' | 51 | 0.0621 | -0.06497 | 76
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.00216 | WERE | 'SMOKEY HILLS 34KV' | 51 | 0.0621 | -0.06426 | 76
WERE | 'CITY OF WINFIELD 69KV' | 40 | -0.00093 | WERE | 'SMOKEY HILLS 34KV' | 51 | 0.0621 | -0.06303 | 78
WERE | 'EVANS ENERGY CENTER 138KV' | 1002 | -0.00011 | WERE | 'SMOKEY HILLS 34KV' | 51 | 0.0621 | -0.06221 | 79
WERE | 'EVANS N4 138 16KV' | 360 | -0.0001 | WERE | 'SMOKEY HILLS 34KV' | 51 | 0.0621 | -0.0622 | 79
WERE | 'CLR_3 .575 34KV' | 200 | 0.00089 | WERE | 'SMOKEY HILLS 34KV' | 51 | 0.0621 | -0.06121 | 80
WERE | 'GETTY 69KV' | 35 | 0.00047 | WERE | 'SMOKEY HILLS 34KV' | 51 | 0.0621 | -0.06163 | 80
WERE | 'LATHAM1234.0 345KV' | 150 | 0.00089 | WERE | 'SMOKEY HILLS 34KV' | 51 | 0.0621 | -0.06121 | 80
WERE | 'LYONS 115KV' | 999 | 0.0009 | WERE | 'SMOKEY HILLS 34KV' | 51 | 0.0621 | -0.0612 | 80
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | WICHITA - RENO 345KV
Limiting Facility: | EXIDE JUNCTION - SUMMIT 115KV CKT 1
Direction: | To->From
Line Outage: | NORTHVIEW - SUMMIT 115KV CKT 1
Flowgate: | 57368573811573715738112207SH
Date Redispatch Needed: | 6/1/07 - 10/1/07 Until EOC of Upgrade
Season Flowgate Identified: | 2007 Summer Shoulder
Reservation | Relief Amount | Aggregate Relief Amount
1161997 | 6.8296 | 6.8296
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.35349 | WERE | 'CHANUTE 69KV' | 46.617 | 7e-05 | -0.35356 | 19
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.35349 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | -0.00061 | -0.35288 | 19
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.35349 | WERE | 'CITY OF ERIE 69KV' | 23.258 | 7e-05 | -0.35356 | 19
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.35349 | WERE | 'CITY OF IOLA 69KV' | 19.865 | 0.00016 | -0.35365 | 19
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.35349 | WERE | 'CITY OF WELLINGTON 69KV' | 31.07 | -0.00103 | -0.35246 | 19
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.35349 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.96 | 0.00029 | -0.35378 | 19
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.35349 | WERE | 'EVANS ENERGY CENTER 138KV' | 269.2019 | -0.00062 | -0.35287 | 19
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.35349 | WERE | 'GILL ENERGY CENTER 138KV' | 77 | -0.0016 | -0.35189 | 19
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.35349 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.00382 | -0.35731 | 19
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.35349 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01248 | -0.36597 | 19
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.35349 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | -0.00061 | -0.35288 | 19
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.35349 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 235.3866 | -0.00073 | -0.35276 | 19
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.35349 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | -0.00319 | -0.3503 | 19
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.35349 | WERE | 'WACO 138KV' | 17.947 | -0.0015 | -0.35199 | 19
WERE | 'ABILENE ENERGY CENTER 115KV' | 66 | -0.35349 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 80 | -0.09794 | -0.25555 | 27
WERE | 'CLAY CENTER JUNCTION 115KV' | 26.275 | -0.23215 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01248 | -0.24463 | 28
WERE | 'CLAY CENTER JUNCTION 115KV' | 26.275 | -0.23215 | WERE | 'CHANUTE 69KV' | 46.617 | 7e-05 | -0.23222 | 29
WERE | 'CLAY CENTER JUNCTION 115KV' | 26.275 | -0.23215 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | -0.00061 | -0.23154 | 29
WERE | 'CLAY CENTER JUNCTION 115KV' | 26.275 | -0.23215 | WERE | 'CITY OF ERIE 69KV' | 23.258 | 7e-05 | -0.23222 | 29
WERE | 'CLAY CENTER JUNCTION 115KV' | 26.275 | -0.23215 | WERE | 'CITY OF IOLA 69KV' | 19.865 | 0.00016 | -0.23231 | 29
WERE | 'CLAY CENTER JUNCTION 115KV' | 26.275 | -0.23215 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.96 | 0.00029 | -0.23244 | 29
WERE | 'CLAY CENTER JUNCTION 115KV' | 26.275 | -0.23215 | WERE | 'EVANS ENERGY CENTER 138KV' | 269.2019 | -0.00062 | -0.23153 | 29
WERE | 'CLAY CENTER JUNCTION 115KV' | 26.275 | -0.23215 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.00382 | -0.23597 | 29
WERE | 'CLAY CENTER JUNCTION 115KV' | 26.275 | -0.23215 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | -0.00061 | -0.23154 | 29
WERE | 'CLAY CENTER JUNCTION 115KV' | 26.275 | -0.23215 | WERE | 'CITY OF WELLINGTON 69KV' | 31.07 | -0.00103 | -0.23112 | 30
WERE | 'CLAY CENTER JUNCTION 115KV' | 26.275 | -0.23215 | WERE | 'GILL ENERGY CENTER 138KV' | 77 | -0.0016 | -0.23055 | 30
WERE | 'CLAY CENTER JUNCTION 115KV' | 26.275 | -0.23215 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 235.3866 | -0.00073 | -0.23142 | 30
WERE | 'CLAY CENTER JUNCTION 115KV' | 26.275 | -0.23215 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | -0.00319 | -0.22896 | 30
WERE | 'CLAY CENTER JUNCTION 115KV' | 26.275 | -0.23215 | WERE | 'WACO 138KV' | 17.947 | -0.0015 | -0.23065 | 30
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.16334 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01248 | -0.17582 | 39
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.16334 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.00382 | -0.16716 | 41
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.16334 | WERE | 'CHANUTE 69KV' | 46.617 | 7e-05 | -0.16341 | 42
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.16334 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | -0.00061 | -0.16273 | 42
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.16334 | WERE | 'CITY OF ERIE 69KV' | 23.258 | 7e-05 | -0.16341 | 42
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.16334 | WERE | 'CITY OF IOLA 69KV' | 19.865 | 0.00016 | -0.1635 | 42
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.16334 | WERE | 'CITY OF WELLINGTON 69KV' | 31.07 | -0.00103 | -0.16231 | 42
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.16334 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.96 | 0.00029 | -0.16363 | 42
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.16334 | WERE | 'EVANS ENERGY CENTER 138KV' | 269.2019 | -0.00062 | -0.16272 | 42
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.16334 | WERE | 'GILL ENERGY CENTER 138KV' | 77 | -0.0016 | -0.16174 | 42
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.16334 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | -0.00061 | -0.16273 | 42
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.16334 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 235.3866 | -0.00073 | -0.16261 | 42
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.16334 | WERE | 'WACO 138KV' | 17.947 | -0.0015 | -0.16184 | 42
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.16334 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | -0.00319 | -0.16015 | 43
WERE | 'CLAY CENTER JUNCTION 115KV' | 26.275 | -0.23215 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 80 | -0.09794 | -0.13421 | 51
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.09794 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01248 | -0.11042 | 62
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.09788 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01248 | -0.11036 | 62
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.09794 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.00382 | -0.10176 | 67
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.09788 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.00382 | -0.1017 | 67
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.09794 | WERE | 'CHANUTE 69KV' | 46.617 | 7e-05 | -0.09801 | 70
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.09794 | WERE | 'CITY OF WELLINGTON 69KV' | 31.07 | -0.00103 | -0.09691 | 70
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.09794 | WERE | 'EVANS ENERGY CENTER 138KV' | 269.2019 | -0.00062 | -0.09732 | 70
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.09794 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | -0.00061 | -0.09733 | 70
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.09794 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 235.3866 | -0.00073 | -0.09721 | 70
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.09788 | WERE | 'CHANUTE 69KV' | 46.617 | 7e-05 | -0.09795 | 70
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.09788 | WERE | 'EVANS ENERGY CENTER 138KV' | 269.2019 | -0.00062 | -0.09726 | 70
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.09788 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | -0.00061 | -0.09727 | 70
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.09788 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 235.3866 | -0.00073 | -0.09715 | 70
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.09794 | WERE | 'GILL ENERGY CENTER 138KV' | 77 | -0.0016 | -0.09634 | 71
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.09788 | WERE | 'CITY OF WELLINGTON 69KV' | 31.07 | -0.00103 | -0.09685 | 71
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.09788 | WERE | 'GILL ENERGY CENTER 138KV' | 77 | -0.0016 | -0.09628 | 71
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 303 | -0.09794 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | -0.00319 | -0.09475 | 72
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.09788 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | -0.00319 | -0.09469 | 72
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.16334 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 80 | -0.09794 | -0.0654 | 104
WERE | 'PAWNEE 115KV' | 999 | -0.04301 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01248 | -0.05549 | 123
WERE | 'RICE 115KV' | 999 | -0.04301 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01248 | -0.05549 | 123
WERE | 'PAWNEE 115KV' | 999 | -0.04301 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.00382 | -0.04683 | 146
WERE | 'RICE 115KV' | 999 | -0.04301 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.00382 | -0.04683 | 146
WERE | 'PAWNEE 115KV' | 999 | -0.04301 | WERE | 'EVANS ENERGY CENTER 138KV' | 269.2019 | -0.00062 | -0.04239 | 161
WERE | 'PAWNEE 115KV' | 999 | -0.04301 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | -0.00061 | -0.0424 | 161
WERE | 'RICE 115KV' | 999 | -0.04301 | WERE | 'EVANS ENERGY CENTER 138KV' | 269.2019 | -0.00062 | -0.04239 | 161
WERE | 'RICE 115KV' | 999 | -0.04301 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 60 | -0.00061 | -0.0424 | 161
WERE | 'PAWNEE 115KV' | 999 | -0.04301 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 235.3866 | -0.00073 | -0.04228 | 162
WERE | 'RICE 115KV' | 999 | -0.04301 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 235.3866 | -0.00073 | -0.04228 | 162
WERE | 'PAWNEE 115KV' | 999 | -0.04301 | WERE | 'GILL ENERGY CENTER 138KV' | 77 | -0.0016 | -0.04141 | 165
WERE | 'RICE 115KV' | 999 | -0.04301 | WERE | 'GILL ENERGY CENTER 138KV' | 77 | -0.0016 | -0.04141 | 165
WERE | 'PAWNEE 115KV' | 999 | -0.04301 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | -0.00319 | -0.03982 | 172
WERE | 'RICE 115KV' | 999 | -0.04301 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | -0.00319 | -0.03982 | 172
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | WICHITA - RENO 345KV
Limiting Facility: | EXIDE JUNCTION - SUMMIT 115KV CKT 1
Direction: | To->From
Line Outage: | NORTHVIEW - SUMMIT 115KV CKT 1
Flowgate: | 57368573811573715738112208SP
Date Redispatch Needed: | Starting 2008 6/1 - 10/1 Until EOC of Upgrade
Season Flowgate Identified: | 2008 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1161506 | 9.1325 | 17.9711
1161997 | 8.8386 | 17.9711
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.16261 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08284 | -0.24545 | 73
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.16261 | WERE | 'KNOLL 3 115 115KV' | 75 | 0.01715 | -0.17976 | 100
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.09467 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08284 | -0.17751 | 101
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.09461 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08284 | -0.17745 | 101
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.16261 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | 0.01102 | -0.17363 | 104
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.16261 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | 0.00237 | -0.16498 | 109
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.16261 | WERE | 'LANG 7 345 345KV' | 310 | 0.00063 | -0.16324 | 110
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.16261 | WERE | 'CHANUTE 69KV' | 55.637 | -8e-05 | -0.16253 | 111
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.16261 | WERE | 'CITY OF WELLINGTON 69KV' | 41.45 | -0.001 | -0.16161 | 111
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.16261 | WERE | 'EVANS ENERGY CENTER 138KV' | 320.8022 | -0.00076 | -0.16185 | 111
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.16261 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00151 | -0.1611 | 112
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.16261 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | -0.00152 | -0.16109 | 112
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.16261 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 274.2987 | -0.00168 | -0.16093 | 112
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.16261 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | -0.00421 | -0.1584 | 113
WERE | 'PAWNEE 115KV' | 999 | -0.03606 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08284 | -0.1189 | 151
WERE | 'RICE 115KV' | 999 | -0.03606 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08284 | -0.1189 | 151
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.09467 | WERE | 'KNOLL 3 115 115KV' | 75 | 0.01715 | -0.11182 | 161
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.09461 | WERE | 'KNOLL 3 115 115KV' | 75 | 0.01715 | -0.11176 | 161
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.09467 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | 0.01102 | -0.10569 | 170
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.09461 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | 0.01102 | -0.10563 | 170
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.09467 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | 0.00237 | -0.09704 | 185
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.09461 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | 0.00237 | -0.09698 | 185
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.09467 | WERE | 'LANG 7 345 345KV' | 310 | 0.00063 | -0.0953 | 189
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.09461 | WERE | 'LANG 7 345 345KV' | 310 | 0.00063 | -0.09524 | 189
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.09467 | WERE | 'EVANS ENERGY CENTER 138KV' | 320.8022 | -0.00076 | -0.09391 | 191
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.09461 | WERE | 'EVANS ENERGY CENTER 138KV' | 320.8022 | -0.00076 | -0.09385 | 191
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.09467 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00151 | -0.09316 | 193
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.09467 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | -0.00152 | -0.09315 | 193
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.09467 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 274.2987 | -0.00168 | -0.09299 | 193
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.09461 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00151 | -0.0931 | 193
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.09461 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | -0.00152 | -0.09309 | 193
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.09461 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 274.2987 | -0.00168 | -0.09293 | 193
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.09467 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | -0.00421 | -0.09046 | 199
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.09461 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | -0.00421 | -0.0904 | 199
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.0013 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08284 | -0.08414 | 214
WERE | 'EVANS ENERGY CENTER 138KV' | 486.1978 | -0.00076 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08284 | -0.0836 | 215
WERE | 'EVANS N4 138 16KV' | 360 | -0.00075 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08284 | -0.08359 | 215
WERE | 'CLR_3 .575 34KV' | 300 | -0.00035 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08284 | -0.08319 | 216
WERE | 'LATHAM1234.0 345KV' | 150 | -0.00035 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08284 | -0.08319 | 216
WERE | 'LYONS 115KV' | 999 | 5e-05 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08284 | -0.08279 | 217
WERE | 'LANG 7 345 345KV' | 518 | 0.00063 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08284 | -0.08221 | 219
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.16261 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 120 | -0.09467 | -0.06794 | 265
WERE | 'PAWNEE 115KV' | 999 | -0.03606 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | 0.01102 | -0.04708 | 382
WERE | 'RICE 115KV' | 999 | -0.03606 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | 0.01102 | -0.04708 | 382
WERE | 'PAWNEE 115KV' | 999 | -0.03606 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | 0.00237 | -0.03843 | 468
WERE | 'RICE 115KV' | 999 | -0.03606 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | 0.00237 | -0.03843 | 468
WERE | 'PAWNEE 115KV' | 999 | -0.03606 | WERE | 'LANG 7 345 345KV' | 310 | 0.00063 | -0.03669 | 490
WERE | 'RICE 115KV' | 999 | -0.03606 | WERE | 'LANG 7 345 345KV' | 310 | 0.00063 | -0.03669 | 490
WERE | 'PAWNEE 115KV' | 999 | -0.03606 | WERE | 'EVANS ENERGY CENTER 138KV' | 320.8022 | -0.00076 | -0.0353 | 509
WERE | 'RICE 115KV' | 999 | -0.03606 | WERE | 'EVANS ENERGY CENTER 138KV' | 320.8022 | -0.00076 | -0.0353 | 509
WERE | 'PAWNEE 115KV' | 999 | -0.03606 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 274.2987 | -0.00168 | -0.03438 | 523
WERE | 'RICE 115KV' | 999 | -0.03606 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 274.2987 | -0.00168 | -0.03438 | 523
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | WICHITA - RENO 345KV
Limiting Facility: | EXIDE JUNCTION - SUMMIT 115KV CKT 1
Direction: | To->From
Line Outage: | NORTHVIEW - SUMMIT 115KV CKT 1
Flowgate: | 57368573811573715738112211SP
Date Redispatch Needed: | 6/1/09 - 7/1/09
Season Flowgate Identified: | 2011 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1140120 | 12.504 | 37.9708
1161506 | 12.9208 | 37.9708
1161997 | 12.546 | 37.9708
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.16271 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08273 | -0.24544 | 155
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.09476 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08273 | -0.17749 | 214
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.16271 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01086 | -0.17357 | 219
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.16271 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.00225 | -0.16496 | 230
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.16271 | WERE | 'LANG 7 345 345KV' | 610 | 0.00057 | -0.16328 | 233
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.16271 | WERE | 'EVANS ENERGY CENTER 138KV' | 331.6143 | -0.00079 | -0.16192 | 235
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.16271 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00153 | -0.16118 | 236
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.16271 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | -0.00148 | -0.16123 | 236
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.16271 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 201.5866 | -0.00167 | -0.16104 | 236
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.16271 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | -0.00428 | -0.15843 | 240
WERE | 'PAWNEE 115KV' | 999 | -0.03611 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08273 | -0.11884 | 320
WERE | 'RICE 115KV' | 999 | -0.03611 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08273 | -0.11884 | 320
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.09476 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01086 | -0.10562 | 360
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.09476 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.00225 | -0.09701 | 391
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.09476 | WERE | 'LANG 7 345 345KV' | 610 | 0.00057 | -0.09533 | 398
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.09476 | WERE | 'EVANS ENERGY CENTER 138KV' | 331.6143 | -0.00079 | -0.09397 | 404
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.09476 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00153 | -0.09323 | 407
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.09476 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 201.5866 | -0.00167 | -0.09309 | 408
WERE | 'EVANS ENERGY CENTER 138KV' | 475.3857 | -0.00079 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08273 | -0.08352 | 455
WERE | 'EVANS N4 138 16KV' | 360 | -0.00079 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08273 | -0.08352 | 455
WERE | 'PAWNEE 115KV' | 999 | -0.03611 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01086 | -0.04697 | 808
WERE | 'RICE 115KV' | 999 | -0.03611 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.01086 | -0.04697 | 808
WERE | 'PAWNEE 115KV' | 999 | -0.03611 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.00225 | -0.03836 | 990
WERE | 'RICE 115KV' | 999 | -0.03611 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.00225 | -0.03836 | 990
WERE | 'PAWNEE 115KV' | 999 | -0.03611 | WERE | 'LANG 7 345 345KV' | 610 | 0.00057 | -0.03668 | 1035
WERE | 'RICE 115KV' | 999 | -0.03611 | WERE | 'LANG 7 345 345KV' | 610 | 0.00057 | -0.03668 | 1035
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | WICHITA - RENO 345KV
Limiting Facility: | EXIDE JUNCTION - SUMMIT 115KV CKT 1
Direction: | To->From
Line Outage: | WR-DOUBLE21
Flowgate: | 57368573811WR-DOUBLE212211SP
Date Redispatch Needed: | 6/1/09 - 7/1/09
Season Flowgate Identified: | 2011 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1140120 | 0.12495 | 0.37446
1161506 | 0.12495 | 0.37446
1161997 | 0.12456 | 0.37446
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.18503 | WERE | 'CHANUTE 69KV' | 58.843 | 0.00042 | -0.18545 | 2
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.18503 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | -0.00011 | -0.18492 | 2
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.18503 | WERE | 'CITY OF BURLINGTON 69KV' | 7.8 | 0.00079 | -0.18582 | 2
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.18503 | WERE | 'CITY OF ERIE 69KV' | 23.579 | 0.00042 | -0.18545 | 2
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.18503 | WERE | 'CITY OF FREDONIA 69KV' | 3.897 | 0.00029 | -0.18532 | 2
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.18503 | WERE | 'CITY OF GIRARD 69KV' | 5.092 | 0.00046 | -0.18549 | 2
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.18503 | WERE | 'CITY OF IOLA 69KV' | 27.273 | 0.00053 | -0.18556 | 2
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.18503 | WERE | 'CITY OF MULVANE 69KV' | 9.291 | -0.00065 | -0.18438 | 2
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.18503 | WERE | 'CITY OF WELLINGTON 69KV' | 41.45 | -0.00092 | -0.18411 | 2
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.18503 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.98 | 0.00079 | -0.18582 | 2
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.18503 | WERE | 'COLBY 115KV' | 5.4881 | -0.015 | -0.17003 | 2
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.18503 | WERE | 'EVANS ENERGY CENTER 138KV' | 331.6143 | -0.0003 | -0.18473 | 2
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.18503 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.0016 | -0.18343 | 2
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.18503 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.00622 | -0.19125 | 2
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.18503 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.00913 | -0.19416 | 2
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.18503 | WERE | 'KNOLL 3 115 115KV' | 21.7 | -0.01237 | -0.17266 | 2
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.18503 | WERE | 'LANG 7 345 345KV' | 610 | 0.00295 | -0.18798 | 2
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.18503 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | 0.00279 | -0.18782 | 2
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.18503 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 201.5866 | 0.00291 | -0.18794 | 2
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.18503 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.03213 | -0.21716 | 2
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.18503 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00238 | -0.18741 | 2
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.18503 | WERE | 'WACO 138KV' | 17.972 | -0.00146 | -0.18357 | 2
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.11973 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.03213 | -0.15186 | 2
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.1196 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.03213 | -0.15173 | 2
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.08725 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.03213 | -0.11938 | 3
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.18503 | WERE | 'CLAY CENTER JUNCTION 115KV' | 19.866 | -0.05566 | -0.12937 | 3
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.11973 | WERE | 'CHANUTE 69KV' | 58.843 | 0.00042 | -0.12015 | 3
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.11973 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | -0.00011 | -0.11962 | 3
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.11973 | WERE | 'CITY OF BURLINGTON 69KV' | 7.8 | 0.00079 | -0.12052 | 3
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.11973 | WERE | 'CITY OF ERIE 69KV' | 23.579 | 0.00042 | -0.12015 | 3
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.11973 | WERE | 'CITY OF FREDONIA 69KV' | 3.897 | 0.00029 | -0.12002 | 3
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.11973 | WERE | 'CITY OF GIRARD 69KV' | 5.092 | 0.00046 | -0.12019 | 3
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.11973 | WERE | 'CITY OF IOLA 69KV' | 27.273 | 0.00053 | -0.12026 | 3
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.11973 | WERE | 'CITY OF MULVANE 69KV' | 9.291 | -0.00065 | -0.11908 | 3
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.11973 | WERE | 'CITY OF WELLINGTON 69KV' | 41.45 | -0.00092 | -0.11881 | 3
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.11973 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.98 | 0.00079 | -0.12052 | 3
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.11973 | WERE | 'EVANS ENERGY CENTER 138KV' | 331.6143 | -0.0003 | -0.11943 | 3
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.11973 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.0016 | -0.11813 | 3
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.11973 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.00622 | -0.12595 | 3
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.11973 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.00913 | -0.12886 | 3
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.11973 | WERE | 'KNOLL 3 115 115KV' | 21.7 | -0.01237 | -0.10736 | 3
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.11973 | WERE | 'LANG 7 345 345KV' | 610 | 0.00295 | -0.12268 | 3
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.11973 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | 0.00279 | -0.12252 | 3
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.11973 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 201.5866 | 0.00291 | -0.12264 | 3
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.11973 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00238 | -0.12211 | 3
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.11973 | WERE | 'WACO 138KV' | 17.972 | -0.00146 | -0.11827 | 3
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.1196 | WERE | 'CHANUTE 69KV' | 58.843 | 0.00042 | -0.12002 | 3
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.1196 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | -0.00011 | -0.11949 | 3
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.1196 | WERE | 'CITY OF BURLINGTON 69KV' | 7.8 | 0.00079 | -0.12039 | 3
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.1196 | WERE | 'CITY OF ERIE 69KV' | 23.579 | 0.00042 | -0.12002 | 3
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.1196 | WERE | 'CITY OF FREDONIA 69KV' | 3.897 | 0.00029 | -0.11989 | 3
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.1196 | WERE | 'CITY OF GIRARD 69KV' | 5.092 | 0.00046 | -0.12006 | 3
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.1196 | WERE | 'CITY OF IOLA 69KV' | 27.273 | 0.00053 | -0.12013 | 3
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.1196 | WERE | 'CITY OF MULVANE 69KV' | 9.291 | -0.00065 | -0.11895 | 3
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.1196 | WERE | 'CITY OF WELLINGTON 69KV' | 41.45 | -0.00092 | -0.11868 | 3
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.1196 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.98 | 0.00079 | -0.12039 | 3
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.1196 | WERE | 'EVANS ENERGY CENTER 138KV' | 331.6143 | -0.0003 | -0.1193 | 3
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.1196 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.0016 | -0.118 | 3
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.1196 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.00622 | -0.12582 | 3
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.1196 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.00913 | -0.12873 | 3
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.1196 | WERE | 'KNOLL 3 115 115KV' | 21.7 | -0.01237 | -0.10723 | 3
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.1196 | WERE | 'LANG 7 345 345KV' | 610 | 0.00295 | -0.12255 | 3
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.1196 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | 0.00279 | -0.12239 | 3
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.1196 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 201.5866 | 0.00291 | -0.12251 | 3
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.1196 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00238 | -0.12198 | 3
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.1196 | WERE | 'WACO 138KV' | 17.972 | -0.00146 | -0.11814 | 3
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.08725 | WERE | 'CHANUTE 69KV' | 58.843 | 0.00042 | -0.08767 | 4
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.08725 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | -0.00011 | -0.08714 | 4
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.08725 | WERE | 'CITY OF BURLINGTON 69KV' | 7.8 | 0.00079 | -0.08804 | 4
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.08725 | WERE | 'CITY OF ERIE 69KV' | 23.579 | 0.00042 | -0.08767 | 4
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.08725 | WERE | 'CITY OF FREDONIA 69KV' | 3.897 | 0.00029 | -0.08754 | 4
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.08725 | WERE | 'CITY OF GIRARD 69KV' | 5.092 | 0.00046 | -0.08771 | 4
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.08725 | WERE | 'CITY OF IOLA 69KV' | 27.273 | 0.00053 | -0.08778 | 4
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.08725 | WERE | 'CITY OF MULVANE 69KV' | 9.291 | -0.00065 | -0.0866 | 4
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.08725 | WERE | 'CITY OF WELLINGTON 69KV' | 41.45 | -0.00092 | -0.08633 | 4
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.08725 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.98 | 0.00079 | -0.08804 | 4
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.08725 | WERE | 'EVANS ENERGY CENTER 138KV' | 331.6143 | -0.0003 | -0.08695 | 4
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.08725 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.0016 | -0.08565 | 4
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.08725 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.00622 | -0.09347 | 4
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.08725 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.00913 | -0.09638 | 4
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.08725 | WERE | 'LANG 7 345 345KV' | 610 | 0.00295 | -0.0902 | 4
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.08725 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | 0.00279 | -0.09004 | 4
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.08725 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 201.5866 | 0.00291 | -0.09016 | 4
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.08725 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.00238 | -0.08963 | 4
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.08725 | WERE | 'WACO 138KV' | 17.972 | -0.00146 | -0.08579 | 4
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.18503 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | -0.08725 | -0.09778 | 4
WERE | 'CLAY CENTER JUNCTION 115KV' | 18.234 | -0.05566 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.03213 | -0.08779 | 4
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.11973 | WERE | 'COLBY 115KV' | 5.4881 | -0.015 | -0.10473 | 4
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.1196 | WERE | 'COLBY 115KV' | 5.4881 | -0.015 | -0.1046 | 4
WERE | 'PAWNEE 115KV' | 999 | -0.05669 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.03213 | -0.08882 | 4
WERE | 'RICE 115KV' | 999 | -0.05669 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.03213 | -0.08882 | 4
WERE | 'ST JOHN 115KV' | 7.5 | -0.05669 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.03213 | -0.08882 | 4
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.08725 | WERE | 'COLBY 115KV' | 5.4881 | -0.015 | -0.07225 | 5
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.08725 | WERE | 'KNOLL 3 115 115KV' | 21.7 | -0.01237 | -0.07488 | 5
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.04126 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.03213 | -0.07339 | 5
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.18503 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 120 | -0.11973 | -0.0653 | 6
WERE | 'CLAY CENTER JUNCTION 115KV' | 18.234 | -0.05566 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.00622 | -0.06188 | 6
WERE | 'CLAY CENTER JUNCTION 115KV' | 18.234 | -0.05566 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.00913 | -0.06479 | 6
WERE | 'CLAY CENTER JUNCTION 115KV' | 18.234 | -0.05566 | WERE | 'LANG 7 345 345KV' | 610 | 0.00295 | -0.05861 | 6
WERE | 'CLAY CENTER JUNCTION 115KV' | 18.234 | -0.05566 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | 0.00279 | -0.05845 | 6
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | WICHITA - RENO 345KV
Limiting Facility: | NORTHVIEW - SUMMIT 115KV CKT 1
Direction: | To->From
Line Outage: | EXIDE JUNCTION - SUMMIT 115KV CKT 1
Flowgate: | 57371573811573685738112208SP
Date Redispatch Needed: | Starting 2008 6/1 - 10/1 Until EOC of Upgrade
Season Flowgate Identified: | 2008 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1161506 | 6.1198 | 12.0776
1161997 | 5.9577 | 12.0776
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'CLAY CENTER JUNCTION 115KV' | 17.044 | -0.24138 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08159 | -0.32297 | 37
WERE | 'CLAY CENTER JUNCTION 115KV' | 17.044 | -0.24138 | WERE | 'KNOLL 3 115 115KV' | 75 | 0.02275 | -0.26413 | 46
WERE | 'CLAY CENTER JUNCTION 115KV' | 17.044 | -0.24138 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | 0.00929 | -0.25067 | 48
WERE | 'CLAY CENTER JUNCTION 115KV' | 17.044 | -0.24138 | WERE | 'CHANUTE 69KV' | 55.637 | -0.00023 | -0.24115 | 50
WERE | 'CLAY CENTER JUNCTION 115KV' | 17.044 | -0.24138 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | -0.00082 | -0.24056 | 50
WERE | 'CLAY CENTER JUNCTION 115KV' | 17.044 | -0.24138 | WERE | 'CITY OF ERIE 69KV' | 23.374 | -0.00023 | -0.24115 | 50
WERE | 'CLAY CENTER JUNCTION 115KV' | 17.044 | -0.24138 | WERE | 'CITY OF IOLA 69KV' | 24.471 | -0.00018 | -0.2412 | 50
WERE | 'CLAY CENTER JUNCTION 115KV' | 17.044 | -0.24138 | WERE | 'CITY OF WELLINGTON 69KV' | 41.45 | -0.00084 | -0.24054 | 50
WERE | 'CLAY CENTER JUNCTION 115KV' | 17.044 | -0.24138 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.98 | -0.00031 | -0.24107 | 50
WERE | 'CLAY CENTER JUNCTION 115KV' | 17.044 | -0.24138 | WERE | 'EVANS ENERGY CENTER 138KV' | 320.8022 | -0.00076 | -0.24062 | 50
WERE | 'CLAY CENTER JUNCTION 115KV' | 17.044 | -0.24138 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00118 | -0.2402 | 50
WERE | 'CLAY CENTER JUNCTION 115KV' | 17.044 | -0.24138 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | 0.00064 | -0.24202 | 50
WERE | 'CLAY CENTER JUNCTION 115KV' | 17.044 | -0.24138 | WERE | 'LANG 7 345 345KV' | 310 | -0.00025 | -0.24113 | 50
WERE | 'CLAY CENTER JUNCTION 115KV' | 17.044 | -0.24138 | WERE | 'WACO 138KV' | 17.967 | -0.00114 | -0.24024 | 50
WERE | 'CLAY CENTER JUNCTION 115KV' | 17.044 | -0.24138 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | -0.00259 | -0.23879 | 51
WERE | 'CLAY CENTER JUNCTION 115KV' | 17.044 | -0.24138 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 274.2987 | -0.00281 | -0.23857 | 51
WERE | 'CLAY CENTER JUNCTION 115KV' | 17.044 | -0.24138 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | -0.00544 | -0.23594 | 51
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.12261 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08159 | -0.2042 | 59
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.06768 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08159 | -0.14927 | 81
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.06764 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08159 | -0.14923 | 81
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.12261 | WERE | 'KNOLL 3 115 115KV' | 75 | 0.02275 | -0.14536 | 83
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.12261 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | 0.00929 | -0.1319 | 92
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.12261 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | 0.00064 | -0.12325 | 98
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.12261 | WERE | 'CHANUTE 69KV' | 55.637 | -0.00023 | -0.12238 | 99
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.12261 | WERE | 'CITY OF WELLINGTON 69KV' | 41.45 | -0.00084 | -0.12177 | 99
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.12261 | WERE | 'EVANS ENERGY CENTER 138KV' | 320.8022 | -0.00076 | -0.12185 | 99
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.12261 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00118 | -0.12143 | 99
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.12261 | WERE | 'LANG 7 345 345KV' | 310 | -0.00025 | -0.12236 | 99
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.12261 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | -0.00259 | -0.12002 | 101
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.12261 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 274.2987 | -0.00281 | -0.1198 | 101
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.12261 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | -0.00544 | -0.11717 | 103
WERE | 'PAWNEE 115KV' | 999 | -0.02237 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08159 | -0.10396 | 116
WERE | 'RICE 115KV' | 999 | -0.02237 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08159 | -0.10396 | 116
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.06768 | WERE | 'KNOLL 3 115 115KV' | 75 | 0.02275 | -0.09043 | 134
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.06764 | WERE | 'KNOLL 3 115 115KV' | 75 | 0.02275 | -0.09039 | 134
WERE | 'TECUMSEH ENERGY CENTER 115KV' | 53 | -0.00544 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08159 | -0.08703 | 139
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.00107 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08159 | -0.08266 | 146
WERE | 'CLR_3 .575 34KV' | 300 | -0.00047 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08159 | -0.08206 | 147
WERE | 'EVANS ENERGY CENTER 138KV' | 486.1978 | -0.00076 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08159 | -0.08235 | 147
WERE | 'EVANS N4 138 16KV' | 360 | -0.00076 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08159 | -0.08235 | 147
WERE | 'LATHAM1234.0 345KV' | 150 | -0.00047 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08159 | -0.08206 | 147
WERE | 'LANG 7 345 345KV' | 518 | -0.00025 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08159 | -0.08184 | 148
WERE | 'LYONS 115KV' | 999 | -7e-05 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08159 | -0.08166 | 148
WERE | 'NEOSHO ENERGY CENTER 138KV' | 67 | -0.00021 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08159 | -0.0818 | 148
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.06768 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | 0.00929 | -0.07697 | 157
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.06764 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | 0.00929 | -0.07693 | 157
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.06768 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | 0.00064 | -0.06832 | 177
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.06764 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | 0.00064 | -0.06828 | 177
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.06768 | WERE | 'LANG 7 345 345KV' | 310 | -0.00025 | -0.06743 | 179
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.06764 | WERE | 'LANG 7 345 345KV' | 310 | -0.00025 | -0.06739 | 179
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.06768 | WERE | 'EVANS ENERGY CENTER 138KV' | 320.8022 | -0.00076 | -0.06692 | 180
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.06764 | WERE | 'EVANS ENERGY CENTER 138KV' | 320.8022 | -0.00076 | -0.06688 | 181
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.06768 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00118 | -0.0665 | 182
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.06764 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00118 | -0.06646 | 182
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.06768 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | -0.00259 | -0.06509 | 186
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.06768 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 274.2987 | -0.00281 | -0.06487 | 186
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.06764 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | -0.00259 | -0.06505 | 186
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.06764 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 274.2987 | -0.00281 | -0.06483 | 186
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.06768 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | -0.00544 | -0.06224 | 194
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.06764 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | -0.00544 | -0.0622 | 194
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.12261 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 120 | -0.06768 | -0.05493 | 220
WERE | 'PAWNEE 115KV' | 999 | -0.02237 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | 0.00929 | -0.03166 | 381
WERE | 'RICE 115KV' | 999 | -0.02237 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | 0.00929 | -0.03166 | 381
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | WICHITA - RENO 345KV
Limiting Facility: | NORTHVIEW - SUMMIT 115KV CKT 1
Direction: | To->From
Line Outage: | EXIDE JUNCTION - SUMMIT 115KV CKT 1
Flowgate: | 57371573811573685738112411SP
Date Redispatch Needed: | 6/1/09 - 7/1/09
Season Flowgate Identified: | 2011 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1140120 | 0.29264 | 0.88176
1161506 | 0.29264 | 0.88176
1161997 | 0.29648 | 0.88176
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.36594 | WERE | 'CHANUTE 69KV' | 58.843 | -0.00025 | -0.36569 | 2
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.36594 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | -0.00082 | -0.36512 | 2
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.36594 | WERE | 'CITY OF BURLINGTON 69KV' | 7.8 | -0.00034 | -0.3656 | 2
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.36594 | WERE | 'CITY OF ERIE 69KV' | 23.579 | -0.00025 | -0.36569 | 2
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.36594 | WERE | 'CITY OF FREDONIA 69KV' | 3.897 | -0.00031 | -0.36563 | 2
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.36594 | WERE | 'CITY OF GIRARD 69KV' | 5.092 | -0.00017 | -0.36577 | 2
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.36594 | WERE | 'CITY OF IOLA 69KV' | 27.273 | -0.0002 | -0.36574 | 2
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.36594 | WERE | 'CITY OF MULVANE 69KV' | 9.291 | -0.00088 | -0.36506 | 2
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.36594 | WERE | 'CITY OF WELLINGTON 69KV' | 41.45 | -0.00086 | -0.36508 | 2
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.36594 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.98 | -0.00034 | -0.3656 | 2
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.36594 | WERE | 'COLBY 115KV' | 5.6267 | 0.00254 | -0.36848 | 2
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.36594 | WERE | 'EVANS ENERGY CENTER 138KV' | 340.124 | -0.00078 | -0.36516 | 2
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.36594 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.0012 | -0.36474 | 2
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.36594 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.00056 | -0.3665 | 2
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.36594 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.00918 | -0.37512 | 2
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.36594 | WERE | 'KNOLL 3 115 115KV' | 44.7 | 0.02262 | -0.38856 | 2
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.36594 | WERE | 'LANG 7 345 345KV' | 610 | -0.00028 | -0.36566 | 2
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.36594 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | -0.0025 | -0.36344 | 2
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.36594 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 215.1338 | -0.00275 | -0.36319 | 2
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.36594 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08151 | -0.44745 | 2
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.36594 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 128 | -0.00546 | -0.36048 | 2
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.36594 | WERE | 'WACO 138KV' | 17.972 | -0.00115 | -0.36479 | 2
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.36594 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 120 | -0.06775 | -0.29819 | 3
WERE | 'CLAY CENTER JUNCTION 115KV' | 18.234 | -0.24142 | WERE | 'KNOLL 3 115 115KV' | 44.7 | 0.02262 | -0.26404 | 3
WERE | 'CLAY CENTER JUNCTION 115KV' | 18.234 | -0.24142 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08151 | -0.32293 | 3
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.36594 | WERE | 'BPU - CITY OF MCPHERSON 115KV' | 135 | -0.12268 | -0.24326 | 4
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 39 | -0.12268 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08151 | -0.20419 | 4
WERE | 'CLAY CENTER JUNCTION 115KV' | 18.234 | -0.24142 | WERE | 'CHANUTE 69KV' | 58.843 | -0.00025 | -0.24117 | 4
WERE | 'CLAY CENTER JUNCTION 115KV' | 18.234 | -0.24142 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | -0.00082 | -0.2406 | 4
WERE | 'CLAY CENTER JUNCTION 115KV' | 18.234 | -0.24142 | WERE | 'CITY OF BURLINGTON 69KV' | 7.8 | -0.00034 | -0.24108 | 4
WERE | 'CLAY CENTER JUNCTION 115KV' | 18.234 | -0.24142 | WERE | 'CITY OF ERIE 69KV' | 23.579 | -0.00025 | -0.24117 | 4
WERE | 'CLAY CENTER JUNCTION 115KV' | 18.234 | -0.24142 | WERE | 'CITY OF FREDONIA 69KV' | 3.897 | -0.00031 | -0.24111 | 4
WERE | 'CLAY CENTER JUNCTION 115KV' | 18.234 | -0.24142 | WERE | 'CITY OF GIRARD 69KV' | 5.092 | -0.00017 | -0.24125 | 4
WERE | 'CLAY CENTER JUNCTION 115KV' | 18.234 | -0.24142 | WERE | 'CITY OF IOLA 69KV' | 27.273 | -0.0002 | -0.24122 | 4
WERE | 'CLAY CENTER JUNCTION 115KV' | 18.234 | -0.24142 | WERE | 'CITY OF MULVANE 69KV' | 9.291 | -0.00088 | -0.24054 | 4
WERE | 'CLAY CENTER JUNCTION 115KV' | 18.234 | -0.24142 | WERE | 'CITY OF WELLINGTON 69KV' | 41.45 | -0.00086 | -0.24056 | 4
WERE | 'CLAY CENTER JUNCTION 115KV' | 18.234 | -0.24142 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.98 | -0.00034 | -0.24108 | 4
WERE | 'CLAY CENTER JUNCTION 115KV' | 18.234 | -0.24142 | WERE | 'COLBY 115KV' | 5.6267 | 0.00254 | -0.24396 | 4
WERE | 'CLAY CENTER JUNCTION 115KV' | 18.234 | -0.24142 | WERE | 'EVANS ENERGY CENTER 138KV' | 340.124 | -0.00078 | -0.24064 | 4
WERE | 'CLAY CENTER JUNCTION 115KV' | 18.234 | -0.24142 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.0012 | -0.24022 | 4
WERE | 'CLAY CENTER JUNCTION 115KV' | 18.234 | -0.24142 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.00056 | -0.24198 | 4
WERE | 'CLAY CENTER JUNCTION 115KV' | 18.234 | -0.24142 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.00918 | -0.2506 | 4
WERE | 'CLAY CENTER JUNCTION 115KV' | 18.234 | -0.24142 | WERE | 'LANG 7 345 345KV' | 610 | -0.00028 | -0.24114 | 4
WERE | 'CLAY CENTER JUNCTION 115KV' | 18.234 | -0.24142 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | -0.0025 | -0.23892 | 4
WERE | 'CLAY CENTER JUNCTION 115KV' | 18.234 | -0.24142 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 215.1338 | -0.00275 | -0.23867 | 4
WERE | 'CLAY CENTER JUNCTION 115KV' | 18.234 | -0.24142 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 128 | -0.00546 | -0.23596 | 4
WERE | 'CLAY CENTER JUNCTION 115KV' | 18.234 | -0.24142 | WERE | 'WACO 138KV' | 17.972 | -0.00115 | -0.24027 | 4
WERE | 'CLAY CENTER JUNCTION 115KV' | 18.234 | -0.24142 | WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 120 | -0.06775 | -0.17367 | 5
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 39 | -0.12268 | WERE | 'KNOLL 3 115 115KV' | 44.7 | 0.02262 | -0.1453 | 6
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.06775 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08151 | -0.14926 | 6
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.06766 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08151 | -0.14917 | 6
WERE | 'ABILENE ENERGY CENTER 115KV' | 6 | -0.36594 | WERE | 'CLAY CENTER JUNCTION 115KV' | 19.866 | -0.24142 | -0.12452 | 7
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 39 | -0.12268 | WERE | 'CHANUTE 69KV' | 58.843 | -0.00025 | -0.12243 | 7
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 39 | -0.12268 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | -0.00082 | -0.12186 | 7
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 39 | -0.12268 | WERE | 'CITY OF BURLINGTON 69KV' | 7.8 | -0.00034 | -0.12234 | 7
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 39 | -0.12268 | WERE | 'CITY OF ERIE 69KV' | 23.579 | -0.00025 | -0.12243 | 7
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 39 | -0.12268 | WERE | 'CITY OF FREDONIA 69KV' | 3.897 | -0.00031 | -0.12237 | 7
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 39 | -0.12268 | WERE | 'CITY OF GIRARD 69KV' | 5.092 | -0.00017 | -0.12251 | 7
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 39 | -0.12268 | WERE | 'CITY OF IOLA 69KV' | 27.273 | -0.0002 | -0.12248 | 7
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 39 | -0.12268 | WERE | 'CITY OF MULVANE 69KV' | 9.291 | -0.00088 | -0.1218 | 7
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 39 | -0.12268 | WERE | 'CITY OF WELLINGTON 69KV' | 41.45 | -0.00086 | -0.12182 | 7
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 39 | -0.12268 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.98 | -0.00034 | -0.12234 | 7
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 39 | -0.12268 | WERE | 'COLBY 115KV' | 5.6267 | 0.00254 | -0.12522 | 7
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 39 | -0.12268 | WERE | 'EVANS ENERGY CENTER 138KV' | 340.124 | -0.00078 | -0.1219 | 7
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 39 | -0.12268 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.0012 | -0.12148 | 7
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 39 | -0.12268 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.00056 | -0.12324 | 7
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 39 | -0.12268 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.00918 | -0.13186 | 7
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 39 | -0.12268 | WERE | 'LANG 7 345 345KV' | 610 | -0.00028 | -0.1224 | 7
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 39 | -0.12268 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | -0.0025 | -0.12018 | 7
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 39 | -0.12268 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 215.1338 | -0.00275 | -0.11993 | 7
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 39 | -0.12268 | WERE | 'WACO 138KV' | 17.972 | -0.00115 | -0.12153 | 7
WERE | 'CLAY CENTER JUNCTION 115KV' | 18.234 | -0.24142 | WERE | 'BPU - CITY OF MCPHERSON 115KV' | 135 | -0.12268 | -0.11874 | 7
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 39 | -0.12268 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 128 | -0.00546 | -0.11722 | 8
WERE | 'PAWNEE 115KV' | 999 | -0.0224 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08151 | -0.10391 | 8
WERE | 'RICE 115KV' | 999 | -0.0224 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08151 | -0.10391 | 8
WERE | 'ST JOHN 115KV' | 7.5 | -0.0224 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08151 | -0.10391 | 8
WERE | 'BROWN COUNTY 115KV' | 5.5 | -0.00259 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08151 | -0.0841 | 10
WERE | 'CITY OF OSAGE CITY 115KV' | 8.85 | -0.00406 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08151 | -0.08557 | 10
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.00785 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08151 | -0.08936 | 10
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.06775 | WERE | 'KNOLL 3 115 115KV' | 44.7 | 0.02262 | -0.09037 | 10
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.06766 | WERE | 'KNOLL 3 115 115KV' | 44.7 | 0.02262 | -0.09028 | 10
WERE | 'LAWRENCE ENERGY CENTER 115KV' | 28 | -0.0025 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08151 | -0.08401 | 10
WERE | 'LAWRENCE ENERGY CENTER 230KV' | 53.8662 | -0.00275 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08151 | -0.08426 | 10
WERE | 'SOUTH SENECA 115KV' | 16.7 | -0.00377 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08151 | -0.08528 | 10
WERE | 'TECUMSEH ENERGY CENTER 115KV' | 33 | -0.00546 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08151 | -0.08697 | 10
WERE | 'TECUMSEH ENERGY CENTER 69KV' | 41 | -0.00599 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08151 | -0.0875 | 10
WERE | 'ATWOOD 115KV' | 4 | 0.00286 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08151 | -0.07865 | 11
WERE | 'CHANUTE 69KV' | 28.957 | -0.00025 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08151 | -0.08176 | 11
WERE | 'CITY OF AUGUSTA 69KV' | 7.32 | -0.00082 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08151 | -0.08233 | 11
WERE | 'CITY OF BURLINGTON 69KV' | 4.7 | -0.00034 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08151 | -0.08185 | 11
WERE | 'CITY OF FREDONIA 69KV' | 6.397 | -0.00031 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08151 | -0.08182 | 11
WERE | 'CITY OF GIRARD 69KV' | 5.608 | -0.00017 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08151 | -0.08168 | 11
WERE | 'CITY OF IOLA 69KV' | 10.355 | -0.0002 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08151 | -0.08171 | 11
WERE | 'CITY OF MULVANE 69KV' | 6.499 | -0.00088 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08151 | -0.08239 | 11
WERE | 'CITY OF NEODESHA 69KV' | 4.5 | -0.0003 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08151 | -0.08181 | 11
WERE | 'CITY OF WINFIELD 69KV' | 40 | -0.00071 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08151 | -0.08222 | 11
WERE | 'CLR_3 .575 34KV' | 300 | -0.0005 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08151 | -0.08201 | 11
WERE | 'COLBY 115KV' | 7.3733 | 0.00254 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08151 | -0.07897 | 11
WERE | 'EVANS ENERGY CENTER 138KV' | 386.876 | -0.00078 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08151 | -0.08229 | 11
WERE | 'EVANS N4 138 16KV' | 360 | -0.00078 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.08151 | -0.08229 | 11
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | WICHITA - RENO 345KV
Limiting Facility: | NORTH AMERICAN PHILIPS - NORTH AMERICAN PHILIPS JUNCTION (SOUTH) 115KV CKT 1
Direction: | From->To
Line Outage: | EAST MCPHERSON - SUMMIT 230KV CKT 1
Flowgate: | 57372573741568725687312208SP
Date Redispatch Needed: | Starting 2008 6/1 - 10/1 Until EOC of Upgrade
Season Flowgate Identified: | 2008 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1161506 | 4.1304 | 4.1304
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.50613 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | 0.11586 | -0.62199 | 7
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.50613 | WERE | 'CLAY CENTER JUNCTION 115KV' | 21.056 | 0.0854 | -0.59153 | 7
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.50613 | WERE | 'CHANUTE 69KV' | 55.637 | 0.00263 | -0.50876 | 8
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.50613 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | 0.00124 | -0.50737 | 8
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.50613 | WERE | 'CITY OF BURLINGTON 69KV' | 7.8 | 0.0047 | -0.51083 | 8
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.50613 | WERE | 'CITY OF ERIE 69KV' | 23.374 | 0.00263 | -0.50876 | 8
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.50613 | WERE | 'CITY OF FREDONIA 69KV' | 3.596 | 0.00213 | -0.50826 | 8
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.50613 | WERE | 'CITY OF GIRARD 69KV' | 4.592 | 0.00265 | -0.50878 | 8
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.50613 | WERE | 'CITY OF IOLA 69KV' | 24.471 | 0.00304 | -0.50917 | 8
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.50613 | WERE | 'CITY OF MULVANE 69KV' | 8.29 | -0.00106 | -0.50507 | 8
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.50613 | WERE | 'CITY OF WELLINGTON 69KV' | 41.45 | -0.00234 | -0.50379 | 8
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.50613 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.98 | 0.0047 | -0.51083 | 8
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.50613 | WERE | 'EVANS ENERGY CENTER 138KV' | 320.8022 | 0.00051 | -0.50664 | 8
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.50613 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00477 | -0.50136 | 8
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.50613 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | 0.02838 | -0.53451 | 8
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.50613 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | 0.02959 | -0.53572 | 8
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.50613 | WERE | 'LANG 7 345 345KV' | 310 | 0.01524 | -0.52137 | 8
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.50613 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | 0.01734 | -0.52347 | 8
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.50613 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 274.2987 | 0.0182 | -0.52433 | 8
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.50613 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.02975 | -0.53588 | 8
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.50613 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.0196 | -0.52573 | 8
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.50613 | WERE | 'WACO 138KV' | 17.967 | -0.00424 | -0.50189 | 8
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.40078 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | 0.11586 | -0.51664 | 8
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.40078 | WERE | 'CLAY CENTER JUNCTION 115KV' | 21.056 | 0.0854 | -0.48618 | 8
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40059 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | 0.11586 | -0.51645 | 8
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40059 | WERE | 'CLAY CENTER JUNCTION 115KV' | 21.056 | 0.0854 | -0.48599 | 8
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 239 | -0.50613 | WERE | 'KNOLL 3 115 115KV' | 75 | -0.09259 | -0.41354 | 10
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.40078 | WERE | 'CHANUTE 69KV' | 55.637 | 0.00263 | -0.40341 | 10
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.40078 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | 0.00124 | -0.40202 | 10
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.40078 | WERE | 'CITY OF BURLINGTON 69KV' | 7.8 | 0.0047 | -0.40548 | 10
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.40078 | WERE | 'CITY OF ERIE 69KV' | 23.374 | 0.00263 | -0.40341 | 10
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.40078 | WERE | 'CITY OF FREDONIA 69KV' | 3.596 | 0.00213 | -0.40291 | 10
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.40078 | WERE | 'CITY OF GIRARD 69KV' | 4.592 | 0.00265 | -0.40343 | 10
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.40078 | WERE | 'CITY OF IOLA 69KV' | 24.471 | 0.00304 | -0.40382 | 10
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.40078 | WERE | 'CITY OF MULVANE 69KV' | 8.29 | -0.00106 | -0.39972 | 10
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.40078 | WERE | 'CITY OF WELLINGTON 69KV' | 41.45 | -0.00234 | -0.39844 | 10
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.40078 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.98 | 0.0047 | -0.40548 | 10
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.40078 | WERE | 'EVANS ENERGY CENTER 138KV' | 320.8022 | 0.00051 | -0.40129 | 10
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.40078 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00477 | -0.39601 | 10
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.40078 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | 0.02838 | -0.42916 | 10
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.40078 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | 0.02959 | -0.43037 | 10
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.40078 | WERE | 'LANG 7 345 345KV' | 310 | 0.01524 | -0.41602 | 10
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.40078 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | 0.01734 | -0.41812 | 10
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.40078 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 274.2987 | 0.0182 | -0.41898 | 10
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.40078 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.02975 | -0.43053 | 10
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.40078 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.0196 | -0.42038 | 10
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.40078 | WERE | 'WACO 138KV' | 17.967 | -0.00424 | -0.39654 | 10
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40059 | WERE | 'CHANUTE 69KV' | 55.637 | 0.00263 | -0.40322 | 10
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40059 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | 0.00124 | -0.40183 | 10
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40059 | WERE | 'CITY OF BURLINGTON 69KV' | 7.8 | 0.0047 | -0.40529 | 10
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40059 | WERE | 'CITY OF ERIE 69KV' | 23.374 | 0.00263 | -0.40322 | 10
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40059 | WERE | 'CITY OF FREDONIA 69KV' | 3.596 | 0.00213 | -0.40272 | 10
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40059 | WERE | 'CITY OF GIRARD 69KV' | 4.592 | 0.00265 | -0.40324 | 10
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40059 | WERE | 'CITY OF IOLA 69KV' | 24.471 | 0.00304 | -0.40363 | 10
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40059 | WERE | 'CITY OF MULVANE 69KV' | 8.29 | -0.00106 | -0.39953 | 10
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40059 | WERE | 'CITY OF WELLINGTON 69KV' | 41.45 | -0.00234 | -0.39825 | 10
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40059 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.98 | 0.0047 | -0.40529 | 10
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40059 | WERE | 'EVANS ENERGY CENTER 138KV' | 320.8022 | 0.00051 | -0.4011 | 10
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40059 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00477 | -0.39582 | 10
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40059 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | 0.02838 | -0.42897 | 10
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40059 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | 0.02959 | -0.43018 | 10
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40059 | WERE | 'LANG 7 345 345KV' | 310 | 0.01524 | -0.41583 | 10
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40059 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | 0.01734 | -0.41793 | 10
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40059 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 274.2987 | 0.0182 | -0.41879 | 10
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40059 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.02975 | -0.43034 | 10
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40059 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.0196 | -0.42019 | 10
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40059 | WERE | 'WACO 138KV' | 17.967 | -0.00424 | -0.39635 | 10
WERE | 'PAWNEE 115KV' | 999 | -0.21553 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | 0.11586 | -0.33139 | 12
WERE | 'RICE 115KV' | 999 | -0.21553 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | 0.11586 | -0.33139 | 12
WERE | 'ST JOHN 115KV' | 7.5 | -0.21553 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | 0.11586 | -0.33139 | 12
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.40078 | WERE | 'KNOLL 3 115 115KV' | 75 | -0.09259 | -0.30819 | 13
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40059 | WERE | 'KNOLL 3 115 115KV' | 75 | -0.09259 | -0.308 | 13
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.17955 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | 0.11586 | -0.29541 | 14
WERE | 'PAWNEE 115KV' | 999 | -0.21553 | WERE | 'CLAY CENTER JUNCTION 115KV' | 21.056 | 0.0854 | -0.30093 | 14
WERE | 'RICE 115KV' | 999 | -0.21553 | WERE | 'CLAY CENTER JUNCTION 115KV' | 21.056 | 0.0854 | -0.30093 | 14
WERE | 'ST JOHN 115KV' | 7.5 | -0.21553 | WERE | 'CLAY CENTER JUNCTION 115KV' | 21.056 | 0.0854 | -0.30093 | 14
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.17955 | WERE | 'CLAY CENTER JUNCTION 115KV' | 21.056 | 0.0854 | -0.26495 | 16
WERE | 'PAWNEE 115KV' | 999 | -0.21553 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | 0.02838 | -0.24391 | 17
WERE | 'PAWNEE 115KV' | 999 | -0.21553 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | 0.02959 | -0.24512 | 17
WERE | 'PAWNEE 115KV' | 999 | -0.21553 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.02975 | -0.24528 | 17
WERE | 'RICE 115KV' | 999 | -0.21553 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | 0.02838 | -0.24391 | 17
WERE | 'RICE 115KV' | 999 | -0.21553 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | 0.02959 | -0.24512 | 17
WERE | 'RICE 115KV' | 999 | -0.21553 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.02975 | -0.24528 | 17
WERE | 'ST JOHN 115KV' | 7.5 | -0.21553 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 494 | 0.02838 | -0.24391 | 17
WERE | 'ST JOHN 115KV' | 7.5 | -0.21553 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 982 | 0.02959 | -0.24512 | 17
WERE | 'ST JOHN 115KV' | 7.5 | -0.21553 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.02975 | -0.24528 | 17
WERE | 'PAWNEE 115KV' | 999 | -0.21553 | WERE | 'LANG 7 345 345KV' | 310 | 0.01524 | -0.23077 | 18
WERE | 'PAWNEE 115KV' | 999 | -0.21553 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | 0.01734 | -0.23287 | 18
WERE | 'PAWNEE 115KV' | 999 | -0.21553 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 274.2987 | 0.0182 | -0.23373 | 18
WERE | 'PAWNEE 115KV' | 999 | -0.21553 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.0196 | -0.23513 | 18
WERE | 'RICE 115KV' | 999 | -0.21553 | WERE | 'LANG 7 345 345KV' | 310 | 0.01524 | -0.23077 | 18
WERE | 'RICE 115KV' | 999 | -0.21553 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | 0.01734 | -0.23287 | 18
WERE | 'RICE 115KV' | 999 | -0.21553 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 274.2987 | 0.0182 | -0.23373 | 18
WERE | 'RICE 115KV' | 999 | -0.21553 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.0196 | -0.23513 | 18
WERE | 'ST JOHN 115KV' | 7.5 | -0.21553 | WERE | 'LANG 7 345 345KV' | 310 | 0.01524 | -0.23077 | 18
WERE | 'ST JOHN 115KV' | 7.5 | -0.21553 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | 0.01734 | -0.23287 | 18
WERE | 'ST JOHN 115KV' | 7.5 | -0.21553 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 274.2987 | 0.0182 | -0.23373 | 18
WERE | 'ST JOHN 115KV' | 7.5 | -0.21553 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.0196 | -0.23513 | 18
WERE | 'PAWNEE 115KV' | 999 | -0.21553 | WERE | 'CHANUTE 69KV' | 55.637 | 0.00263 | -0.21816 | 19
WERE | 'PAWNEE 115KV' | 999 | -0.21553 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | 0.00124 | -0.21677 | 19
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | WICHITA - RENO 345KV
Limiting Facility: | NORTH AMERICAN PHILIPS - NORTH AMERICAN PHILIPS JUNCTION (SOUTH) 115KV CKT 1
Direction: | From->To
Line Outage: | EAST MCPHERSON - SUMMIT 230KV CKT 1
Flowgate: | 57372573741568725687312211SP
Date Redispatch Needed: | 6/1/09 - 7/1/09
Season Flowgate Identified: | 2011 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1140120 | 6.305 | 12.8102
1161506 | 6.5052 | 12.8102
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.5065 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | 0.11518 | -0.62168 | 21
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.5065 | WERE | 'CLAY CENTER JUNCTION 115KV' | 19.866 | 0.08468 | -0.59118 | 22
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.5065 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.02748 | -0.53398 | 24
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.5065 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02867 | -0.53517 | 24
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.5065 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | 0.01643 | -0.52293 | 24
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.5065 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 201.5866 | 0.01737 | -0.52387 | 24
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.5065 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.02926 | -0.53576 | 24
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.5065 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.0188 | -0.5253 | 24
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.5065 | WERE | 'CHANUTE 69KV' | 58.843 | 0.00245 | -0.50895 | 25
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.5065 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | 0.00107 | -0.50757 | 25
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.5065 | WERE | 'CITY OF ERIE 69KV' | 23.579 | 0.00245 | -0.50895 | 25
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.5065 | WERE | 'CITY OF IOLA 69KV' | 27.273 | 0.00286 | -0.50936 | 25
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.5065 | WERE | 'CITY OF MULVANE 69KV' | 9.291 | -0.00119 | -0.50531 | 25
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.5065 | WERE | 'CITY OF WELLINGTON 69KV' | 41.45 | -0.00252 | -0.50398 | 25
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.5065 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.98 | 0.00439 | -0.51089 | 25
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.5065 | WERE | 'EVANS ENERGY CENTER 138KV' | 331.6143 | 0.00025 | -0.50675 | 25
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.5065 | WERE | 'LANG 7 345 345KV' | 610 | 0.01466 | -0.52116 | 25
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.40109 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | 0.11518 | -0.51627 | 25
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40069 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | 0.11518 | -0.51587 | 25
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.5065 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00496 | -0.50154 | 26
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.5065 | WERE | 'WACO 138KV' | 17.972 | -0.00443 | -0.50207 | 26
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.40109 | WERE | 'CLAY CENTER JUNCTION 115KV' | 19.866 | 0.08468 | -0.48577 | 26
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40069 | WERE | 'CLAY CENTER JUNCTION 115KV' | 19.866 | 0.08468 | -0.48537 | 26
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.40109 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.02748 | -0.42857 | 30
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.40109 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02867 | -0.42976 | 30
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.40109 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.02926 | -0.43035 | 30
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40069 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.02748 | -0.42817 | 30
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40069 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02867 | -0.42936 | 30
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40069 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.02926 | -0.42995 | 30
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.5065 | WERE | 'KNOLL 3 115 115KV' | 21.7 | -0.0927 | -0.4138 | 31
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.40109 | WERE | 'LANG 7 345 345KV' | 610 | 0.01466 | -0.41575 | 31
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.40109 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | 0.01643 | -0.41752 | 31
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.40109 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 201.5866 | 0.01737 | -0.41846 | 31
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.40109 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.0188 | -0.41989 | 31
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40069 | WERE | 'LANG 7 345 345KV' | 610 | 0.01466 | -0.41535 | 31
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40069 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | 0.01643 | -0.41712 | 31
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40069 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 201.5866 | 0.01737 | -0.41806 | 31
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40069 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.0188 | -0.41949 | 31
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.40109 | WERE | 'CHANUTE 69KV' | 58.843 | 0.00245 | -0.40354 | 32
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.40109 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | 0.00107 | -0.40216 | 32
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.40109 | WERE | 'CITY OF ERIE 69KV' | 23.579 | 0.00245 | -0.40354 | 32
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.40109 | WERE | 'CITY OF IOLA 69KV' | 27.273 | 0.00286 | -0.40395 | 32
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.40109 | WERE | 'CITY OF WELLINGTON 69KV' | 41.45 | -0.00252 | -0.39857 | 32
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.40109 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.98 | 0.00439 | -0.40548 | 32
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.40109 | WERE | 'EVANS ENERGY CENTER 138KV' | 331.6143 | 0.00025 | -0.40134 | 32
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.40109 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00496 | -0.39613 | 32
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.40109 | WERE | 'WACO 138KV' | 17.972 | -0.00443 | -0.39666 | 32
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40069 | WERE | 'CHANUTE 69KV' | 58.843 | 0.00245 | -0.40314 | 32
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40069 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | 0.00107 | -0.40176 | 32
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40069 | WERE | 'CITY OF ERIE 69KV' | 23.579 | 0.00245 | -0.40314 | 32
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40069 | WERE | 'CITY OF IOLA 69KV' | 27.273 | 0.00286 | -0.40355 | 32
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40069 | WERE | 'CITY OF WELLINGTON 69KV' | 41.45 | -0.00252 | -0.39817 | 32
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40069 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.98 | 0.00439 | -0.40508 | 32
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40069 | WERE | 'EVANS ENERGY CENTER 138KV' | 331.6143 | 0.00025 | -0.40094 | 32
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40069 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00496 | -0.39573 | 32
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40069 | WERE | 'WACO 138KV' | 17.972 | -0.00443 | -0.39626 | 32
WERE | 'PAWNEE 115KV' | 999 | -0.21568 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | 0.11518 | -0.33086 | 39
WERE | 'RICE 115KV' | 999 | -0.21568 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | 0.11518 | -0.33086 | 39
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 263 | -0.40109 | WERE | 'KNOLL 3 115 115KV' | 21.7 | -0.0927 | -0.30839 | 42
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40069 | WERE | 'KNOLL 3 115 115KV' | 21.7 | -0.0927 | -0.30799 | 42
WERE | 'PAWNEE 115KV' | 999 | -0.21568 | WERE | 'CLAY CENTER JUNCTION 115KV' | 19.866 | 0.08468 | -0.30036 | 43
WERE | 'RICE 115KV' | 999 | -0.21568 | WERE | 'CLAY CENTER JUNCTION 115KV' | 19.866 | 0.08468 | -0.30036 | 43
WERE | 'PAWNEE 115KV' | 999 | -0.21568 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02867 | -0.24435 | 52
WERE | 'PAWNEE 115KV' | 999 | -0.21568 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.02926 | -0.24494 | 52
WERE | 'RICE 115KV' | 999 | -0.21568 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02867 | -0.24435 | 52
WERE | 'RICE 115KV' | 999 | -0.21568 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.02926 | -0.24494 | 52
WERE | 'PAWNEE 115KV' | 999 | -0.21568 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.02748 | -0.24316 | 53
WERE | 'RICE 115KV' | 999 | -0.21568 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.02748 | -0.24316 | 53
WERE | 'PAWNEE 115KV' | 999 | -0.21568 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | 0.01643 | -0.23211 | 55
WERE | 'PAWNEE 115KV' | 999 | -0.21568 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 201.5866 | 0.01737 | -0.23305 | 55
WERE | 'PAWNEE 115KV' | 999 | -0.21568 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.0188 | -0.23448 | 55
WERE | 'RICE 115KV' | 999 | -0.21568 | WERE | 'LAWRENCE ENERGY CENTER 115KV' | 85 | 0.01643 | -0.23211 | 55
WERE | 'RICE 115KV' | 999 | -0.21568 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 201.5866 | 0.01737 | -0.23305 | 55
WERE | 'RICE 115KV' | 999 | -0.21568 | WERE | 'TECUMSEH ENERGY CENTER 115KV' | 108 | 0.0188 | -0.23448 | 55
WERE | 'PAWNEE 115KV' | 999 | -0.21568 | WERE | 'LANG 7 345 345KV' | 610 | 0.01466 | -0.23034 | 56
WERE | 'RICE 115KV' | 999 | -0.21568 | WERE | 'LANG 7 345 345KV' | 610 | 0.01466 | -0.23034 | 56
WERE | 'PAWNEE 115KV' | 999 | -0.21568 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.98 | 0.00439 | -0.22007 | 58
WERE | 'RICE 115KV' | 999 | -0.21568 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.98 | 0.00439 | -0.22007 | 58
WERE | 'PAWNEE 115KV' | 999 | -0.21568 | WERE | 'CHANUTE 69KV' | 58.843 | 0.00245 | -0.21813 | 59
WERE | 'PAWNEE 115KV' | 999 | -0.21568 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | 0.00107 | -0.21675 | 59
WERE | 'PAWNEE 115KV' | 999 | -0.21568 | WERE | 'CITY OF ERIE 69KV' | 23.579 | 0.00245 | -0.21813 | 59
WERE | 'PAWNEE 115KV' | 999 | -0.21568 | WERE | 'CITY OF IOLA 69KV' | 27.273 | 0.00286 | -0.21854 | 59
WERE | 'PAWNEE 115KV' | 999 | -0.21568 | WERE | 'EVANS ENERGY CENTER 138KV' | 331.6143 | 0.00025 | -0.21593 | 59
WERE | 'RICE 115KV' | 999 | -0.21568 | WERE | 'CHANUTE 69KV' | 58.843 | 0.00245 | -0.21813 | 59
WERE | 'RICE 115KV' | 999 | -0.21568 | WERE | 'CITY OF AUGUSTA 69KV' | 20.02 | 0.00107 | -0.21675 | 59
WERE | 'RICE 115KV' | 999 | -0.21568 | WERE | 'CITY OF ERIE 69KV' | 23.579 | 0.00245 | -0.21813 | 59
WERE | 'RICE 115KV' | 999 | -0.21568 | WERE | 'CITY OF IOLA 69KV' | 27.273 | 0.00286 | -0.21854 | 59
WERE | 'RICE 115KV' | 999 | -0.21568 | WERE | 'EVANS ENERGY CENTER 138KV' | 331.6143 | 0.00025 | -0.21593 | 59
WERE | 'PAWNEE 115KV' | 999 | -0.21568 | WERE | 'CITY OF WELLINGTON 69KV' | 41.45 | -0.00252 | -0.21316 | 60
WERE | 'RICE 115KV' | 999 | -0.21568 | WERE | 'CITY OF WELLINGTON 69KV' | 41.45 | -0.00252 | -0.21316 | 60
WERE | 'PAWNEE 115KV' | 999 | -0.21568 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00496 | -0.21072 | 61
WERE | 'RICE 115KV' | 999 | -0.21568 | WERE | 'GILL ENERGY CENTER 138KV' | 155 | -0.00496 | -0.21072 | 61
WERE | 'KNOLL 3 115 115KV' | 62.66 | -0.0927 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | 0.11518 | -0.20788 | 62
WERE | 'KNOLL 3 115 115KV' | 62.66 | -0.0927 | WERE | 'SMOKEY HILLS 34KV' | 152 | 0.02926 | -0.12196 | 105
WERE | 'KNOLL 3 115 115KV' | 62.66 | -0.0927 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 940 | 0.02867 | -0.12137 | 106
WERE | 'KNOLL 3 115 115KV' | 62.66 | -0.0927 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 470 | 0.02748 | -0.12018 | 107
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.00359 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | 0.11518 | -0.11877 | 108
WERE | 'CITY OF WINFIELD 69KV' | 40 | -0.00135 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | 0.11518 | -0.11653 | 110
WERE | 'EVANS ENERGY CENTER 138KV' | 475.3857 | 0.00025 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | 0.11518 | -0.11493 | 111
WERE | 'EVANS N4 138 16KV' | 360 | 0.00028 | WERE | 'ABILENE ENERGY CENTER 115KV' | 40 | 0.11518 | -0.1149 | 111
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | WICHITA - RENO 345KV
Limiting Facility: | NORTH AMERICAN PHILIPS - NORTH AMERICAN PHILIPS JUNCTION (SOUTH) 115KV CKT 1
Direction: | From->To
Line Outage: | EAST MCPHERSON - SUMMIT 230KV CKT 1
Flowgate: | 57372573741568725687314208WP
Date Redispatch Needed: | Starting 2008 12/1 - 4/1 Until EOC of Upgrade
Season Flowgate Identified: | 2008 Winter Peak
Reservation | Relief Amount | Aggregate Relief Amount
1161506 | 6.0353 | 6.0353
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50615 | WERE | 'CLAY CENTER JUNCTION 115KV' | 6.7 | 0.08529 | -0.59144 | 10
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50615 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 490 | 0.02826 | -0.53441 | 11
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50615 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 974.2261 | 0.02949 | -0.53564 | 11
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50615 | WERE | 'SMOKEY HILLS 34KV' | 51 | 0.02972 | -0.53587 | 11
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50615 | WERE | 'CHANUTE 69KV' | 34.903 | 0.00262 | -0.50877 | 12
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50615 | WERE | 'CITY OF AUGUSTA 69KV' | 15.285 | 0.00121 | -0.50736 | 12
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50615 | WERE | 'CITY OF BURLINGTON 69KV' | 4.8 | 0.00468 | -0.51083 | 12
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50615 | WERE | 'CITY OF IOLA 69KV' | 19.902 | 0.00303 | -0.50918 | 12
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50615 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00236 | -0.50379 | 12
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50615 | WERE | 'CLR_3 .575 34KV' | 100 | 0.00228 | -0.50843 | 12
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50615 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.61 | 0.00468 | -0.51083 | 12
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50615 | WERE | 'LANG 7 345 345KV' | 380 | 0.01517 | -0.52132 | 12
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50615 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 154.9715 | 0.01814 | -0.52429 | 12
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50615 | WERE | 'WACO 138KV' | 17.414 | -0.00427 | -0.50188 | 12
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.4008 | WERE | 'CLAY CENTER JUNCTION 115KV' | 6.7 | 0.08529 | -0.48609 | 12
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40041 | WERE | 'CLAY CENTER JUNCTION 115KV' | 6.7 | 0.08529 | -0.4857 | 12
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50615 | WERE | 'COLBY 115KV' | 6.4335 | -0.07459 | -0.43156 | 14
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.4008 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 490 | 0.02826 | -0.42906 | 14
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.4008 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 974.2261 | 0.02949 | -0.43029 | 14
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.4008 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 154.9715 | 0.01814 | -0.41894 | 14
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.4008 | WERE | 'SMOKEY HILLS 34KV' | 51 | 0.02972 | -0.43052 | 14
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40041 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 490 | 0.02826 | -0.42867 | 14
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40041 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 974.2261 | 0.02949 | -0.4299 | 14
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40041 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 154.9715 | 0.01814 | -0.41855 | 14
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40041 | WERE | 'SMOKEY HILLS 34KV' | 51 | 0.02972 | -0.43013 | 14
WERE | 'BPU - CITY OF MCPHERSON 115KV' | 259 | -0.50615 | WERE | 'KNOLL 3 115 115KV' | 39.9 | -0.09249 | -0.41366 | 15
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.4008 | WERE | 'CHANUTE 69KV' | 34.903 | 0.00262 | -0.40342 | 15
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.4008 | WERE | 'CITY OF AUGUSTA 69KV' | 15.285 | 0.00121 | -0.40201 | 15
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.4008 | WERE | 'CITY OF IOLA 69KV' | 19.902 | 0.00303 | -0.40383 | 15
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.4008 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00236 | -0.39844 | 15
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.4008 | WERE | 'CLR_3 .575 34KV' | 100 | 0.00228 | -0.40308 | 15
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.4008 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.61 | 0.00468 | -0.40548 | 15
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.4008 | WERE | 'LANG 7 345 345KV' | 380 | 0.01517 | -0.41597 | 15
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.4008 | WERE | 'WACO 138KV' | 17.414 | -0.00427 | -0.39653 | 15
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40041 | WERE | 'CHANUTE 69KV' | 34.903 | 0.00262 | -0.40303 | 15
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40041 | WERE | 'CITY OF AUGUSTA 69KV' | 15.285 | 0.00121 | -0.40162 | 15
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40041 | WERE | 'CITY OF IOLA 69KV' | 19.902 | 0.00303 | -0.40344 | 15
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40041 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00236 | -0.39805 | 15
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40041 | WERE | 'CLR_3 .575 34KV' | 100 | 0.00228 | -0.40269 | 15
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40041 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.61 | 0.00468 | -0.40509 | 15
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40041 | WERE | 'LANG 7 345 345KV' | 380 | 0.01517 | -0.41558 | 15
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40041 | WERE | 'WACO 138KV' | 17.414 | -0.00427 | -0.39614 | 15
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.4008 | WERE | 'COLBY 115KV' | 6.4335 | -0.07459 | -0.32621 | 19
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40041 | WERE | 'COLBY 115KV' | 6.4335 | -0.07459 | -0.32582 | 19
WERE | 'HUTCHINSON ENERGY CENTER 115KV' | 423 | -0.4008 | WERE | 'KNOLL 3 115 115KV' | 39.9 | -0.09249 | -0.30831 | 20
WERE | 'HUTCHINSON ENERGY CENTER 69KV' | 67 | -0.40041 | WERE | 'KNOLL 3 115 115KV' | 39.9 | -0.09249 | -0.30792 | 20
WERE | 'PAWNEE 115KV' | 999 | -0.21559 | WERE | 'CLAY CENTER JUNCTION 115KV' | 6.7 | 0.08529 | -0.30088 | 20
WERE | 'RICE 115KV' | 999 | -0.21559 | WERE | 'CLAY CENTER JUNCTION 115KV' | 6.7 | 0.08529 | -0.30088 | 20
WERE | 'ST JOHN 115KV' | 7.5 | -0.21559 | WERE | 'CLAY CENTER JUNCTION 115KV' | 6.7 | 0.08529 | -0.30088 | 20
WERE | 'PAWNEE 115KV' | 999 | -0.21559 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 490 | 0.02826 | -0.24385 | 25
WERE | 'PAWNEE 115KV' | 999 | -0.21559 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 974.2261 | 0.02949 | -0.24508 | 25
WERE | 'PAWNEE 115KV' | 999 | -0.21559 | WERE | 'SMOKEY HILLS 34KV' | 51 | 0.02972 | -0.24531 | 25
WERE | 'RICE 115KV' | 999 | -0.21559 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 490 | 0.02826 | -0.24385 | 25
WERE | 'RICE 115KV' | 999 | -0.21559 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 974.2261 | 0.02949 | -0.24508 | 25
WERE | 'RICE 115KV' | 999 | -0.21559 | WERE | 'SMOKEY HILLS 34KV' | 51 | 0.02972 | -0.24531 | 25
WERE | 'PAWNEE 115KV' | 999 | -0.21559 | WERE | 'LANG 7 345 345KV' | 380 | 0.01517 | -0.23076 | 26
WERE | 'PAWNEE 115KV' | 999 | -0.21559 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 154.9715 | 0.01814 | -0.23373 | 26
WERE | 'RICE 115KV' | 999 | -0.21559 | WERE | 'LANG 7 345 345KV' | 380 | 0.01517 | -0.23076 | 26
WERE | 'RICE 115KV' | 999 | -0.21559 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 154.9715 | 0.01814 | -0.23373 | 26
WERE | 'PAWNEE 115KV' | 999 | -0.21559 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.61 | 0.00468 | -0.22027 | 27
WERE | 'RICE 115KV' | 999 | -0.21559 | WERE | 'COFFEY COUNTY NO. 2 SHARPE 69KV' | 19.61 | 0.00468 | -0.22027 | 27
WERE | 'PAWNEE 115KV' | 999 | -0.21559 | WERE | 'CHANUTE 69KV' | 34.903 | 0.00262 | -0.21821 | 28
WERE | 'PAWNEE 115KV' | 999 | -0.21559 | WERE | 'CITY OF AUGUSTA 69KV' | 15.285 | 0.00121 | -0.2168 | 28
WERE | 'PAWNEE 115KV' | 999 | -0.21559 | WERE | 'CITY OF IOLA 69KV' | 19.902 | 0.00303 | -0.21862 | 28
WERE | 'PAWNEE 115KV' | 999 | -0.21559 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00236 | -0.21323 | 28
WERE | 'PAWNEE 115KV' | 999 | -0.21559 | WERE | 'CLR_3 .575 34KV' | 100 | 0.00228 | -0.21787 | 28
WERE | 'RICE 115KV' | 999 | -0.21559 | WERE | 'CHANUTE 69KV' | 34.903 | 0.00262 | -0.21821 | 28
WERE | 'RICE 115KV' | 999 | -0.21559 | WERE | 'CITY OF AUGUSTA 69KV' | 15.285 | 0.00121 | -0.2168 | 28
WERE | 'RICE 115KV' | 999 | -0.21559 | WERE | 'CITY OF IOLA 69KV' | 19.902 | 0.00303 | -0.21862 | 28
WERE | 'RICE 115KV' | 999 | -0.21559 | WERE | 'CITY OF WELLINGTON 69KV' | 20 | -0.00236 | -0.21323 | 28
WERE | 'RICE 115KV' | 999 | -0.21559 | WERE | 'CLR_3 .575 34KV' | 100 | 0.00228 | -0.21787 | 28
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.17956 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 490 | 0.02826 | -0.20782 | 29
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.17956 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 974.2261 | 0.02949 | -0.20905 | 29
WERE | 'GREAT BEND PLANT 69KV' | 10 | -0.17956 | WERE | 'SMOKEY HILLS 34KV' | 51 | 0.02972 | -0.20928 | 29
WERE | 'PAWNEE 115KV' | 999 | -0.21559 | WERE | 'WACO 138KV' | 17.414 | -0.00427 | -0.21132 | 29
WERE | 'RICE 115KV' | 999 | -0.21559 | WERE | 'WACO 138KV' | 17.414 | -0.00427 | -0.21132 | 29
WERE | 'KNOLL 3 115 115KV' | 44.46 | -0.09249 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 974.2261 | 0.02949 | -0.12198 | 49
WERE | 'KNOLL 3 115 115KV' | 44.46 | -0.09249 | WERE | 'SMOKEY HILLS 34KV' | 51 | 0.02972 | -0.12221 | 49
WERE | 'PAWNEE 115KV' | 999 | -0.21559 | WERE | 'KNOLL 3 115 115KV' | 39.9 | -0.09249 | -0.1231 | 49
WERE | 'RICE 115KV' | 999 | -0.21559 | WERE | 'KNOLL 3 115 115KV' | 39.9 | -0.09249 | -0.1231 | 49
WERE | 'KNOLL 3 115 115KV' | 44.46 | -0.09249 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 490 | 0.02826 | -0.12075 | 50
WERE | 'KNOLL 3 115 115KV' | 44.46 | -0.09249 | WERE | 'LAWRENCE ENERGY CENTER 230KV' | 154.9715 | 0.01814 | -0.11063 | 55
WERE | 'KNOLL 3 115 115KV' | 44.46 | -0.09249 | WERE | 'LANG 7 345 345KV' | 380 | 0.01517 | -0.10766 | 56
WERE | 'KNOLL 3 115 115KV' | 44.46 | -0.09249 | WERE | 'CHANUTE 69KV' | 34.903 | 0.00262 | -0.09511 | 63
WERE | 'KNOLL 3 115 115KV' | 44.46 | -0.09249 | WERE | 'CLR_3 .575 34KV' | 100 | 0.00228 | -0.09477 | 64
WEPL | 'A. M. MULLERGREN GENERATOR 115KV' | 63 | -0.17709 | WEPL | 'GRAY COUNTY WIND FARM 115KV' | 60 | -0.11605 | -0.06104 | 99
WERE | 'GILL ENERGY CENTER 138KV' | 218 | -0.00481 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 974.2261 | 0.02949 | -0.0343 | 176
WERE | 'GILL ENERGY CENTER 138KV' | 218 | -0.00481 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 490 | 0.02826 | -0.03307 | 183
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.00344 | WERE | 'JEFFREY ENERGY CENTER 345KV' | 974.2261 | 0.02949 | -0.03293 | 183
WERE | 'GILL ENERGY CENTER 69KV' | 118 | -0.00344 | WERE | 'JEFFREY ENERGY CENTER 230KV' | 490 | 0.02826 | -0.0317 | 190
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor