## Table1
Customer | Study Number | Reservation |  | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date | Deferred Stop Date | Mimimum Allocated ATC (MW) within reservation period | Season of Minimum Allocated ATC within reservation period
AEPM | AG1-2006-006D | 1019914 |  | CSWS | CSWS | 168 | 2008-07-01 | 2013-07-01 |  |  | 0 | 07FA
AEPM | AG1-2006-007D | 1023236 | 1 | WFEC | CSWS | 80 | 2007-01-01 | 2027-01-01 |  |  | 0 | 07SP
EDE | AG1-2006-027 | 1032183 |  | EES | EDE | 50 | 2010-06-01 | 2040-06-01 |  |  | 0 | 11SP
INDP | AG1-2006-051 | 1033791 |  | KCPL | INDN | 50 | 2010-06-01 | 2040-06-01 |  |  | 0 | 11SP
KCPS | AG1-2006-009 | 979750 |  | KCPL | KCPL | 168 | 2009-06-01 | 2029-06-01 |  |  | 0 | 11SP
KCPS | AG1-2006-070 | 1034307 | 1 | KCPL | EES | 103 | 2006-06-01 | 2007-06-01 |  |  | 0 | 06SP
KMEA | AG1-2006-068 | 1034247 |  | GRDA | WR | 1 | 2010-05-01 | 2026-05-01 |  |  | 0 | 06SP
KPP | AG1-2006-042 | 1032991 |  | WPEK | WPEK | 80 | 2006-06-01 | 2016-06-01 |  |  | 0 | 07FA
OGE | AG1-2006-040 | 1032973 | 1 | OKGE | OKGE | 120 | 2006-09-01 | 2031-09-01 |  |  | 0 | 07SP
OMPA | AG1-2006-010 | 977481 | 1 | GRDA | OKGE | 25 | 2007-05-01 | 2040-05-01 |  |  | 0 | 07SP
WRGS | AG1-2006-029D | 1031553 | 1 | KCPL | AECI | 15 | 2006-06-01 | 2007-06-01 |  |  | 0 | 06SH
WRGS | AG1-2006-037D | 1032955 | 1 | AECI | KCPL | 15 | 2006-06-01 | 2007-06-01 |  |  | 0 | 06SP
1Start and Stop Dates are determined based on customers choosing option to pursue redispatch to start service at Requested Start and Stop Dates or earliest date possible.

## Table2
Customer | Study Number | Reservation | Engineering and Construction Cost of Upgrades Allocated to Customer for Revenue Requirements | 4 Letter of Credit Amount Required | 3 Potential Base Plan Engineering and Construction Funding Allowable |  | 5 Total Revenue Requirements for Assigned Upgrades over term of reservation WITHOUT potential base plan funding allocation in consideration of redispatch if applicable | Total Revenue Requirements for Assigned Upgrades over term of reservation WITH potential base plan funding allocation in consideration of redispatch if applicable | Point-to-Point Base Rate over reservation period | 2Total Cost of Reservation Assignable to Customer contingent upon base plan funding
AEPM | AG1-2006-006D | 1019914 | 2685128 | 2000000 | 2685128 |  | 3726550.3667 | 0 | 0 | Schedule 9 charges
AEPM | AG1-2006-007D | 1023236 | 4192590 | 3877718 | 1440000 |  | 10987300.3701 | 7213568.0182 | 0 | 7213568.0182
EDE | AG1-2006-027 | 1032183 | 0 |  | 0 |  | 0 | 0 | 0 | Schedule 9 charges
INDP | AG1-2006-051 | 1033791 | 1477174 | 1477174 | 0 |  | 5988578.4422 | 5988578.4422 | 15840000 | 15840000
KCPS | AG1-2006-009 | 979750 | 6022826 | 5322826 | 6022826 |  | 17130387.8829 | 0 | 0 | Schedule 9 charges
KCPS | AG1-2006-070 | 1034307 | 0 | 0 | 0 |  | 0 | 0 | 1050600 | 1050600
KMEA | AG1-2006-068 | 1034247 | 0 | 0 | 0 |  | 0 | 0 | 249600 | 249600
KPP | AG1-2006-042 | 1032991 | 1518000 | 1518000 | 1518000 | 1 | 2749001.8657 | 0 | 0 | Schedule 9 charges
OGE | AG1-2006-040 | 1032973 | 4142282 | 2871270 | 1440000 |  | 13458257.2284 | 8779703.1235 | 0 | 8779703.1235
OMPA | AG1-2006-010 | 977481 | 0 | 0 | 0 |  | 0 | 0 | 0 | Schedule 9 charges
WRGS | AG1-2006-029D | 1031553 | 0 |  | 0 |  | 0 | 0 | 153000 | 153000
WRGS | AG1-2006-037D | 1032955 | 0 | 0 | 0 |  | 0 | 0 | 158400 | 158400
|  |  | 20038000 |  | 13105954 |  | 54040076.156 | 21981849.5839
Note 1: 92MW potential base plan funding for year 2008 for KPP WPEK requests.
Note 2. For PTP requests, total cost is based on the higher of the base rate or assigned upgrade revenue requirements. For Network requests, the total cost is based on the assigned upgrade revenue requirement. Allocation of base plan funding will be determined after verification of designated resource meeting Attachment J, Section II B Criteria. Additionally E & C of 3rd Party upgrades is assignable to Customer. Revenue requirements for 3rd Party facilities are not calculated. Total cost to customer is based on assumption of Revenue Requirements with confirmation of base plan funding. Customer is responsible for negotiating redispatch costs if applicable. Customer is also responsible to pay credits for previously assigned upgrades that are impacted by their request. Credits required will be determined at a later date.
Note 3. If potential base plan funding is applicable, this value is the lesser of the Engineering and Construction costs of assignable upgrades or the value of base plan funding calculated pursuant to Attachment J, Section III B criteria. Allocation of base plan funding is contingent upon verification of customer agreements meeting Attachment J, Section II B criteria. Not applicable if PTP base rate exceeds revenue requirements.
Note 4: Letter of Credit required for financial security for transmission owner for network upgrades is determined by allocated engineering and construction costs less engineering and construction costs for upgrades when network customer is the transmission owner plus network upgrades for assigned upgrades less that $100,000 which are base plan funded but still require a letter of credit.
Note 5: Revenue Requirements are based upon customer's prior selection of intention to pursue redispatch if applicable.

## Table3
Customer | Study Number
AEPM | AG1-2006-006D
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AEPM | 1019914 | CSWS | CSWS | 168 | 2008-07-01 | 2013-07-01 | 2008-07-01 | 2013-07-01 | 2685128 | 0 | 2695388 | 0
[9 empty] | 2685128 | 0 | 2695388 | 3726550.37
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1019914 | ALUMAX TAP - BANN 138KV CKT 1 | 2008-06-01 | 2008-06-01 |  |  | 685128 | 1000000 | 1350112.08
| ANADARKO 138/69KV TRANSFORMER CKT 1 | 2011-06-01 | 2011-06-01 |  |  | 2000000 | 2000000 | 2376438.28
| BANN - NW TEXARKANA-BANN T 138KV CKT 1 | 2012-06-01 | 2012-06-01 |  |  | 10260 | 15000 | 0
[5 empty] | Total | 2695388 | 3015000 | 3726550.36
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1019914 | ALUMAX TAP - NORTHWEST TEXARKANA 138KV CKT 1 | 2007-06-01 | 2008-04-01 | 2007-10-01 | No
| LINWOOD - MCWILLIE STREET 138KV CKT 1 | 2007-06-01 | 2008-04-01 | 2007-10-01 | No
Customer | Study Number
AEPM | AG1-2006-007D
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AEPM | 1023236 | WFEC | CSWS | 80 | 2007-01-01 | 2027-01-01 | 2008-06-01 | 2028-06-01 | 1440000 | 0 | 4212330 | 0
[9 empty] | 1440000 | 0 | 4212330 | 10987300.37
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1023236 | 36TH & LEWIS - 52ND & DELAWARE TAP 138KV CKT 1 | 2016-06-01 | 2016-06-01 |  |  | 15000 | 15000 | 0
| ALUMAX TAP - BANN 138KV CKT 1 | 2008-06-01 | 2008-06-01 |  |  | 314872 | 1000000 | 917374.3
| BANN - NW TEXARKANA-BANN T 138KV CKT 1 | 2012-06-01 | 2012-06-01 |  |  | 4740 | 15000 | 0
| FT SUPPLY 138/69KV TRANSFORMER CKT 1 | 2006-12-01 | 2008-06-01 |  | Yes | 2000000 | 2000000 | 4495992.08
| HAMON BUTLER - MOREWOOD 69KV CKT 1 | 2006-06-01 | 2008-04-01 |  | Yes | 1278730 | 3400000 | 3038092.76
| KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1 | 2006-06-01 | 2008-06-01 |  | Yes | 598988 | 1750000 | 2535841.23
[5 empty] | Total | 4212330 | 8180000 | 10987300.37
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1023236 | ALUMAX TAP - NORTHWEST TEXARKANA 138KV CKT 1 | 2007-06-01 | 2008-04-01 | 2007-10-01 | Yes
| LINWOOD - MCWILLIE STREET 138KV CKT 1 | 2007-06-01 | 2008-04-01 | 2007-10-01 | Yes
Customer | Study Number
EDE | AG1-2006-027
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
EDE | 1032183 | EES | EDE | 50 | 2010-06-01 | 2040-06-01 | 2010-06-01 | 2040-06-01 | 0 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0 | 0
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1032183 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1032183 | BULL SHOALS - BULL SHOALS 161KV CKT 1 | 2010-06-01 | 2010-06-01
| JAMESVILLE - SUB 415 - BLACKHAWK JCT. 69KV CKT 1 | 2013-06-01 | 2013-06-01
| JONES - JONESBORO 161KV CKT 1 | 2009-06-01 | 2009-06-01
| SUB 110 - ORONOGO JCT. (ORONOGO) 161/69/12.5KV TRANSFORMER CKT 1 | 2016-06-01 | 2016-06-01
| SUB 124 - AURORA H.T. - SUB 152 - MONETT H.T. 69KV CKT 1 | 2011-06-01 | 2011-06-01
| SUB 145 - JOPLIN WEST 7TH - SUB 64 - JOPLIN 10TH ST. 69KV CKT 1 | 2014-06-01 | 2014-06-01
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1032183 | SUB 110 - ORONOGO JCT. - SUB 167 - RIVERTON 161KV CKT 1 | 2011-06-01 | 2011-06-01
| SUB 110 - ORONOGO JCT. (ORONOGO) 161/69/12.5KV TRANSFORMER CKT 1 | 2011-06-01 | 2011-06-01
Customer | Study Number
INDP | AG1-2006-051
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
INDP | 1033791 | KCPL | INDN | 50 | 2010-06-01 | 2040-06-01 | 2010-06-01 | 2040-06-01 | 0 | 15840000 | 1477174 | 0
[9 empty] | 0 | 15840000 | 1477174 | 5988578.44
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1033791 | 166TH STREET - JAGGARD JUNCTION 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 213226 | 1000000 | 1105108.88
| 166TH STREET - JARBALO JUNCTION SWITCHING STATION 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 405130 | 1900000 | 577383.55
| JAGGARD JUNCTION - PENTAGON 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 319839 | 1500000 | 1657663.33
| STRANGER CREEK - NW LEAVENWORTH 115KV | 2010-06-01 | 2010-06-01 |  |  | 538979 | 2400000 | 2648422.68
[5 empty] | Total | 1477174 | 6800000 | 5988578.44
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1033791 | IATAN - ST JOE 345KV CKT 1 | 2011-12-01 | 2011-12-01
| IATAN5 161 - PLATTE CITY 161KV CKT 1 | 2011-06-01 | 2011-06-01
Customer | Study Number
KCPS | AG1-2006-009
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
KCPS | 979750 | KCPL | KCPL | 168 | 2009-06-01 | 2029-06-01 | 2009-06-01 | 2029-06-01 | 6022826 | 0 | 6022826 | 0
[9 empty] | 6022826 | 0 | 6022826 | 17130387.88
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
979750 | 166TH STREET - JAGGARD JUNCTION 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 786774 | 1000000 | 2927001.15
| 166TH STREET - JARBALO JUNCTION SWITCHING STATION 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 1494870 | 1900000 | 1529260.8
| COLLEGE - CRAIG 161KV CKT 1 | 2016-06-01 | 2016-06-01 |  |  | 700000 | 700000 | 1719531.39
| JAGGARD JUNCTION - PENTAGON 115KV CKT 1 | 2009-06-01 | 2009-06-01 |  |  | 1180161 | 1500000 | 4390501.74
| STRANGER CREEK - NW LEAVENWORTH 115KV | 2010-06-01 | 2010-06-01 |  |  | 1861021 | 2400000 | 6564092.8
[5 empty] | Total | 6022826 | 7500000 | 17130387.88
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
979750 | AVONDALE - GLADSTONE 161KV CKT 1 | 2014-06-01 | 2014-06-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
979750 | IATAN - ST JOE 345KV CKT 1 | 2011-12-01 | 2011-12-01
979750 | IATAN5 161 - PLATTE CITY 161KV CKT 1 | 2011-06-01 | 2011-06-01
Customer | Study Number
KCPS | AG1-2006-070
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
KCPS | 1034307 | KCPL | EES | 103 | 2006-06-01 | 2007-06-01 | 2008-04-01 | 2009-04-01 | 0 | 1050600 | 0 | 0
[9 empty] | 0 | 1050600 | 0 | 0
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1034307 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1034307 | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | 2006-06-01 | 2008-04-01 | 2007-10-01 | Yes
Customer | Study Number
KMEA | AG1-2006-068
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
KMEA | 1034247 | GRDA | WR | 1 | 2010-05-01 | 2026-05-01 | 2010-05-01 | 2026-05-01 | 0 | 249600 | 0 | 0
[9 empty] | 0 | 249600 | 0 | 0
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1034247 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1034247 | CIRCLEVILLE - HOYT HTI SWITCHING JUNCTION 115KV CKT 1 | 2006-10-01 | 2009-06-01 03:00 |  | No
| CIRCLEVILLE - KING HILL N.M. COOP 115KV CKT 1 | 2006-10-01 | 2009-04-01 |  | No
| COFFEYVILLE TAP - DEARING 138KV CKT 1 AEPW | 2016-06-01 | 2016-06-01
| COFFEYVILLE TAP - DEARING 138KV CKT 1 WERE | 2016-06-01 | 2016-06-01
| GRAY TAP - PENSACOLA 69KV CKT 1 | 2006-06-01 | 2008-12-01 | 2008-10-01 | No
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1034247 | 412SUB - KANSAS TAP 161KV CKT 1 | 2015-06-01 | 2015-06-01
| 412SUB - KERR 161KV CKT 1 | 2015-06-01 | 2015-06-01
| ARCADIA - REDBUD 345 KV CKT 1 | 2006-06-01 | 2006-06-01
| ARCADIA - REDBUD 345 KV CKT 2 | 2006-06-01 | 2006-06-01
| SUB 110 - ORONOGO JCT. - SUB 167 - RIVERTON 161KV CKT 1 | 2011-06-01 | 2011-06-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1034247 | AEPW PLANNED UPGRADE FOR NW ARKANSAS | 2006-06-01 | 2009-06-01 |  | No
Customer | Study Number
KPP | AG1-2006-042
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
KPP | 1032991 | WPEK | WPEK | 80 | 2006-06-01 | 2016-06-01 |  |  | 1518000 | 0 | 1518000 | 0
[9 empty] | 1518000 | 0 | 1518000 | 2749001.87
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1032991 | Greenleaf 34.5 kV System Improvements | 2008-06-01 | 2008-06-01 |  |  | 797000 | 797000 | 1403696.48
| Greensburg 34.5 kV System Improvements | 2007-10-01 | 2007-10-01 |  |  | 721000 | 721000 | 1345305.38
[5 empty] | Total | 1518000 | 1518000 | 2749001.86
Customer | Study Number
OGE | AG1-2006-040
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
OGE | 1032973 | OKGE | OKGE | 120 | 2006-09-01 | 2031-09-01 | 2008-12-01 | 2033-12-01 | 1440000 | 0 | 4142282 | 0
[9 empty] | 1440000 | 0 | 4142282 | 13458257.23
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1032973 | FPL SWITCH - MOORELAND 138KV CKT 1 OKGE | 2006-06-01 | 2008-04-01 |  | Yes | 120000 | 120000 | 575561.85
| FPL SWITCH - MOORELAND 138KV CKT 1 WFEC | 2006-06-01 | 2008-04-01 |  | Yes | 750000 | 750000 | 1923027.19
| HAMON BUTLER - MOREWOOD 69KV CKT 1 | 2006-06-01 | 2008-04-01 |  | Yes | 2121270 | 3400000 | 5439013.22
| KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1 | 2006-06-01 | 2008-06-01 |  | Yes | 1151012 | 1750000 | 5520654.96
[5 empty] | Total | 4142282 | 6020000 | 13458257.22
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1032973 | COLONY - FT SMITH 161KV CKT 1 | 2011-06-01 | 2011-06-01
| PENNSYLVANIA - WESTMOORE 138KV CKT 1 | 2007-10-01 | 2009-04-01 | 2008-12-01 | Yes
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1032973 | IODINE - WOODWARD 138kV CKT 1 | 2006-06-01 | 2006-12-01 |  | Yes
Customer | Study Number
OMPA | AG1-2006-010
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
OMPA | 977481 | GRDA | OKGE | 25 | 2007-05-01 | 2040-05-01 | 2008-12-01 | 2041-12-01 | 0 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0 | 0
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
977481 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
977481 | GRAY TAP - PENSACOLA 69KV CKT 1 | 2006-06-01 | 2008-12-01 | 2008-10-01 | Yes
| GRAY TAP - PENSACOLA 69KV CKT 1 | 2006-06-01 | 2008-12-01 | 2008-10-01 | Yes
| PENNSYLVANIA - WESTMOORE 138KV CKT 1 | 2007-10-01 | 2009-04-01 | 2008-12-01 | Yes
| ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 | 2013-06-01 | 2013-06-01
| WAUKOMIS TAP - WOODRING 138KV CKT 1 | 2011-06-01 | 2011-06-01
Credits may be required for the following network upgrades directly assigned to transmission customers in previous aggregate study.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
977481 | 412SUB - KANSAS TAP 161KV CKT 1 | 2015-06-01 | 2015-06-01
| 412SUB - KERR 161KV CKT 1 | 2015-06-01 | 2015-06-01
| ARCADIA - REDBUD 345 KV CKT 1 | 2006-06-01 | 2006-06-01
| ARCADIA - REDBUD 345 KV CKT 2 | 2006-06-01 | 2006-06-01
| SUB 110 - ORONOGO JCT. - SUB 167 - RIVERTON 161KV CKT 1 | 2011-06-01 | 2011-06-01
Customer | Study Number
WRGS | AG1-2006-029D
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
WRGS | 1031553 | KCPL | AECI | 15 | 2006-06-01 | 2007-06-01 | 2006-10-01 | 2007-10-01 | 0 | 153000 | 0 | 0
[9 empty] | 0 | 153000 | 0 | 0
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1031553 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1031553 | SOUTH WAVERLY 161/69KV TRANSFORMER CKT 1 Redispatch | 2006-06-01 | 2006-10-01 |  | Yes
Customer | Study Number
WRGS | AG1-2006-037D
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
WRGS | 1032955 | AECI | KCPL | 15 | 2006-06-01 | 2007-06-01 | 2008-04-01 | 2009-04-01 | 0 | 158400 | 0 | 0
[9 empty] | 0 | 158400 | 0 | 0
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
1032955 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | COD | EOC | Earliest Service Start Date | Redispatch Available
1032955 | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | 2006-06-01 | 2008-04-01 | 2007-10-01 | Yes

## Table4
Transmission Owner | Upgrade | Solution | Minimum ATC per Upgrade (MW) | Season of Minimum Allocated ATC | Earliest Data Upgrade Required (COD) | Estimated Date of Upgrade Completion (EOC) | Estimated Engineering & Construction Cost
AEPW | 36TH & LEWIS - 52ND & DELAWARE TAP 138KV CKT 1 | Reset Relays @ 36th & Lewis | 182.8302 | 16SP | 2016-06-01 | 2016-06-01 | 15000
AEPW | ALUMAX TAP - BANN 138KV CKT 1 | Replace six (6) 138 kV switches, five at Bann & one at Alumax Tap. Rebuild 0.67 miles of 1024 ACAR with 2156 ACSR. Replace wavetrap & jumpers @ Bann. Replace breaker 3300 @ Bann. | 0 | 11SP | 2008-06-01 | 2008-06-01 | 1000000
AEPW | BANN - NW TEXARKANA-BANN T 138KV CKT 1 | Reset Relays | 0 | 16SP | 2012-06-01 | 2012-06-01 | 15000
KACP | COLLEGE - CRAIG 161KV CKT 1 | Reconductor 4 miles with 1192.5 ACSS, 558 normal/emergency rating and upgrade breaker. | 143.0591 | 16SP | 2016-06-01 | 2016-06-01 | 700000
OKGE | FPL SWITCH - MOORELAND 138KV CKT 1 OKGE | OGE would rebuild .18 miles of 267AS33 with 795AS33. This would raise OGE's summer and winter Rate B to 287MVA. The limit will still be at WFEC's Mooreland at 390A & 600A. | 53.8909 | 06FA | 2006-06-01 | 2008-04-01 | 120000
OKGE | KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1 | Replace bus tie with 100MVA transformer | 86.7104 | 08SP | 2006-06-01 | 2008-06-01 | 1750000
WEPL | Greenleaf 34.5 kV System Improvements | Build a new 5.1 mile 34.5 kV line from Greenleaf to the City of Washington | 0 | 08SP | 2008-06-01 | 2008-06-01 | 797000
WEPL | Greensburg 34.5 kV System Improvements | Build a new 4.5 miles 34.5 kV line From Greensburg 115/34.5 kV Sub to the City of Greensburg | 0 | 07FA | 2007-10-01 | 2007-10-01 | 721000
WERE | 166TH STREET - JAGGARD JUNCTION 115KV CKT 1 | Tear down and rebuild 3.66 mile 166-Jaggard 115 kV line. | 0 | 11SP | 2009-06-01 | 2009-06-01 | 1000000
WERE | 166TH STREET - JARBALO JUNCTION SWITCHING STATION 115KV CKT 1 | Tear down and rebuild 7.22 mile Jarbalo-166 115 kV line. | 0 | 11SP | 2009-06-01 | 2009-06-01 | 1900000
WERE | JAGGARD JUNCTION - PENTAGON 115KV CKT 1 | Tear down and rebuild Jaggard - Pentagon 115 kV line. | 0 | 11SP | 2009-06-01 | 2009-06-01 | 1500000
WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Teardown/rebuild Jarbalo-NW Leavenworth 115 kV line with double circuit tap to Stranger Creek | 0 | 11SP | 2010-06-01 | 2010-06-01 | 2400000
WFEC | ANADARKO 138/69KV TRANSFORMER CKT 1 | Install 2nd 112 MVA auto in parallel with existing Unit | 48.7042 | 16SP | 2011-06-01 | 2011-06-01 | 2000000
WFEC | FPL SWITCH - MOORELAND 138KV CKT 1 WFEC | Upgrade terminal equipment FPL Sw & Mooreland | 53.8909 | 06FA | 2006-06-01 | 2008-04-01 | 750000
WFEC | FT SUPPLY 138/69KV TRANSFORMER CKT 1 | Install 2nd 70 MVA auto at Ft Supply | 66.8275 | 07FA | 2006-12-01 | 2008-06-01 | 2000000
WFEC | HAMON BUTLER - MOREWOOD 69KV CKT 1 | Reconductor 1/0 to 336 ACSR - 15.0 miles | 0 | 16SP | 2006-06-01 | 2008-04-01 | 3400000
Construction Pending Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
AEPW | AEPW PLANNED UPGRADE FOR NW ARKANSAS | NW Project phase II scheduled to be in-service 06/2009 | 0 | 06SP | 2006-06-01 | 2009-06-01
MIPU | IATAN - ST JOE 345KV CKT 1 | Circuit Breaker | 164.9918 | 11WP | 2011-12-01 | 2011-12-01
MIPU | IATAN5 161 - PLATTE CITY 161KV CKT 1 | Terminal Equipment | 0 | 11WP | 2011-06-01 | 2011-06-01
OKGE | IODINE - WOODWARD 138kV CKT 1 | New line will be in service by 12/1/2006 | 36.6844 | 06SH | 2006-06-01 | 2006-12-01
Expansion Plan Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
AEPW | ALUMAX TAP - NORTHWEST TEXARKANA 138KV CKT 1 | Rebuild 1.68 miles of 1024 ACAR with 2156 ACSR, Replace wavetrap & jumpers with 2156 ACSR. Replace Switch 2285 @ Alumax Tap. | 0 | 08SP | 2007-06-01 | 2008-04-01
AEPW | COFFEYVILLE TAP - DEARING 138KV CKT 1 AEPW | Tie Line, Reconductor 1.09 miles of 795 ACSR with 1590 ACSR. | 0 | 16SP | 2016-06-01 | 2016-06-01
AEPW | LINWOOD - MCWILLIE STREET 138KV CKT 1 | Rebuild 2.09 miles of 666 ACSR with 1272 ACSR | 0 | 07SP | 2007-06-01 | 2008-04-01
EMDE | JAMESVILLE - SUB 415 - BLACKHAWK JCT. 69KV CKT 1 | Replace Jumpers to breaker #6950 at Blackhawk Jct. | 0 | 16SP | 2013-06-01 | 2013-06-01
EMDE | SUB 110 - ORONOGO JCT. (ORONOGO) 161/69/12.5KV TRANSFORMER CKT 1 | Replace 75 MVA Auto-xfmr at Oronogo Jct with 150 MVA Auto-xfmr and install 69 kV bank breaker. Auto-xfmr will have an impedance similar to Aurora 59468, 59537, 59704. | 0 | 16SP | 2016-06-01 | 2016-06-01
EMDE | SUB 124 - AURORA H.T. - SUB 152 - MONETT H.T. 69KV CKT 1 | Change CT Ratio on breaker #6936 at Aurora #124 | 0 | 11SP | 2011-06-01 | 2011-06-01
EMDE | SUB 145 - JOPLIN WEST 7TH - SUB 64 - JOPLIN 10TH ST. 69KV CKT 1 | Replace 600 amp disconnects and leads to breaker #6965 at Joplin #64 | 0 | 16SP | 2014-06-01 | 2014-06-01
GRDA | GRAY TAP - PENSACOLA 69KV CKT 1 | Rebuild of Pensacola - Jayline (not owned by GRDA -- have tried to convince owner) | 0 | 06SP | 2006-06-01 | 2008-12-01
KACP | AVONDALE - GLADSTONE 161KV CKT 1 | Replace 800 amp wavetrap at Gladstone with 1200 amp wavetrap | 0 | 16SP | 2014-06-01 | 2014-06-01
KACP | SOUTH WAVERLY 161/69KV TRANSFORMER CKT 1 Redispatch | Redispatch for the 06 Summer Shoulder | 0 | 06SH | 2006-06-01 | 2006-10-01
MIPU | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | Conductor | 0 | 06SP | 2006-06-01 | 2008-04-01
OKGE | COLONY - FT SMITH 161KV CKT 1 | Reconductor 2.2 miles to Drake ACCC/TW and change terminal equipment at Ft. Smith & Colony to 2000A. | 0 | 11SP | 2011-06-01 | 2011-06-01
OKGE | PENNSYLVANIA - WESTMOORE 138KV CKT 1 | Replace the disconnect switches for breaker 108 at Pennsylvania Substation. Replace the 1200A trap. Increase CTR. Relay replacement may be required. | 0 | 07FA | 2007-10-01 | 2009-04-01
OKGE | WAUKOMIS TAP - WOODRING 138KV CKT 1 | Reconductor 2.75 miles of line with Drake ACCC conductor and increase CTR. | 0 | 11SP | 2011-06-01 | 2011-06-01
SWPA | BULL SHOALS - BULL SHOALS 161KV CKT 1 | Replace bus at Bull Shoals. | 0 | 16SP | 2010-06-01 | 2010-06-01
SWPA | JONES - JONESBORO 161KV CKT 1 | Change the ratio on the metering CTs to 1200/5 and adjust the meters | 0 | 11SP | 2009-06-01 | 2009-06-01
WERE | CIRCLEVILLE - HOYT HTI SWITCHING JUNCTION 115KV CKT 1 | Rebuild 16.66 mile Circleville-Hoyt HTI Junction 115 kV line. | 0 | 07FA | 2006-10-01 | 2009-06-01 03:00
WERE | CIRCLEVILLE - KING HILL N.M. COOP 115KV CKT 1 | Rebuild 15.15 mile line with 1192.5 kcmil ACSR and replace CTs | 0 | 08WP | 2006-10-01 | 2009-04-01 06:00
WERE | COFFEYVILLE TAP - DEARING 138KV CKT 1 WERE | Tie Line, Rebuild 5.02-mile 138kV line from Dearing to S Coffeyville Tap and replace Dearing 138kV main bus and connections. | 0 | 16SP | 2016-06-01 | 2016-06-01
WERE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 | Add third 345-138 kV transformer at Rose Hill | 0 | 16SP | 2013-06-01 | 2013-06-01
Previously Assigned Aggregate Study Upgrades requiring credits to Previous Aggregate Study Customers
EMDE | SUB 110 - ORONOGO JCT. - SUB 167 - RIVERTON 161KV CKT 1 | Reconductor Oronogo 59467 to Riverton 59469 with Bundled 556 ACSR | N/A | N/A | 2011-06-01 | 2011-06-01
EMDE | SUB 110 - ORONOGO JCT. (ORONOGO) 161/69/12.5KV TRANSFORMER CKT 1 | Installl new 161/12 kV 22.4 transmer and take load off 69 kV system | 0 | 16SP | 2011-06-01 | 2011-06-01
GRRD | 412SUB - KANSAS TAP 161KV CKT 1 | Reconductor 9.7 miles with 1590MCM ACSR. | N/A | N/A | 2015-06-01 | 2015-06-01
GRRD | 412SUB - KERR 161KV CKT 1 | Reconductor 12.5 miles with 1590MCM ACSR | N/A | N/A | 2015-06-01 | 2015-06-01
OKGE | ARCADIA - REDBUD 345 KV CKT 1 | Sponsored Project to Uprate Terninal Equipment | N/A | N/A | 2006-06-01 | 2006-06-01
OKGE | ARCADIA - REDBUD 345 KV CKT 2 | Sponsored Project to Uprate Terninal Equipment | N/A | N/A | 2006-06-01 | 2006-06-01

## Table5
Transmission Owner | Upgrade | Solution | Minimum ATC per Upgrade (MW) | Season of Minimum Allocated ATC | Earliest Date Upgrade Required (COD) | Estimated Date of Upgrade Completion (EOC) | Estimated Engineering & Construction Cost
None

## Table6
Upgrade: | ALUMAX TAP - NORTHWEST TEXARKANA 138KV CKT 1
Limiting Facility: | ALUMAX TAP - NORTHWEST TEXARKANA 138KV CKT 1
Direction: | To->From
Line Outage: | SPP-AEPW-29
Flowgate: | 53245533001SPP-AEPW-291107SP
Date Redispatch Needed: | 6/1/07 - 10/1/07
Season Flowgate Identified: | 2007 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1023236 | 2.9136 | 2.9136
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
AEPW | 'LONESTAR POWER PLANT 69KV' | 50 | -0.08758 | AEPW | 'COMANCHE 138KV' | 160 | 0.01244 | -0.10002 | 29
AEPW | 'LONESTAR POWER PLANT 69KV' | 50 | -0.08758 | AEPW | 'COMANCHE 69KV' | 63 | 0.01239 | -0.09997 | 29
AEPW | 'LONESTAR POWER PLANT 69KV' | 50 | -0.08758 | AEPW | 'SOUTHWESTERN STATION 138KV' | 327 | 0.01212 | -0.0997 | 29
AEPW | 'LONESTAR POWER PLANT 69KV' | 50 | -0.08758 | AEPW | 'WELSH 345KV' | 990 | 0.01228 | -0.09986 | 29
AEPW | 'LONESTAR POWER PLANT 69KV' | 50 | -0.08758 | AEPW | 'COGENTRIX 345KV' | 665 | 0.00882 | -0.0964 | 30
AEPW | 'LONESTAR POWER PLANT 69KV' | 50 | -0.08758 | AEPW | 'NORTHEASTERN STATION 138KV' | 405 | 0.00807 | -0.09565 | 30
AEPW | 'LONESTAR POWER PLANT 69KV' | 50 | -0.08758 | AEPW | 'NORTHEASTERN STATION 138KV' | 95 | 0.00807 | -0.09565 | 30
AEPW | 'LONESTAR POWER PLANT 69KV' | 50 | -0.08758 | AEPW | 'NORTHEASTERN STATION 345KV' | 645 | 0.00807 | -0.09565 | 30
AEPW | 'LONESTAR POWER PLANT 69KV' | 50 | -0.08758 | AEPW | 'RIVERSIDE STATION 138KV' | 646 | 0.00877 | -0.09635 | 30
AEPW | 'LONESTAR POWER PLANT 69KV' | 50 | -0.08758 | AEPW | 'TULSA POWER STATION 138KV' | 93 | 0.0087 | -0.09628 | 30
AEPW | 'LONESTAR POWER PLANT 69KV' | 50 | -0.08758 | AEPW | 'TULSA POWER STATION 138KV' | 147 | 0.0087 | -0.09628 | 30
AEPW | 'LONESTAR POWER PLANT 69KV' | 50 | -0.08758 | AEPW | 'WELEETKA 138KV' | 70 | 0.00961 | -0.09719 | 30
AEPW | 'LONESTAR POWER PLANT 69KV' | 50 | -0.08758 | AEPW | 'FITZHUGH 161KV' | 126 | 0.00382 | -0.0914 | 32
AEPW | 'LONESTAR POWER PLANT 69KV' | 50 | -0.08758 | AEPW | 'LEBROCK 345KV' | 365 | -0.00885 | -0.07873 | 37
AEPW | 'LONESTAR POWER PLANT 69KV' | 50 | -0.08758 | AEPW | 'NARROWS 69KV' | 22 | -0.00834 | -0.07924 | 37
AEPW | 'LONESTAR POWER PLANT 69KV' | 50 | -0.08758 | AEPW | 'PIRKEY GENERATION 138KV' | 248 | -0.01312 | -0.07446 | 39
AEPW | 'LONESTAR POWER PLANT 69KV' | 50 | -0.08758 | AEPW | 'EASTMAN 138KV' | 355 | -0.01562 | -0.07196 | 40
AEPW | 'WILKES 138KV' | 116.6958 | -0.06077 | AEPW | 'COMANCHE 138KV' | 160 | 0.01244 | -0.07321 | 40
AEPW | 'WILKES 138KV' | 116.6958 | -0.06077 | AEPW | 'COMANCHE 69KV' | 63 | 0.01239 | -0.07316 | 40
AEPW | 'WILKES 138KV' | 116.6958 | -0.06077 | AEPW | 'SOUTHWESTERN STATION 138KV' | 327 | 0.01212 | -0.07289 | 40
AEPW | 'WILKES 138KV' | 116.6958 | -0.06077 | AEPW | 'WELSH 345KV' | 990 | 0.01228 | -0.07305 | 40
AEPW | 'LONESTAR POWER PLANT 69KV' | 50 | -0.08758 | AEPW | 'KNOXLEE 138KV' | 262.5121 | -0.01564 | -0.07194 | 41
AEPW | 'WILKES 138KV' | 116.6958 | -0.06077 | AEPW | 'WELEETKA 138KV' | 70 | 0.00961 | -0.07038 | 41
AEPW | 'LONESTAR POWER PLANT 69KV' | 50 | -0.08758 | AEPW | 'WILKES 345KV' | 311 | -0.01738 | -0.0702 | 42
AEPW | 'WILKES 138KV' | 116.6958 | -0.06077 | AEPW | 'COGENTRIX 345KV' | 665 | 0.00882 | -0.06959 | 42
AEPW | 'WILKES 138KV' | 116.6958 | -0.06077 | AEPW | 'NORTHEASTERN STATION 138KV' | 405 | 0.00807 | -0.06884 | 42
AEPW | 'WILKES 138KV' | 116.6958 | -0.06077 | AEPW | 'NORTHEASTERN STATION 138KV' | 95 | 0.00807 | -0.06884 | 42
AEPW | 'WILKES 138KV' | 116.6958 | -0.06077 | AEPW | 'NORTHEASTERN STATION 345KV' | 645 | 0.00807 | -0.06884 | 42
AEPW | 'WILKES 138KV' | 116.6958 | -0.06077 | AEPW | 'RIVERSIDE STATION 138KV' | 646 | 0.00877 | -0.06954 | 42
AEPW | 'WILKES 138KV' | 116.6958 | -0.06077 | AEPW | 'TULSA POWER STATION 138KV' | 93 | 0.0087 | -0.06947 | 42
AEPW | 'WILKES 138KV' | 116.6958 | -0.06077 | AEPW | 'TULSA POWER STATION 138KV' | 147 | 0.0087 | -0.06947 | 42
AEPW | 'WILKES 138KV' | 116.6958 | -0.06077 | AEPW | 'FITZHUGH 161KV' | 126 | 0.00382 | -0.06459 | 45
AEPW | 'WILKES 138KV' | 116.6958 | -0.06077 | AEPW | 'LEBROCK 345KV' | 365 | -0.00885 | -0.05192 | 56
AEPW | 'WILKES 138KV' | 116.6958 | -0.06077 | AEPW | 'NARROWS 69KV' | 22 | -0.00834 | -0.05243 | 56
AEPW | 'WILKES 138KV' | 116.6958 | -0.06077 | AEPW | 'PIRKEY GENERATION 138KV' | 248 | -0.01312 | -0.04765 | 61
AEPW | 'WILKES 138KV' | 116.6958 | -0.06077 | AEPW | 'EASTMAN 138KV' | 355 | -0.01562 | -0.04515 | 65
AEPW | 'WILKES 138KV' | 116.6958 | -0.06077 | AEPW | 'KNOXLEE 138KV' | 262.5121 | -0.01564 | -0.04513 | 65
AEPW | 'WILKES 138KV' | 116.6958 | -0.06077 | AEPW | 'WILKES 345KV' | 311 | -0.01738 | -0.04339 | 67
AEPW | 'LIEBERMAN 138KV' | 137 | -0.02651 | AEPW | 'COMANCHE 138KV' | 160 | 0.01244 | -0.03895 | 75
AEPW | 'LIEBERMAN 138KV' | 137 | -0.02651 | AEPW | 'SOUTHWESTERN STATION 138KV' | 327 | 0.01212 | -0.03863 | 75
AEPW | 'LIEBERMAN 138KV' | 137 | -0.02651 | AEPW | 'WELSH 345KV' | 990 | 0.01228 | -0.03879 | 75
AEPW | 'LIEBERMAN 138KV' | 137 | -0.02651 | AEPW | 'WELEETKA 138KV' | 70 | 0.00961 | -0.03612 | 81
AEPW | 'LIEBERMAN 138KV' | 137 | -0.02651 | AEPW | 'COGENTRIX 345KV' | 665 | 0.00882 | -0.03533 | 82
AEPW | 'LIEBERMAN 138KV' | 137 | -0.02651 | AEPW | 'RIVERSIDE STATION 138KV' | 646 | 0.00877 | -0.03528 | 83
AEPW | 'LIEBERMAN 138KV' | 137 | -0.02651 | AEPW | 'TULSA POWER STATION 138KV' | 93 | 0.0087 | -0.03521 | 83
AEPW | 'LIEBERMAN 138KV' | 137 | -0.02651 | AEPW | 'TULSA POWER STATION 138KV' | 147 | 0.0087 | -0.03521 | 83
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.02242 | AEPW | 'COMANCHE 138KV' | 160 | 0.01244 | -0.03486 | 84
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.02242 | AEPW | 'SOUTHWESTERN STATION 138KV' | 327 | 0.01212 | -0.03454 | 84
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.02242 | AEPW | 'WELSH 345KV' | 990 | 0.01228 | -0.0347 | 84
AEPW | 'LIEBERMAN 138KV' | 137 | -0.02651 | AEPW | 'NORTHEASTERN STATION 138KV' | 405 | 0.00807 | -0.03458 | 84
AEPW | 'LIEBERMAN 138KV' | 137 | -0.02651 | AEPW | 'NORTHEASTERN STATION 138KV' | 95 | 0.00807 | -0.03458 | 84
AEPW | 'LIEBERMAN 138KV' | 137 | -0.02651 | AEPW | 'NORTHEASTERN STATION 345KV' | 645 | 0.00807 | -0.03458 | 84
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.02242 | AEPW | 'WELEETKA 138KV' | 70 | 0.00961 | -0.03203 | 91
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.02242 | AEPW | 'COGENTRIX 345KV' | 665 | 0.00882 | -0.03124 | 93
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.02242 | AEPW | 'RIVERSIDE STATION 138KV' | 646 | 0.00877 | -0.03119 | 93
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.02242 | AEPW | 'TULSA POWER STATION 138KV' | 93 | 0.0087 | -0.03112 | 94
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.02242 | AEPW | 'TULSA POWER STATION 138KV' | 147 | 0.0087 | -0.03112 | 94
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.02242 | AEPW | 'NORTHEASTERN STATION 138KV' | 405 | 0.00807 | -0.03049 | 96
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.02242 | AEPW | 'NORTHEASTERN STATION 138KV' | 95 | 0.00807 | -0.03049 | 96
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.02242 | AEPW | 'NORTHEASTERN STATION 345KV' | 645 | 0.00807 | -0.03049 | 96
AEPW | 'LIEBERMAN 138KV' | 137 | -0.02651 | AEPW | 'FITZHUGH 161KV' | 126 | 0.00382 | -0.03033 | 96
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1
Limiting Facility: | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1
Direction: | To->From
Line Outage: | ORRICK - SIBLEY 161KV CKT 1
Flowgate: | 59205592351592445920211106SP
Date Redispatch Needed: | 6/1/06 - 10/1/06
Season Flowgate Identified: | 2006 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1032955 | 0.7533 | 4.828
1034307 | 4.0747 | 4.828
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
MIPU | 'GREENWOOD 161KV' | 255.8 | -0.18518 | MIPU | 'SIBLEY 161KV' | 230.2336 | 0.19121 | -0.37639 | 13
MIPU | 'ARIES 161KV' | 595 | -0.14198 | MIPU | 'SIBLEY 161KV' | 230.2336 | 0.19121 | -0.33319 | 14
MIPU | 'GREENWOOD 161KV' | 255.8 | -0.18518 | MIPU | 'SIBLEY 69KV' | 46 | 0.16359 | -0.34877 | 14
MIPU | 'ARIES 161KV' | 595 | -0.14198 | MIPU | 'SIBLEY 69KV' | 46 | 0.16359 | -0.30557 | 16
MIPU | 'RALPH GREEN 69KV' | 73.7 | -0.11371 | MIPU | 'SIBLEY 161KV' | 230.2336 | 0.19121 | -0.30492 | 16
MIPU | 'RALPH GREEN 69KV' | 73.7 | -0.11371 | MIPU | 'SIBLEY 69KV' | 46 | 0.16359 | -0.2773 | 17
MIPU | 'NEVADA 69KV' | 20.3 | -0.04556 | MIPU | 'SIBLEY 161KV' | 230.2336 | 0.19121 | -0.23677 | 20
MIPU | 'GREENWOOD 161KV' | 255.8 | -0.18518 | MIPU | 'LAKE ROAD 161KV' | 35 | 0.03552 | -0.2207 | 22
MIPU | 'GREENWOOD 161KV' | 255.8 | -0.18518 | MIPU | 'LAKE ROAD 34KV' | 92 | 0.03552 | -0.2207 | 22
MIPU | 'NEVADA 69KV' | 20.3 | -0.04556 | MIPU | 'SIBLEY 69KV' | 46 | 0.16359 | -0.20915 | 23
MIPU | 'ARIES 161KV' | 595 | -0.14198 | MIPU | 'LAKE ROAD 161KV' | 35 | 0.03552 | -0.1775 | 27
MIPU | 'ARIES 161KV' | 595 | -0.14198 | MIPU | 'LAKE ROAD 34KV' | 92 | 0.03552 | -0.1775 | 27
MIPU | 'RALPH GREEN 69KV' | 73.7 | -0.11371 | MIPU | 'LAKE ROAD 161KV' | 35 | 0.03552 | -0.14923 | 32
MIPU | 'RALPH GREEN 69KV' | 73.7 | -0.11371 | MIPU | 'LAKE ROAD 34KV' | 92 | 0.03552 | -0.14923 | 32
MIPU | 'GREENWOOD 161KV' | 255.8 | -0.18518 | MIPU | 'SOUTH HARPER 161KV' | 232.4752 | -0.04893 | -0.13625 | 35
MIPU | 'ARIES 161KV' | 595 | -0.14198 | MIPU | 'SOUTH HARPER 161KV' | 232.4752 | -0.04893 | -0.09305 | 52
MIPU | 'NEVADA 69KV' | 20.3 | -0.04556 | MIPU | 'LAKE ROAD 161KV' | 35 | 0.03552 | -0.08108 | 60
MIPU | 'NEVADA 69KV' | 20.3 | -0.04556 | MIPU | 'LAKE ROAD 34KV' | 92 | 0.03552 | -0.08108 | 60
KACP | 'MARSHALL 161KV' | 39.1 | -0.03666 | KACP | 'HAWTHORN 161KV' | 455 | 0.04087 | -0.07753 | 62
KACP | 'MARSHALL 161KV' | 39.1 | -0.03666 | KACP | 'HAWTHORN 161KV' | 314 | 0.04087 | -0.07753 | 62
KACP | 'MARSHALL 161KV' | 39.1 | -0.03666 | KACP | 'NORTHEAST 13KV' | 36 | 0.03795 | -0.07461 | 65
KACP | 'MARSHALL 161KV' | 39.1 | -0.03666 | KACP | 'NORTHEAST 13KV' | 36 | 0.03795 | -0.07461 | 65
KACP | 'MARSHALL 161KV' | 39.1 | -0.03666 | KACP | 'NORTHEAST 13KV' | 38 | 0.03795 | -0.07461 | 65
KACP | 'MARSHALL 161KV' | 39.1 | -0.03666 | KACP | 'NORTHEAST 161KV' | 35 | 0.03795 | -0.07461 | 65
KACP | 'MARSHALL 161KV' | 39.1 | -0.03666 | KACP | 'NORTHEAST 161KV' | 38 | 0.03795 | -0.07461 | 65
KACP | 'MARSHALL 161KV' | 39.1 | -0.03666 | KACP | 'NORTHEAST 161KV' | 27.8936 | 0.03795 | -0.07461 | 65
KACP | 'MONTROSE 161KV' | 27.8148 | -0.02891 | KACP | 'HAWTHORN 161KV' | 455 | 0.04087 | -0.06978 | 69
KACP | 'MONTROSE 161KV' | 27.8148 | -0.02891 | KACP | 'HAWTHORN 161KV' | 314 | 0.04087 | -0.06978 | 69
KACP | 'MONTROSE 161KV' | 27.8148 | -0.02891 | KACP | 'NORTHEAST 13KV' | 36 | 0.03795 | -0.06686 | 72
KACP | 'MONTROSE 161KV' | 27.8148 | -0.02891 | KACP | 'NORTHEAST 13KV' | 36 | 0.03795 | -0.06686 | 72
KACP | 'MONTROSE 161KV' | 27.8148 | -0.02891 | KACP | 'NORTHEAST 13KV' | 38 | 0.03795 | -0.06686 | 72
KACP | 'MONTROSE 161KV' | 27.8148 | -0.02891 | KACP | 'NORTHEAST 161KV' | 35 | 0.03795 | -0.06686 | 72
KACP | 'MONTROSE 161KV' | 27.8148 | -0.02891 | KACP | 'NORTHEAST 161KV' | 38 | 0.03795 | -0.06686 | 72
KACP | 'MONTROSE 161KV' | 27.8148 | -0.02891 | KACP | 'NORTHEAST 161KV' | 27.8936 | 0.03795 | -0.06686 | 72
MIPU | 'RALPH GREEN 69KV' | 73.7 | -0.11371 | MIPU | 'SOUTH HARPER 161KV' | 232.4752 | -0.04893 | -0.06478 | 75
KACP | 'MARSHALL 161KV' | 39.1 | -0.03666 | KACP | 'IATAN 345KV' | 396 | 0.0154 | -0.05206 | 93
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1
Limiting Facility: | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1
Direction: | To->From
Line Outage: | ORRICK - SIBLEY 161KV CKT 1
Flowgate: | 59205592351592445920211107SP
Date Redispatch Needed: | 6/1/07 - 10/1/07
Season Flowgate Identified: | 2007 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1032955 | 0.7509 | 4.737
1034307 | 3.9861 | 4.737
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
MIPU | 'GREENWOOD 161KV' | 255.8 | -0.18515 | MIPU | 'SIBLEY 161KV' | 232.7943 | 0.19105 | -0.3762 | 13
MIPU | 'ARIES 161KV' | 595 | -0.14194 | MIPU | 'SIBLEY 161KV' | 232.7943 | 0.19105 | -0.33299 | 14
MIPU | 'GREENWOOD 161KV' | 255.8 | -0.18515 | MIPU | 'SIBLEY 69KV' | 46 | 0.16339 | -0.34854 | 14
MIPU | 'ARIES 161KV' | 595 | -0.14194 | MIPU | 'SIBLEY 69KV' | 46 | 0.16339 | -0.30533 | 16
MIPU | 'GREENWOOD 161KV' | 255.8 | -0.18515 | MIPU | 'LAKE ROAD 161KV' | 35 | 0.03534 | -0.22049 | 21
MIPU | 'GREENWOOD 161KV' | 255.8 | -0.18515 | MIPU | 'LAKE ROAD 34KV' | 92 | 0.03534 | -0.22049 | 21
MIPU | 'ARIES 161KV' | 595 | -0.14194 | MIPU | 'LAKE ROAD 161KV' | 35 | 0.03534 | -0.17728 | 27
MIPU | 'ARIES 161KV' | 595 | -0.14194 | MIPU | 'LAKE ROAD 34KV' | 92 | 0.03534 | -0.17728 | 27
MIPU | 'GREENWOOD 161KV' | 255.8 | -0.18515 | MIPU | 'SOUTH HARPER 161KV' | 274.6863 | -0.04884 | -0.13631 | 35
MIPU | 'ARIES 161KV' | 595 | -0.14194 | MIPU | 'SOUTH HARPER 161KV' | 274.6863 | -0.04884 | -0.0931 | 51
MIPU | 'NEVADA 69KV' | 20.3 | -0.04529 | MIPU | 'LAKE ROAD 161KV' | 35 | 0.03534 | -0.08063 | 59
MIPU | 'NEVADA 69KV' | 20.3 | -0.04529 | MIPU | 'LAKE ROAD 34KV' | 92 | 0.03534 | -0.08063 | 59
KACP | 'MARSHALL 161KV' | 39.1 | -0.03669 | KACP | 'HAWTHORN 161KV' | 455 | 0.04042 | -0.07711 | 61
KACP | 'MARSHALL 161KV' | 39.1 | -0.03669 | KACP | 'HAWTHORN 161KV' | 314 | 0.04042 | -0.07711 | 61
KACP | 'MARSHALL 161KV' | 39.1 | -0.03669 | KACP | 'NORTHEAST 13KV' | 36 | 0.03717 | -0.07386 | 64
KACP | 'MARSHALL 161KV' | 39.1 | -0.03669 | KACP | 'NORTHEAST 13KV' | 36 | 0.03717 | -0.07386 | 64
KACP | 'MARSHALL 161KV' | 39.1 | -0.03669 | KACP | 'NORTHEAST 13KV' | 38 | 0.03717 | -0.07386 | 64
KACP | 'MARSHALL 161KV' | 39.1 | -0.03669 | KACP | 'NORTHEAST 161KV' | 35 | 0.03717 | -0.07386 | 64
KACP | 'MARSHALL 161KV' | 39.1 | -0.03669 | KACP | 'NORTHEAST 161KV' | 38 | 0.03717 | -0.07386 | 64
KACP | 'MARSHALL 161KV' | 39.1 | -0.03669 | KACP | 'NORTHEAST 161KV' | 32.5508 | 0.03717 | -0.07386 | 64
KACP | 'MONTROSE 161KV' | 27.6861 | -0.0288 | KACP | 'HAWTHORN 161KV' | 455 | 0.04042 | -0.06922 | 68
KACP | 'MONTROSE 161KV' | 27.6861 | -0.0288 | KACP | 'HAWTHORN 161KV' | 314 | 0.04042 | -0.06922 | 68
KACP | 'MONTROSE 161KV' | 27.6861 | -0.0288 | KACP | 'NORTHEAST 13KV' | 36 | 0.03717 | -0.06597 | 72
KACP | 'MONTROSE 161KV' | 27.6861 | -0.0288 | KACP | 'NORTHEAST 13KV' | 36 | 0.03717 | -0.06597 | 72
KACP | 'MONTROSE 161KV' | 27.6861 | -0.0288 | KACP | 'NORTHEAST 13KV' | 38 | 0.03717 | -0.06597 | 72
KACP | 'MONTROSE 161KV' | 27.6861 | -0.0288 | KACP | 'NORTHEAST 161KV' | 35 | 0.03717 | -0.06597 | 72
KACP | 'MONTROSE 161KV' | 27.6861 | -0.0288 | KACP | 'NORTHEAST 161KV' | 38 | 0.03717 | -0.06597 | 72
KACP | 'MONTROSE 161KV' | 27.6861 | -0.0288 | KACP | 'NORTHEAST 161KV' | 32.5508 | 0.03717 | -0.06597 | 72
MIPU | 'RALPH GREEN 69KV' | 73.7 | -0.11364 | MIPU | 'SOUTH HARPER 161KV' | 274.6863 | -0.04884 | -0.0648 | 73
KACP | 'MARSHALL 161KV' | 39.1 | -0.03669 | KACP | 'IATAN 345KV' | 396 | 0.01542 | -0.05211 | 91
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1
Limiting Facility: | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1
Direction: | To->From
Line Outage: | ORRICK - RICHMOND 161KV CKT 1
Flowgate: | 59205592351592445923611106SP
Date Redispatch Needed: | 6/1/06 - 10/1/06
Season Flowgate Identified: | 2006 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1032955 | 0.7533 | 4.828
1034307 | 4.0747 | 4.828
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
MIPU | 'GREENWOOD 161KV' | 255.8 | -0.18518 | MIPU | 'SIBLEY 161KV' | 230.2336 | 0.19121 | -0.37639 | 13
MIPU | 'ARIES 161KV' | 595 | -0.14198 | MIPU | 'SIBLEY 161KV' | 230.2336 | 0.19121 | -0.33319 | 14
MIPU | 'GREENWOOD 161KV' | 255.8 | -0.18518 | MIPU | 'SIBLEY 69KV' | 46 | 0.16359 | -0.34877 | 14
MIPU | 'ARIES 161KV' | 595 | -0.14198 | MIPU | 'SIBLEY 69KV' | 46 | 0.16359 | -0.30557 | 16
MIPU | 'RALPH GREEN 69KV' | 73.7 | -0.11371 | MIPU | 'SIBLEY 161KV' | 230.2336 | 0.19121 | -0.30492 | 16
MIPU | 'RALPH GREEN 69KV' | 73.7 | -0.11371 | MIPU | 'SIBLEY 69KV' | 46 | 0.16359 | -0.2773 | 17
MIPU | 'NEVADA 69KV' | 20.3 | -0.04556 | MIPU | 'SIBLEY 161KV' | 230.2336 | 0.19121 | -0.23677 | 20
MIPU | 'GREENWOOD 161KV' | 255.8 | -0.18518 | MIPU | 'LAKE ROAD 161KV' | 35 | 0.03552 | -0.2207 | 22
MIPU | 'GREENWOOD 161KV' | 255.8 | -0.18518 | MIPU | 'LAKE ROAD 34KV' | 92 | 0.03552 | -0.2207 | 22
MIPU | 'NEVADA 69KV' | 20.3 | -0.04556 | MIPU | 'SIBLEY 69KV' | 46 | 0.16359 | -0.20915 | 23
MIPU | 'ARIES 161KV' | 595 | -0.14198 | MIPU | 'LAKE ROAD 161KV' | 35 | 0.03552 | -0.1775 | 27
MIPU | 'ARIES 161KV' | 595 | -0.14198 | MIPU | 'LAKE ROAD 34KV' | 92 | 0.03552 | -0.1775 | 27
MIPU | 'RALPH GREEN 69KV' | 73.7 | -0.11371 | MIPU | 'LAKE ROAD 161KV' | 35 | 0.03552 | -0.14923 | 32
MIPU | 'RALPH GREEN 69KV' | 73.7 | -0.11371 | MIPU | 'LAKE ROAD 34KV' | 92 | 0.03552 | -0.14923 | 32
MIPU | 'GREENWOOD 161KV' | 255.8 | -0.18518 | MIPU | 'SOUTH HARPER 161KV' | 232.4752 | -0.04893 | -0.13625 | 35
MIPU | 'ARIES 161KV' | 595 | -0.14198 | MIPU | 'SOUTH HARPER 161KV' | 232.4752 | -0.04893 | -0.09305 | 52
MIPU | 'NEVADA 69KV' | 20.3 | -0.04556 | MIPU | 'LAKE ROAD 161KV' | 35 | 0.03552 | -0.08108 | 60
MIPU | 'NEVADA 69KV' | 20.3 | -0.04556 | MIPU | 'LAKE ROAD 34KV' | 92 | 0.03552 | -0.08108 | 60
KACP | 'MARSHALL 161KV' | 39.1 | -0.03666 | KACP | 'HAWTHORN 161KV' | 455 | 0.04087 | -0.07753 | 62
KACP | 'MARSHALL 161KV' | 39.1 | -0.03666 | KACP | 'HAWTHORN 161KV' | 314 | 0.04087 | -0.07753 | 62
KACP | 'MARSHALL 161KV' | 39.1 | -0.03666 | KACP | 'NORTHEAST 13KV' | 36 | 0.03795 | -0.07461 | 65
KACP | 'MARSHALL 161KV' | 39.1 | -0.03666 | KACP | 'NORTHEAST 13KV' | 36 | 0.03795 | -0.07461 | 65
KACP | 'MARSHALL 161KV' | 39.1 | -0.03666 | KACP | 'NORTHEAST 13KV' | 38 | 0.03795 | -0.07461 | 65
KACP | 'MARSHALL 161KV' | 39.1 | -0.03666 | KACP | 'NORTHEAST 161KV' | 35 | 0.03795 | -0.07461 | 65
KACP | 'MARSHALL 161KV' | 39.1 | -0.03666 | KACP | 'NORTHEAST 161KV' | 38 | 0.03795 | -0.07461 | 65
KACP | 'MARSHALL 161KV' | 39.1 | -0.03666 | KACP | 'NORTHEAST 161KV' | 27.8936 | 0.03795 | -0.07461 | 65
KACP | 'MONTROSE 161KV' | 27.8148 | -0.02891 | KACP | 'HAWTHORN 161KV' | 455 | 0.04087 | -0.06978 | 69
KACP | 'MONTROSE 161KV' | 27.8148 | -0.02891 | KACP | 'HAWTHORN 161KV' | 314 | 0.04087 | -0.06978 | 69
KACP | 'MONTROSE 161KV' | 27.8148 | -0.02891 | KACP | 'NORTHEAST 13KV' | 36 | 0.03795 | -0.06686 | 72
KACP | 'MONTROSE 161KV' | 27.8148 | -0.02891 | KACP | 'NORTHEAST 13KV' | 36 | 0.03795 | -0.06686 | 72
KACP | 'MONTROSE 161KV' | 27.8148 | -0.02891 | KACP | 'NORTHEAST 13KV' | 38 | 0.03795 | -0.06686 | 72
KACP | 'MONTROSE 161KV' | 27.8148 | -0.02891 | KACP | 'NORTHEAST 161KV' | 35 | 0.03795 | -0.06686 | 72
KACP | 'MONTROSE 161KV' | 27.8148 | -0.02891 | KACP | 'NORTHEAST 161KV' | 38 | 0.03795 | -0.06686 | 72
KACP | 'MONTROSE 161KV' | 27.8148 | -0.02891 | KACP | 'NORTHEAST 161KV' | 27.8936 | 0.03795 | -0.06686 | 72
MIPU | 'RALPH GREEN 69KV' | 73.7 | -0.11371 | MIPU | 'SOUTH HARPER 161KV' | 232.4752 | -0.04893 | -0.06478 | 75
KACP | 'MARSHALL 161KV' | 39.1 | -0.03666 | KACP | 'IATAN 345KV' | 396 | 0.0154 | -0.05206 | 93
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1
Limiting Facility: | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1
Direction: | To->From
Line Outage: | ORRICK - RICHMOND 161KV CKT 1
Flowgate: | 59205592351592445923611107SP
Date Redispatch Needed: | 6/1/07 - 10/1/07
Season Flowgate Identified: | 2007 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1032955 | 0.7509 | 4.737
1034307 | 3.9861 | 4.737
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
MIPU | 'GREENWOOD 161KV' | 255.8 | -0.18515 | MIPU | 'SIBLEY 161KV' | 232.7943 | 0.19105 | -0.3762 | 13
MIPU | 'ARIES 161KV' | 595 | -0.14194 | MIPU | 'SIBLEY 161KV' | 232.7943 | 0.19105 | -0.33299 | 14
MIPU | 'GREENWOOD 161KV' | 255.8 | -0.18515 | MIPU | 'SIBLEY 69KV' | 46 | 0.16339 | -0.34854 | 14
MIPU | 'ARIES 161KV' | 595 | -0.14194 | MIPU | 'SIBLEY 69KV' | 46 | 0.16339 | -0.30533 | 16
MIPU | 'GREENWOOD 161KV' | 255.8 | -0.18515 | MIPU | 'LAKE ROAD 161KV' | 35 | 0.03534 | -0.22049 | 21
MIPU | 'GREENWOOD 161KV' | 255.8 | -0.18515 | MIPU | 'LAKE ROAD 34KV' | 92 | 0.03534 | -0.22049 | 21
MIPU | 'ARIES 161KV' | 595 | -0.14194 | MIPU | 'LAKE ROAD 161KV' | 35 | 0.03534 | -0.17728 | 27
MIPU | 'ARIES 161KV' | 595 | -0.14194 | MIPU | 'LAKE ROAD 34KV' | 92 | 0.03534 | -0.17728 | 27
MIPU | 'GREENWOOD 161KV' | 255.8 | -0.18515 | MIPU | 'SOUTH HARPER 161KV' | 274.6863 | -0.04884 | -0.13631 | 35
MIPU | 'ARIES 161KV' | 595 | -0.14194 | MIPU | 'SOUTH HARPER 161KV' | 274.6863 | -0.04884 | -0.0931 | 51
MIPU | 'NEVADA 69KV' | 20.3 | -0.04529 | MIPU | 'LAKE ROAD 161KV' | 35 | 0.03534 | -0.08063 | 59
MIPU | 'NEVADA 69KV' | 20.3 | -0.04529 | MIPU | 'LAKE ROAD 34KV' | 92 | 0.03534 | -0.08063 | 59
KACP | 'MARSHALL 161KV' | 39.1 | -0.03669 | KACP | 'HAWTHORN 161KV' | 455 | 0.04042 | -0.07711 | 61
KACP | 'MARSHALL 161KV' | 39.1 | -0.03669 | KACP | 'HAWTHORN 161KV' | 314 | 0.04042 | -0.07711 | 61
KACP | 'MARSHALL 161KV' | 39.1 | -0.03669 | KACP | 'NORTHEAST 13KV' | 36 | 0.03717 | -0.07386 | 64
KACP | 'MARSHALL 161KV' | 39.1 | -0.03669 | KACP | 'NORTHEAST 13KV' | 36 | 0.03717 | -0.07386 | 64
KACP | 'MARSHALL 161KV' | 39.1 | -0.03669 | KACP | 'NORTHEAST 13KV' | 38 | 0.03717 | -0.07386 | 64
KACP | 'MARSHALL 161KV' | 39.1 | -0.03669 | KACP | 'NORTHEAST 161KV' | 35 | 0.03717 | -0.07386 | 64
KACP | 'MARSHALL 161KV' | 39.1 | -0.03669 | KACP | 'NORTHEAST 161KV' | 38 | 0.03717 | -0.07386 | 64
KACP | 'MARSHALL 161KV' | 39.1 | -0.03669 | KACP | 'NORTHEAST 161KV' | 32.5508 | 0.03717 | -0.07386 | 64
KACP | 'MONTROSE 161KV' | 27.6861 | -0.0288 | KACP | 'HAWTHORN 161KV' | 455 | 0.04042 | -0.06922 | 68
KACP | 'MONTROSE 161KV' | 27.6861 | -0.0288 | KACP | 'HAWTHORN 161KV' | 314 | 0.04042 | -0.06922 | 68
KACP | 'MONTROSE 161KV' | 27.6861 | -0.0288 | KACP | 'NORTHEAST 13KV' | 36 | 0.03717 | -0.06597 | 72
KACP | 'MONTROSE 161KV' | 27.6861 | -0.0288 | KACP | 'NORTHEAST 13KV' | 36 | 0.03717 | -0.06597 | 72
KACP | 'MONTROSE 161KV' | 27.6861 | -0.0288 | KACP | 'NORTHEAST 13KV' | 38 | 0.03717 | -0.06597 | 72
KACP | 'MONTROSE 161KV' | 27.6861 | -0.0288 | KACP | 'NORTHEAST 161KV' | 35 | 0.03717 | -0.06597 | 72
KACP | 'MONTROSE 161KV' | 27.6861 | -0.0288 | KACP | 'NORTHEAST 161KV' | 38 | 0.03717 | -0.06597 | 72
KACP | 'MONTROSE 161KV' | 27.6861 | -0.0288 | KACP | 'NORTHEAST 161KV' | 32.5508 | 0.03717 | -0.06597 | 72
MIPU | 'RALPH GREEN 69KV' | 73.7 | -0.11364 | MIPU | 'SOUTH HARPER 161KV' | 274.6863 | -0.04884 | -0.0648 | 73
KACP | 'MARSHALL 161KV' | 39.1 | -0.03669 | KACP | 'IATAN 345KV' | 396 | 0.01542 | -0.05211 | 91
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1
Limiting Facility: | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1
Direction: | To->From
Line Outage: | PLEASANT HILL () 345/161/13.8KV TRANSFORMER CKT 1
Flowgate: | 59205592351PHILL737511106SP
Date Redispatch Needed: | 6/1/06 - 10/1/06
Season Flowgate Identified: | 2006 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1032955 | 0.49125 | 3.6266
1034307 | 3.1353 | 3.6266
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
MIPU | 'GREENWOOD 161KV' | 255.8 | -0.2726 | MIPU | 'SIBLEY 161KV' | 230.2336 | 0.15485 | -0.42745 | 8
MIPU | 'ARIES 161KV' | 595 | -0.24243 | MIPU | 'SIBLEY 161KV' | 230.2336 | 0.15485 | -0.39728 | 9
MIPU | 'GREENWOOD 161KV' | 255.8 | -0.2726 | MIPU | 'SIBLEY 69KV' | 46 | 0.13272 | -0.40532 | 9
MIPU | 'ARIES 161KV' | 595 | -0.24243 | MIPU | 'SIBLEY 69KV' | 46 | 0.13272 | -0.37515 | 10
MIPU | 'RALPH GREEN 69KV' | 73.7 | -0.16187 | MIPU | 'SIBLEY 161KV' | 230.2336 | 0.15485 | -0.31672 | 11
MIPU | 'GREENWOOD 161KV' | 255.8 | -0.2726 | MIPU | 'LAKE ROAD 161KV' | 35 | 0.02878 | -0.30138 | 12
MIPU | 'GREENWOOD 161KV' | 255.8 | -0.2726 | MIPU | 'LAKE ROAD 34KV' | 92 | 0.02878 | -0.30138 | 12
MIPU | 'RALPH GREEN 69KV' | 73.7 | -0.16187 | MIPU | 'SIBLEY 69KV' | 46 | 0.13272 | -0.29459 | 12
MIPU | 'ARIES 161KV' | 595 | -0.24243 | MIPU | 'LAKE ROAD 161KV' | 35 | 0.02878 | -0.27121 | 13
MIPU | 'ARIES 161KV' | 595 | -0.24243 | MIPU | 'LAKE ROAD 34KV' | 92 | 0.02878 | -0.27121 | 13
MIPU | 'GREENWOOD 161KV' | 255.8 | -0.2726 | MIPU | 'SOUTH HARPER 161KV' | 232.4752 | -0.05024 | -0.22236 | 16
MIPU | 'NEVADA 69KV' | 20.3 | -0.06432 | MIPU | 'SIBLEY 161KV' | 230.2336 | 0.15485 | -0.21917 | 17
MIPU | 'NEVADA 69KV' | 20.3 | -0.06432 | MIPU | 'SIBLEY 69KV' | 46 | 0.13272 | -0.19704 | 18
MIPU | 'ARIES 161KV' | 595 | -0.24243 | MIPU | 'SOUTH HARPER 161KV' | 232.4752 | -0.05024 | -0.19219 | 19
MIPU | 'RALPH GREEN 69KV' | 73.7 | -0.16187 | MIPU | 'LAKE ROAD 161KV' | 35 | 0.02878 | -0.19065 | 19
MIPU | 'RALPH GREEN 69KV' | 73.7 | -0.16187 | MIPU | 'LAKE ROAD 34KV' | 92 | 0.02878 | -0.19065 | 19
MIPU | 'RALPH GREEN 69KV' | 73.7 | -0.16187 | MIPU | 'SOUTH HARPER 161KV' | 232.4752 | -0.05024 | -0.11163 | 32
MIPU | 'NEVADA 69KV' | 20.3 | -0.06432 | MIPU | 'LAKE ROAD 161KV' | 35 | 0.02878 | -0.0931 | 39
MIPU | 'NEVADA 69KV' | 20.3 | -0.06432 | MIPU | 'LAKE ROAD 34KV' | 92 | 0.02878 | -0.0931 | 39
KACP | 'MONTROSE 161KV' | 27.8148 | -0.04268 | KACP | 'HAWTHORN 161KV' | 455 | 0.03194 | -0.07462 | 49
KACP | 'MONTROSE 161KV' | 27.8148 | -0.04268 | KACP | 'HAWTHORN 161KV' | 314 | 0.03194 | -0.07462 | 49
KACP | 'MONTROSE 161KV' | 27.8148 | -0.04268 | KACP | 'NORTHEAST 13KV' | 36 | 0.02881 | -0.07149 | 51
KACP | 'MONTROSE 161KV' | 27.8148 | -0.04268 | KACP | 'NORTHEAST 13KV' | 36 | 0.02881 | -0.07149 | 51
KACP | 'MONTROSE 161KV' | 27.8148 | -0.04268 | KACP | 'NORTHEAST 13KV' | 38 | 0.02881 | -0.07149 | 51
KACP | 'MONTROSE 161KV' | 27.8148 | -0.04268 | KACP | 'NORTHEAST 161KV' | 35 | 0.02881 | -0.07149 | 51
KACP | 'MONTROSE 161KV' | 27.8148 | -0.04268 | KACP | 'NORTHEAST 161KV' | 38 | 0.02881 | -0.07149 | 51
KACP | 'MONTROSE 161KV' | 27.8148 | -0.04268 | KACP | 'NORTHEAST 161KV' | 27.8936 | 0.02881 | -0.07149 | 51
KACP | 'MARSHALL 161KV' | 39.1 | -0.02274 | KACP | 'HAWTHORN 161KV' | 455 | 0.03194 | -0.05468 | 66
KACP | 'MARSHALL 161KV' | 39.1 | -0.02274 | KACP | 'HAWTHORN 161KV' | 314 | 0.03194 | -0.05468 | 66
KACP | 'MONTROSE 161KV' | 27.8148 | -0.04268 | KACP | 'IATAN 345KV' | 396 | 0.0114 | -0.05408 | 67
KACP | 'MARSHALL 161KV' | 39.1 | -0.02274 | KACP | 'NORTHEAST 13KV' | 36 | 0.02881 | -0.05155 | 70
KACP | 'MARSHALL 161KV' | 39.1 | -0.02274 | KACP | 'NORTHEAST 13KV' | 36 | 0.02881 | -0.05155 | 70
KACP | 'MARSHALL 161KV' | 39.1 | -0.02274 | KACP | 'NORTHEAST 13KV' | 38 | 0.02881 | -0.05155 | 70
KACP | 'MARSHALL 161KV' | 39.1 | -0.02274 | KACP | 'NORTHEAST 161KV' | 35 | 0.02881 | -0.05155 | 70
KACP | 'MARSHALL 161KV' | 39.1 | -0.02274 | KACP | 'NORTHEAST 161KV' | 38 | 0.02881 | -0.05155 | 70
KACP | 'MARSHALL 161KV' | 39.1 | -0.02274 | KACP | 'NORTHEAST 161KV' | 27.8936 | 0.02881 | -0.05155 | 70
KACP | 'MARSHALL 161KV' | 39.1 | -0.02274 | KACP | 'IATAN 345KV' | 396 | 0.0114 | -0.03414 | 106
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1
Limiting Facility: | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1
Direction: | To->From
Line Outage: | PLEASANT HILL () 345/161/13.8KV TRANSFORMER CKT 1
Flowgate: | 59205592351PHILL737511107SP
Date Redispatch Needed: | 6/1/07 - 10/1/07
Season Flowgate Identified: | 2007 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1032955 | 0.4899 | 0.4899
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
MIPU | 'ARIES 161KV' | 595 | -0.24241 | MIPU | 'SIBLEY 161KV' | 232.7943 | 0.15465 | -0.39706 | 1
MIPU | 'ARIES 161KV' | 595 | -0.24241 | MIPU | 'SIBLEY 69KV' | 46 | 0.1325 | -0.37491 | 1
MIPU | 'GREENWOOD 161KV' | 255.8 | -0.2726 | MIPU | 'SIBLEY 161KV' | 232.7943 | 0.15465 | -0.42725 | 1
MIPU | 'GREENWOOD 161KV' | 255.8 | -0.2726 | MIPU | 'SIBLEY 69KV' | 46 | 0.1325 | -0.4051 | 1
MIPU | 'ARIES 161KV' | 595 | -0.24241 | MIPU | 'LAKE ROAD 161KV' | 35 | 0.02858 | -0.27099 | 2
MIPU | 'ARIES 161KV' | 595 | -0.24241 | MIPU | 'LAKE ROAD 34KV' | 92 | 0.02858 | -0.27099 | 2
MIPU | 'GREENWOOD 161KV' | 255.8 | -0.2726 | MIPU | 'LAKE ROAD 161KV' | 35 | 0.02858 | -0.30118 | 2
MIPU | 'GREENWOOD 161KV' | 255.8 | -0.2726 | MIPU | 'LAKE ROAD 34KV' | 92 | 0.02858 | -0.30118 | 2
MIPU | 'GREENWOOD 161KV' | 255.8 | -0.2726 | MIPU | 'SOUTH HARPER 161KV' | 274.6863 | -0.05019 | -0.22241 | 2
MIPU | 'RALPH GREEN 69KV' | 73.7 | -0.16184 | MIPU | 'SIBLEY 161KV' | 232.7943 | 0.15465 | -0.31649 | 2
MIPU | 'RALPH GREEN 69KV' | 73.7 | -0.16184 | MIPU | 'SIBLEY 69KV' | 46 | 0.1325 | -0.29434 | 2
MIPU | 'ARIES 161KV' | 595 | -0.24241 | MIPU | 'SOUTH HARPER 161KV' | 274.6863 | -0.05019 | -0.19222 | 3
MIPU | 'RALPH GREEN 69KV' | 73.7 | -0.16184 | MIPU | 'LAKE ROAD 161KV' | 35 | 0.02858 | -0.19042 | 3
MIPU | 'RALPH GREEN 69KV' | 73.7 | -0.16184 | MIPU | 'LAKE ROAD 34KV' | 92 | 0.02858 | -0.19042 | 3
MIPU | 'RALPH GREEN 69KV' | 73.7 | -0.16184 | MIPU | 'SOUTH HARPER 161KV' | 274.6863 | -0.05019 | -0.11165 | 4
MIPU | 'NEVADA 69KV' | 20.3 | -0.06403 | MIPU | 'LAKE ROAD 161KV' | 35 | 0.02858 | -0.09261 | 5
MIPU | 'NEVADA 69KV' | 20.3 | -0.06403 | MIPU | 'LAKE ROAD 34KV' | 92 | 0.02858 | -0.09261 | 5
KACP | 'MONTROSE 161KV' | 27.6861 | -0.0426 | KACP | 'HAWTHORN 161KV' | 455 | 0.03149 | -0.07409 | 7
KACP | 'MONTROSE 161KV' | 27.6861 | -0.0426 | KACP | 'HAWTHORN 161KV' | 314 | 0.03149 | -0.07409 | 7
KACP | 'MONTROSE 161KV' | 27.6861 | -0.0426 | KACP | 'NORTHEAST 13KV' | 36 | 0.02805 | -0.07065 | 7
KACP | 'MONTROSE 161KV' | 27.6861 | -0.0426 | KACP | 'NORTHEAST 13KV' | 36 | 0.02805 | -0.07065 | 7
KACP | 'MONTROSE 161KV' | 27.6861 | -0.0426 | KACP | 'NORTHEAST 13KV' | 38 | 0.02805 | -0.07065 | 7
KACP | 'MONTROSE 161KV' | 27.6861 | -0.0426 | KACP | 'NORTHEAST 161KV' | 35 | 0.02805 | -0.07065 | 7
KACP | 'MONTROSE 161KV' | 27.6861 | -0.0426 | KACP | 'NORTHEAST 161KV' | 38 | 0.02805 | -0.07065 | 7
KACP | 'MONTROSE 161KV' | 27.6861 | -0.0426 | KACP | 'NORTHEAST 161KV' | 32.5508 | 0.02805 | -0.07065 | 7
KACP | 'MARSHALL 161KV' | 39.1 | -0.02291 | KACP | 'HAWTHORN 161KV' | 455 | 0.03149 | -0.0544 | 9
KACP | 'MARSHALL 161KV' | 39.1 | -0.02291 | KACP | 'HAWTHORN 161KV' | 314 | 0.03149 | -0.0544 | 9
KACP | 'MONTROSE 161KV' | 27.6861 | -0.0426 | KACP | 'IATAN 345KV' | 396 | 0.01139 | -0.05399 | 9
KACP | 'MARSHALL 161KV' | 39.1 | -0.02291 | KACP | 'NORTHEAST 13KV' | 36 | 0.02805 | -0.05096 | 10
KACP | 'MARSHALL 161KV' | 39.1 | -0.02291 | KACP | 'NORTHEAST 13KV' | 36 | 0.02805 | -0.05096 | 10
KACP | 'MARSHALL 161KV' | 39.1 | -0.02291 | KACP | 'NORTHEAST 13KV' | 38 | 0.02805 | -0.05096 | 10
KACP | 'MARSHALL 161KV' | 39.1 | -0.02291 | KACP | 'NORTHEAST 161KV' | 35 | 0.02805 | -0.05096 | 10
KACP | 'MARSHALL 161KV' | 39.1 | -0.02291 | KACP | 'NORTHEAST 161KV' | 38 | 0.02805 | -0.05096 | 10
KACP | 'MARSHALL 161KV' | 39.1 | -0.02291 | KACP | 'NORTHEAST 161KV' | 32.5508 | 0.02805 | -0.05096 | 10
SWPA | 'STOCKTON 161KV' | 7.9 | -0.03235 | SWPA | 'CLARENCE CANNON DAM 69KV' | 39.2 | 0.00498 | -0.03733 | 13
KACP | 'MARSHALL 161KV' | 39.1 | -0.02291 | KACP | 'IATAN 345KV' | 396 | 0.01139 | -0.0343 | 14
KACP | 'MONTROSE 161KV' | 27.6861 | -0.0426 | KACP | 'BULL CREEK 161KV' | 308 | -0.00865 | -0.03395 | 14
SWPA | 'STOCKTON 161KV' | 7.9 | -0.03235 | SWPA | 'SIKESTON 161KV' | 235 | -0.00028 | -0.03207 | 15
KACP | 'MONTROSE 161KV' | 27.6861 | -0.0426 | KACP | 'LACYGNE UNIT 345KV' | 958 | -0.01131 | -0.03129 | 16
SWPA | 'STOCKTON 161KV' | 7.9 | -0.03235 | SWPA | 'JONESBORO 161KV' | 63 | -0.00167 | -0.03068 | 16
SWPA | 'STOCKTON 161KV' | 7.9 | -0.03235 | SWPA | 'KENNETT 69KV' | 7.2 | -0.00098 | -0.03137 | 16
SWPA | 'STOCKTON 161KV' | 7.9 | -0.03235 | SWPA | 'MALDEN 69KV' | 7 | -0.00075 | -0.0316 | 16
SWPA | 'STOCKTON 161KV' | 7.9 | -0.03235 | SWPA | 'PARAGOULD 69KV' | 5.5 | -0.00138 | -0.03097 | 16
SWPA | 'STOCKTON 161KV' | 7.9 | -0.03235 | SWPA | 'POPLAR BLUFF 69KV' | 6 | -0.00092 | -0.03143 | 16
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | FPL SWITCH - MOORELAND 138KV CKT 1 OKGE & FPL SWITCH - MOORELAND 138KV CKT 1 WFEC
Limiting Facility: | FPL SWITCH - MOORELAND 138KV CKT 1
Direction: | From->To
Line Outage: | WOODWARD - WOODWARD 69KV CKT 1
Flowgate: | 55785559991547825609611106FA
Date Redispatch Needed: | 10/1/06 - 12/1/06
Season Flowgate Identified: | 2006 Fall Peak
Reservation | Relief Amount | Aggregate Relief Amount
1032973 | 31.1302 | 31.1302
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 31
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 31
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 31
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 31
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 31
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 31
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 31
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 31
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 31
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 31
OKGE | 'MCCLAIN 138KV' | 42 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 31
OKGE | 'MCCLAIN 138KV' | 42 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 31
OKGE | 'MUSKOGEE 161KV' | 166 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 31
OKGE | 'MUSKOGEE 161KV' | 31 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 31
OKGE | 'MUSKOGEE 161KV' | 31 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 31
OKGE | 'MUSKOGEE 161KV' | 166 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 31
OKGE | 'MUSKOGEE 345KV' | 20 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 31
OKGE | 'MUSKOGEE 345KV' | 20 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 31
OKGE | 'MUSTANG 138KV' | 365.5 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 31
OKGE | 'MUSTANG 138KV' | 365.5 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 31
OKGE | 'MUSTANG 69KV' | 106 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 31
OKGE | 'MUSTANG 69KV' | 106 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 31
OKGE | 'ONE OAK 345KV' | 236 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 31
OKGE | 'ONE OAK 345KV' | 236 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 31
OKGE | 'REDBUD 345KV' | 421.65 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 31
OKGE | 'REDBUD 345KV' | 900 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 31
OKGE | 'REDBUD 345KV' | 421.65 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 31
OKGE | 'REDBUD 345KV' | 900 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 31
OKGE | 'SEMINOLE 138KV' | 262.1816 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 31
OKGE | 'SEMINOLE 138KV' | 262.1816 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 31
OKGE | 'SEMINOLE 345KV' | 507.6 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 31
OKGE | 'SEMINOLE 345KV' | 507.6 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 31
OKGE | 'SOONER 138KV' | 25 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 31
OKGE | 'SOONER 138KV' | 25 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 31
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 31
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 31
OKGE | 'TINKER 5G 138KV' | 62 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 31
OKGE | 'TINKER 5G 138KV' | 62 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 31
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | FPL SWITCH - MOORELAND 138KV CKT 1 OKGE & FPL SWITCH - MOORELAND 138KV CKT 1 WFEC
Limiting Facility: | FPL SWITCH - MOORELAND 138KV CKT 1
Direction: | From->To
Line Outage: | WOODWARD - WOODWARD 69KV CKT 1
Flowgate: | 55785559991547825609611106SH
Date Redispatch Needed: | 6/1/06 - 10/1/06
Season Flowgate Identified: | 2006 Summer Shoulder
Reservation | Relief Amount | Aggregate Relief Amount
1032973 | 20.5028 | 20.5028
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 21
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 21
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 21
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 21
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 21
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 21
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 21
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 21
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 21
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 21
OKGE | 'MCCLAIN 138KV' | 42 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 21
OKGE | 'MCCLAIN 138KV' | 42 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 21
OKGE | 'MUSKOGEE 161KV' | 31 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 21
OKGE | 'MUSKOGEE 161KV' | 166 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 21
OKGE | 'MUSKOGEE 161KV' | 166 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 21
OKGE | 'MUSKOGEE 161KV' | 31 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 21
OKGE | 'MUSKOGEE 345KV' | 20 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 21
OKGE | 'MUSKOGEE 345KV' | 20 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 21
OKGE | 'MUSTANG 138KV' | 365.5 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 21
OKGE | 'MUSTANG 138KV' | 365.5 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 21
OKGE | 'MUSTANG 69KV' | 106 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 21
OKGE | 'MUSTANG 69KV' | 106 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 21
OKGE | 'ONE OAK 345KV' | 236 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 21
OKGE | 'ONE OAK 345KV' | 236 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 21
OKGE | 'REDBUD 345KV' | 421.65 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 21
OKGE | 'REDBUD 345KV' | 460 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 21
OKGE | 'REDBUD 345KV' | 460 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 21
OKGE | 'REDBUD 345KV' | 421.65 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 21
OKGE | 'SEMINOLE 138KV' | 47.215 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 21
OKGE | 'SEMINOLE 138KV' | 47.215 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 21
OKGE | 'SEMINOLE 345KV' | 406.08 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 21
OKGE | 'SEMINOLE 345KV' | 406.08 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 21
OKGE | 'SOONER 138KV' | 25 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 21
OKGE | 'SOONER 138KV' | 25 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 21
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 21
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 21
OKGE | 'TINKER 5G 138KV' | 62 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 21
OKGE | 'TINKER 5G 138KV' | 62 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 21
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | FPL SWITCH - MOORELAND 138KV CKT 1 OKGE & FPL SWITCH - MOORELAND 138KV CKT 1 WFEC
Limiting Facility: | FPL SWITCH - MOORELAND 138KV CKT 1
Direction: | From->To
Line Outage: | WOODWARD - WOODWARD 69KV CKT 1
Flowgate: | 55785559991547825609611306SP
Date Redispatch Needed: | 6/1/06 - 10/1/06
Season Flowgate Identified: | 2006 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1032973 | 11.5251 | 11.5251
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 12
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 12
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 12
OKGE | 'HORSESHOE LAKE 138KV' | 337.7 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 12
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 12
OKGE | 'HORSESHOE LAKE 138KV' | 337.7 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 12
OKGE | 'MCCLAIN 138KV' | 42 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 12
OKGE | 'MCCLAIN 138KV' | 42 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 12
OKGE | 'MUSKOGEE 161KV' | 31 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 12
OKGE | 'MUSKOGEE 161KV' | 166 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 12
OKGE | 'MUSKOGEE 161KV' | 31 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 12
OKGE | 'MUSKOGEE 161KV' | 166 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 12
OKGE | 'MUSTANG 138KV' | 147.3059 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 12
OKGE | 'MUSTANG 138KV' | 147.3059 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 12
OKGE | 'ONE OAK 345KV' | 204 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 12
OKGE | 'ONE OAK 345KV' | 204 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 12
OKGE | 'REDBUD 345KV' | 460 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 12
OKGE | 'REDBUD 345KV' | 421.65 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 12
OKGE | 'REDBUD 345KV' | 460 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 12
OKGE | 'REDBUD 345KV' | 421.65 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 12
OKGE | 'SEMINOLE 138KV' | 17.4764 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 12
OKGE | 'SEMINOLE 138KV' | 17.4764 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 12
OKGE | 'SOONER 138KV' | 25 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 12
OKGE | 'SOONER 138KV' | 25 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 12
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 12
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 12
OKGE | 'TINKER 5G 138KV' | 62 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 12
OKGE | 'TINKER 5G 138KV' | 62 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 12
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | FPL SWITCH - MOORELAND 138KV CKT 1 OKGE & FPL SWITCH - MOORELAND 138KV CKT 1 WFEC
Limiting Facility: | FPL SWITCH - MOORELAND 138KV CKT 1
Direction: | From->To
Line Outage: | DEWEY - IODINE 138KV CKT 1
Flowgate: | 55785559991547875479611107AP
Date Redispatch Needed: | Starting 2007 4/1 - 6/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 April Minimum
Reservation | Relief Amount | Aggregate Relief Amount
1023236 | 1.3679 | 32.3728
1032973 | 31.0048 | 32.3728
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'AES 161KV' | 160 | 3e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97306 | 33
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00022 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97287 | 33
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00022 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97287 | 33
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00022 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97287 | 33
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.00021 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97288 | 33
OKGE | 'MCCLAIN 138KV' | 520 | 0.00036 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97273 | 33
OKGE | 'MUSKOGEE 161KV' | 166 | 4e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97305 | 33
OKGE | 'MUSKOGEE 161KV' | 31 | 4e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97305 | 33
OKGE | 'MUSKOGEE 345KV' | 717.4685 | 5e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97304 | 33
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00036 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97273 | 33
OKGE | 'MUSTANG 69KV' | 106 | 0.0004 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97269 | 33
OKGE | 'ONE OAK 345KV' | 236 | 0.00012 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97297 | 33
OKGE | 'REDBUD 345KV' | 421.65 | 0.00014 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97295 | 33
OKGE | 'REDBUD 345KV' | 900 | 0.00014 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97295 | 33
OKGE | 'SEMINOLE 138KV' | 508.3745 | 0.00019 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.9729 | 33
OKGE | 'SEMINOLE 345KV' | 996.6 | 0.00019 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.9729 | 33
OKGE | 'SMITH COGEN 138KV' | 110 | 0.00034 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97275 | 33
OKGE | 'SOONER 138KV' | 25 | -0.00031 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.9734 | 33
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.00162 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97471 | 33
OKGE | 'TINKER 5G 138KV' | 62 | 0.00025 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97284 | 33
OKGE | 'AES 161KV' | 160 | 3e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81255 | 40
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00022 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81236 | 40
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00022 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81236 | 40
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00022 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81236 | 40
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.00021 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81237 | 40
OKGE | 'MCCLAIN 138KV' | 520 | 0.00036 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81222 | 40
OKGE | 'MUSKOGEE 161KV' | 31 | 4e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81254 | 40
OKGE | 'MUSKOGEE 161KV' | 166 | 4e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81254 | 40
OKGE | 'MUSKOGEE 345KV' | 717.4685 | 5e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81253 | 40
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00036 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81222 | 40
OKGE | 'MUSTANG 69KV' | 106 | 0.0004 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81218 | 40
OKGE | 'ONE OAK 345KV' | 236 | 0.00012 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81246 | 40
OKGE | 'REDBUD 345KV' | 900 | 0.00014 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81244 | 40
OKGE | 'REDBUD 345KV' | 421.65 | 0.00014 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81244 | 40
OKGE | 'SEMINOLE 138KV' | 508.3745 | 0.00019 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81239 | 40
OKGE | 'SEMINOLE 345KV' | 996.6 | 0.00019 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81239 | 40
OKGE | 'SMITH COGEN 138KV' | 110 | 0.00034 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81224 | 40
OKGE | 'SOONER 138KV' | 25 | -0.00031 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81289 | 40
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.00162 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.8142 | 40
OKGE | 'TINKER 5G 138KV' | 62 | 0.00025 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81233 | 40
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | FPL SWITCH - MOORELAND 138KV CKT 1 OKGE & FPL SWITCH - MOORELAND 138KV CKT 1 WFEC
Limiting Facility: | FPL SWITCH - MOORELAND 138KV CKT 1
Direction: | From->To
Line Outage: | DEWEY - IODINE 138KV CKT 1
Flowgate: | 55785559991547875479611107G
Date Redispatch Needed: | Starting 2007 4/1 - 6/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 Spring Peak
Reservation | Relief Amount | Aggregate Relief Amount
1023236 | 0.66189 | 15.6555
1032973 | 14.9936 | 15.6555
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'AES 161KV' | 40 | 3e-05 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.97309 | -0.97306 | 16
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00022 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.97309 | -0.97287 | 16
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00022 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.97309 | -0.97287 | 16
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00022 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.97309 | -0.97287 | 16
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.00022 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.97309 | -0.97287 | 16
OKGE | 'MCCLAIN 138KV' | 42 | 0.00034 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.97309 | -0.97275 | 16
OKGE | 'MUSKOGEE 161KV' | 166 | 3e-05 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.97309 | -0.97306 | 16
OKGE | 'MUSKOGEE 161KV' | 31 | 3e-05 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.97309 | -0.97306 | 16
OKGE | 'MUSKOGEE 345KV' | 20 | 5e-05 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.97309 | -0.97304 | 16
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00036 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.97309 | -0.97273 | 16
OKGE | 'MUSTANG 69KV' | 106 | 0.00041 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.97309 | -0.97268 | 16
OKGE | 'ONE OAK 345KV' | 236 | 0.00012 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.97309 | -0.97297 | 16
OKGE | 'REDBUD 345KV' | 900 | 0.00014 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.97309 | -0.97295 | 16
OKGE | 'REDBUD 345KV' | 421.65 | 0.00014 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.97309 | -0.97295 | 16
OKGE | 'SEMINOLE 138KV' | 401.2314 | 0.00019 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.97309 | -0.9729 | 16
OKGE | 'SEMINOLE 345KV' | 608.1636 | 0.00019 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.97309 | -0.9729 | 16
OKGE | 'SOONER 138KV' | 25 | -0.00031 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.97309 | -0.9734 | 16
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.00162 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.97309 | -0.97471 | 16
OKGE | 'TINKER 5G 138KV' | 62 | 0.00025 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.97309 | -0.97284 | 16
OKGE | 'AES 161KV' | 40 | 3e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81255 | 19
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00022 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81236 | 19
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00022 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81236 | 19
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00022 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81236 | 19
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.00022 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81236 | 19
OKGE | 'MCCLAIN 138KV' | 42 | 0.00034 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81224 | 19
OKGE | 'MUSKOGEE 161KV' | 166 | 3e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81255 | 19
OKGE | 'MUSKOGEE 161KV' | 31 | 3e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81255 | 19
OKGE | 'MUSKOGEE 345KV' | 20 | 5e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81253 | 19
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00036 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81222 | 19
OKGE | 'MUSTANG 69KV' | 106 | 0.00041 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81217 | 19
OKGE | 'ONE OAK 345KV' | 236 | 0.00012 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81246 | 19
OKGE | 'REDBUD 345KV' | 421.65 | 0.00014 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81244 | 19
OKGE | 'REDBUD 345KV' | 900 | 0.00014 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81244 | 19
OKGE | 'SEMINOLE 138KV' | 401.2314 | 0.00019 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81239 | 19
OKGE | 'SEMINOLE 345KV' | 608.1636 | 0.00019 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81239 | 19
OKGE | 'SOONER 138KV' | 25 | -0.00031 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81289 | 19
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.00162 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.8142 | 19
OKGE | 'TINKER 5G 138KV' | 62 | 0.00025 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81233 | 19
WFEC | 'MORLND 138KV' | 320 | -0.02454 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 0.05339 | -0.07793 | 201
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | FPL SWITCH - MOORELAND 138KV CKT 1 OKGE & FPL SWITCH - MOORELAND 138KV CKT 1 WFEC
Limiting Facility: | FPL SWITCH - MOORELAND 138KV CKT 1
Direction: | From->To
Line Outage: | DEWEY - IODINE 138KV CKT 1
Flowgate: | 55785559991547875479611206WP
Date Redispatch Needed: | 12/1/06 - 4/1/07
Season Flowgate Identified: | 2006 Winter Peak
Reservation | Relief Amount | Aggregate Relief Amount
1023236 | 0.36282 | 8.5844
1032973 | 8.2216 | 8.5844
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'AES 161KV' | 10 | 3e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97306 | 9
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | -0.00045 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97354 | 9
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00023 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97286 | 9
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00023 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97286 | 9
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00023 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97286 | 9
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.00022 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97287 | 9
OKGE | 'MCCLAIN 138KV' | 42 | 0.00036 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97273 | 9
OKGE | 'MUSKOGEE 161KV' | 31 | 4e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97305 | 9
OKGE | 'MUSKOGEE 161KV' | 166 | 4e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97305 | 9
OKGE | 'MUSKOGEE 345KV' | 20 | 5e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97304 | 9
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00036 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97273 | 9
OKGE | 'MUSTANG 69KV' | 106 | 0.0004 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97269 | 9
OKGE | 'ONE OAK 345KV' | 336 | 0.00012 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97297 | 9
OKGE | 'REDBUD 345KV' | 421.65 | 0.00014 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97295 | 9
OKGE | 'REDBUD 345KV' | 900 | 0.00014 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97295 | 9
OKGE | 'SEMINOLE 138KV' | 395.2155 | 0.00019 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.9729 | 9
OKGE | 'SEMINOLE 345KV' | 558.5093 | 0.00019 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.9729 | 9
OKGE | 'SOONER 138KV' | 25 | -0.00031 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.9734 | 9
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.00162 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97471 | 9
OKGE | 'TINKER 5G 138KV' | 62 | 0.00025 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97284 | 9
OKGE | 'AES 161KV' | 10 | 3e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81255 | 11
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | -0.00045 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81303 | 11
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00023 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81235 | 11
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00023 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81235 | 11
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00023 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81235 | 11
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.00022 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81236 | 11
OKGE | 'MCCLAIN 138KV' | 42 | 0.00036 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81222 | 11
OKGE | 'MUSKOGEE 161KV' | 31 | 4e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81254 | 11
OKGE | 'MUSKOGEE 161KV' | 166 | 4e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81254 | 11
OKGE | 'MUSKOGEE 345KV' | 20 | 5e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81253 | 11
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00036 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81222 | 11
OKGE | 'MUSTANG 69KV' | 106 | 0.0004 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81218 | 11
OKGE | 'ONE OAK 345KV' | 336 | 0.00012 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81246 | 11
OKGE | 'REDBUD 345KV' | 421.65 | 0.00014 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81244 | 11
OKGE | 'REDBUD 345KV' | 900 | 0.00014 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81244 | 11
OKGE | 'SEMINOLE 138KV' | 395.2155 | 0.00019 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81239 | 11
OKGE | 'SEMINOLE 345KV' | 558.5093 | 0.00019 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81239 | 11
OKGE | 'SOONER 138KV' | 25 | -0.00031 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81289 | 11
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.00162 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.8142 | 11
OKGE | 'TINKER 5G 138KV' | 62 | 0.00025 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81233 | 11
WFEC | 'MORLND 138KV' | 166.1695 | -0.02454 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 0.05339 | -0.07793 | 110
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | FPL SWITCH - MOORELAND 138KV CKT 1 OKGE & FPL SWITCH - MOORELAND 138KV CKT 1 WFEC
Limiting Facility: | FPL SWITCH - MOORELAND 138KV CKT 1
Direction: | From->To
Line Outage: | DEWEY - IODINE 138KV CKT 1
Flowgate: | 55785559991547875479611207FA
Date Redispatch Needed: | Starting 2007 10/1 - 12/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 Fall Peak
Reservation | Relief Amount | Aggregate Relief Amount
1023236 | 0.44841 | 10.606
1032973 | 10.1576 | 10.606
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'CONTINENTAL EMPIRE 138KV' | 64 | -0.00045 | OKGE | 'FPLWND2 34KV' | 102 | 0.97308 | -0.97353 | 11
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00022 | OKGE | 'FPLWND2 34KV' | 102 | 0.97308 | -0.97286 | 11
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00022 | OKGE | 'FPLWND2 34KV' | 102 | 0.97308 | -0.97286 | 11
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00022 | OKGE | 'FPLWND2 34KV' | 102 | 0.97308 | -0.97286 | 11
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.00021 | OKGE | 'FPLWND2 34KV' | 102 | 0.97308 | -0.97287 | 11
OKGE | 'MCCLAIN 138KV' | 42 | 0.00034 | OKGE | 'FPLWND2 34KV' | 102 | 0.97308 | -0.97274 | 11
OKGE | 'MUSKOGEE 161KV' | 31 | 3e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.97308 | -0.97305 | 11
OKGE | 'MUSKOGEE 161KV' | 166 | 3e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.97308 | -0.97305 | 11
OKGE | 'MUSKOGEE 345KV' | 20 | 4e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.97308 | -0.97304 | 11
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00035 | OKGE | 'FPLWND2 34KV' | 102 | 0.97308 | -0.97273 | 11
OKGE | 'MUSTANG 69KV' | 106 | 0.0004 | OKGE | 'FPLWND2 34KV' | 102 | 0.97308 | -0.97268 | 11
OKGE | 'ONE OAK 345KV' | 323 | 0.00013 | OKGE | 'FPLWND2 34KV' | 102 | 0.97308 | -0.97295 | 11
OKGE | 'REDBUD 345KV' | 900 | 0.00014 | OKGE | 'FPLWND2 34KV' | 102 | 0.97308 | -0.97294 | 11
OKGE | 'REDBUD 345KV' | 421.65 | 0.00014 | OKGE | 'FPLWND2 34KV' | 102 | 0.97308 | -0.97294 | 11
OKGE | 'SEMINOLE 138KV' | 34.4273 | 0.00018 | OKGE | 'FPLWND2 34KV' | 102 | 0.97308 | -0.9729 | 11
OKGE | 'SEMINOLE 345KV' | 507.6 | 0.00018 | OKGE | 'FPLWND2 34KV' | 102 | 0.97308 | -0.9729 | 11
OKGE | 'SMITH COGEN 138KV' | 110 | 0.00034 | OKGE | 'FPLWND2 34KV' | 102 | 0.97308 | -0.97274 | 11
OKGE | 'SOONER 138KV' | 25 | -0.00031 | OKGE | 'FPLWND2 34KV' | 102 | 0.97308 | -0.97339 | 11
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.00162 | OKGE | 'FPLWND2 34KV' | 102 | 0.97308 | -0.9747 | 11
OKGE | 'TINKER 5G 138KV' | 62 | 0.00024 | OKGE | 'FPLWND2 34KV' | 102 | 0.97308 | -0.97284 | 11
OKGE | 'CONTINENTAL EMPIRE 138KV' | 64 | -0.00045 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81303 | 13
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00022 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81236 | 13
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00022 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81236 | 13
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00022 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81236 | 13
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.00021 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81237 | 13
OKGE | 'MCCLAIN 138KV' | 42 | 0.00034 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81224 | 13
OKGE | 'MUSKOGEE 161KV' | 166 | 3e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81255 | 13
OKGE | 'MUSKOGEE 161KV' | 31 | 3e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81255 | 13
OKGE | 'MUSKOGEE 345KV' | 20 | 4e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81254 | 13
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00035 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81223 | 13
OKGE | 'MUSTANG 69KV' | 106 | 0.0004 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81218 | 13
OKGE | 'ONE OAK 345KV' | 323 | 0.00013 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81245 | 13
OKGE | 'REDBUD 345KV' | 421.65 | 0.00014 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81244 | 13
OKGE | 'REDBUD 345KV' | 900 | 0.00014 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81244 | 13
OKGE | 'SEMINOLE 138KV' | 34.4273 | 0.00018 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.8124 | 13
OKGE | 'SEMINOLE 345KV' | 507.6 | 0.00018 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.8124 | 13
OKGE | 'SMITH COGEN 138KV' | 110 | 0.00034 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81224 | 13
OKGE | 'SOONER 138KV' | 25 | -0.00031 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81289 | 13
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.00162 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.8142 | 13
OKGE | 'TINKER 5G 138KV' | 62 | 0.00024 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81234 | 13
WFEC | 'MORLND 138KV' | 320 | -0.02454 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 0.05338 | -0.07792 | 136
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | FPL SWITCH - MOORELAND 138KV CKT 1 OKGE & FPL SWITCH - MOORELAND 138KV CKT 1 WFEC
Limiting Facility: | FPL SWITCH - MOORELAND 138KV CKT 1
Direction: | From->To
Line Outage: | DEWEY - IODINE 138KV CKT 1
Flowgate: | 55785559991547875479611207SH
Date Redispatch Needed: | 6/1 - 10/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 Summer Shoulder
Reservation | Relief Amount | Aggregate Relief Amount
1023236 | 0.1 | 0.60832
1032973 | 0.5826 | 0.60832
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00022 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97287 | 1
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00022 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97287 | 1
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00022 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81236 | 1
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00022 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81236 | 1
OKGE | 'MCCLAIN 138KV' | 42 | 0.00034 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97275 | 1
OKGE | 'MCCLAIN 138KV' | 42 | 0.00034 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81224 | 1
OKGE | 'MUSKOGEE 161KV' | 166 | 3e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97306 | 1
OKGE | 'MUSKOGEE 161KV' | 31 | 3e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97306 | 1
OKGE | 'MUSKOGEE 161KV' | 166 | 3e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81255 | 1
OKGE | 'MUSKOGEE 161KV' | 31 | 3e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81255 | 1
OKGE | 'MUSKOGEE 345KV' | 20 | 4e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97305 | 1
OKGE | 'MUSKOGEE 345KV' | 20 | 4e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81254 | 1
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00035 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97274 | 1
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00035 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81223 | 1
OKGE | 'MUSTANG 69KV' | 57.4609 | 0.0004 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97269 | 1
OKGE | 'MUSTANG 69KV' | 57.4609 | 0.0004 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81218 | 1
OKGE | 'ONE OAK 345KV' | 274 | 0.00013 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97296 | 1
OKGE | 'ONE OAK 345KV' | 274 | 0.00013 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81245 | 1
OKGE | 'REDBUD 345KV' | 900 | 0.00014 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97295 | 1
OKGE | 'REDBUD 345KV' | 421.65 | 0.00014 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97295 | 1
OKGE | 'REDBUD 345KV' | 421.65 | 0.00014 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81244 | 1
OKGE | 'REDBUD 345KV' | 900 | 0.00014 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81244 | 1
OKGE | 'SEMINOLE 138KV' | 20.9004 | 0.00018 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97291 | 1
OKGE | 'SEMINOLE 138KV' | 20.9004 | 0.00018 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.8124 | 1
OKGE | 'SOONER 138KV' | 25 | -0.00031 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.9734 | 1
OKGE | 'SOONER 138KV' | 25 | -0.00031 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81289 | 1
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.00162 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97471 | 1
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.00162 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.8142 | 1
OKGE | 'TINKER 5G 138KV' | 62 | 0.00024 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97285 | 1
OKGE | 'TINKER 5G 138KV' | 62 | 0.00024 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81234 | 1
OKGE | 'WOODWARD 24KV' | 9.3 | 0.81258 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.16051 | 4
WFEC | 'MORLND 138KV' | 173.8576 | -0.02454 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 0.05338 | -0.07792 | 8
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | FPL SWITCH - MOORELAND 138KV CKT 1 OKGE & FPL SWITCH - MOORELAND 138KV CKT 1 WFEC
Limiting Facility: | FPL SWITCH - MOORELAND 138KV CKT 1
Direction: | From->To
Line Outage: | DEWEY - IODINE 138KV CKT 1
Flowgate: | 55785559991547875479611207WP
Date Redispatch Needed: | 12/1/07 - 4/1/08
Season Flowgate Identified: | 2007 Winter Peak
Reservation | Relief Amount | Aggregate Relief Amount
1023236 | 0.33168 | 7.8487
1032973 | 7.517 | 7.8487
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'AES 161KV' | 79 | 3e-05 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.97308 | -0.97305 | 8
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00022 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.97308 | -0.97286 | 8
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00022 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.97308 | -0.97286 | 8
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00022 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.97308 | -0.97286 | 8
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.00021 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.97308 | -0.97287 | 8
OKGE | 'MCCLAIN 138KV' | 42 | 0.00034 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.97308 | -0.97274 | 8
OKGE | 'MUSKOGEE 161KV' | 31 | 3e-05 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.97308 | -0.97305 | 8
OKGE | 'MUSKOGEE 161KV' | 166 | 3e-05 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.97308 | -0.97305 | 8
OKGE | 'MUSKOGEE 345KV' | 20 | 4e-05 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.97308 | -0.97304 | 8
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00035 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.97308 | -0.97273 | 8
OKGE | 'MUSTANG 69KV' | 106 | 0.0004 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.97308 | -0.97268 | 8
OKGE | 'ONE OAK 345KV' | 319 | 0.00012 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.97308 | -0.97296 | 8
OKGE | 'REDBUD 345KV' | 900 | 0.00014 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.97308 | -0.97294 | 8
OKGE | 'REDBUD 345KV' | 421.65 | 0.00014 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.97308 | -0.97294 | 8
OKGE | 'SEMINOLE 138KV' | 309.6299 | 0.00018 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.97308 | -0.9729 | 8
OKGE | 'SEMINOLE 345KV' | 507.6 | 0.00018 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.97308 | -0.9729 | 8
OKGE | 'SOONER 138KV' | 25 | -0.00031 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.97308 | -0.97339 | 8
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.00162 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.97308 | -0.9747 | 8
OKGE | 'TINKER 5G 138KV' | 62 | 0.00024 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.97308 | -0.97284 | 8
OKGE | 'AES 161KV' | 79 | 3e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81255 | 10
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00022 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81236 | 10
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00022 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81236 | 10
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00022 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81236 | 10
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.00021 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81237 | 10
OKGE | 'MCCLAIN 138KV' | 42 | 0.00034 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81224 | 10
OKGE | 'MUSKOGEE 161KV' | 31 | 3e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81255 | 10
OKGE | 'MUSKOGEE 161KV' | 166 | 3e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81255 | 10
OKGE | 'MUSKOGEE 345KV' | 20 | 4e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81254 | 10
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00035 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81223 | 10
OKGE | 'MUSTANG 69KV' | 106 | 0.0004 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81218 | 10
OKGE | 'ONE OAK 345KV' | 319 | 0.00012 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81246 | 10
OKGE | 'REDBUD 345KV' | 421.65 | 0.00014 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81244 | 10
OKGE | 'REDBUD 345KV' | 900 | 0.00014 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81244 | 10
OKGE | 'SEMINOLE 138KV' | 309.6299 | 0.00018 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.8124 | 10
OKGE | 'SEMINOLE 345KV' | 507.6 | 0.00018 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.8124 | 10
OKGE | 'SOONER 138KV' | 25 | -0.00031 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81289 | 10
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.00162 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.8142 | 10
OKGE | 'TINKER 5G 138KV' | 62 | 0.00024 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81234 | 10
WFEC | 'MORLND 138KV' | 148.9085 | -0.02454 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 0.05338 | -0.07792 | 101
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | FPL SWITCH - MOORELAND 138KV CKT 1 OKGE & FPL SWITCH - MOORELAND 138KV CKT 1 WFEC
Limiting Facility: | FPL SWITCH - MOORELAND 138KV CKT 1
Direction: | From->To
Line Outage: | IODINE - WOODWARD 138KV CKT 1
Flowgate: | 55785559991547965478511107AP
Date Redispatch Needed: | Starting 2007 4/1 - 6/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 April Minimum
Reservation | Relief Amount | Aggregate Relief Amount
1023236 | 1.4475 | 34.2947
1032973 | 32.8472 | 34.2947
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'AES 161KV' | 160 | 3e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97306 | 35
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00022 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97287 | 35
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00022 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97287 | 35
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00022 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97287 | 35
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.00021 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97288 | 35
OKGE | 'MCCLAIN 138KV' | 520 | 0.00036 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97273 | 35
OKGE | 'MUSKOGEE 161KV' | 166 | 4e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97305 | 35
OKGE | 'MUSKOGEE 161KV' | 31 | 4e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97305 | 35
OKGE | 'MUSKOGEE 345KV' | 717.4685 | 5e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97304 | 35
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00036 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97273 | 35
OKGE | 'MUSTANG 69KV' | 106 | 0.0004 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97269 | 35
OKGE | 'ONE OAK 345KV' | 236 | 0.00012 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97297 | 35
OKGE | 'REDBUD 345KV' | 421.65 | 0.00014 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97295 | 35
OKGE | 'REDBUD 345KV' | 900 | 0.00014 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97295 | 35
OKGE | 'SEMINOLE 138KV' | 508.3745 | 0.00019 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.9729 | 35
OKGE | 'SEMINOLE 345KV' | 996.6 | 0.00019 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.9729 | 35
OKGE | 'SMITH COGEN 138KV' | 110 | 0.00034 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97275 | 35
OKGE | 'SOONER 138KV' | 25 | -0.00031 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.9734 | 35
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.00162 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97471 | 35
OKGE | 'TINKER 5G 138KV' | 62 | 0.00025 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97284 | 35
OKGE | 'AES 161KV' | 160 | 3e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81255 | 42
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00022 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81236 | 42
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00022 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81236 | 42
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00022 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81236 | 42
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.00021 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81237 | 42
OKGE | 'MCCLAIN 138KV' | 520 | 0.00036 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81222 | 42
OKGE | 'MUSKOGEE 161KV' | 31 | 4e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81254 | 42
OKGE | 'MUSKOGEE 161KV' | 166 | 4e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81254 | 42
OKGE | 'MUSKOGEE 345KV' | 717.4685 | 5e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81253 | 42
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00036 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81222 | 42
OKGE | 'MUSTANG 69KV' | 106 | 0.0004 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81218 | 42
OKGE | 'ONE OAK 345KV' | 236 | 0.00012 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81246 | 42
OKGE | 'REDBUD 345KV' | 900 | 0.00014 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81244 | 42
OKGE | 'REDBUD 345KV' | 421.65 | 0.00014 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81244 | 42
OKGE | 'SEMINOLE 138KV' | 508.3745 | 0.00019 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81239 | 42
OKGE | 'SEMINOLE 345KV' | 996.6 | 0.00019 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81239 | 42
OKGE | 'SMITH COGEN 138KV' | 110 | 0.00034 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81224 | 42
OKGE | 'SOONER 138KV' | 25 | -0.00031 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81289 | 42
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.00162 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.8142 | 42
OKGE | 'TINKER 5G 138KV' | 62 | 0.00025 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81233 | 42
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | FPL SWITCH - MOORELAND 138KV CKT 1 OKGE & FPL SWITCH - MOORELAND 138KV CKT 1 WFEC
Limiting Facility: | FPL SWITCH - MOORELAND 138KV CKT 1
Direction: | From->To
Line Outage: | IODINE - WOODWARD 138KV CKT 1
Flowgate: | 55785559991547965478511107FA
Date Redispatch Needed: | Starting 2007 10/1 - 12/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 Fall Peak
Reservation | Relief Amount | Aggregate Relief Amount
1023236 | 0.58794 | 13.9203
1032973 | 13.3324 | 13.9203
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'CONTINENTAL EMPIRE 138KV' | 64 | -0.00045 | OKGE | 'FPLWND2 34KV' | 102 | 0.97308 | -0.97353 | 14
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00022 | OKGE | 'FPLWND2 34KV' | 102 | 0.97308 | -0.97286 | 14
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00022 | OKGE | 'FPLWND2 34KV' | 102 | 0.97308 | -0.97286 | 14
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00022 | OKGE | 'FPLWND2 34KV' | 102 | 0.97308 | -0.97286 | 14
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.00021 | OKGE | 'FPLWND2 34KV' | 102 | 0.97308 | -0.97287 | 14
OKGE | 'MUSKOGEE 161KV' | 31 | 3e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.97308 | -0.97305 | 14
OKGE | 'MUSKOGEE 161KV' | 166 | 3e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.97308 | -0.97305 | 14
OKGE | 'MUSKOGEE 345KV' | 20 | 4e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.97308 | -0.97304 | 14
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00035 | OKGE | 'FPLWND2 34KV' | 102 | 0.97308 | -0.97273 | 14
OKGE | 'MUSTANG 69KV' | 106 | 0.0004 | OKGE | 'FPLWND2 34KV' | 102 | 0.97308 | -0.97268 | 14
OKGE | 'ONE OAK 345KV' | 236 | 0.00013 | OKGE | 'FPLWND2 34KV' | 102 | 0.97308 | -0.97295 | 14
OKGE | 'REDBUD 345KV' | 900 | 0.00014 | OKGE | 'FPLWND2 34KV' | 102 | 0.97308 | -0.97294 | 14
OKGE | 'REDBUD 345KV' | 421.65 | 0.00014 | OKGE | 'FPLWND2 34KV' | 102 | 0.97308 | -0.97294 | 14
OKGE | 'SEMINOLE 138KV' | 99.8037 | 0.00018 | OKGE | 'FPLWND2 34KV' | 102 | 0.97308 | -0.9729 | 14
OKGE | 'SEMINOLE 345KV' | 507.6 | 0.00018 | OKGE | 'FPLWND2 34KV' | 102 | 0.97308 | -0.9729 | 14
OKGE | 'SMITH COGEN 138KV' | 110 | 0.00034 | OKGE | 'FPLWND2 34KV' | 102 | 0.97308 | -0.97274 | 14
OKGE | 'SOONER 138KV' | 25 | -0.00031 | OKGE | 'FPLWND2 34KV' | 102 | 0.97308 | -0.97339 | 14
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.00162 | OKGE | 'FPLWND2 34KV' | 102 | 0.97308 | -0.9747 | 14
OKGE | 'TINKER 5G 138KV' | 62 | 0.00024 | OKGE | 'FPLWND2 34KV' | 102 | 0.97308 | -0.97284 | 14
OKGE | 'CONTINENTAL EMPIRE 138KV' | 64 | -0.00045 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81303 | 17
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00022 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81236 | 17
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00022 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81236 | 17
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00022 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81236 | 17
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.00021 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81237 | 17
OKGE | 'MUSKOGEE 161KV' | 31 | 3e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81255 | 17
OKGE | 'MUSKOGEE 161KV' | 166 | 3e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81255 | 17
OKGE | 'MUSKOGEE 345KV' | 20 | 4e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81254 | 17
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00035 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81223 | 17
OKGE | 'MUSTANG 69KV' | 106 | 0.0004 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81218 | 17
OKGE | 'ONE OAK 345KV' | 236 | 0.00013 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81245 | 17
OKGE | 'REDBUD 345KV' | 900 | 0.00014 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81244 | 17
OKGE | 'REDBUD 345KV' | 421.65 | 0.00014 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81244 | 17
OKGE | 'SEMINOLE 138KV' | 99.8037 | 0.00018 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.8124 | 17
OKGE | 'SEMINOLE 345KV' | 507.6 | 0.00018 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.8124 | 17
OKGE | 'SMITH COGEN 138KV' | 110 | 0.00034 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81224 | 17
OKGE | 'SOONER 138KV' | 25 | -0.00031 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81289 | 17
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.00162 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.8142 | 17
OKGE | 'TINKER 5G 138KV' | 62 | 0.00024 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81234 | 17
WFEC | 'MORLND 138KV' | 320 | -0.02454 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 0.05338 | -0.07792 | 179
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | FPL SWITCH - MOORELAND 138KV CKT 1 OKGE & FPL SWITCH - MOORELAND 138KV CKT 1 WFEC
Limiting Facility: | FPL SWITCH - MOORELAND 138KV CKT 1
Direction: | From->To
Line Outage: | IODINE - WOODWARD 138KV CKT 1
Flowgate: | 55785559991547965478511206WP
Date Redispatch Needed: | 12/1/06 - 4/1/07
Season Flowgate Identified: | 2006 Winter Peak
Reservation | Relief Amount | Aggregate Relief Amount
1023236 | 0.50906 | 12.0579
1032973 | 11.5488 | 12.0579
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'AES 161KV' | 10 | 3e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97306 | 12
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | -0.00045 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97354 | 12
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00023 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97286 | 12
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00023 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97286 | 12
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00023 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97286 | 12
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.00022 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97287 | 12
OKGE | 'MCCLAIN 138KV' | 42 | 0.00036 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97273 | 12
OKGE | 'MUSKOGEE 161KV' | 166 | 4e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97305 | 12
OKGE | 'MUSKOGEE 161KV' | 31 | 4e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97305 | 12
OKGE | 'MUSKOGEE 345KV' | 20 | 5e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97304 | 12
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00036 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97273 | 12
OKGE | 'MUSTANG 69KV' | 106 | 0.0004 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97269 | 12
OKGE | 'ONE OAK 345KV' | 336 | 0.00012 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97297 | 12
OKGE | 'REDBUD 345KV' | 900 | 0.00014 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97295 | 12
OKGE | 'REDBUD 345KV' | 421.65 | 0.00014 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97295 | 12
OKGE | 'SEMINOLE 138KV' | 395.2155 | 0.00019 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.9729 | 12
OKGE | 'SEMINOLE 345KV' | 558.5093 | 0.00019 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.9729 | 12
OKGE | 'SOONER 138KV' | 25 | -0.00031 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.9734 | 12
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.00162 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97471 | 12
OKGE | 'TINKER 5G 138KV' | 62 | 0.00025 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97284 | 12
OKGE | 'AES 161KV' | 10 | 3e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81255 | 15
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | -0.00045 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81303 | 15
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00023 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81235 | 15
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00023 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81235 | 15
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00023 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81235 | 15
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.00022 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81236 | 15
OKGE | 'MCCLAIN 138KV' | 42 | 0.00036 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81222 | 15
OKGE | 'MUSKOGEE 161KV' | 166 | 4e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81254 | 15
OKGE | 'MUSKOGEE 161KV' | 31 | 4e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81254 | 15
OKGE | 'MUSKOGEE 345KV' | 20 | 5e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81253 | 15
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00036 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81222 | 15
OKGE | 'MUSTANG 69KV' | 106 | 0.0004 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81218 | 15
OKGE | 'ONE OAK 345KV' | 336 | 0.00012 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81246 | 15
OKGE | 'REDBUD 345KV' | 900 | 0.00014 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81244 | 15
OKGE | 'REDBUD 345KV' | 421.65 | 0.00014 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81244 | 15
OKGE | 'SEMINOLE 138KV' | 395.2155 | 0.00019 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81239 | 15
OKGE | 'SEMINOLE 345KV' | 558.5093 | 0.00019 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81239 | 15
OKGE | 'SOONER 138KV' | 25 | -0.00031 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81289 | 15
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.00162 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.8142 | 15
OKGE | 'TINKER 5G 138KV' | 62 | 0.00025 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81233 | 15
WFEC | 'MORLND 138KV' | 166.1695 | -0.02454 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 0.05339 | -0.07793 | 155
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | FPL SWITCH - MOORELAND 138KV CKT 1 OKGE & FPL SWITCH - MOORELAND 138KV CKT 1 WFEC
Limiting Facility: | FPL SWITCH - MOORELAND 138KV CKT 1
Direction: | From->To
Line Outage: | IODINE - WOODWARD 138KV CKT 1
Flowgate: | 55785559991547965478511207SH
Date Redispatch Needed: | 6/1 - 10/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 Summer Shoulder
Reservation | Relief Amount | Aggregate Relief Amount
1023236 | 0.19181 | 4.5414
1032973 | 4.3496 | 4.5414
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00022 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97287 | 5
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00022 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97287 | 5
OKGE | 'MCCLAIN 138KV' | 42 | 0.00034 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97275 | 5
OKGE | 'MUSKOGEE 161KV' | 166 | 3e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97306 | 5
OKGE | 'MUSKOGEE 161KV' | 31 | 3e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97306 | 5
OKGE | 'MUSKOGEE 345KV' | 20 | 4e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97305 | 5
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00035 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97274 | 5
OKGE | 'MUSTANG 69KV' | 57.4609 | 0.0004 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97269 | 5
OKGE | 'ONE OAK 345KV' | 274 | 0.00013 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97296 | 5
OKGE | 'REDBUD 345KV' | 900 | 0.00014 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97295 | 5
OKGE | 'REDBUD 345KV' | 421.65 | 0.00014 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97295 | 5
OKGE | 'SEMINOLE 138KV' | 20.9004 | 0.00018 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97291 | 5
OKGE | 'SOONER 138KV' | 25 | -0.00031 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.9734 | 5
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.00162 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97471 | 5
OKGE | 'TINKER 5G 138KV' | 62 | 0.00024 | OKGE | 'FPLWND2 34KV' | 102 | 0.97309 | -0.97285 | 5
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00022 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81236 | 6
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00022 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81236 | 6
OKGE | 'MCCLAIN 138KV' | 42 | 0.00034 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81224 | 6
OKGE | 'MUSKOGEE 161KV' | 31 | 3e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81255 | 6
OKGE | 'MUSKOGEE 161KV' | 166 | 3e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81255 | 6
OKGE | 'MUSKOGEE 345KV' | 20 | 4e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81254 | 6
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00035 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81223 | 6
OKGE | 'MUSTANG 69KV' | 57.4609 | 0.0004 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81218 | 6
OKGE | 'ONE OAK 345KV' | 274 | 0.00013 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81245 | 6
OKGE | 'REDBUD 345KV' | 421.65 | 0.00014 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81244 | 6
OKGE | 'REDBUD 345KV' | 900 | 0.00014 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81244 | 6
OKGE | 'SEMINOLE 138KV' | 20.9004 | 0.00018 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.8124 | 6
OKGE | 'SOONER 138KV' | 25 | -0.00031 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81289 | 6
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.00162 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.8142 | 6
OKGE | 'TINKER 5G 138KV' | 62 | 0.00024 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81234 | 6
WFEC | 'MORLND 138KV' | 173.8576 | -0.02454 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 0.05338 | -0.07792 | 58
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | FPL SWITCH - MOORELAND 138KV CKT 1 OKGE & FPL SWITCH - MOORELAND 138KV CKT 1 WFEC
Limiting Facility: | FPL SWITCH - MOORELAND 138KV CKT 1
Direction: | From->To
Line Outage: | IODINE - WOODWARD 138KV CKT 1
Flowgate: | 55785559991547965478511207WP
Date Redispatch Needed: | 12/1/07 - 4/1/08
Season Flowgate Identified: | 2007 Winter Peak
Reservation | Relief Amount | Aggregate Relief Amount
1023236 | 0.47764 | 11.3149
1032973 | 10.8372 | 11.3149
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'AES 161KV' | 79 | 3e-05 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.97308 | -0.97305 | 12
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00022 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.97308 | -0.97286 | 12
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00022 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.97308 | -0.97286 | 12
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00022 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.97308 | -0.97286 | 12
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.00021 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.97308 | -0.97287 | 12
OKGE | 'MCCLAIN 138KV' | 42 | 0.00034 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.97308 | -0.97274 | 12
OKGE | 'MUSKOGEE 161KV' | 31 | 3e-05 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.97308 | -0.97305 | 12
OKGE | 'MUSKOGEE 161KV' | 166 | 3e-05 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.97308 | -0.97305 | 12
OKGE | 'MUSKOGEE 345KV' | 20 | 4e-05 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.97308 | -0.97304 | 12
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00035 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.97308 | -0.97273 | 12
OKGE | 'MUSTANG 69KV' | 106 | 0.0004 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.97308 | -0.97268 | 12
OKGE | 'ONE OAK 345KV' | 319 | 0.00012 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.97308 | -0.97296 | 12
OKGE | 'REDBUD 345KV' | 900 | 0.00014 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.97308 | -0.97294 | 12
OKGE | 'REDBUD 345KV' | 421.65 | 0.00014 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.97308 | -0.97294 | 12
OKGE | 'SEMINOLE 138KV' | 309.6299 | 0.00018 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.97308 | -0.9729 | 12
OKGE | 'SEMINOLE 345KV' | 507.6 | 0.00018 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.97308 | -0.9729 | 12
OKGE | 'SOONER 138KV' | 25 | -0.00031 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.97308 | -0.97339 | 12
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.00162 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.97308 | -0.9747 | 12
OKGE | 'TINKER 5G 138KV' | 62 | 0.00024 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.97308 | -0.97284 | 12
OKGE | 'AES 161KV' | 79 | 3e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81255 | 14
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00022 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81236 | 14
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00022 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81236 | 14
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00022 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81236 | 14
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.00021 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81237 | 14
OKGE | 'MCCLAIN 138KV' | 42 | 0.00034 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81224 | 14
OKGE | 'MUSKOGEE 161KV' | 166 | 3e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81255 | 14
OKGE | 'MUSKOGEE 161KV' | 31 | 3e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81255 | 14
OKGE | 'MUSKOGEE 345KV' | 20 | 4e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81254 | 14
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00035 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81223 | 14
OKGE | 'MUSTANG 69KV' | 106 | 0.0004 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81218 | 14
OKGE | 'ONE OAK 345KV' | 319 | 0.00012 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81246 | 14
OKGE | 'REDBUD 345KV' | 900 | 0.00014 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81244 | 14
OKGE | 'REDBUD 345KV' | 421.65 | 0.00014 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81244 | 14
OKGE | 'SEMINOLE 138KV' | 309.6299 | 0.00018 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.8124 | 14
OKGE | 'SEMINOLE 345KV' | 507.6 | 0.00018 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.8124 | 14
OKGE | 'SOONER 138KV' | 25 | -0.00031 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81289 | 14
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.00162 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.8142 | 14
OKGE | 'TINKER 5G 138KV' | 62 | 0.00024 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81234 | 14
WFEC | 'MORLND 138KV' | 148.9085 | -0.02454 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 0.05338 | -0.07792 | 145
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | FPL SWITCH - MOORELAND 138KV CKT 1 OKGE & FPL SWITCH - MOORELAND 138KV CKT 1 WFEC
Limiting Facility: | FPL SWITCH - MOORELAND 138KV CKT 1
Direction: | From->To
Line Outage: | IODINE - WOODWARD 138KV CKT 1
Flowgate: | 55785559991547965478511407G
Date Redispatch Needed: | Starting 2007 4/1 - 6/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 Spring Peak
Reservation | Relief Amount | Aggregate Relief Amount
1023236 | 0.79011 | 18.707
1032973 | 17.9169 | 18.707
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'AES 161KV' | 40 | 3e-05 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.97309 | -0.97306 | 19
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00022 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.97309 | -0.97287 | 19
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00022 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.97309 | -0.97287 | 19
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00022 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.97309 | -0.97287 | 19
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.00022 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.97309 | -0.97287 | 19
OKGE | 'MCCLAIN 138KV' | 42 | 0.00034 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.97309 | -0.97275 | 19
OKGE | 'MUSKOGEE 161KV' | 31 | 3e-05 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.97309 | -0.97306 | 19
OKGE | 'MUSKOGEE 161KV' | 166 | 3e-05 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.97309 | -0.97306 | 19
OKGE | 'MUSKOGEE 345KV' | 20 | 5e-05 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.97309 | -0.97304 | 19
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00036 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.97309 | -0.97273 | 19
OKGE | 'MUSTANG 69KV' | 106 | 0.00041 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.97309 | -0.97268 | 19
OKGE | 'ONE OAK 345KV' | 319 | 0.00012 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.97309 | -0.97297 | 19
OKGE | 'REDBUD 345KV' | 421.65 | 0.00014 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.97309 | -0.97295 | 19
OKGE | 'REDBUD 345KV' | 900 | 0.00014 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.97309 | -0.97295 | 19
OKGE | 'SEMINOLE 138KV' | 404.9767 | 0.00019 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.97309 | -0.9729 | 19
OKGE | 'SEMINOLE 345KV' | 572.6229 | 0.00019 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.97309 | -0.9729 | 19
OKGE | 'SOONER 138KV' | 25 | -0.00031 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.97309 | -0.9734 | 19
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.00162 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.97309 | -0.97471 | 19
OKGE | 'TINKER 5G 138KV' | 62 | 0.00025 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.97309 | -0.97284 | 19
OKGE | 'AES 161KV' | 40 | 3e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81255 | 23
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00022 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81236 | 23
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00022 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81236 | 23
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00022 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81236 | 23
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.00022 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81236 | 23
OKGE | 'MCCLAIN 138KV' | 42 | 0.00034 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81224 | 23
OKGE | 'MUSKOGEE 161KV' | 31 | 3e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81255 | 23
OKGE | 'MUSKOGEE 161KV' | 166 | 3e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81255 | 23
OKGE | 'MUSKOGEE 345KV' | 20 | 5e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81253 | 23
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00036 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81222 | 23
OKGE | 'MUSTANG 69KV' | 106 | 0.00041 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81217 | 23
OKGE | 'ONE OAK 345KV' | 319 | 0.00012 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81246 | 23
OKGE | 'REDBUD 345KV' | 900 | 0.00014 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81244 | 23
OKGE | 'REDBUD 345KV' | 421.65 | 0.00014 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81244 | 23
OKGE | 'SEMINOLE 138KV' | 404.9767 | 0.00019 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81239 | 23
OKGE | 'SEMINOLE 345KV' | 572.6229 | 0.00019 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81239 | 23
OKGE | 'SOONER 138KV' | 25 | -0.00031 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81289 | 23
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.00162 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.8142 | 23
OKGE | 'TINKER 5G 138KV' | 62 | 0.00025 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.81258 | -0.81233 | 23
WFEC | 'MORLND 138KV' | 320 | -0.02454 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 0.05339 | -0.07793 | 240
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | FPL SWITCH - MOORELAND 138KV CKT 1 OKGE & FPL SWITCH - MOORELAND 138KV CKT 1 WFEC
Limiting Facility: | FPL SWITCH - MOORELAND 138KV CKT 1
Direction: | From->To
Line Outage: | FT SUPPLY - IODINE 138KV CKT 1
Flowgate: | 55785559991559205595711207AP
Date Redispatch Needed: | Starting 2007 4/1 - 6/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 April Minimum
Reservation | Relief Amount | Aggregate Relief Amount
1023236 | 4.3356 | 19.152
1032973 | 14.8164 | 19.152
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.01423 | OKGE | 'FPLWND2 34KV' | 102 | 0.88636 | -0.90059 | 21
OKGE | 'AES 161KV' | 160 | 0.00036 | OKGE | 'FPLWND2 34KV' | 102 | 0.88636 | -0.886 | 22
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00236 | OKGE | 'FPLWND2 34KV' | 102 | 0.88636 | -0.884 | 22
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00236 | OKGE | 'FPLWND2 34KV' | 102 | 0.88636 | -0.884 | 22
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00236 | OKGE | 'FPLWND2 34KV' | 102 | 0.88636 | -0.884 | 22
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.00227 | OKGE | 'FPLWND2 34KV' | 102 | 0.88636 | -0.88409 | 22
OKGE | 'MCCLAIN 138KV' | 520 | 0.00378 | OKGE | 'FPLWND2 34KV' | 102 | 0.88636 | -0.88258 | 22
OKGE | 'MUSKOGEE 161KV' | 166 | 0.00042 | OKGE | 'FPLWND2 34KV' | 102 | 0.88636 | -0.88594 | 22
OKGE | 'MUSKOGEE 161KV' | 31 | 0.00042 | OKGE | 'FPLWND2 34KV' | 102 | 0.88636 | -0.88594 | 22
OKGE | 'MUSKOGEE 345KV' | 714.519 | 0.00053 | OKGE | 'FPLWND2 34KV' | 102 | 0.88636 | -0.88583 | 22
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00388 | OKGE | 'FPLWND2 34KV' | 102 | 0.88636 | -0.88248 | 22
OKGE | 'MUSTANG 69KV' | 106 | 0.00421 | OKGE | 'FPLWND2 34KV' | 102 | 0.88636 | -0.88215 | 22
OKGE | 'ONE OAK 345KV' | 336 | 0.00153 | OKGE | 'FPLWND2 34KV' | 102 | 0.88636 | -0.88483 | 22
OKGE | 'REDBUD 345KV' | 421.65 | 0.0016 | OKGE | 'FPLWND2 34KV' | 102 | 0.88636 | -0.88476 | 22
OKGE | 'REDBUD 345KV' | 900 | 0.0016 | OKGE | 'FPLWND2 34KV' | 102 | 0.88636 | -0.88476 | 22
OKGE | 'SEMINOLE 138KV' | 507.6138 | 0.00182 | OKGE | 'FPLWND2 34KV' | 102 | 0.88636 | -0.88454 | 22
OKGE | 'SEMINOLE 345KV' | 996.6 | 0.00189 | OKGE | 'FPLWND2 34KV' | 102 | 0.88636 | -0.88447 | 22
OKGE | 'SMITH COGEN 138KV' | 110 | 0.00368 | OKGE | 'FPLWND2 34KV' | 102 | 0.88636 | -0.88268 | 22
OKGE | 'SOONER 138KV' | 25 | -0.0024 | OKGE | 'FPLWND2 34KV' | 102 | 0.88636 | -0.88876 | 22
OKGE | 'TINKER 5G 138KV' | 62 | 0.00256 | OKGE | 'FPLWND2 34KV' | 102 | 0.88636 | -0.8838 | 22
OKGE | 'AES 161KV' | 160 | 0.00036 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.63019 | -0.62983 | 30
OKGE | 'MUSKOGEE 161KV' | 166 | 0.00042 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.63019 | -0.62977 | 30
OKGE | 'MUSKOGEE 161KV' | 31 | 0.00042 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.63019 | -0.62977 | 30
OKGE | 'MUSKOGEE 345KV' | 714.519 | 0.00053 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.63019 | -0.62966 | 30
OKGE | 'ONE OAK 345KV' | 336 | 0.00153 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.63019 | -0.62866 | 30
OKGE | 'REDBUD 345KV' | 421.65 | 0.0016 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.63019 | -0.62859 | 30
OKGE | 'REDBUD 345KV' | 900 | 0.0016 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.63019 | -0.62859 | 30
OKGE | 'SEMINOLE 138KV' | 507.6138 | 0.00182 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.63019 | -0.62837 | 30
OKGE | 'SEMINOLE 345KV' | 996.6 | 0.00189 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.63019 | -0.6283 | 30
OKGE | 'SOONER 138KV' | 25 | -0.0024 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.63019 | -0.63259 | 30
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.01423 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.63019 | -0.64442 | 30
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00236 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.63019 | -0.62783 | 31
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00236 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.63019 | -0.62783 | 31
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00236 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.63019 | -0.62783 | 31
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.00227 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.63019 | -0.62792 | 31
OKGE | 'MCCLAIN 138KV' | 520 | 0.00378 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.63019 | -0.62641 | 31
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00388 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.63019 | -0.62631 | 31
OKGE | 'MUSTANG 69KV' | 106 | 0.00421 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.63019 | -0.62598 | 31
OKGE | 'SMITH COGEN 138KV' | 110 | 0.00368 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.63019 | -0.62651 | 31
OKGE | 'TINKER 5G 138KV' | 62 | 0.00256 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.63019 | -0.62763 | 31
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | FPL SWITCH - MOORELAND 138KV CKT 1 OKGE & FPL SWITCH - MOORELAND 138KV CKT 1 WFEC
Limiting Facility: | FPL SWITCH - MOORELAND 138KV CKT 1
Direction: | From->To
Line Outage: | VICI - WOODWARD 69KV CKT 1
Flowgate: | 55785559991560825609611106FA
Date Redispatch Needed: | 10/1/06 - 12/1/06
Season Flowgate Identified: | 2006 Fall Peak
Reservation | Relief Amount | Aggregate Relief Amount
1032973 | 16.6768 | 16.6768
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | 0.00026 | OKGE | 'FPLWND2 34KV' | 102 | 0.99327 | -0.99301 | 17
OKGE | 'HORSESHOE LAKE 138KV' | 380 | -3e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.99327 | -0.9933 | 17
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | -3e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.99327 | -0.9933 | 17
OKGE | 'HORSESHOE LAKE 138KV' | 91 | -3e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.99327 | -0.9933 | 17
OKGE | 'HORSESHOE LAKE 69KV' | 16 | -3e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.99327 | -0.9933 | 17
OKGE | 'MCCLAIN 138KV' | 42 | -7e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.99327 | -0.99334 | 17
OKGE | 'MUSKOGEE 161KV' | 166 | 1e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.99327 | -0.99326 | 17
OKGE | 'MUSKOGEE 161KV' | 31 | 1e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.99327 | -0.99326 | 17
OKGE | 'MUSKOGEE 345KV' | 20 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 0.99327 | -0.99327 | 17
OKGE | 'MUSTANG 138KV' | 365.5 | -6e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.99327 | -0.99333 | 17
OKGE | 'MUSTANG 69KV' | 106 | -7e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.99327 | -0.99334 | 17
OKGE | 'ONE OAK 345KV' | 236 | 1e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.99327 | -0.99326 | 17
OKGE | 'REDBUD 345KV' | 421.65 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 0.99327 | -0.99327 | 17
OKGE | 'REDBUD 345KV' | 900 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 0.99327 | -0.99327 | 17
OKGE | 'SEMINOLE 138KV' | 262.1816 | -4e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.99327 | -0.99331 | 17
OKGE | 'SEMINOLE 345KV' | 507.6 | -3e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.99327 | -0.9933 | 17
OKGE | 'SOONER 138KV' | 25 | 0.00019 | OKGE | 'FPLWND2 34KV' | 102 | 0.99327 | -0.99308 | 17
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | 0.00121 | OKGE | 'FPLWND2 34KV' | 102 | 0.99327 | -0.99206 | 17
OKGE | 'TINKER 5G 138KV' | 62 | -4e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.99327 | -0.99331 | 17
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | 0.00026 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.84686 | -0.8466 | 20
OKGE | 'HORSESHOE LAKE 138KV' | 91 | -3e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.84686 | -0.84689 | 20
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | -3e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.84686 | -0.84689 | 20
OKGE | 'HORSESHOE LAKE 138KV' | 380 | -3e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.84686 | -0.84689 | 20
OKGE | 'HORSESHOE LAKE 69KV' | 16 | -3e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.84686 | -0.84689 | 20
OKGE | 'MCCLAIN 138KV' | 42 | -7e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.84686 | -0.84693 | 20
OKGE | 'MUSKOGEE 161KV' | 166 | 1e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.84686 | -0.84685 | 20
OKGE | 'MUSKOGEE 161KV' | 31 | 1e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.84686 | -0.84685 | 20
OKGE | 'MUSKOGEE 345KV' | 20 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.84686 | -0.84686 | 20
OKGE | 'MUSTANG 138KV' | 365.5 | -6e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.84686 | -0.84692 | 20
OKGE | 'MUSTANG 69KV' | 106 | -7e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.84686 | -0.84693 | 20
OKGE | 'ONE OAK 345KV' | 236 | 1e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.84686 | -0.84685 | 20
OKGE | 'REDBUD 345KV' | 421.65 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.84686 | -0.84686 | 20
OKGE | 'REDBUD 345KV' | 900 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.84686 | -0.84686 | 20
OKGE | 'SEMINOLE 138KV' | 262.1816 | -4e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.84686 | -0.8469 | 20
OKGE | 'SEMINOLE 345KV' | 507.6 | -3e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.84686 | -0.84689 | 20
OKGE | 'SOONER 138KV' | 25 | 0.00019 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.84686 | -0.84667 | 20
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | 0.00121 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.84686 | -0.84565 | 20
OKGE | 'TINKER 5G 138KV' | 62 | -4e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.84686 | -0.8469 | 20
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | FPL SWITCH - MOORELAND 138KV CKT 1 OKGE & FPL SWITCH - MOORELAND 138KV CKT 1 WFEC
Limiting Facility: | FPL SWITCH - MOORELAND 138KV CKT 1
Direction: | From->To
Line Outage: | VICI - WOODWARD 69KV CKT 1
Flowgate: | 55785559991560825609611206SH
Date Redispatch Needed: | 6/1/06 - 10/1/06
Season Flowgate Identified: | 2006 Summer Shoulder
Reservation | Relief Amount | Aggregate Relief Amount
1032973 | 7.9549 | 7.9549
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | 0.00026 | OKGE | 'FPLWND2 34KV' | 102 | 0.99327 | -0.99301 | 8
OKGE | 'HORSESHOE LAKE 138KV' | 380 | -3e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.99327 | -0.9933 | 8
OKGE | 'HORSESHOE LAKE 138KV' | 91 | -3e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.99327 | -0.9933 | 8
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | -3e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.99327 | -0.9933 | 8
OKGE | 'HORSESHOE LAKE 69KV' | 16 | -3e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.99327 | -0.9933 | 8
OKGE | 'MCCLAIN 138KV' | 42 | -7e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.99327 | -0.99334 | 8
OKGE | 'MUSKOGEE 161KV' | 166 | 1e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.99327 | -0.99326 | 8
OKGE | 'MUSKOGEE 161KV' | 31 | 1e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.99327 | -0.99326 | 8
OKGE | 'MUSKOGEE 345KV' | 20 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 0.99327 | -0.99327 | 8
OKGE | 'MUSTANG 138KV' | 365.5 | -6e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.99327 | -0.99333 | 8
OKGE | 'MUSTANG 69KV' | 106 | -7e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.99327 | -0.99334 | 8
OKGE | 'ONE OAK 345KV' | 293 | 1e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.99327 | -0.99326 | 8
OKGE | 'REDBUD 345KV' | 253 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 0.99327 | -0.99327 | 8
OKGE | 'REDBUD 345KV' | 421.65 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 0.99327 | -0.99327 | 8
OKGE | 'SEMINOLE 138KV' | 34.1504 | -4e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.99327 | -0.99331 | 8
OKGE | 'SEMINOLE 345KV' | 385.6923 | -3e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.99327 | -0.9933 | 8
OKGE | 'SOONER 138KV' | 25 | 0.00019 | OKGE | 'FPLWND2 34KV' | 102 | 0.99327 | -0.99308 | 8
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | 0.00121 | OKGE | 'FPLWND2 34KV' | 102 | 0.99327 | -0.99206 | 8
OKGE | 'TINKER 5G 138KV' | 62 | -4e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.99327 | -0.99331 | 8
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | 0.00026 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.84686 | -0.8466 | 9
OKGE | 'HORSESHOE LAKE 138KV' | 91 | -3e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.84686 | -0.84689 | 9
OKGE | 'HORSESHOE LAKE 138KV' | 380 | -3e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.84686 | -0.84689 | 9
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | -3e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.84686 | -0.84689 | 9
OKGE | 'HORSESHOE LAKE 69KV' | 16 | -3e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.84686 | -0.84689 | 9
OKGE | 'MCCLAIN 138KV' | 42 | -7e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.84686 | -0.84693 | 9
OKGE | 'MUSKOGEE 161KV' | 31 | 1e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.84686 | -0.84685 | 9
OKGE | 'MUSKOGEE 161KV' | 166 | 1e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.84686 | -0.84685 | 9
OKGE | 'MUSKOGEE 345KV' | 20 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.84686 | -0.84686 | 9
OKGE | 'MUSTANG 138KV' | 365.5 | -6e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.84686 | -0.84692 | 9
OKGE | 'MUSTANG 69KV' | 106 | -7e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.84686 | -0.84693 | 9
OKGE | 'ONE OAK 345KV' | 293 | 1e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.84686 | -0.84685 | 9
OKGE | 'REDBUD 345KV' | 421.65 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.84686 | -0.84686 | 9
OKGE | 'REDBUD 345KV' | 253 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.84686 | -0.84686 | 9
OKGE | 'SEMINOLE 138KV' | 34.1504 | -4e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.84686 | -0.8469 | 9
OKGE | 'SEMINOLE 345KV' | 385.6923 | -3e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.84686 | -0.84689 | 9
OKGE | 'SOONER 138KV' | 25 | 0.00019 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.84686 | -0.84667 | 9
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | 0.00121 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.84686 | -0.84565 | 9
OKGE | 'TINKER 5G 138KV' | 62 | -4e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.84686 | -0.8469 | 9
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | FPL SWITCH - MOORELAND 138KV CKT 1 OKGE & FPL SWITCH - MOORELAND 138KV CKT 1 WFEC
Limiting Facility: | FPL SWITCH - MOORELAND 138KV CKT 1
Direction: | From->To
Line Outage: | WOODWARD (WOODWRD2) 138/69/13.2KV TRANSFORMER CKT 1
Flowgate: | 55785559991WOODODWRD24211106FA
Date Redispatch Needed: | 10/1/06 - 12/1/06
Season Flowgate Identified: | 2006 Fall Peak
Reservation | Relief Amount | Aggregate Relief Amount
1032973 | 66.0516 | 66.0516
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 66
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 66
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 66
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 66
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 66
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 66
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 66
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 66
OKGE | 'MCCLAIN 138KV' | 42 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 66
OKGE | 'MCCLAIN 138KV' | 42 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 66
OKGE | 'MUSKOGEE 161KV' | 166 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 66
OKGE | 'MUSKOGEE 161KV' | 31 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 66
OKGE | 'MUSKOGEE 161KV' | 166 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 66
OKGE | 'MUSKOGEE 161KV' | 31 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 66
OKGE | 'MUSTANG 138KV' | 365.5 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 66
OKGE | 'MUSTANG 138KV' | 365.5 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 66
OKGE | 'MUSTANG 69KV' | 106 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 66
OKGE | 'MUSTANG 69KV' | 106 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 66
OKGE | 'ONE OAK 345KV' | 236 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 66
OKGE | 'ONE OAK 345KV' | 236 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 66
OKGE | 'REDBUD 345KV' | 900 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 66
OKGE | 'REDBUD 345KV' | 421.65 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 66
OKGE | 'REDBUD 345KV' | 900 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 66
OKGE | 'REDBUD 345KV' | 421.65 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 66
OKGE | 'SEMINOLE 138KV' | 262.1816 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 66
OKGE | 'SEMINOLE 138KV' | 262.1816 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 66
OKGE | 'SEMINOLE 345KV' | 507.6 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 66
OKGE | 'SEMINOLE 345KV' | 507.6 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 66
OKGE | 'SOONER 138KV' | 25 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 66
OKGE | 'SOONER 138KV' | 25 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 66
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 66
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 66
OKGE | 'TINKER 5G 138KV' | 62 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 66
OKGE | 'TINKER 5G 138KV' | 62 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 66
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | FPL SWITCH - MOORELAND 138KV CKT 1 OKGE & FPL SWITCH - MOORELAND 138KV CKT 1 WFEC
Limiting Facility: | FPL SWITCH - MOORELAND 138KV CKT 1
Direction: | From->To
Line Outage: | WOODWARD (WOODWRD2) 138/69/13.2KV TRANSFORMER CKT 1
Flowgate: | 55785559991WOODODWRD24211206SH
Date Redispatch Needed: | 6/1/06 - 10/1/06
Season Flowgate Identified: | 2006 Summer Shoulder
Reservation | Relief Amount | Aggregate Relief Amount
1032973 | 64.6108 | 64.6108
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 65
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 65
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 65
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 65
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 65
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 65
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 65
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 65
OKGE | 'MCCLAIN 138KV' | 42 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 65
OKGE | 'MCCLAIN 138KV' | 42 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 65
OKGE | 'MUSKOGEE 161KV' | 31 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 65
OKGE | 'MUSKOGEE 161KV' | 166 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 65
OKGE | 'MUSKOGEE 161KV' | 166 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 65
OKGE | 'MUSKOGEE 161KV' | 31 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 65
OKGE | 'MUSTANG 138KV' | 365.5 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 65
OKGE | 'MUSTANG 138KV' | 365.5 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 65
OKGE | 'MUSTANG 69KV' | 106 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 65
OKGE | 'MUSTANG 69KV' | 106 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 65
OKGE | 'ONE OAK 345KV' | 293 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 65
OKGE | 'ONE OAK 345KV' | 293 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 65
OKGE | 'REDBUD 345KV' | 421.65 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 65
OKGE | 'REDBUD 345KV' | 253 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 65
OKGE | 'REDBUD 345KV' | 421.65 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 65
OKGE | 'REDBUD 345KV' | 253 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 65
OKGE | 'SEMINOLE 138KV' | 34.1504 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 65
OKGE | 'SEMINOLE 138KV' | 34.1504 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 65
OKGE | 'SEMINOLE 345KV' | 385.6923 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 65
OKGE | 'SEMINOLE 345KV' | 385.6923 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 65
OKGE | 'SOONER 138KV' | 25 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 65
OKGE | 'SOONER 138KV' | 25 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 65
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 65
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 65
OKGE | 'TINKER 5G 138KV' | 62 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 65
OKGE | 'TINKER 5G 138KV' | 62 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 65
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | FPL SWITCH - MOORELAND 138KV CKT 1 OKGE & FPL SWITCH - MOORELAND 138KV CKT 1 WFEC
Limiting Facility: | FPL SWITCH - MOORELAND 138KV CKT 1
Direction: | From->To
Line Outage: | WOODWARD (WOODWRD2) 138/69/13.2KV TRANSFORMER CKT 1
Flowgate: | 55785559991WOODODWRD24211206SP
Date Redispatch Needed: | 6/1/06 - 10/1/06
Season Flowgate Identified: | 2006 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1032973 | 63.2063 | 63.2063
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 63
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 63
OKGE | 'HORSESHOE LAKE 138KV' | 337.7 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 63
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 63
OKGE | 'HORSESHOE LAKE 138KV' | 337.7 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 63
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 63
OKGE | 'MCCLAIN 138KV' | 42 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 63
OKGE | 'MCCLAIN 138KV' | 42 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 63
OKGE | 'MUSKOGEE 161KV' | 166 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 63
OKGE | 'MUSKOGEE 161KV' | 31 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 63
OKGE | 'MUSKOGEE 161KV' | 166 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 63
OKGE | 'MUSKOGEE 161KV' | 31 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 63
OKGE | 'MUSTANG 138KV' | 142.3459 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 63
OKGE | 'MUSTANG 138KV' | 142.3459 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 63
OKGE | 'ONE OAK 345KV' | 261 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 63
OKGE | 'ONE OAK 345KV' | 261 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 63
OKGE | 'REDBUD 345KV' | 253 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 63
OKGE | 'REDBUD 345KV' | 421.65 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 63
OKGE | 'REDBUD 345KV' | 253 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 63
OKGE | 'REDBUD 345KV' | 421.65 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 63
OKGE | 'SEMINOLE 138KV' | 21.7803 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 63
OKGE | 'SEMINOLE 138KV' | 21.7803 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 63
OKGE | 'SOONER 138KV' | 25 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 63
OKGE | 'SOONER 138KV' | 25 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 63
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 63
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 63
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | FPL SWITCH - MOORELAND 138KV CKT 1 OKGE & FPL SWITCH - MOORELAND 138KV CKT 1 WFEC
Limiting Facility: | FPL SWITCH - MOORELAND 138KV CKT 1
Direction: | From->To
Line Outage: | WOODWARD (WOODWRD2) 138/69/13.2KV TRANSFORMER CKT 1
Flowgate: | 55785559991WOODODWRD24214206WP
Date Redispatch Needed: | 12/1/06 - 4/1/07
Season Flowgate Identified: | 2006 Winter Peak
Reservation | Relief Amount | Aggregate Relief Amount
1032973 | 13.7058 | 13.7058
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'AES 161KV' | 10 | 0.00038 | OKGE | 'FPLWND2 34KV' | 102 | 0.89961 | -0.89923 | 15
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | -0.00402 | OKGE | 'FPLWND2 34KV' | 102 | 0.89961 | -0.90363 | 15
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00264 | OKGE | 'FPLWND2 34KV' | 102 | 0.89961 | -0.89697 | 15
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00264 | OKGE | 'FPLWND2 34KV' | 102 | 0.89961 | -0.89697 | 15
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00264 | OKGE | 'FPLWND2 34KV' | 102 | 0.89961 | -0.89697 | 15
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.00252 | OKGE | 'FPLWND2 34KV' | 102 | 0.89961 | -0.89709 | 15
OKGE | 'MCCLAIN 138KV' | 42 | 0.00414 | OKGE | 'FPLWND2 34KV' | 102 | 0.89961 | -0.89547 | 15
OKGE | 'MUSKOGEE 161KV' | 31 | 0.00045 | OKGE | 'FPLWND2 34KV' | 102 | 0.89961 | -0.89916 | 15
OKGE | 'MUSKOGEE 161KV' | 166 | 0.00045 | OKGE | 'FPLWND2 34KV' | 102 | 0.89961 | -0.89916 | 15
OKGE | 'MUSKOGEE 345KV' | 20 | 0.00057 | OKGE | 'FPLWND2 34KV' | 102 | 0.89961 | -0.89904 | 15
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00425 | OKGE | 'FPLWND2 34KV' | 102 | 0.89961 | -0.89536 | 15
OKGE | 'MUSTANG 69KV' | 106 | 0.00459 | OKGE | 'FPLWND2 34KV' | 102 | 0.89961 | -0.89502 | 15
OKGE | 'ONE OAK 345KV' | 336 | 0.00166 | OKGE | 'FPLWND2 34KV' | 102 | 0.89961 | -0.89795 | 15
OKGE | 'REDBUD 345KV' | 421.65 | 0.00175 | OKGE | 'FPLWND2 34KV' | 102 | 0.89961 | -0.89786 | 15
OKGE | 'REDBUD 345KV' | 900 | 0.00175 | OKGE | 'FPLWND2 34KV' | 102 | 0.89961 | -0.89786 | 15
OKGE | 'SEMINOLE 138KV' | 398.7187 | 0.00199 | OKGE | 'FPLWND2 34KV' | 102 | 0.89961 | -0.89762 | 15
OKGE | 'SEMINOLE 345KV' | 558.5093 | 0.00206 | OKGE | 'FPLWND2 34KV' | 102 | 0.89961 | -0.89755 | 15
OKGE | 'SOONER 138KV' | 25 | -0.00271 | OKGE | 'FPLWND2 34KV' | 102 | 0.89961 | -0.90232 | 15
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.0164 | OKGE | 'FPLWND2 34KV' | 102 | 0.89961 | -0.91601 | 15
OKGE | 'TINKER 5G 138KV' | 62 | 0.00279 | OKGE | 'FPLWND2 34KV' | 102 | 0.89961 | -0.89682 | 15
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.0164 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.75121 | 18
OKGE | 'AES 161KV' | 10 | 0.00038 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73443 | 19
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | -0.00402 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73883 | 19
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00264 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73217 | 19
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00264 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73217 | 19
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00264 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73217 | 19
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.00252 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73229 | 19
OKGE | 'MCCLAIN 138KV' | 42 | 0.00414 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73067 | 19
OKGE | 'MUSKOGEE 161KV' | 31 | 0.00045 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73436 | 19
OKGE | 'MUSKOGEE 161KV' | 166 | 0.00045 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73436 | 19
OKGE | 'MUSKOGEE 345KV' | 20 | 0.00057 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73424 | 19
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00425 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73056 | 19
OKGE | 'MUSTANG 69KV' | 106 | 0.00459 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73022 | 19
OKGE | 'ONE OAK 345KV' | 336 | 0.00166 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73315 | 19
OKGE | 'REDBUD 345KV' | 421.65 | 0.00175 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73306 | 19
OKGE | 'REDBUD 345KV' | 900 | 0.00175 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73306 | 19
OKGE | 'SEMINOLE 138KV' | 398.7187 | 0.00199 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73282 | 19
OKGE | 'SEMINOLE 345KV' | 558.5093 | 0.00206 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73275 | 19
OKGE | 'SOONER 138KV' | 25 | -0.00271 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73752 | 19
OKGE | 'TINKER 5G 138KV' | 62 | 0.00279 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73202 | 19
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | FPL SWITCH - MOORELAND 138KV CKT 1 OKGE & FPL SWITCH - MOORELAND 138KV CKT 1 WFEC
Limiting Facility: | FPL SWITCH - MOORELAND 138KV CKT 1
Direction: | From->To
Line Outage: | WOODWARD (WOODWRD2) 138/69/13.2KV TRANSFORMER CKT 1
Flowgate: | 55785559991WOODODWRD24214207AP
Date Redispatch Needed: | Starting 2007 4/1 - 6/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 April Minimum
Reservation | Relief Amount | Aggregate Relief Amount
1032973 | 25.5674 | 25.5674
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'AES 161KV' | 160 | 0.00038 | OKGE | 'FPLWND2 34KV' | 102 | 0.89961 | -0.89923 | 28
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.00248 | OKGE | 'FPLWND2 34KV' | 102 | 0.89961 | -0.89713 | 28
OKGE | 'MUSKOGEE 161KV' | 31 | 0.00045 | OKGE | 'FPLWND2 34KV' | 102 | 0.89961 | -0.89916 | 28
OKGE | 'MUSKOGEE 161KV' | 166 | 0.00045 | OKGE | 'FPLWND2 34KV' | 102 | 0.89961 | -0.89916 | 28
OKGE | 'MUSKOGEE 345KV' | 714.519 | 0.00057 | OKGE | 'FPLWND2 34KV' | 102 | 0.89961 | -0.89904 | 28
OKGE | 'ONE OAK 345KV' | 336 | 0.00167 | OKGE | 'FPLWND2 34KV' | 102 | 0.89961 | -0.89794 | 28
OKGE | 'REDBUD 345KV' | 900 | 0.00175 | OKGE | 'FPLWND2 34KV' | 102 | 0.89961 | -0.89786 | 28
OKGE | 'REDBUD 345KV' | 421.65 | 0.00175 | OKGE | 'FPLWND2 34KV' | 102 | 0.89961 | -0.89786 | 28
OKGE | 'SEMINOLE 138KV' | 511.8863 | 0.00199 | OKGE | 'FPLWND2 34KV' | 102 | 0.89961 | -0.89762 | 28
OKGE | 'SEMINOLE 345KV' | 996.6 | 0.00207 | OKGE | 'FPLWND2 34KV' | 102 | 0.89961 | -0.89754 | 28
OKGE | 'SOONER 138KV' | 25 | -0.00271 | OKGE | 'FPLWND2 34KV' | 102 | 0.89961 | -0.90232 | 28
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.0164 | OKGE | 'FPLWND2 34KV' | 102 | 0.89961 | -0.91601 | 28
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00258 | OKGE | 'FPLWND2 34KV' | 102 | 0.89961 | -0.89703 | 29
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00258 | OKGE | 'FPLWND2 34KV' | 102 | 0.89961 | -0.89703 | 29
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00258 | OKGE | 'FPLWND2 34KV' | 102 | 0.89961 | -0.89703 | 29
OKGE | 'MCCLAIN 138KV' | 520 | 0.00416 | OKGE | 'FPLWND2 34KV' | 102 | 0.89961 | -0.89545 | 29
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00427 | OKGE | 'FPLWND2 34KV' | 102 | 0.89961 | -0.89534 | 29
OKGE | 'MUSTANG 69KV' | 106 | 0.00462 | OKGE | 'FPLWND2 34KV' | 102 | 0.89961 | -0.89499 | 29
OKGE | 'SMITH COGEN 138KV' | 110 | 0.00405 | OKGE | 'FPLWND2 34KV' | 102 | 0.89961 | -0.89556 | 29
OKGE | 'TINKER 5G 138KV' | 62 | 0.0028 | OKGE | 'FPLWND2 34KV' | 102 | 0.89961 | -0.89681 | 29
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.0164 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.75121 | 34
OKGE | 'AES 161KV' | 160 | 0.00038 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73443 | 35
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00258 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73223 | 35
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00258 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73223 | 35
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00258 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73223 | 35
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.00248 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73233 | 35
OKGE | 'MCCLAIN 138KV' | 520 | 0.00416 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73065 | 35
OKGE | 'MUSKOGEE 161KV' | 166 | 0.00045 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73436 | 35
OKGE | 'MUSKOGEE 161KV' | 31 | 0.00045 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73436 | 35
OKGE | 'MUSKOGEE 345KV' | 714.519 | 0.00057 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73424 | 35
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00427 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73054 | 35
OKGE | 'MUSTANG 69KV' | 106 | 0.00462 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73019 | 35
OKGE | 'ONE OAK 345KV' | 336 | 0.00167 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73314 | 35
OKGE | 'REDBUD 345KV' | 421.65 | 0.00175 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73306 | 35
OKGE | 'REDBUD 345KV' | 900 | 0.00175 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73306 | 35
OKGE | 'SEMINOLE 138KV' | 511.8863 | 0.00199 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73282 | 35
OKGE | 'SEMINOLE 345KV' | 996.6 | 0.00207 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73274 | 35
OKGE | 'SMITH COGEN 138KV' | 110 | 0.00405 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73076 | 35
OKGE | 'SOONER 138KV' | 25 | -0.00271 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73752 | 35
OKGE | 'TINKER 5G 138KV' | 62 | 0.0028 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73201 | 35
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | FPL SWITCH - MOORELAND 138KV CKT 1 OKGE & FPL SWITCH - MOORELAND 138KV CKT 1 WFEC
Limiting Facility: | FPL SWITCH - MOORELAND 138KV CKT 1
Direction: | From->To
Line Outage: | WOODWARD (WOODWRD2) 138/69/13.2KV TRANSFORMER CKT 1
Flowgate: | 55785559991WOODODWRD24214207FA
Date Redispatch Needed: | Starting 2007 10/1 - 12/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 Fall Peak
Reservation | Relief Amount | Aggregate Relief Amount
1032973 | 27.0998 | 27.0998
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'CONTINENTAL EMPIRE 138KV' | 64 | -0.004 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.90358 | 30
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00256 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.89702 | 30
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00256 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.89702 | 30
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00256 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.89702 | 30
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.00246 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.89712 | 30
OKGE | 'MUSKOGEE 161KV' | 31 | 0.00044 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.89914 | 30
OKGE | 'MUSKOGEE 161KV' | 166 | 0.00044 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.89914 | 30
OKGE | 'MUSKOGEE 345KV' | 20 | 0.00053 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.89905 | 30
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00419 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.89539 | 30
OKGE | 'MUSTANG 69KV' | 106 | 0.00455 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.89503 | 30
OKGE | 'ONE OAK 345KV' | 323 | 0.00169 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.89789 | 30
OKGE | 'REDBUD 345KV' | 900 | 0.00174 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.89784 | 30
OKGE | 'REDBUD 345KV' | 421.65 | 0.00174 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.89784 | 30
OKGE | 'SEMINOLE 138KV' | 32.6937 | 0.00197 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.89761 | 30
OKGE | 'SEMINOLE 345KV' | 507.6 | 0.00204 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.89754 | 30
OKGE | 'SMITH COGEN 138KV' | 110 | 0.00399 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.89559 | 30
OKGE | 'SOONER 138KV' | 25 | -0.0027 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.90228 | 30
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.0164 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.91598 | 30
OKGE | 'TINKER 5G 138KV' | 62 | 0.00277 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.89681 | 30
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.0164 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.75118 | 36
OKGE | 'CONTINENTAL EMPIRE 138KV' | 64 | -0.004 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.73878 | 37
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00256 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.73222 | 37
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00256 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.73222 | 37
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00256 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.73222 | 37
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.00246 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.73232 | 37
OKGE | 'MUSKOGEE 161KV' | 31 | 0.00044 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.73434 | 37
OKGE | 'MUSKOGEE 161KV' | 166 | 0.00044 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.73434 | 37
OKGE | 'MUSKOGEE 345KV' | 20 | 0.00053 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.73425 | 37
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00419 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.73059 | 37
OKGE | 'MUSTANG 69KV' | 106 | 0.00455 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.73023 | 37
OKGE | 'ONE OAK 345KV' | 323 | 0.00169 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.73309 | 37
OKGE | 'REDBUD 345KV' | 900 | 0.00174 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.73304 | 37
OKGE | 'REDBUD 345KV' | 421.65 | 0.00174 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.73304 | 37
OKGE | 'SEMINOLE 138KV' | 32.6937 | 0.00197 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.73281 | 37
OKGE | 'SEMINOLE 345KV' | 507.6 | 0.00204 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.73274 | 37
OKGE | 'SMITH COGEN 138KV' | 110 | 0.00399 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.73079 | 37
OKGE | 'SOONER 138KV' | 25 | -0.0027 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.73748 | 37
OKGE | 'TINKER 5G 138KV' | 62 | 0.00277 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.73201 | 37
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | FPL SWITCH - MOORELAND 138KV CKT 1 OKGE & FPL SWITCH - MOORELAND 138KV CKT 1 WFEC
Limiting Facility: | FPL SWITCH - MOORELAND 138KV CKT 1
Direction: | From->To
Line Outage: | WOODWARD (WOODWRD2) 138/69/13.2KV TRANSFORMER CKT 1
Flowgate: | 55785559991WOODODWRD24214207G
Date Redispatch Needed: | Starting 2007 4/1 - 6/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 Spring Peak
Reservation | Relief Amount | Aggregate Relief Amount
1032973 | 26.4127 | 26.4127
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'AES 161KV' | 40 | 0.00038 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.89961 | -0.89923 | 29
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00259 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.89961 | -0.89702 | 29
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00259 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.89961 | -0.89702 | 29
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00259 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.89961 | -0.89702 | 29
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.00249 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.89961 | -0.89712 | 29
OKGE | 'MCCLAIN 138KV' | 42 | 0.00394 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.89961 | -0.89567 | 29
OKGE | 'MUSKOGEE 161KV' | 31 | 0.00045 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.89961 | -0.89916 | 29
OKGE | 'MUSKOGEE 161KV' | 166 | 0.00045 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.89961 | -0.89916 | 29
OKGE | 'MUSKOGEE 345KV' | 20 | 0.00057 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.89961 | -0.89904 | 29
OKGE | 'ONE OAK 345KV' | 319 | 0.00166 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.89961 | -0.89795 | 29
OKGE | 'REDBUD 345KV' | 421.65 | 0.00175 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.89961 | -0.89786 | 29
OKGE | 'REDBUD 345KV' | 900 | 0.00175 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.89961 | -0.89786 | 29
OKGE | 'SEMINOLE 138KV' | 405.9938 | 0.00199 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.89961 | -0.89762 | 29
OKGE | 'SEMINOLE 345KV' | 574.3335 | 0.00207 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.89961 | -0.89754 | 29
OKGE | 'SOONER 138KV' | 25 | -0.00271 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.89961 | -0.90232 | 29
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.0164 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.89961 | -0.91601 | 29
OKGE | 'TINKER 5G 138KV' | 62 | 0.00281 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.89961 | -0.8968 | 29
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00429 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.89961 | -0.89532 | 30
OKGE | 'MUSTANG 69KV' | 106 | 0.00464 | OKGE | 'FPLWND2 34KV' | 101.9988 | 0.89961 | -0.89497 | 30
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.0164 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.75121 | 35
OKGE | 'AES 161KV' | 40 | 0.00038 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73443 | 36
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00259 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73222 | 36
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00259 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73222 | 36
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00259 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73222 | 36
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.00249 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73232 | 36
OKGE | 'MCCLAIN 138KV' | 42 | 0.00394 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73087 | 36
OKGE | 'MUSKOGEE 161KV' | 31 | 0.00045 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73436 | 36
OKGE | 'MUSKOGEE 161KV' | 166 | 0.00045 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73436 | 36
OKGE | 'MUSKOGEE 345KV' | 20 | 0.00057 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73424 | 36
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00429 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73052 | 36
OKGE | 'MUSTANG 69KV' | 106 | 0.00464 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73017 | 36
OKGE | 'ONE OAK 345KV' | 319 | 0.00166 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73315 | 36
OKGE | 'REDBUD 345KV' | 900 | 0.00175 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73306 | 36
OKGE | 'REDBUD 345KV' | 421.65 | 0.00175 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73306 | 36
OKGE | 'SEMINOLE 138KV' | 405.9938 | 0.00199 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73282 | 36
OKGE | 'SEMINOLE 345KV' | 574.3335 | 0.00207 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73274 | 36
OKGE | 'SOONER 138KV' | 25 | -0.00271 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.73752 | 36
OKGE | 'TINKER 5G 138KV' | 62 | 0.00281 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73481 | -0.732 | 36
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | FPL SWITCH - MOORELAND 138KV CKT 1 OKGE & FPL SWITCH - MOORELAND 138KV CKT 1 WFEC
Limiting Facility: | FPL SWITCH - MOORELAND 138KV CKT 1
Direction: | From->To
Line Outage: | WOODWARD (WOODWRD2) 138/69/13.2KV TRANSFORMER CKT 1
Flowgate: | 55785559991WOODODWRD24214207SH
Date Redispatch Needed: | 6/1 - 10/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 Summer Shoulder
Reservation | Relief Amount | Aggregate Relief Amount
1032973 | 13.3847 | 13.3847
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00256 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.89702 | 15
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00256 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.89702 | 15
OKGE | 'MCCLAIN 138KV' | 42 | 0.00387 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.89571 | 15
OKGE | 'MUSKOGEE 161KV' | 166 | 0.00045 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.89913 | 15
OKGE | 'MUSKOGEE 161KV' | 31 | 0.00045 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.89913 | 15
OKGE | 'MUSKOGEE 345KV' | 20 | 0.00053 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.89905 | 15
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00419 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.89539 | 15
OKGE | 'MUSTANG 69KV' | 57.4609 | 0.00455 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.89503 | 15
OKGE | 'ONE OAK 345KV' | 299 | 0.00169 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.89789 | 15
OKGE | 'REDBUD 345KV' | 421.65 | 0.00174 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.89784 | 15
OKGE | 'REDBUD 345KV' | 900 | 0.00174 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.89784 | 15
OKGE | 'SEMINOLE 138KV' | 21.2824 | 0.00197 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.89761 | 15
OKGE | 'SOONER 138KV' | 25 | -0.00269 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.90227 | 15
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.0164 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.91598 | 15
OKGE | 'TINKER 5G 138KV' | 62 | 0.00277 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.89681 | 15
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00256 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.73222 | 18
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00256 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.73222 | 18
OKGE | 'MCCLAIN 138KV' | 42 | 0.00387 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.73091 | 18
OKGE | 'MUSKOGEE 161KV' | 166 | 0.00045 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.73433 | 18
OKGE | 'MUSKOGEE 161KV' | 31 | 0.00045 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.73433 | 18
OKGE | 'MUSKOGEE 345KV' | 20 | 0.00053 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.73425 | 18
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00419 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.73059 | 18
OKGE | 'MUSTANG 69KV' | 57.4609 | 0.00455 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.73023 | 18
OKGE | 'ONE OAK 345KV' | 299 | 0.00169 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.73309 | 18
OKGE | 'REDBUD 345KV' | 900 | 0.00174 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.73304 | 18
OKGE | 'REDBUD 345KV' | 421.65 | 0.00174 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.73304 | 18
OKGE | 'SEMINOLE 138KV' | 21.2824 | 0.00197 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.73281 | 18
OKGE | 'SOONER 138KV' | 25 | -0.00269 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.73747 | 18
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.0164 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.75118 | 18
OKGE | 'TINKER 5G 138KV' | 62 | 0.00277 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.73201 | 18
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | FPL SWITCH - MOORELAND 138KV CKT 1 OKGE & FPL SWITCH - MOORELAND 138KV CKT 1 WFEC
Limiting Facility: | FPL SWITCH - MOORELAND 138KV CKT 1
Direction: | From->To
Line Outage: | WOODWARD (WOODWRD2) 138/69/13.2KV TRANSFORMER CKT 1
Flowgate: | 55785559991WOODODWRD24214207SP
Date Redispatch Needed: | 6/1/07 - 10/1/07
Season Flowgate Identified: | 2007 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1032973 | 2.2563 | 2.2563
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.0164 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.91598 | 2
OKGE | 'HORSESHOE LAKE 138KV' | 293.3623 | 0.00256 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.89702 | 3
OKGE | 'HORSESHOE LAKE 138KV' | 293.3623 | 0.00256 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.73222 | 3
OKGE | 'MCCLAIN 138KV' | 42 | 0.00387 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.89571 | 3
OKGE | 'MCCLAIN 138KV' | 42 | 0.00387 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.73091 | 3
OKGE | 'MUSKOGEE 161KV' | 166 | 0.00045 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.89913 | 3
OKGE | 'MUSKOGEE 161KV' | 31 | 0.00045 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.89913 | 3
OKGE | 'MUSKOGEE 161KV' | 31 | 0.00045 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.73433 | 3
OKGE | 'MUSKOGEE 161KV' | 166 | 0.00045 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.73433 | 3
OKGE | 'MUSKOGEE 345KV' | 20 | 0.00053 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.89905 | 3
OKGE | 'MUSKOGEE 345KV' | 20 | 0.00053 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.73425 | 3
OKGE | 'ONE OAK 345KV' | 261 | 0.00169 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.89789 | 3
OKGE | 'ONE OAK 345KV' | 261 | 0.00169 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.73309 | 3
OKGE | 'REDBUD 345KV' | 421.65 | 0.00174 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.89784 | 3
OKGE | 'REDBUD 345KV' | 900 | 0.00174 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.89784 | 3
OKGE | 'REDBUD 345KV' | 421.65 | 0.00174 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.73304 | 3
OKGE | 'REDBUD 345KV' | 900 | 0.00174 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.73304 | 3
OKGE | 'SEMINOLE 138KV' | 22.6577 | 0.00197 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.89761 | 3
OKGE | 'SEMINOLE 138KV' | 22.6577 | 0.00197 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.73281 | 3
OKGE | 'SOONER 138KV' | 25 | -0.00269 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.90227 | 3
OKGE | 'SOONER 138KV' | 25 | -0.00269 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.73747 | 3
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.0164 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.75118 | 3
OKGE | 'TINKER 5G 138KV' | 62 | 0.00277 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.89681 | 3
OKGE | 'TINKER 5G 138KV' | 62 | 0.00277 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73478 | -0.73201 | 3
OKGE | 'WOODWARD 24KV' | 9.3 | 0.73478 | OKGE | 'FPLWND2 34KV' | 102 | 0.89958 | -0.1648 | 14
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | FPL SWITCH - MOORELAND 138KV CKT 1 OKGE & FPL SWITCH - MOORELAND 138KV CKT 1 WFEC
Limiting Facility: | FPL SWITCH - MOORELAND 138KV CKT 1
Direction: | From->To
Line Outage: | WOODWARD (WOODWRD2) 138/69/13.2KV TRANSFORMER CKT 1
Flowgate: | 55785559991WOODODWRD24214207WP
Date Redispatch Needed: | 12/1/07 - 4/1/08
Season Flowgate Identified: | 2007 Winter Peak
Reservation | Relief Amount | Aggregate Relief Amount
1032973 | 11.258 | 11.258
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'SOONER 138KV' | 25 | -0.00271 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.89957 | -0.90228 | 12
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.01641 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.89957 | -0.91598 | 12
OKGE | 'AES 161KV' | 79 | 0.00036 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.89957 | -0.89921 | 13
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00255 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.89957 | -0.89702 | 13
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00255 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.89957 | -0.89702 | 13
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00255 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.89957 | -0.89702 | 13
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.00245 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.89957 | -0.89712 | 13
OKGE | 'MCCLAIN 138KV' | 42 | 0.00386 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.89957 | -0.89571 | 13
OKGE | 'MUSKOGEE 161KV' | 166 | 0.00043 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.89957 | -0.89914 | 13
OKGE | 'MUSKOGEE 161KV' | 31 | 0.00043 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.89957 | -0.89914 | 13
OKGE | 'MUSKOGEE 345KV' | 20 | 0.00051 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.89957 | -0.89906 | 13
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00418 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.89957 | -0.89539 | 13
OKGE | 'MUSTANG 69KV' | 106 | 0.00454 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.89957 | -0.89503 | 13
OKGE | 'ONE OAK 345KV' | 336 | 0.00168 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.89957 | -0.89789 | 13
OKGE | 'REDBUD 345KV' | 900 | 0.00173 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.89957 | -0.89784 | 13
OKGE | 'REDBUD 345KV' | 421.65 | 0.00173 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.89957 | -0.89784 | 13
OKGE | 'SEMINOLE 138KV' | 319.239 | 0.00195 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.89957 | -0.89762 | 13
OKGE | 'SEMINOLE 345KV' | 507.6 | 0.00203 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.89957 | -0.89754 | 13
OKGE | 'TINKER 5G 138KV' | 62 | 0.00276 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.89957 | -0.89681 | 13
OKGE | 'AES 161KV' | 79 | 0.00036 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73477 | -0.73441 | 15
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00255 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73477 | -0.73222 | 15
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00255 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73477 | -0.73222 | 15
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00255 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73477 | -0.73222 | 15
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.00245 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73477 | -0.73232 | 15
OKGE | 'MCCLAIN 138KV' | 42 | 0.00386 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73477 | -0.73091 | 15
OKGE | 'MUSKOGEE 161KV' | 31 | 0.00043 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73477 | -0.73434 | 15
OKGE | 'MUSKOGEE 161KV' | 166 | 0.00043 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73477 | -0.73434 | 15
OKGE | 'MUSKOGEE 345KV' | 20 | 0.00051 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73477 | -0.73426 | 15
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00418 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73477 | -0.73059 | 15
OKGE | 'MUSTANG 69KV' | 106 | 0.00454 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73477 | -0.73023 | 15
OKGE | 'ONE OAK 345KV' | 336 | 0.00168 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73477 | -0.73309 | 15
OKGE | 'REDBUD 345KV' | 900 | 0.00173 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73477 | -0.73304 | 15
OKGE | 'REDBUD 345KV' | 421.65 | 0.00173 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73477 | -0.73304 | 15
OKGE | 'SEMINOLE 138KV' | 319.239 | 0.00195 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73477 | -0.73282 | 15
OKGE | 'SEMINOLE 345KV' | 507.6 | 0.00203 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73477 | -0.73274 | 15
OKGE | 'SOONER 138KV' | 25 | -0.00271 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73477 | -0.73748 | 15
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.01641 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73477 | -0.75118 | 15
OKGE | 'TINKER 5G 138KV' | 62 | 0.00276 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.73477 | -0.73201 | 15
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | FT SUPPLY 138/69KV TRANSFORMER CKT 1
Limiting Facility: | FT SUPPLY 138/69KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | FT SUPPLY - IODINE 138KV CKT 1
Flowgate: | 55919559201559205595711107G
Date Redispatch Needed: | Starting 2007 4/1 - 6/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 Spring Peak
Reservation | Relief Amount | Aggregate Relief Amount
1023236 | 10.1102 | 10.1102
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
WFEC | 'MORLND 138KV' | 320 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 10
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | FT SUPPLY 138/69KV TRANSFORMER CKT 1
Limiting Facility: | FT SUPPLY 138/69KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | FT SUPPLY - IODINE 138KV CKT 1
Flowgate: | 55919559201559205595713106WP
Date Redispatch Needed: | 12/1/06 - 4/1/07
Season Flowgate Identified: | 2006 Winter Peak
Reservation | Relief Amount | Aggregate Relief Amount
1023236 | 12.6153 | 12.6153
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
WFEC | 'ANADARKO 138KV' | 6.5018 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 13
WFEC | 'ANADARKO 138KV' | 90 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 13
WFEC | 'ANADARKO 69KV' | 76 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 13
WFEC | 'MORLND 138KV' | 166.1695 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 13
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | FT SUPPLY 138/69KV TRANSFORMER CKT 1
Limiting Facility: | FT SUPPLY 138/69KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | FT SUPPLY - IODINE 138KV CKT 1
Flowgate: | 55919559201559205595713107AP
Date Redispatch Needed: | Starting 2007 4/1 - 6/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 April Minimum
Reservation | Relief Amount | Aggregate Relief Amount
1023236 | 11.2916 | 11.2916
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
WFEC | 'ANADARKO 138KV' | 260.5816 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 11
WFEC | 'ANADARKO 138KV' | 90 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 11
WFEC | 'ANADARKO 69KV' | 76 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 11
WFEC | 'HUGO 138KV' | 191.9206 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 11
WFEC | 'MORLND 138KV' | 320 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 11
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | FT SUPPLY 138/69KV TRANSFORMER CKT 1
Limiting Facility: | FT SUPPLY 138/69KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | FT SUPPLY - IODINE 138KV CKT 1
Flowgate: | 55919559201559205595713107FA
Date Redispatch Needed: | Starting 2007 10/1 - 12/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 Fall Peak
Reservation | Relief Amount | Aggregate Relief Amount
1023236 | 13.1725 | 13.1725
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
WFEC | 'ANADARKO 138KV' | 90 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 13
WFEC | 'ANADARKO 138KV' | 56.2138 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 13
WFEC | 'ANADARKO 69KV' | 76 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 13
WFEC | 'MORLND 138KV' | 320 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 13
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | FT SUPPLY 138/69KV TRANSFORMER CKT 1
Limiting Facility: | FT SUPPLY 138/69KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | FT SUPPLY - IODINE 138KV CKT 1
Flowgate: | 55919559201559205595713107SP
Date Redispatch Needed: | 6/1/07 - 10/1/07
Season Flowgate Identified: | 2007 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1023236 | 12.0611 | 12.0611
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
WFEC | 'ANADARKO 138KV' | 90 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 12
WFEC | 'ANADARKO 138KV' | 6.4398 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 12
WFEC | 'ANADARKO 69KV' | 76 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 12
WFEC | 'MORLND 138KV' | 39.6068 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 12
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | FT SUPPLY 138/69KV TRANSFORMER CKT 1
Limiting Facility: | FT SUPPLY 138/69KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | FT SUPPLY - IODINE 138KV CKT 1
Flowgate: | 55919559201559205595713107WP
Date Redispatch Needed: | 12/1/07 - 4/1/08
Season Flowgate Identified: | 2007 Winter Peak
Reservation | Relief Amount | Aggregate Relief Amount
1023236 | 12.5219 | 12.5219
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
WFEC | 'ANADARKO 138KV' | 90 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 13
WFEC | 'ANADARKO 138KV' | 6.419 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 13
WFEC | 'ANADARKO 69KV' | 76 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 13
WFEC | 'MORLND 138KV' | 148.9085 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 13
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | FT SUPPLY 138/69KV TRANSFORMER CKT 1
Limiting Facility: | FT SUPPLY 138/69KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | FT SUPPLY - IODINE 138KV CKT 1
Flowgate: | 55919559201559205595713307SH
Date Redispatch Needed: | 6/1 - 10/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 Summer Shoulder
Reservation | Relief Amount | Aggregate Relief Amount
1023236 | 12.5426 | 12.5426
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
WFEC | 'ANADARKO 138KV' | 9.3668 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 13
WFEC | 'ANADARKO 138KV' | 90 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 13
WFEC | 'ANADARKO 69KV' | 76 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 13
WFEC | 'MORLND 138KV' | 173.8576 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 13
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | FT SUPPLY 138/69KV TRANSFORMER CKT 1
Limiting Facility: | FT SUPPLY 138/69KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | IODINE - MOORELAND 138KV CKT 1
Flowgate: | 55919559201559575599911107G
Date Redispatch Needed: | Starting 2007 4/1 - 6/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 Spring Peak
Reservation | Relief Amount | Aggregate Relief Amount
1023236 | 7.378 | 7.378
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
WFEC | 'MORLND 138KV' | 320 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 7
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | FT SUPPLY 138/69KV TRANSFORMER CKT 1
Limiting Facility: | FT SUPPLY 138/69KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | IODINE - MOORELAND 138KV CKT 1
Flowgate: | 55919559201559575599913106WP
Date Redispatch Needed: | 12/1/06 - 4/1/07
Season Flowgate Identified: | 2006 Winter Peak
Reservation | Relief Amount | Aggregate Relief Amount
1023236 | 9.3213 | 9.3213
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
WFEC | 'ANADARKO 138KV' | 90 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 9
WFEC | 'ANADARKO 138KV' | 6.5018 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 9
WFEC | 'ANADARKO 69KV' | 76 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 9
WFEC | 'MORLND 138KV' | 166.1695 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 9
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | FT SUPPLY 138/69KV TRANSFORMER CKT 1
Limiting Facility: | FT SUPPLY 138/69KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | IODINE - MOORELAND 138KV CKT 1
Flowgate: | 55919559201559575599913107AP
Date Redispatch Needed: | Starting 2007 4/1 - 6/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 April Minimum
Reservation | Relief Amount | Aggregate Relief Amount
1023236 | 9.6661 | 9.6661
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
WFEC | 'ANADARKO 138KV' | 260.5816 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 10
WFEC | 'ANADARKO 138KV' | 90 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 10
WFEC | 'ANADARKO 69KV' | 76 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 10
WFEC | 'HUGO 138KV' | 191.9206 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 10
WFEC | 'MORLND 138KV' | 320 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 10
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | FT SUPPLY 138/69KV TRANSFORMER CKT 1
Limiting Facility: | FT SUPPLY 138/69KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | IODINE - MOORELAND 138KV CKT 1
Flowgate: | 55919559201559575599913107FA
Date Redispatch Needed: | Starting 2007 10/1 - 12/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 Fall Peak
Reservation | Relief Amount | Aggregate Relief Amount
1023236 | 10.4624 | 10.4624
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
WFEC | 'ANADARKO 138KV' | 56.2138 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 10
WFEC | 'ANADARKO 138KV' | 90 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 10
WFEC | 'ANADARKO 69KV' | 76 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 10
WFEC | 'MORLND 138KV' | 320 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 10
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | FT SUPPLY 138/69KV TRANSFORMER CKT 1
Limiting Facility: | FT SUPPLY 138/69KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | IODINE - MOORELAND 138KV CKT 1
Flowgate: | 55919559201559575599913107SP
Date Redispatch Needed: | 6/1/07 - 10/1/07
Season Flowgate Identified: | 2007 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1023236 | 8.412 | 8.412
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
WFEC | 'ANADARKO 138KV' | 90 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 8
WFEC | 'ANADARKO 138KV' | 6.4398 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 8
WFEC | 'ANADARKO 69KV' | 76 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 8
WFEC | 'MORLND 138KV' | 39.6068 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 8
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | FT SUPPLY 138/69KV TRANSFORMER CKT 1
Limiting Facility: | FT SUPPLY 138/69KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | IODINE - MOORELAND 138KV CKT 1
Flowgate: | 55919559201559575599913107WP
Date Redispatch Needed: | 12/1/07 - 4/1/08
Season Flowgate Identified: | 2007 Winter Peak
Reservation | Relief Amount | Aggregate Relief Amount
1023236 | 9.178 | 9.178
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
WFEC | 'ANADARKO 138KV' | 90 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 9
WFEC | 'ANADARKO 138KV' | 6.419 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 9
WFEC | 'ANADARKO 69KV' | 76 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 9
WFEC | 'MORLND 138KV' | 148.9085 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 9
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | FT SUPPLY 138/69KV TRANSFORMER CKT 1
Limiting Facility: | FT SUPPLY 138/69KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | IODINE - MOORELAND 138KV CKT 1
Flowgate: | 55919559201559575599913307SH
Date Redispatch Needed: | 6/1 - 10/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 Summer Shoulder
Reservation | Relief Amount | Aggregate Relief Amount
1023236 | 9.2694 | 9.2694
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
WFEC | 'ANADARKO 138KV' | 9.3668 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 9
WFEC | 'ANADARKO 138KV' | 90 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 9
WFEC | 'ANADARKO 69KV' | 76 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 9
WFEC | 'MORLND 138KV' | 173.8576 | 0 | WFEC | 'SLEEPING BEAR 138KV' | 80 | 1 | -1 | 9
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | GRAY TAP - PENSACOLA 69KV CKT 1
Limiting Facility: | GRAY TAP - PENSACOLA 69KV CKT 1
Direction: | To->From
Line Outage: | KANSAS - KANSAS TAP 161KV CKT 1
Flowgate: | 54465544281545165451413108SP
Date Redispatch Needed: | Starting 2008 6/1 - 10/1 Until EOC
Season Flowgate Identified: | 2008 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
977481 | 0.64547 | 0.64547
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
GRDA | 'KERR 161KV' | 28.5 | 0.01034 | GRDA | 'PENSACOLA 69KV' | 6.5035 | 0.12967 | -0.11933 | 5
GRDA | 'SALINA 161KV' | 72.4557 | 0.01034 | GRDA | 'PENSACOLA 69KV' | 6.5035 | 0.12967 | -0.11933 | 5
GRDA | 'KERR 115KV' | 28.5 | 0.01611 | GRDA | 'PENSACOLA 69KV' | 6.5035 | 0.12967 | -0.11356 | 6
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | GRAY TAP - PENSACOLA 69KV CKT 1
Limiting Facility: | GRAY TAP - PENSACOLA 69KV CKT 1
Direction: | To->From
Line Outage: | KANSAS (KANAUTO1) 161/69/13.8KV TRANSFORMER CKT 1
Flowgate: | 54465544281KANSNAUTO15213108SP
Date Redispatch Needed: | Starting 2008 6/1 - 10/1 Until EOC
Season Flowgate Identified: | 2008 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
977481 | 0.64515 | 0.64515
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
GRDA | 'KERR 161KV' | 28.5 | 0.01034 | GRDA | 'PENSACOLA 69KV' | 6.5035 | 0.12967 | -0.11933 | 5
GRDA | 'SALINA 161KV' | 72.4557 | 0.01034 | GRDA | 'PENSACOLA 69KV' | 6.5035 | 0.12967 | -0.11933 | 5
GRDA | 'KERR 115KV' | 28.5 | 0.01611 | GRDA | 'PENSACOLA 69KV' | 6.5035 | 0.12967 | -0.11356 | 6
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | HAMON BUTLER - MOREWOOD 69KV CKT 1
Limiting Facility: | HAMON BUTLER - MOREWOOD 69KV CKT 1
Direction: | From->To
Line Outage: | MOORELAND - MOREWOOD SW 138KV CKT 1
Flowgate: | 55942560001559995600111206SP
Date Redispatch Needed: | 6/1/06 - 10/1/06
Season Flowgate Identified: | 2006 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1032973 | 6.8318 | 6.8318
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'MUSKOGEE 161KV' | 31 | 0.001 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.08619 | -0.08519 | 80
OKGE | 'MUSKOGEE 161KV' | 166 | 0.001 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.08619 | -0.08519 | 80
OKGE | 'HORSESHOE LAKE 138KV' | 337.7 | 0.00194 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.08619 | -0.08425 | 81
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00194 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.08619 | -0.08425 | 81
OKGE | 'MCCLAIN 138KV' | 42 | 0.00178 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.08619 | -0.08441 | 81
OKGE | 'REDBUD 345KV' | 421.65 | 0.00226 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.08619 | -0.08393 | 81
OKGE | 'REDBUD 345KV' | 253 | 0.00226 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.08619 | -0.08393 | 81
OKGE | 'MUSTANG 138KV' | 142.3459 | 0.00252 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.08619 | -0.08367 | 82
OKGE | 'ONE OAK 345KV' | 261 | 0.00297 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.08619 | -0.08322 | 82
OKGE | 'MCCLAIN 138KV' | 42 | 0.00178 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.08263 | -0.08085 | 84
OKGE | 'MUSKOGEE 161KV' | 166 | 0.001 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.08263 | -0.08163 | 84
OKGE | 'MUSKOGEE 161KV' | 31 | 0.001 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.08263 | -0.08163 | 84
OKGE | 'HORSESHOE LAKE 138KV' | 337.7 | 0.00194 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.08263 | -0.08069 | 85
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00194 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.08263 | -0.08069 | 85
OKGE | 'MUSTANG 138KV' | 142.3459 | 0.00252 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.08263 | -0.08011 | 85
OKGE | 'REDBUD 345KV' | 253 | 0.00226 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.08263 | -0.08037 | 85
OKGE | 'REDBUD 345KV' | 421.65 | 0.00226 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.08263 | -0.08037 | 85
OKGE | 'ONE OAK 345KV' | 261 | 0.00297 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.08263 | -0.07966 | 86
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | 0.00765 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.08619 | -0.07854 | 87
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | 0.00765 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.08263 | -0.07498 | 91
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | 0.02113 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.08619 | -0.06506 | 105
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | 0.02113 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.08263 | -0.0615 | 111
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | HAMON BUTLER - MOREWOOD 69KV CKT 1
Limiting Facility: | HAMON BUTLER - MOREWOOD 69KV CKT 1
Direction: | From->To
Line Outage: | MOORELAND - MOREWOOD SW 138KV CKT 1
Flowgate: | 55942560001559995600111206WP
Date Redispatch Needed: | 12/1/06 - 4/1/07
Season Flowgate Identified: | 2006 Winter Peak
Reservation | Relief Amount | Aggregate Relief Amount
1023236 | 2.9278 | 7.2613
1032973 | 4.3335 | 7.2613
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'MUSKOGEE 161KV' | 31 | 0.00099 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09028 | -0.08929 | 81
OKGE | 'SEMINOLE 138KV' | 395.2155 | 0.00043 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09028 | -0.08985 | 81
OKGE | 'SEMINOLE 345KV' | 558.5093 | 0.00091 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09028 | -0.08937 | 81
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00194 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09028 | -0.08834 | 82
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00194 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09028 | -0.08834 | 82
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00194 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09028 | -0.08834 | 82
OKGE | 'MCCLAIN 138KV' | 42 | 0.00172 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09028 | -0.08856 | 82
OKGE | 'REDBUD 345KV' | 900 | 0.00223 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09028 | -0.08805 | 82
OKGE | 'REDBUD 345KV' | 421.65 | 0.00223 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09028 | -0.08805 | 82
OKGE | 'TINKER 5G 138KV' | 62 | 0.00166 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09028 | -0.08862 | 82
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00244 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09028 | -0.08784 | 83
OKGE | 'MUSTANG 69KV' | 106 | 0.00321 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09028 | -0.08707 | 83
OKGE | 'ONE OAK 345KV' | 336 | 0.00294 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09028 | -0.08734 | 83
OKGE | 'SEMINOLE 138KV' | 395.2155 | 0.00043 | OKGE | 'FPLWND2 34KV' | 102 | 0.08464 | -0.08421 | 86
OKGE | 'MUSKOGEE 161KV' | 31 | 0.00099 | OKGE | 'FPLWND2 34KV' | 102 | 0.08464 | -0.08365 | 87
OKGE | 'SEMINOLE 345KV' | 558.5093 | 0.00091 | OKGE | 'FPLWND2 34KV' | 102 | 0.08464 | -0.08373 | 87
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | 0.00775 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09028 | -0.08253 | 88
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00194 | OKGE | 'FPLWND2 34KV' | 102 | 0.08464 | -0.0827 | 88
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00194 | OKGE | 'FPLWND2 34KV' | 102 | 0.08464 | -0.0827 | 88
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00194 | OKGE | 'FPLWND2 34KV' | 102 | 0.08464 | -0.0827 | 88
OKGE | 'MCCLAIN 138KV' | 42 | 0.00172 | OKGE | 'FPLWND2 34KV' | 102 | 0.08464 | -0.08292 | 88
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00244 | OKGE | 'FPLWND2 34KV' | 102 | 0.08464 | -0.0822 | 88
OKGE | 'REDBUD 345KV' | 421.65 | 0.00223 | OKGE | 'FPLWND2 34KV' | 102 | 0.08464 | -0.08241 | 88
OKGE | 'REDBUD 345KV' | 900 | 0.00223 | OKGE | 'FPLWND2 34KV' | 102 | 0.08464 | -0.08241 | 88
OKGE | 'TINKER 5G 138KV' | 62 | 0.00166 | OKGE | 'FPLWND2 34KV' | 102 | 0.08464 | -0.08298 | 88
OKGE | 'MUSTANG 69KV' | 106 | 0.00321 | OKGE | 'FPLWND2 34KV' | 102 | 0.08464 | -0.08143 | 89
OKGE | 'ONE OAK 345KV' | 336 | 0.00294 | OKGE | 'FPLWND2 34KV' | 102 | 0.08464 | -0.0817 | 89
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | 0.00775 | OKGE | 'FPLWND2 34KV' | 102 | 0.08464 | -0.07689 | 94
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | 0.02149 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09028 | -0.06879 | 106
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | 0.02149 | OKGE | 'FPLWND2 34KV' | 102 | 0.08464 | -0.06315 | 115
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | HAMON BUTLER - MOREWOOD 69KV CKT 1
Limiting Facility: | HAMON BUTLER - MOREWOOD 69KV CKT 1
Direction: | From->To
Line Outage: | MOORELAND - MOREWOOD SW 138KV CKT 1
Flowgate: | 55942560001559995600111207AP
Date Redispatch Needed: | Starting 2007 4/1 - 6/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 April Minimum
Reservation | Relief Amount | Aggregate Relief Amount
1023236 | 0.8352 | 2.0734
1032973 | 1.2382 | 2.0734
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'AES 161KV' | 160 | 0.0006 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09027 | -0.08967 | 23
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00194 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09027 | -0.08833 | 23
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00194 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09027 | -0.08833 | 23
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00194 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09027 | -0.08833 | 23
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.00172 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09027 | -0.08855 | 23
OKGE | 'MCCLAIN 138KV' | 520 | 0.00172 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09027 | -0.08855 | 23
OKGE | 'MUSKOGEE 161KV' | 31 | 0.001 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09027 | -0.08927 | 23
OKGE | 'MUSKOGEE 161KV' | 166 | 0.001 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09027 | -0.08927 | 23
OKGE | 'MUSKOGEE 345KV' | 714.519 | 0.00097 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09027 | -0.0893 | 23
OKGE | 'SEMINOLE 138KV' | 507.6138 | 0.00043 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09027 | -0.08984 | 23
OKGE | 'SEMINOLE 345KV' | 996.6 | 0.00092 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09027 | -0.08935 | 23
OKGE | 'TINKER 5G 138KV' | 62 | 0.00166 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09027 | -0.08861 | 23
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00244 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09027 | -0.08783 | 24
OKGE | 'MUSTANG 69KV' | 106 | 0.00321 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09027 | -0.08706 | 24
OKGE | 'ONE OAK 345KV' | 336 | 0.00295 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09027 | -0.08732 | 24
OKGE | 'REDBUD 345KV' | 421.65 | 0.00223 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09027 | -0.08804 | 24
OKGE | 'REDBUD 345KV' | 900 | 0.00223 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09027 | -0.08804 | 24
OKGE | 'SMITH COGEN 138KV' | 110 | 0.00228 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09027 | -0.08799 | 24
OKGE | 'AES 161KV' | 160 | 0.0006 | OKGE | 'FPLWND2 34KV' | 102 | 0.08463 | -0.08403 | 25
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00194 | OKGE | 'FPLWND2 34KV' | 102 | 0.08463 | -0.08269 | 25
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00194 | OKGE | 'FPLWND2 34KV' | 102 | 0.08463 | -0.08269 | 25
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00194 | OKGE | 'FPLWND2 34KV' | 102 | 0.08463 | -0.08269 | 25
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.00172 | OKGE | 'FPLWND2 34KV' | 102 | 0.08463 | -0.08291 | 25
OKGE | 'MCCLAIN 138KV' | 520 | 0.00172 | OKGE | 'FPLWND2 34KV' | 102 | 0.08463 | -0.08291 | 25
OKGE | 'MUSKOGEE 161KV' | 31 | 0.001 | OKGE | 'FPLWND2 34KV' | 102 | 0.08463 | -0.08363 | 25
OKGE | 'MUSKOGEE 161KV' | 166 | 0.001 | OKGE | 'FPLWND2 34KV' | 102 | 0.08463 | -0.08363 | 25
OKGE | 'MUSKOGEE 345KV' | 714.519 | 0.00097 | OKGE | 'FPLWND2 34KV' | 102 | 0.08463 | -0.08366 | 25
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00244 | OKGE | 'FPLWND2 34KV' | 102 | 0.08463 | -0.08219 | 25
OKGE | 'MUSTANG 69KV' | 106 | 0.00321 | OKGE | 'FPLWND2 34KV' | 102 | 0.08463 | -0.08142 | 25
OKGE | 'ONE OAK 345KV' | 336 | 0.00295 | OKGE | 'FPLWND2 34KV' | 102 | 0.08463 | -0.08168 | 25
OKGE | 'REDBUD 345KV' | 900 | 0.00223 | OKGE | 'FPLWND2 34KV' | 102 | 0.08463 | -0.0824 | 25
OKGE | 'REDBUD 345KV' | 421.65 | 0.00223 | OKGE | 'FPLWND2 34KV' | 102 | 0.08463 | -0.0824 | 25
OKGE | 'SEMINOLE 138KV' | 507.6138 | 0.00043 | OKGE | 'FPLWND2 34KV' | 102 | 0.08463 | -0.0842 | 25
OKGE | 'SEMINOLE 345KV' | 996.6 | 0.00092 | OKGE | 'FPLWND2 34KV' | 102 | 0.08463 | -0.08371 | 25
OKGE | 'SMITH COGEN 138KV' | 110 | 0.00228 | OKGE | 'FPLWND2 34KV' | 102 | 0.08463 | -0.08235 | 25
OKGE | 'SOONER 138KV' | 25 | 0.0068 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09027 | -0.08347 | 25
OKGE | 'TINKER 5G 138KV' | 62 | 0.00166 | OKGE | 'FPLWND2 34KV' | 102 | 0.08463 | -0.08297 | 25
OKGE | 'SOONER 138KV' | 25 | 0.0068 | OKGE | 'FPLWND2 34KV' | 102 | 0.08463 | -0.07783 | 27
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | 0.02149 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09027 | -0.06878 | 30
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | 0.02149 | OKGE | 'FPLWND2 34KV' | 102 | 0.08463 | -0.06314 | 33
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | HAMON BUTLER - MOREWOOD 69KV CKT 1
Limiting Facility: | HAMON BUTLER - MOREWOOD 69KV CKT 1
Direction: | From->To
Line Outage: | MOORELAND - MOREWOOD SW 138KV CKT 1
Flowgate: | 55942560001559995600111407SH
Date Redispatch Needed: | 6/1 - 10/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 Summer Shoulder
Reservation | Relief Amount | Aggregate Relief Amount
1023236 | 1.1438 | 2.8324
1032973 | 1.6885 | 2.8324
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00195 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09029 | -0.08834 | 32
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00195 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09029 | -0.08834 | 32
OKGE | 'MCCLAIN 138KV' | 42 | 0.00175 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09029 | -0.08854 | 32
OKGE | 'MUSKOGEE 161KV' | 166 | 0.001 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09029 | -0.08929 | 32
OKGE | 'MUSKOGEE 161KV' | 31 | 0.001 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09029 | -0.08929 | 32
OKGE | 'MUSKOGEE 345KV' | 20 | 0.00098 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09029 | -0.08931 | 32
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00244 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09029 | -0.08785 | 32
OKGE | 'ONE OAK 345KV' | 274 | 0.00295 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09029 | -0.08734 | 32
OKGE | 'REDBUD 345KV' | 421.65 | 0.00224 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09029 | -0.08805 | 32
OKGE | 'REDBUD 345KV' | 900 | 0.00224 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09029 | -0.08805 | 32
OKGE | 'SEMINOLE 138KV' | 21.4325 | 0.00044 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09029 | -0.08985 | 32
OKGE | 'TINKER 5G 138KV' | 62 | 0.00167 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09029 | -0.08862 | 32
OKGE | 'MUSTANG 69KV' | 55.6045 | 0.00321 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09029 | -0.08708 | 33
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00195 | OKGE | 'FPLWND2 34KV' | 102 | 0.08465 | -0.0827 | 34
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00195 | OKGE | 'FPLWND2 34KV' | 102 | 0.08465 | -0.0827 | 34
OKGE | 'MCCLAIN 138KV' | 42 | 0.00175 | OKGE | 'FPLWND2 34KV' | 102 | 0.08465 | -0.0829 | 34
OKGE | 'MUSKOGEE 161KV' | 166 | 0.001 | OKGE | 'FPLWND2 34KV' | 102 | 0.08465 | -0.08365 | 34
OKGE | 'MUSKOGEE 161KV' | 31 | 0.001 | OKGE | 'FPLWND2 34KV' | 102 | 0.08465 | -0.08365 | 34
OKGE | 'MUSKOGEE 345KV' | 20 | 0.00098 | OKGE | 'FPLWND2 34KV' | 102 | 0.08465 | -0.08367 | 34
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00244 | OKGE | 'FPLWND2 34KV' | 102 | 0.08465 | -0.08221 | 34
OKGE | 'REDBUD 345KV' | 421.65 | 0.00224 | OKGE | 'FPLWND2 34KV' | 102 | 0.08465 | -0.08241 | 34
OKGE | 'REDBUD 345KV' | 900 | 0.00224 | OKGE | 'FPLWND2 34KV' | 102 | 0.08465 | -0.08241 | 34
OKGE | 'SEMINOLE 138KV' | 21.4325 | 0.00044 | OKGE | 'FPLWND2 34KV' | 102 | 0.08465 | -0.08421 | 34
OKGE | 'SOONER 138KV' | 25 | 0.0068 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09029 | -0.08349 | 34
OKGE | 'TINKER 5G 138KV' | 62 | 0.00167 | OKGE | 'FPLWND2 34KV' | 102 | 0.08465 | -0.08298 | 34
OKGE | 'MUSTANG 69KV' | 55.6045 | 0.00321 | OKGE | 'FPLWND2 34KV' | 102 | 0.08465 | -0.08144 | 35
OKGE | 'ONE OAK 345KV' | 274 | 0.00295 | OKGE | 'FPLWND2 34KV' | 102 | 0.08465 | -0.0817 | 35
OKGE | 'SOONER 138KV' | 25 | 0.0068 | OKGE | 'FPLWND2 34KV' | 102 | 0.08465 | -0.07785 | 36
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | 0.02149 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09029 | -0.0688 | 41
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | 0.02149 | OKGE | 'FPLWND2 34KV' | 102 | 0.08465 | -0.06316 | 45
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | HAMON BUTLER - MOREWOOD 69KV CKT 1
Limiting Facility: | HAMON BUTLER - MOREWOOD 69KV CKT 1
Direction: | From->To
Line Outage: | MOORELAND - MOREWOOD SW 138KV CKT 1
Flowgate: | 55942560001559995600111407SP
Date Redispatch Needed: | 6/1/07 - 10/1/07
Season Flowgate Identified: | 2007 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1023236 | 4.6237 | 11.4484
1032973 | 6.8247 | 11.4484
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'TINKER 5G 138KV' | 62 | 0.00167 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09029 | -0.08862 | 129
OKGE | 'HORSESHOE LAKE 138KV' | 291.8916 | 0.00194 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09029 | -0.08835 | 130
OKGE | 'REDBUD 345KV' | 421.65 | 0.00224 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09029 | -0.08805 | 130
OKGE | 'REDBUD 345KV' | 900 | 0.00224 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09029 | -0.08805 | 130
OKGE | 'ONE OAK 345KV' | 261 | 0.00295 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09029 | -0.08734 | 131
OKGE | 'MUSKOGEE 161KV' | 166 | 0.00099 | OKGE | 'FPLWND2 34KV' | 102 | 0.08465 | -0.08366 | 137
OKGE | 'HORSESHOE LAKE 138KV' | 291.8916 | 0.00194 | OKGE | 'FPLWND2 34KV' | 102 | 0.08465 | -0.08271 | 138
OKGE | 'TINKER 5G 138KV' | 62 | 0.00167 | OKGE | 'FPLWND2 34KV' | 102 | 0.08465 | -0.08298 | 138
OKGE | 'REDBUD 345KV' | 421.65 | 0.00224 | OKGE | 'FPLWND2 34KV' | 102 | 0.08465 | -0.08241 | 139
OKGE | 'REDBUD 345KV' | 900 | 0.00224 | OKGE | 'FPLWND2 34KV' | 102 | 0.08465 | -0.08241 | 139
OKGE | 'ONE OAK 345KV' | 261 | 0.00295 | OKGE | 'FPLWND2 34KV' | 102 | 0.08465 | -0.0817 | 140
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | HAMON BUTLER - MOREWOOD 69KV CKT 1
Limiting Facility: | HAMON BUTLER - MOREWOOD 69KV CKT 1
Direction: | From->To
Line Outage: | MOORELAND - MOREWOOD SW 138KV CKT 1
Flowgate: | 55942560001559995600111407WP
Date Redispatch Needed: | 12/1/07 - 4/1/08
Season Flowgate Identified: | 2007 Winter Peak
Reservation | Relief Amount | Aggregate Relief Amount
1023236 | 2.4815 | 6.1554
1032973 | 3.6739 | 6.1554
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'AES 161KV' | 79 | 0.00058 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09028 | -0.0897 | 69
OKGE | 'MUSKOGEE 161KV' | 166 | 0.00098 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09028 | -0.0893 | 69
OKGE | 'MUSKOGEE 161KV' | 31 | 0.00098 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09028 | -0.0893 | 69
OKGE | 'SEMINOLE 138KV' | 305.394 | 0.00043 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09028 | -0.08985 | 69
OKGE | 'SEMINOLE 345KV' | 507.6 | 0.00091 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09028 | -0.08937 | 69
OKGE | 'TINKER 5G 138KV' | 62 | 0.00165 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09028 | -0.08863 | 69
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00193 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09028 | -0.08835 | 70
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00193 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09028 | -0.08835 | 70
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00193 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09028 | -0.08835 | 70
OKGE | 'MCCLAIN 138KV' | 42 | 0.00173 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09028 | -0.08855 | 70
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00242 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09028 | -0.08786 | 70
OKGE | 'ONE OAK 345KV' | 319 | 0.00294 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09028 | -0.08734 | 70
OKGE | 'REDBUD 345KV' | 421.65 | 0.00223 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09028 | -0.08805 | 70
OKGE | 'REDBUD 345KV' | 900 | 0.00223 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09028 | -0.08805 | 70
OKGE | 'MUSTANG 69KV' | 106 | 0.00319 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09028 | -0.08709 | 71
OKGE | 'AES 161KV' | 79 | 0.00058 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.08464 | -0.08406 | 73
OKGE | 'SEMINOLE 138KV' | 305.394 | 0.00043 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.08464 | -0.08421 | 73
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00193 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.08464 | -0.08271 | 74
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00193 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.08464 | -0.08271 | 74
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00193 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.08464 | -0.08271 | 74
OKGE | 'MCCLAIN 138KV' | 42 | 0.00173 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.08464 | -0.08291 | 74
OKGE | 'MUSKOGEE 161KV' | 31 | 0.00098 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.08464 | -0.08366 | 74
OKGE | 'MUSKOGEE 161KV' | 166 | 0.00098 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.08464 | -0.08366 | 74
OKGE | 'SEMINOLE 345KV' | 507.6 | 0.00091 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.08464 | -0.08373 | 74
OKGE | 'SOONER 138KV' | 25 | 0.00678 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09028 | -0.0835 | 74
OKGE | 'TINKER 5G 138KV' | 62 | 0.00165 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.08464 | -0.08299 | 74
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00242 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.08464 | -0.08222 | 75
OKGE | 'ONE OAK 345KV' | 319 | 0.00294 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.08464 | -0.0817 | 75
OKGE | 'REDBUD 345KV' | 421.65 | 0.00223 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.08464 | -0.08241 | 75
OKGE | 'REDBUD 345KV' | 900 | 0.00223 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.08464 | -0.08241 | 75
OKGE | 'MUSTANG 69KV' | 106 | 0.00319 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.08464 | -0.08145 | 76
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | 0.02148 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09028 | -0.0688 | 89
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | 0.02148 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.08464 | -0.06316 | 97
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | IODINE - WOODWARD 138kV CKT 1
Limiting Facility: | MOORELAND 138/69KV TRANSFORMER CKT 1
Direction: | To->From
Line Outage: | FPL SWITCH - MOORELAND 138KV CKT 1
Flowgate: | 55995559991559995578511206SH
Date Redispatch Needed: | 6/1/06 - 10/1/06
Season Flowgate Identified: | 2006 Summer Shoulder
Reservation | Relief Amount | Aggregate Relief Amount
1032973 | 9.9546 | 9.9546
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | -0.00055 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50514 | 20
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | -0.00055 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50514 | 20
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00027 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50432 | 20
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00027 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50432 | 20
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00027 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50432 | 20
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00027 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50432 | 20
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00027 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50432 | 20
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00027 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50432 | 20
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.00027 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50432 | 20
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.00027 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50432 | 20
OKGE | 'MCCLAIN 138KV' | 42 | 0.00044 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50415 | 20
OKGE | 'MCCLAIN 138KV' | 42 | 0.00044 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50415 | 20
OKGE | 'MUSKOGEE 161KV' | 31 | 4e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50455 | 20
OKGE | 'MUSKOGEE 161KV' | 166 | 4e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50455 | 20
OKGE | 'MUSKOGEE 161KV' | 31 | 4e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50455 | 20
OKGE | 'MUSKOGEE 161KV' | 166 | 4e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50455 | 20
OKGE | 'MUSKOGEE 345KV' | 20 | 6e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50453 | 20
OKGE | 'MUSKOGEE 345KV' | 20 | 6e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50453 | 20
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00044 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50415 | 20
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00044 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50415 | 20
OKGE | 'MUSTANG 69KV' | 106 | 0.00049 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.5041 | 20
OKGE | 'MUSTANG 69KV' | 106 | 0.00049 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.5041 | 20
OKGE | 'ONE OAK 345KV' | 293 | 0.00015 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50444 | 20
OKGE | 'ONE OAK 345KV' | 293 | 0.00015 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50444 | 20
OKGE | 'REDBUD 345KV' | 253 | 0.00017 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50442 | 20
OKGE | 'REDBUD 345KV' | 421.65 | 0.00017 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50442 | 20
OKGE | 'REDBUD 345KV' | 253 | 0.00017 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50442 | 20
OKGE | 'REDBUD 345KV' | 421.65 | 0.00017 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50442 | 20
OKGE | 'SEMINOLE 138KV' | 34.1504 | 0.00023 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50436 | 20
OKGE | 'SEMINOLE 138KV' | 34.1504 | 0.00023 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50436 | 20
OKGE | 'SEMINOLE 345KV' | 385.6923 | 0.00023 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50436 | 20
OKGE | 'SEMINOLE 345KV' | 385.6923 | 0.00023 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50436 | 20
OKGE | 'SOONER 138KV' | 25 | -0.00038 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50497 | 20
OKGE | 'SOONER 138KV' | 25 | -0.00038 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50497 | 20
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.00198 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50657 | 20
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.00198 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50657 | 20
OKGE | 'TINKER 5G 138KV' | 62 | 0.0003 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50429 | 20
OKGE | 'TINKER 5G 138KV' | 62 | 0.0003 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50429 | 20
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | IODINE - WOODWARD 138kV CKT 1
Limiting Facility: | MOORELAND 138/69KV TRANSFORMER CKT 1
Direction: | To->From
Line Outage: | FPL SWITCH - MOORELAND 138KV CKT 1
Flowgate: | 55995559991559995578511406FA
Date Redispatch Needed: | 10/1/06 - 12/1/06
Season Flowgate Identified: | 2006 Fall Peak
Reservation | Relief Amount | Aggregate Relief Amount
1032973 | 20.1102 | 20.1102
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | -0.00055 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50514 | 40
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | -0.00055 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50514 | 40
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00027 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50432 | 40
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00027 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50432 | 40
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00027 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50432 | 40
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00027 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50432 | 40
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00027 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50432 | 40
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00027 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50432 | 40
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.00026 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50433 | 40
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.00026 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50433 | 40
OKGE | 'MCCLAIN 138KV' | 42 | 0.00044 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50415 | 40
OKGE | 'MCCLAIN 138KV' | 42 | 0.00044 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50415 | 40
OKGE | 'MUSKOGEE 161KV' | 166 | 4e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50455 | 40
OKGE | 'MUSKOGEE 161KV' | 31 | 4e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50455 | 40
OKGE | 'MUSKOGEE 161KV' | 31 | 4e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50455 | 40
OKGE | 'MUSKOGEE 161KV' | 166 | 4e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50455 | 40
OKGE | 'MUSKOGEE 345KV' | 20 | 6e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50453 | 40
OKGE | 'MUSKOGEE 345KV' | 20 | 6e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50453 | 40
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00044 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50415 | 40
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00044 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50415 | 40
OKGE | 'MUSTANG 69KV' | 106 | 0.00049 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.5041 | 40
OKGE | 'MUSTANG 69KV' | 106 | 0.00049 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.5041 | 40
OKGE | 'ONE OAK 345KV' | 336 | 0.00015 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50444 | 40
OKGE | 'ONE OAK 345KV' | 336 | 0.00015 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50444 | 40
OKGE | 'REDBUD 345KV' | 421.65 | 0.00017 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50442 | 40
OKGE | 'REDBUD 345KV' | 900 | 0.00017 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50442 | 40
OKGE | 'REDBUD 345KV' | 900 | 0.00017 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50442 | 40
OKGE | 'REDBUD 345KV' | 421.65 | 0.00017 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50442 | 40
OKGE | 'SEMINOLE 138KV' | 241.6956 | 0.00023 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50436 | 40
OKGE | 'SEMINOLE 138KV' | 241.6956 | 0.00023 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50436 | 40
OKGE | 'SEMINOLE 345KV' | 507.6 | 0.00023 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50436 | 40
OKGE | 'SEMINOLE 345KV' | 507.6 | 0.00023 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50436 | 40
OKGE | 'SOONER 138KV' | 25 | -0.00038 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50497 | 40
OKGE | 'SOONER 138KV' | 25 | -0.00038 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50497 | 40
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.00199 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50658 | 40
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.00199 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50658 | 40
OKGE | 'TINKER 5G 138KV' | 62 | 0.0003 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50429 | 40
OKGE | 'TINKER 5G 138KV' | 62 | 0.0003 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50429 | 40
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | IODINE - WOODWARD 138kV CKT 1
Limiting Facility: | MOORELAND - WOODWARD 69KV CKT 1
Direction: | To->From
Line Outage: | FPL SWITCH - MOORELAND 138KV CKT 1
Flowgate: | 55995560961559995578511106SH
Date Redispatch Needed: | 6/1/06 - 10/1/06
Season Flowgate Identified: | 2006 Summer Shoulder
Reservation | Relief Amount | Aggregate Relief Amount
1032973 | 13.6642 | 13.6642
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | -0.00055 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50514 | 27
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | -0.00055 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50514 | 27
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00027 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50432 | 27
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00027 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50432 | 27
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00027 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50432 | 27
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00027 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50432 | 27
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00027 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50432 | 27
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00027 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50432 | 27
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.00027 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50432 | 27
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.00027 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50432 | 27
OKGE | 'MCCLAIN 138KV' | 42 | 0.00044 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50415 | 27
OKGE | 'MCCLAIN 138KV' | 42 | 0.00044 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50415 | 27
OKGE | 'MUSKOGEE 161KV' | 31 | 4e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50455 | 27
OKGE | 'MUSKOGEE 161KV' | 166 | 4e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50455 | 27
OKGE | 'MUSKOGEE 161KV' | 31 | 4e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50455 | 27
OKGE | 'MUSKOGEE 161KV' | 166 | 4e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50455 | 27
OKGE | 'MUSKOGEE 345KV' | 20 | 6e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50453 | 27
OKGE | 'MUSKOGEE 345KV' | 20 | 6e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50453 | 27
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00044 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50415 | 27
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00044 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50415 | 27
OKGE | 'MUSTANG 69KV' | 106 | 0.00049 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.5041 | 27
OKGE | 'MUSTANG 69KV' | 106 | 0.00049 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.5041 | 27
OKGE | 'ONE OAK 345KV' | 236 | 0.00015 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50444 | 27
OKGE | 'ONE OAK 345KV' | 236 | 0.00015 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50444 | 27
OKGE | 'REDBUD 345KV' | 421.65 | 0.00017 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50442 | 27
OKGE | 'REDBUD 345KV' | 460 | 0.00017 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50442 | 27
OKGE | 'REDBUD 345KV' | 460 | 0.00017 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50442 | 27
OKGE | 'REDBUD 345KV' | 421.65 | 0.00017 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50442 | 27
OKGE | 'SEMINOLE 138KV' | 47.215 | 0.00023 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50436 | 27
OKGE | 'SEMINOLE 138KV' | 47.215 | 0.00023 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50436 | 27
OKGE | 'SEMINOLE 345KV' | 406.08 | 0.00023 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50436 | 27
OKGE | 'SEMINOLE 345KV' | 406.08 | 0.00023 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50436 | 27
OKGE | 'SOONER 138KV' | 25 | -0.00038 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50497 | 27
OKGE | 'SOONER 138KV' | 25 | -0.00038 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50497 | 27
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.00198 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50657 | 27
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.00198 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50657 | 27
OKGE | 'TINKER 5G 138KV' | 62 | 0.0003 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50429 | 27
OKGE | 'TINKER 5G 138KV' | 62 | 0.0003 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50429 | 27
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | IODINE - WOODWARD 138kV CKT 1
Limiting Facility: | MOORELAND - WOODWARD 69KV CKT 1
Direction: | To->From
Line Outage: | FPL SWITCH - MOORELAND 138KV CKT 1
Flowgate: | 55995560961559995578511206FA
Date Redispatch Needed: | 10/1/06 - 12/1/06
Season Flowgate Identified: | 2006 Fall Peak
Reservation | Relief Amount | Aggregate Relief Amount
1032973 | 21.4345 | 21.4345
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | -0.00055 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50514 | 42
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | -0.00055 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50514 | 42
OKGE | 'MUSKOGEE 161KV' | 166 | 4e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50455 | 42
OKGE | 'MUSKOGEE 161KV' | 31 | 4e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50455 | 42
OKGE | 'MUSKOGEE 161KV' | 166 | 4e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50455 | 42
OKGE | 'MUSKOGEE 161KV' | 31 | 4e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50455 | 42
OKGE | 'MUSKOGEE 345KV' | 20 | 6e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50453 | 42
OKGE | 'MUSKOGEE 345KV' | 20 | 6e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50453 | 42
OKGE | 'ONE OAK 345KV' | 336 | 0.00015 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50444 | 42
OKGE | 'ONE OAK 345KV' | 336 | 0.00015 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50444 | 42
OKGE | 'REDBUD 345KV' | 900 | 0.00017 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50442 | 42
OKGE | 'REDBUD 345KV' | 421.65 | 0.00017 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50442 | 42
OKGE | 'REDBUD 345KV' | 421.65 | 0.00017 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50442 | 42
OKGE | 'REDBUD 345KV' | 900 | 0.00017 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50442 | 42
OKGE | 'SEMINOLE 138KV' | 243.9512 | 0.00023 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50436 | 42
OKGE | 'SEMINOLE 138KV' | 243.9512 | 0.00023 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50436 | 42
OKGE | 'SEMINOLE 345KV' | 507.6 | 0.00023 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50436 | 42
OKGE | 'SEMINOLE 345KV' | 507.6 | 0.00023 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50436 | 42
OKGE | 'SOONER 138KV' | 25 | -0.00038 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50497 | 42
OKGE | 'SOONER 138KV' | 25 | -0.00038 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50497 | 42
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.00199 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50658 | 42
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.00199 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50658 | 42
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00027 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50432 | 43
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00027 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50432 | 43
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00027 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50432 | 43
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00027 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50432 | 43
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00027 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50432 | 43
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00027 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50432 | 43
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.00026 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50433 | 43
OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.00026 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50433 | 43
OKGE | 'MCCLAIN 138KV' | 42 | 0.00044 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50415 | 43
OKGE | 'MCCLAIN 138KV' | 42 | 0.00044 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50415 | 43
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00044 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50415 | 43
OKGE | 'MUSTANG 138KV' | 365.5 | 0.00044 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50415 | 43
OKGE | 'MUSTANG 69KV' | 106 | 0.00049 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.5041 | 43
OKGE | 'MUSTANG 69KV' | 106 | 0.00049 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.5041 | 43
OKGE | 'TINKER 5G 138KV' | 62 | 0.0003 | OKGE | 'FPLWND2 34KV' | 102 | 0.50459 | -0.50429 | 43
OKGE | 'TINKER 5G 138KV' | 62 | 0.0003 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50429 | 43
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | IODINE - WOODWARD 138kV CKT 1
Limiting Facility: | MOORELAND - WOODWARD 69KV CKT 1
Direction: | To->From
Line Outage: | FPL SWITCH - MOORELAND 138KV CKT 1
Flowgate: | 55995560961559995578511206SP
Date Redispatch Needed: | 6/1/06 - 10/1/06
Season Flowgate Identified: | 2006 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1032973 | 0.10638 | 0.10638
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | -0.00055 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.50459 | -0.50514 | 1
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | -0.00055 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50514 | 1
OKGE | 'HORSESHOE LAKE 138KV' | 337.7 | 0.00027 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.50459 | -0.50432 | 1
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00027 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.50459 | -0.50432 | 1
OKGE | 'HORSESHOE LAKE 138KV' | 337.7 | 0.00027 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50432 | 1
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00027 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50432 | 1
OKGE | 'MCCLAIN 138KV' | 42 | 0.00044 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.50459 | -0.50415 | 1
OKGE | 'MCCLAIN 138KV' | 42 | 0.00044 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50415 | 1
OKGE | 'MUSKOGEE 161KV' | 166 | 4e-05 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.50459 | -0.50455 | 1
OKGE | 'MUSKOGEE 161KV' | 31 | 4e-05 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.50459 | -0.50455 | 1
OKGE | 'MUSKOGEE 161KV' | 166 | 4e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50455 | 1
OKGE | 'MUSKOGEE 161KV' | 31 | 4e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50455 | 1
OKGE | 'MUSKOGEE 345KV' | 20 | 6e-05 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.50459 | -0.50453 | 1
OKGE | 'MUSKOGEE 345KV' | 20 | 6e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50453 | 1
OKGE | 'MUSTANG 138KV' | 142.3459 | 0.00044 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.50459 | -0.50415 | 1
OKGE | 'MUSTANG 138KV' | 142.3459 | 0.00044 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50415 | 1
OKGE | 'ONE OAK 345KV' | 261 | 0.00015 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.50459 | -0.50444 | 1
OKGE | 'ONE OAK 345KV' | 261 | 0.00015 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50444 | 1
OKGE | 'REDBUD 345KV' | 253 | 0.00017 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.50459 | -0.50442 | 1
OKGE | 'REDBUD 345KV' | 421.65 | 0.00017 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.50459 | -0.50442 | 1
OKGE | 'REDBUD 345KV' | 253 | 0.00017 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50442 | 1
OKGE | 'REDBUD 345KV' | 421.65 | 0.00017 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50442 | 1
OKGE | 'SEMINOLE 138KV' | 21.7803 | 0.00023 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.50459 | -0.50436 | 1
OKGE | 'SEMINOLE 138KV' | 21.7803 | 0.00023 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50436 | 1
OKGE | 'SOONER 138KV' | 25 | -0.00038 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.50459 | -0.50497 | 1
OKGE | 'SOONER 138KV' | 25 | -0.00038 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50497 | 1
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.00198 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.50459 | -0.50657 | 1
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.00198 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50657 | 1
OKGE | 'TINKER 5G 138KV' | 62 | 0.0003 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.50459 | -0.50429 | 1
OKGE | 'TINKER 5G 138KV' | 62 | 0.0003 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.50459 | -0.50429 | 1
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | IODINE - WOODWARD 138kV CKT 1
Limiting Facility: | WOODWARD - WOODWARD 69KV CKT 1
Direction: | From->To
Line Outage: | FPL SWITCH - MOORELAND 138KV CKT 1
Flowgate: | 56096547821559995578511106SH
Date Redispatch Needed: | 6/1/06 - 10/1/06
Season Flowgate Identified: | 2006 Summer Shoulder
Reservation | Relief Amount | Aggregate Relief Amount
1032973 | 80.1613 | 80.1613
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 80
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 80
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 80
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 80
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 80
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 80
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 80
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 80
OKGE | 'MCCLAIN 138KV' | 42 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 80
OKGE | 'MCCLAIN 138KV' | 42 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 80
OKGE | 'MUSKOGEE 161KV' | 31 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 80
OKGE | 'MUSKOGEE 161KV' | 166 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 80
OKGE | 'MUSKOGEE 161KV' | 31 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 80
OKGE | 'MUSKOGEE 161KV' | 166 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 80
OKGE | 'MUSTANG 138KV' | 365.5 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 80
OKGE | 'MUSTANG 138KV' | 365.5 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 80
OKGE | 'MUSTANG 69KV' | 106 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 80
OKGE | 'MUSTANG 69KV' | 106 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 80
OKGE | 'ONE OAK 345KV' | 236 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 80
OKGE | 'ONE OAK 345KV' | 236 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 80
OKGE | 'REDBUD 345KV' | 460 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 80
OKGE | 'REDBUD 345KV' | 421.65 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 80
OKGE | 'REDBUD 345KV' | 421.65 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 80
OKGE | 'REDBUD 345KV' | 460 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 80
OKGE | 'SEMINOLE 138KV' | 47.215 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 80
OKGE | 'SEMINOLE 138KV' | 47.215 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 80
OKGE | 'SEMINOLE 345KV' | 406.08 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 80
OKGE | 'SEMINOLE 345KV' | 406.08 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 80
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 80
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 80
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | IODINE - WOODWARD 138kV CKT 1
Limiting Facility: | WOODWARD - WOODWARD 69KV CKT 1
Direction: | From->To
Line Outage: | FPL SWITCH - MOORELAND 138KV CKT 1
Flowgate: | 56096547821559995578511206FA
Date Redispatch Needed: | 10/1/06 - 12/1/06
Season Flowgate Identified: | 2006 Fall Peak
Reservation | Relief Amount | Aggregate Relief Amount
1032973 | 71.8837 | 71.8837
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 72
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 72
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 72
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 72
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 72
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 72
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 72
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 72
OKGE | 'MCCLAIN 138KV' | 42 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 72
OKGE | 'MCCLAIN 138KV' | 42 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 72
OKGE | 'MUSKOGEE 161KV' | 31 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 72
OKGE | 'MUSKOGEE 161KV' | 166 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 72
OKGE | 'MUSKOGEE 161KV' | 31 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 72
OKGE | 'MUSKOGEE 161KV' | 166 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 72
OKGE | 'MUSTANG 138KV' | 365.5 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 72
OKGE | 'MUSTANG 138KV' | 365.5 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 72
OKGE | 'MUSTANG 69KV' | 106 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 72
OKGE | 'MUSTANG 69KV' | 106 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 72
OKGE | 'ONE OAK 345KV' | 336 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 72
OKGE | 'ONE OAK 345KV' | 336 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 72
OKGE | 'REDBUD 345KV' | 421.65 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 72
OKGE | 'REDBUD 345KV' | 900 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 72
OKGE | 'REDBUD 345KV' | 421.65 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 72
OKGE | 'REDBUD 345KV' | 900 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 72
OKGE | 'SEMINOLE 138KV' | 243.9512 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 72
OKGE | 'SEMINOLE 138KV' | 243.9512 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 72
OKGE | 'SEMINOLE 345KV' | 507.6 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 72
OKGE | 'SEMINOLE 345KV' | 507.6 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 72
OKGE | 'SOONER 138KV' | 25 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 72
OKGE | 'SOONER 138KV' | 25 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 72
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 72
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 72
OKGE | 'TINKER 5G 138KV' | 62 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 72
OKGE | 'TINKER 5G 138KV' | 62 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 72
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | IODINE - WOODWARD 138kV CKT 1
Limiting Facility: | WOODWARD - WOODWARD 69KV CKT 1
Direction: | From->To
Line Outage: | FPL SWITCH - MOORELAND 138KV CKT 1
Flowgate: | 56096547821559995578511406SP
Date Redispatch Needed: | 6/1/06 - 10/1/06
Season Flowgate Identified: | 2006 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1032973 | 70.9811 | 70.9811
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 71
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 71
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 71
OKGE | 'HORSESHOE LAKE 138KV' | 337.7 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 71
OKGE | 'HORSESHOE LAKE 138KV' | 337.7 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 71
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 71
OKGE | 'MCCLAIN 138KV' | 42 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 71
OKGE | 'MCCLAIN 138KV' | 42 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 71
OKGE | 'MUSKOGEE 161KV' | 166 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 71
OKGE | 'MUSKOGEE 161KV' | 31 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 71
OKGE | 'MUSKOGEE 161KV' | 31 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 71
OKGE | 'MUSKOGEE 161KV' | 166 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 71
OKGE | 'MUSTANG 138KV' | 144.3298 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 71
OKGE | 'MUSTANG 138KV' | 144.3298 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 71
OKGE | 'ONE OAK 345KV' | 261 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 71
OKGE | 'ONE OAK 345KV' | 261 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 71
OKGE | 'REDBUD 345KV' | 253 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 71
OKGE | 'REDBUD 345KV' | 421.65 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 71
OKGE | 'REDBUD 345KV' | 421.65 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 71
OKGE | 'REDBUD 345KV' | 253 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 71
OKGE | 'SOONER 138KV' | 25 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 71
OKGE | 'SOONER 138KV' | 25 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 71
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 71
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 71
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | IODINE - WOODWARD 138kV CKT 1
Limiting Facility: | WOODWARD (WOODWRD2) 138/69/13.2KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | FPL SWITCH - MOORELAND 138KV CKT 1
Flowgate: | WODODWRD21421559995578511106FA
Date Redispatch Needed: | 10/1/06 - 12/1/06
Season Flowgate Identified: | 2006 Fall Peak
Reservation | Relief Amount | Aggregate Relief Amount
1032973 | 82.1629 | 82.1629
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 82
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 82
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 82
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 82
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 82
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 82
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 82
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 82
OKGE | 'MCCLAIN 138KV' | 42 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 82
OKGE | 'MCCLAIN 138KV' | 42 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 82
OKGE | 'MUSKOGEE 161KV' | 166 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 82
OKGE | 'MUSKOGEE 161KV' | 31 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 82
OKGE | 'MUSKOGEE 161KV' | 166 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 82
OKGE | 'MUSKOGEE 161KV' | 31 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 82
OKGE | 'MUSTANG 138KV' | 365.5 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 82
OKGE | 'MUSTANG 138KV' | 365.5 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 82
OKGE | 'MUSTANG 69KV' | 106 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 82
OKGE | 'MUSTANG 69KV' | 106 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 82
OKGE | 'ONE OAK 345KV' | 236 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 82
OKGE | 'ONE OAK 345KV' | 236 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 82
OKGE | 'REDBUD 345KV' | 900 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 82
OKGE | 'REDBUD 345KV' | 421.65 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 82
OKGE | 'REDBUD 345KV' | 421.65 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 82
OKGE | 'REDBUD 345KV' | 900 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 82
OKGE | 'SEMINOLE 138KV' | 262.1816 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 82
OKGE | 'SEMINOLE 138KV' | 262.1816 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 82
OKGE | 'SEMINOLE 345KV' | 507.6 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 82
OKGE | 'SEMINOLE 345KV' | 507.6 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 82
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 82
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 82
OKGE | 'TINKER 5G 138KV' | 62 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 82
OKGE | 'TINKER 5G 138KV' | 62 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 82
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | IODINE - WOODWARD 138kV CKT 1
Limiting Facility: | WOODWARD (WOODWRD2) 138/69/13.2KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | FPL SWITCH - MOORELAND 138KV CKT 1
Flowgate: | WODODWRD21421559995578511106SH
Date Redispatch Needed: | 6/1/06 - 10/1/06
Season Flowgate Identified: | 2006 Summer Shoulder
Reservation | Relief Amount | Aggregate Relief Amount
1032973 | 83.2298 | 83.2298
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 83
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 83
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 83
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 83
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 83
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 83
OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 83
OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 83
OKGE | 'MCCLAIN 138KV' | 42 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 83
OKGE | 'MCCLAIN 138KV' | 42 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 83
OKGE | 'MUSKOGEE 161KV' | 166 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 83
OKGE | 'MUSKOGEE 161KV' | 31 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 83
OKGE | 'MUSKOGEE 161KV' | 166 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 83
OKGE | 'MUSKOGEE 161KV' | 31 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 83
OKGE | 'MUSTANG 138KV' | 365.5 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 83
OKGE | 'MUSTANG 138KV' | 365.5 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 83
OKGE | 'MUSTANG 69KV' | 106 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 83
OKGE | 'MUSTANG 69KV' | 106 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 83
OKGE | 'ONE OAK 345KV' | 236 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 83
OKGE | 'ONE OAK 345KV' | 236 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 83
OKGE | 'REDBUD 345KV' | 421.65 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 83
OKGE | 'REDBUD 345KV' | 460 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 83
OKGE | 'REDBUD 345KV' | 460 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 83
OKGE | 'REDBUD 345KV' | 421.65 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 83
OKGE | 'SEMINOLE 138KV' | 47.215 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 83
OKGE | 'SEMINOLE 138KV' | 47.215 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 83
OKGE | 'SEMINOLE 345KV' | 406.08 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 83
OKGE | 'SEMINOLE 345KV' | 406.08 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 83
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | 0 | OKGE | 'FPLWND2 34KV' | 102 | 1 | -1 | 83
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 83
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | IODINE - WOODWARD 138kV CKT 1
Limiting Facility: | WOODWARD (WOODWRD2) 138/69/13.2KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | FPL SWITCH - MOORELAND 138KV CKT 1
Flowgate: | WODODWRD21421559995578511106SP
Date Redispatch Needed: | 6/1/06 - 10/1/06
Season Flowgate Identified: | 2006 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1032973 | 81.345 | 81.345
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 81
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 81
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 81
OKGE | 'HORSESHOE LAKE 138KV' | 337.7 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 81
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 81
OKGE | 'HORSESHOE LAKE 138KV' | 337.7 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 81
OKGE | 'MCCLAIN 138KV' | 42 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 81
OKGE | 'MCCLAIN 138KV' | 42 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 81
OKGE | 'MUSKOGEE 161KV' | 166 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 81
OKGE | 'MUSKOGEE 161KV' | 31 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 81
OKGE | 'MUSKOGEE 161KV' | 166 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 81
OKGE | 'MUSKOGEE 161KV' | 31 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 81
OKGE | 'MUSTANG 138KV' | 147.8137 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 81
OKGE | 'MUSTANG 138KV' | 147.8137 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 81
OKGE | 'ONE OAK 345KV' | 204 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 81
OKGE | 'ONE OAK 345KV' | 204 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 81
OKGE | 'REDBUD 345KV' | 421.65 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 81
OKGE | 'REDBUD 345KV' | 460 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 81
OKGE | 'REDBUD 345KV' | 460 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 81
OKGE | 'REDBUD 345KV' | 421.65 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 81
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | 0 | OKGE | 'FPLWND2 34KV' | 101.9968 | 1 | -1 | 81
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | 0 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 1 | -1 | 81
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1
Limiting Facility: | KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | CLEO CORNER - GLASS MOUNTAIN 138KV CKT 1
Flowgate: | KNOOBHIL41421547785478811307SP
Date Redispatch Needed: | 6/1/07 - 10/1/07
Season Flowgate Identified: | 2007 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1023236 | 3.0591 | 8.1644
1032973 | 5.1054 | 8.1644
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.0368 | OKGE | 'FPLWND2 34KV' | 102 | 0.12343 | -0.16023 | 51
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.0368 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.1126 | -0.1494 | 55
OKGE | 'SOONER 138KV' | 25 | -0.00627 | OKGE | 'FPLWND2 34KV' | 102 | 0.12343 | -0.1297 | 63
OKGE | 'MUSKOGEE 161KV' | 166 | -0.00016 | OKGE | 'FPLWND2 34KV' | 102 | 0.12343 | -0.12359 | 66
OKGE | 'MUSKOGEE 161KV' | 31 | -0.00016 | OKGE | 'FPLWND2 34KV' | 102 | 0.12343 | -0.12359 | 66
OKGE | 'ONE OAK 345KV' | 179 | -0.00018 | OKGE | 'FPLWND2 34KV' | 102 | 0.12343 | -0.12361 | 66
OKGE | 'REDBUD 345KV' | 900 | 0.00028 | OKGE | 'FPLWND2 34KV' | 102 | 0.12343 | -0.12315 | 66
OKGE | 'REDBUD 345KV' | 421.65 | 0.00028 | OKGE | 'FPLWND2 34KV' | 102 | 0.12343 | -0.12315 | 66
OKGE | 'HORSESHOE LAKE 138KV' | 293.7871 | 0.00116 | OKGE | 'FPLWND2 34KV' | 102 | 0.12343 | -0.12227 | 67
OKGE | 'MCCLAIN 138KV' | 42 | 0.00235 | OKGE | 'FPLWND2 34KV' | 102 | 0.12343 | -0.12108 | 67
OKGE | 'TINKER 5G 138KV' | 62 | 0.0015 | OKGE | 'FPLWND2 34KV' | 102 | 0.12343 | -0.12193 | 67
OKGE | 'SOONER 138KV' | 25 | -0.00627 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.1126 | -0.11887 | 69
OKGE | 'MUSKOGEE 161KV' | 166 | -0.00016 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.1126 | -0.11276 | 72
OKGE | 'MUSKOGEE 161KV' | 31 | -0.00016 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.1126 | -0.11276 | 72
OKGE | 'ONE OAK 345KV' | 179 | -0.00018 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.1126 | -0.11278 | 72
OKGE | 'HORSESHOE LAKE 138KV' | 293.7871 | 0.00116 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.1126 | -0.11144 | 73
OKGE | 'REDBUD 345KV' | 421.65 | 0.00028 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.1126 | -0.11232 | 73
OKGE | 'REDBUD 345KV' | 900 | 0.00028 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.1126 | -0.11232 | 73
OKGE | 'TINKER 5G 138KV' | 62 | 0.0015 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.1126 | -0.1111 | 73
OKGE | 'MCCLAIN 138KV' | 42 | 0.00235 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.1126 | -0.11025 | 74
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1
Limiting Facility: | KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | GLASS MOUNTAIN - MOORELAND 138KV CKT 1
Flowgate: | KNOOBHIL41421547885599911307SP
Date Redispatch Needed: | 6/1/07 - 10/1/07
Season Flowgate Identified: | 2007 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1023236 | 3.3114 | 8.8385
1032973 | 5.5271 | 8.8385
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.0368 | OKGE | 'FPLWND2 34KV' | 102 | 0.12343 | -0.16023 | 55
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.0368 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.1126 | -0.1494 | 59
OKGE | 'SOONER 138KV' | 25 | -0.00627 | OKGE | 'FPLWND2 34KV' | 102 | 0.12343 | -0.1297 | 68
OKGE | 'HORSESHOE LAKE 138KV' | 293.7871 | 0.00116 | OKGE | 'FPLWND2 34KV' | 102 | 0.12343 | -0.12227 | 72
OKGE | 'MUSKOGEE 161KV' | 31 | -0.00016 | OKGE | 'FPLWND2 34KV' | 102 | 0.12343 | -0.12359 | 72
OKGE | 'MUSKOGEE 161KV' | 166 | -0.00016 | OKGE | 'FPLWND2 34KV' | 102 | 0.12343 | -0.12359 | 72
OKGE | 'ONE OAK 345KV' | 179 | -0.00018 | OKGE | 'FPLWND2 34KV' | 102 | 0.12343 | -0.12361 | 72
OKGE | 'REDBUD 345KV' | 900 | 0.00028 | OKGE | 'FPLWND2 34KV' | 102 | 0.12343 | -0.12315 | 72
OKGE | 'REDBUD 345KV' | 421.65 | 0.00028 | OKGE | 'FPLWND2 34KV' | 102 | 0.12343 | -0.12315 | 72
OKGE | 'TINKER 5G 138KV' | 62 | 0.0015 | OKGE | 'FPLWND2 34KV' | 102 | 0.12343 | -0.12193 | 72
OKGE | 'MCCLAIN 138KV' | 42 | 0.00235 | OKGE | 'FPLWND2 34KV' | 102 | 0.12343 | -0.12108 | 73
OKGE | 'SOONER 138KV' | 25 | -0.00627 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.1126 | -0.11887 | 74
OKGE | 'MUSKOGEE 161KV' | 31 | -0.00016 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.1126 | -0.11276 | 78
OKGE | 'MUSKOGEE 161KV' | 166 | -0.00016 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.1126 | -0.11276 | 78
OKGE | 'ONE OAK 345KV' | 179 | -0.00018 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.1126 | -0.11278 | 78
OKGE | 'HORSESHOE LAKE 138KV' | 293.7871 | 0.00116 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.1126 | -0.11144 | 79
OKGE | 'REDBUD 345KV' | 900 | 0.00028 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.1126 | -0.11232 | 79
OKGE | 'REDBUD 345KV' | 421.65 | 0.00028 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.1126 | -0.11232 | 79
OKGE | 'MCCLAIN 138KV' | 42 | 0.00235 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.1126 | -0.11025 | 80
OKGE | 'TINKER 5G 138KV' | 62 | 0.0015 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.1126 | -0.1111 | 80
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1
Limiting Facility: | KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | OKGEMTL-5
Flowgate: | KNOOBHIL41421OKGEMTL-51306SP
Date Redispatch Needed: | 6/1/06 - 10/1/06
Season Flowgate Identified: | 2006 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1032973 | 0.20154 | 0.20154
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.04191 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.09565 | -0.13756 | 1
WFEC | 'ANADARKO 138KV' | 90 | 0.00539 | WFEC | 'MORLND 138KV' | 260.8777 | 0.09573 | -0.09034 | 2
WFEC | 'ANADARKO 138KV' | 3.1503 | 0.00539 | WFEC | 'MORLND 138KV' | 260.8777 | 0.09573 | -0.09034 | 2
WFEC | 'ANADARKO 69KV' | 76 | 0.00519 | WFEC | 'MORLND 138KV' | 260.8777 | 0.09573 | -0.09054 | 2
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | -0.00598 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.09565 | -0.10163 | 2
OKGE | 'CONTINENTAL EMPIRE 138KV' | 63 | -0.00598 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09024 | -0.09622 | 2
OKGE | 'HORSESHOE LAKE 138KV' | 337.7 | 0.00073 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.09565 | -0.09492 | 2
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00073 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.09565 | -0.09492 | 2
OKGE | 'HORSESHOE LAKE 138KV' | 337.7 | 0.00073 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09024 | -0.08951 | 2
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | 0.00073 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09024 | -0.08951 | 2
OKGE | 'MCCLAIN 138KV' | 42 | 0.00158 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.09565 | -0.09407 | 2
OKGE | 'MCCLAIN 138KV' | 42 | 0.00158 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09024 | -0.08866 | 2
OKGE | 'MUSKOGEE 161KV' | 166 | -0.00014 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.09565 | -0.09579 | 2
OKGE | 'MUSKOGEE 161KV' | 31 | -0.00014 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.09565 | -0.09579 | 2
OKGE | 'MUSKOGEE 161KV' | 166 | -0.00014 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09024 | -0.09038 | 2
OKGE | 'MUSKOGEE 161KV' | 31 | -0.00014 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09024 | -0.09038 | 2
OKGE | 'MUSTANG 138KV' | 147.3059 | 0.00139 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.09565 | -0.09426 | 2
OKGE | 'MUSTANG 138KV' | 147.3059 | 0.00139 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09024 | -0.08885 | 2
OMPA | 'OMPA-FAIRVIEW 69KV' | 1.8 | -0.10568 | OMPA | 'OMPA-KINGFISHER BOWMAN 69KV' | 19.7 | 0.00179 | -0.10747 | 2
OMPA | 'OMPA-FAIRVIEW 69KV' | 1.8 | -0.10568 | OMPA | 'OMPA-PONCA CITY 69KV' | 93.647 | -0.00635 | -0.09933 | 2
OKGE | 'ONE OAK 345KV' | 204 | -0.00021 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.09565 | -0.09586 | 2
OKGE | 'ONE OAK 345KV' | 204 | -0.00021 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09024 | -0.09045 | 2
OKGE | 'REDBUD 345KV' | 460 | 0.00013 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.09565 | -0.09552 | 2
OKGE | 'REDBUD 345KV' | 421.65 | 0.00013 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.09565 | -0.09552 | 2
OKGE | 'REDBUD 345KV' | 421.65 | 0.00013 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09024 | -0.09011 | 2
OKGE | 'REDBUD 345KV' | 460 | 0.00013 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09024 | -0.09011 | 2
OKGE | 'SEMINOLE 138KV' | 17.4764 | 0.00096 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.09565 | -0.09469 | 2
OKGE | 'SEMINOLE 138KV' | 17.4764 | 0.00096 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09024 | -0.08928 | 2
OKGE | 'SOONER 138KV' | 25 | -0.00433 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.09565 | -0.09998 | 2
OKGE | 'SOONER 138KV' | 25 | -0.00433 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09024 | -0.09457 | 2
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.04191 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09024 | -0.13215 | 2
OKGE | 'TINKER 5G 138KV' | 62 | 0.00093 | OKGE | 'FPLWND2 34KV' | 101.9968 | 0.09565 | -0.09472 | 2
OKGE | 'TINKER 5G 138KV' | 62 | 0.00093 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.09024 | -0.08931 | 2
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.04191 | OKGE | 'MCCLAIN 138KV' | 478 | 0.00158 | -0.04349 | 5
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.04191 | OKGE | 'MUSKOGEE 345KV' | 1516 | -6e-05 | -0.04185 | 5
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.04191 | OKGE | 'MUSTANG 138KV' | 218.1941 | 0.00139 | -0.0433 | 5
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.04191 | OKGE | 'MUSTANG 69KV' | 106 | 0.00159 | -0.0435 | 5
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.04191 | OKGE | 'ONE OAK 345KV' | 132 | -0.00021 | -0.0417 | 5
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.04191 | OKGE | 'REDBUD 345KV' | 440 | 0.00013 | -0.04204 | 5
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.04191 | OKGE | 'SEMINOLE 138KV' | 487.5236 | 0.00096 | -0.04287 | 5
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.04191 | OKGE | 'SEMINOLE 345KV' | 996 | 0.00081 | -0.04272 | 5
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.04191 | OKGE | 'SMITH COGEN 138KV' | 110 | 0.00134 | -0.04325 | 5
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.04191 | OKGE | 'SOONER 138KV' | 505 | -0.00433 | -0.03758 | 5
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.04191 | OKGE | 'SOONER 345KV' | 513 | -0.0028 | -0.03911 | 5
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1
Limiting Facility: | KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | OKGEMTL-5
Flowgate: | KNOOBHIL41421OKGEMTL-54307SP
Date Redispatch Needed: | 6/1/07 - 10/1/07
Season Flowgate Identified: | 2007 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1023236 | 0.51035 | 1.4566
1032973 | 0.94623 | 1.4566
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.04229 | OKGE | 'FPLWND2 34KV' | 102 | 0.09159 | -0.13388 | 11
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.04229 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.08188 | -0.12417 | 12
OKGE | 'SOONER 138KV' | 25 | -0.00436 | OKGE | 'FPLWND2 34KV' | 102 | 0.09159 | -0.09595 | 15
OKGE | 'HORSESHOE LAKE 138KV' | 293.7871 | 0.00076 | OKGE | 'FPLWND2 34KV' | 102 | 0.09159 | -0.09083 | 16
OKGE | 'MCCLAIN 138KV' | 42 | 0.00155 | OKGE | 'FPLWND2 34KV' | 102 | 0.09159 | -0.09004 | 16
OKGE | 'MUSKOGEE 161KV' | 166 | -0.00013 | OKGE | 'FPLWND2 34KV' | 102 | 0.09159 | -0.09172 | 16
OKGE | 'MUSKOGEE 161KV' | 31 | -0.00013 | OKGE | 'FPLWND2 34KV' | 102 | 0.09159 | -0.09172 | 16
OKGE | 'MUSKOGEE 345KV' | 20 | -7e-05 | OKGE | 'FPLWND2 34KV' | 102 | 0.09159 | -0.09166 | 16
OKGE | 'ONE OAK 345KV' | 204 | -0.00014 | OKGE | 'FPLWND2 34KV' | 102 | 0.09159 | -0.09173 | 16
OKGE | 'REDBUD 345KV' | 900 | 0.00017 | OKGE | 'FPLWND2 34KV' | 102 | 0.09159 | -0.09142 | 16
OKGE | 'REDBUD 345KV' | 421.65 | 0.00017 | OKGE | 'FPLWND2 34KV' | 102 | 0.09159 | -0.09142 | 16
OKGE | 'SEMINOLE 138KV' | 20.0377 | 0.00099 | OKGE | 'FPLWND2 34KV' | 102 | 0.09159 | -0.0906 | 16
OKGE | 'TINKER 5G 138KV' | 62 | 0.00099 | OKGE | 'FPLWND2 34KV' | 102 | 0.09159 | -0.0906 | 16
OKGE | 'SOONER 138KV' | 25 | -0.00436 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.08188 | -0.08624 | 17
OKGE | 'HORSESHOE LAKE 138KV' | 293.7871 | 0.00076 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.08188 | -0.08112 | 18
OKGE | 'MCCLAIN 138KV' | 42 | 0.00155 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.08188 | -0.08033 | 18
OKGE | 'MUSKOGEE 161KV' | 31 | -0.00013 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.08188 | -0.08201 | 18
OKGE | 'MUSKOGEE 161KV' | 166 | -0.00013 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.08188 | -0.08201 | 18
OKGE | 'MUSKOGEE 345KV' | 20 | -7e-05 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.08188 | -0.08195 | 18
OKGE | 'ONE OAK 345KV' | 204 | -0.00014 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.08188 | -0.08202 | 18
OKGE | 'REDBUD 345KV' | 421.65 | 0.00017 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.08188 | -0.08171 | 18
OKGE | 'REDBUD 345KV' | 900 | 0.00017 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.08188 | -0.08171 | 18
OKGE | 'SEMINOLE 138KV' | 20.0377 | 0.00099 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.08188 | -0.08089 | 18
OKGE | 'TINKER 5G 138KV' | 62 | 0.00099 | OKGE | 'SLEEPING BEAR 34KV' | 120 | 0.08188 | -0.08089 | 18
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.04229 | OKGE | 'MCCLAIN 138KV' | 478 | 0.00155 | -0.04384 | 33
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.04229 | OKGE | 'MUSTANG 138KV' | 365.5 | 0.00148 | -0.04377 | 33
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.04229 | OKGE | 'MUSTANG 69KV' | 106 | 0.00169 | -0.04398 | 33
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.04229 | OKGE | 'SMITH COGEN 138KV' | 110 | 0.00144 | -0.04373 | 33
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.04229 | OKGE | 'AES 161KV' | 320 | -1e-05 | -0.04228 | 34
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.04229 | OKGE | 'HORSESHOE LAKE 138KV' | 380 | 0.00076 | -0.04305 | 34
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.04229 | OKGE | 'HORSESHOE LAKE 138KV' | 86.7129 | 0.00076 | -0.04305 | 34
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.04229 | OKGE | 'HORSESHOE LAKE 138KV' | 91 | 0.00076 | -0.04305 | 34
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.04229 | OKGE | 'HORSESHOE LAKE 69KV' | 16 | 0.00079 | -0.04308 | 34
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.04229 | OKGE | 'MUSKOGEE 345KV' | 1516 | -7e-05 | -0.04222 | 34
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.04229 | OKGE | 'SEMINOLE 138KV' | 484.9624 | 0.00099 | -0.04328 | 34
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.04229 | OKGE | 'SEMINOLE 345KV' | 996 | 0.00085 | -0.04314 | 34
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.04229 | OKGE | 'ONE OAK 345KV' | 132 | -0.00014 | -0.04215 | 35
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.04229 | OKGE | 'SOONER 345KV' | 513 | -0.00281 | -0.03948 | 37
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.04229 | OKGE | 'SOONER 138KV' | 505 | -0.00436 | -0.03793 | 38
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | LINWOOD - MCWILLIE STREET 138KV CKT 1
Limiting Facility: | LINWOOD - MCWILLIE STREET 138KV CKT 1
Direction: | From->To
Line Outage: | HARTS ISLAND - SOUTH SHREVEPORT 138KV CKT 1
Flowgate: | 53422534281534145344611407SP
Date Redispatch Needed: | 6/1/07 - 10/1/07
Season Flowgate Identified: | 2007 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
1023236 | 2.804 | 2.804
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.36071 | AEPW | 'COGENTRIX 345KV' | 200 | -0.00424 | -0.35647 | 8
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.36071 | AEPW | 'COMANCHE 138KV' | 160 | -0.00564 | -0.35507 | 8
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.36071 | AEPW | 'COMANCHE 69KV' | 63 | -0.00565 | -0.35506 | 8
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.36071 | AEPW | 'EASTMAN 138KV' | 355 | -0.01329 | -0.34742 | 8
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.36071 | AEPW | 'FITZHUGH 161KV' | 126 | -0.00242 | -0.35829 | 8
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.36071 | AEPW | 'KNOXLEE 138KV' | 284 | -0.00944 | -0.35127 | 8
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.36071 | AEPW | 'LEBROCK 345KV' | 365 | -0.01842 | -0.34229 | 8
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.36071 | AEPW | 'NORTHEASTERN STATION 138KV' | 405 | -0.00393 | -0.35678 | 8
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.36071 | AEPW | 'NORTHEASTERN STATION 138KV' | 95 | -0.00393 | -0.35678 | 8
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.36071 | AEPW | 'NORTHEASTERN STATION 345KV' | 645 | -0.00391 | -0.3568 | 8
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.36071 | AEPW | 'OEC 345KV' | 269 | -0.00412 | -0.35659 | 8
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.36071 | AEPW | 'PIRKEY GENERATION 138KV' | 248 | -0.02472 | -0.33599 | 8
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.36071 | AEPW | 'RIVERSIDE STATION 138KV' | 669 | -0.00425 | -0.35646 | 8
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.36071 | AEPW | 'SOUTHWESTERN STATION 138KV' | 355 | -0.00558 | -0.35513 | 8
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.36071 | AEPW | 'TULSA POWER STATION 138KV' | 112 | -0.00421 | -0.3565 | 8
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.36071 | AEPW | 'TULSA POWER STATION 138KV' | 147 | -0.00421 | -0.3565 | 8
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.36071 | AEPW | 'WELEETKA 138KV' | 70 | -0.00513 | -0.35558 | 8
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.36071 | AEPW | 'WELSH 345KV' | 990 | -0.01281 | -0.3479 | 8
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.36071 | AEPW | 'WILKES 138KV' | 388.4218 | -0.02872 | -0.33199 | 8
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.36071 | AEPW | 'WILKES 345KV' | 311 | -0.01662 | -0.34409 | 8
AEPW | 'LIEBERMAN 138KV' | 137 | -0.21194 | AEPW | 'FITZHUGH 161KV' | 126 | -0.00242 | -0.20952 | 13
AEPW | 'LIEBERMAN 138KV' | 137 | -0.21194 | AEPW | 'NORTHEASTERN STATION 138KV' | 405 | -0.00393 | -0.20801 | 13
AEPW | 'LIEBERMAN 138KV' | 137 | -0.21194 | AEPW | 'NORTHEASTERN STATION 138KV' | 95 | -0.00393 | -0.20801 | 13
AEPW | 'LIEBERMAN 138KV' | 137 | -0.21194 | AEPW | 'NORTHEASTERN STATION 345KV' | 645 | -0.00391 | -0.20803 | 13
AEPW | 'LIEBERMAN 138KV' | 137 | -0.21194 | AEPW | 'OEC 345KV' | 269 | -0.00412 | -0.20782 | 13
AEPW | 'LIEBERMAN 138KV' | 137 | -0.21194 | AEPW | 'TULSA POWER STATION 138KV' | 112 | -0.00421 | -0.20773 | 13
AEPW | 'LIEBERMAN 138KV' | 137 | -0.21194 | AEPW | 'TULSA POWER STATION 138KV' | 147 | -0.00421 | -0.20773 | 13
AEPW | 'LIEBERMAN 138KV' | 137 | -0.21194 | AEPW | 'COGENTRIX 345KV' | 200 | -0.00424 | -0.2077 | 14
AEPW | 'LIEBERMAN 138KV' | 137 | -0.21194 | AEPW | 'COMANCHE 138KV' | 160 | -0.00564 | -0.2063 | 14
AEPW | 'LIEBERMAN 138KV' | 137 | -0.21194 | AEPW | 'COMANCHE 69KV' | 63 | -0.00565 | -0.20629 | 14
AEPW | 'LIEBERMAN 138KV' | 137 | -0.21194 | AEPW | 'EASTMAN 138KV' | 355 | -0.01329 | -0.19865 | 14
AEPW | 'LIEBERMAN 138KV' | 137 | -0.21194 | AEPW | 'KNOXLEE 138KV' | 284 | -0.00944 | -0.2025 | 14
AEPW | 'LIEBERMAN 138KV' | 137 | -0.21194 | AEPW | 'LEBROCK 345KV' | 365 | -0.01842 | -0.19352 | 14
AEPW | 'LIEBERMAN 138KV' | 137 | -0.21194 | AEPW | 'RIVERSIDE STATION 138KV' | 669 | -0.00425 | -0.20769 | 14
AEPW | 'LIEBERMAN 138KV' | 137 | -0.21194 | AEPW | 'SOUTHWESTERN STATION 138KV' | 355 | -0.00558 | -0.20636 | 14
AEPW | 'LIEBERMAN 138KV' | 137 | -0.21194 | AEPW | 'WELEETKA 138KV' | 70 | -0.00513 | -0.20681 | 14
AEPW | 'LIEBERMAN 138KV' | 137 | -0.21194 | AEPW | 'WELSH 345KV' | 990 | -0.01281 | -0.19913 | 14
AEPW | 'LIEBERMAN 138KV' | 137 | -0.21194 | AEPW | 'WILKES 345KV' | 311 | -0.01662 | -0.19532 | 14
AEPW | 'LIEBERMAN 138KV' | 137 | -0.21194 | AEPW | 'PIRKEY GENERATION 138KV' | 248 | -0.02472 | -0.18722 | 15
AEPW | 'LIEBERMAN 138KV' | 137 | -0.21194 | AEPW | 'WILKES 138KV' | 388.4218 | -0.02872 | -0.18322 | 15
AEPW | 'ARSENAL HILL 69KV' | 75 | -0.36071 | AEPW | 'LIEBERMAN 138KV' | 91 | -0.21194 | -0.14877 | 19
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | PENNSYLVANIA - WESTMOORE 138KV CKT 1
Limiting Facility: | PENNSYLVANIA - WESTMOORE 138KV CKT 1
Direction: | To->From
Line Outage: | CIMARRON - CZECH HALL 138KV CKT 1
Flowgate: | 54925548871548985489412307FA
Date Redispatch Needed: | Starting 2007 10/1 - 12/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 Fall Peak
Reservation | Relief Amount | Aggregate Relief Amount
1032973 | 4.4892 | 4.4892
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'SMITH COGEN 138KV' | 110 | -0.21281 | OKGE | 'MCCLAIN 138KV' | 478 | 0.32194 | -0.53475 | 8
OKGE | 'MUSTANG 138KV' | 365.5 | -0.16736 | OKGE | 'MCCLAIN 138KV' | 478 | 0.32194 | -0.4893 | 9
OKGE | 'MUSTANG 69KV' | 106 | -0.15652 | OKGE | 'MCCLAIN 138KV' | 478 | 0.32194 | -0.47846 | 9
OKGE | 'HORSESHOE LAKE 138KV' | 380 | -0.05493 | OKGE | 'MCCLAIN 138KV' | 478 | 0.32194 | -0.37687 | 12
OKGE | 'HORSESHOE LAKE 138KV' | 91 | -0.05493 | OKGE | 'MCCLAIN 138KV' | 478 | 0.32194 | -0.37687 | 12
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | -0.05493 | OKGE | 'MCCLAIN 138KV' | 478 | 0.32194 | -0.37687 | 12
OKGE | 'HORSESHOE LAKE 69KV' | 16 | -0.05468 | OKGE | 'MCCLAIN 138KV' | 478 | 0.32194 | -0.37662 | 12
OKGE | 'ONE OAK 345KV' | 236 | -0.01201 | OKGE | 'MCCLAIN 138KV' | 478 | 0.32194 | -0.33395 | 13
OKGE | 'REDBUD 345KV' | 900 | -0.01473 | OKGE | 'MCCLAIN 138KV' | 478 | 0.32194 | -0.33667 | 13
OKGE | 'REDBUD 345KV' | 421.65 | -0.01473 | OKGE | 'MCCLAIN 138KV' | 478 | 0.32194 | -0.33667 | 13
OKGE | 'TINKER 5G 138KV' | 62 | -0.03232 | OKGE | 'MCCLAIN 138KV' | 478 | 0.32194 | -0.35426 | 13
OKGE | 'CONTINENTAL EMPIRE 138KV' | 64 | -0.00716 | OKGE | 'MCCLAIN 138KV' | 478 | 0.32194 | -0.3291 | 14
OKGE | 'MUSKOGEE 161KV' | 166 | -0.00241 | OKGE | 'MCCLAIN 138KV' | 478 | 0.32194 | -0.32435 | 14
OKGE | 'MUSKOGEE 161KV' | 31 | -0.00241 | OKGE | 'MCCLAIN 138KV' | 478 | 0.32194 | -0.32435 | 14
OKGE | 'MUSKOGEE 345KV' | 20 | -0.00225 | OKGE | 'MCCLAIN 138KV' | 478 | 0.32194 | -0.32419 | 14
OKGE | 'SEMINOLE 138KV' | 47.691 | 0.00867 | OKGE | 'MCCLAIN 138KV' | 478 | 0.32194 | -0.31327 | 14
OKGE | 'SEMINOLE 345KV' | 406.08 | 0.00924 | OKGE | 'MCCLAIN 138KV' | 478 | 0.32194 | -0.3127 | 14
OKGE | 'SOONER 138KV' | 25 | -0.00825 | OKGE | 'MCCLAIN 138KV' | 478 | 0.32194 | -0.33019 | 14
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.00605 | OKGE | 'MCCLAIN 138KV' | 478 | 0.32194 | -0.32799 | 14
OKGE | 'WOODWARD 24KV' | 9.3 | 0.0058 | OKGE | 'MCCLAIN 138KV' | 478 | 0.32194 | -0.31614 | 14
OKGE | 'SMITH COGEN 138KV' | 110 | -0.21281 | OKGE | 'SEMINOLE 138KV' | 457.309 | 0.00867 | -0.22148 | 20
OKGE | 'SMITH COGEN 138KV' | 110 | -0.21281 | OKGE | 'SEMINOLE 345KV' | 590.52 | 0.00924 | -0.22205 | 20
OKGE | 'SMITH COGEN 138KV' | 110 | -0.21281 | OKGE | 'AES 161KV' | 320 | -0.00018 | -0.21263 | 21
OKGE | 'SMITH COGEN 138KV' | 110 | -0.21281 | OKGE | 'FPLWND2 34KV' | 43.0032 | 0.0052 | -0.21801 | 21
OKGE | 'SMITH COGEN 138KV' | 110 | -0.21281 | OKGE | 'MUSKOGEE 345KV' | 1516 | -0.00225 | -0.21056 | 21
OKGE | 'SMITH COGEN 138KV' | 110 | -0.21281 | OKGE | 'ONE OAK 345KV' | 100 | -0.01201 | -0.2008 | 22
OKGE | 'SMITH COGEN 138KV' | 110 | -0.21281 | OKGE | 'SOONER 138KV' | 505 | -0.00825 | -0.20456 | 22
OKGE | 'SMITH COGEN 138KV' | 110 | -0.21281 | OKGE | 'SOONER 345KV' | 513 | -0.00735 | -0.20546 | 22
OKGE | 'MUSTANG 138KV' | 365.5 | -0.16736 | OKGE | 'SEMINOLE 345KV' | 590.52 | 0.00924 | -0.1766 | 25
OKGE | 'MUSTANG 138KV' | 365.5 | -0.16736 | OKGE | 'FPLWND2 34KV' | 43.0032 | 0.0052 | -0.17256 | 26
OKGE | 'MUSTANG 138KV' | 365.5 | -0.16736 | OKGE | 'SEMINOLE 138KV' | 457.309 | 0.00867 | -0.17603 | 26
OKGE | 'MUSTANG 138KV' | 365.5 | -0.16736 | OKGE | 'AES 161KV' | 320 | -0.00018 | -0.16718 | 27
OKGE | 'MUSTANG 138KV' | 365.5 | -0.16736 | OKGE | 'MUSKOGEE 345KV' | 1516 | -0.00225 | -0.16511 | 27
OKGE | 'MUSTANG 69KV' | 106 | -0.15652 | OKGE | 'SEMINOLE 138KV' | 457.309 | 0.00867 | -0.16519 | 27
OKGE | 'MUSTANG 69KV' | 106 | -0.15652 | OKGE | 'SEMINOLE 345KV' | 590.52 | 0.00924 | -0.16576 | 27
OKGE | 'MUSTANG 138KV' | 365.5 | -0.16736 | OKGE | 'SOONER 138KV' | 505 | -0.00825 | -0.15911 | 28
OKGE | 'MUSTANG 138KV' | 365.5 | -0.16736 | OKGE | 'SOONER 345KV' | 513 | -0.00735 | -0.16001 | 28
OKGE | 'MUSTANG 69KV' | 106 | -0.15652 | OKGE | 'FPLWND2 34KV' | 43.0032 | 0.0052 | -0.16172 | 28
OKGE | 'MUSTANG 138KV' | 365.5 | -0.16736 | OKGE | 'ONE OAK 345KV' | 100 | -0.01201 | -0.15535 | 29
OKGE | 'MUSTANG 69KV' | 106 | -0.15652 | OKGE | 'AES 161KV' | 320 | -0.00018 | -0.15634 | 29
OKGE | 'MUSTANG 69KV' | 106 | -0.15652 | OKGE | 'MUSKOGEE 345KV' | 1516 | -0.00225 | -0.15427 | 29
OKGE | 'MUSTANG 69KV' | 106 | -0.15652 | OKGE | 'SOONER 138KV' | 505 | -0.00825 | -0.14827 | 30
OKGE | 'MUSTANG 69KV' | 106 | -0.15652 | OKGE | 'SOONER 345KV' | 513 | -0.00735 | -0.14917 | 30
OKGE | 'MUSTANG 69KV' | 106 | -0.15652 | OKGE | 'ONE OAK 345KV' | 100 | -0.01201 | -0.14451 | 31
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | -0.05493 | OKGE | 'SEMINOLE 345KV' | 590.52 | 0.00924 | -0.06417 | 70
OKGE | 'HORSESHOE LAKE 138KV' | 91 | -0.05493 | OKGE | 'SEMINOLE 345KV' | 590.52 | 0.00924 | -0.06417 | 70
OKGE | 'HORSESHOE LAKE 138KV' | 380 | -0.05493 | OKGE | 'SEMINOLE 345KV' | 590.52 | 0.00924 | -0.06417 | 70
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | -0.05493 | OKGE | 'SEMINOLE 138KV' | 457.309 | 0.00867 | -0.0636 | 71
OKGE | 'HORSESHOE LAKE 138KV' | 91 | -0.05493 | OKGE | 'SEMINOLE 138KV' | 457.309 | 0.00867 | -0.0636 | 71
OKGE | 'HORSESHOE LAKE 138KV' | 380 | -0.05493 | OKGE | 'SEMINOLE 138KV' | 457.309 | 0.00867 | -0.0636 | 71
OKGE | 'HORSESHOE LAKE 138KV' | 91 | -0.05493 | OKGE | 'FPLWND2 34KV' | 43.0032 | 0.0052 | -0.06013 | 75
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | -0.05493 | OKGE | 'FPLWND2 34KV' | 43.0032 | 0.0052 | -0.06013 | 75
OKGE | 'HORSESHOE LAKE 138KV' | 380 | -0.05493 | OKGE | 'FPLWND2 34KV' | 43.0032 | 0.0052 | -0.06013 | 75
OKGE | 'HORSESHOE LAKE 138KV' | 91 | -0.05493 | OKGE | 'AES 161KV' | 320 | -0.00018 | -0.05475 | 82
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | -0.05493 | OKGE | 'AES 161KV' | 320 | -0.00018 | -0.05475 | 82
OKGE | 'HORSESHOE LAKE 138KV' | 380 | -0.05493 | OKGE | 'AES 161KV' | 320 | -0.00018 | -0.05475 | 82
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | -0.05493 | OKGE | 'MUSKOGEE 345KV' | 1516 | -0.00225 | -0.05268 | 85
OKGE | 'HORSESHOE LAKE 138KV' | 91 | -0.05493 | OKGE | 'MUSKOGEE 345KV' | 1516 | -0.00225 | -0.05268 | 85
OKGE | 'HORSESHOE LAKE 138KV' | 380 | -0.05493 | OKGE | 'MUSKOGEE 345KV' | 1516 | -0.00225 | -0.05268 | 85
OKGE | 'HORSESHOE LAKE 138KV' | 380 | -0.05493 | OKGE | 'SOONER 345KV' | 513 | -0.00735 | -0.04758 | 94
OKGE | 'HORSESHOE LAKE 138KV' | 91 | -0.05493 | OKGE | 'SOONER 345KV' | 513 | -0.00735 | -0.04758 | 94
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | -0.05493 | OKGE | 'SOONER 345KV' | 513 | -0.00735 | -0.04758 | 94
OKGE | 'HORSESHOE LAKE 138KV' | 91 | -0.05493 | OKGE | 'SOONER 138KV' | 505 | -0.00825 | -0.04668 | 96
OKGE | 'HORSESHOE LAKE 138KV' | 380 | -0.05493 | OKGE | 'SOONER 138KV' | 505 | -0.00825 | -0.04668 | 96
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | -0.05493 | OKGE | 'SOONER 138KV' | 505 | -0.00825 | -0.04668 | 96
OKGE | 'HORSESHOE LAKE 138KV' | 91 | -0.05493 | OKGE | 'ONE OAK 345KV' | 100 | -0.01201 | -0.04292 | 105
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | -0.05493 | OKGE | 'ONE OAK 345KV' | 100 | -0.01201 | -0.04292 | 105
OKGE | 'HORSESHOE LAKE 138KV' | 380 | -0.05493 | OKGE | 'ONE OAK 345KV' | 100 | -0.01201 | -0.04292 | 105
OKGE | 'TINKER 5G 138KV' | 62 | -0.03232 | OKGE | 'SEMINOLE 345KV' | 590.52 | 0.00924 | -0.04156 | 108
OKGE | 'TINKER 5G 138KV' | 62 | -0.03232 | OKGE | 'SEMINOLE 138KV' | 457.309 | 0.00867 | -0.04099 | 110
OKGE | 'TINKER 5G 138KV' | 62 | -0.03232 | OKGE | 'FPLWND2 34KV' | 43.0032 | 0.0052 | -0.03752 | 120
OKGE | 'TINKER 5G 138KV' | 62 | -0.03232 | OKGE | 'AES 161KV' | 320 | -0.00018 | -0.03214 | 140
OKGE | 'TINKER 5G 138KV' | 62 | -0.03232 | OKGE | 'MUSKOGEE 345KV' | 1516 | -0.00225 | -0.03007 | 149
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | PENNSYLVANIA - WESTMOORE 138KV CKT 1
Limiting Facility: | PENNSYLVANIA - WESTMOORE 138KV CKT 1
Direction: | To->From
Line Outage: | HOLLYWOOD - INDIAN HILLS 138KV CKT 1
Flowgate: | 54925548871549535495412307FA
Date Redispatch Needed: | Starting 2007 10/1 - 12/1 Until EOC of Upgrade
Season Flowgate Identified: | 2007 Fall Peak
Reservation | Relief Amount | Aggregate Relief Amount
977481 | 0.8025 | 0.8025
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
OKGE | 'SMITH COGEN 138KV' | 110 | -0.19229 | OKGE | 'MCCLAIN 138KV' | 478 | 0.35498 | -0.54727 | 1
OKGE | 'CONTINENTAL EMPIRE 138KV' | 64 | -0.01233 | OKGE | 'MCCLAIN 138KV' | 478 | 0.35498 | -0.36731 | 2
OKGE | 'HORSESHOE LAKE 138KV' | 91 | -0.0583 | OKGE | 'MCCLAIN 138KV' | 478 | 0.35498 | -0.41328 | 2
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | -0.0583 | OKGE | 'MCCLAIN 138KV' | 478 | 0.35498 | -0.41328 | 2
OKGE | 'HORSESHOE LAKE 138KV' | 380 | -0.0583 | OKGE | 'MCCLAIN 138KV' | 478 | 0.35498 | -0.41328 | 2
OKGE | 'HORSESHOE LAKE 69KV' | 16 | -0.056 | OKGE | 'MCCLAIN 138KV' | 478 | 0.35498 | -0.41098 | 2
OKGE | 'MUSKOGEE 161KV' | 166 | -0.0016 | OKGE | 'MCCLAIN 138KV' | 478 | 0.35498 | -0.35658 | 2
OKGE | 'MUSKOGEE 161KV' | 31 | -0.0016 | OKGE | 'MCCLAIN 138KV' | 478 | 0.35498 | -0.35658 | 2
OKGE | 'MUSKOGEE 345KV' | 20 | -0.00178 | OKGE | 'MCCLAIN 138KV' | 478 | 0.35498 | -0.35676 | 2
OKGE | 'MUSTANG 138KV' | 365.5 | -0.13538 | OKGE | 'MCCLAIN 138KV' | 478 | 0.35498 | -0.49036 | 2
OKGE | 'MUSTANG 69KV' | 106 | -0.13972 | OKGE | 'MCCLAIN 138KV' | 478 | 0.35498 | -0.4947 | 2
OKGE | 'ONE OAK 345KV' | 236 | -0.01875 | OKGE | 'MCCLAIN 138KV' | 478 | 0.35498 | -0.37373 | 2
OKGE | 'REDBUD 345KV' | 421.65 | -0.01763 | OKGE | 'MCCLAIN 138KV' | 478 | 0.35498 | -0.37261 | 2
OKGE | 'REDBUD 345KV' | 900 | -0.01763 | OKGE | 'MCCLAIN 138KV' | 478 | 0.35498 | -0.37261 | 2
OKGE | 'SEMINOLE 138KV' | 47.691 | 0.01443 | OKGE | 'MCCLAIN 138KV' | 478 | 0.35498 | -0.34055 | 2
OKGE | 'SEMINOLE 345KV' | 406.08 | 0.01418 | OKGE | 'MCCLAIN 138KV' | 478 | 0.35498 | -0.3408 | 2
OKGE | 'SOONER 138KV' | 25 | -0.01389 | OKGE | 'MCCLAIN 138KV' | 478 | 0.35498 | -0.36887 | 2
OKGE | 'SOUTH 4TH ST 69KV' | 42.7 | -0.01312 | OKGE | 'MCCLAIN 138KV' | 478 | 0.35498 | -0.3681 | 2
OKGE | 'TINKER 5G 138KV' | 62 | -0.02998 | OKGE | 'MCCLAIN 138KV' | 478 | 0.35498 | -0.38496 | 2
OKGE | 'WOODWARD 24KV' | 9.3 | -0.00592 | OKGE | 'MCCLAIN 138KV' | 478 | 0.35498 | -0.3609 | 2
OKGE | 'SMITH COGEN 138KV' | 110 | -0.19229 | OKGE | 'AES 161KV' | 320 | 0.00089 | -0.19318 | 4
OKGE | 'SMITH COGEN 138KV' | 110 | -0.19229 | OKGE | 'FPLWND2 34KV' | 43.0032 | -0.00582 | -0.18647 | 4
OKGE | 'SMITH COGEN 138KV' | 110 | -0.19229 | OKGE | 'MUSKOGEE 345KV' | 1516 | -0.00178 | -0.19051 | 4
OKGE | 'SMITH COGEN 138KV' | 110 | -0.19229 | OKGE | 'SEMINOLE 138KV' | 457.309 | 0.01443 | -0.20672 | 4
OKGE | 'SMITH COGEN 138KV' | 110 | -0.19229 | OKGE | 'SEMINOLE 345KV' | 590.52 | 0.01418 | -0.20647 | 4
OKGE | 'SMITH COGEN 138KV' | 110 | -0.19229 | OKGE | 'SOONER 138KV' | 505 | -0.01389 | -0.1784 | 4
OKGE | 'SMITH COGEN 138KV' | 110 | -0.19229 | OKGE | 'SOONER 345KV' | 513 | -0.01395 | -0.17834 | 4
OKGE | 'MUSTANG 138KV' | 365.5 | -0.13538 | OKGE | 'SEMINOLE 138KV' | 457.309 | 0.01443 | -0.14981 | 5
OKGE | 'MUSTANG 138KV' | 365.5 | -0.13538 | OKGE | 'SEMINOLE 345KV' | 590.52 | 0.01418 | -0.14956 | 5
OKGE | 'MUSTANG 69KV' | 106 | -0.13972 | OKGE | 'SEMINOLE 138KV' | 457.309 | 0.01443 | -0.15415 | 5
OKGE | 'MUSTANG 69KV' | 106 | -0.13972 | OKGE | 'SEMINOLE 345KV' | 590.52 | 0.01418 | -0.1539 | 5
OKGE | 'SMITH COGEN 138KV' | 110 | -0.19229 | OKGE | 'ONE OAK 345KV' | 100 | -0.01875 | -0.17354 | 5
OKGE | 'MUSTANG 138KV' | 365.5 | -0.13538 | OKGE | 'AES 161KV' | 320 | 0.00089 | -0.13627 | 6
OKGE | 'MUSTANG 138KV' | 365.5 | -0.13538 | OKGE | 'FPLWND2 34KV' | 43.0032 | -0.00582 | -0.12956 | 6
OKGE | 'MUSTANG 138KV' | 365.5 | -0.13538 | OKGE | 'MUSKOGEE 345KV' | 1516 | -0.00178 | -0.1336 | 6
OKGE | 'MUSTANG 69KV' | 106 | -0.13972 | OKGE | 'AES 161KV' | 320 | 0.00089 | -0.14061 | 6
OKGE | 'MUSTANG 69KV' | 106 | -0.13972 | OKGE | 'FPLWND2 34KV' | 43.0032 | -0.00582 | -0.1339 | 6
OKGE | 'MUSTANG 69KV' | 106 | -0.13972 | OKGE | 'MUSKOGEE 345KV' | 1516 | -0.00178 | -0.13794 | 6
OKGE | 'MUSTANG 69KV' | 106 | -0.13972 | OKGE | 'SOONER 138KV' | 505 | -0.01389 | -0.12583 | 6
OKGE | 'MUSTANG 69KV' | 106 | -0.13972 | OKGE | 'SOONER 345KV' | 513 | -0.01395 | -0.12577 | 6
OKGE | 'MUSTANG 138KV' | 365.5 | -0.13538 | OKGE | 'ONE OAK 345KV' | 100 | -0.01875 | -0.11663 | 7
OKGE | 'MUSTANG 138KV' | 365.5 | -0.13538 | OKGE | 'SOONER 138KV' | 505 | -0.01389 | -0.12149 | 7
OKGE | 'MUSTANG 138KV' | 365.5 | -0.13538 | OKGE | 'SOONER 345KV' | 513 | -0.01395 | -0.12143 | 7
OKGE | 'MUSTANG 69KV' | 106 | -0.13972 | OKGE | 'ONE OAK 345KV' | 100 | -0.01875 | -0.12097 | 7
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | -0.0583 | OKGE | 'SEMINOLE 138KV' | 457.309 | 0.01443 | -0.07273 | 11
OKGE | 'HORSESHOE LAKE 138KV' | 91 | -0.0583 | OKGE | 'SEMINOLE 138KV' | 457.309 | 0.01443 | -0.07273 | 11
OKGE | 'HORSESHOE LAKE 138KV' | 380 | -0.0583 | OKGE | 'SEMINOLE 138KV' | 457.309 | 0.01443 | -0.07273 | 11
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | -0.0583 | OKGE | 'SEMINOLE 345KV' | 590.52 | 0.01418 | -0.07248 | 11
OKGE | 'HORSESHOE LAKE 138KV' | 380 | -0.0583 | OKGE | 'SEMINOLE 345KV' | 590.52 | 0.01418 | -0.07248 | 11
OKGE | 'HORSESHOE LAKE 138KV' | 91 | -0.0583 | OKGE | 'SEMINOLE 345KV' | 590.52 | 0.01418 | -0.07248 | 11
OKGE | 'HORSESHOE LAKE 69KV' | 16 | -0.056 | OKGE | 'SEMINOLE 138KV' | 457.309 | 0.01443 | -0.07043 | 11
OKGE | 'HORSESHOE LAKE 69KV' | 16 | -0.056 | OKGE | 'SEMINOLE 345KV' | 590.52 | 0.01418 | -0.07018 | 11
OKGE | 'HORSESHOE LAKE 138KV' | 380 | -0.0583 | OKGE | 'AES 161KV' | 320 | 0.00089 | -0.05919 | 14
OKGE | 'HORSESHOE LAKE 138KV' | 91 | -0.0583 | OKGE | 'AES 161KV' | 320 | 0.00089 | -0.05919 | 14
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | -0.0583 | OKGE | 'AES 161KV' | 320 | 0.00089 | -0.05919 | 14
OKGE | 'HORSESHOE LAKE 138KV' | 380 | -0.0583 | OKGE | 'MUSKOGEE 345KV' | 1516 | -0.00178 | -0.05652 | 14
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | -0.0583 | OKGE | 'MUSKOGEE 345KV' | 1516 | -0.00178 | -0.05652 | 14
OKGE | 'HORSESHOE LAKE 138KV' | 91 | -0.0583 | OKGE | 'MUSKOGEE 345KV' | 1516 | -0.00178 | -0.05652 | 14
OKGE | 'HORSESHOE LAKE 69KV' | 16 | -0.056 | OKGE | 'AES 161KV' | 320 | 0.00089 | -0.05689 | 14
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | -0.0583 | OKGE | 'FPLWND2 34KV' | 43.0032 | -0.00582 | -0.05248 | 15
OKGE | 'HORSESHOE LAKE 138KV' | 380 | -0.0583 | OKGE | 'FPLWND2 34KV' | 43.0032 | -0.00582 | -0.05248 | 15
OKGE | 'HORSESHOE LAKE 138KV' | 91 | -0.0583 | OKGE | 'FPLWND2 34KV' | 43.0032 | -0.00582 | -0.05248 | 15
OKGE | 'HORSESHOE LAKE 69KV' | 16 | -0.056 | OKGE | 'MUSKOGEE 345KV' | 1516 | -0.00178 | -0.05422 | 15
OKGE | 'HORSESHOE LAKE 69KV' | 16 | -0.056 | OKGE | 'FPLWND2 34KV' | 43.0032 | -0.00582 | -0.05018 | 16
OKGE | 'HORSESHOE LAKE 138KV' | 380 | -0.0583 | OKGE | 'SOONER 138KV' | 505 | -0.01389 | -0.04441 | 18
OKGE | 'HORSESHOE LAKE 138KV' | 91 | -0.0583 | OKGE | 'SOONER 138KV' | 505 | -0.01389 | -0.04441 | 18
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | -0.0583 | OKGE | 'SOONER 138KV' | 505 | -0.01389 | -0.04441 | 18
OKGE | 'HORSESHOE LAKE 138KV' | 91 | -0.0583 | OKGE | 'SOONER 345KV' | 513 | -0.01395 | -0.04435 | 18
OKGE | 'HORSESHOE LAKE 138KV' | 380 | -0.0583 | OKGE | 'SOONER 345KV' | 513 | -0.01395 | -0.04435 | 18
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | -0.0583 | OKGE | 'SOONER 345KV' | 513 | -0.01395 | -0.04435 | 18
OKGE | 'TINKER 5G 138KV' | 62 | -0.02998 | OKGE | 'SEMINOLE 138KV' | 457.309 | 0.01443 | -0.04441 | 18
OKGE | 'TINKER 5G 138KV' | 62 | -0.02998 | OKGE | 'SEMINOLE 345KV' | 590.52 | 0.01418 | -0.04416 | 18
OKGE | 'HORSESHOE LAKE 69KV' | 16 | -0.056 | OKGE | 'SOONER 138KV' | 505 | -0.01389 | -0.04211 | 19
OKGE | 'HORSESHOE LAKE 69KV' | 16 | -0.056 | OKGE | 'SOONER 345KV' | 513 | -0.01395 | -0.04205 | 19
OKGE | 'HORSESHOE LAKE 138KV' | 91 | -0.0583 | OKGE | 'ONE OAK 345KV' | 100 | -0.01875 | -0.03955 | 20
OKGE | 'HORSESHOE LAKE 138KV' | 380 | -0.0583 | OKGE | 'ONE OAK 345KV' | 100 | -0.01875 | -0.03955 | 20
OKGE | 'HORSESHOE LAKE 138KV' | 380.5 | -0.0583 | OKGE | 'ONE OAK 345KV' | 100 | -0.01875 | -0.03955 | 20
WFEC | 'MORLND 138KV' | 320 | -0.00582 | WFEC | 'ANADARKO 138KV' | 227.0117 | 0.03305 | -0.03887 | 21
OKGE | 'HORSESHOE LAKE 69KV' | 16 | -0.056 | OKGE | 'ONE OAK 345KV' | 100 | -0.01875 | -0.03725 | 22
OKGE | 'ONE OAK 345KV' | 236 | -0.01875 | OKGE | 'SEMINOLE 138KV' | 457.309 | 0.01443 | -0.03318 | 24
OKGE | 'ONE OAK 345KV' | 236 | -0.01875 | OKGE | 'SEMINOLE 345KV' | 590.52 | 0.01418 | -0.03293 | 24
OKGE | 'REDBUD 345KV' | 900 | -0.01763 | OKGE | 'SEMINOLE 138KV' | 457.309 | 0.01443 | -0.03206 | 25
OKGE | 'REDBUD 345KV' | 421.65 | -0.01763 | OKGE | 'SEMINOLE 138KV' | 457.309 | 0.01443 | -0.03206 | 25
OKGE | 'REDBUD 345KV' | 900 | -0.01763 | OKGE | 'SEMINOLE 345KV' | 590.52 | 0.01418 | -0.03181 | 25
OKGE | 'REDBUD 345KV' | 421.65 | -0.01763 | OKGE | 'SEMINOLE 345KV' | 590.52 | 0.01418 | -0.03181 | 25
AEPW | 'COGENTRIX 345KV' | 229 | -0.0049 | AEPW | 'SOUTHWESTERN STATION 138KV' | 29 | 0.02625 | -0.03115 | 26
AEPW | 'NORTHEASTERN STATION 138KV' | 198 | -0.00457 | AEPW | 'SOUTHWESTERN STATION 138KV' | 29 | 0.02625 | -0.03082 | 26
AEPW | 'NORTHEASTERN STATION 345KV' | 95 | -0.00435 | AEPW | 'SOUTHWESTERN STATION 138KV' | 29 | 0.02625 | -0.0306 | 26
AEPW | 'OEC 345KV' | 1210 | -0.00407 | AEPW | 'SOUTHWESTERN STATION 138KV' | 29 | 0.02625 | -0.03032 | 26
AEPW | 'RIVERSIDE STATION 138KV' | 535 | -0.00442 | AEPW | 'SOUTHWESTERN STATION 138KV' | 29 | 0.02625 | -0.03067 | 26
OKGE | 'TINKER 5G 138KV' | 62 | -0.02998 | OKGE | 'AES 161KV' | 320 | 0.00089 | -0.03087 | 26
AEPW | 'TULSA POWER STATION 138KV' | 147 | -0.00475 | AEPW | 'SOUTHWESTERN STATION 138KV' | 29 | 0.02625 | -0.031 | 26
AEPW | 'TULSA POWER STATION 138KV' | 147 | -0.00475 | AEPW | 'SOUTHWESTERN STATION 138KV' | 29 | 0.02625 | -0.031 | 26
AEPW | 'TULSA POWER STATION 69KV' | 24 | -0.00475 | AEPW | 'SOUTHWESTERN STATION 138KV' | 29 | 0.02625 | -0.031 | 26
AEPW | 'TULSA POWER STATION 69KV' | 33 | -0.00475 | AEPW | 'SOUTHWESTERN STATION 138KV' | 29 | 0.02625 | -0.031 | 26
AEPW | 'TULSA POWER STATION 69KV' | 23 | -0.00475 | AEPW | 'SOUTHWESTERN STATION 138KV' | 29 | 0.02625 | -0.031 | 26
AEPW | 'MID-CONTINENT 138KV' | 142.11 | -0.00392 | AEPW | 'SOUTHWESTERN STATION 138KV' | 29 | 0.02625 | -0.03017 | 27
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | SOUTH WAVERLY 161/69KV TRANSFORMER CKT 1 Redispatch
Limiting Facility: | SOUTH WAVERLY 161/69KV TRANSFORMER CKT 1
Direction: | From->To
Line Outage: | NORTON - NORTON 161KV CKT 1
Flowgate: | 58063580941961055806411206SH
Date Redispatch Needed: | 6/1/06 - 10/1/06
Season Flowgate Identified: | 2006 Summer Shoulder
Reservation | Relief Amount | Aggregate Relief Amount
1031553 | 0.9774 | 0.9774
Source Control Area | Source | Maximum Increment(MW) | GSF | Sink Control Area | Sink | Maximum Decrement(MW) | GSF | Factor | Redispatch Amount (MW)
KACP | 'CITY OF HIGGINSVILLE 69KV' | 36 | -0.24049 | KACP | 'MARSHALL 161KV' | 30 | 0.06905 | -0.30954 | 3
KACP | 'CITY OF HIGGINSVILLE 69KV' | 36 | -0.24049 | KACP | 'HAWTHORN 161KV' | 455 | -0.00474 | -0.23575 | 4
KACP | 'CITY OF HIGGINSVILLE 69KV' | 36 | -0.24049 | KACP | 'HAWTHORN 161KV' | 254.7039 | -0.00474 | -0.23575 | 4
KACP | 'CITY OF HIGGINSVILLE 69KV' | 36 | -0.24049 | KACP | 'IATAN 345KV' | 396 | -0.00378 | -0.23671 | 4
KACP | 'CITY OF HIGGINSVILLE 69KV' | 36 | -0.24049 | KACP | 'LACYGNE UNIT 345KV' | 962 | -0.00432 | -0.23617 | 4
KACP | 'CITY OF HIGGINSVILLE 69KV' | 36 | -0.24049 | KACP | 'MONTROSE 161KV' | 353.6805 | -0.00673 | -0.23376 | 4
KACP | 'BULL CREEK 161KV' | 308 | -0.00461 | KACP | 'MARSHALL 161KV' | 30 | 0.06905 | -0.07366 | 13
KACP | 'GARDNER 161KV' | 11 | -0.00466 | KACP | 'MARSHALL 161KV' | 30 | 0.06905 | -0.07371 | 13
KACP | 'GRAND AVENUE 161KV' | 65 | -0.00476 | KACP | 'MARSHALL 161KV' | 30 | 0.06905 | -0.07381 | 13
KACP | 'HAWTHORN 161KV' | 59.2961 | -0.00474 | KACP | 'MARSHALL 161KV' | 30 | 0.06905 | -0.07379 | 13
KACP | 'MONTROSE 161KV' | 27.3195 | -0.00673 | KACP | 'MARSHALL 161KV' | 30 | 0.06905 | -0.07578 | 13
KACP | 'NORTHEAST 13KV' | 59 | -0.00476 | KACP | 'MARSHALL 161KV' | 30 | 0.06905 | -0.07381 | 13
KACP | 'NORTHEAST 13KV' | 58 | -0.00476 | KACP | 'MARSHALL 161KV' | 30 | 0.06905 | -0.07381 | 13
KACP | 'NORTHEAST 13KV' | 56 | -0.00476 | KACP | 'MARSHALL 161KV' | 30 | 0.06905 | -0.07381 | 13
KACP | 'NORTHEAST 13KV' | 56 | -0.00476 | KACP | 'MARSHALL 161KV' | 30 | 0.06905 | -0.07381 | 13
KACP | 'NORTHEAST 161KV' | 58 | -0.00476 | KACP | 'MARSHALL 161KV' | 30 | 0.06905 | -0.07381 | 13
KACP | 'NORTHEAST 161KV' | 58 | -0.00476 | KACP | 'MARSHALL 161KV' | 30 | 0.06905 | -0.07381 | 13
KACP | 'NORTHEAST 161KV' | 58 | -0.00476 | KACP | 'MARSHALL 161KV' | 30 | 0.06905 | -0.07381 | 13
KACP | 'NORTHEAST 161KV' | 55 | -0.00476 | KACP | 'MARSHALL 161KV' | 30 | 0.06905 | -0.07381 | 13
KACP | 'PAOLA COMBUSTION TURBINES 161KV' | 77 | -0.00464 | KACP | 'MARSHALL 161KV' | 30 | 0.06905 | -0.07369 | 13
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor