## tblAllFacilityLog
STUDYDES | STUDYDES2 | EVENTTYPE | AssessmentSOLUTIONTYPE | AssessmenFDNS-TERMINATION | SOLUTIONTYPE | FDNS-TERMINATION | GROUP | SCENARIO | ContractDate | FGNAME | DIRECTION | Bidirectional | FacilityName | FacilityUpgradeCode | ModelArea1 | ModelArea2 | FZONENAME | TZONENAME | MONTFLAG | MONTFB | MONTFNAME | MONTTB1 | MONTTNAME1 | MONTTB2 | MONTTNAME2 | MONTCKT | Case | SISRateA | SISRateB | AG1Assessment Loading | BaseCaseLoading | TransferCaseLoading | NameOfBusWithMonitoredVoltage | BaseCaseVoltage | TransferCaseVoltage | VINIT | VMIN | VMAX | CATEGORY | CONTTYPE | CONTNAME | CONTXFMRFLAG | CONTFB | CONTFNAME | CONTTB1 | CONTTNAME1 | CONTTB2 | CONTTNAME2 | CONTCKT | Decide | TransmissionProviderSystemImpactStudyNotesComments | RequiredRateB | TransmissionOwnerComments | OwnerDesignation | UpgradeName | UpgradeComponentWithinFacility | NewSummerA | NewSummerB | NewOtherA | NewOtherB | DistToConstruct | TotalLead | ConstructionLeadOnly | NewOrConstructWhileEnergized | NewR | NewX | NewB | CommentsRegardingUpgradeRequirements | NewCost | EffDate | NetPlantDate | ReusableEx_GrossValue | ReusableEx_NetValue | Reusable_EndofDepr | SalvageValue | NewCostWhileExpediting | EffDateExpedited | StartDeprExpedited | EndDeprExpedited | NetPlantDateExpedited | ReusableEx_GrossExpedited | ReusableEx_NetExpedited | Reusable_EndofDeprExpedited | SalvageValueExpedited | Generation 1 Owner & Unit (Name) | Generation 1 Redispatch Cost ($) | Generation 1 Redispatch Date (M/D/Y) | Generation 2 Owner & Unit (Name) | Generation 2 Redispatch Cost ($) | Generation 2 Redispatch Date (M/D/Y) | Generation 3 Owner & Unit (Name) | Generation 3 Redispatch Cost ($) | Generation 3 Redispatch Date (M/D/Y) | COD | EOC | EarliestDate
2007-AG1 | AFS11 | NCONV |  |  | FNSL-Blown up | FDNS-Iteration limit exceeded | 1 | 2 | 2008-12-01 | 2007AG1AFS84L351212SP |  |  | SPP-SUNC-05 | EXP |  |  |  |  | 4 | 0 |  | 0 |  | 0 |  |  | 12SP | 0 | 0 |  | -9999 | 9999 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | Cimarron Plant Substation Expansion | Integrate SUNC North Cimarron Top into reconfigured WEPL Cimarron Plant Sub | [12 empty] | 2500000 | 2006-06-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 | NCONV |  |  | FNSL-Blown up | FDNS-Iteration limit exceeded | 3 | 2 | 2008-12-01 | 2007AG1AFS84L383212SP |  |  | SPP-SUNC-05 | EXP |  |  |  |  | 4 | 0 |  | 0 |  | 0 |  |  | 12SP | 0 | 0 |  | -9999 | 9999 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | Cimarron Plant Substation Expansion | Integrate SUNC North Cimarron Top into reconfigured WEPL Cimarron Plant Sub | [12 empty] | 2500000 | 2006-06-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 | NCONV | FNSL-Blown up | FDNS-Blown up | FNSL-Blown up | FDNS-Blown up | 3 | 3 | 2008-12-01 | 2007AG1AFS84L313312SP |  |  | SPP-SUNC-05 | EXP |  |  |  |  | 4 | 0 |  | 0 |  | 0 |  |  | 12SP | 0 | 0 | -9999.0 | -9999 | 9999 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | Cimarron Plant Substation Expansion | Integrate SUNC North Cimarron Top into reconfigured WEPL Cimarron Plant Sub | [12 empty] | 2500000 | 2006-06-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 | NCONV |  |  | FNSL-Blown up | FDNS-Iteration limit exceeded | 2 | 2 | 2008-12-01 | 2007AG1AFS84L352212SP |  |  | SPP-SUNC-05 | EXP |  |  |  |  | 4 | 0 |  | 0 |  | 0 |  |  | 12SP | 0 | 0 |  | -9999 | 9999 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | Cimarron Plant Substation Expansion | Integrate SUNC North Cimarron Top into reconfigured WEPL Cimarron Plant Sub | [12 empty] | 2500000 | 2006-06-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 | NCONV | FNSL-Blown up | FDNS-Blown up | FNSL-Blown up | FDNS-Blown up | 1 | 3 | 2008-12-01 | 2007AG1AFS84L321312SP |  |  | SPP-SUNC-05 | EXP |  |  |  |  | 4 | 0 |  | 0 |  | 0 |  |  | 12SP | 0 | 0 | -9999.0 | -9999 | 9999 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | Cimarron Plant Substation Expansion | Integrate SUNC North Cimarron Top into reconfigured WEPL Cimarron Plant Sub | [12 empty] | 2500000 | 2006-06-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 | NCONV |  |  | FNSL-Blown up | FDNS-Iteration limit exceeded | 4 | 2 | 2008-12-01 | 2007AG1AFS84L334212SP |  |  | SPP-SUNC-05 | EXP |  |  |  |  | 4 | 0 |  | 0 |  | 0 |  |  | 12SP | 0 | 0 |  | -9999 | 9999 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | Cimarron Plant Substation Expansion | Integrate SUNC North Cimarron Top into reconfigured WEPL Cimarron Plant Sub | [12 empty] | 2500000 | 2006-06-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 | NCONV |  |  | FNSL-Blown up | FDNS-Iteration limit exceeded | 1 | 2 | 2008-12-01 | 2007AG1AFS84L351212SP |  |  | SPP-SUNC-05 | EXP |  |  |  |  | 4 | 0 |  | 0 |  | 0 |  |  | 12SP | 0 | 0 |  | -9999 | 9999 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | SUNC | NORTH CIMARRON CAPACITOR | Install 24 MVAR Capacitor bank at North Cimarron | [5 empty] | 18 | 18 | [5 empty] | 1400000 | 2006-07-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 | NCONV |  |  | FNSL-Blown up | FDNS-Iteration limit exceeded | 3 | 2 | 2008-12-01 | 2007AG1AFS84L383212SP |  |  | SPP-SUNC-05 | EXP |  |  |  |  | 4 | 0 |  | 0 |  | 0 |  |  | 12SP | 0 | 0 |  | -9999 | 9999 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | SUNC | NORTH CIMARRON CAPACITOR | Install 24 MVAR Capacitor bank at North Cimarron | [5 empty] | 18 | 18 | [5 empty] | 1400000 | 2006-07-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 | NCONV | FNSL-Blown up | FDNS-Blown up | FNSL-Blown up | FDNS-Blown up | 3 | 3 | 2008-12-01 | 2007AG1AFS84L313312SP |  |  | SPP-SUNC-05 | EXP |  |  |  |  | 4 | 0 |  | 0 |  | 0 |  |  | 12SP | 0 | 0 | -9999.0 | -9999 | 9999 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | SUNC | NORTH CIMARRON CAPACITOR | Install 24 MVAR Capacitor bank at North Cimarron | [5 empty] | 18 | 18 | [5 empty] | 1400000 | 2006-07-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 | NCONV |  |  | FNSL-Blown up | FDNS-Iteration limit exceeded | 2 | 2 | 2008-12-01 | 2007AG1AFS84L352212SP |  |  | SPP-SUNC-05 | EXP |  |  |  |  | 4 | 0 |  | 0 |  | 0 |  |  | 12SP | 0 | 0 |  | -9999 | 9999 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | SUNC | NORTH CIMARRON CAPACITOR | Install 24 MVAR Capacitor bank at North Cimarron | [5 empty] | 18 | 18 | [5 empty] | 1400000 | 2006-07-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 | NCONV | FNSL-Blown up | FDNS-Blown up | FNSL-Blown up | FDNS-Blown up | 1 | 3 | 2008-12-01 | 2007AG1AFS84L321312SP |  |  | SPP-SUNC-05 | EXP |  |  |  |  | 4 | 0 |  | 0 |  | 0 |  |  | 12SP | 0 | 0 | -9999.0 | -9999 | 9999 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | SUNC | NORTH CIMARRON CAPACITOR | Install 24 MVAR Capacitor bank at North Cimarron | [5 empty] | 18 | 18 | [5 empty] | 1400000 | 2006-07-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 | NCONV |  |  | FNSL-Blown up | FDNS-Iteration limit exceeded | 4 | 2 | 2008-12-01 | 2007AG1AFS84L334212SP |  |  | SPP-SUNC-05 | EXP |  |  |  |  | 4 | 0 |  | 0 |  | 0 |  |  | 12SP | 0 | 0 |  | -9999 | 9999 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | SUNC | NORTH CIMARRON CAPACITOR | Install 24 MVAR Capacitor bank at North Cimarron | [5 empty] | 18 | 18 | [5 empty] | 1400000 | 2006-07-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 | NCONV |  |  | FNSL-Blown up | FDNS-Blown up | 2 | 3 | 2008-12-01 | 2007AG1AFS84L212312SP |  |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE | WERE | SEAST | SEAST | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12SP | 100 | 110 |  | 35.2975 | 94.9359 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2511112SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 12SP | 100 | 110 |  | -999 | 175.4199 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T9051112SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 12SP | 100 | 110 |  | -999 | 175.0419 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T3032412SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 12SP | 100 | 110 |  | 84.218 | 115.8165 | [6 empty] | CATEGORYB | SINGLE | LITCHFIELD - PITNAC 69KV CKT 1 | 0 | 533765 | LITCH 2 69.000 | 533769 | PITNAC 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2842412SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12SP | 100 | 110 |  | 51.5783 | 159.3738 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T3032112SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12SP | 100 | 110 |  | 50.3095 | 156.797 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2732412SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12SP | 100 | 110 |  | 44.1373 | 139.5273 | [6 empty] | CATEGORYB | SINGLE | ALLEN - ZILA JUNCTION 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T3394412WP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 12WP | 100 | 110 |  | 55.0718 | 155.5426 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T644412WP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 12WP | 100 | 110 |  | 55.2621 | 155.4764 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T724412WP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12WP | 100 | 110 |  | 42.0319 | 106.4225 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T753312WP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12WP | 100 | 110 |  | 40.9272 | 105.4264 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T931212WP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12WP | 100 | 110 |  | 36.5829 | 103.0556 | [6 empty] | CATEGORYB | SINGLE | ALLEN - ZILA JUNCTION 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T5502417SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 17SP | 100 | 110 |  | 63.5797 | 140.1274 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T21222417SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 17SP | 100 | 110 |  | 63.2793 | 139.6252 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T5922217SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 17SP | 100 | 110 |  | 92.6805 | 119.6911 | [6 empty] | CATEGORYB | SINGLE | LITCHFIELD - PITNAC 69KV CKT 1 | 0 | 533765 | LITCH 2 69.000 | 533769 | PITNAC 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T4822117SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 17SP | 100 | 110 |  | 37.2997 | 112.3477 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T4872117SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 17SP | 100 | 110 |  | 35.9913 | 110.9839 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T16262117SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 17SP | 100 | 110 |  | 47.4206 | 109.3609 | [6 empty] | CATEGORYB | SINGLE | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | NCONV |  |  | FNSL-Blown up | FDNS-Blown up | 2 | 3 | 2008-12-01 | 2007AG1AFS84L212312SP |  |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE | WERE | SEAST | SEAST | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12SP | 100 | 110 |  | 35.2975 | 94.9359 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2511112SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 12SP | 100 | 110 |  | -999 | 175.4199 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T9051112SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 12SP | 100 | 110 |  | -999 | 175.0419 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T3032412SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 12SP | 100 | 110 |  | 84.218 | 115.8165 | [6 empty] | CATEGORYB | SINGLE | LITCHFIELD - PITNAC 69KV CKT 1 | 0 | 533765 | LITCH 2 69.000 | 533769 | PITNAC 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2842412SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12SP | 100 | 110 |  | 51.5783 | 159.3738 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T3032112SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12SP | 100 | 110 |  | 50.3095 | 156.797 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2732412SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12SP | 100 | 110 |  | 44.1373 | 139.5273 | [6 empty] | CATEGORYB | SINGLE | ALLEN - ZILA JUNCTION 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T3394412WP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 12WP | 100 | 110 |  | 55.0718 | 155.5426 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T644412WP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 12WP | 100 | 110 |  | 55.2621 | 155.4764 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T724412WP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12WP | 100 | 110 |  | 42.0319 | 106.4225 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T753312WP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12WP | 100 | 110 |  | 40.9272 | 105.4264 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T931212WP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12WP | 100 | 110 |  | 36.5829 | 103.0556 | [6 empty] | CATEGORYB | SINGLE | ALLEN - ZILA JUNCTION 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T5502417SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 17SP | 100 | 110 |  | 63.5797 | 140.1274 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T21222417SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 17SP | 100 | 110 |  | 63.2793 | 139.6252 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T5922217SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 17SP | 100 | 110 |  | 92.6805 | 119.6911 | [6 empty] | CATEGORYB | SINGLE | LITCHFIELD - PITNAC 69KV CKT 1 | 0 | 533765 | LITCH 2 69.000 | 533769 | PITNAC 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T4822117SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 17SP | 100 | 110 |  | 37.2997 | 112.3477 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T4872117SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 17SP | 100 | 110 |  | 35.9913 | 110.9839 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T16262117SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 17SP | 100 | 110 |  | 47.4206 | 109.3609 | [6 empty] | CATEGORYB | SINGLE | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | NCONV |  |  | FNSL-Blown up | FDNS-Blown up | 2 | 3 | 2008-12-01 | 2007AG1AFS84L212312SP |  |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE | WERE | SEAST | SEAST | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12SP | 100 | 110 |  | 35.2975 | 94.9359 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2511112SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 12SP | 100 | 110 |  | -999 | 175.4199 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T9051112SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 12SP | 100 | 110 |  | -999 | 175.0419 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T3032412SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 12SP | 100 | 110 |  | 84.218 | 115.8165 | [6 empty] | CATEGORYB | SINGLE | LITCHFIELD - PITNAC 69KV CKT 1 | 0 | 533765 | LITCH 2 69.000 | 533769 | PITNAC 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2842412SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12SP | 100 | 110 |  | 51.5783 | 159.3738 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T3032112SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12SP | 100 | 110 |  | 50.3095 | 156.797 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2732412SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12SP | 100 | 110 |  | 44.1373 | 139.5273 | [6 empty] | CATEGORYB | SINGLE | ALLEN - ZILA JUNCTION 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T3394412WP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 12WP | 100 | 110 |  | 55.0718 | 155.5426 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T644412WP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 12WP | 100 | 110 |  | 55.2621 | 155.4764 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T724412WP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12WP | 100 | 110 |  | 42.0319 | 106.4225 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T753312WP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12WP | 100 | 110 |  | 40.9272 | 105.4264 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T931212WP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12WP | 100 | 110 |  | 36.5829 | 103.0556 | [6 empty] | CATEGORYB | SINGLE | ALLEN - ZILA JUNCTION 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T5502417SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 17SP | 100 | 110 |  | 63.5797 | 140.1274 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T21222417SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 17SP | 100 | 110 |  | 63.2793 | 139.6252 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T5922217SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 17SP | 100 | 110 |  | 92.6805 | 119.6911 | [6 empty] | CATEGORYB | SINGLE | LITCHFIELD - PITNAC 69KV CKT 1 | 0 | 533765 | LITCH 2 69.000 | 533769 | PITNAC 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T4822117SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 17SP | 100 | 110 |  | 37.2997 | 112.3477 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T4872117SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 17SP | 100 | 110 |  | 35.9913 | 110.9839 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T16262117SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 17SP | 100 | 110 |  | 47.4206 | 109.3609 | [6 empty] | CATEGORYB | SINGLE | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | NCONV |  |  | FNSL-Blown up | FDNS-Blown up | 2 | 3 | 2008-12-01 | 2007AG1AFS84L212312SP |  |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE | WERE | SEAST | SEAST | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12SP | 100 | 110 |  | 35.2975 | 94.9359 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2511112SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 12SP | 100 | 110 |  | -999 | 175.4199 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T9051112SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 12SP | 100 | 110 |  | -999 | 175.0419 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T3032412SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 12SP | 100 | 110 |  | 84.218 | 115.8165 | [6 empty] | CATEGORYB | SINGLE | LITCHFIELD - PITNAC 69KV CKT 1 | 0 | 533765 | LITCH 2 69.000 | 533769 | PITNAC 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2842412SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12SP | 100 | 110 |  | 51.5783 | 159.3738 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T3032112SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12SP | 100 | 110 |  | 50.3095 | 156.797 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2732412SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12SP | 100 | 110 |  | 44.1373 | 139.5273 | [6 empty] | CATEGORYB | SINGLE | ALLEN - ZILA JUNCTION 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T3394412WP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 12WP | 100 | 110 |  | 55.0718 | 155.5426 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T644412WP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 12WP | 100 | 110 |  | 55.2621 | 155.4764 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T724412WP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12WP | 100 | 110 |  | 42.0319 | 106.4225 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T753312WP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12WP | 100 | 110 |  | 40.9272 | 105.4264 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T931212WP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12WP | 100 | 110 |  | 36.5829 | 103.0556 | [6 empty] | CATEGORYB | SINGLE | ALLEN - ZILA JUNCTION 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T5502417SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 17SP | 100 | 110 |  | 63.5797 | 140.1274 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T21222417SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 17SP | 100 | 110 |  | 63.2793 | 139.6252 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T5922217SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 17SP | 100 | 110 |  | 92.6805 | 119.6911 | [6 empty] | CATEGORYB | SINGLE | LITCHFIELD - PITNAC 69KV CKT 1 | 0 | 533765 | LITCH 2 69.000 | 533769 | PITNAC 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T4822117SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 17SP | 100 | 110 |  | 37.2997 | 112.3477 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T4872117SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 17SP | 100 | 110 |  | 35.9913 | 110.9839 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T16262117SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 17SP | 100 | 110 |  | 47.4206 | 109.3609 | [6 empty] | CATEGORYB | SINGLE | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | NCONV |  |  | FNSL-Blown up | FDNS-Blown up | 2 | 3 | 2008-12-01 | 2007AG1AFS84L212312SP |  |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE | WERE | SEAST | SEAST | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12SP | 100 | 110 |  | 35.2975 | 94.9359 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2511112SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 12SP | 100 | 110 |  | -999 | 175.4199 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T9051112SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 12SP | 100 | 110 |  | -999 | 175.0419 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T3032412SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 12SP | 100 | 110 |  | 84.218 | 115.8165 | [6 empty] | CATEGORYB | SINGLE | LITCHFIELD - PITNAC 69KV CKT 1 | 0 | 533765 | LITCH 2 69.000 | 533769 | PITNAC 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2842412SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12SP | 100 | 110 |  | 51.5783 | 159.3738 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T3032112SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12SP | 100 | 110 |  | 50.3095 | 156.797 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2732412SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12SP | 100 | 110 |  | 44.1373 | 139.5273 | [6 empty] | CATEGORYB | SINGLE | ALLEN - ZILA JUNCTION 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T3394412WP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 12WP | 100 | 110 |  | 55.0718 | 155.5426 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T644412WP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 12WP | 100 | 110 |  | 55.2621 | 155.4764 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T724412WP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12WP | 100 | 110 |  | 42.0319 | 106.4225 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T753312WP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12WP | 100 | 110 |  | 40.9272 | 105.4264 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T931212WP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12WP | 100 | 110 |  | 36.5829 | 103.0556 | [6 empty] | CATEGORYB | SINGLE | ALLEN - ZILA JUNCTION 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T5502417SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 17SP | 100 | 110 |  | 63.5797 | 140.1274 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T21222417SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 17SP | 100 | 110 |  | 63.2793 | 139.6252 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T5922217SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 17SP | 100 | 110 |  | 92.6805 | 119.6911 | [6 empty] | CATEGORYB | SINGLE | LITCHFIELD - PITNAC 69KV CKT 1 | 0 | 533765 | LITCH 2 69.000 | 533769 | PITNAC 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T4822117SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 17SP | 100 | 110 |  | 37.2997 | 112.3477 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T4872117SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 17SP | 100 | 110 |  | 35.9913 | 110.9839 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T16262117SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 17SP | 100 | 110 |  | 47.4206 | 109.3609 | [6 empty] | CATEGORYB | SINGLE | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T13363212SP | FROM->TO |  | LITCHFIELD (LITCH 1X) 161/69/13.2KV TRANSFORMER CKT 1 | EXP | WERE |  | SEAST |  | 2 | 532932 | LITCH 5 161.00 | 533765 | LITCH 2 69.000 | 532952 | LITCH1 1 13.200 | 1 | 12SP | 100 | 110 |  | 95.0175 | 104.9804 | [6 empty] | CATEGORYB | SINGLE | LITCHFIELD (LITCH 2X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532932 | LITCH 5 161.00 | 533765 | LITCH 2 69.000 | 532953 | LITCH2 1 13.200 | 1 |  |  |  |  | WERE | Fort Scott - SW Bourbon 161 kV | Tap Litchfield-Marmaton 161 kV with new SW Bourbon Sub to Ft Scott, and new 161/69 kV transformer at Ft Scott. | [5 empty] | 18 | 18 | [30 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T13343212SP | FROM->TO |  | LITCHFIELD (LITCH 2X) 161/69/13.2KV TRANSFORMER CKT 1 | EXP | WERE |  | SEAST |  | 2 | 532932 | LITCH 5 161.00 | 533765 | LITCH 2 69.000 | 532953 | LITCH2 1 13.200 | 1 | 12SP | 100 | 110 |  | 94.5703 | 104.5828 | [6 empty] | CATEGORYB | SINGLE | LITCHFIELD (LITCH 1X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532932 | LITCH 5 161.00 | 533765 | LITCH 2 69.000 | 532952 | LITCH1 1 13.200 | 1 |  |  |  |  | WERE | Fort Scott - SW Bourbon 161 kV | Tap Litchfield-Marmaton 161 kV with new SW Bourbon Sub to Ft Scott, and new 161/69 kV transformer at Ft Scott. | [5 empty] | 18 | 18 | [30 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T20653217SP | FROM->TO |  | LITCHFIELD (LITCH 1X) 161/69/13.2KV TRANSFORMER CKT 1 | EXP | WERE |  | SEAST |  | 2 | 532932 | LITCH 5 161.00 | 533765 | LITCH 2 69.000 | 532952 | LITCH1 1 13.200 | 1 | 17SP | 100 | 110 | 109.0 | 106.8502 | 117.2661 | [6 empty] | CATEGORYB | SINGLE | LITCHFIELD (LITCH 2X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532932 | LITCH 5 161.00 | 533765 | LITCH 2 69.000 | 532953 | LITCH2 1 13.200 | 1 |  |  |  |  | WERE | Fort Scott - SW Bourbon 161 kV | Tap Litchfield-Marmaton 161 kV with new SW Bourbon Sub to Ft Scott, and new 161/69 kV transformer at Ft Scott. | [5 empty] | 18 | 18 | [30 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T20633217SP | FROM->TO |  | LITCHFIELD (LITCH 2X) 161/69/13.2KV TRANSFORMER CKT 1 | EXP | WERE |  | SEAST |  | 2 | 532932 | LITCH 5 161.00 | 533765 | LITCH 2 69.000 | 532953 | LITCH2 1 13.200 | 1 | 17SP | 100 | 110 | 108.6 | 106.5052 | 116.8815 | [6 empty] | CATEGORYB | SINGLE | LITCHFIELD (LITCH 1X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532932 | LITCH 5 161.00 | 533765 | LITCH 2 69.000 | 532952 | LITCH1 1 13.200 | 1 |  |  |  |  | WERE | Fort Scott - SW Bourbon 161 kV | Tap Litchfield-Marmaton 161 kV with new SW Bourbon Sub to Ft Scott, and new 161/69 kV transformer at Ft Scott. | [5 empty] | 18 | 18 | [30 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 | NCONV |  |  | FNSL-Blown up | FDNS-Blown up | 2 | 3 | 2008-12-01 | 2007AG1AFS84L212312SP |  |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE | WERE | SEAST | SEAST | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12SP | 100 | 110 |  | 35.2975 | 94.9359 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2511112SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 12SP | 100 | 110 |  | -999 | 175.4199 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T9051112SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 12SP | 100 | 110 |  | -999 | 175.0419 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T3032412SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 12SP | 100 | 110 |  | 84.218 | 115.8165 | [6 empty] | CATEGORYB | SINGLE | LITCHFIELD - PITNAC 69KV CKT 1 | 0 | 533765 | LITCH 2 69.000 | 533769 | PITNAC 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2842412SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12SP | 100 | 110 |  | 51.5783 | 159.3738 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T3032112SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12SP | 100 | 110 |  | 50.3095 | 156.797 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2732412SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12SP | 100 | 110 |  | 44.1373 | 139.5273 | [6 empty] | CATEGORYB | SINGLE | ALLEN - ZILA JUNCTION 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T3394412WP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 12WP | 100 | 110 |  | 55.0718 | 155.5426 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T644412WP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 12WP | 100 | 110 |  | 55.2621 | 155.4764 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T724412WP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12WP | 100 | 110 |  | 42.0319 | 106.4225 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T753312WP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12WP | 100 | 110 |  | 40.9272 | 105.4264 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T931212WP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12WP | 100 | 110 |  | 36.5829 | 103.0556 | [6 empty] | CATEGORYB | SINGLE | ALLEN - ZILA JUNCTION 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T5502417SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 17SP | 100 | 110 |  | 63.5797 | 140.1274 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T21222417SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 17SP | 100 | 110 |  | 63.2793 | 139.6252 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T5922217SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 17SP | 100 | 110 |  | 92.6805 | 119.6911 | [6 empty] | CATEGORYB | SINGLE | LITCHFIELD - PITNAC 69KV CKT 1 | 0 | 533765 | LITCH 2 69.000 | 533769 | PITNAC 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T4822117SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 17SP | 100 | 110 |  | 37.2997 | 112.3477 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T4872117SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 17SP | 100 | 110 |  | 35.9913 | 110.9839 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T16262117SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 17SP | 100 | 110 |  | 47.4206 | 109.3609 | [6 empty] | CATEGORYB | SINGLE | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T18474417SP | FROM->TO |  | HUBEN (HUBEN) 345/161/13.8KV TRANSFORMER CKT 1 | S | AECI |  | AECI |  | 2 | 96042 | 7HUBEN 345.00 | 96088 | 5HUBEN 161.00 | 96151 | 1HUBENTR 13.800 | 1 | 17SP | 392 | 392 | 106.9 | 103.163 | 105.3167 | [6 empty] | CATEGORYB | SINGLE | BROOKLINE - MORGAN 345KV CKT 1 | 0 | 549984 | BRKLNE 7 345.00 | 96045 | 7MORGAN 345.00 | 0 |  | 1 | ASSIGN |  |  |  | AECI | HUBEN (HUBEN) 345/161/13.8KV TRANSFORMER CKT 1 | Install a second Huben 345/161kV transformer | [12 empty] | 6500000 | [24 empty] | 2016-06-01 | 2016-06-01
2007-AG1 | AFS11 | NCONV |  |  | FNSL-Blown up | FDNS-Blown up | 2 | 3 | 2008-12-01 | 2007AG1AFS84L212312SP |  |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE | WERE | SEAST | SEAST | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12SP | 100 | 110 |  | 35.2975 | 94.9359 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2511112SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 12SP | 100 | 110 |  | -999 | 175.4199 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T9051112SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 12SP | 100 | 110 |  | -999 | 175.0419 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T3032412SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 12SP | 100 | 110 |  | 84.218 | 115.8165 | [6 empty] | CATEGORYB | SINGLE | LITCHFIELD - PITNAC 69KV CKT 1 | 0 | 533765 | LITCH 2 69.000 | 533769 | PITNAC 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2842412SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12SP | 100 | 110 |  | 51.5783 | 159.3738 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T3032112SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12SP | 100 | 110 |  | 50.3095 | 156.797 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2732412SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12SP | 100 | 110 |  | 44.1373 | 139.5273 | [6 empty] | CATEGORYB | SINGLE | ALLEN - ZILA JUNCTION 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T3394412WP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 12WP | 100 | 110 |  | 55.0718 | 155.5426 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T644412WP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 12WP | 100 | 110 |  | 55.2621 | 155.4764 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T724412WP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12WP | 100 | 110 |  | 42.0319 | 106.4225 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T753312WP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12WP | 100 | 110 |  | 40.9272 | 105.4264 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T931212WP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12WP | 100 | 110 |  | 36.5829 | 103.0556 | [6 empty] | CATEGORYB | SINGLE | ALLEN - ZILA JUNCTION 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T5502417SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 17SP | 100 | 110 |  | 63.5797 | 140.1274 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T21222417SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 17SP | 100 | 110 |  | 63.2793 | 139.6252 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T5922217SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 17SP | 100 | 110 |  | 92.6805 | 119.6911 | [6 empty] | CATEGORYB | SINGLE | LITCHFIELD - PITNAC 69KV CKT 1 | 0 | 533765 | LITCH 2 69.000 | 533769 | PITNAC 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T4822117SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 17SP | 100 | 110 |  | 37.2997 | 112.3477 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T4872117SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 17SP | 100 | 110 |  | 35.9913 | 110.9839 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T16262117SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 17SP | 100 | 110 |  | 47.4206 | 109.3609 | [6 empty] | CATEGORYB | SINGLE | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T3883208FA | FROM->TO |  | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 1 | CP | WERE |  | SCENTRAL |  | 2 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532826 | ROSEH1 1 13.800 | 1 | 08FA | 400 | 440 | 110.2 | 108.7 | 111.3894 | [6 empty] | CATEGORYB | SINGLE | ROSE HILL (ROSEHL3X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532827 | ROSEH3 1 13.800 | 1 |  |  |  |  | WERE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 Displacement | Add third 345-138 kV transformer at Rose Hill | 400 | 440 | 400 | 440 | 0 | 15 | 2 | Y | 0 | 0 | 0 | Like existing Rose Hill 345-138 units | [25 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T3863208FA | FROM->TO |  | ROSE HILL (ROSEHL3X) 345/138/13.8KV TRANSFORMER CKT 1 | CP | WERE |  | SCENTRAL |  | 2 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532827 | ROSEH3 1 13.800 | 1 | 08FA | 400 | 440 | 110.2 | 108.7522 | 111.4431 | [6 empty] | CATEGORYB | SINGLE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532826 | ROSEH1 1 13.800 | 1 |  |  |  |  | WERE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 Displacement | Add third 345-138 kV transformer at Rose Hill | 400 | 440 | 400 | 440 | 0 | 15 | 2 | Y | 0 | 0 | 0 | Like existing Rose Hill 345-138 units | [25 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T3883208FA | FROM->TO |  | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 1 | CP | WERE |  | SCENTRAL |  | 2 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532826 | ROSEH1 1 13.800 | 1 | 08FA | 400 | 440 | 110.2 | 108.7 | 111.3894 | [6 empty] | CATEGORYB | SINGLE | ROSE HILL (ROSEHL3X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532827 | ROSEH3 1 13.800 | 1 |  |  |  |  | WERE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 Displacement | Add third 345-138 kV transformer at Rose Hill | 400 | 440 | 400 | 440 | 0 | 15 | 2 | Y | 0 | 0 | 0 | Like existing Rose Hill 345-138 units | [25 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T3883208FA | FROM->TO |  | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 1 | CP | WERE |  | SCENTRAL |  | 2 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532826 | ROSEH1 1 13.800 | 1 | 08FA | 400 | 440 | 110.2 | 108.7 | 111.3894 | [6 empty] | CATEGORYB | SINGLE | ROSE HILL (ROSEHL3X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532827 | ROSEH3 1 13.800 | 1 |  |  |  |  | WERE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 Displacement | Add third 345-138 kV transformer at Rose Hill | 400 | 440 | 400 | 440 | 0 | 15 | 2 | Y | 0 | 0 | 0 | Like existing Rose Hill 345-138 units | [25 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T3863208FA | FROM->TO |  | ROSE HILL (ROSEHL3X) 345/138/13.8KV TRANSFORMER CKT 1 | CP | WERE |  | SCENTRAL |  | 2 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532827 | ROSEH3 1 13.800 | 1 | 08FA | 400 | 440 | 110.2 | 108.7522 | 111.4431 | [6 empty] | CATEGORYB | SINGLE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532826 | ROSEH1 1 13.800 | 1 |  |  |  |  | WERE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 Displacement | Add third 345-138 kV transformer at Rose Hill | 400 | 440 | 400 | 440 | 0 | 15 | 2 | Y | 0 | 0 | 0 | Like existing Rose Hill 345-138 units | [25 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T3863208FA | FROM->TO |  | ROSE HILL (ROSEHL3X) 345/138/13.8KV TRANSFORMER CKT 1 | CP | WERE |  | SCENTRAL |  | 2 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532827 | ROSEH3 1 13.800 | 1 | 08FA | 400 | 440 | 110.2 | 108.7522 | 111.4431 | [6 empty] | CATEGORYB | SINGLE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532826 | ROSEH1 1 13.800 | 1 |  |  |  |  | WERE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 Displacement | Add third 345-138 kV transformer at Rose Hill | 400 | 440 | 400 | 440 | 0 | 15 | 2 | Y | 0 | 0 | 0 | Like existing Rose Hill 345-138 units | [25 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T3863208FA | FROM->TO |  | ROSE HILL (ROSEHL3X) 345/138/13.8KV TRANSFORMER CKT 1 | CP | WERE |  | SCENTRAL |  | 2 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532827 | ROSEH3 1 13.800 | 1 | 08FA | 400 | 440 | 110.2 | 108.7522 | 111.4431 | [6 empty] | CATEGORYB | SINGLE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532826 | ROSEH1 1 13.800 | 1 |  |  |  |  | WERE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 Displacement | Add third 345-138 kV transformer at Rose Hill | 400 | 440 | 400 | 440 | 0 | 15 | 2 | Y | 0 | 0 | 0 | Like existing Rose Hill 345-138 units | [25 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T2542208G | FROM->TO |  | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 1 | CP | WERE |  | SCENTRAL |  | 2 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532826 | ROSEH1 1 13.800 | 1 | 08G | 400 | 440 |  | 98.3761 | 100.2811 | [6 empty] | CATEGORYB | SINGLE | ROSE HILL (ROSEHL3X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532827 | ROSEH3 1 13.800 | 1 |  |  |  |  | WERE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 Displacement | Add third 345-138 kV transformer at Rose Hill | 400 | 440 | 400 | 440 | 0 | 15 | 2 | Y | 0 | 0 | 0 | Like existing Rose Hill 345-138 units | [25 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T2532208G | FROM->TO |  | ROSE HILL (ROSEHL3X) 345/138/13.8KV TRANSFORMER CKT 1 | CP | WERE |  | SCENTRAL |  | 2 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532827 | ROSEH3 1 13.800 | 1 | 08G | 400 | 440 |  | 98.4095 | 100.3146 | [6 empty] | CATEGORYB | SINGLE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532826 | ROSEH1 1 13.800 | 1 |  |  |  |  | WERE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 Displacement | Add third 345-138 kV transformer at Rose Hill | 400 | 440 | 400 | 440 | 0 | 15 | 2 | Y | 0 | 0 | 0 | Like existing Rose Hill 345-138 units | [25 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T2542208G | FROM->TO |  | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 1 | CP | WERE |  | SCENTRAL |  | 2 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532826 | ROSEH1 1 13.800 | 1 | 08G | 400 | 440 |  | 98.3761 | 100.2811 | [6 empty] | CATEGORYB | SINGLE | ROSE HILL (ROSEHL3X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532827 | ROSEH3 1 13.800 | 1 |  |  |  |  | WERE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 Displacement | Add third 345-138 kV transformer at Rose Hill | 400 | 440 | 400 | 440 | 0 | 15 | 2 | Y | 0 | 0 | 0 | Like existing Rose Hill 345-138 units | [25 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T2542208G | FROM->TO |  | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 1 | CP | WERE |  | SCENTRAL |  | 2 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532826 | ROSEH1 1 13.800 | 1 | 08G | 400 | 440 |  | 98.3761 | 100.2811 | [6 empty] | CATEGORYB | SINGLE | ROSE HILL (ROSEHL3X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532827 | ROSEH3 1 13.800 | 1 |  |  |  |  | WERE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 Displacement | Add third 345-138 kV transformer at Rose Hill | 400 | 440 | 400 | 440 | 0 | 15 | 2 | Y | 0 | 0 | 0 | Like existing Rose Hill 345-138 units | [25 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T2532208G | FROM->TO |  | ROSE HILL (ROSEHL3X) 345/138/13.8KV TRANSFORMER CKT 1 | CP | WERE |  | SCENTRAL |  | 2 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532827 | ROSEH3 1 13.800 | 1 | 08G | 400 | 440 |  | 98.4095 | 100.3146 | [6 empty] | CATEGORYB | SINGLE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532826 | ROSEH1 1 13.800 | 1 |  |  |  |  | WERE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 Displacement | Add third 345-138 kV transformer at Rose Hill | 400 | 440 | 400 | 440 | 0 | 15 | 2 | Y | 0 | 0 | 0 | Like existing Rose Hill 345-138 units | [25 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T2532208G | FROM->TO |  | ROSE HILL (ROSEHL3X) 345/138/13.8KV TRANSFORMER CKT 1 | CP | WERE |  | SCENTRAL |  | 2 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532827 | ROSEH3 1 13.800 | 1 | 08G | 400 | 440 |  | 98.4095 | 100.3146 | [6 empty] | CATEGORYB | SINGLE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532826 | ROSEH1 1 13.800 | 1 |  |  |  |  | WERE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 Displacement | Add third 345-138 kV transformer at Rose Hill | 400 | 440 | 400 | 440 | 0 | 15 | 2 | Y | 0 | 0 | 0 | Like existing Rose Hill 345-138 units | [25 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T2532208G | FROM->TO |  | ROSE HILL (ROSEHL3X) 345/138/13.8KV TRANSFORMER CKT 1 | CP | WERE |  | SCENTRAL |  | 2 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532827 | ROSEH3 1 13.800 | 1 | 08G | 400 | 440 |  | 98.4095 | 100.3146 | [6 empty] | CATEGORYB | SINGLE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532826 | ROSEH1 1 13.800 | 1 |  |  |  |  | WERE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 Displacement | Add third 345-138 kV transformer at Rose Hill | 400 | 440 | 400 | 440 | 0 | 15 | 2 | Y | 0 | 0 | 0 | Like existing Rose Hill 345-138 units | [25 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T2883208WP | FROM->TO |  | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 1 | CP | WERE |  | SCENTRAL |  | 2 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532826 | ROSEH1 1 13.800 | 1 | 08WP | 400 | 440 |  | 102.0358 | 100.9055 | [6 empty] | CATEGORYB | SINGLE | ROSE HILL (ROSEHL3X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532827 | ROSEH3 1 13.800 | 1 |  |  |  |  | WERE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 Displacement | Add third 345-138 kV transformer at Rose Hill | 400 | 440 | 400 | 440 | 0 | 15 | 2 | Y | 0 | 0 | 0 | Like existing Rose Hill 345-138 units | [25 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T2873208WP | FROM->TO |  | ROSE HILL (ROSEHL3X) 345/138/13.8KV TRANSFORMER CKT 1 | CP | WERE |  | SCENTRAL |  | 2 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532827 | ROSEH3 1 13.800 | 1 | 08WP | 400 | 440 |  | 102.0854 | 100.9415 | [6 empty] | CATEGORYB | SINGLE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532826 | ROSEH1 1 13.800 | 1 |  |  |  |  | WERE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 Displacement | Add third 345-138 kV transformer at Rose Hill | 400 | 440 | 400 | 440 | 0 | 15 | 2 | Y | 0 | 0 | 0 | Like existing Rose Hill 345-138 units | [25 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T2883208WP | FROM->TO |  | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 1 | CP | WERE |  | SCENTRAL |  | 2 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532826 | ROSEH1 1 13.800 | 1 | 08WP | 400 | 440 |  | 102.0358 | 100.9055 | [6 empty] | CATEGORYB | SINGLE | ROSE HILL (ROSEHL3X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532827 | ROSEH3 1 13.800 | 1 |  |  |  |  | WERE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 Displacement | Add third 345-138 kV transformer at Rose Hill | 400 | 440 | 400 | 440 | 0 | 15 | 2 | Y | 0 | 0 | 0 | Like existing Rose Hill 345-138 units | [25 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T2883208WP | FROM->TO |  | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 1 | CP | WERE |  | SCENTRAL |  | 2 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532826 | ROSEH1 1 13.800 | 1 | 08WP | 400 | 440 |  | 102.0358 | 100.9055 | [6 empty] | CATEGORYB | SINGLE | ROSE HILL (ROSEHL3X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532827 | ROSEH3 1 13.800 | 1 |  |  |  |  | WERE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 Displacement | Add third 345-138 kV transformer at Rose Hill | 400 | 440 | 400 | 440 | 0 | 15 | 2 | Y | 0 | 0 | 0 | Like existing Rose Hill 345-138 units | [25 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T2873208WP | FROM->TO |  | ROSE HILL (ROSEHL3X) 345/138/13.8KV TRANSFORMER CKT 1 | CP | WERE |  | SCENTRAL |  | 2 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532827 | ROSEH3 1 13.800 | 1 | 08WP | 400 | 440 |  | 102.0854 | 100.9415 | [6 empty] | CATEGORYB | SINGLE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532826 | ROSEH1 1 13.800 | 1 |  |  |  |  | WERE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 Displacement | Add third 345-138 kV transformer at Rose Hill | 400 | 440 | 400 | 440 | 0 | 15 | 2 | Y | 0 | 0 | 0 | Like existing Rose Hill 345-138 units | [25 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T2873208WP | FROM->TO |  | ROSE HILL (ROSEHL3X) 345/138/13.8KV TRANSFORMER CKT 1 | CP | WERE |  | SCENTRAL |  | 2 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532827 | ROSEH3 1 13.800 | 1 | 08WP | 400 | 440 |  | 102.0854 | 100.9415 | [6 empty] | CATEGORYB | SINGLE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532826 | ROSEH1 1 13.800 | 1 |  |  |  |  | WERE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 Displacement | Add third 345-138 kV transformer at Rose Hill | 400 | 440 | 400 | 440 | 0 | 15 | 2 | Y | 0 | 0 | 0 | Like existing Rose Hill 345-138 units | [25 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T2873208WP | FROM->TO |  | ROSE HILL (ROSEHL3X) 345/138/13.8KV TRANSFORMER CKT 1 | CP | WERE |  | SCENTRAL |  | 2 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532827 | ROSEH3 1 13.800 | 1 | 08WP | 400 | 440 |  | 102.0854 | 100.9415 | [6 empty] | CATEGORYB | SINGLE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532826 | ROSEH1 1 13.800 | 1 |  |  |  |  | WERE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 Displacement | Add third 345-138 kV transformer at Rose Hill | 400 | 440 | 400 | 440 | 0 | 15 | 2 | Y | 0 | 0 | 0 | Like existing Rose Hill 345-138 units | [25 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T10953212SP | FROM->TO |  | SPRINGFIELD (SPF X1) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505492 | SPRGFLD5 161.00 | 505494 | SPRGFLD2 69.000 | 505491 | SPF X1 1 13.800 | 1 | 12SP | 80 | 80 |  | 55.5849 | 101.3159 | [6 empty] | CATEGORYB | SINGLE | SPRINGFIELD (SPF X2) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505492 | SPRGFLD5 161.00 | 505494 | SPRGFLD2 69.000 | 505493 | SPF X2 1 13.800 | 1 |  |  |  |  | SWPA | SPRINGFIELD (SPF X3) 161/69/13.8KV TRANSFORMER CKT 1 | Add Third Transformer | [5 empty] | 24 | [6 empty] | 1500000 | 2008-05-29 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T3653312SP | FROM->TO |  | SPRINGFIELD (SPF X1) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505492 | SPRGFLD5 161.00 | 505494 | SPRGFLD2 69.000 | 505491 | SPF X1 1 13.800 | 1 | 12SP | 80 | 80 |  | 64.4504 | 100.5949 | [6 empty] | CATEGORYB | SINGLE | JAMES RIVER - PLAINVIEW 69KV CKT 1 | 0 | 549904 | JRPS 2 69.000 | 549905 | PLAINVI2 69.000 | 0 |  | 1 |  |  |  |  | SWPA | SPRINGFIELD (SPF X3) 161/69/13.8KV TRANSFORMER CKT 1 | Add Third Transformer | [5 empty] | 24 | [6 empty] | 1500000 | 2008-05-29 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T14002317SP | FROM->TO |  | SPRINGFIELD (SPF X1) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505492 | SPRGFLD5 161.00 | 505494 | SPRGFLD2 69.000 | 505491 | SPF X1 1 13.800 | 1 | 17SP | 80 | 80 |  | 70.1042 | 105.3072 | [6 empty] | CATEGORYB | SINGLE | SPRINGFIELD (SPF X2) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505492 | SPRGFLD5 161.00 | 505494 | SPRGFLD2 69.000 | 505493 | SPF X2 1 13.800 | 1 |  |  |  |  | SWPA | SPRINGFIELD (SPF X3) 161/69/13.8KV TRANSFORMER CKT 1 | Add Third Transformer | [5 empty] | 24 | [6 empty] | 1500000 | 2008-05-29 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T13972317SP | FROM->TO |  | SPRINGFIELD (SPF X2) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505492 | SPRGFLD5 161.00 | 505494 | SPRGFLD2 69.000 | 505493 | SPF X2 1 13.800 | 1 | 17SP | 70 | 70 | 102.2 | 67.4607 | 107.7526 | [6 empty] | CATEGORYB | SINGLE | SPRINGFIELD (SPF X1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505492 | SPRGFLD5 161.00 | 505494 | SPRGFLD2 69.000 | 505491 | SPF X1 1 13.800 | 1 |  |  |  |  | SWPA | SPRINGFIELD (SPF X3) 161/69/13.8KV TRANSFORMER CKT 1 | Add Third Transformer | [5 empty] | 24 | [6 empty] | 1500000 | 2008-05-29 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T27095517SP | FROM->TO |  | TUCO INTERCHANGE (TUCO XX4) 345/230/13.2KV TRANSFORMER CKT 1 | REL | SPS |  | SPS-CNPL |  | 2 | 525832 | TUCO7 345.00 | 525830 | TUCO6 230.00 | 525824 | TUCO 1 13.200 | 1 | 17SP | 436 | 502 | 120.0 | 119.803 | 120.942 | [6 empty] | CATEGORYB | GENOUT | GEN525562 1-TOLK GEN #2 24 KV | 0 | 0 |  | 0 |  | 0 | [6 empty] | SPS | TUCO INTERCHANGE 345/115KV TRANSFORMER CKT 1 | Install 345/115 kV Transformer at Tuco | 560 | 560 |  |  |  | 27 | 5 | [5 empty] | 10318679 | 2007-01-01 | [23 empty] | 2017-06-01 | 2017-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T27005517SP | FROM->TO |  | TUCO INTERCHANGE (TUCO XX4) 345/230/13.2KV TRANSFORMER CKT 1 | REL | SPS |  | SPS-CNPL |  | 2 | 525832 | TUCO7 345.00 | 525830 | TUCO6 230.00 | 525824 | TUCO 1 13.200 | 1 | 17SP | 436 | 502 | 112.4 | 112.715 | 113.8882 | [6 empty] | CATEGORYB | GENOUT | GEN525561 1-TOLK GEN #1 24 KV | 0 | 0 |  | 0 |  | 0 | [6 empty] | SPS | TUCO INTERCHANGE 345/115KV TRANSFORMER CKT 1 | Install 345/115 kV Transformer at Tuco | 560 | 560 |  |  |  | 27 | 5 | [5 empty] | 10318679 | 2007-01-01 | [23 empty] | 2017-06-01 | 2017-06-01
2007-AG1 | AFS11 | NCONV |  |  | FNSL-Blown up | FDNS-Blown up | 2 | 3 | 2008-12-01 | 2007AG1AFS84L212312SP |  |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE | WERE | SEAST | SEAST | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12SP | 100 | 110 |  | 35.2975 | 94.9359 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2511112SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 12SP | 100 | 110 |  | -999 | 175.4199 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T9051112SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 12SP | 100 | 110 |  | -999 | 175.0419 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T3032412SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 12SP | 100 | 110 |  | 84.218 | 115.8165 | [6 empty] | CATEGORYB | SINGLE | LITCHFIELD - PITNAC 69KV CKT 1 | 0 | 533765 | LITCH 2 69.000 | 533769 | PITNAC 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2842412SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12SP | 100 | 110 |  | 51.5783 | 159.3738 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T3032112SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12SP | 100 | 110 |  | 50.3095 | 156.797 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2732412SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12SP | 100 | 110 |  | 44.1373 | 139.5273 | [6 empty] | CATEGORYB | SINGLE | ALLEN - ZILA JUNCTION 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T3394412WP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 12WP | 100 | 110 |  | 55.0718 | 155.5426 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T644412WP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 12WP | 100 | 110 |  | 55.2621 | 155.4764 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T724412WP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12WP | 100 | 110 |  | 42.0319 | 106.4225 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T753312WP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12WP | 100 | 110 |  | 40.9272 | 105.4264 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T931212WP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 12WP | 100 | 110 |  | 36.5829 | 103.0556 | [6 empty] | CATEGORYB | SINGLE | ALLEN - ZILA JUNCTION 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T5502417SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 17SP | 100 | 110 |  | 63.5797 | 140.1274 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T21222417SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 17SP | 100 | 110 |  | 63.2793 | 139.6252 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T5922217SP | FROM->TO |  | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 17SP | 100 | 110 |  | 92.6805 | 119.6911 | [6 empty] | CATEGORYB | SINGLE | LITCHFIELD - PITNAC 69KV CKT 1 | 0 | 533765 | LITCH 2 69.000 | 533769 | PITNAC 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T4822117SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 17SP | 100 | 110 |  | 37.2997 | 112.3477 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T4872117SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 17SP | 100 | 110 |  | 35.9913 | 110.9839 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T16262117SP | FROM->TO |  | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | S | WERE |  | SEAST |  | 2 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 | 17SP | 100 | 110 |  | 47.4206 | 109.3609 | [6 empty] | CATEGORYB | SINGLE | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2006-AG1 | 2006-AG1 | [5 empty] | 1 | 3 | 2006-10-01 | KNOOBHIL41421OKGEMTL-51316SP |  |  | KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1 | U | OKGE |  |  |  | 1 | 514795 | KNOBHIL4 138 | 514794 | KNOBHIL269.0 | 515732 | KNOBHIL113.2 | 1 | 16SP |  | 67 | [10 empty] | NONSINGLE | OKGEMTL-5 | 0 | 0 |  | 0 |  | 0 | [6 empty] | OKGE | KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1 | Replace bus tie with 100MVA transformer | 123 | 134 | 123 | 134 |  | 15 | 12 | [5 empty] | 1750000 | [24 empty] | 2006-06-01 | 2008-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T3664117SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 17SP | 280 | 308 | 120.9 | 121.0238 | 122.1796 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 2 | Add second Auburn 230-115 kV transformer. | 280 | 308 | 280 | 308 |  | 12 | 2 | Y |  |  |  | See transformer #1 for NewR, NewX, NewB | 2250000 | 2004-06-24 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T3664117SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 17SP | 280 | 308 | 120.9 | 121.0238 | 122.1796 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 2 | Add second Auburn 230-115 kV transformer. | 280 | 308 | 280 | 308 |  | 12 | 2 | Y |  |  |  | See transformer #1 for NewR, NewX, NewB | 2250000 | 2004-06-24 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T3664117SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 17SP | 280 | 308 | 120.9 | 121.0238 | 122.1796 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 2 | Add second Auburn 230-115 kV transformer. | 280 | 308 | 280 | 308 |  | 12 | 2 | Y |  |  |  | See transformer #1 for NewR, NewX, NewB | 2250000 | 2004-06-24 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T3664117SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 17SP | 280 | 308 | 120.9 | 121.0238 | 122.1796 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 2 | Add second Auburn 230-115 kV transformer. | 280 | 308 | 280 | 308 |  | 12 | 2 | Y |  |  |  | See transformer #1 for NewR, NewX, NewB | 2250000 | 2004-06-24 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T3664117SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 17SP | 280 | 308 | 120.9 | 121.0238 | 122.1796 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 2 | Add second Auburn 230-115 kV transformer. | 280 | 308 | 280 | 308 |  | 12 | 2 | Y |  |  |  | See transformer #1 for NewR, NewX, NewB | 2250000 | 2004-06-24 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T3664117SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 17SP | 280 | 308 | 120.9 | 121.0238 | 122.1796 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 2 | Add second Auburn 230-115 kV transformer. | 280 | 308 | 280 | 308 |  | 12 | 2 | Y |  |  |  | See transformer #1 for NewR, NewX, NewB | 2250000 | 2004-06-24 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T3664117SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 17SP | 280 | 308 | 120.9 | 121.0238 | 122.1796 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 2 | Add second Auburn 230-115 kV transformer. | 280 | 308 | 280 | 308 |  | 12 | 2 | Y |  |  |  | See transformer #1 for NewR, NewX, NewB | 2250000 | 2004-06-24 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T3664117SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 17SP | 280 | 308 | 120.9 | 121.0238 | 122.1796 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 2 | Add second Auburn 230-115 kV transformer. | 280 | 308 | 280 | 308 |  | 12 | 2 | Y |  |  |  | See transformer #1 for NewR, NewX, NewB | 2250000 | 2004-06-24 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T3664117SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 17SP | 280 | 308 | 120.9 | 121.0238 | 122.1796 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 2 | Add second Auburn 230-115 kV transformer. | 280 | 308 | 280 | 308 |  | 12 | 2 | Y |  |  |  | See transformer #1 for NewR, NewX, NewB | 2250000 | 2004-06-24 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T3664117SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 17SP | 280 | 308 | 120.9 | 121.0238 | 122.1796 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 2 | Add second Auburn 230-115 kV transformer. | 280 | 308 | 280 | 308 |  | 12 | 2 | Y |  |  |  | See transformer #1 for NewR, NewX, NewB | 2250000 | 2004-06-24 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81T2194212SP | FROM->TO |  | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | S | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 12SP | 280 | 308 |  | 95.4737 | 101.2223 | [6 empty] | CATEGORYB | SINGLE | MCDOWELL CREEK - MORRIS COUNTY 230KV CKT 1 | 0 | 532862 | MCDOWEL6 230.00 | 532863 | MORRIS 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 Displacement | Uprate JEC- E.Manhattan 230 kV line to 100 deg C operation by raising structures | [12 empty] | 17085937.5 | 2008-01-01 | [23 empty] | 2013-06-01 | 2013-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81T9324212SP | FROM->TO |  | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | S | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 12SP | 280 | 308 |  | 95.4448 | 101.1926 | [6 empty] | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 |  |  |  |  | WERE | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 Displacement | Uprate JEC- E.Manhattan 230 kV line to 100 deg C operation by raising structures | [12 empty] | 17085937.5 | 2008-01-01 | [23 empty] | 2013-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T4844417SP | FROM->TO |  | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | S | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 17SP | 280 | 308 | 104.0 | 103.8801 | 110.071 | [6 empty] | CATEGORYB | SINGLE | MCDOWELL CREEK - MORRIS COUNTY 230KV CKT 1 | 0 | 532862 | MCDOWEL6 230.00 | 532863 | MORRIS 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 Displacement | Uprate JEC- E.Manhattan 230 kV line to 100 deg C operation by raising structures | [12 empty] | 17085937.5 | 2008-01-01 | [23 empty] | 2013-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T16984417SP | FROM->TO |  | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | S | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 17SP | 280 | 308 | 104.0 | 103.8597 | 110.0518 | [6 empty] | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 |  |  |  |  | WERE | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 Displacement | Uprate JEC- E.Manhattan 230 kV line to 100 deg C operation by raising structures | [12 empty] | 17085937.5 | 2008-01-01 | [23 empty] | 2013-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T3734317SP | FROM->TO |  | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | S | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 17SP | 280 | 308 | 100.1 | 99.1851 | 108.5524 | [6 empty] | CATEGORYB | SINGLE | AUBURN ROAD - JEFFREY ENERGY CENTER 230KV CKT 1 | 0 | 532851 | AUBURN 6 230.00 | 532852 | JEC 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 Displacement | Uprate JEC- E.Manhattan 230 kV line to 100 deg C operation by raising structures | [12 empty] | 17085937.5 | 2008-01-01 | [23 empty] | 2013-06-01 | 2013-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81T2194212SP | FROM->TO |  | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | S | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 12SP | 280 | 308 |  | 95.4737 | 101.2223 | [6 empty] | CATEGORYB | SINGLE | MCDOWELL CREEK - MORRIS COUNTY 230KV CKT 1 | 0 | 532862 | MCDOWEL6 230.00 | 532863 | MORRIS 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | EAST MANHATTAN - NW MANHATTAN 230/115KV Displacement | Tap the Concordia - East Manhattan 230kV line and add a new substation"NW Manhattan"; Add a 230kV/115kV transformer and tap the KSU - Wildcat 115kV line into NW Manhattan | [12 empty] | 17437500 | 2008-01-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81T9324212SP | FROM->TO |  | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | S | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 12SP | 280 | 308 |  | 95.4448 | 101.1926 | [6 empty] | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 |  |  |  |  | WERE | EAST MANHATTAN - NW MANHATTAN 230/115KV Displacement | Tap the Concordia - East Manhattan 230kV line and add a new substation"NW Manhattan"; Add a 230kV/115kV transformer and tap the KSU - Wildcat 115kV line into NW Manhattan | [12 empty] | 17437500 | 2008-01-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81T2194212SP | FROM->TO |  | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | S | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 12SP | 280 | 308 |  | 95.4737 | 101.2223 | [6 empty] | CATEGORYB | SINGLE | MCDOWELL CREEK - MORRIS COUNTY 230KV CKT 1 | 0 | 532862 | MCDOWEL6 230.00 | 532863 | MORRIS 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | EAST MANHATTAN - NW MANHATTAN 230/115KV Displacement | Tap the Concordia - East Manhattan 230kV line and add a new substation"NW Manhattan"; Add a 230kV/115kV transformer and tap the KSU - Wildcat 115kV line into NW Manhattan | [12 empty] | 17437500 | 2008-01-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81T9324212SP | FROM->TO |  | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | S | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 12SP | 280 | 308 |  | 95.4448 | 101.1926 | [6 empty] | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 |  |  |  |  | WERE | EAST MANHATTAN - NW MANHATTAN 230/115KV Displacement | Tap the Concordia - East Manhattan 230kV line and add a new substation"NW Manhattan"; Add a 230kV/115kV transformer and tap the KSU - Wildcat 115kV line into NW Manhattan | [12 empty] | 17437500 | 2008-01-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81T2194212SP | FROM->TO |  | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | S | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 12SP | 280 | 308 |  | 95.4737 | 101.2223 | [6 empty] | CATEGORYB | SINGLE | MCDOWELL CREEK - MORRIS COUNTY 230KV CKT 1 | 0 | 532862 | MCDOWEL6 230.00 | 532863 | MORRIS 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | EAST MANHATTAN - NW MANHATTAN 230/115KV Displacement | Tap the Concordia - East Manhattan 230kV line and add a new substation"NW Manhattan"; Add a 230kV/115kV transformer and tap the KSU - Wildcat 115kV line into NW Manhattan | [12 empty] | 17437500 | 2008-01-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81T9324212SP | FROM->TO |  | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | S | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 12SP | 280 | 308 |  | 95.4448 | 101.1926 | [6 empty] | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 |  |  |  |  | WERE | EAST MANHATTAN - NW MANHATTAN 230/115KV Displacement | Tap the Concordia - East Manhattan 230kV line and add a new substation"NW Manhattan"; Add a 230kV/115kV transformer and tap the KSU - Wildcat 115kV line into NW Manhattan | [12 empty] | 17437500 | 2008-01-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T4844417SP | FROM->TO |  | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | S | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 17SP | 280 | 308 | 104.0 | 103.8801 | 110.071 | [6 empty] | CATEGORYB | SINGLE | MCDOWELL CREEK - MORRIS COUNTY 230KV CKT 1 | 0 | 532862 | MCDOWEL6 230.00 | 532863 | MORRIS 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | EAST MANHATTAN - NW MANHATTAN 230/115KV Displacement | Tap the Concordia - East Manhattan 230kV line and add a new substation"NW Manhattan"; Add a 230kV/115kV transformer and tap the KSU - Wildcat 115kV line into NW Manhattan | [12 empty] | 17437500 | 2008-01-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T16984417SP | FROM->TO |  | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | S | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 17SP | 280 | 308 | 104.0 | 103.8597 | 110.0518 | [6 empty] | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 |  |  |  |  | WERE | EAST MANHATTAN - NW MANHATTAN 230/115KV Displacement | Tap the Concordia - East Manhattan 230kV line and add a new substation"NW Manhattan"; Add a 230kV/115kV transformer and tap the KSU - Wildcat 115kV line into NW Manhattan | [12 empty] | 17437500 | 2008-01-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T3734317SP | FROM->TO |  | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | S | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 17SP | 280 | 308 | 100.1 | 99.1851 | 108.5524 | [6 empty] | CATEGORYB | SINGLE | AUBURN ROAD - JEFFREY ENERGY CENTER 230KV CKT 1 | 0 | 532851 | AUBURN 6 230.00 | 532852 | JEC 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | EAST MANHATTAN - NW MANHATTAN 230/115KV Displacement | Tap the Concordia - East Manhattan 230kV line and add a new substation"NW Manhattan"; Add a 230kV/115kV transformer and tap the KSU - Wildcat 115kV line into NW Manhattan | [12 empty] | 17437500 | 2008-01-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T4844417SP | FROM->TO |  | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | S | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 17SP | 280 | 308 | 104.0 | 103.8801 | 110.071 | [6 empty] | CATEGORYB | SINGLE | MCDOWELL CREEK - MORRIS COUNTY 230KV CKT 1 | 0 | 532862 | MCDOWEL6 230.00 | 532863 | MORRIS 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | EAST MANHATTAN - NW MANHATTAN 230/115KV Displacement | Tap the Concordia - East Manhattan 230kV line and add a new substation"NW Manhattan"; Add a 230kV/115kV transformer and tap the KSU - Wildcat 115kV line into NW Manhattan | [12 empty] | 17437500 | 2008-01-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T16984417SP | FROM->TO |  | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | S | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 17SP | 280 | 308 | 104.0 | 103.8597 | 110.0518 | [6 empty] | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 |  |  |  |  | WERE | EAST MANHATTAN - NW MANHATTAN 230/115KV Displacement | Tap the Concordia - East Manhattan 230kV line and add a new substation"NW Manhattan"; Add a 230kV/115kV transformer and tap the KSU - Wildcat 115kV line into NW Manhattan | [12 empty] | 17437500 | 2008-01-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T3734317SP | FROM->TO |  | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | S | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 17SP | 280 | 308 | 100.1 | 99.1851 | 108.5524 | [6 empty] | CATEGORYB | SINGLE | AUBURN ROAD - JEFFREY ENERGY CENTER 230KV CKT 1 | 0 | 532851 | AUBURN 6 230.00 | 532852 | JEC 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | EAST MANHATTAN - NW MANHATTAN 230/115KV Displacement | Tap the Concordia - East Manhattan 230kV line and add a new substation"NW Manhattan"; Add a 230kV/115kV transformer and tap the KSU - Wildcat 115kV line into NW Manhattan | [12 empty] | 17437500 | 2008-01-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T4844417SP | FROM->TO |  | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | S | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 17SP | 280 | 308 | 104.0 | 103.8801 | 110.071 | [6 empty] | CATEGORYB | SINGLE | MCDOWELL CREEK - MORRIS COUNTY 230KV CKT 1 | 0 | 532862 | MCDOWEL6 230.00 | 532863 | MORRIS 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | EAST MANHATTAN - NW MANHATTAN 230/115KV Displacement | Tap the Concordia - East Manhattan 230kV line and add a new substation"NW Manhattan"; Add a 230kV/115kV transformer and tap the KSU - Wildcat 115kV line into NW Manhattan | [12 empty] | 17437500 | 2008-01-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T16984417SP | FROM->TO |  | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | S | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 17SP | 280 | 308 | 104.0 | 103.8597 | 110.0518 | [6 empty] | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 |  |  |  |  | WERE | EAST MANHATTAN - NW MANHATTAN 230/115KV Displacement | Tap the Concordia - East Manhattan 230kV line and add a new substation"NW Manhattan"; Add a 230kV/115kV transformer and tap the KSU - Wildcat 115kV line into NW Manhattan | [12 empty] | 17437500 | 2008-01-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T3734317SP | FROM->TO |  | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | S | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 17SP | 280 | 308 | 100.1 | 99.1851 | 108.5524 | [6 empty] | CATEGORYB | SINGLE | AUBURN ROAD - JEFFREY ENERGY CENTER 230KV CKT 1 | 0 | 532851 | AUBURN 6 230.00 | 532852 | JEC 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | EAST MANHATTAN - NW MANHATTAN 230/115KV Displacement | Tap the Concordia - East Manhattan 230kV line and add a new substation"NW Manhattan"; Add a 230kV/115kV transformer and tap the KSU - Wildcat 115kV line into NW Manhattan | [12 empty] | 17437500 | 2008-01-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81T2194212SP | FROM->TO |  | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | S | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 12SP | 280 | 308 |  | 95.4737 | 101.2223 | [6 empty] | CATEGORYB | SINGLE | MCDOWELL CREEK - MORRIS COUNTY 230KV CKT 1 | 0 | 532862 | MCDOWEL6 230.00 | 532863 | MORRIS 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | East Manhattan to Mcdowell 230 kV Displacement | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 |  | 1000000 | 2007-01-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81T9324212SP | FROM->TO |  | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | S | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 12SP | 280 | 308 |  | 95.4448 | 101.1926 | [6 empty] | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 |  |  |  |  | WERE | East Manhattan to Mcdowell 230 kV Displacement | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 |  | 1000000 | 2007-01-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T4844417SP | FROM->TO |  | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | S | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 17SP | 280 | 308 | 104.0 | 103.8801 | 110.071 | [6 empty] | CATEGORYB | SINGLE | MCDOWELL CREEK - MORRIS COUNTY 230KV CKT 1 | 0 | 532862 | MCDOWEL6 230.00 | 532863 | MORRIS 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | East Manhattan to Mcdowell 230 kV Displacement | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 |  | 1000000 | 2007-01-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T16984417SP | FROM->TO |  | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | S | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 17SP | 280 | 308 | 104.0 | 103.8597 | 110.0518 | [6 empty] | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 |  |  |  |  | WERE | East Manhattan to Mcdowell 230 kV Displacement | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 |  | 1000000 | 2007-01-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T3734317SP | FROM->TO |  | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | S | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 17SP | 280 | 308 | 100.1 | 99.1851 | 108.5524 | [6 empty] | CATEGORYB | SINGLE | AUBURN ROAD - JEFFREY ENERGY CENTER 230KV CKT 1 | 0 | 532851 | AUBURN 6 230.00 | 532852 | JEC 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | East Manhattan to Mcdowell 230 kV Displacement | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 |  | 1000000 | 2007-01-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T5531217SP | FROM->TO |  | SUB 389 - JOPLIN SOUTHWEST (JOPLINSW) 161/69/12.5KV TRANSFORMER CKT 1 | REL | EMDE |  | JOPLIN |  | 1 | 547483 | JOP389 5 161.00 | 547592 | JOP389 2 69.000 | 547713 | JOP389 1 12.500 | 1 | 17SP | 75 | 75 | 102.1 | 102.1011 | 102.3786 | [6 empty] | CATEGORYB | SINGLE | SUB 292 - TIPTON FORD - SUB 389 - JOPLIN SOUTHWEST 161KV CKT 1 | 0 | 547472 | TIP292 5 161.00 | 547483 | JOP389 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | JOPLIN 59 - SUB 439 - STATELINE 161KV CKT 1 | Install new line from Sub #439 to new Sub Joplin 59. | [5 empty] | 48 | 48 | [5 empty] | 7182217 | 2007-01-01 | [23 empty] | 2012-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T5633317SP | FROM->TO |  | SUB 389 - JOPLIN SOUTHWEST (JOPLINSW) 161/69/12.5KV TRANSFORMER CKT 1 | REL | EMDE |  | JOPLIN |  | 1 | 547483 | JOP389 5 161.00 | 547592 | JOP389 2 69.000 | 547713 | JOP389 1 12.500 | 1 | 17SP | 75 | 75 | 100.6 | 100.6232 | 101.848 | [6 empty] | CATEGORYB | SINGLE | SUB 145 - JOPLIN WEST 7TH - SUB 439 - STATELINE 161KV CKT 1 | 0 | 547470 | JOP145 5 161.00 | 547498 | STL439 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | JOPLIN 59 - SUB 439 - STATELINE 161KV CKT 1 | Install new line from Sub #439 to new Sub Joplin 59. | [5 empty] | 48 | 48 | [5 empty] | 7182217 | 2007-01-01 | [23 empty] | 2012-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T5531217SP | FROM->TO |  | SUB 389 - JOPLIN SOUTHWEST (JOPLINSW) 161/69/12.5KV TRANSFORMER CKT 1 | REL | EMDE |  | JOPLIN |  | 1 | 547483 | JOP389 5 161.00 | 547592 | JOP389 2 69.000 | 547713 | JOP389 1 12.500 | 1 | 17SP | 75 | 75 | 102.1 | 102.1011 | 102.3786 | [6 empty] | CATEGORYB | SINGLE | SUB 292 - TIPTON FORD - SUB 389 - JOPLIN SOUTHWEST 161KV CKT 1 | 0 | 547472 | TIP292 5 161.00 | 547483 | JOP389 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | JOPLIN 59 - SUB 59 - JOPLIN 26TH ST. 161/69kV TRANSFORMER CKT 1 | Install 3-wind transformer from 161 kV Joplin 59 bus to Sub #59 Joplin 26th St. | [5 empty] | 48 | 48 | [5 empty] | 9200000 | 2007-01-01 | [23 empty] | 2012-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T5633317SP | FROM->TO |  | SUB 389 - JOPLIN SOUTHWEST (JOPLINSW) 161/69/12.5KV TRANSFORMER CKT 1 | REL | EMDE |  | JOPLIN |  | 1 | 547483 | JOP389 5 161.00 | 547592 | JOP389 2 69.000 | 547713 | JOP389 1 12.500 | 1 | 17SP | 75 | 75 | 100.6 | 100.6232 | 101.848 | [6 empty] | CATEGORYB | SINGLE | SUB 145 - JOPLIN WEST 7TH - SUB 439 - STATELINE 161KV CKT 1 | 0 | 547470 | JOP145 5 161.00 | 547498 | STL439 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | JOPLIN 59 - SUB 59 - JOPLIN 26TH ST. 161/69kV TRANSFORMER CKT 1 | Install 3-wind transformer from 161 kV Joplin 59 bus to Sub #59 Joplin 26th St. | [5 empty] | 48 | 48 | [5 empty] | 9200000 | 2007-01-01 | [23 empty] | 2012-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T4993217SP | FROM->TO |  | SEVENTEENTH (17TH 4X) 138/69/11.295KV TRANSFORMER CKT 1 | REL | WERE |  | SCENTRAL |  | 1 | 533064 | 17TH 4 138.00 | 533840 | 17TH 2 69.000 | 533112 | 17TH 1 11.295 | 1 | 17SP | 150 | 165 | 106.9 | 106.2801 | 106.3193 | [6 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  |  | WERE | SEVENTEENTH () 138/69/11.295KV TRANSFORMER CKT 2 | Install second 17th St. 138-69 kV transformer | 150 | 165 | 150 | 165 |  | 12 | 6 |  | 0.002 | 0.0653 |  | 165 MVA is transformer limit | 2400000 | 2006-03-21 | [23 empty] | 2015-06-01 | 2015-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T4993217SP | FROM->TO |  | SEVENTEENTH (17TH 4X) 138/69/11.295KV TRANSFORMER CKT 1 | REL | WERE |  | SCENTRAL |  | 1 | 533064 | 17TH 4 138.00 | 533840 | 17TH 2 69.000 | 533112 | 17TH 1 11.295 | 1 | 17SP | 150 | 165 | 106.9 | 106.2801 | 106.3193 | [6 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  |  | WERE | SEVENTEENTH () 138/69/11.295KV TRANSFORMER CKT 2 | Install second 17th St. 138-69 kV transformer | 150 | 165 | 150 | 165 |  | 12 | 6 |  | 0.002 | 0.0653 |  | 165 MVA is transformer limit | 2400000 | 2006-03-21 | [23 empty] | 2015-06-01 | 2015-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T4993217SP | FROM->TO |  | SEVENTEENTH (17TH 4X) 138/69/11.295KV TRANSFORMER CKT 1 | REL | WERE |  | SCENTRAL |  | 1 | 533064 | 17TH 4 138.00 | 533840 | 17TH 2 69.000 | 533112 | 17TH 1 11.295 | 1 | 17SP | 150 | 165 | 106.9 | 106.2801 | 106.3193 | [6 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  |  | WERE | SEVENTEENTH () 138/69/11.295KV TRANSFORMER CKT 2 | Install second 17th St. 138-69 kV transformer | 150 | 165 | 150 | 165 |  | 12 | 6 |  | 0.002 | 0.0653 |  | 165 MVA is transformer limit | 2400000 | 2006-03-21 | [23 empty] | 2015-06-01 | 2015-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T4993217SP | FROM->TO |  | SEVENTEENTH (17TH 4X) 138/69/11.295KV TRANSFORMER CKT 1 | REL | WERE |  | SCENTRAL |  | 1 | 533064 | 17TH 4 138.00 | 533840 | 17TH 2 69.000 | 533112 | 17TH 1 11.295 | 1 | 17SP | 150 | 165 | 106.9 | 106.2801 | 106.3193 | [6 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  |  | WERE | SEVENTEENTH () 138/69/11.295KV TRANSFORMER CKT 2 | Install second 17th St. 138-69 kV transformer | 150 | 165 | 150 | 165 |  | 12 | 6 |  | 0.002 | 0.0653 |  | 165 MVA is transformer limit | 2400000 | 2006-03-21 | [23 empty] | 2015-06-01 | 2015-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T19455517SP | FROM->TO |  | SEVENTEENTH (17TH 4X) 138/69/11.295KV TRANSFORMER CKT 1 | REL | WERE |  | SCENTRAL |  | 1 | 533064 | 17TH 4 138.00 | 533840 | 17TH 2 69.000 | 533112 | 17TH 1 11.295 | 1 | 17SP | 150 | 165 | 104.3 | 103.7679 | 103.6289 | [6 empty] | CATEGORYB | SINGLE | CHISHOLM (CHISLM1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 533035 | CHISHLM4 138.00 | 533786 | CHISHLM2 69.000 | 533103 | CHISOLM1 13.200 | 1 |  |  |  |  | WERE | SEVENTEENTH () 138/69/11.295KV TRANSFORMER CKT 2 | Install second 17th St. 138-69 kV transformer | 150 | 165 | 150 | 165 |  | 12 | 6 |  | 0.002 | 0.0653 |  | 165 MVA is transformer limit | 2400000 | 2006-03-21 | [23 empty] | 2015-06-01 | 2015-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T19455517SP | FROM->TO |  | SEVENTEENTH (17TH 4X) 138/69/11.295KV TRANSFORMER CKT 1 | REL | WERE |  | SCENTRAL |  | 1 | 533064 | 17TH 4 138.00 | 533840 | 17TH 2 69.000 | 533112 | 17TH 1 11.295 | 1 | 17SP | 150 | 165 | 104.3 | 103.7679 | 103.6289 | [6 empty] | CATEGORYB | SINGLE | CHISHOLM (CHISLM1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 533035 | CHISHLM4 138.00 | 533786 | CHISHLM2 69.000 | 533103 | CHISOLM1 13.200 | 1 |  |  |  |  | WERE | SEVENTEENTH () 138/69/11.295KV TRANSFORMER CKT 2 | Install second 17th St. 138-69 kV transformer | 150 | 165 | 150 | 165 |  | 12 | 6 |  | 0.002 | 0.0653 |  | 165 MVA is transformer limit | 2400000 | 2006-03-21 | [23 empty] | 2015-06-01 | 2015-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T19455517SP | FROM->TO |  | SEVENTEENTH (17TH 4X) 138/69/11.295KV TRANSFORMER CKT 1 | REL | WERE |  | SCENTRAL |  | 1 | 533064 | 17TH 4 138.00 | 533840 | 17TH 2 69.000 | 533112 | 17TH 1 11.295 | 1 | 17SP | 150 | 165 | 104.3 | 103.7679 | 103.6289 | [6 empty] | CATEGORYB | SINGLE | CHISHOLM (CHISLM1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 533035 | CHISHLM4 138.00 | 533786 | CHISHLM2 69.000 | 533103 | CHISOLM1 13.200 | 1 |  |  |  |  | WERE | SEVENTEENTH () 138/69/11.295KV TRANSFORMER CKT 2 | Install second 17th St. 138-69 kV transformer | 150 | 165 | 150 | 165 |  | 12 | 6 |  | 0.002 | 0.0653 |  | 165 MVA is transformer limit | 2400000 | 2006-03-21 | [23 empty] | 2015-06-01 | 2015-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T19455517SP | FROM->TO |  | SEVENTEENTH (17TH 4X) 138/69/11.295KV TRANSFORMER CKT 1 | REL | WERE |  | SCENTRAL |  | 1 | 533064 | 17TH 4 138.00 | 533840 | 17TH 2 69.000 | 533112 | 17TH 1 11.295 | 1 | 17SP | 150 | 165 | 104.3 | 103.7679 | 103.6289 | [6 empty] | CATEGORYB | SINGLE | CHISHOLM (CHISLM1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 533035 | CHISHLM4 138.00 | 533786 | CHISHLM2 69.000 | 533103 | CHISOLM1 13.200 | 1 |  |  |  |  | WERE | SEVENTEENTH () 138/69/11.295KV TRANSFORMER CKT 2 | Install second 17th St. 138-69 kV transformer | 150 | 165 | 150 | 165 |  | 12 | 6 |  | 0.002 | 0.0653 |  | 165 MVA is transformer limit | 2400000 | 2006-03-21 | [23 empty] | 2015-06-01 | 2015-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T5013217SP | FROM->TO |  | SEVENTEENTH (17TH 4X) 138/69/11.295KV TRANSFORMER CKT 1 | REL | WERE |  | SCENTRAL |  | 1 | 533064 | 17TH 4 138.00 | 533840 | 17TH 2 69.000 | 533112 | 17TH 1 11.295 | 1 | 17SP | 150 | 165 | 102.3 | 101.6251 | 101.6798 | [6 empty] | CATEGORYB | SINGLE | HOOVER NORTH - LAKERIDGE 138KV CKT 1 | 0 | 533049 | HOOVERN4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  |  | WERE | SEVENTEENTH () 138/69/11.295KV TRANSFORMER CKT 2 | Install second 17th St. 138-69 kV transformer | 150 | 165 | 150 | 165 |  | 12 | 6 |  | 0.002 | 0.0653 |  | 165 MVA is transformer limit | 2400000 | 2006-03-21 | [23 empty] | 2015-06-01 | 2015-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T5013217SP | FROM->TO |  | SEVENTEENTH (17TH 4X) 138/69/11.295KV TRANSFORMER CKT 1 | REL | WERE |  | SCENTRAL |  | 1 | 533064 | 17TH 4 138.00 | 533840 | 17TH 2 69.000 | 533112 | 17TH 1 11.295 | 1 | 17SP | 150 | 165 | 102.3 | 101.6251 | 101.6798 | [6 empty] | CATEGORYB | SINGLE | HOOVER NORTH - LAKERIDGE 138KV CKT 1 | 0 | 533049 | HOOVERN4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  |  | WERE | SEVENTEENTH () 138/69/11.295KV TRANSFORMER CKT 2 | Install second 17th St. 138-69 kV transformer | 150 | 165 | 150 | 165 |  | 12 | 6 |  | 0.002 | 0.0653 |  | 165 MVA is transformer limit | 2400000 | 2006-03-21 | [23 empty] | 2015-06-01 | 2015-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T5013217SP | FROM->TO |  | SEVENTEENTH (17TH 4X) 138/69/11.295KV TRANSFORMER CKT 1 | REL | WERE |  | SCENTRAL |  | 1 | 533064 | 17TH 4 138.00 | 533840 | 17TH 2 69.000 | 533112 | 17TH 1 11.295 | 1 | 17SP | 150 | 165 | 102.3 | 101.6251 | 101.6798 | [6 empty] | CATEGORYB | SINGLE | HOOVER NORTH - LAKERIDGE 138KV CKT 1 | 0 | 533049 | HOOVERN4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  |  | WERE | SEVENTEENTH () 138/69/11.295KV TRANSFORMER CKT 2 | Install second 17th St. 138-69 kV transformer | 150 | 165 | 150 | 165 |  | 12 | 6 |  | 0.002 | 0.0653 |  | 165 MVA is transformer limit | 2400000 | 2006-03-21 | [23 empty] | 2015-06-01 | 2015-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T5013217SP | FROM->TO |  | SEVENTEENTH (17TH 4X) 138/69/11.295KV TRANSFORMER CKT 1 | REL | WERE |  | SCENTRAL |  | 1 | 533064 | 17TH 4 138.00 | 533840 | 17TH 2 69.000 | 533112 | 17TH 1 11.295 | 1 | 17SP | 150 | 165 | 102.3 | 101.6251 | 101.6798 | [6 empty] | CATEGORYB | SINGLE | HOOVER NORTH - LAKERIDGE 138KV CKT 1 | 0 | 533049 | HOOVERN4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  |  | WERE | SEVENTEENTH () 138/69/11.295KV TRANSFORMER CKT 2 | Install second 17th St. 138-69 kV transformer | 150 | 165 | 150 | 165 |  | 12 | 6 |  | 0.002 | 0.0653 |  | 165 MVA is transformer limit | 2400000 | 2006-03-21 | [23 empty] | 2015-06-01 | 2015-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T10492312SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 12SP | 280 | 308 | 103.0 | 103.3556 | 104.9146 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T10492312SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 12SP | 280 | 308 | 103.0 | 103.3556 | 104.9146 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T10492312SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 12SP | 280 | 308 | 103.0 | 103.3556 | 104.9146 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T10492312SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 12SP | 280 | 308 | 103.0 | 103.3556 | 104.9146 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T10622312SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 12SP | 280 | 308 | 118.6 | 119.2468 | 122.4982 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T10622312SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 12SP | 280 | 308 | 118.6 | 119.2468 | 122.4982 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T10622312SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 12SP | 280 | 308 | 118.6 | 119.2468 | 122.4982 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T10622312SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 12SP | 280 | 308 | 118.6 | 119.2468 | 122.4982 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T2682312SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 12SP | 280 | 308 | 118.7 | 119.3373 | 122.5338 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T2682312SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 12SP | 280 | 308 | 118.7 | 119.3373 | 122.5338 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T2682312SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 12SP | 280 | 308 | 118.7 | 119.3373 | 122.5338 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T2682312SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 12SP | 280 | 308 | 118.7 | 119.3373 | 122.5338 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81T16131417SP | FROM->TO |  | EDWARDSVILLE (EDWRDV4X) 161/115/12.47KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532912 | EDWRDVL5 161.00 | 533238 | EDWARVL3 115.00 | 532940 | EDWRDVL1 12.470 | 1 | 17SP | 168 | 185 | 108.0 | 107.3295 | 108.3952 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16242317SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 17SP | 280 | 308 | 110.9 | 110.872 | 112.8908 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16242317SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 17SP | 280 | 308 | 110.9 | 110.872 | 112.8908 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16242317SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 17SP | 280 | 308 | 110.9 | 110.872 | 112.8908 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16242317SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 17SP | 280 | 308 | 110.9 | 110.872 | 112.8908 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16452317SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 17SP | 280 | 308 | 126.8 | 127.2149 | 129.7051 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16452317SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 17SP | 280 | 308 | 126.8 | 127.2149 | 129.7051 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16452317SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 17SP | 280 | 308 | 126.8 | 127.2149 | 129.7051 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16452317SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 17SP | 280 | 308 | 126.8 | 127.2149 | 129.7051 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4012317SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 17SP | 280 | 308 | 126.8 | 127.197 | 129.6893 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4012317SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 17SP | 280 | 308 | 126.8 | 127.197 | 129.6893 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4012317SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 17SP | 280 | 308 | 126.8 | 127.197 | 129.6893 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4012317SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 17SP | 280 | 308 | 126.8 | 127.197 | 129.6893 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T1294109SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 09SP | 280 | 308 | 120.0 | 119.8539 | 122.2204 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T1294109SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 09SP | 280 | 308 | 120.0 | 119.8539 | 122.2204 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T1294109SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 09SP | 280 | 308 | 120.0 | 119.8539 | 122.2204 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T1294109SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 09SP | 280 | 308 | 120.0 | 119.8539 | 122.2204 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T1294109SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 09SP | 280 | 308 | 120.0 | 119.8539 | 122.2204 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T1294109SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 09SP | 280 | 308 | 120.0 | 119.8539 | 122.2204 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T1294109SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 09SP | 280 | 308 | 120.0 | 119.8539 | 122.2204 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T1294109SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 09SP | 280 | 308 | 120.0 | 119.8539 | 122.2204 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T1294109SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 09SP | 280 | 308 | 120.0 | 119.8539 | 122.2204 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T1294109SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 09SP | 280 | 308 | 120.0 | 119.8539 | 122.2204 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T1294109SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 09SP | 280 | 308 | 120.0 | 119.8539 | 122.2204 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T1294109SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 09SP | 280 | 308 | 120.0 | 119.8539 | 122.2204 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T1294109SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 09SP | 280 | 308 | 120.0 | 119.8539 | 122.2204 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T1294109SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 09SP | 280 | 308 | 120.0 | 119.8539 | 122.2204 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T1294109SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 09SP | 280 | 308 | 120.0 | 119.8539 | 122.2204 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T1294109SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 09SP | 280 | 308 | 120.0 | 119.8539 | 122.2204 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T1294109SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 09SP | 280 | 308 | 120.0 | 119.8539 | 122.2204 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T1294109SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 09SP | 280 | 308 | 120.0 | 119.8539 | 122.2204 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T1294109SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 09SP | 280 | 308 | 120.0 | 119.8539 | 122.2204 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T1294109SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 09SP | 280 | 308 | 120.0 | 119.8539 | 122.2204 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T1294109SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 09SP | 280 | 308 | 120.0 | 119.8539 | 122.2204 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T1294109SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 09SP | 280 | 308 | 120.0 | 119.8539 | 122.2204 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T1294109SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 09SP | 280 | 308 | 120.0 | 119.8539 | 122.2204 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T1294109SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 09SP | 280 | 308 | 120.0 | 119.8539 | 122.2204 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T1294109SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 09SP | 280 | 308 | 120.0 | 119.8539 | 122.2204 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T1294109SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 09SP | 280 | 308 | 120.0 | 119.8539 | 122.2204 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T1294109SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 09SP | 280 | 308 | 120.0 | 119.8539 | 122.2204 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T1294109SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 09SP | 280 | 308 | 120.0 | 119.8539 | 122.2204 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T1294109SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 09SP | 280 | 308 | 120.0 | 119.8539 | 122.2204 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T1294109SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 09SP | 280 | 308 | 120.0 | 119.8539 | 122.2204 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T1294109SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 09SP | 280 | 308 | 120.0 | 119.8539 | 122.2204 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T1294109SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 09SP | 280 | 308 | 120.0 | 119.8539 | 122.2204 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T1294109SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 09SP | 280 | 308 | 120.0 | 119.8539 | 122.2204 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T1294109SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 09SP | 280 | 308 | 120.0 | 119.8539 | 122.2204 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T1294109SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 09SP | 280 | 308 | 120.0 | 119.8539 | 122.2204 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T1294109SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 09SP | 280 | 308 | 120.0 | 119.8539 | 122.2204 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T1294109SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 09SP | 280 | 308 | 120.0 | 119.8539 | 122.2204 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T1294109SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 09SP | 280 | 308 | 120.0 | 119.8539 | 122.2204 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T1294109SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 09SP | 280 | 308 | 120.0 | 119.8539 | 122.2204 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T1294109SP | FROM->TO |  | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 09SP | 280 | 308 | 120.0 | 119.8539 | 122.2204 | [6 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1422109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1813 | 122.1891 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1422109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1813 | 122.1891 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1422109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1813 | 122.1891 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1422109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1813 | 122.1891 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1422109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1813 | 122.1891 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1422109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1813 | 122.1891 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1422109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1813 | 122.1891 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1422109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1813 | 122.1891 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1422109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1813 | 122.1891 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1422109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1813 | 122.1891 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1422109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1813 | 122.1891 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1422109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1813 | 122.1891 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1422109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1813 | 122.1891 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1422109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1813 | 122.1891 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1422109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1813 | 122.1891 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1422109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1813 | 122.1891 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T6492109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1891 | 122.061 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T6492109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1891 | 122.061 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T6492109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1891 | 122.061 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T6492109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1891 | 122.061 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T6492109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1891 | 122.061 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T6492109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1891 | 122.061 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T6492109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1891 | 122.061 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T6492109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1891 | 122.061 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T6492109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1891 | 122.061 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T6492109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1891 | 122.061 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T6492109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1891 | 122.061 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T6492109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1891 | 122.061 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T6492109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1891 | 122.061 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T6492109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1891 | 122.061 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T6492109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1891 | 122.061 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T6492109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1891 | 122.061 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T10492312SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 12SP | 280 | 308 | 103.0 | 103.3556 | 104.9146 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T10492312SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 12SP | 280 | 308 | 103.0 | 103.3556 | 104.9146 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T10492312SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 12SP | 280 | 308 | 103.0 | 103.3556 | 104.9146 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T10492312SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 12SP | 280 | 308 | 103.0 | 103.3556 | 104.9146 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T10622312SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 12SP | 280 | 308 | 118.6 | 119.2468 | 122.4982 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T10622312SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 12SP | 280 | 308 | 118.6 | 119.2468 | 122.4982 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T10622312SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 12SP | 280 | 308 | 118.6 | 119.2468 | 122.4982 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T10622312SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 12SP | 280 | 308 | 118.6 | 119.2468 | 122.4982 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T2682312SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 12SP | 280 | 308 | 118.7 | 119.3373 | 122.5338 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T2682312SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 12SP | 280 | 308 | 118.7 | 119.3373 | 122.5338 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T2682312SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 12SP | 280 | 308 | 118.7 | 119.3373 | 122.5338 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T2682312SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 12SP | 280 | 308 | 118.7 | 119.3373 | 122.5338 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81T16131417SP | FROM->TO |  | EDWARDSVILLE (EDWRDV4X) 161/115/12.47KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532912 | EDWRDVL5 161.00 | 533238 | EDWARVL3 115.00 | 532940 | EDWRDVL1 12.470 | 1 | 17SP | 168 | 185 | 108.0 | 107.3295 | 108.3952 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16242317SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 17SP | 280 | 308 | 110.9 | 110.872 | 112.8908 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16242317SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 17SP | 280 | 308 | 110.9 | 110.872 | 112.8908 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16242317SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 17SP | 280 | 308 | 110.9 | 110.872 | 112.8908 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16242317SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 17SP | 280 | 308 | 110.9 | 110.872 | 112.8908 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16452317SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 17SP | 280 | 308 | 126.8 | 127.2149 | 129.7051 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16452317SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 17SP | 280 | 308 | 126.8 | 127.2149 | 129.7051 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16452317SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 17SP | 280 | 308 | 126.8 | 127.2149 | 129.7051 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16452317SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 17SP | 280 | 308 | 126.8 | 127.2149 | 129.7051 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4012317SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 17SP | 280 | 308 | 126.8 | 127.197 | 129.6893 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4012317SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 17SP | 280 | 308 | 126.8 | 127.197 | 129.6893 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4012317SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 17SP | 280 | 308 | 126.8 | 127.197 | 129.6893 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4012317SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 17SP | 280 | 308 | 126.8 | 127.197 | 129.6893 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 3 | 2008-12-01 | 2007AG1AFS81T5091317SP | FROM->TO |  | SUB 383 - MONETT (MONETT) 161/69/12.5KV TRANSFORMER CKT 1 | EXP | EMDE |  | AURORA |  | 1 | 547480 | MON383 5 161.00 | 547591 | MON383 2 69.000 | 547712 | MON383 1 12.500 | 1 | 17SP | 150 | 150 | 104.7 | 102.53 | 103.1725 | [6 empty] | CATEGORYB | SINGLE | SUB 124 - AURORA H.T. - SUB 383 - MONETT 161KV CKT 1 | 0 | 547468 | AUR124 5 161.00 | 547480 | MON383 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 383 - MONETT - SUB 376 - MONETT CITY SOUTH 161/69/12.5KV TRANSFORMER CKT 1 | Install new line from Sub #383 to new Sub MONETT 5. Install 3-wind transformer from 161 kV new bus to Monett city south 69kV | [12 empty] | 8000000 | 2016-06-01 | [23 empty] | 2015-06-01 | 2015-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1422109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1813 | 122.1891 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1422109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1813 | 122.1891 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1422109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1813 | 122.1891 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1422109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1813 | 122.1891 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1422109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1813 | 122.1891 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1422109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1813 | 122.1891 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1422109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1813 | 122.1891 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1422109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1813 | 122.1891 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1422109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1813 | 122.1891 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1422109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1813 | 122.1891 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1422109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1813 | 122.1891 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1422109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1813 | 122.1891 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1422109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1813 | 122.1891 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1422109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1813 | 122.1891 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1422109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1813 | 122.1891 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1422109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1813 | 122.1891 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T6492109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1891 | 122.061 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T6492109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1891 | 122.061 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T6492109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1891 | 122.061 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T6492109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1891 | 122.061 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T6492109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1891 | 122.061 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T6492109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1891 | 122.061 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T6492109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1891 | 122.061 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T6492109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1891 | 122.061 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T6492109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1891 | 122.061 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T6492109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1891 | 122.061 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T6492109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1891 | 122.061 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T6492109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1891 | 122.061 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T6492109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1891 | 122.061 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T6492109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1891 | 122.061 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T6492109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1891 | 122.061 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T6492109SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 09SP | 280 | 308 | 119.6 | 120.1891 | 122.061 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T10492312SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 12SP | 280 | 308 | 103.0 | 103.3556 | 104.9146 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T10492312SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 12SP | 280 | 308 | 103.0 | 103.3556 | 104.9146 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T10492312SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 12SP | 280 | 308 | 103.0 | 103.3556 | 104.9146 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T10492312SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 12SP | 280 | 308 | 103.0 | 103.3556 | 104.9146 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T10622312SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 12SP | 280 | 308 | 118.6 | 119.2468 | 122.4982 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T10622312SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 12SP | 280 | 308 | 118.6 | 119.2468 | 122.4982 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T10622312SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 12SP | 280 | 308 | 118.6 | 119.2468 | 122.4982 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T10622312SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 12SP | 280 | 308 | 118.6 | 119.2468 | 122.4982 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T2682312SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 12SP | 280 | 308 | 118.7 | 119.3373 | 122.5338 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T2682312SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 12SP | 280 | 308 | 118.7 | 119.3373 | 122.5338 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T2682312SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 12SP | 280 | 308 | 118.7 | 119.3373 | 122.5338 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T2682312SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 12SP | 280 | 308 | 118.7 | 119.3373 | 122.5338 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81T16131417SP | FROM->TO |  | EDWARDSVILLE (EDWRDV4X) 161/115/12.47KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532912 | EDWRDVL5 161.00 | 533238 | EDWARVL3 115.00 | 532940 | EDWRDVL1 12.470 | 1 | 17SP | 168 | 185 | 108.0 | 107.3295 | 108.3952 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16242317SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 17SP | 280 | 308 | 110.9 | 110.872 | 112.8908 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16242317SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 17SP | 280 | 308 | 110.9 | 110.872 | 112.8908 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16242317SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 17SP | 280 | 308 | 110.9 | 110.872 | 112.8908 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16242317SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 17SP | 280 | 308 | 110.9 | 110.872 | 112.8908 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16452317SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 17SP | 280 | 308 | 126.8 | 127.2149 | 129.7051 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16452317SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 17SP | 280 | 308 | 126.8 | 127.2149 | 129.7051 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16452317SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 17SP | 280 | 308 | 126.8 | 127.2149 | 129.7051 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16452317SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 17SP | 280 | 308 | 126.8 | 127.2149 | 129.7051 | [6 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4012317SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 17SP | 280 | 308 | 126.8 | 127.197 | 129.6893 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4012317SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 17SP | 280 | 308 | 126.8 | 127.197 | 129.6893 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4012317SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 17SP | 280 | 308 | 126.8 | 127.197 | 129.6893 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4012317SP | FROM->TO |  | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | S | WERE |  | NEAST |  | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 17SP | 280 | 308 | 126.8 | 127.197 | 129.6893 | [6 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
GEN-2004-014 | Spearville2 | [8 empty] | 53969453969553993512SP | FROM->TO |  | SPEARVILLE (SPEARVL6) 230/115/13.8KV TRANSFORMER CKT 1 | U | MKEC |  |  |  | 1 | 539694 | SPEARVL3 115.00 | 539695 | SPEARVL6 230.00 | 539935 | SPERVLTT 13.800 | 1 |  | 205 | 205 |  |  | 38.8 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | SPEARVILLE (SPEARVL6) 230/115/13.8KV TRANSFORMER CKT 1 | 230kv line terminal at Spearville | [12 empty] | 650000 | [24 empty] | 2009-12-31 | 2009-12-31
GEN-2006-010 | Turk | [8 empty] | 50742850742750744212SP | FROM->TO |  | OKAY 138/69KV TRANSFORMER CKT 1 | U | AEPW | AEPW | SARK | SARK | 1 | 507428 | OKAY 4 138.00 | 507427 | OKAY 2 69.000 | 507442 |  | 1 |  | 150 | 174 |  |  | 57.8 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | AEPW | OKAY 138/69KV TRANSFORMER CKT 1 | Replace three single-phase 115-69 kV autotransformers with one 90 MVA, three-phase 138-69 kV autotransformer and convert high side of station to 138 kV | [11 empty] | 3400000 | 3400000 | [24 empty] | 2012-07-01 | 2012-07-01
GEN-2006-010 | Turk | [8 empty] | 50745450745650745812SP | FROM->TO |  | TURK (HEMP 1) 138/115/13.8KV TRANSFORMER CKT 1 | U | AEPW |  | SARK |  | 1 | 507454 | HEMPSTD4 138.00 | 507456 | HEMPSTD3 115.00 | 507458 | HEMP1 1 13.800 | 1 |  | 175 | 234 |  |  | 109.4 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | AEPW | TURK (HEMP 1) 138/115/13.8KV TRANSFORMER CKT 1 | Build Turk 138-115 kV station and relocate autotransformer (and spare) from Patterson to this new Turk station | [11 empty] | 9110000 | 9110000 | [24 empty] | 2012-07-01 | 2012-07-01
GEN-2006-010 | Turk | [8 empty] | 50745650745450745912SP | FROM->TO |  | TURK (HEMP 2) 138/115/13.8KV TRANSFORMER CKT 2 | U | AEPW |  | SARK |  | 1 | 507456 | HEMPSTD3 115.00 | 507454 | HEMPSTD4 138.00 | 507459 | HEMP2 1 13.800 | 2 |  | 147 | 170 |  |  | 0 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | AEPW | TURK (HEMP 2) 138/115/13.8KV TRANSFORMER CKT 2 | Relocate autotransformer from Patterson to this new Turk substation | [11 empty] | 0 | 0 | [24 empty] | 2012-07-01 | 2012-07-01
NA | [9 empty] | NAWERERENNO 1X731 |  |  | RENO 345/115KV CKT 1 | U | WERE | WERE |  |  | 1 | 532771 | RENO 7 345.00 | 533416 | RENO 3 115.00 | 532807 |  | 1 | [27 empty] | WERE | RENO 345/115KV CKT 1 | New stepdown transformer at a new substation in Reno County east northeast of Hutchinson | [37 empty] | 2009-06-01 | 2009-06-01
NA | [9 empty] | NAWERERENNO 2X731 |  |  | RENO 345/115KV CKT 2 | U | WERE | WERE |  |  | 1 | 532771 | RENO 7 345.00 | 533416 | RENO 3 115.00 | 532810 |  | 1 | [27 empty] | WERE | RENO 345/115KV CKT 2 | Install 2nd stepdown transformer at Reno County substation east northeast of Hutchinson | [37 empty] | 2010-06-01 | 2010-06-01
2005-AG2 | 2005-AG2 | [5 empty] | 3 | 3 | 2006-04-01 | 55948540441559485607913310SP |  |  | HUGO POWER PLANT - VALLIANT 138KV CKT 1 | U | WFEC | AEPW |  |  | 0 | 55948 | HUGO PP4 138 | 54044 | VALIANT4 138 | 0 |  | 1 | 10SP |  | 315 | [10 empty] | SINGLE | HUGO POWER PLANT - VALLENT 138KV CKT 1 | 0 | 55948 | HUGO PP4 138 | 56079 | VALLANT4 138 | 0 |  | 1 |  |  |  |  | AEPW | HUGO POWER PLANT - VALLIANT 345 KV AEPW | Vallient 345 KV line terminal | [5 empty] | 24 |  | Y |  |  |  |  | 2500000 | [24 empty] | 2012-07-01 | 2012-07-01
2005-AG2 | 2005-AG2 | [5 empty] | 3 | 3 | 2006-04-01 | 55948540441559485607913310SP |  |  | HUGO POWER PLANT - VALLIANT 138KV CKT 1 | U | WFEC | AEPW |  |  | 0 | 55948 | HUGO PP4 138 | 54044 | VALIANT4 138 | 0 |  | 1 | 10SP |  | 315 | [10 empty] | SINGLE | HUGO POWER PLANT - VALLENT 138KV CKT 1 | 0 | 55948 | HUGO PP4 138 | 56079 | VALLANT4 138 | 0 |  | 1 |  |  |  |  | WFEC | HUGO POWER PLANT - VALLIANT 345 KV WFEC | New 19 miles 345 KV | 500 | 500 |  |  | 19 | 24 |  | Y |  |  |  | The 345kv line would go: From Hugo Power Station (55948) to a new 500 MVA 138/345kv autotransformer at the Hugo plant site to PSO Valiant (54037) USE data from GEN-2004-018 | 16000000 | [24 empty] | 2012-07-01 | 2012-07-01
2005-AG2 | 2005-AG2 | [5 empty] | 3 | 3 | 2006-04-01 | 55948540441559485607913310SP |  |  | HUGO POWER PLANT - VALLIANT 138KV CKT 1 | U | WFEC | AEPW |  |  | 0 | 55948 | HUGO PP4 138 | 54044 | VALIANT4 138 | 0 |  | 1 | 10SP |  | 315 | [10 empty] | SINGLE | HUGO POWER PLANT - VALLENT 138KV CKT 1 | 0 | 55948 | HUGO PP4 138 | 56079 | VALLANT4 138 | 0 |  | 1 |  |  |  |  | WFEC | HUGO POWER PLANT 345/138KV TRANSFORMER CKT 1 | New 345/138 kv Auto | 500 | 500 |  |  | 19 | 24 |  | Y |  |  |  | The 345kv line would go: From Hugo Power Station (55948) to a new 500 MVA 138/345kv autotransformer at the Hugo plant site to PSO Valiant (54037) USE data from GEN-2004-018 | 16000000 | [24 empty] | 2012-07-01 | 2012-07-01
2005-AG2 | 2005-AG2 | [5 empty] | 3 | 3 | 2006-04-01 | 59467594691594705949813315SP |  |  | SUB 110 - ORONOGO JCT. - SUB 167 - RIVERTON 161KV CKT 1 | U | EMDE | EMDE |  |  | 0 | 547469 | RIV167 5 161 | 547467 | ORO110 5 161 | 0 |  | 1 | 15SP |  | 214 | [10 empty] | SINGLE | SUB 145 - JOPLIN WEST 7TH - SUB 439 - STATELINE 161KV CKT 1 | 0 | 59470 | JOP145 5 161 | 59498 | STL439 5 161 | 0 |  | 1 |  |  |  |  | EMDE | SUB 110 - ORONOGO JCT. - SUB 167 - RIVERTON 161KV CKT 1 | Reconductor Oronogo 59467 to Riverton 59469 with Bundled 556 ACSR | 299 | 335 | 299 | 335 | 11.84 | 24 | 12 |  | 0.00379 | 0.02451 | 0.02427 |  | 5400000 | [24 empty] | 2011-06-01 | 2011-06-01
2006-AG1 | 2006-AG1 | [5 empty] | 3 | 2 | 2006-10-01 | 53245532501SPP-AEPW-293216SP |  |  | ALUMAX TAP - BANN 138KV CKT 1 | U | AEPW | AEPW |  |  | 0 | 508049 | ALUMXT 4 138 | 508054 | BANN 4 138 | 0 |  | 1 | 16SP |  | 261 | [10 empty] | NONSINGLE | SPP-AEPW-29 | 0 | 0 |  | 0 |  | 0 | [6 empty] | AEPW | ALUMAX TAP - BANN 138KV CKT 1 | Replace six (6) 138 kV switches, five at Bann & one at Alumax Tap. Rebuild 0.67 miles of 1024 ACAR with 2156 ACSR. Replace wavetrap & jumpers @ Bann. Replace breaker 3300 @ Bann. | 430 | 449 | 430 | 449 | 0.67 | 15 | 6 |  | 0.00018 | 0.002397 | 0.00081 | New limits are CTs and relay settings @ Bann | 1000000 | [24 empty] | 2008-06-01 | 2008-06-01
2006-AG1 | 2006-AG1 | [5 empty] | 3 | 3 | 2006-10-01 | 55919559201559575599913316SP |  |  | FT SUPPLY 138/69KV TRANSFORMER CKT 1 | U | WFEC | WFEC |  |  | 0 | 520920 | FTSUPLY4 138 | 520919 | FTSUPLY269.0 | 0 |  | 1 | 16SP |  | 70 | [10 empty] | SINGLE | IODINE - MOORELAND 138KV CKT 1 | 0 | 55957 | IODINE 4 138 | 55999 | MOORLND4 138 | 0 |  | 1 |  |  |  |  | WFEC | FT SUPPLY 138/69KV TRANSFORMER CKT 1 | Install 2nd 70 MVA auto at Ft Supply | 70 | 70 |  |  |  | 12 | 18 |  |  |  |  | Use RS from Ft Supply Auto | 2000000 | [24 empty] | 2006-12-01 | 2008-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T6552209SP | FROM->TO | Bidirectional | 5CALCR - NORFORK 161KV CKT 1 | S | ENTR | SWPA | EES-ARK | EMINTH | 0 | 99803 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 09SP | 148 | 148 | 107.0 | 106.49 | 114.0063 | [6 empty] | CATEGORYB | SINGLE | DELL - INDEPENDENCE 500KV CKT 1 | 0 | 99742 | 8DELL 5 500.00 | 99818 | 8ISES 5 500.00 | 0 |  | 1 | ASSIGN |  |  | AP&L (EES) owns the line (SWPAs facilities good for 167 MVA) | SWPA | 5CALCR - NORFORK 161KV CKT 1 SWPA | Replace buswork within bay and change metering CT ratio, replace wavetraps. Entergy must also reconductor their line to increase the rating. | 236 | 236 | 236 | 236 |  | 18 | 3 |  |  |  |  | New ratings are based on CT limits. They assume that Entergy also upgrades their line. | 100000 | 2007-04-20 | [23 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T9422209SP | FROM->TO | Bidirectional | 5CALCR - NORFORK 161KV CKT 1 | S | ENTR | SWPA | EES-ARK | EMINTH | 0 | 99803 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 09SP | 148 | 148 | 101.2 | 100.6025 | 109.2921 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  | AP&L (EES) owns the line (SWPAs facilities good for 167 MVA) | SWPA | 5CALCR - NORFORK 161KV CKT 1 SWPA | Replace buswork within bay and change metering CT ratio, replace wavetraps. Entergy must also reconductor their line to increase the rating. | 236 | 236 | 236 | 236 |  | 18 | 3 |  |  |  |  | New ratings are based on CT limits. They assume that Entergy also upgrades their line. | 100000 | 2007-04-20 | [23 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T16432209SP | FROM->TO | Bidirectional | 5CALCR - NORFORK 161KV CKT 1 | S | ENTR | SWPA | EES-ARK | EMINTH | 0 | 99803 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 09SP | 148 | 148 |  | 98.4369 | 106.0011 | [6 empty] | CATEGORYB | GENOUT | GEN532751 1-WOLF CREEK GENERATING STATION UNIT 1 | 0 | 0 |  | 0 |  | 0 |  |  | ASSIGN |  |  | AP&L (EES) owns the line (SWPAs facilities good for 167 MVA) | SWPA | 5CALCR - NORFORK 161KV CKT 1 SWPA | Replace buswork within bay and change metering CT ratio, replace wavetraps. Entergy must also reconductor their line to increase the rating. | 236 | 236 | 236 | 236 |  | 18 | 3 |  |  |  |  | New ratings are based on CT limits. They assume that Entergy also upgrades their line. | 100000 | 2007-04-20 | [23 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 | NCONV | FNSL-Iteration limit exceeded | FDNS-Iteration limit exceeded | FNSL-Iteration limit exceeded | FDNS-Iteration limit exceeded | 2 | 2 | 2008-12-01 | 2007AG1AFS84L172209SP |  | Bidirectional | 5CALCR - NORFORK 161KV CKT 1 | S | ENTR | SWPA | EES-ARK | EMINTH | 0 | 99803 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 09SP | 148 | 148 | 83.85991 | 83.2403 | 90.6237 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | ASSIGN |  |  | AP&L (EES) owns the line (SWPAs facilities good for 167 MVA) | SWPA | 5CALCR - NORFORK 161KV CKT 1 SWPA | Replace buswork within bay and change metering CT ratio, replace wavetraps. Entergy must also reconductor their line to increase the rating. | 236 | 236 | 236 | 236 |  | 18 | 3 |  |  |  |  | New ratings are based on CT limits. They assume that Entergy also upgrades their line. | 100000 | 2007-04-20 | [23 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T13532212SP | FROM->TO | Bidirectional | 5CALCR - NORFORK 161KV CKT 1 | S | ENTR | SWPA | EES-ARK | EMINTH | 0 | 99803 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 12SP | 148 | 148 | 102.4 | 102.7951 | 111.7764 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  | AP&L (EES) owns the line (SWPAs facilities good for 167 MVA) | SWPA | 5CALCR - NORFORK 161KV CKT 1 SWPA | Replace buswork within bay and change metering CT ratio, replace wavetraps. Entergy must also reconductor their line to increase the rating. | 236 | 236 | 236 | 236 |  | 18 | 3 |  |  |  |  | New ratings are based on CT limits. They assume that Entergy also upgrades their line. | 100000 | 2007-04-20 | [23 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T9952212SP | FROM->TO | Bidirectional | 5CALCR - NORFORK 161KV CKT 1 | S | ENTR | SWPA | EES-ARK | EMINTH | 0 | 99803 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 12SP | 148 | 148 | 103.7 | 104.0517 | 111.4696 | [6 empty] | CATEGORYB | SINGLE | DELL - INDEPENDENCE 500KV CKT 1 | 0 | 99742 | 8DELL 5 500.00 | 99818 | 8ISES 5 500.00 | 0 |  | 1 | ASSIGN |  |  | AP&L (EES) owns the line (SWPAs facilities good for 167 MVA) | SWPA | 5CALCR - NORFORK 161KV CKT 1 SWPA | Replace buswork within bay and change metering CT ratio, replace wavetraps. Entergy must also reconductor their line to increase the rating. | 236 | 236 | 236 | 236 |  | 18 | 3 |  |  |  |  | New ratings are based on CT limits. They assume that Entergy also upgrades their line. | 100000 | 2007-04-20 | [23 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T23602212SP | FROM->TO | Bidirectional | 5CALCR - NORFORK 161KV CKT 1 | S | ENTR | SWPA | EES-ARK | EMINTH | 0 | 99803 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 12SP | 148 | 148 |  | 99.0433 | 106.69 | [6 empty] | CATEGORYB | GENOUT | GEN532751 1-WOLF CREEK GENERATING STATION UNIT 1 | 0 | 0 |  | 0 |  | 0 |  |  | ASSIGN |  |  | AP&L (EES) owns the line (SWPAs facilities good for 167 MVA) | SWPA | 5CALCR - NORFORK 161KV CKT 1 SWPA | Replace buswork within bay and change metering CT ratio, replace wavetraps. Entergy must also reconductor their line to increase the rating. | 236 | 236 | 236 | 236 |  | 18 | 3 |  |  |  |  | New ratings are based on CT limits. They assume that Entergy also upgrades their line. | 100000 | 2007-04-20 | [23 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 | NCONV | FNSL-Iteration limit exceeded | FDNS-Iteration limit exceeded | FNSL-Iteration limit exceeded | FDNS-Iteration limit exceeded | 2 | 2 | 2008-12-01 | 2007AG1AFS84L322212SP |  | Bidirectional | 5CALCR - NORFORK 161KV CKT 1 | S | ENTR | SWPA | EES-ARK | EMINTH | 0 | 99803 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 12SP | 148 | 148 | 84.56422 | 84.9413 | 92.1768 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | ASSIGN |  |  | AP&L (EES) owns the line (SWPAs facilities good for 167 MVA) | SWPA | 5CALCR - NORFORK 161KV CKT 1 SWPA | Replace buswork within bay and change metering CT ratio, replace wavetraps. Entergy must also reconductor their line to increase the rating. | 236 | 236 | 236 | 236 |  | 18 | 3 |  |  |  |  | New ratings are based on CT limits. They assume that Entergy also upgrades their line. | 100000 | 2007-04-20 | [23 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T4692212WP | FROM->TO | Bidirectional | 5CALCR - NORFORK 161KV CKT 1 | S | ENTR | SWPA | EES-ARK | EMINTH | 0 | 99803 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 12WP | 148 | 148 | 107.1 | 106.654 | 113.8356 | [6 empty] | CATEGORYB | SINGLE | DELL - INDEPENDENCE 500KV CKT 1 | 0 | 99742 | 8DELL 5 500.00 | 99818 | 8ISES 5 500.00 | 0 |  | 1 | ASSIGN |  |  | AP&L (EES) owns the line (SWPAs facilities good for 167 MVA) | SWPA | 5CALCR - NORFORK 161KV CKT 1 SWPA | Replace buswork within bay and change metering CT ratio, replace wavetraps. Entergy must also reconductor their line to increase the rating. | 236 | 236 | 236 | 236 |  | 18 | 3 |  |  |  |  | New ratings are based on CT limits. They assume that Entergy also upgrades their line. | 100000 | 2007-04-20 | [23 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T7442212WP | FROM->TO | Bidirectional | 5CALCR - NORFORK 161KV CKT 1 | S | ENTR | SWPA | EES-ARK | EMINTH | 0 | 99803 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 12WP | 148 | 148 | 101.1 | 99.9301 | 108.3881 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  | AP&L (EES) owns the line (SWPAs facilities good for 167 MVA) | SWPA | 5CALCR - NORFORK 161KV CKT 1 SWPA | Replace buswork within bay and change metering CT ratio, replace wavetraps. Entergy must also reconductor their line to increase the rating. | 236 | 236 | 236 | 236 |  | 18 | 3 |  |  |  |  | New ratings are based on CT limits. They assume that Entergy also upgrades their line. | 100000 | 2007-04-20 | [23 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T3412212WP | FROM->TO | Bidirectional | 5CALCR - NORFORK 161KV CKT 1 | S | ENTR | SWPA | EES-ARK | EMINTH | 0 | 99803 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 12WP | 148 | 148 |  | 96.2059 | 103.957 | [6 empty] | CATEGORYB | SINGLE | WHITEWATER EAST - WILHELMINA 345KV CKT 1 | 0 | 96051 | 7WILHLM 345.00 | 96054 | 7GOBKNO 345.00 | 0 |  | 1 | ASSIGN |  |  | AP&L (EES) owns the line (SWPAs facilities good for 167 MVA) | SWPA | 5CALCR - NORFORK 161KV CKT 1 SWPA | Replace buswork within bay and change metering CT ratio, replace wavetraps. Entergy must also reconductor their line to increase the rating. | 236 | 236 | 236 | 236 |  | 18 | 3 |  |  |  |  | New ratings are based on CT limits. They assume that Entergy also upgrades their line. | 100000 | 2007-04-20 | [23 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T15322417SP | FROM->TO | Bidirectional | 5CALCR - NORFORK 161KV CKT 1 | S | ENTR | SWPA | EES-ARK | EMINTH | 0 | 99803 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 17SP | 148 | 148 | 109.7 | 108.5296 | 115.643 | [6 empty] | CATEGORYB | SINGLE | DELL - INDEPENDENCE 500KV CKT 1 | 0 | 99742 | 8DELL 5 500.00 | 99818 | 8ISES 5 500.00 | 0 |  | 1 | ASSIGN |  |  | AP&L (EES) owns the line (SWPAs facilities good for 167 MVA) | SWPA | 5CALCR - NORFORK 161KV CKT 1 SWPA | Replace buswork within bay and change metering CT ratio, replace wavetraps. Entergy must also reconductor their line to increase the rating. | 236 | 236 | 236 | 236 |  | 18 | 3 |  |  |  |  | New ratings are based on CT limits. They assume that Entergy also upgrades their line. | 100000 | 2007-04-20 | [23 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T20482217SP | FROM->TO | Bidirectional | 5CALCR - NORFORK 161KV CKT 1 | S | ENTR | SWPA | EES-ARK | EMINTH | 0 | 99803 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 17SP | 148 | 148 | 106.5 | 105.7732 | 115.4392 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  | AP&L (EES) owns the line (SWPAs facilities good for 167 MVA) | SWPA | 5CALCR - NORFORK 161KV CKT 1 SWPA | Replace buswork within bay and change metering CT ratio, replace wavetraps. Entergy must also reconductor their line to increase the rating. | 236 | 236 | 236 | 236 |  | 18 | 3 |  |  |  |  | New ratings are based on CT limits. They assume that Entergy also upgrades their line. | 100000 | 2007-04-20 | [23 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 | NCONV | FNSL-Iteration limit exceeded | FDNS-Iteration limit exceeded | FNSL-Iteration limit exceeded | FDNS-Iteration limit exceeded | 2 | 2 | 2008-12-01 | 2007AG1AFS84L302217SP |  | Bidirectional | 5CALCR - NORFORK 161KV CKT 1 | S | ENTR | SWPA | EES-ARK | EMINTH | 0 | 99803 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 17SP | 148 | 148 | 86.82906 | 85.9511 | 93.5027 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | ASSIGN |  |  | AP&L (EES) owns the line (SWPAs facilities good for 167 MVA) | SWPA | 5CALCR - NORFORK 161KV CKT 1 SWPA | Replace buswork within bay and change metering CT ratio, replace wavetraps. Entergy must also reconductor their line to increase the rating. | 236 | 236 | 236 | 236 |  | 18 | 3 |  |  |  |  | New ratings are based on CT limits. They assume that Entergy also upgrades their line. | 100000 | 2007-04-20 | [23 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T3712208FA | FROM->TO |  | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99860 | 5ST_JOE 161.00 | 99843 | 5EVRTON 161.00 | 0 |  | 1 | 08FA | 167 | 167 |  | 98.8668 | 101.0455 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | Indeterminate | [37 empty] | 2008-10-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1872208WP | FROM->TO |  | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99860 | 5ST_JOE 161.00 | 99843 | 5EVRTON 161.00 | 0 |  | 1 | 08WP | 167 | 167 | 110.9 | 109.7747 | 112.5309 | [6 empty] | CATEGORYB | SINGLE | BULL SHOALS - BULL SHOALS 161KV CKT 1 | 0 | 505460 | BULL SH5 161.00 | 99802 | 5BULLSH* 161.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | Indeterminate | [37 empty] | 2008-10-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1582208WP | FROM->TO |  | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99860 | 5ST_JOE 161.00 | 99843 | 5EVRTON 161.00 | 0 |  | 1 | 08WP | 167 | 167 | 109.6 | 108.5428 | 111.3135 | [6 empty] | CATEGORYB | SINGLE | 5FLIPN - BULL SHOALS HES 161KV CKT 1 | 0 | 99802 | 5BULLSH* 161.00 | 99809 | 5FLIPN 161.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | Indeterminate | [37 empty] | 2008-10-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1602208WP | FROM->TO |  | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99860 | 5ST_JOE 161.00 | 99843 | 5EVRTON 161.00 | 0 |  | 1 | 08WP | 167 | 167 | 106.8 | 105.7627 | 108.5395 | [6 empty] | CATEGORYB | SINGLE | FLIPPIN - SUMMIT 161KV CKT 1 | 0 | 99809 | 5FLIPN 161.00 | 99837 | 5SUMMIT 161.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | Indeterminate | [37 empty] | 2008-10-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T7632209SP | FROM->TO |  | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99860 | 5ST_JOE 161.00 | 99843 | 5EVRTON 161.00 | 0 |  | 1 | 09SP | 167 | 167 | 115.1 | 113.8212 | 123.792 | [6 empty] | CATEGORYB | SINGLE | BULL SHOALS - BULL SHOALS 161KV CKT 1 | 0 | 505460 | BULL SH5 161.00 | 99802 | 5BULLSH* 161.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | Indeterminate | [37 empty] | 2008-10-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T6892209SP | FROM->TO |  | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99860 | 5ST_JOE 161.00 | 99843 | 5EVRTON 161.00 | 0 |  | 1 | 09SP | 167 | 167 | 113.6 | 112.3358 | 122.1098 | [6 empty] | CATEGORYB | SINGLE | 5FLIPN - BULL SHOALS HES 161KV CKT 1 | 0 | 99802 | 5BULLSH* 161.00 | 99809 | 5FLIPN 161.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | Indeterminate | [37 empty] | 2008-10-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T6962209SP | FROM->TO |  | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99860 | 5ST_JOE 161.00 | 99843 | 5EVRTON 161.00 | 0 |  | 1 | 09SP | 167 | 167 | 109.9 | 108.6537 | 118.5475 | [6 empty] | CATEGORYB | SINGLE | FLIPPIN - SUMMIT 161KV CKT 1 | 0 | 99809 | 5FLIPN 161.00 | 99837 | 5SUMMIT 161.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | Indeterminate | [37 empty] | 2008-10-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T4272209WP | FROM->TO |  | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99860 | 5ST_JOE 161.00 | 99843 | 5EVRTON 161.00 | 0 |  | 1 | 09WP | 167 | 167 | 112.6 | 111.1736 | 120.7274 | [6 empty] | CATEGORYB | SINGLE | BULL SHOALS - BULL SHOALS 161KV CKT 1 | 0 | 505460 | BULL SH5 161.00 | 99802 | 5BULLSH* 161.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | Indeterminate | [37 empty] | 2008-10-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T3432209WP | FROM->TO |  | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99860 | 5ST_JOE 161.00 | 99843 | 5EVRTON 161.00 | 0 |  | 1 | 09WP | 167 | 167 | 111.4 | 109.9701 | 119.5383 | [6 empty] | CATEGORYB | SINGLE | 5FLIPN - BULL SHOALS HES 161KV CKT 1 | 0 | 99802 | 5BULLSH* 161.00 | 99809 | 5FLIPN 161.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | Indeterminate | [37 empty] | 2008-10-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T3522209WP | FROM->TO |  | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99860 | 5ST_JOE 161.00 | 99843 | 5EVRTON 161.00 | 0 |  | 1 | 09WP | 167 | 167 | 108.6 | 107.1361 | 116.7648 | [6 empty] | CATEGORYB | SINGLE | FLIPPIN - SUMMIT 161KV CKT 1 | 0 | 99809 | 5FLIPN 161.00 | 99837 | 5SUMMIT 161.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | Indeterminate | [37 empty] | 2008-10-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T11352212SP | FROM->TO |  | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99860 | 5ST_JOE 161.00 | 99843 | 5EVRTON 161.00 | 0 |  | 1 | 12SP | 167 | 167 | 128.6 | 126.9593 | 139.0858 | [6 empty] | CATEGORYB | SINGLE | BULL SHOALS - BULL SHOALS 161KV CKT 1 | 0 | 505460 | BULL SH5 161.00 | 99802 | 5BULLSH* 161.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | Indeterminate | [37 empty] | 2008-10-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T10392212SP | FROM->TO |  | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99860 | 5ST_JOE 161.00 | 99843 | 5EVRTON 161.00 | 0 |  | 1 | 12SP | 167 | 167 | 126.9 | 125.2883 | 137.4184 | [6 empty] | CATEGORYB | SINGLE | 5FLIPN - BULL SHOALS HES 161KV CKT 1 | 0 | 99802 | 5BULLSH* 161.00 | 99809 | 5FLIPN 161.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | Indeterminate | [37 empty] | 2008-10-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T10512212SP | FROM->TO |  | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99860 | 5ST_JOE 161.00 | 99843 | 5EVRTON 161.00 | 0 |  | 1 | 12SP | 167 | 167 | 122.7 | 121.0779 | 133.1501 | [6 empty] | CATEGORYB | SINGLE | FLIPPIN - SUMMIT 161KV CKT 1 | 0 | 99809 | 5FLIPN 161.00 | 99837 | 5SUMMIT 161.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | Indeterminate | [37 empty] | 2008-10-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T5842212WP | FROM->TO |  | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99860 | 5ST_JOE 161.00 | 99843 | 5EVRTON 161.00 | 0 |  | 1 | 12WP | 167 | 167 | 120.9 | 117.1307 | 128.2838 | [6 empty] | CATEGORYB | SINGLE | BULL SHOALS - BULL SHOALS 161KV CKT 1 | 0 | 505460 | BULL SH5 161.00 | 99802 | 5BULLSH* 161.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | Indeterminate | [37 empty] | 2008-10-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T5002212WP | FROM->TO |  | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99860 | 5ST_JOE 161.00 | 99843 | 5EVRTON 161.00 | 0 |  | 1 | 12WP | 167 | 167 | 119.7 | 115.9082 | 127.0473 | [6 empty] | CATEGORYB | SINGLE | 5FLIPN - BULL SHOALS HES 161KV CKT 1 | 0 | 99802 | 5BULLSH* 161.00 | 99809 | 5FLIPN 161.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | Indeterminate | [37 empty] | 2008-10-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T5082212WP | FROM->TO |  | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99860 | 5ST_JOE 161.00 | 99843 | 5EVRTON 161.00 | 0 |  | 1 | 12WP | 167 | 167 | 116.5 | 112.8173 | 123.9102 | [6 empty] | CATEGORYB | SINGLE | FLIPPIN - SUMMIT 161KV CKT 1 | 0 | 99809 | 5FLIPN 161.00 | 99837 | 5SUMMIT 161.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | Indeterminate | [37 empty] | 2008-10-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T17062417SP | FROM->TO |  | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99860 | 5ST_JOE 161.00 | 99843 | 5EVRTON 161.00 | 0 |  | 1 | 17SP | 167 | 167 | 131.2 | 126.8563 | 139.0087 | [6 empty] | CATEGORYB | SINGLE | BULL SHOALS - BULL SHOALS 161KV CKT 1 | 0 | 505460 | BULL SH5 161.00 | 99802 | 5BULLSH* 161.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | Indeterminate | [37 empty] | 2008-10-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T16062417SP | FROM->TO |  | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99860 | 5ST_JOE 161.00 | 99843 | 5EVRTON 161.00 | 0 |  | 1 | 17SP | 167 | 167 | 129.4 | 125.0827 | 137.1491 | [6 empty] | CATEGORYB | SINGLE | 5FLIPN - BULL SHOALS HES 161KV CKT 1 | 0 | 99802 | 5BULLSH* 161.00 | 99809 | 5FLIPN 161.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | Indeterminate | [37 empty] | 2008-10-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T16172417SP | FROM->TO |  | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99860 | 5ST_JOE 161.00 | 99843 | 5EVRTON 161.00 | 0 |  | 1 | 17SP | 167 | 167 | 124.5 | 120.384 | 132.409 | [6 empty] | CATEGORYB | SINGLE | FLIPPIN - SUMMIT 161KV CKT 1 | 0 | 99809 | 5FLIPN 161.00 | 99837 | 5SUMMIT 161.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | Indeterminate | [37 empty] | 2008-10-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4502317SP | TO->FROM |  | 95TH & WAVERLY - CAPTAIN JUNCTION 115KV CKT 1 | REL | WERE | WERE | NEAST | NEAST | 0 | 533235 | CAPTAIN3 115.00 | 533278 | WAVERLY3 115.00 | 0 |  | 1 | 17SP | 118 | 118 | 104.6 | 104.287 | 112.3242 | [6 empty] | CATEGORYB | SINGLE | MONTICELLO - PENTAGON 115KV CKT 1 | 0 | 533261 | PENTAGN3 115.00 | 533281 | MNTCLLO3 115.00 | 0 |  | 1 |  |  |  |  | WERE | 95TH & WAVERLY - CAPTAIN JUNCTION 115KV CKT 1 | Rebuild 7.61 miles from 95th & Waverly-Captain Junction 115 kV line. | 223 | 240 | 223 | 240 | 7.61 | 12 | 5 |  | 0.00464 | 0.041 | 0.00606 | 240 MVA is breaker and CT limit. | 2580000 | 2006-07-21 | [23 empty] | 2017-06-01 | 2017-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T5972317SP | TO->FROM |  | 95TH & WAVERLY - CAPTAIN JUNCTION 115KV CKT 1 | REL | WERE | WERE | NEAST | NEAST | 0 | 533235 | CAPTAIN3 115.00 | 533278 | WAVERLY3 115.00 | 0 |  | 1 | 17SP | 118 | 118 |  | 96.0746 | 100.5398 | [6 empty] | CATEGORYB | SINGLE | LACKMAN - STILWELL 161KV CKT 1 | 0 | 542969 | STILWEL5 161.00 | 543126 | LACKMAN5 161.00 | 0 |  | 1 |  |  |  |  | WERE | 95TH & WAVERLY - CAPTAIN JUNCTION 115KV CKT 1 | Rebuild 7.61 miles from 95th & Waverly-Captain Junction 115 kV line. | 223 | 240 | 223 | 240 | 7.61 | 12 | 5 |  | 0.00464 | 0.041 | 0.00606 | 240 MVA is breaker and CT limit. | 2580000 | 2006-07-21 | [23 empty] | 2017-06-01 | 2017-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4532317SP | TO->FROM |  | 95TH & WAVERLY - CAPTAIN JUNCTION 115KV CKT 1 | REL | WERE | WERE | NEAST | NEAST | 0 | 533235 | CAPTAIN3 115.00 | 533278 | WAVERLY3 115.00 | 0 |  | 1 | 17SP | 118 | 118 |  | 92.5489 | 100 | [6 empty] | CATEGORYB | SINGLE | MONTICELLO - TIMBERLANE 115KV CKT 1 | 0 | 533273 | TIMBRLN3 115.00 | 533281 | MNTCLLO3 115.00 | 0 |  | 1 |  |  |  |  | WERE | 95TH & WAVERLY - CAPTAIN JUNCTION 115KV CKT 1 | Rebuild 7.61 miles from 95th & Waverly-Captain Junction 115 kV line. | 223 | 240 | 223 | 240 | 7.61 | 12 | 5 |  | 0.00464 | 0.041 | 0.00606 | 240 MVA is breaker and CT limit. | 2580000 | 2006-07-21 | [23 empty] | 2017-06-01 | 2017-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T3442312SP | TO->FROM |  | ALABAMA - LAKE ROAD 161KV CKT 1 | REL | MIPU | MIPU | FLA | FLA | 0 | 541255 | LAKE RD5 161.00 | 541354 | ALABAMA5 161.00 | 0 |  | 1 | 12SP | 151 | 161 | 106.6 | 108.9554 | 108.5238 | [6 empty] | CATEGORYB | SINGLE | HAWTHORN - ST JOE 345KV CKT 1 | 0 | 541199 | ST JOE 3 345.00 | 542972 | HAWTH 7 345.00 | 0 |  | 1 |  |  |  | re-set the over current relay to trip the Lake Road-Alabama section when flow goes above 161 MVA | MIPU | ALABAMA - LAKE ROAD 161KV CKT 1 | re-set the over current relay to trip the Lake Road-Alabama section when flow goes above 161 MVA | [37 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T3572312SP | TO->FROM |  | ALABAMA - LAKE ROAD 161KV CKT 1 | REL | MIPU | MIPU | FLA | FLA | 0 | 541255 | LAKE RD5 161.00 | 541354 | ALABAMA5 161.00 | 0 |  | 1 | 12SP | 151 | 161 | 100.8 | 101.905 | 101.6453 | [6 empty] | CATEGORYB | SINGLE | IATAN - PLATTE CITY 161KV CKT 1 | 0 | 541221 | PLTCTY 5 161.00 | 541350 | IATAN5 161.00 | 0 |  | 1 |  |  |  | re-set the over current relay to trip the Lake Road-Alabama section when flow goes above 161 MVA | MIPU | ALABAMA - LAKE ROAD 161KV CKT 1 | re-set the over current relay to trip the Lake Road-Alabama section when flow goes above 161 MVA | [37 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T4804317SP | TO->FROM |  | ALABAMA - LAKE ROAD 161KV CKT 1 | REL | MIPU | MIPU | FLA | FLA | 0 | 541255 | LAKE RD5 161.00 | 541354 | ALABAMA5 161.00 | 0 |  | 1 | 17SP | 151 | 161 | 110.1 | 111.3154 | 108.7037 | [6 empty] | CATEGORYB | SINGLE | HAWTHORN - ST JOE 345KV CKT 1 | 0 | 541199 | ST JOE 3 345.00 | 542972 | HAWTH 7 345.00 | 0 |  | 1 |  |  |  | re-set the over current relay to trip the Lake Road-Alabama section when flow goes above 161 MVA | MIPU | ALABAMA - LAKE ROAD 161KV CKT 1 | re-set the over current relay to trip the Lake Road-Alabama section when flow goes above 161 MVA | [37 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T4884317SP | TO->FROM |  | ALABAMA - LAKE ROAD 161KV CKT 1 | REL | MIPU | MIPU | FLA | FLA | 0 | 541255 | LAKE RD5 161.00 | 541354 | ALABAMA5 161.00 | 0 |  | 1 | 17SP | 151 | 161 | 107.5 | 108.4357 | 105.9899 | [6 empty] | CATEGORYB | SINGLE | IATAN - PLATTE CITY 161KV CKT 1 | 0 | 541221 | PLTCTY 5 161.00 | 541350 | IATAN5 161.00 | 0 |  | 1 |  |  |  | re-set the over current relay to trip the Lake Road-Alabama section when flow goes above 161 MVA | MIPU | ALABAMA - LAKE ROAD 161KV CKT 1 | re-set the over current relay to trip the Lake Road-Alabama section when flow goes above 161 MVA | [37 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T1052408SH | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 08SH | 32 | 32 |  | 25.2998 | 101.9869 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1872208SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 08SP | 32 | 32 |  | 29.7355 | 122.0877 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1862208SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 08SP | 32 | 32 |  | 26.3121 | 118.4294 | [6 empty] | CATEGORYB | SINGLE | ORCHARD - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533643 | ORCHARD2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T1652308SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 08SP | 32 | 32 |  | 12.5859 | 111.7993 | [6 empty] | CATEGORYB | SINGLE | ATHENS SWITCHING STATION - OWL CREEK 69KV CKT 1 | 0 | 533623 | ATHENS 2 69.000 | 533642 | OWL CRK2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T1582408SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 08SP | 58 | 58 |  | 65.4461 | 103.802 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T1612408SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 08SP | 58 | 58 |  | 63.6438 | 101.879 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1492108SP | TO->FROM |  | LEHIGH TAP - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 08SP | 32 | 32 |  | 9.733 | 120.9169 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T1883309SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 09SP | 32 | 32 |  | 29.8705 | 124.2703 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T1873309SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 09SP | 32 | 32 |  | 26.4167 | 120.5106 | [6 empty] | CATEGORYB | SINGLE | ORCHARD - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533643 | ORCHARD2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T1833309SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 09SP | 32 | 32 |  | 12.6944 | 113.9161 | [6 empty] | CATEGORYB | SINGLE | ATHENS SWITCHING STATION - OWL CREEK 69KV CKT 1 | 0 | 533623 | ATHENS 2 69.000 | 533642 | OWL CRK2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T1794409SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 09SP | 58 | 58 |  | 65.5805 | 104.7422 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T1824409SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 09SP | 58 | 58 |  | 63.7171 | 102.7839 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T6324109SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 09SP | 58 | 58 |  | 72.8628 | 100.1831 | [6 empty] | CATEGORYB | SINGLE | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81T1751409SP | TO->FROM |  | LEHIGH TAP - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 09SP | 32 | 32 |  | 8.7892 | 124.0056 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2451112SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12SP | 32 | 32 |  | -999 | 185.4455 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T8991112SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12SP | 32 | 32 |  | -999 | 184.8256 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T2942112SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12SP | 32 | 32 |  | 31.8691 | 130.8571 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2461112SP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 157.4692 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T9001112SP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 156.7557 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2471112SP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 12SP | 108 | 108 |  | -999 | 170.7109 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T9011112SP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 12SP | 108 | 108 |  | -999 | 170.0226 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2792412SP | TO->FROM |  | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 56.0845 | 117.3039 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2912412SP | TO->FROM |  | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 55.5503 | 112.3373 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1582212SP | TO->FROM |  | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 72.3233 | 103.7043 | [6 empty] | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2782412SP | FROM->TO |  | ALTOONA - TIOGA 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 41.4013 | 157.0806 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T2972112SP | FROM->TO |  | ALTOONA - TIOGA 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 40.3416 | 153.9666 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T2772112SP | FROM->TO |  | ALTOONA - TIOGA 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 35.1642 | 128.815 | [6 empty] | CATEGORYB | SINGLE | ALLEN - ZILA JUNCTION 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | NCONV |  |  | FNSL-Blown up | FDNS-Blown up | 2 | 3 | 2008-12-01 | 2007AG1AFS84L32312SP |  |  | ALTOONA - TIOGA 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 25.1844 | 72.1214 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2812412SP | TO->FROM | Bidirectional | ARCO TAP - ENA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533634 | ENA 2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | 51.9299 | 110.5372 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2431112SP | FROM->TO | Bidirectional | ARCO TAP - ENA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533620 | ARCOTAP2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 108.209 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T8971112SP | FROM->TO | Bidirectional | ARCO TAP - ENA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533620 | ARCOTAP2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 107.7968 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2441112SP | TO->FROM | Bidirectional | ARCO TAP - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533641 | MONARCH2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 111.7972 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T8981112SP | TO->FROM | Bidirectional | ARCO TAP - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533641 | MONARCH2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 111.3621 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2822412SP | FROM->TO | Bidirectional | ARCO TAP - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533620 | ARCOTAP2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | 49.4684 | 107.2233 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2662412SP | FROM->TO |  | ATHENS SWITCHING STATION - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533623 | ATHENS 2 69.000 | 533642 | OWL CRK2 69.000 | 0 |  | 1 | 12SP | 41 | 41 |  | 10.1577 | 122.0473 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2832412SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12SP | 58 | 58 |  | 67.3281 | 140.9509 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T3022112SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12SP | 58 | 58 |  | 65.3825 | 136.6898 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2481112SP | FROM->TO | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533634 | ENA 2 69.000 | 533646 | TIOGA 2 69.000 | 0 |  | 1 | 12SP | 58 | 58 |  | -999 | 130.2259 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2672412SP | TO->FROM |  | LEHIGH TAP - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12SP | 32 | 32 |  | 9.2569 | 152.3867 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2491112SP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 12SP | 100 | 100 |  | -999 | 193.7517 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T9031112SP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 12SP | 100 | 100 |  | -999 | 192.9783 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2501112SP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 12SP | 108 | 108 |  | -999 | 178.3467 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T9041112SP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 12SP | 108 | 108 |  | -999 | 177.6278 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T572112WP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12WP | 32 | 32 |  | 24.6721 | 179.9951 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T3802112WP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12WP | 32 | 32 |  | 24.8481 | 179.8879 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T574312WP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12WP | 32 | 32 |  | 22.9815 | 100.7665 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T582112WP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 39.9857 | 150.9578 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T3812112WP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 40.0893 | 150.8733 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T553312WP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 12WP | 108 | 108 |  | 36.4684 | 159.2099 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T3843312WP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 12WP | 108 | 108 |  | 36.5782 | 159.1568 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T464112WP | FROM->TO | Bidirectional | ARCO TAP - ENA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533620 | ARCOTAP2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 9.7864 | 101.0901 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T3394112WP | FROM->TO | Bidirectional | ARCO TAP - ENA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533620 | ARCOTAP2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 10.0489 | 100.9961 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T474112WP | TO->FROM | Bidirectional | ARCO TAP - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533641 | MONARCH2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 11.0682 | 103.599 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T3404112WP | TO->FROM | Bidirectional | ARCO TAP - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533641 | MONARCH2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 11.2882 | 103.5055 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T514112WP | FROM->TO | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533634 | ENA 2 69.000 | 533646 | TIOGA 2 69.000 | 0 |  | 1 | 12WP | 58 | 58 |  | 10.7435 | 122.8447 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T3444112WP | FROM->TO | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533634 | ENA 2 69.000 | 533646 | TIOGA 2 69.000 | 0 |  | 1 | 12WP | 58 | 58 |  | 11.1297 | 122.7501 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81T964212WP | TO->FROM |  | LEHIGH TAP - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12WP | 32 | 32 |  | 7.335 | 100.4311 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T593312WP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 12WP | 100 | 100 |  | 44.6309 | 179.6932 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T3883312WP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 12WP | 100 | 100 |  | 44.776 | 179.5805 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T613312WP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 12WP | 108 | 108 |  | 40.4185 | 165.4322 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T3024312WP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 12WP | 108 | 108 |  | 40.5965 | 165.359 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4092317SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 17SP | 32 | 32 |  | 14.5581 | 132.3017 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16612317SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 17SP | 32 | 32 |  | 14.4858 | 131.4416 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4832317SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 17SP | 32 | 32 |  | 35.6597 | 126.9833 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4102317SP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 17SP | 72 | 72 |  | 23.268 | 100.8105 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16622317SP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 17SP | 72 | 72 |  | 23.1386 | 100.3044 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4112317SP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 17SP | 108 | 108 |  | 28.8307 | 116.5141 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16632317SP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 17SP | 108 | 108 |  | 28.7177 | 115.9243 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T6122417SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 17SP | 58 | 58 |  | 70.7819 | 101.4296 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T4742117SP | TO->FROM |  | LEHIGH TAP - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 17SP | 32 | 32 |  | 11.392 | 117.9501 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4122317SP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 17SP | 100 | 100 |  | 38.8083 | 133.7621 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16642317SP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 17SP | 100 | 100 |  | 38.688 | 133.0647 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4132317SP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 17SP | 108 | 108 |  | 34.6116 | 122.4871 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16652317SP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 17SP | 108 | 108 |  | 34.4969 | 121.8479 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T752308SH | TO->FROM |  | ARKANSAS CITY - PARIS 69KV CKT 1 | S | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533548 | PARIS 2 69.000 | 533542 | ARKCITY2 69.000 | 0 |  | 1 | 08SH | 72 | 72 |  | 44.6329 | 104.0432 | [6 empty] | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ARKANSAS CITY - PARIS 69KV CKT 1 #1 Displacement | Replace Disconnect Switches and Bus Jumpers at Paris and Ark City 69 kV substations | 80 | 80 | 80 | 80 |  | 5 | 1 |  |  |  |  | 80 MVA is the new conductor sag limit | 50000 | 2006-03-21 | [23 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T4354317SP | TO->FROM |  | ARKANSAS CITY - PARIS 69KV CKT 1 | S | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533548 | PARIS 2 69.000 | 533542 | ARKCITY2 69.000 | 0 |  | 1 | 17SP | 72 | 72 | 104.8 | 57.2015 | 104.8555 | [6 empty] | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ARKANSAS CITY - PARIS 69KV CKT 1 #1 Displacement | Replace Disconnect Switches and Bus Jumpers at Paris and Ark City 69 kV substations | 80 | 80 | 80 | 80 |  | 5 | 1 |  |  |  |  | 80 MVA is the new conductor sag limit | 50000 | 2006-03-21 | [23 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T3182417SP | TO->FROM |  | ARKOMA - FT SMITHW 161KV CKT 1 | EXP | OKGE | OKGE | FT SMITH | FT SMITH | 0 | 515301 | FTSMTHW5 161.00 | 515306 | ARKOMA 5 161.00 | 0 |  | 1 | 17SP | 313 | 335 | 108.0 | 108.4546 | 112.0093 | [6 empty] | CATEGORYB | SINGLE | MASSARD - WHITESIDE 161KV CKT 1 | 0 | 515341 | WHITESD5 161.00 | 515343 | MASSARD5 161.00 | 0 |  | 1 |  |  |  |  | OKGE | ARKOMA - FT SMITHW 161KV CKT 1 | Replace 1200A terminal equipment at Arkoma to 2000A and rebuild 4.47 miles of line to 1590AS52. | 446 | 446 | 446 | 446 | 4.47 | 18 | 12 |  | 0.00116 | 0.01187 | 0.00721 |  | 3100000 | 2008-01-02 | [23 empty] | 2014-06-01 | 2014-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T3182417SP | TO->FROM |  | ARKOMA - FT SMITHW 161KV CKT 1 | EXP | OKGE | OKGE | FT SMITH | FT SMITH | 0 | 515301 | FTSMTHW5 161.00 | 515306 | ARKOMA 5 161.00 | 0 |  | 1 | 17SP | 313 | 335 | 108.0 | 108.4546 | 112.0093 | [6 empty] | CATEGORYB | SINGLE | MASSARD - WHITESIDE 161KV CKT 1 | 0 | 515341 | WHITESD5 161.00 | 515343 | MASSARD5 161.00 | 0 |  | 1 |  |  |  |  | OKGE | ARKOMA - FT SMITHW 161KV CKT 1 | Replace 1200A terminal equipment at Arkoma to 2000A and rebuild 4.47 miles of line to 1590AS52. | 446 | 446 | 446 | 446 | 4.47 | 18 | 12 |  | 0.00116 | 0.01187 | 0.00721 |  | 3100000 | 2008-01-02 | [23 empty] | 2014-06-01 | 2014-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T2962112SP | TO->FROM |  | ASH GROVE JCT2 - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533660 | ASHGRJ22 69.000 | 0 |  | 1 | 12SP | 37 | 37 |  | 10.7628 | 189.1539 | [6 empty] | CATEGORYB | SINGLE | CHANUTE TAP - TIOGA 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533666 | CHANTAP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ASH GROVE JCT2 - TIOGA 69KV CKT 1 | Rebuild 2.13 miles |  |  |  |  | 2.13 |  |  |  | 0.0044777 | 0.03078 | 0.00063104 | 450k per mile | 958500 | 2008-01-01 | [23 empty] | 2010-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T3672212SP | TO->FROM |  | ASH GROVE JCT2 - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533660 | ASHGRJ22 69.000 | 0 |  | 1 | 12SP | 37 | 37 |  | 0.33806 | 173.3156 | [6 empty] | CATEGORYB | SINGLE | CHANUTE GENERATION SUB - CHANUTE TAP 69KV CKT 1 | 0 | 533662 | CGENSUB2 69.000 | 533666 | CHANTAP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ASH GROVE JCT2 - TIOGA 69KV CKT 1 | Rebuild 2.13 miles |  |  |  |  | 2.13 |  |  |  | 0.0044777 | 0.03078 | 0.00063104 | 450k per mile | 958500 | 2008-01-01 | [23 empty] | 2010-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T15105512SP | TO->FROM |  | ASH GROVE JCT2 - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533660 | ASHGRJ22 69.000 | 0 |  | 1 | 12SP | 37 | 37 |  | 4.5688 | 101.5507 | [6 empty] | CATEGORYB | GENOUT | GEN533662 14-CHANUTE GENERATION SUB | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ASH GROVE JCT2 - TIOGA 69KV CKT 1 | Rebuild 2.13 miles |  |  |  |  | 2.13 |  |  |  | 0.0044777 | 0.03078 | 0.00063104 | 450k per mile | 958500 | 2008-01-01 | [23 empty] | 2010-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1712212WP | TO->FROM |  | ASH GROVE JCT2 - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533660 | ASHGRJ22 69.000 | 0 |  | 1 | 12WP | 37 | 37 |  | 7.8046 | 135.8767 | [6 empty] | CATEGORYB | SINGLE | CHANUTE TAP - TIOGA 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533666 | CHANTAP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ASH GROVE JCT2 - TIOGA 69KV CKT 1 | Rebuild 2.13 miles |  |  |  |  | 2.13 |  |  |  | 0.0044777 | 0.03078 | 0.00063104 | 450k per mile | 958500 | 2008-01-01 | [23 empty] | 2010-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 4 | 2008-12-01 | 2007AG1AFS81T893412WP | TO->FROM |  | ASH GROVE JCT2 - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533660 | ASHGRJ22 69.000 | 0 |  | 1 | 12WP | 37 | 37 |  | 0.3249 | 128.4224 | [6 empty] | CATEGORYB | SINGLE | CHANUTE GENERATION SUB - CHANUTE TAP 69KV CKT 1 | 0 | 533662 | CGENSUB2 69.000 | 533666 | CHANTAP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ASH GROVE JCT2 - TIOGA 69KV CKT 1 | Rebuild 2.13 miles |  |  |  |  | 2.13 |  |  |  | 0.0044777 | 0.03078 | 0.00063104 | 450k per mile | 958500 | 2008-01-01 | [23 empty] | 2010-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T3484112WP | TO->FROM |  | ASH GROVE JCT2 - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533660 | ASHGRJ22 69.000 | 0 |  | 1 | 12WP | 37 | 37 |  | 3.4085 | 117.3806 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ASH GROVE JCT2 - TIOGA 69KV CKT 1 | Rebuild 2.13 miles |  |  |  |  | 2.13 |  |  |  | 0.0044777 | 0.03078 | 0.00063104 | 450k per mile | 958500 | 2008-01-01 | [23 empty] | 2010-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T4892117SP | TO->FROM |  | ASH GROVE JCT2 - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533660 | ASHGRJ22 69.000 | 0 |  | 1 | 17SP | 37 | 37 |  | 2.2078 | 144.7767 | [6 empty] | CATEGORYB | SINGLE | CHANUTE GENERATION SUB - CHANUTE TAP 69KV CKT 1 | 0 | 533662 | CGENSUB2 69.000 | 533666 | CHANTAP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ASH GROVE JCT2 - TIOGA 69KV CKT 1 | Rebuild 2.13 miles |  |  |  |  | 2.13 |  |  |  | 0.0044777 | 0.03078 | 0.00063104 | 450k per mile | 958500 | 2008-01-01 | [23 empty] | 2010-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T5662217SP | TO->FROM |  | ASH GROVE JCT2 - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533660 | ASHGRJ22 69.000 | 0 |  | 1 | 17SP | 37 | 37 |  | 41.2844 | 106.7215 | [6 empty] | CATEGORYB | SINGLE | CHANUTE TAP - TIOGA 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533666 | CHANTAP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ASH GROVE JCT2 - TIOGA 69KV CKT 1 | Rebuild 2.13 miles |  |  |  |  | 2.13 |  |  |  | 0.0044777 | 0.03078 | 0.00063104 | 450k per mile | 958500 | 2008-01-01 | [23 empty] | 2010-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T1052408SH | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 08SH | 32 | 32 |  | 25.2998 | 101.9869 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1872208SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 08SP | 32 | 32 |  | 29.7355 | 122.0877 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1862208SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 08SP | 32 | 32 |  | 26.3121 | 118.4294 | [6 empty] | CATEGORYB | SINGLE | ORCHARD - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533643 | ORCHARD2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T1652308SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 08SP | 32 | 32 |  | 12.5859 | 111.7993 | [6 empty] | CATEGORYB | SINGLE | ATHENS SWITCHING STATION - OWL CREEK 69KV CKT 1 | 0 | 533623 | ATHENS 2 69.000 | 533642 | OWL CRK2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T1582408SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 08SP | 58 | 58 |  | 65.4461 | 103.802 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T1612408SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 08SP | 58 | 58 |  | 63.6438 | 101.879 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1492108SP | TO->FROM |  | LEHIGH TAP - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 08SP | 32 | 32 |  | 9.733 | 120.9169 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T1883309SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 09SP | 32 | 32 |  | 29.8705 | 124.2703 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T1873309SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 09SP | 32 | 32 |  | 26.4167 | 120.5106 | [6 empty] | CATEGORYB | SINGLE | ORCHARD - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533643 | ORCHARD2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T1833309SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 09SP | 32 | 32 |  | 12.6944 | 113.9161 | [6 empty] | CATEGORYB | SINGLE | ATHENS SWITCHING STATION - OWL CREEK 69KV CKT 1 | 0 | 533623 | ATHENS 2 69.000 | 533642 | OWL CRK2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T1794409SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 09SP | 58 | 58 |  | 65.5805 | 104.7422 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T1824409SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 09SP | 58 | 58 |  | 63.7171 | 102.7839 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T6324109SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 09SP | 58 | 58 |  | 72.8628 | 100.1831 | [6 empty] | CATEGORYB | SINGLE | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81T1751409SP | TO->FROM |  | LEHIGH TAP - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 09SP | 32 | 32 |  | 8.7892 | 124.0056 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2451112SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12SP | 32 | 32 |  | -999 | 185.4455 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T8991112SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12SP | 32 | 32 |  | -999 | 184.8256 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T2942112SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12SP | 32 | 32 |  | 31.8691 | 130.8571 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2461112SP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 157.4692 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T9001112SP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 156.7557 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2471112SP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 12SP | 108 | 108 |  | -999 | 170.7109 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T9011112SP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 12SP | 108 | 108 |  | -999 | 170.0226 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2792412SP | TO->FROM |  | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 56.0845 | 117.3039 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2912412SP | TO->FROM |  | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 55.5503 | 112.3373 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1582212SP | TO->FROM |  | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 72.3233 | 103.7043 | [6 empty] | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2782412SP | FROM->TO |  | ALTOONA - TIOGA 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 41.4013 | 157.0806 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T2972112SP | FROM->TO |  | ALTOONA - TIOGA 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 40.3416 | 153.9666 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T2772112SP | FROM->TO |  | ALTOONA - TIOGA 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 35.1642 | 128.815 | [6 empty] | CATEGORYB | SINGLE | ALLEN - ZILA JUNCTION 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | NCONV |  |  | FNSL-Blown up | FDNS-Blown up | 2 | 3 | 2008-12-01 | 2007AG1AFS84L32312SP |  |  | ALTOONA - TIOGA 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 25.1844 | 72.1214 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2812412SP | TO->FROM | Bidirectional | ARCO TAP - ENA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533634 | ENA 2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | 51.9299 | 110.5372 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2431112SP | FROM->TO | Bidirectional | ARCO TAP - ENA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533620 | ARCOTAP2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 108.209 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T8971112SP | FROM->TO | Bidirectional | ARCO TAP - ENA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533620 | ARCOTAP2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 107.7968 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2441112SP | TO->FROM | Bidirectional | ARCO TAP - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533641 | MONARCH2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 111.7972 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T8981112SP | TO->FROM | Bidirectional | ARCO TAP - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533641 | MONARCH2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 111.3621 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2822412SP | FROM->TO | Bidirectional | ARCO TAP - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533620 | ARCOTAP2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | 49.4684 | 107.2233 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2662412SP | FROM->TO |  | ATHENS SWITCHING STATION - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533623 | ATHENS 2 69.000 | 533642 | OWL CRK2 69.000 | 0 |  | 1 | 12SP | 41 | 41 |  | 10.1577 | 122.0473 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2832412SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12SP | 58 | 58 |  | 67.3281 | 140.9509 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T3022112SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12SP | 58 | 58 |  | 65.3825 | 136.6898 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2481112SP | FROM->TO | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533634 | ENA 2 69.000 | 533646 | TIOGA 2 69.000 | 0 |  | 1 | 12SP | 58 | 58 |  | -999 | 130.2259 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2672412SP | TO->FROM |  | LEHIGH TAP - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12SP | 32 | 32 |  | 9.2569 | 152.3867 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2491112SP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 12SP | 100 | 100 |  | -999 | 193.7517 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T9031112SP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 12SP | 100 | 100 |  | -999 | 192.9783 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2501112SP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 12SP | 108 | 108 |  | -999 | 178.3467 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T9041112SP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 12SP | 108 | 108 |  | -999 | 177.6278 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T572112WP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12WP | 32 | 32 |  | 24.6721 | 179.9951 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T3802112WP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12WP | 32 | 32 |  | 24.8481 | 179.8879 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T574312WP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12WP | 32 | 32 |  | 22.9815 | 100.7665 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T582112WP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 39.9857 | 150.9578 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T3812112WP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 40.0893 | 150.8733 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T553312WP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 12WP | 108 | 108 |  | 36.4684 | 159.2099 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T3843312WP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 12WP | 108 | 108 |  | 36.5782 | 159.1568 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T464112WP | FROM->TO | Bidirectional | ARCO TAP - ENA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533620 | ARCOTAP2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 9.7864 | 101.0901 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T3394112WP | FROM->TO | Bidirectional | ARCO TAP - ENA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533620 | ARCOTAP2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 10.0489 | 100.9961 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T474112WP | TO->FROM | Bidirectional | ARCO TAP - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533641 | MONARCH2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 11.0682 | 103.599 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T3404112WP | TO->FROM | Bidirectional | ARCO TAP - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533641 | MONARCH2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 11.2882 | 103.5055 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T514112WP | FROM->TO | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533634 | ENA 2 69.000 | 533646 | TIOGA 2 69.000 | 0 |  | 1 | 12WP | 58 | 58 |  | 10.7435 | 122.8447 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T3444112WP | FROM->TO | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533634 | ENA 2 69.000 | 533646 | TIOGA 2 69.000 | 0 |  | 1 | 12WP | 58 | 58 |  | 11.1297 | 122.7501 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81T964212WP | TO->FROM |  | LEHIGH TAP - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12WP | 32 | 32 |  | 7.335 | 100.4311 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T593312WP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 12WP | 100 | 100 |  | 44.6309 | 179.6932 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T3883312WP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 12WP | 100 | 100 |  | 44.776 | 179.5805 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T613312WP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 12WP | 108 | 108 |  | 40.4185 | 165.4322 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T3024312WP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 12WP | 108 | 108 |  | 40.5965 | 165.359 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4092317SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 17SP | 32 | 32 |  | 14.5581 | 132.3017 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16612317SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 17SP | 32 | 32 |  | 14.4858 | 131.4416 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4832317SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 17SP | 32 | 32 |  | 35.6597 | 126.9833 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4102317SP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 17SP | 72 | 72 |  | 23.268 | 100.8105 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16622317SP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 17SP | 72 | 72 |  | 23.1386 | 100.3044 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4112317SP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 17SP | 108 | 108 |  | 28.8307 | 116.5141 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16632317SP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 17SP | 108 | 108 |  | 28.7177 | 115.9243 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T6122417SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 17SP | 58 | 58 |  | 70.7819 | 101.4296 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T4742117SP | TO->FROM |  | LEHIGH TAP - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 17SP | 32 | 32 |  | 11.392 | 117.9501 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4122317SP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 17SP | 100 | 100 |  | 38.8083 | 133.7621 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16642317SP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 17SP | 100 | 100 |  | 38.688 | 133.0647 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4132317SP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 17SP | 108 | 108 |  | 34.6116 | 122.4871 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16652317SP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 17SP | 108 | 108 |  | 34.4969 | 121.8479 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Athens to Owl Creek 69 kV | Rebuild Athens to Owl Creek (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 2.93 | 18 | 6 |  | 0.00618 | 0.04207 | 0.00089 | Terminal equipment limit | 1208769 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T232308SH | FROM->TO |  | BARTLESVILLE SOUTHEAST - NORTH BARTLESVILLE 138KV CKT 1 | S | AEPW | AEPW | NORTHERN | TS-KAMO | 0 | 510391 | BV-SE--4 138.00 | 510386 | NBVILLE4 138.00 | 0 |  | 1 | 08SH | 202 | 235 |  | 97.9161 | 100.5716 | [6 empty] | CATEGORYB | SINGLE | DELAWARE - NORTHEAST STATION 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 510406 | N.E.S.-7 345.00 | 0 |  | 1 |  |  |  |  | AEPW | BARTLESVILLE SOUTHEAST - NORTH BARTLESVILLE 138KV CKT 1 | Rebuild 8.37 miles of 795 ACSR with 1590 ACSR & reset relays @ BSE | 280 | 287 | 287 | 287 | 8.37 | 24 | 9 |  | 0.00286 | 0.03081 | 0.0097 | New limits will be wavetrap jumpers, breakers & switches | 8400000 | 2007-04-11 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T502308SP | FROM->TO |  | BARTLESVILLE SOUTHEAST - NORTH BARTLESVILLE 138KV CKT 1 | S | AEPW | AEPW | NORTHERN | TS-KAMO | 0 | 510391 | BV-SE--4 138.00 | 510386 | NBVILLE4 138.00 | 0 |  | 1 | 08SP | 202 | 235 |  | 97.952 | 101.1703 | [6 empty] | CATEGORYB | SINGLE | DELAWARE - NORTHEAST STATION 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 510406 | N.E.S.-7 345.00 | 0 |  | 1 |  |  |  |  | AEPW | BARTLESVILLE SOUTHEAST - NORTH BARTLESVILLE 138KV CKT 1 | Rebuild 8.37 miles of 795 ACSR with 1590 ACSR & reset relays @ BSE | 280 | 287 | 287 | 287 | 8.37 | 24 | 9 |  | 0.00286 | 0.03081 | 0.0097 | New limits will be wavetrap jumpers, breakers & switches | 8400000 | 2007-04-11 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T623309SP | FROM->TO |  | BARTLESVILLE SOUTHEAST - NORTH BARTLESVILLE 138KV CKT 1 | S | AEPW | AEPW | NORTHERN | TS-KAMO | 0 | 510391 | BV-SE--4 138.00 | 510386 | NBVILLE4 138.00 | 0 |  | 1 | 09SP | 202 | 235 | 101.2 | 100.1216 | 108.1133 | [6 empty] | CATEGORYB | SINGLE | DELAWARE - NORTHEAST STATION 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 510406 | N.E.S.-7 345.00 | 0 |  | 1 |  |  |  |  | AEPW | BARTLESVILLE SOUTHEAST - NORTH BARTLESVILLE 138KV CKT 1 | Rebuild 8.37 miles of 795 ACSR with 1590 ACSR & reset relays @ BSE | 280 | 287 | 287 | 287 | 8.37 | 24 | 9 |  | 0.00286 | 0.03081 | 0.0097 | New limits will be wavetrap jumpers, breakers & switches | 8400000 | 2007-04-11 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T1113312SP | FROM->TO |  | BARTLESVILLE SOUTHEAST - NORTH BARTLESVILLE 138KV CKT 1 | S | AEPW | AEPW | NORTHERN | TS-KAMO | 0 | 510391 | BV-SE--4 138.00 | 510386 | NBVILLE4 138.00 | 0 |  | 1 | 12SP | 202 | 235 |  | 92.3598 | 103.8291 | [6 empty] | CATEGORYB | SINGLE | DELAWARE - NORTHEAST STATION 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 510406 | N.E.S.-7 345.00 | 0 |  | 1 |  |  |  |  | AEPW | BARTLESVILLE SOUTHEAST - NORTH BARTLESVILLE 138KV CKT 1 | Rebuild 8.37 miles of 795 ACSR with 1590 ACSR & reset relays @ BSE | 280 | 287 | 287 | 287 | 8.37 | 24 | 9 |  | 0.00286 | 0.03081 | 0.0097 | New limits will be wavetrap jumpers, breakers & switches | 8400000 | 2007-04-11 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T293312WP | FROM->TO |  | BARTLESVILLE SOUTHEAST - NORTH BARTLESVILLE 138KV CKT 1 | S | AEPW | AEPW | NORTHERN | TS-KAMO | 0 | 510391 | BV-SE--4 138.00 | 510386 | NBVILLE4 138.00 | 0 |  | 1 | 12WP | 215 | 237 |  | 91.7979 | 101.4133 | [6 empty] | CATEGORYB | SINGLE | DELAWARE - NORTHEAST STATION 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 510406 | N.E.S.-7 345.00 | 0 |  | 1 |  |  |  |  | AEPW | BARTLESVILLE SOUTHEAST - NORTH BARTLESVILLE 138KV CKT 1 | Rebuild 8.37 miles of 795 ACSR with 1590 ACSR & reset relays @ BSE | 280 | 287 | 287 | 287 | 8.37 | 24 | 9 |  | 0.00286 | 0.03081 | 0.0097 | New limits will be wavetrap jumpers, breakers & switches | 8400000 | 2007-04-11 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T1533317SP | FROM->TO |  | BARTLESVILLE SOUTHEAST - NORTH BARTLESVILLE 138KV CKT 1 | S | AEPW | AEPW | NORTHERN | TS-KAMO | 0 | 510391 | BV-SE--4 138.00 | 510386 | NBVILLE4 138.00 | 0 |  | 1 | 17SP | 202 | 235 |  | 89.8134 | 100.3615 | [6 empty] | CATEGORYB | SINGLE | DELAWARE - NORTHEAST STATION 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 510406 | N.E.S.-7 345.00 | 0 |  | 1 |  |  |  |  | AEPW | BARTLESVILLE SOUTHEAST - NORTH BARTLESVILLE 138KV CKT 1 | Rebuild 8.37 miles of 795 ACSR with 1590 ACSR & reset relays @ BSE | 280 | 287 | 287 | 287 | 8.37 | 24 | 9 |  | 0.00286 | 0.03081 | 0.0097 | New limits will be wavetrap jumpers, breakers & switches | 8400000 | 2007-04-11 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T762108SH | FROM->TO |  | BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541340 | BELTONS5 161.00 | 541259 | TURNER 5 161.00 | 0 |  | 1 | 08SH | 282 | 282 | 101.4 | 101.7888 | 102.5663 | 540_BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 |  |  |  | Reconductor Belton South-Turner Road 161 kV line with ACSS conductor | MIPU | BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | Reconductor to Bundled Drake | 466 | 558 |  |  | 3.3 | 18 | 18 |  | 0.00049628 | 0.0041779 | 0.004053 |  | 1350000 | 2006-01-01 | [23 empty] | 2008-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1622108SP | FROM->TO |  | BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541340 | BELTONS5 161.00 | 541259 | TURNER 5 161.00 | 0 |  | 1 | 08SP | 282 | 282 | 103.9 | 104.1677 | 104.4905 | 540_BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 |  |  |  | Reconductor Belton South-Turner Road 161 kV line with ACSS conductor | MIPU | BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | Reconductor to Bundled Drake | 466 | 558 |  |  | 3.3 | 18 | 18 |  | 0.00049628 | 0.0041779 | 0.004053 |  | 1350000 | 2006-01-01 | [23 empty] | 2008-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1752109SP | FROM->TO |  | BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541340 | BELTONS5 161.00 | 541259 | TURNER 5 161.00 | 0 |  | 1 | 09SP | 282 | 282 | 106.8 | 107.0737 | 109.7616 | 540_BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 |  |  |  | Reconductor Belton South-Turner Road 161 kV line with ACSS conductor | MIPU | BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | Reconductor to Bundled Drake | 466 | 558 |  |  | 3.3 | 18 | 18 |  | 0.00049628 | 0.0041779 | 0.004053 |  | 1350000 | 2006-01-01 | [23 empty] | 2008-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T2894312SP | FROM->TO |  | BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541340 | BELTONS5 161.00 | 541259 | TURNER 5 161.00 | 0 |  | 1 | 12SP | 282 | 282 | 107.7 | 108.7077 | 110.5249 | 540_BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 |  |  |  | Reconductor Belton South-Turner Road 161 kV line with ACSS conductor | MIPU | BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | Reconductor to Bundled Drake | 466 | 558 |  |  | 3.3 | 18 | 18 |  | 0.00049628 | 0.0041779 | 0.004053 |  | 1350000 | 2006-01-01 | [23 empty] | 2008-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T3174312SP | FROM->TO |  | BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541340 | BELTONS5 161.00 | 541259 | TURNER 5 161.00 | 0 |  | 1 | 12SP | 282 | 282 | 102.6 | 103.3672 | 104.1189 | 540_BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | REDEL - STILWELL 161KV CKT 1 | 0 | 542969 | STILWEL5 161.00 | 543053 | REDEL 5 161.00 | 0 |  | 1 |  |  |  | Reconductor Belton South-Turner Road 161 kV line with ACSS conductor | MIPU | BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | Reconductor to Bundled Drake | 466 | 558 |  |  | 3.3 | 18 | 18 |  | 0.00049628 | 0.0041779 | 0.004053 |  | 1350000 | 2006-01-01 | [23 empty] | 2008-06-01 | 2013-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T3104312SP | FROM->TO |  | BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541340 | BELTONS5 161.00 | 541259 | TURNER 5 161.00 | 0 |  | 1 | 12SP | 282 | 282 |  | 100.1688 | 101.1286 | 540_BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | BELTON SOUTH 161/69KV TRANSFORMER CKT 1 | 0 | 541290 | BELTONS2 69.000 | 541340 | BELTONS5 161.00 | 0 |  | 1 |  |  |  | Reconductor Belton South-Turner Road 161 kV line with ACSS conductor | MIPU | BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | Reconductor to Bundled Drake | 466 | 558 |  |  | 3.3 | 18 | 18 |  | 0.00049628 | 0.0041779 | 0.004053 |  | 1350000 | 2006-01-01 | [23 empty] | 2008-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T4794317SP | FROM->TO |  | BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541340 | BELTONS5 161.00 | 541259 | TURNER 5 161.00 | 0 |  | 1 | 17SP | 282 | 282 | 110.1 | 111.4292 | 110.8298 | 540_BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 |  |  |  | Reconductor Belton South-Turner Road 161 kV line with ACSS conductor | MIPU | BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | Reconductor to Bundled Drake | 466 | 558 |  |  | 3.3 | 18 | 18 |  | 0.00049628 | 0.0041779 | 0.004053 |  | 1350000 | 2006-01-01 | [23 empty] | 2008-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T5084317SP | FROM->TO |  | BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541340 | BELTONS5 161.00 | 541259 | TURNER 5 161.00 | 0 |  | 1 | 17SP | 282 | 282 | 106.4 | 107.2151 | 106.0258 | 540_BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | REDEL - STILWELL 161KV CKT 1 | 0 | 542969 | STILWEL5 161.00 | 543053 | REDEL 5 161.00 | 0 |  | 1 |  |  |  | Reconductor Belton South-Turner Road 161 kV line with ACSS conductor | MIPU | BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | Reconductor to Bundled Drake | 466 | 558 |  |  | 3.3 | 18 | 18 |  | 0.00049628 | 0.0041779 | 0.004053 |  | 1350000 | 2006-01-01 | [23 empty] | 2008-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T5154317SP | FROM->TO |  | BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541340 | BELTONS5 161.00 | 541259 | TURNER 5 161.00 | 0 |  | 1 | 17SP | 282 | 282 | 103.0 | 103.8676 | 102.7304 | 540_BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | MARTIN CITY - REDEL 161KV CKT 1 | 0 | 543002 | MARTCIT5 161.00 | 543053 | REDEL 5 161.00 | 0 |  | 1 |  |  |  | Reconductor Belton South-Turner Road 161 kV line with ACSS conductor | MIPU | BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | Reconductor to Bundled Drake | 466 | 558 |  |  | 3.3 | 18 | 18 |  | 0.00049628 | 0.0041779 | 0.004053 |  | 1350000 | 2006-01-01 | [23 empty] | 2008-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4482317SP | FROM->TO |  | BISMARK JUNCTION SWITCHING STATION - FARMERS CONSUMER CO-OP 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533234 | BISMARK3 115.00 | 533236 | COOP 3 115.00 | 0 |  | 1 | 17SP | 118 | 118 | 130.3 | 129.7945 | 133.9867 | [6 empty] | CATEGORYB | SINGLE | MOCKINGBIRD HILL SWITCHING STATION - SOUTHWEST LAWRENCE 115KV CKT 1 | 0 | 533253 | MOCKBRD3 115.00 | 533271 | SWLWRNC3 115.00 | 0 |  | 1 |  |  |  |  | WERE | BISMARK JUNCTION SWITCHING STATION - FARMERS CONSUMER CO-OP 115KV CKT 1 | Rebuild 2.9 mi 115 kV line Bismark to COOP | [37 empty] | 2015-06-01 | 2015-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4432317SP | FROM->TO |  | BISMARK JUNCTION SWITCHING STATION - FARMERS CONSUMER CO-OP 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533234 | BISMARK3 115.00 | 533236 | COOP 3 115.00 | 0 |  | 1 | 17SP | 118 | 118 | 106.2 | 106.0863 | 107.51 | [6 empty] | CATEGORYB | SINGLE | BALDWIN CREEK - LAWRENCE HILL 115KV CKT 1 | 0 | 533232 | BALDCRK3 115.00 | 533250 | LWRNCHL3 115.00 | 0 |  | 1 |  |  |  |  | WERE | BISMARK JUNCTION SWITCHING STATION - FARMERS CONSUMER CO-OP 115KV CKT 1 | Rebuild 2.9 mi 115 kV line Bismark to COOP | [37 empty] | 2015-06-01 | 2015-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4492317SP | FROM->TO |  | BISMARK JUNCTION SWITCHING STATION - FARMERS CONSUMER CO-OP 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533234 | BISMARK3 115.00 | 533236 | COOP 3 115.00 | 0 |  | 1 | 17SP | 118 | 118 | 100.7 | 100.4878 | 103.4315 | [6 empty] | CATEGORYB | SINGLE | MONTICELLO - PENTAGON 115KV CKT 1 | 0 | 533261 | PENTAGN3 115.00 | 533281 | MNTCLLO3 115.00 | 0 |  | 1 |  |  |  |  | WERE | BISMARK JUNCTION SWITCHING STATION - FARMERS CONSUMER CO-OP 115KV CKT 1 | Rebuild 2.9 mi 115 kV line Bismark to COOP | [37 empty] | 2015-06-01 | 2015-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4472317SP | TO->FROM |  | BISMARK JUNCTION SWITCHING STATION - MIDLAND JUNCTION 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533252 | MIDLAND3 115.00 | 533234 | BISMARK3 115.00 | 0 |  | 1 | 17SP | 118 | 118 | 104.5 | 104.337 | 105.5384 | [6 empty] | CATEGORYB | SINGLE | 6TH STREET - LAWRENCE HILL 115KV CKT 1 | 0 | 533250 | LWRNCHL3 115.00 | 533264 | 6TH ST 3 115.00 | 0 |  | 1 |  |  |  |  | WERE | BISMARK JUNCTION SWITCHING STATION - MIDLAND JUNCTION 115KV CKT 1 | Rebuild 5.2 miles Bismark to Midland 115 kV line | [37 empty] | 2015-06-01 | 2015-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T6862308SP | TO->FROM |  | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541235 | DUNCAN 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 | 08SP | 250 | 275 | 100.8 | 100.7207 | 100.8973 | 540_BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | PLEASANT HILL () 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 541200 | PHILL 7 345.00 | 541225 | PHILL 5 161.00 | 541361 | PHILL T 13.800 | 1 |  |  |  | Upgrade to Bundled Drake Conductor | MIPU | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | Upgrade to conductor Bundled Drake | 446 | 558 |  |  |  | 18 | 18 |  | 0.00061 | 0.00534 | 0.00479 | [26 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T10062209SP | TO->FROM |  | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541235 | DUNCAN 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 | 09SP | 250 | 275 |  | 90.7558 | 106.3317 | 540_BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | PLEASANT HILL () 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 541200 | PHILL 7 345.00 | 541225 | PHILL 5 161.00 | 541361 | PHILL T 13.800 | 1 |  |  |  | Upgrade to Bundled Drake Conductor | MIPU | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | Upgrade to conductor Bundled Drake | 446 | 558 |  |  |  | 18 | 18 |  | 0.00061 | 0.00534 | 0.00479 | [26 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T9454312SP | TO->FROM |  | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541235 | DUNCAN 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 | 12SP | 250 | 275 | 114.2 | 116.9709 | 117.3139 | 540_BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | PLEASANT HILL () 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 541200 | PHILL 7 345.00 | 541225 | PHILL 5 161.00 | 541361 | PHILL T 13.800 | 1 |  |  |  | Upgrade to Bundled Drake Conductor | MIPU | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | Upgrade to conductor Bundled Drake | 446 | 558 |  |  |  | 18 | 18 |  | 0.00061 | 0.00534 | 0.00479 | [26 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T2944312SP | TO->FROM |  | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541235 | DUNCAN 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 | 12SP | 250 | 275 | 103.8 | 105.328 | 105.4531 | 540_BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | ORRICK - SIBLEY 161KV CKT 1 | 0 | 541202 | SIBLEY 5 161.00 | 541244 | ORRICK 5 161.00 | 0 |  | 1 |  |  |  | Upgrade to Bundled Drake Conductor | MIPU | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | Upgrade to conductor Bundled Drake | 446 | 558 |  |  |  | 18 | 18 |  | 0.00061 | 0.00534 | 0.00479 | [26 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T3034312SP | TO->FROM |  | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541235 | DUNCAN 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 | 12SP | 250 | 275 | 102.2 | 103.5894 | 103.875 | 540_BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | ORRICK - RICHMOND 161KV CKT 1 | 0 | 541236 | RICHMND5 161.00 | 541244 | ORRICK 5 161.00 | 0 |  | 1 |  |  |  | Upgrade to Bundled Drake Conductor | MIPU | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | Upgrade to conductor Bundled Drake | 446 | 558 |  |  |  | 18 | 18 |  | 0.00061 | 0.00534 | 0.00479 | [26 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81T4334212WP | TO->FROM |  | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541235 | DUNCAN 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 | 12WP | 250 | 275 | 102.6 | 102.518 | 102.7773 | 540_BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | PLEASANT HILL () 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 541200 | PHILL 7 345.00 | 541225 | PHILL 5 161.00 | 541361 | PHILL T 13.800 | 1 |  |  |  | Upgrade to Bundled Drake Conductor | MIPU | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | Upgrade to conductor Bundled Drake | 446 | 558 |  |  |  | 18 | 18 |  | 0.00061 | 0.00534 | 0.00479 | [26 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T17212317SP | TO->FROM |  | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541235 | DUNCAN 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 | 17SP | 250 | 275 |  | 88.4333 | 121.8559 | 540_BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | PLEASANT HILL () 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 541200 | PHILL 7 345.00 | 541225 | PHILL 5 161.00 | 541361 | PHILL T 13.800 | 1 |  |  |  | Upgrade to Bundled Drake Conductor | MIPU | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | Upgrade to conductor Bundled Drake | 446 | 558 |  |  |  | 18 | 18 |  | 0.00061 | 0.00534 | 0.00479 | [26 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T5562317SP | TO->FROM |  | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541235 | DUNCAN 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 | 17SP | 250 | 275 |  | 77.6316 | 106.9382 | 540_BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | GRANDVIEW EAST - MARTIN CITY 161KV CKT 1 | 0 | 541210 | MARTCTY5 161.00 | 541223 | GRDVWE 5 161.00 | 0 |  | 1 |  |  |  | Upgrade to Bundled Drake Conductor | MIPU | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | Upgrade to conductor Bundled Drake | 446 | 558 |  |  |  | 18 | 18 |  | 0.00061 | 0.00534 | 0.00479 | [26 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T5462317SP | TO->FROM |  | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541235 | DUNCAN 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 | 17SP | 250 | 275 |  | 84.9701 | 105.8187 | 540_BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | ORRICK - SIBLEY 161KV CKT 1 | 0 | 541202 | SIBLEY 5 161.00 | 541244 | ORRICK 5 161.00 | 0 |  | 1 |  |  |  | Upgrade to Bundled Drake Conductor | MIPU | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | Upgrade to conductor Bundled Drake | 446 | 558 |  |  |  | 18 | 18 |  | 0.00061 | 0.00534 | 0.00479 | [26 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1182208SH | TO->FROM |  | BPU - CITY OF MCPHERSON JOHNS-MANVILLE - EAST MCPHERSON SWITCHING STATION 115KV CKT 1 | REL | WERE | WERE | WEST | WEST | 0 | 533417 | EMCPHER3 115.00 | 533426 | MANVILE3 115.00 | 0 |  | 1 | 08SH | 84 | 84 | 103.7 | 103.227 | 105.4919 | [6 empty] | CATEGORYB | SINGLE | EAST MCPHERSON SWITCHING STATION - REFINRY3 115.00 115KV CKT 1 | 0 | 533417 | EMCPHER3 115.00 | 533427 | REFINRY3 115.00 | 0 |  | 1 |  |  |  |  | WERE | BPU - CITY OF MCPHERSON JOHNS-MANVILLE - EAST MCPHERSON SWITCHING STATION 115KV CKT 1 | Rebuild Line | 248 | 248 |  |  | 5.7 | 24 | 24 |  | 0.00392 | 0.03057 | 0.00456 | Line owned by City of McPherson Board of Public Utilities | [25 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1182208SH | TO->FROM |  | BPU - CITY OF MCPHERSON JOHNS-MANVILLE - EAST MCPHERSON SWITCHING STATION 115KV CKT 1 | REL | WERE | WERE | WEST | WEST | 0 | 533417 | EMCPHER3 115.00 | 533426 | MANVILE3 115.00 | 0 |  | 1 | 08SH | 84 | 84 | 103.7 | 103.227 | 105.4919 | [6 empty] | CATEGORYB | SINGLE | EAST MCPHERSON SWITCHING STATION - REFINRY3 115.00 115KV CKT 1 | 0 | 533417 | EMCPHER3 115.00 | 533427 | REFINRY3 115.00 | 0 |  | 1 |  |  |  |  | WERE | BPU - CITY OF MCPHERSON JOHNS-MANVILLE - EAST MCPHERSON SWITCHING STATION 115KV CKT 1 | Rebuild Line | 248 | 248 |  |  | 5.7 | 24 | 24 |  | 0.00392 | 0.03057 | 0.00456 | Line owned by City of McPherson Board of Public Utilities | [25 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T5604117SP | FROM->TO |  | BROOKLINE - JUNCTION 161KV CKT 1 | S | SPRM | SPRM | SPRM | SPRM | 0 | 549969 | BRKLNE 5 161.00 | 549955 | JUNCTN 5 161.00 | 0 |  | 1 | 17SP | 340 | 358 |  | 67.8067 | 100.7305 | [6 empty] | CATEGORYB | SINGLE | BATTLEFIELD - MAIN 161KV CKT 1 | 0 | 549958 | MAIN 5 161.00 | 549959 | BATFLD 5 161.00 | 0 |  | 1 |  |  |  |  | SPRM | BROOKLINE - JUNCTION 161KV CKT 1 | Brookline: Replace 1,200 amp switches with 2,000 amp units and replace metering CTs. Junction: Replace 1,200 amp switches with 2,000 amp units. |  |  |  |  | 0 | 12 | 1 | N |  |  |  | Given small overload and low voltage mitigation requirements in 2008 STEP, cap bank application should suffice. 25 MVAR capacitor bank already installed at Norton 69kV bus 549928. Model this bank with idev file provided to represent it energized. Line rat | 120000 | 2008-01-01 | [23 empty] | 2013-06-01 | 2013-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T5604117SP | FROM->TO |  | BROOKLINE - JUNCTION 161KV CKT 1 | S | SPRM | SPRM | SPRM | SPRM | 0 | 549969 | BRKLNE 5 161.00 | 549955 | JUNCTN 5 161.00 | 0 |  | 1 | 17SP | 340 | 358 |  | 67.8067 | 100.7305 | [6 empty] | CATEGORYB | SINGLE | BATTLEFIELD - MAIN 161KV CKT 1 | 0 | 549958 | MAIN 5 161.00 | 549959 | BATFLD 5 161.00 | 0 |  | 1 |  |  |  |  | SPRM | BROOKLINE - JUNCTION 161KV CKT 1 | Brookline: Replace 1,200 amp switches with 2,000 amp units and replace metering CTs. Junction: Replace 1,200 amp switches with 2,000 amp units. |  |  |  |  | 0 | 12 | 1 | N |  |  |  | Given small overload and low voltage mitigation requirements in 2008 STEP, cap bank application should suffice. 25 MVAR capacitor bank already installed at Norton 69kV bus 549928. Model this bank with idev file provided to represent it energized. Line rat | 120000 | 2008-01-01 | [23 empty] | 2013-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T7132209SP | TO->FROM |  | BULL SHOALS - BULL SHOALS 161KV CKT 1 | EXP | SWPA | ENTR | EMINTH | EES-ARK | 0 | 505460 | BULL SH5 161.00 | 99802 | 5BULLSH* 161.00 | 0 |  | 1 | 09SP | 167 | 167 | 104.8 | 103.5344 | 110.7274 | [6 empty] | CATEGORYB | SINGLE | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | 0 | 99843 | 5EVRTON 161.00 | 99860 | 5ST_JOE 161.00 | 0 |  | 1 | ASSIGN |  |  | Replace bus at Bull Shoals. | SWPA | BULL SHOALS - BULL SHOALS 161KV CKT 1 | Replace buswork in Bull Shoals switchyard. | 335 | 335 |  |  |  | 18 | 18 | [5 empty] | 1400000 | 2006-07-21 | [23 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T6992209SP | TO->FROM |  | BULL SHOALS - BULL SHOALS 161KV CKT 1 | EXP | SWPA | ENTR | EMINTH | EES-ARK | 0 | 505460 | BULL SH5 161.00 | 99802 | 5BULLSH* 161.00 | 0 |  | 1 | 09SP | 167 | 167 | 103.0 | 101.7261 | 108.9214 | [6 empty] | CATEGORYB | SINGLE | EVERTON - HARRISON-EAST 161KV CKT 1 | 0 | 99811 | 5HARR-E 161.00 | 99843 | 5EVRTON 161.00 | 0 |  | 1 | ASSIGN |  |  | Replace bus at Bull Shoals. | SWPA | BULL SHOALS - BULL SHOALS 161KV CKT 1 | Replace buswork in Bull Shoals switchyard. | 335 | 335 |  |  |  | 18 | 18 | [5 empty] | 1400000 | 2006-07-21 | [23 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T3832209WP | TO->FROM |  | BULL SHOALS - BULL SHOALS 161KV CKT 1 | EXP | SWPA | ENTR | EMINTH | EES-ARK | 0 | 505460 | BULL SH5 161.00 | 99802 | 5BULLSH* 161.00 | 0 |  | 1 | 09WP | 167 | 167 |  | 94.7129 | 101.4619 | [6 empty] | CATEGORYB | SINGLE | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | 0 | 99843 | 5EVRTON 161.00 | 99860 | 5ST_JOE 161.00 | 0 |  | 1 | ASSIGN |  |  | Replace bus at Bull Shoals. | SWPA | BULL SHOALS - BULL SHOALS 161KV CKT 1 | Replace buswork in Bull Shoals switchyard. | 335 | 335 |  |  |  | 18 | 18 | [5 empty] | 1400000 | 2006-07-21 | [23 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T3582209WP | TO->FROM |  | BULL SHOALS - BULL SHOALS 161KV CKT 1 | EXP | SWPA | ENTR | EMINTH | EES-ARK | 0 | 505460 | BULL SH5 161.00 | 99802 | 5BULLSH* 161.00 | 0 |  | 1 | 09WP | 167 | 167 |  | 93.3447 | 100.0962 | [6 empty] | CATEGORYB | SINGLE | EVERTON - HARRISON-EAST 161KV CKT 1 | 0 | 99811 | 5HARR-E 161.00 | 99843 | 5EVRTON 161.00 | 0 |  | 1 | ASSIGN |  |  | Replace bus at Bull Shoals. | SWPA | BULL SHOALS - BULL SHOALS 161KV CKT 1 | Replace buswork in Bull Shoals switchyard. | 335 | 335 |  |  |  | 18 | 18 | [5 empty] | 1400000 | 2006-07-21 | [23 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T10752212SP | TO->FROM |  | BULL SHOALS - BULL SHOALS 161KV CKT 1 | EXP | SWPA | ENTR | EMINTH | EES-ARK | 0 | 505460 | BULL SH5 161.00 | 99802 | 5BULLSH* 161.00 | 0 |  | 1 | 12SP | 167 | 167 | 119.5 | 117.4034 | 127.0617 | [6 empty] | CATEGORYB | SINGLE | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | 0 | 99843 | 5EVRTON 161.00 | 99860 | 5ST_JOE 161.00 | 0 |  | 1 | ASSIGN |  |  | Replace bus at Bull Shoals. | SWPA | BULL SHOALS - BULL SHOALS 161KV CKT 1 | Replace buswork in Bull Shoals switchyard. | 335 | 335 |  |  |  | 18 | 18 | [5 empty] | 1400000 | 2006-07-21 | [23 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T10552212SP | TO->FROM |  | BULL SHOALS - BULL SHOALS 161KV CKT 1 | EXP | SWPA | ENTR | EMINTH | EES-ARK | 0 | 505460 | BULL SH5 161.00 | 99802 | 5BULLSH* 161.00 | 0 |  | 1 | 12SP | 167 | 167 | 117.4 | 115.3665 | 124.9537 | [6 empty] | CATEGORYB | SINGLE | EVERTON - HARRISON-EAST 161KV CKT 1 | 0 | 99811 | 5HARR-E 161.00 | 99843 | 5EVRTON 161.00 | 0 |  | 1 | ASSIGN |  |  | Replace bus at Bull Shoals. | SWPA | BULL SHOALS - BULL SHOALS 161KV CKT 1 | Replace buswork in Bull Shoals switchyard. | 335 | 335 |  |  |  | 18 | 18 | [5 empty] | 1400000 | 2006-07-21 | [23 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T5312212WP | TO->FROM |  | BULL SHOALS - BULL SHOALS 161KV CKT 1 | EXP | SWPA | ENTR | EMINTH | EES-ARK | 0 | 505460 | BULL SH5 161.00 | 99802 | 5BULLSH* 161.00 | 0 |  | 1 | 12WP | 167 | 167 | 105.0 | 101.3598 | 109.928 | [6 empty] | CATEGORYB | SINGLE | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | 0 | 99843 | 5EVRTON 161.00 | 99860 | 5ST_JOE 161.00 | 0 |  | 1 | ASSIGN |  |  | Replace bus at Bull Shoals. | SWPA | BULL SHOALS - BULL SHOALS 161KV CKT 1 | Replace buswork in Bull Shoals switchyard. | 335 | 335 |  |  |  | 18 | 18 | [5 empty] | 1400000 | 2006-07-21 | [23 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T5132212WP | TO->FROM |  | BULL SHOALS - BULL SHOALS 161KV CKT 1 | EXP | SWPA | ENTR | EMINTH | EES-ARK | 0 | 505460 | BULL SH5 161.00 | 99802 | 5BULLSH* 161.00 | 0 |  | 1 | 12WP | 167 | 167 | 103.5 | 99.8256 | 108.3894 | [6 empty] | CATEGORYB | SINGLE | EVERTON - HARRISON-EAST 161KV CKT 1 | 0 | 99811 | 5HARR-E 161.00 | 99843 | 5EVRTON 161.00 | 0 |  | 1 | ASSIGN |  |  | Replace bus at Bull Shoals. | SWPA | BULL SHOALS - BULL SHOALS 161KV CKT 1 | Replace buswork in Bull Shoals switchyard. | 335 | 335 |  |  |  | 18 | 18 | [5 empty] | 1400000 | 2006-07-21 | [23 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T16442417SP | TO->FROM |  | BULL SHOALS - BULL SHOALS 161KV CKT 1 | EXP | SWPA | ENTR | EMINTH | EES-ARK | 0 | 505460 | BULL SH5 161.00 | 99802 | 5BULLSH* 161.00 | 0 |  | 1 | 17SP | 167 | 167 | 124.1 | 119.8628 | 130.1102 | [6 empty] | CATEGORYB | SINGLE | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | 0 | 99843 | 5EVRTON 161.00 | 99860 | 5ST_JOE 161.00 | 0 |  | 1 | ASSIGN |  |  | Replace bus at Bull Shoals. | SWPA | BULL SHOALS - BULL SHOALS 161KV CKT 1 | Replace buswork in Bull Shoals switchyard. | 335 | 335 |  |  |  | 18 | 18 | [5 empty] | 1400000 | 2006-07-21 | [23 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T16212417SP | TO->FROM |  | BULL SHOALS - BULL SHOALS 161KV CKT 1 | EXP | SWPA | ENTR | EMINTH | EES-ARK | 0 | 505460 | BULL SH5 161.00 | 99802 | 5BULLSH* 161.00 | 0 |  | 1 | 17SP | 167 | 167 | 121.7 | 117.5404 | 127.6727 | [6 empty] | CATEGORYB | SINGLE | EVERTON - HARRISON-EAST 161KV CKT 1 | 0 | 99811 | 5HARR-E 161.00 | 99843 | 5EVRTON 161.00 | 0 |  | 1 | ASSIGN |  |  | Replace bus at Bull Shoals. | SWPA | BULL SHOALS - BULL SHOALS 161KV CKT 1 | Replace buswork in Bull Shoals switchyard. | 335 | 335 |  |  |  | 18 | 18 | [5 empty] | 1400000 | 2006-07-21 | [23 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T1052408SH | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 08SH | 32 | 32 |  | 25.2998 | 101.9869 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1872208SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 08SP | 32 | 32 |  | 29.7355 | 122.0877 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1862208SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 08SP | 32 | 32 |  | 26.3121 | 118.4294 | [6 empty] | CATEGORYB | SINGLE | ORCHARD - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533643 | ORCHARD2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T1652308SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 08SP | 32 | 32 |  | 12.5859 | 111.7993 | [6 empty] | CATEGORYB | SINGLE | ATHENS SWITCHING STATION - OWL CREEK 69KV CKT 1 | 0 | 533623 | ATHENS 2 69.000 | 533642 | OWL CRK2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T1582408SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 08SP | 58 | 58 |  | 65.4461 | 103.802 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T1612408SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 08SP | 58 | 58 |  | 63.6438 | 101.879 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1492108SP | TO->FROM |  | LEHIGH TAP - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 08SP | 32 | 32 |  | 9.733 | 120.9169 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T1883309SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 09SP | 32 | 32 |  | 29.8705 | 124.2703 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T1873309SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 09SP | 32 | 32 |  | 26.4167 | 120.5106 | [6 empty] | CATEGORYB | SINGLE | ORCHARD - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533643 | ORCHARD2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T1833309SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 09SP | 32 | 32 |  | 12.6944 | 113.9161 | [6 empty] | CATEGORYB | SINGLE | ATHENS SWITCHING STATION - OWL CREEK 69KV CKT 1 | 0 | 533623 | ATHENS 2 69.000 | 533642 | OWL CRK2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T1794409SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 09SP | 58 | 58 |  | 65.5805 | 104.7422 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T1824409SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 09SP | 58 | 58 |  | 63.7171 | 102.7839 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T6324109SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 09SP | 58 | 58 |  | 72.8628 | 100.1831 | [6 empty] | CATEGORYB | SINGLE | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81T1751409SP | TO->FROM |  | LEHIGH TAP - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 09SP | 32 | 32 |  | 8.7892 | 124.0056 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2451112SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12SP | 32 | 32 |  | -999 | 185.4455 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T8991112SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12SP | 32 | 32 |  | -999 | 184.8256 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T2942112SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12SP | 32 | 32 |  | 31.8691 | 130.8571 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2461112SP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 157.4692 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T9001112SP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 156.7557 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2471112SP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 12SP | 108 | 108 |  | -999 | 170.7109 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T9011112SP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 12SP | 108 | 108 |  | -999 | 170.0226 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2792412SP | TO->FROM |  | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 56.0845 | 117.3039 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2912412SP | TO->FROM |  | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 55.5503 | 112.3373 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1582212SP | TO->FROM |  | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 72.3233 | 103.7043 | [6 empty] | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2782412SP | FROM->TO |  | ALTOONA - TIOGA 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 41.4013 | 157.0806 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T2972112SP | FROM->TO |  | ALTOONA - TIOGA 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 40.3416 | 153.9666 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T2772112SP | FROM->TO |  | ALTOONA - TIOGA 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 35.1642 | 128.815 | [6 empty] | CATEGORYB | SINGLE | ALLEN - ZILA JUNCTION 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | NCONV |  |  | FNSL-Blown up | FDNS-Blown up | 2 | 3 | 2008-12-01 | 2007AG1AFS84L32312SP |  |  | ALTOONA - TIOGA 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 25.1844 | 72.1214 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2812412SP | TO->FROM | Bidirectional | ARCO TAP - ENA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533634 | ENA 2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | 51.9299 | 110.5372 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2431112SP | FROM->TO | Bidirectional | ARCO TAP - ENA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533620 | ARCOTAP2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 108.209 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T8971112SP | FROM->TO | Bidirectional | ARCO TAP - ENA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533620 | ARCOTAP2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 107.7968 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2441112SP | TO->FROM | Bidirectional | ARCO TAP - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533641 | MONARCH2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 111.7972 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T8981112SP | TO->FROM | Bidirectional | ARCO TAP - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533641 | MONARCH2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 111.3621 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2822412SP | FROM->TO | Bidirectional | ARCO TAP - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533620 | ARCOTAP2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | 49.4684 | 107.2233 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2662412SP | FROM->TO |  | ATHENS SWITCHING STATION - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533623 | ATHENS 2 69.000 | 533642 | OWL CRK2 69.000 | 0 |  | 1 | 12SP | 41 | 41 |  | 10.1577 | 122.0473 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2832412SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12SP | 58 | 58 |  | 67.3281 | 140.9509 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T3022112SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12SP | 58 | 58 |  | 65.3825 | 136.6898 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2481112SP | FROM->TO | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533634 | ENA 2 69.000 | 533646 | TIOGA 2 69.000 | 0 |  | 1 | 12SP | 58 | 58 |  | -999 | 130.2259 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2672412SP | TO->FROM |  | LEHIGH TAP - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12SP | 32 | 32 |  | 9.2569 | 152.3867 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2491112SP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 12SP | 100 | 100 |  | -999 | 193.7517 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T9031112SP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 12SP | 100 | 100 |  | -999 | 192.9783 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2501112SP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 12SP | 108 | 108 |  | -999 | 178.3467 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T9041112SP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 12SP | 108 | 108 |  | -999 | 177.6278 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T572112WP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12WP | 32 | 32 |  | 24.6721 | 179.9951 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T3802112WP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12WP | 32 | 32 |  | 24.8481 | 179.8879 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T574312WP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12WP | 32 | 32 |  | 22.9815 | 100.7665 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T582112WP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 39.9857 | 150.9578 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T3812112WP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 40.0893 | 150.8733 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T553312WP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 12WP | 108 | 108 |  | 36.4684 | 159.2099 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T3843312WP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 12WP | 108 | 108 |  | 36.5782 | 159.1568 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T464112WP | FROM->TO | Bidirectional | ARCO TAP - ENA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533620 | ARCOTAP2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 9.7864 | 101.0901 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T3394112WP | FROM->TO | Bidirectional | ARCO TAP - ENA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533620 | ARCOTAP2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 10.0489 | 100.9961 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T474112WP | TO->FROM | Bidirectional | ARCO TAP - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533641 | MONARCH2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 11.0682 | 103.599 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T3404112WP | TO->FROM | Bidirectional | ARCO TAP - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533641 | MONARCH2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 11.2882 | 103.5055 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T514112WP | FROM->TO | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533634 | ENA 2 69.000 | 533646 | TIOGA 2 69.000 | 0 |  | 1 | 12WP | 58 | 58 |  | 10.7435 | 122.8447 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T3444112WP | FROM->TO | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533634 | ENA 2 69.000 | 533646 | TIOGA 2 69.000 | 0 |  | 1 | 12WP | 58 | 58 |  | 11.1297 | 122.7501 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81T964212WP | TO->FROM |  | LEHIGH TAP - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12WP | 32 | 32 |  | 7.335 | 100.4311 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T593312WP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 12WP | 100 | 100 |  | 44.6309 | 179.6932 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T3883312WP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 12WP | 100 | 100 |  | 44.776 | 179.5805 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T613312WP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 12WP | 108 | 108 |  | 40.4185 | 165.4322 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T3024312WP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 12WP | 108 | 108 |  | 40.5965 | 165.359 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4092317SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 17SP | 32 | 32 |  | 14.5581 | 132.3017 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16612317SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 17SP | 32 | 32 |  | 14.4858 | 131.4416 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4832317SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 17SP | 32 | 32 |  | 35.6597 | 126.9833 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4102317SP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 17SP | 72 | 72 |  | 23.268 | 100.8105 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16622317SP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 17SP | 72 | 72 |  | 23.1386 | 100.3044 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4112317SP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 17SP | 108 | 108 |  | 28.8307 | 116.5141 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16632317SP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 17SP | 108 | 108 |  | 28.7177 | 115.9243 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T6122417SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 17SP | 58 | 58 |  | 70.7819 | 101.4296 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T4742117SP | TO->FROM |  | LEHIGH TAP - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 17SP | 32 | 32 |  | 11.392 | 117.9501 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4122317SP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 17SP | 100 | 100 |  | 38.8083 | 133.7621 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16642317SP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 17SP | 100 | 100 |  | 38.688 | 133.0647 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4132317SP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 17SP | 108 | 108 |  | 34.6116 | 122.4871 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16652317SP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 17SP | 108 | 108 |  | 34.4969 | 121.8479 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - COFFEY COUNTY NO. 3 WESTPHALIA 69KV CKT 1 | Rebuild 7.2 miles (138kV/69kV Operation) | [8 empty] | 0.015136 | 0.10405 | 0.0021331 | 450k per mile | 3240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T1052408SH | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 08SH | 32 | 32 |  | 25.2998 | 101.9869 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1872208SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 08SP | 32 | 32 |  | 29.7355 | 122.0877 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1862208SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 08SP | 32 | 32 |  | 26.3121 | 118.4294 | [6 empty] | CATEGORYB | SINGLE | ORCHARD - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533643 | ORCHARD2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T1652308SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 08SP | 32 | 32 |  | 12.5859 | 111.7993 | [6 empty] | CATEGORYB | SINGLE | ATHENS SWITCHING STATION - OWL CREEK 69KV CKT 1 | 0 | 533623 | ATHENS 2 69.000 | 533642 | OWL CRK2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T1582408SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 08SP | 58 | 58 |  | 65.4461 | 103.802 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T1612408SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 08SP | 58 | 58 |  | 63.6438 | 101.879 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1492108SP | TO->FROM |  | LEHIGH TAP - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 08SP | 32 | 32 |  | 9.733 | 120.9169 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T1883309SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 09SP | 32 | 32 |  | 29.8705 | 124.2703 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T1873309SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 09SP | 32 | 32 |  | 26.4167 | 120.5106 | [6 empty] | CATEGORYB | SINGLE | ORCHARD - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533643 | ORCHARD2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T1833309SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 09SP | 32 | 32 |  | 12.6944 | 113.9161 | [6 empty] | CATEGORYB | SINGLE | ATHENS SWITCHING STATION - OWL CREEK 69KV CKT 1 | 0 | 533623 | ATHENS 2 69.000 | 533642 | OWL CRK2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T1794409SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 09SP | 58 | 58 |  | 65.5805 | 104.7422 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T1824409SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 09SP | 58 | 58 |  | 63.7171 | 102.7839 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T6324109SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 09SP | 58 | 58 |  | 72.8628 | 100.1831 | [6 empty] | CATEGORYB | SINGLE | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81T1751409SP | TO->FROM |  | LEHIGH TAP - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 09SP | 32 | 32 |  | 8.7892 | 124.0056 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2451112SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12SP | 32 | 32 |  | -999 | 185.4455 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T8991112SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12SP | 32 | 32 |  | -999 | 184.8256 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T2942112SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12SP | 32 | 32 |  | 31.8691 | 130.8571 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2461112SP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 157.4692 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T9001112SP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 156.7557 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2471112SP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 12SP | 108 | 108 |  | -999 | 170.7109 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T9011112SP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 12SP | 108 | 108 |  | -999 | 170.0226 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2792412SP | TO->FROM |  | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 56.0845 | 117.3039 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2912412SP | TO->FROM |  | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 55.5503 | 112.3373 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1582212SP | TO->FROM |  | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 72.3233 | 103.7043 | [6 empty] | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2782412SP | FROM->TO |  | ALTOONA - TIOGA 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 41.4013 | 157.0806 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T2972112SP | FROM->TO |  | ALTOONA - TIOGA 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 40.3416 | 153.9666 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T2772112SP | FROM->TO |  | ALTOONA - TIOGA 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 35.1642 | 128.815 | [6 empty] | CATEGORYB | SINGLE | ALLEN - ZILA JUNCTION 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | NCONV |  |  | FNSL-Blown up | FDNS-Blown up | 2 | 3 | 2008-12-01 | 2007AG1AFS84L32312SP |  |  | ALTOONA - TIOGA 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 25.1844 | 72.1214 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2812412SP | TO->FROM | Bidirectional | ARCO TAP - ENA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533634 | ENA 2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | 51.9299 | 110.5372 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2431112SP | FROM->TO | Bidirectional | ARCO TAP - ENA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533620 | ARCOTAP2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 108.209 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T8971112SP | FROM->TO | Bidirectional | ARCO TAP - ENA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533620 | ARCOTAP2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 107.7968 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2441112SP | TO->FROM | Bidirectional | ARCO TAP - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533641 | MONARCH2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 111.7972 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T8981112SP | TO->FROM | Bidirectional | ARCO TAP - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533641 | MONARCH2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 111.3621 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2822412SP | FROM->TO | Bidirectional | ARCO TAP - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533620 | ARCOTAP2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | 49.4684 | 107.2233 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2662412SP | FROM->TO |  | ATHENS SWITCHING STATION - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533623 | ATHENS 2 69.000 | 533642 | OWL CRK2 69.000 | 0 |  | 1 | 12SP | 41 | 41 |  | 10.1577 | 122.0473 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2832412SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12SP | 58 | 58 |  | 67.3281 | 140.9509 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T3022112SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12SP | 58 | 58 |  | 65.3825 | 136.6898 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2481112SP | FROM->TO | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533634 | ENA 2 69.000 | 533646 | TIOGA 2 69.000 | 0 |  | 1 | 12SP | 58 | 58 |  | -999 | 130.2259 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2672412SP | TO->FROM |  | LEHIGH TAP - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12SP | 32 | 32 |  | 9.2569 | 152.3867 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2491112SP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 12SP | 100 | 100 |  | -999 | 193.7517 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T9031112SP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 12SP | 100 | 100 |  | -999 | 192.9783 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2501112SP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 12SP | 108 | 108 |  | -999 | 178.3467 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T9041112SP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 12SP | 108 | 108 |  | -999 | 177.6278 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T572112WP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12WP | 32 | 32 |  | 24.6721 | 179.9951 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T3802112WP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12WP | 32 | 32 |  | 24.8481 | 179.8879 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T574312WP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12WP | 32 | 32 |  | 22.9815 | 100.7665 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T582112WP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 39.9857 | 150.9578 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T3812112WP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 40.0893 | 150.8733 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T553312WP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 12WP | 108 | 108 |  | 36.4684 | 159.2099 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T3843312WP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 12WP | 108 | 108 |  | 36.5782 | 159.1568 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T464112WP | FROM->TO | Bidirectional | ARCO TAP - ENA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533620 | ARCOTAP2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 9.7864 | 101.0901 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T3394112WP | FROM->TO | Bidirectional | ARCO TAP - ENA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533620 | ARCOTAP2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 10.0489 | 100.9961 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T474112WP | TO->FROM | Bidirectional | ARCO TAP - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533641 | MONARCH2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 11.0682 | 103.599 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T3404112WP | TO->FROM | Bidirectional | ARCO TAP - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533641 | MONARCH2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 11.2882 | 103.5055 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T514112WP | FROM->TO | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533634 | ENA 2 69.000 | 533646 | TIOGA 2 69.000 | 0 |  | 1 | 12WP | 58 | 58 |  | 10.7435 | 122.8447 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T3444112WP | FROM->TO | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533634 | ENA 2 69.000 | 533646 | TIOGA 2 69.000 | 0 |  | 1 | 12WP | 58 | 58 |  | 11.1297 | 122.7501 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81T964212WP | TO->FROM |  | LEHIGH TAP - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12WP | 32 | 32 |  | 7.335 | 100.4311 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T593312WP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 12WP | 100 | 100 |  | 44.6309 | 179.6932 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T3883312WP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 12WP | 100 | 100 |  | 44.776 | 179.5805 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T613312WP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 12WP | 108 | 108 |  | 40.4185 | 165.4322 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T3024312WP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 12WP | 108 | 108 |  | 40.5965 | 165.359 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4092317SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 17SP | 32 | 32 |  | 14.5581 | 132.3017 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16612317SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 17SP | 32 | 32 |  | 14.4858 | 131.4416 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4832317SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 17SP | 32 | 32 |  | 35.6597 | 126.9833 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4102317SP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 17SP | 72 | 72 |  | 23.268 | 100.8105 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16622317SP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 17SP | 72 | 72 |  | 23.1386 | 100.3044 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4112317SP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 17SP | 108 | 108 |  | 28.8307 | 116.5141 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16632317SP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 17SP | 108 | 108 |  | 28.7177 | 115.9243 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T6122417SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 17SP | 58 | 58 |  | 70.7819 | 101.4296 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T4742117SP | TO->FROM |  | LEHIGH TAP - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 17SP | 32 | 32 |  | 11.392 | 117.9501 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4122317SP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 17SP | 100 | 100 |  | 38.8083 | 133.7621 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16642317SP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 17SP | 100 | 100 |  | 38.688 | 133.0647 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4132317SP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 17SP | 108 | 108 |  | 34.6116 | 122.4871 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16652317SP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 17SP | 108 | 108 |  | 34.4969 | 121.8479 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | Rebuild 4.1 miles (138kV/69kV Operation) | [8 empty] | 0.008619 | 0.059249 | 0.0012147 | 450k per mile | 1845000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T2952112SP | TO->FROM |  | CHANUTE TAP - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533666 | CHANTAP2 69.000 | 0 |  | 1 | 12SP | 43 | 43 |  | 8.6818 | 161.896 | [6 empty] | CATEGORYB | SINGLE | ASH GROVE JCT2 - TIOGA 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533660 | ASHGRJ22 69.000 | 0 |  | 1 |  |  |  |  | WERE | CHANUTE TAP - TIOGA 69KV CKT 1 | Replace Jumpers | 72 | 72 | 72 | 72 | 4.82 | [7 empty] | 112500 | 2008-01-01 | [23 empty] | 2010-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T3222312SP | TO->FROM |  | CHANUTE TAP - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533666 | CHANTAP2 69.000 | 0 |  | 1 | 12SP | 43 | 43 |  | 8.6787 | 130.6846 | [6 empty] | CATEGORYB | SINGLE | ASH GROVE JCT2 - CHANUTE GENERATION SUB 69KV CKT 1 | 0 | 533660 | ASHGRJ22 69.000 | 533662 | CGENSUB2 69.000 | 0 |  | 1 |  |  |  |  | WERE | CHANUTE TAP - TIOGA 69KV CKT 1 | Replace Jumpers | 72 | 72 | 72 | 72 | 4.82 | [7 empty] | 112500 | 2008-01-01 | [23 empty] | 2010-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1702212WP | TO->FROM |  | CHANUTE TAP - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533666 | CHANTAP2 69.000 | 0 |  | 1 | 12WP | 43 | 43 |  | 6.3486 | 116.1317 | [6 empty] | CATEGORYB | SINGLE | ASH GROVE JCT2 - TIOGA 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533660 | ASHGRJ22 69.000 | 0 |  | 1 |  |  |  |  | WERE | CHANUTE TAP - TIOGA 69KV CKT 1 | Replace Jumpers | 72 | 72 | 72 | 72 | 4.82 | [7 empty] | 112500 | 2008-01-01 | [23 empty] | 2010-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T371208FA | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08FA | 92 | 92 |  | 98.8597 | 101.7605 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - EAST MANHATTAN 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 539600 | 2003-6AT 230.00 | 0 |  | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T371208FA | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08FA | 92 | 92 |  | 98.8597 | 101.7605 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - EAST MANHATTAN 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 539600 | 2003-6AT 230.00 | 0 |  | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T511208FA | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08FA | 92 | 92 |  | 98.6174 | 101.6608 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - CONCORDIA 230KV CKT 1 | 0 | 539600 | 2003-6AT 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T511208FA | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08FA | 92 | 92 |  | 98.6174 | 101.6608 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - CONCORDIA 230KV CKT 1 | 0 | 539600 | 2003-6AT 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T3101208FA | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08FA | 92 | 92 |  | 98.616 | 101.6588 | [6 empty] | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539657 | CONCORD3 115.00 | 539658 | CONCRD6 230.00 | 539904 | CONCOD-T 13.800 | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T3101208FA | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08FA | 92 | 92 |  | 98.616 | 101.6588 | [6 empty] | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539657 | CONCORD3 115.00 | 539658 | CONCRD6 230.00 | 539904 | CONCOD-T 13.800 | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T441208G | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08G | 92 | 92 | 102.9 | 103.9984 | 108.4956 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - EAST MANHATTAN 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 539600 | 2003-6AT 230.00 | 0 |  | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T441208G | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08G | 92 | 92 | 102.9 | 103.9984 | 108.4956 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - EAST MANHATTAN 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 539600 | 2003-6AT 230.00 | 0 |  | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T571208G | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08G | 92 | 92 | 102.9 | 103.7888 | 108.2477 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - CONCORDIA 230KV CKT 1 | 0 | 539600 | 2003-6AT 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T571208G | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08G | 92 | 92 | 102.9 | 103.7888 | 108.2477 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - CONCORDIA 230KV CKT 1 | 0 | 539600 | 2003-6AT 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T2531208G | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08G | 92 | 92 | 102.7 | 103.7868 | 108.2456 | [6 empty] | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539657 | CONCORD3 115.00 | 539658 | CONCRD6 230.00 | 539904 | CONCOD-T 13.800 | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T2531208G | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08G | 92 | 92 | 102.7 | 103.7868 | 108.2456 | [6 empty] | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539657 | CONCORD3 115.00 | 539658 | CONCRD6 230.00 | 539904 | CONCOD-T 13.800 | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T882208SH | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08SH | 92 | 92 | 118.6 | 120.6515 | 122.044 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - EAST MANHATTAN 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 539600 | 2003-6AT 230.00 | 0 |  | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T882208SH | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08SH | 92 | 92 | 118.6 | 120.6515 | 122.044 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - EAST MANHATTAN 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 539600 | 2003-6AT 230.00 | 0 |  | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1242208SH | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08SH | 92 | 92 | 118.5 | 120.4762 | 121.9174 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - CONCORDIA 230KV CKT 1 | 0 | 539600 | 2003-6AT 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1242208SH | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08SH | 92 | 92 | 118.5 | 120.4762 | 121.9174 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - CONCORDIA 230KV CKT 1 | 0 | 539600 | 2003-6AT 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T6352208SH | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08SH | 92 | 92 | 118.5 | 120.4804 | 121.9161 | [6 empty] | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539657 | CONCORD3 115.00 | 539658 | CONCRD6 230.00 | 539904 | CONCOD-T 13.800 | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T6352208SH | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08SH | 92 | 92 | 118.5 | 120.4804 | 121.9161 | [6 empty] | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539657 | CONCORD3 115.00 | 539658 | CONCRD6 230.00 | 539904 | CONCOD-T 13.800 | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1622208SP | TO->FROM |  | CLIFTON - CONCORDIA 115KV CKT 1 | REL | WEPL | WEPL |  |  | 0 | 539657 | CONCORD3 115.00 | 539656 | CLIFTON3 115.00 | 0 |  | 1 | 08SP | 83.9 | 89.6 |  | 142.9194 | 145.9767 | [6 empty] | CATEGORYB | SINGLE | KELLY - SOUTH SENECA 115KV CKT 1 | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1632208SP | FROM->TO |  | CLIFTON - GREENLEAF 115KV CKT 1 | REL | WEPL | WEPL |  |  | 0 | 539656 | CLIFTON3 115.00 | 539665 | GRNLEAF3 115.00 | 0 |  | 1 | 08SP | 83.9 | 89.6 |  | 131.2311 | 134.2112 | [6 empty] | CATEGORYB | SINGLE | KELLY - SOUTH SENECA 115KV CKT 1 | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1612208SP | FROM->TO |  | GREENLEAF - KNOB HILL 115KV CKT 1 | REL | WEPL | WERE |  | NCENTRAL | 0 | 539665 | GRNLEAF3 115.00 | 533332 | KNOB HL3 115.00 | 0 |  | 1 | 08SP | 92 | 92 |  | 108.2624 | 111.3446 | [6 empty] | CATEGORYB | SINGLE | KELLY - SOUTH SENECA 115KV CKT 1 | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1612208SP | FROM->TO |  | GREENLEAF - KNOB HILL 115KV CKT 1 | REL | WEPL | WERE |  | NCENTRAL | 0 | 539665 | GRNLEAF3 115.00 | 533332 | KNOB HL3 115.00 | 0 |  | 1 | 08SP | 92 | 92 |  | 108.2624 | 111.3446 | [6 empty] | CATEGORYB | SINGLE | KELLY - SOUTH SENECA 115KV CKT 1 | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1612208SP | FROM->TO |  | GREENLEAF - KNOB HILL 115KV CKT 1 | REL | WEPL | WERE |  | NCENTRAL | 0 | 539665 | GRNLEAF3 115.00 | 533332 | KNOB HL3 115.00 | 0 |  | 1 | 08SP | 92 | 92 |  | 108.2624 | 111.3446 | [6 empty] | CATEGORYB | SINGLE | KELLY - SOUTH SENECA 115KV CKT 1 | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T1861208SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08SP | 92 | 92 | 113.6 | 136.649 | 137.6673 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - CONCORDIA 230KV CKT 1 | 0 | 539600 | 2003-6AT 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T1861208SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08SP | 92 | 92 | 113.6 | 136.649 | 137.6673 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - CONCORDIA 230KV CKT 1 | 0 | 539600 | 2003-6AT 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T7271208SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08SP | 92 | 92 | 113.6 | 136.6472 | 137.6658 | [6 empty] | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539657 | CONCORD3 115.00 | 539658 | CONCRD6 230.00 | 539904 | CONCOD-T 13.800 | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T7271208SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08SP | 92 | 92 | 113.6 | 136.6472 | 137.6658 | [6 empty] | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539657 | CONCORD3 115.00 | 539658 | CONCRD6 230.00 | 539904 | CONCOD-T 13.800 | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T1421208SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08SP | 92 | 92 | 113.7 | 136.5674 | 137.5915 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - EAST MANHATTAN 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 539600 | 2003-6AT 230.00 | 0 |  | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T1421208SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08SP | 92 | 92 | 113.7 | 136.5674 | 137.5915 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - EAST MANHATTAN 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 539600 | 2003-6AT 230.00 | 0 |  | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T1691209SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 09SP | 92 | 92 | 105.5 | 105.3498 | 105.3683 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - EAST MANHATTAN 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 539600 | 2003-6AT 230.00 | 0 |  | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T1691209SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 09SP | 92 | 92 | 105.5 | 105.3498 | 105.3683 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - EAST MANHATTAN 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 539600 | 2003-6AT 230.00 | 0 |  | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T1991209SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 09SP | 92 | 92 | 105.5 | 105.2741 | 105.2931 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - CONCORDIA 230KV CKT 1 | 0 | 539600 | 2003-6AT 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T1991209SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 09SP | 92 | 92 | 105.5 | 105.2741 | 105.2931 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - CONCORDIA 230KV CKT 1 | 0 | 539600 | 2003-6AT 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T7491209SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 09SP | 92 | 92 | 105.5 | 105.274 | 105.293 | [6 empty] | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539657 | CONCORD3 115.00 | 539658 | CONCRD6 230.00 | 539904 | CONCOD-T 13.800 | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T7491209SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 09SP | 92 | 92 | 105.5 | 105.274 | 105.293 | [6 empty] | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539657 | CONCORD3 115.00 | 539658 | CONCRD6 230.00 | 539904 | CONCOD-T 13.800 | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T2594312SP | FROM->TO |  | CLIFTON - GREENLEAF 115KV CKT 1 | REL | WEPL | WEPL |  |  | 0 | 539656 | CLIFTON3 115.00 | 539665 | GRNLEAF3 115.00 | 0 |  | 1 | 12SP | 83.9 | 89.6 |  | 95.7267 | 101.0446 | [6 empty] | CATEGORYB | SINGLE | KELLY - SOUTH SENECA 115KV CKT 1 | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81T9524212SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 12SP | 92 | 92 | 104.5 | 103.3871 | 104.6447 | [6 empty] | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539657 | CONCORD3 115.00 | 539658 | CONCRD6 230.00 | 539904 | CONCOD-T 13.800 | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81T9524212SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 12SP | 92 | 92 | 104.5 | 103.3871 | 104.6447 | [6 empty] | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539657 | CONCORD3 115.00 | 539658 | CONCRD6 230.00 | 539904 | CONCOD-T 13.800 | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81T2504212SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 12SP | 92 | 92 | 104.5 | 103.3872 | 104.5844 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - CONCORDIA 230KV CKT 1 | 0 | 539600 | 2003-6AT 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81T2504212SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 12SP | 92 | 92 | 104.5 | 103.3872 | 104.5844 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - CONCORDIA 230KV CKT 1 | 0 | 539600 | 2003-6AT 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81T4584217SP | FROM->TO |  | CLIFTON - GREENLEAF 115KV CKT 1 | REL | WEPL | WEPL |  |  | 0 | 539656 | CLIFTON3 115.00 | 539665 | GRNLEAF3 115.00 | 0 |  | 1 | 17SP | 83.9 | 89.6 |  | 97.6472 | 103.3971 | [6 empty] | CATEGORYB | SINGLE | KELLY - SOUTH SENECA 115KV CKT 1 | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81T5174217SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 106.2 | 104.4324 | 107.7297 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - CONCORDIA 230KV CKT 1 | 0 | 539600 | 2003-6AT 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81T5174217SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 106.2 | 104.4324 | 107.7297 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - CONCORDIA 230KV CKT 1 | 0 | 539600 | 2003-6AT 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81T17454217SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 106.3 | 104.4326 | 107.729 | [6 empty] | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539657 | CONCORD3 115.00 | 539658 | CONCRD6 230.00 | 539904 | CONCOD-T 13.800 | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81T17454217SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 106.3 | 104.4326 | 107.729 | [6 empty] | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539657 | CONCORD3 115.00 | 539658 | CONCRD6 230.00 | 539904 | CONCOD-T 13.800 | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T4763217SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 106.3 | 104.5608 | 102.8161 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - EAST MANHATTAN 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 539600 | 2003-6AT 230.00 | 0 |  | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T4763217SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 106.3 | 104.5608 | 102.8161 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - EAST MANHATTAN 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 539600 | 2003-6AT 230.00 | 0 |  | 1 |  |  |  |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 | 0 | 6 | 1 | No | [29 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 | 0634 - Weaver 138-69kV Xfmr |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81T5601408SH | FROM->TO |  | CHASE - WHITE JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533588 | CHASE 2 69.000 | 533605 | WHITE J2 69.000 | 0 |  | 1 | 08SH | 43 | 43 |  | 85.4039 | 101.1405 | [6 empty] | CATEGORYB | SINGLE | WEAVER (WEAVER2X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532991 | WEAVER 4 138.00 | 533604 | WEAVER 2 69.000 | 533083 | WEAVER 1 13.200 | 1 |  |  |  |  | WERE | CHASE - WHITE JUNCTION 69KV CKT 1 | Tear down / Rebuild 7.3-mile Chase - White Junction 69 kV line. Replace existing 2/0 copper conductor with 795 kcmil ACSR conductor. | 72 | 72 | 72 | 72 | 7.3 | 12 | 12 | No | 0.015368 | 0.10483 | 0.022284 | Rating will be limited by disconnect switches. | 2400000 | 2006-01-01 | [23 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 | 0634 - Weaver 138-69kV Xfmr | FDNS |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81T6211408SP | FROM->TO |  | CHASE - WHITE JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533588 | CHASE 2 69.000 | 533605 | WHITE J2 69.000 | 0 |  | 1 | 08SP | 43 | 43 | 107.8 | 94.0962 | 107.6008 | [6 empty] | CATEGORYB | SINGLE | WEAVER (WEAVER2X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532991 | WEAVER 4 138.00 | 533604 | WEAVER 2 69.000 | 533083 | WEAVER 1 13.200 | 1 |  |  |  |  | WERE | CHASE - WHITE JUNCTION 69KV CKT 1 | Tear down / Rebuild 7.3-mile Chase - White Junction 69 kV line. Replace existing 2/0 copper conductor with 795 kcmil ACSR conductor. | 72 | 72 | 72 | 72 | 7.3 | 12 | 12 | No | 0.015368 | 0.10483 | 0.022284 | Rating will be limited by disconnect switches. | 2400000 | 2006-01-01 | [23 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 | 0634 - Weaver 138-69kV Xfmr | FDNS |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T6684409SP | FROM->TO |  | CHASE - WHITE JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533588 | CHASE 2 69.000 | 533605 | WHITE J2 69.000 | 0 |  | 1 | 09SP | 43 | 43 | 108.9 | 92.6382 | 106.1884 | [6 empty] | CATEGORYB | SINGLE | WEAVER (WEAVER2X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532991 | WEAVER 4 138.00 | 533604 | WEAVER 2 69.000 | 533083 | WEAVER 1 13.200 | 1 |  |  |  |  | WERE | CHASE - WHITE JUNCTION 69KV CKT 1 | Tear down / Rebuild 7.3-mile Chase - White Junction 69 kV line. Replace existing 2/0 copper conductor with 795 kcmil ACSR conductor. | 72 | 72 | 72 | 72 | 7.3 | 12 | 12 | No | 0.015368 | 0.10483 | 0.022284 | Rating will be limited by disconnect switches. | 2400000 | 2006-01-01 | [23 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 | 0634 - Weaver 138-69kV Xfmr | FDNS |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T8804412SP | FROM->TO |  | CHASE - WHITE JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533588 | CHASE 2 69.000 | 533605 | WHITE J2 69.000 | 0 |  | 1 | 12SP | 43 | 43 | 113.0 | 94.4019 | 110.4249 | [6 empty] | CATEGORYB | SINGLE | WEAVER (WEAVER2X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532991 | WEAVER 4 138.00 | 533604 | WEAVER 2 69.000 | 533083 | WEAVER 1 13.200 | 1 |  |  |  |  | WERE | CHASE - WHITE JUNCTION 69KV CKT 1 | Tear down / Rebuild 7.3-mile Chase - White Junction 69 kV line. Replace existing 2/0 copper conductor with 795 kcmil ACSR conductor. | 72 | 72 | 72 | 72 | 7.3 | 12 | 12 | No | 0.015368 | 0.10483 | 0.022284 | Rating will be limited by disconnect switches. | 2400000 | 2006-01-01 | [23 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 | 0634 - Weaver 138-69kV Xfmr | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81T17014217SP | FROM->TO |  | CHASE - WHITE JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533588 | CHASE 2 69.000 | 533605 | WHITE J2 69.000 | 0 |  | 1 | 17SP | 43 | 43 | 116.5 | 93.2831 | 115.3919 | [6 empty] | CATEGORYB | SINGLE | WEAVER (WEAVER2X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532991 | WEAVER 4 138.00 | 533604 | WEAVER 2 69.000 | 533083 | WEAVER 1 13.200 | 1 |  |  |  |  | WERE | CHASE - WHITE JUNCTION 69KV CKT 1 | Tear down / Rebuild 7.3-mile Chase - White Junction 69 kV line. Replace existing 2/0 copper conductor with 795 kcmil ACSR conductor. | 72 | 72 | 72 | 72 | 7.3 | 12 | 12 | No | 0.015368 | 0.10483 | 0.022284 | Rating will be limited by disconnect switches. | 2400000 | 2006-01-01 | [23 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 | NCONV | FNSL-Blown up | FDNS-Blown up | FNSL-Blown up | FDNS-Blown up | 3 | 3 | 2008-12-01 | 2007AG1AFS84L83312SP |  |  | FLETCHER - HOLCOMB 115KV CKT 1 | EXP | SUNC | SUNC | SEPC | WHEATLAN | 0 | 531448 | HOLCOMB3 115.00 | 531420 | FLETCHR3 115.00 | 0 |  | 1 | 12SP | 165 | 198 | 62.88427 | 63.0275 | 63.2224 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | Cimarron Plant Substation Expansion | Integrate SUNC North Cimarron Top into reconfigured WEPL Cimarron Plant Sub | [12 empty] | 2500000 | 2006-06-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FNSL | FDNS-Blown up | 3 | 3 | 2008-12-01 | 2007AG1AFS82T43312SP | TO->FROM |  | CIMARRON RIVER PLANT - NORTH CIMARRON 115KV CKT 1 | EXP | SUNC | WEPL | SEPC |  | 0 | 531455 | NCIMARN3 115.00 | 539654 | CIM-PLT3 115.00 | 0 |  | 1 | 12SP | 120 | 143 | 107.6 | -999 | 107.6186 | [6 empty] | CATEGORYB | SINGLE | CUDAHY - JUDSON LARGE 115KV CKT 1 | 0 | 539659 | CUDAHY 3 115.00 | 539671 | JUD-LRG3 115.00 | 0 |  | 1 |  |  |  |  | MKEC | Cimarron Plant Substation Expansion | Integrate SUNC North Cimarron Top into reconfigured WEPL Cimarron Plant Sub | [12 empty] | 2500000 | 2006-06-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FNSL | FDNS-Blown up | 3 | 3 | 2008-12-01 | 2007AG1AFS82T43312SP | TO->FROM |  | CIMARRON RIVER PLANT - NORTH CIMARRON 115KV CKT 1 | EXP | SUNC | WEPL | SEPC |  | 0 | 531455 | NCIMARN3 115.00 | 539654 | CIM-PLT3 115.00 | 0 |  | 1 | 12SP | 120 | 143 | 107.6 | -999 | 107.6186 | [6 empty] | CATEGORYB | SINGLE | CUDAHY - JUDSON LARGE 115KV CKT 1 | 0 | 539659 | CUDAHY 3 115.00 | 539671 | JUD-LRG3 115.00 | 0 |  | 1 |  |  |  |  | MKEC | Cimarron Plant Substation Expansion | Integrate SUNC North Cimarron Top into reconfigured WEPL Cimarron Plant Sub | [12 empty] | 2500000 | 2006-06-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 | NCONV | FNSL-Blown up | FDNS-Blown up | FNSL-Blown up | FDNS-Iteration limit exceeded | 3 | 2 | 2008-12-01 | 2007AG1AFS84L93212SP |  |  | CIMARRON RIVER PLANT - NORTH CIMARRON 115KV CKT 1 | EXP | SUNC | WEPL | SEPC |  | 0 | 531455 | NCIMARN3 115.00 | 539654 | CIM-PLT3 115.00 | 0 |  | 1 | 12SP | 120 | 143 | 55.6476 | 56.181 | 56.3055 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | Cimarron Plant Substation Expansion | Integrate SUNC North Cimarron Top into reconfigured WEPL Cimarron Plant Sub | [12 empty] | 2500000 | 2006-06-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 | NCONV | FNSL-Singular jacobian or 0.0 voltage | FDNS-Blown up | FNSL-Blown up | FDNS-Blown up | 4 | 2 | 2008-12-01 | 2007AG1AFS84L114212SP |  |  | CUDAHY - JUDSON LARGE 115KV CKT 1 | EXP | WEPL | WEPL |  |  | 0 | 539671 | JUD-LRG3 115.00 | 539659 | CUDAHY 3 115.00 | 0 |  | 1 | 12SP | 120.7 | 129.5 | 57.70921 | 57.1273 | 57.6538 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | Cimarron Plant Substation Expansion | Integrate SUNC North Cimarron Top into reconfigured WEPL Cimarron Plant Sub | [12 empty] | 2500000 | 2006-06-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 | NCONV | FNSL-Blown up | FDNS-Blown up | FNSL-Blown up | FDNS-Blown up | 3 | 2 | 2008-12-01 | 2007AG1AFS84L73212SP |  |  | HOLCOMB - PLYMELL 115KV CKT 1 | EXP | SUNC | SUNC | SEPC | PIONEER | 0 | 531448 | HOLCOMB3 115.00 | 531393 | PLYMELL3 115.00 | 0 |  | 1 | 12SP | 120 | 143 | 100.3204 | 100.6549 | 100.7523 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | Cimarron Plant Substation Expansion | Integrate SUNC North Cimarron Top into reconfigured WEPL Cimarron Plant Sub | [12 empty] | 2500000 | 2006-06-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 | NCONV | FDNS |  | FNSL-Blown up | FDNS-Blown up | 3 | 2 | 2008-12-01 | 2007AG1AFS84L73212SP |  |  | HOLCOMB - PLYMELL 115KV CKT 1 | EXP | SUNC | SUNC | SEPC | PIONEER | 0 | 531448 | HOLCOMB3 115.00 | 531393 | PLYMELL3 115.00 | 0 |  | 1 | 12SP | 120 | 143 | 100.3 | 100.6549 | 100.7523 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | Cimarron Plant Substation Expansion | Integrate SUNC North Cimarron Top into reconfigured WEPL Cimarron Plant Sub | [12 empty] | 2500000 | 2006-06-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 | NCONV | FNSL-Blown up | FDNS-Blown up | FNSL-Blown up | FDNS-Blown up | 3 | 2 | 2008-12-01 | 2007AG1AFS84L63212SP |  |  | PIONEER TAP - PLYMELL 115KV CKT 1 | EXP | SUNC | SUNC | PIONEER | PIONEER | 0 | 531393 | PLYMELL3 115.00 | 531392 | PIONTAP3 115.00 | 0 |  | 1 | 12SP | 120 | 143 | 95.98772 | 96.3223 | 96.4189 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | Cimarron Plant Substation Expansion | Integrate SUNC North Cimarron Top into reconfigured WEPL Cimarron Plant Sub | [12 empty] | 2500000 | 2006-06-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 3 | 2008-12-01 | 2007AG1AFS81T31308SP | FROM->TO |  | LEHIGH TAP - UNITED NO. 9 CONGER 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533638 | LEHIGTP2 69.000 | 533651 | UN9CONG2 69.000 | 0 |  | 1 | 08SP | 32 | 32 |  | 9.7113 | 105.3951 | [6 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | CITY OF IOLA - UNITED NO. 9 CONGER 69KV CKT 1 | Tear down / Rebuild 4-mile 69 kV line; 954 kcmiol ACSR | 72 | 72 | 72 | 72 | 0.91 | 3 | 1 |  | 0.0084508 | 0.058093 | 0.001191 | 72 MVA limit is switches 450k per mile | 1800000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T31109SP | FROM->TO |  | LEHIGH TAP - UNITED NO. 9 CONGER 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533638 | LEHIGTP2 69.000 | 533651 | UN9CONG2 69.000 | 0 |  | 1 | 09SP | 32 | 32 |  | 9.8401 | 107.5866 | [6 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | CITY OF IOLA - UNITED NO. 9 CONGER 69KV CKT 1 | Tear down / Rebuild 4-mile 69 kV line; 954 kcmiol ACSR | 72 | 72 | 72 | 72 | 0.91 | 3 | 1 |  | 0.0084508 | 0.058093 | 0.001191 | 72 MVA limit is switches 450k per mile | 1800000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 4 | 2008-12-01 | 2007AG1AFS81T17563412SP | TO->FROM |  | CITY OF IOLA - UNITED NO. 9 CONGER 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533651 | UN9CONG2 69.000 | 533637 | IOLA 2 69.000 | 0 |  | 1 | 12SP | 32 | 32 |  | 0.26852 | 101.5022 | [6 empty] | CATEGORYB | GENOUT | GEN533637 2-CITY OF IOLA | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | CITY OF IOLA - UNITED NO. 9 CONGER 69KV CKT 1 | Tear down / Rebuild 4-mile 69 kV line; 954 kcmiol ACSR | 72 | 72 | 72 | 72 | 0.91 | 3 | 1 |  | 0.0084508 | 0.058093 | 0.001191 | 72 MVA limit is switches 450k per mile | 1800000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T72412SP | TO->FROM |  | CITY OF IOLA - UNITED NO. 9 CONGER 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533651 | UN9CONG2 69.000 | 533637 | IOLA 2 69.000 | 0 |  | 1 | 12SP | 32 | 32 |  | 0.26881 | 101.216 | [6 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | CITY OF IOLA - UNITED NO. 9 CONGER 69KV CKT 1 | Tear down / Rebuild 4-mile 69 kV line; 954 kcmiol ACSR | 72 | 72 | 72 | 72 | 0.91 | 3 | 1 |  | 0.0084508 | 0.058093 | 0.001191 | 72 MVA limit is switches 450k per mile | 1800000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 1 | 2008-12-01 | 2007AG1AFS81T14013112SP | FROM->TO |  | LEHIGH TAP - UNITED NO. 9 CONGER 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533638 | LEHIGTP2 69.000 | 533651 | UN9CONG2 69.000 | 0 |  | 1 | 12SP | 32 | 32 |  | 10.2292 | 112.0964 | [6 empty] | CATEGORYB | GENOUT | GEN533637 2-CITY OF IOLA | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | CITY OF IOLA - UNITED NO. 9 CONGER 69KV CKT 1 | Tear down / Rebuild 4-mile 69 kV line; 954 kcmiol ACSR | 72 | 72 | 72 | 72 | 0.91 | 3 | 1 |  | 0.0084508 | 0.058093 | 0.001191 | 72 MVA limit is switches 450k per mile | 1800000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T82412SP | FROM->TO |  | LEHIGH TAP - UNITED NO. 9 CONGER 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533638 | LEHIGTP2 69.000 | 533651 | UN9CONG2 69.000 | 0 |  | 1 | 12SP | 32 | 32 |  | 10.2574 | 111.6966 | [6 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | CITY OF IOLA - UNITED NO. 9 CONGER 69KV CKT 1 | Tear down / Rebuild 4-mile 69 kV line; 954 kcmiol ACSR | 72 | 72 | 72 | 72 | 0.91 | 3 | 1 |  | 0.0084508 | 0.058093 | 0.001191 | 72 MVA limit is switches 450k per mile | 1800000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T612112WP | TO->FROM |  | CITY OF IOLA - UNITED NO. 9 CONGER 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533651 | UN9CONG2 69.000 | 533637 | IOLA 2 69.000 | 0 |  | 1 | 12WP | 32 | 32 |  | 0.27354 | 127.7648 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | CITY OF IOLA - UNITED NO. 9 CONGER 69KV CKT 1 | Tear down / Rebuild 4-mile 69 kV line; 954 kcmiol ACSR | 72 | 72 | 72 | 72 | 0.91 | 3 | 1 |  | 0.0084508 | 0.058093 | 0.001191 | 72 MVA limit is switches 450k per mile | 1800000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T3842112WP | TO->FROM |  | CITY OF IOLA - UNITED NO. 9 CONGER 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533651 | UN9CONG2 69.000 | 533637 | IOLA 2 69.000 | 0 |  | 1 | 12WP | 32 | 32 |  | 0.27251 | 127.748 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | CITY OF IOLA - UNITED NO. 9 CONGER 69KV CKT 1 | Tear down / Rebuild 4-mile 69 kV line; 954 kcmiol ACSR | 72 | 72 | 72 | 72 | 0.91 | 3 | 1 |  | 0.0084508 | 0.058093 | 0.001191 | 72 MVA limit is switches 450k per mile | 1800000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T622112WP | FROM->TO |  | LEHIGH TAP - UNITED NO. 9 CONGER 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533638 | LEHIGTP2 69.000 | 533651 | UN9CONG2 69.000 | 0 |  | 1 | 12WP | 32 | 32 |  | 7.3147 | 139.5966 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | CITY OF IOLA - UNITED NO. 9 CONGER 69KV CKT 1 | Tear down / Rebuild 4-mile 69 kV line; 954 kcmiol ACSR | 72 | 72 | 72 | 72 | 0.91 | 3 | 1 |  | 0.0084508 | 0.058093 | 0.001191 | 72 MVA limit is switches 450k per mile | 1800000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T3852112WP | FROM->TO |  | LEHIGH TAP - UNITED NO. 9 CONGER 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533638 | LEHIGTP2 69.000 | 533651 | UN9CONG2 69.000 | 0 |  | 1 | 12WP | 32 | 32 |  | 7.3465 | 139.5575 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | CITY OF IOLA - UNITED NO. 9 CONGER 69KV CKT 1 | Tear down / Rebuild 4-mile 69 kV line; 954 kcmiol ACSR | 72 | 72 | 72 | 72 | 0.91 | 3 | 1 |  | 0.0084508 | 0.058093 | 0.001191 | 72 MVA limit is switches 450k per mile | 1800000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T32562217SP | TO->FROM |  | CITY OF IOLA - UNITED NO. 9 CONGER 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533651 | UN9CONG2 69.000 | 533637 | IOLA 2 69.000 | 0 |  | 1 | 17SP | 32 | 32 |  | 0.26916 | 109.7517 | [6 empty] | CATEGORYB | GENOUT | GEN533637 2-CITY OF IOLA | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | CITY OF IOLA - UNITED NO. 9 CONGER 69KV CKT 1 | Tear down / Rebuild 4-mile 69 kV line; 954 kcmiol ACSR | 72 | 72 | 72 | 72 | 0.91 | 3 | 1 |  | 0.0084508 | 0.058093 | 0.001191 | 72 MVA limit is switches 450k per mile | 1800000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T32572217SP | FROM->TO |  | LEHIGH TAP - UNITED NO. 9 CONGER 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533638 | LEHIGTP2 69.000 | 533651 | UN9CONG2 69.000 | 0 |  | 1 | 17SP | 32 | 32 |  | 11.2847 | 121.4824 | [6 empty] | CATEGORYB | GENOUT | GEN533637 2-CITY OF IOLA | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | CITY OF IOLA - UNITED NO. 9 CONGER 69KV CKT 1 | Tear down / Rebuild 4-mile 69 kV line; 954 kcmiol ACSR | 72 | 72 | 72 | 72 | 0.91 | 3 | 1 |  | 0.0084508 | 0.058093 | 0.001191 | 72 MVA limit is switches 450k per mile | 1800000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T142417SP | FROM->TO |  | LEHIGH TAP - UNITED NO. 9 CONGER 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533638 | LEHIGTP2 69.000 | 533651 | UN9CONG2 69.000 | 0 |  | 1 | 17SP | 32 | 32 |  | 11.2829 | 102.7238 | [6 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | CITY OF IOLA - UNITED NO. 9 CONGER 69KV CKT 1 | Tear down / Rebuild 4-mile 69 kV line; 954 kcmiol ACSR | 72 | 72 | 72 | 72 | 0.91 | 3 | 1 |  | 0.0084508 | 0.058093 | 0.001191 | 72 MVA limit is switches 450k per mile | 1800000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T782308SH | TO->FROM |  | CITY OF WINFIELD - RAINBOW 69KV CKT 1 | S | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533549 | RAINBOW2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 08SH | 43 | 43 |  | 3.9416 | 109.4626 | [6 empty] | CATEGORYB | SINGLE | OAK - STROTHER FIELD (CITY OF WINFIELD) 69KV CKT 1 | 0 | 533547 | OAK 2 69.000 | 533556 | STROTHR2 69.000 | 0 |  | 1 |  |  |  |  | WERE | CITY OF WINFIELD - RAINBOW 69KV CKT 1 | Rebuild 3.99-mile Rainbow-Winfield 69 kV line, 954 ACSR | 72 | 72 | 72 | 72 | 3.99 | 12 | 4 | N | 0.00841 | 0.05727 | 0.00122 | Line switches limit to 72 MVA | 1645279 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T13382212SP | TO->FROM |  | CLARKSVILLE - DARDANELLE 161KV CKT 1 | CP | SWPA | SWPA | EMINTH | EMINTH | 0 | 505508 | DARDANE5 161.00 | 505514 | CLARKSV5 161.00 | 0 |  | 1 | 12SP | 189 | 223 |  | 94.1365 | 104.1069 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 |  | assigned in 2006-ag3-afs-10 |  |  | SWPA | CLARKSVILLE - DARDANELLE 161KV CKT 1 | Reconductor Clarksville-Dardanelle line | 279 | 279 |  |  | 34 | 24 | 6 | [5 empty] | 9000000 | 2008-05-28 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T20342217SP | TO->FROM |  | CLARKSVILLE - DARDANELLE 161KV CKT 1 | CP | SWPA | SWPA | EMINTH | EMINTH | 0 | 505508 | DARDANE5 161.00 | 505514 | CLARKSV5 161.00 | 0 |  | 1 | 17SP | 189 | 223 |  | 99.2606 | 108.5741 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 |  | assigned in 2006-ag3-afs-10 |  |  | SWPA | CLARKSVILLE - DARDANELLE 161KV CKT 1 | Reconductor Clarksville-Dardanelle line | 279 | 279 |  |  | 34 | 24 | 6 | [5 empty] | 9000000 | 2008-05-28 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T371208FA | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08FA | 92 | 92 |  | 98.8597 | 101.7605 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - EAST MANHATTAN 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 539600 | 2003-6AT 230.00 | 0 |  | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T371208FA | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08FA | 92 | 92 |  | 98.8597 | 101.7605 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - EAST MANHATTAN 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 539600 | 2003-6AT 230.00 | 0 |  | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T511208FA | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08FA | 92 | 92 |  | 98.6174 | 101.6608 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - CONCORDIA 230KV CKT 1 | 0 | 539600 | 2003-6AT 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T511208FA | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08FA | 92 | 92 |  | 98.6174 | 101.6608 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - CONCORDIA 230KV CKT 1 | 0 | 539600 | 2003-6AT 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T3101208FA | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08FA | 92 | 92 |  | 98.616 | 101.6588 | [6 empty] | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539657 | CONCORD3 115.00 | 539658 | CONCRD6 230.00 | 539904 | CONCOD-T 13.800 | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T3101208FA | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08FA | 92 | 92 |  | 98.616 | 101.6588 | [6 empty] | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539657 | CONCORD3 115.00 | 539658 | CONCRD6 230.00 | 539904 | CONCOD-T 13.800 | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T441208G | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08G | 92 | 92 | 102.9 | 103.9984 | 108.4956 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - EAST MANHATTAN 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 539600 | 2003-6AT 230.00 | 0 |  | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T441208G | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08G | 92 | 92 | 102.9 | 103.9984 | 108.4956 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - EAST MANHATTAN 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 539600 | 2003-6AT 230.00 | 0 |  | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T571208G | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08G | 92 | 92 | 102.9 | 103.7888 | 108.2477 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - CONCORDIA 230KV CKT 1 | 0 | 539600 | 2003-6AT 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T571208G | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08G | 92 | 92 | 102.9 | 103.7888 | 108.2477 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - CONCORDIA 230KV CKT 1 | 0 | 539600 | 2003-6AT 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T2531208G | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08G | 92 | 92 | 102.7 | 103.7868 | 108.2456 | [6 empty] | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539657 | CONCORD3 115.00 | 539658 | CONCRD6 230.00 | 539904 | CONCOD-T 13.800 | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T2531208G | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08G | 92 | 92 | 102.7 | 103.7868 | 108.2456 | [6 empty] | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539657 | CONCORD3 115.00 | 539658 | CONCRD6 230.00 | 539904 | CONCOD-T 13.800 | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T882208SH | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08SH | 92 | 92 | 118.6 | 120.6515 | 122.044 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - EAST MANHATTAN 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 539600 | 2003-6AT 230.00 | 0 |  | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T882208SH | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08SH | 92 | 92 | 118.6 | 120.6515 | 122.044 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - EAST MANHATTAN 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 539600 | 2003-6AT 230.00 | 0 |  | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1242208SH | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08SH | 92 | 92 | 118.5 | 120.4762 | 121.9174 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - CONCORDIA 230KV CKT 1 | 0 | 539600 | 2003-6AT 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1242208SH | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08SH | 92 | 92 | 118.5 | 120.4762 | 121.9174 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - CONCORDIA 230KV CKT 1 | 0 | 539600 | 2003-6AT 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T6352208SH | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08SH | 92 | 92 | 118.5 | 120.4804 | 121.9161 | [6 empty] | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539657 | CONCORD3 115.00 | 539658 | CONCRD6 230.00 | 539904 | CONCOD-T 13.800 | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T6352208SH | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08SH | 92 | 92 | 118.5 | 120.4804 | 121.9161 | [6 empty] | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539657 | CONCORD3 115.00 | 539658 | CONCRD6 230.00 | 539904 | CONCOD-T 13.800 | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1622208SP | TO->FROM |  | CLIFTON - CONCORDIA 115KV CKT 1 | REL | WEPL | WEPL |  |  | 0 | 539657 | CONCORD3 115.00 | 539656 | CLIFTON3 115.00 | 0 |  | 1 | 08SP | 83.9 | 89.6 |  | 142.9194 | 145.9767 | [6 empty] | CATEGORYB | SINGLE | KELLY - SOUTH SENECA 115KV CKT 1 | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1632208SP | FROM->TO |  | CLIFTON - GREENLEAF 115KV CKT 1 | REL | WEPL | WEPL |  |  | 0 | 539656 | CLIFTON3 115.00 | 539665 | GRNLEAF3 115.00 | 0 |  | 1 | 08SP | 83.9 | 89.6 |  | 131.2311 | 134.2112 | [6 empty] | CATEGORYB | SINGLE | KELLY - SOUTH SENECA 115KV CKT 1 | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1612208SP | FROM->TO |  | GREENLEAF - KNOB HILL 115KV CKT 1 | REL | WEPL | WERE |  | NCENTRAL | 0 | 539665 | GRNLEAF3 115.00 | 533332 | KNOB HL3 115.00 | 0 |  | 1 | 08SP | 92 | 92 |  | 108.2624 | 111.3446 | [6 empty] | CATEGORYB | SINGLE | KELLY - SOUTH SENECA 115KV CKT 1 | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1612208SP | FROM->TO |  | GREENLEAF - KNOB HILL 115KV CKT 1 | REL | WEPL | WERE |  | NCENTRAL | 0 | 539665 | GRNLEAF3 115.00 | 533332 | KNOB HL3 115.00 | 0 |  | 1 | 08SP | 92 | 92 |  | 108.2624 | 111.3446 | [6 empty] | CATEGORYB | SINGLE | KELLY - SOUTH SENECA 115KV CKT 1 | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1612208SP | FROM->TO |  | GREENLEAF - KNOB HILL 115KV CKT 1 | REL | WEPL | WERE |  | NCENTRAL | 0 | 539665 | GRNLEAF3 115.00 | 533332 | KNOB HL3 115.00 | 0 |  | 1 | 08SP | 92 | 92 |  | 108.2624 | 111.3446 | [6 empty] | CATEGORYB | SINGLE | KELLY - SOUTH SENECA 115KV CKT 1 | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T1861208SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08SP | 92 | 92 | 113.6 | 136.649 | 137.6673 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - CONCORDIA 230KV CKT 1 | 0 | 539600 | 2003-6AT 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T1861208SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08SP | 92 | 92 | 113.6 | 136.649 | 137.6673 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - CONCORDIA 230KV CKT 1 | 0 | 539600 | 2003-6AT 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T7271208SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08SP | 92 | 92 | 113.6 | 136.6472 | 137.6658 | [6 empty] | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539657 | CONCORD3 115.00 | 539658 | CONCRD6 230.00 | 539904 | CONCOD-T 13.800 | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T7271208SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08SP | 92 | 92 | 113.6 | 136.6472 | 137.6658 | [6 empty] | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539657 | CONCORD3 115.00 | 539658 | CONCRD6 230.00 | 539904 | CONCOD-T 13.800 | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T1421208SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08SP | 92 | 92 | 113.7 | 136.5674 | 137.5915 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - EAST MANHATTAN 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 539600 | 2003-6AT 230.00 | 0 |  | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T1421208SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 08SP | 92 | 92 | 113.7 | 136.5674 | 137.5915 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - EAST MANHATTAN 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 539600 | 2003-6AT 230.00 | 0 |  | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T1691209SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 09SP | 92 | 92 | 105.5 | 105.3498 | 105.3683 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - EAST MANHATTAN 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 539600 | 2003-6AT 230.00 | 0 |  | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T1691209SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 09SP | 92 | 92 | 105.5 | 105.3498 | 105.3683 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - EAST MANHATTAN 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 539600 | 2003-6AT 230.00 | 0 |  | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T1991209SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 09SP | 92 | 92 | 105.5 | 105.2741 | 105.2931 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - CONCORDIA 230KV CKT 1 | 0 | 539600 | 2003-6AT 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T1991209SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 09SP | 92 | 92 | 105.5 | 105.2741 | 105.2931 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - CONCORDIA 230KV CKT 1 | 0 | 539600 | 2003-6AT 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T7491209SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 09SP | 92 | 92 | 105.5 | 105.274 | 105.293 | [6 empty] | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539657 | CONCORD3 115.00 | 539658 | CONCRD6 230.00 | 539904 | CONCOD-T 13.800 | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T7491209SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 09SP | 92 | 92 | 105.5 | 105.274 | 105.293 | [6 empty] | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539657 | CONCORD3 115.00 | 539658 | CONCRD6 230.00 | 539904 | CONCOD-T 13.800 | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T2594312SP | FROM->TO |  | CLIFTON - GREENLEAF 115KV CKT 1 | REL | WEPL | WEPL |  |  | 0 | 539656 | CLIFTON3 115.00 | 539665 | GRNLEAF3 115.00 | 0 |  | 1 | 12SP | 83.9 | 89.6 |  | 95.7267 | 101.0446 | [6 empty] | CATEGORYB | SINGLE | KELLY - SOUTH SENECA 115KV CKT 1 | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81T9524212SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 12SP | 92 | 92 | 104.5 | 103.3871 | 104.6447 | [6 empty] | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539657 | CONCORD3 115.00 | 539658 | CONCRD6 230.00 | 539904 | CONCOD-T 13.800 | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81T9524212SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 12SP | 92 | 92 | 104.5 | 103.3871 | 104.6447 | [6 empty] | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539657 | CONCORD3 115.00 | 539658 | CONCRD6 230.00 | 539904 | CONCOD-T 13.800 | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81T2504212SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 12SP | 92 | 92 | 104.5 | 103.3872 | 104.5844 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - CONCORDIA 230KV CKT 1 | 0 | 539600 | 2003-6AT 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81T2504212SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 12SP | 92 | 92 | 104.5 | 103.3872 | 104.5844 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - CONCORDIA 230KV CKT 1 | 0 | 539600 | 2003-6AT 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81T4584217SP | FROM->TO |  | CLIFTON - GREENLEAF 115KV CKT 1 | REL | WEPL | WEPL |  |  | 0 | 539656 | CLIFTON3 115.00 | 539665 | GRNLEAF3 115.00 | 0 |  | 1 | 17SP | 83.9 | 89.6 |  | 97.6472 | 103.3971 | [6 empty] | CATEGORYB | SINGLE | KELLY - SOUTH SENECA 115KV CKT 1 | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81T5174217SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 106.2 | 104.4324 | 107.7297 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - CONCORDIA 230KV CKT 1 | 0 | 539600 | 2003-6AT 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81T5174217SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 106.2 | 104.4324 | 107.7297 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - CONCORDIA 230KV CKT 1 | 0 | 539600 | 2003-6AT 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81T17454217SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 106.3 | 104.4326 | 107.729 | [6 empty] | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539657 | CONCORD3 115.00 | 539658 | CONCRD6 230.00 | 539904 | CONCOD-T 13.800 | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81T17454217SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 106.3 | 104.4326 | 107.729 | [6 empty] | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539657 | CONCORD3 115.00 | 539658 | CONCRD6 230.00 | 539904 | CONCOD-T 13.800 | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T4763217SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 106.3 | 104.5608 | 102.8161 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - EAST MANHATTAN 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 539600 | 2003-6AT 230.00 | 0 |  | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T4763217SP | FROM->TO |  | KELLY - SOUTH SENECA 115KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 106.3 | 104.5608 | 102.8161 | [6 empty] | CATEGORYB | SINGLE | 2003-6AT 230.00 - EAST MANHATTAN 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 539600 | 2003-6AT 230.00 | 0 |  | 1 |  |  |  |  | MKEC | CLAY CENTER - GREENLEAF 115KV CKT 1 | Building a new 115 kV tie with Westar from Greenleaf to Clay Center | 120 | 130 | 120 | 130 | 30 | 12 | 12 | Y | 0.08247 | 0.18986 | 0.02136 |  | 7520000 | 2006-07-21 | [23 empty] | 2008-04-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T1052408SH | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 08SH | 32 | 32 |  | 25.2998 | 101.9869 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1872208SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 08SP | 32 | 32 |  | 29.7355 | 122.0877 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1862208SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 08SP | 32 | 32 |  | 26.3121 | 118.4294 | [6 empty] | CATEGORYB | SINGLE | ORCHARD - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533643 | ORCHARD2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T1652308SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 08SP | 32 | 32 |  | 12.5859 | 111.7993 | [6 empty] | CATEGORYB | SINGLE | ATHENS SWITCHING STATION - OWL CREEK 69KV CKT 1 | 0 | 533623 | ATHENS 2 69.000 | 533642 | OWL CRK2 69.000 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T1582408SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 08SP | 58 | 58 |  | 65.4461 | 103.802 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T1612408SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 08SP | 58 | 58 |  | 63.6438 | 101.879 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1492108SP | TO->FROM |  | LEHIGH TAP - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 08SP | 32 | 32 |  | 9.733 | 120.9169 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T1883309SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 09SP | 32 | 32 |  | 29.8705 | 124.2703 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T1873309SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 09SP | 32 | 32 |  | 26.4167 | 120.5106 | [6 empty] | CATEGORYB | SINGLE | ORCHARD - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533643 | ORCHARD2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T1833309SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 09SP | 32 | 32 |  | 12.6944 | 113.9161 | [6 empty] | CATEGORYB | SINGLE | ATHENS SWITCHING STATION - OWL CREEK 69KV CKT 1 | 0 | 533623 | ATHENS 2 69.000 | 533642 | OWL CRK2 69.000 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T1794409SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 09SP | 58 | 58 |  | 65.5805 | 104.7422 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T1824409SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 09SP | 58 | 58 |  | 63.7171 | 102.7839 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T6324109SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 09SP | 58 | 58 |  | 72.8628 | 100.1831 | [6 empty] | CATEGORYB | SINGLE | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81T1751409SP | TO->FROM |  | LEHIGH TAP - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 09SP | 32 | 32 |  | 8.7892 | 124.0056 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2451112SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12SP | 32 | 32 |  | -999 | 185.4455 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T8991112SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12SP | 32 | 32 |  | -999 | 184.8256 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T2942112SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12SP | 32 | 32 |  | 31.8691 | 130.8571 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2461112SP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 157.4692 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T9001112SP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 156.7557 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2471112SP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 12SP | 108 | 108 |  | -999 | 170.7109 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T9011112SP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 12SP | 108 | 108 |  | -999 | 170.0226 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2792412SP | TO->FROM |  | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 56.0845 | 117.3039 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2912412SP | TO->FROM |  | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 55.5503 | 112.3373 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1582212SP | TO->FROM |  | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 72.3233 | 103.7043 | [6 empty] | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2782412SP | FROM->TO |  | ALTOONA - TIOGA 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 41.4013 | 157.0806 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T2972112SP | FROM->TO |  | ALTOONA - TIOGA 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 40.3416 | 153.9666 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T2772112SP | FROM->TO |  | ALTOONA - TIOGA 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 35.1642 | 128.815 | [6 empty] | CATEGORYB | SINGLE | ALLEN - ZILA JUNCTION 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | NCONV |  |  | FNSL-Blown up | FDNS-Blown up | 2 | 3 | 2008-12-01 | 2007AG1AFS84L32312SP |  |  | ALTOONA - TIOGA 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 25.1844 | 72.1214 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2812412SP | TO->FROM | Bidirectional | ARCO TAP - ENA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533634 | ENA 2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | 51.9299 | 110.5372 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2431112SP | FROM->TO | Bidirectional | ARCO TAP - ENA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533620 | ARCOTAP2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 108.209 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T8971112SP | FROM->TO | Bidirectional | ARCO TAP - ENA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533620 | ARCOTAP2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 107.7968 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2441112SP | TO->FROM | Bidirectional | ARCO TAP - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533641 | MONARCH2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 111.7972 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T8981112SP | TO->FROM | Bidirectional | ARCO TAP - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533641 | MONARCH2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 111.3621 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2822412SP | FROM->TO | Bidirectional | ARCO TAP - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533620 | ARCOTAP2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | 49.4684 | 107.2233 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2662412SP | FROM->TO |  | ATHENS SWITCHING STATION - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533623 | ATHENS 2 69.000 | 533642 | OWL CRK2 69.000 | 0 |  | 1 | 12SP | 41 | 41 |  | 10.1577 | 122.0473 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2832412SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12SP | 58 | 58 |  | 67.3281 | 140.9509 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T3022112SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12SP | 58 | 58 |  | 65.3825 | 136.6898 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2481112SP | FROM->TO | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533634 | ENA 2 69.000 | 533646 | TIOGA 2 69.000 | 0 |  | 1 | 12SP | 58 | 58 |  | -999 | 130.2259 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2672412SP | TO->FROM |  | LEHIGH TAP - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12SP | 32 | 32 |  | 9.2569 | 152.3867 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2491112SP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 12SP | 100 | 100 |  | -999 | 193.7517 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T9031112SP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 12SP | 100 | 100 |  | -999 | 192.9783 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2501112SP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 12SP | 108 | 108 |  | -999 | 178.3467 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T9041112SP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 12SP | 108 | 108 |  | -999 | 177.6278 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T572112WP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12WP | 32 | 32 |  | 24.6721 | 179.9951 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T3802112WP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12WP | 32 | 32 |  | 24.8481 | 179.8879 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T574312WP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12WP | 32 | 32 |  | 22.9815 | 100.7665 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T582112WP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 39.9857 | 150.9578 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T3812112WP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 40.0893 | 150.8733 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T553312WP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 12WP | 108 | 108 |  | 36.4684 | 159.2099 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T3843312WP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 12WP | 108 | 108 |  | 36.5782 | 159.1568 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T464112WP | FROM->TO | Bidirectional | ARCO TAP - ENA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533620 | ARCOTAP2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 9.7864 | 101.0901 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T3394112WP | FROM->TO | Bidirectional | ARCO TAP - ENA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533620 | ARCOTAP2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 10.0489 | 100.9961 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T474112WP | TO->FROM | Bidirectional | ARCO TAP - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533641 | MONARCH2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 11.0682 | 103.599 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T3404112WP | TO->FROM | Bidirectional | ARCO TAP - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533641 | MONARCH2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 11.2882 | 103.5055 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T514112WP | FROM->TO | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533634 | ENA 2 69.000 | 533646 | TIOGA 2 69.000 | 0 |  | 1 | 12WP | 58 | 58 |  | 10.7435 | 122.8447 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T3444112WP | FROM->TO | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533634 | ENA 2 69.000 | 533646 | TIOGA 2 69.000 | 0 |  | 1 | 12WP | 58 | 58 |  | 11.1297 | 122.7501 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81T964212WP | TO->FROM |  | LEHIGH TAP - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12WP | 32 | 32 |  | 7.335 | 100.4311 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T593312WP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 12WP | 100 | 100 |  | 44.6309 | 179.6932 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T3883312WP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 12WP | 100 | 100 |  | 44.776 | 179.5805 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T613312WP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 12WP | 108 | 108 |  | 40.4185 | 165.4322 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T3024312WP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 12WP | 108 | 108 |  | 40.5965 | 165.359 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4092317SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 17SP | 32 | 32 |  | 14.5581 | 132.3017 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16612317SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 17SP | 32 | 32 |  | 14.4858 | 131.4416 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4832317SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 17SP | 32 | 32 |  | 35.6597 | 126.9833 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4102317SP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 17SP | 72 | 72 |  | 23.268 | 100.8105 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16622317SP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 17SP | 72 | 72 |  | 23.1386 | 100.3044 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4112317SP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 17SP | 108 | 108 |  | 28.8307 | 116.5141 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16632317SP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 17SP | 108 | 108 |  | 28.7177 | 115.9243 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T6122417SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 17SP | 58 | 58 |  | 70.7819 | 101.4296 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T4742117SP | TO->FROM |  | LEHIGH TAP - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 17SP | 32 | 32 |  | 11.392 | 117.9501 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4122317SP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 17SP | 100 | 100 |  | 38.8083 | 133.7621 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16642317SP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 17SP | 100 | 100 |  | 38.688 | 133.0647 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4132317SP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 17SP | 108 | 108 |  | 34.6116 | 122.4871 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16652317SP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 17SP | 108 | 108 |  | 34.4969 | 121.8479 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | COFFEY COUNTY NO. 3 WESTPHALIA - GREEN 69KV CKT 1 | Rebuild 9.22 miles (138kV/69kV Operation) | [8 empty] | 0.019382 | 0.13324 | 0.0027316 | 450k per mile | 4149000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4742308SH | FROM->TO |  | COFFEYVILLE TAP - DEARING 138KV CKT 1 | CP | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 08SH | 202 | 232 |  | 93.2586 | 101.8293 | [6 empty] | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | AEPW | COFFEYVILLE TAP - DEARING 138KV CKT 1 AEPW | Tie Line, Reconductor 1.09 miles of 795 ACSR with 1590 ACSR. | 368 | 512 | 434 | 555 | 1.09 | 15 | 6 |  | 0.00039 | 0.003837 | 0.00133 | AEP: The limiting factor is the AEP portion of 795 ACSR conductor. New ratings are for AEP only. The new limit is the 1590 ACSR conductor. | 950000 | 2007-04-13 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T252308SH | FROM->TO |  | COFFEYVILLE TAP - DEARING 138KV CKT 1 | CP | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 08SH | 202 | 232 |  | 96.2273 | 100.2268 | [6 empty] | CATEGORYB | SINGLE | DELAWARE - NEOSHO 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 532793 | NEOSHO 7 345.00 | 0 |  | 1 |  |  |  | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | AEPW | COFFEYVILLE TAP - DEARING 138KV CKT 1 AEPW | Tie Line, Reconductor 1.09 miles of 795 ACSR with 1590 ACSR. | 368 | 512 | 434 | 555 | 1.09 | 15 | 6 |  | 0.00039 | 0.003837 | 0.00133 | AEP: The limiting factor is the AEP portion of 795 ACSR conductor. New ratings are for AEP only. The new limit is the 1590 ACSR conductor. | 950000 | 2007-04-13 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T6612308SP | FROM->TO |  | COFFEYVILLE TAP - DEARING 138KV CKT 1 | CP | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 08SP | 202 | 232 | 103.8 | 99.4706 | 110.3595 | [6 empty] | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | AEPW | COFFEYVILLE TAP - DEARING 138KV CKT 1 AEPW | Tie Line, Reconductor 1.09 miles of 795 ACSR with 1590 ACSR. | 368 | 512 | 434 | 555 | 1.09 | 15 | 6 |  | 0.00039 | 0.003837 | 0.00133 | AEP: The limiting factor is the AEP portion of 795 ACSR conductor. New ratings are for AEP only. The new limit is the 1590 ACSR conductor. | 950000 | 2007-04-13 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T512308SP | FROM->TO |  | COFFEYVILLE TAP - DEARING 138KV CKT 1 | CP | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 08SP | 202 | 232 |  | 96.7046 | 101.5823 | [6 empty] | CATEGORYB | SINGLE | DELAWARE - NEOSHO 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 532793 | NEOSHO 7 345.00 | 0 |  | 1 |  |  |  | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | AEPW | COFFEYVILLE TAP - DEARING 138KV CKT 1 AEPW | Tie Line, Reconductor 1.09 miles of 795 ACSR with 1590 ACSR. | 368 | 512 | 434 | 555 | 1.09 | 15 | 6 |  | 0.00039 | 0.003837 | 0.00133 | AEP: The limiting factor is the AEP portion of 795 ACSR conductor. New ratings are for AEP only. The new limit is the 1590 ACSR conductor. | 950000 | 2007-04-13 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T6722309SP | FROM->TO |  | COFFEYVILLE TAP - DEARING 138KV CKT 1 | CP | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 09SP | 202 | 232 | 107.4 | 103.5834 | 116.3049 | [6 empty] | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | AEPW | COFFEYVILLE TAP - DEARING 138KV CKT 1 AEPW | Tie Line, Reconductor 1.09 miles of 795 ACSR with 1590 ACSR. | 368 | 512 | 434 | 555 | 1.09 | 15 | 6 |  | 0.00039 | 0.003837 | 0.00133 | AEP: The limiting factor is the AEP portion of 795 ACSR conductor. New ratings are for AEP only. The new limit is the 1590 ACSR conductor. | 950000 | 2007-04-13 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T643309SP | FROM->TO |  | COFFEYVILLE TAP - DEARING 138KV CKT 1 | CP | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 09SP | 202 | 232 | 100.8 | 99.0275 | 108.9347 | [6 empty] | CATEGORYB | SINGLE | DELAWARE - NEOSHO 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 532793 | NEOSHO 7 345.00 | 0 |  | 1 |  |  |  | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | AEPW | COFFEYVILLE TAP - DEARING 138KV CKT 1 AEPW | Tie Line, Reconductor 1.09 miles of 795 ACSR with 1590 ACSR. | 368 | 512 | 434 | 555 | 1.09 | 15 | 6 |  | 0.00039 | 0.003837 | 0.00133 | AEP: The limiting factor is the AEP portion of 795 ACSR conductor. New ratings are for AEP only. The new limit is the 1590 ACSR conductor. | 950000 | 2007-04-13 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T10512312SP | FROM->TO |  | COFFEYVILLE TAP - DEARING 138KV CKT 1 | CP | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 12SP | 287 | 287 |  | 86.3557 | 105.5464 | [6 empty] | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | AEPW | COFFEYVILLE TAP - DEARING 138KV CKT 1 AEPW | Tie Line, Reconductor 1.09 miles of 795 ACSR with 1590 ACSR. | 368 | 512 | 434 | 555 | 1.09 | 15 | 6 |  | 0.00039 | 0.003837 | 0.00133 | AEP: The limiting factor is the AEP portion of 795 ACSR conductor. New ratings are for AEP only. The new limit is the 1590 ACSR conductor. | 950000 | 2007-04-13 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T15443317SP | FROM->TO |  | COFFEYVILLE TAP - DEARING 138KV CKT 1 | CP | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 17SP | 287 | 287 |  | 88.8855 | 106.2845 | [6 empty] | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | AEPW | COFFEYVILLE TAP - DEARING 138KV CKT 1 AEPW | Tie Line, Reconductor 1.09 miles of 795 ACSR with 1590 ACSR. | 368 | 512 | 434 | 555 | 1.09 | 15 | 6 |  | 0.00039 | 0.003837 | 0.00133 | AEP: The limiting factor is the AEP portion of 795 ACSR conductor. New ratings are for AEP only. The new limit is the 1590 ACSR conductor. | 950000 | 2007-04-13 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4742308SH | FROM->TO |  | COFFEYVILLE TAP - DEARING 138KV CKT 1 | CP | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 08SH | 202 | 232 |  | 93.2586 | 101.8293 | [6 empty] | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | WERE | COFFEYVILLE TAP - DEARING 138KV CKT 1 WERE | Tie Line, Rebuild 3.93 miles of 795 ACSR with 1590 ACSR. | 287 | 287 | 287 | 287 | 3.93 | 15 | 6 |  | 0.0014061 | 0.013834 | 0.0047953 |  | 3000000 | 2006-06-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T252308SH | FROM->TO |  | COFFEYVILLE TAP - DEARING 138KV CKT 1 | CP | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 08SH | 202 | 232 |  | 96.2273 | 100.2268 | [6 empty] | CATEGORYB | SINGLE | DELAWARE - NEOSHO 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 532793 | NEOSHO 7 345.00 | 0 |  | 1 |  |  |  | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | WERE | COFFEYVILLE TAP - DEARING 138KV CKT 1 WERE | Tie Line, Rebuild 3.93 miles of 795 ACSR with 1590 ACSR. | 287 | 287 | 287 | 287 | 3.93 | 15 | 6 |  | 0.0014061 | 0.013834 | 0.0047953 |  | 3000000 | 2006-06-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T6612308SP | FROM->TO |  | COFFEYVILLE TAP - DEARING 138KV CKT 1 | CP | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 08SP | 202 | 232 | 103.8 | 99.4706 | 110.3595 | [6 empty] | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | WERE | COFFEYVILLE TAP - DEARING 138KV CKT 1 WERE | Tie Line, Rebuild 3.93 miles of 795 ACSR with 1590 ACSR. | 287 | 287 | 287 | 287 | 3.93 | 15 | 6 |  | 0.0014061 | 0.013834 | 0.0047953 |  | 3000000 | 2006-06-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T512308SP | FROM->TO |  | COFFEYVILLE TAP - DEARING 138KV CKT 1 | CP | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 08SP | 202 | 232 |  | 96.7046 | 101.5823 | [6 empty] | CATEGORYB | SINGLE | DELAWARE - NEOSHO 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 532793 | NEOSHO 7 345.00 | 0 |  | 1 |  |  |  | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | WERE | COFFEYVILLE TAP - DEARING 138KV CKT 1 WERE | Tie Line, Rebuild 3.93 miles of 795 ACSR with 1590 ACSR. | 287 | 287 | 287 | 287 | 3.93 | 15 | 6 |  | 0.0014061 | 0.013834 | 0.0047953 |  | 3000000 | 2006-06-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T6722309SP | FROM->TO |  | COFFEYVILLE TAP - DEARING 138KV CKT 1 | CP | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 09SP | 202 | 232 | 107.4 | 103.5834 | 116.3049 | [6 empty] | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | WERE | COFFEYVILLE TAP - DEARING 138KV CKT 1 WERE | Tie Line, Rebuild 3.93 miles of 795 ACSR with 1590 ACSR. | 287 | 287 | 287 | 287 | 3.93 | 15 | 6 |  | 0.0014061 | 0.013834 | 0.0047953 |  | 3000000 | 2006-06-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T643309SP | FROM->TO |  | COFFEYVILLE TAP - DEARING 138KV CKT 1 | CP | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 09SP | 202 | 232 | 100.8 | 99.0275 | 108.9347 | [6 empty] | CATEGORYB | SINGLE | DELAWARE - NEOSHO 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 532793 | NEOSHO 7 345.00 | 0 |  | 1 |  |  |  | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | WERE | COFFEYVILLE TAP - DEARING 138KV CKT 1 WERE | Tie Line, Rebuild 3.93 miles of 795 ACSR with 1590 ACSR. | 287 | 287 | 287 | 287 | 3.93 | 15 | 6 |  | 0.0014061 | 0.013834 | 0.0047953 |  | 3000000 | 2006-06-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T10512312SP | FROM->TO |  | COFFEYVILLE TAP - DEARING 138KV CKT 1 | CP | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 12SP | 287 | 287 |  | 86.3557 | 105.5464 | [6 empty] | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | WERE | COFFEYVILLE TAP - DEARING 138KV CKT 1 WERE | Tie Line, Rebuild 3.93 miles of 795 ACSR with 1590 ACSR. | 287 | 287 | 287 | 287 | 3.93 | 15 | 6 |  | 0.0014061 | 0.013834 | 0.0047953 |  | 3000000 | 2006-06-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T15443317SP | FROM->TO |  | COFFEYVILLE TAP - DEARING 138KV CKT 1 | CP | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 17SP | 287 | 287 |  | 88.8855 | 106.2845 | [6 empty] | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | WERE | COFFEYVILLE TAP - DEARING 138KV CKT 1 WERE | Tie Line, Rebuild 3.93 miles of 795 ACSR with 1590 ACSR. | 287 | 287 | 287 | 287 | 3.93 | 15 | 6 |  | 0.0014061 | 0.013834 | 0.0047953 |  | 3000000 | 2006-06-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T10512312SP | FROM->TO |  | COFFEYVILLE TAP - DEARING 138KV CKT 1 | S | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 12SP | 287 | 287 |  | 86.3557 | 105.5464 | [6 empty] | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | WERE | COFFEYVILLE TAP - DEARING 138KV CKT 1 WERE #2 | Replace Disconnect Switches, Wavetrap, Breaker, Jumpers | 382 | 382 | 382 | 382 | [8 empty] | 200000 | 2007-01-01 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T15443317SP | FROM->TO |  | COFFEYVILLE TAP - DEARING 138KV CKT 1 | S | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 17SP | 287 | 287 |  | 88.8855 | 106.2845 | [6 empty] | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | WERE | COFFEYVILLE TAP - DEARING 138KV CKT 1 WERE #2 | Replace Disconnect Switches, Wavetrap, Breaker, Jumpers | 382 | 382 | 382 | 382 | [8 empty] | 200000 | 2007-01-01 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T633309SP | TO->FROM |  | COFFEYVILLE TAP - NORTH BARTLESVILLE 138KV CKT 1 | S | AEPW | AEPW | TS-KAMO | NORTHERN | 0 | 510386 | NBVILLE4 138.00 | 510422 | COFFEYT4 138.00 | 0 |  | 1 | 09SP | 202 | 235 |  | 97.6932 | 105.6379 | [6 empty] | CATEGORYB | SINGLE | DELAWARE - NORTHEAST STATION 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 510406 | N.E.S.-7 345.00 | 0 |  | 1 |  |  |  |  | AEPW | COFFEYVILLE TAP - NORTH BARTLESVILLE 138KV CKT 1 | Rebuild 13.11 miles of 795 ACSR with 1590 ACSR. | 287 | 287 | 287 | 287 | 13.11 | 24 | 9 |  | 0.00468 | 0.04865 | 0.01512 | New Limits will be switches on both ends | 13100000 | 2007-09-18 | [23 empty] | 2009-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T1123312SP | TO->FROM |  | COFFEYVILLE TAP - NORTH BARTLESVILLE 138KV CKT 1 | S | AEPW | AEPW | TS-KAMO | NORTHERN | 0 | 510386 | NBVILLE4 138.00 | 510422 | COFFEYT4 138.00 | 0 |  | 1 | 12SP | 202 | 235 |  | 89.8135 | 101.201 | [6 empty] | CATEGORYB | SINGLE | DELAWARE - NORTHEAST STATION 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 510406 | N.E.S.-7 345.00 | 0 |  | 1 |  |  |  |  | AEPW | COFFEYVILLE TAP - NORTH BARTLESVILLE 138KV CKT 1 | Rebuild 13.11 miles of 795 ACSR with 1590 ACSR. | 287 | 287 | 287 | 287 | 13.11 | 24 | 9 |  | 0.00468 | 0.04865 | 0.01512 | New Limits will be switches on both ends | 13100000 | 2007-09-18 | [23 empty] | 2009-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T7155517SP | FROM->TO |  | CONCORDIA - JEWELL 3 115KV CKT 1 | S | WEPL | WEPL |  |  | 0 | 539657 | CONCORD3 115.00 | 539669 | JEWELL 3 115.00 | 0 |  | 1 | 17SP | 83.9 | 89.6 |  | 87.7928 | 101.9207 | [6 empty] | CATEGORYB | SINGLE | BELOIT - CONCORDIA 115KV CKT 1 | 0 | 539650 | BELOIT 3 115.00 | 539657 | CONCORD3 115.00 | 0 |  | 1 |  |  |  |  | MKEC | CONCORDIA - JEWELL 3 115KV CKT 1 | Rebuild 25.8 mile line | [11 empty] | $249,916.24 per mile | 6447839 | 2008-05-15 | [23 empty] | 2013-06-01 | 2013-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T3672312SP | TO->FROM |  | COOK - ST JOE 161KV CKT 1 | S | MIPU | MIPU | FLA | FLA | 0 | 541253 | ST JOE 5 161.00 | 541257 | COOK 5 161.00 | 0 |  | 1 | 12SP | 315 | 315 |  | 80.7408 | 114.1071 | 540_COOK - ST JOE 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | ST JOE - WOODBINE 161KV CKT 1 | 0 | 541253 | ST JOE 5 161.00 | 541258 | WOODBIN5 161.00 | 0 |  | 1 |  |  |  |  | SJLP | COOK - ST JOE 161KV CKT 1 | Conductor, Switch, Relay | 446 | 446 |  |  |  | 18 |  |  | 0.0011358 | 0.010491 | 0.008435 |  | 4400000 | 2007-01-01 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T3682312SP | TO->FROM |  | COOK - ST JOE 161KV CKT 1 | S | MIPU | MIPU | FLA | FLA | 0 | 541253 | ST JOE 5 161.00 | 541257 | COOK 5 161.00 | 0 |  | 1 | 12SP | 315 | 315 |  | 75.4394 | 106.8637 | 540_COOK - ST JOE 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | EAST - WOODBINE 161KV CKT 1 | 0 | 541254 | EAST 5 161.00 | 541258 | WOODBIN5 161.00 | 0 |  | 1 |  |  |  |  | SJLP | COOK - ST JOE 161KV CKT 1 | Conductor, Switch, Relay | 446 | 446 |  |  |  | 18 |  |  | 0.0011358 | 0.010491 | 0.008435 |  | 4400000 | 2007-01-01 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T5772317SP | TO->FROM |  | COOK - ST JOE 161KV CKT 1 | S | MIPU | MIPU | FLA | FLA | 0 | 541253 | ST JOE 5 161.00 | 541257 | COOK 5 161.00 | 0 |  | 1 | 17SP | 315 | 315 |  | 85.831 | 106.2784 | 540_COOK - ST JOE 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | ST JOE - WOODBINE 161KV CKT 1 | 0 | 541253 | ST JOE 5 161.00 | 541258 | WOODBIN5 161.00 | 0 |  | 1 |  |  |  |  | SJLP | COOK - ST JOE 161KV CKT 1 | Conductor, Switch, Relay | 446 | 446 |  |  |  | 18 |  |  | 0.0011358 | 0.010491 | 0.008435 |  | 4400000 | 2007-01-01 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T762308SH | FROM->TO |  | CRESWELL - OAK 69KV CKT 1 | S | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 | 08SH | 90 | 90 |  | 51.7558 | 104.0334 | [6 empty] | CATEGORYB | SINGLE | CRESWELL - PARIS 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533548 | PARIS 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | CRESWELL - OAK 69KV CKT 1 #1 Displacement | Replace jumpers and bus, and reset CTs and relaying. Rebuild substations. | 107 | 107 | 107 | 107 | 0 | 6 | 2 | N |  |  |  | Conductor limit is 107 MVA. | 250000 | 2006-07-21 | [23 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T4364317SP | FROM->TO |  | CRESWELL - OAK 69KV CKT 1 | S | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 | 17SP | 90 | 90 | 110.4 | 69.0764 | 111.7477 | [6 empty] | CATEGORYB | SINGLE | CRESWELL - PARIS 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533548 | PARIS 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | CRESWELL - OAK 69KV CKT 1 #1 Displacement | Replace jumpers and bus, and reset CTs and relaying. Rebuild substations. | 107 | 107 | 107 | 107 | 0 | 6 | 2 | N |  |  |  | Conductor limit is 107 MVA. | 250000 | 2006-07-21 | [23 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T9452209SP | FROM->TO |  | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 | EXP | ENTR | AEPW | EES-ARK | GRWDAECC | 0 | 99496 | 5DANVI 161.00 | 507195 | MAGZREC5 161.00 | 0 |  | 1 | 09SP | 127 | 148 | 115.5 | 115.4683 | 124.2538 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  | Per MW-Mile files, 47.6% AEPW, 47.6% EES, 4.8 OKGE of 17.96 miles. | AEPW | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 AEPW | Rebuild 17.96 miles of 250 Copperweld with 1272 ACSR. | 285 | 335 | 335 | 335 | 17.96 | 30 | 15 |  | 0.00894 | 0.047018 | 0.02948 |  | 8520400 | 2006-07-17 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T9452209SP | FROM->TO |  | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 | EXP | ENTR | AEPW | EES-ARK | GRWDAECC | 0 | 99496 | 5DANVI 161.00 | 507195 | MAGZREC5 161.00 | 0 |  | 1 | 09SP | 127 | 148 | 115.5 | 115.4683 | 124.2538 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  | Per MW-Mile files, 47.6% AEPW, 47.6% EES, 4.8 OKGE of 17.96 miles. | AEPW | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 AEPW | Rebuild 17.96 miles of 250 Copperweld with 1272 ACSR. | 285 | 335 | 335 | 335 | 17.96 | 30 | 15 |  | 0.00894 | 0.047018 | 0.02948 |  | 8520400 | 2006-07-17 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T5802209WP | FROM->TO |  | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 | EXP | ENTR | AEPW | EES-ARK | GRWDAECC | 0 | 99496 | 5DANVI 161.00 | 507195 | MAGZREC5 161.00 | 0 |  | 1 | 09WP | 148 | 148 | 106.1 | 106.0918 | 114.8641 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  | Per MW-Mile files, 47.6% AEPW, 47.6% EES, 4.8 OKGE of 17.96 miles. | AEPW | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 AEPW | Rebuild 17.96 miles of 250 Copperweld with 1272 ACSR. | 285 | 335 | 335 | 335 | 17.96 | 30 | 15 |  | 0.00894 | 0.047018 | 0.02948 |  | 8520400 | 2006-07-17 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T5802209WP | FROM->TO |  | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 | EXP | ENTR | AEPW | EES-ARK | GRWDAECC | 0 | 99496 | 5DANVI 161.00 | 507195 | MAGZREC5 161.00 | 0 |  | 1 | 09WP | 148 | 148 | 106.1 | 106.0918 | 114.8641 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  | Per MW-Mile files, 47.6% AEPW, 47.6% EES, 4.8 OKGE of 17.96 miles. | AEPW | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 AEPW | Rebuild 17.96 miles of 250 Copperweld with 1272 ACSR. | 285 | 335 | 335 | 335 | 17.96 | 30 | 15 |  | 0.00894 | 0.047018 | 0.02948 |  | 8520400 | 2006-07-17 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T13562212SP | FROM->TO |  | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 | EXP | ENTR | AEPW | EES-ARK | GRWDAECC | 0 | 99496 | 5DANVI 161.00 | 507195 | MAGZREC5 161.00 | 0 |  | 1 | 12SP | 127 | 148 | 116.0 | 115.8848 | 127.7453 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  | Per MW-Mile files, 47.6% AEPW, 47.6% EES, 4.8 OKGE of 17.96 miles. | AEPW | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 AEPW | Rebuild 17.96 miles of 250 Copperweld with 1272 ACSR. | 285 | 335 | 335 | 335 | 17.96 | 30 | 15 |  | 0.00894 | 0.047018 | 0.02948 |  | 8520400 | 2006-07-17 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T13562212SP | FROM->TO |  | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 | EXP | ENTR | AEPW | EES-ARK | GRWDAECC | 0 | 99496 | 5DANVI 161.00 | 507195 | MAGZREC5 161.00 | 0 |  | 1 | 12SP | 127 | 148 | 116.0 | 115.8848 | 127.7453 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  | Per MW-Mile files, 47.6% AEPW, 47.6% EES, 4.8 OKGE of 17.96 miles. | AEPW | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 AEPW | Rebuild 17.96 miles of 250 Copperweld with 1272 ACSR. | 285 | 335 | 335 | 335 | 17.96 | 30 | 15 |  | 0.00894 | 0.047018 | 0.02948 |  | 8520400 | 2006-07-17 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T7462212WP | FROM->TO |  | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 | EXP | ENTR | AEPW | EES-ARK | GRWDAECC | 0 | 99496 | 5DANVI 161.00 | 507195 | MAGZREC5 161.00 | 0 |  | 1 | 12WP | 127 | 148 |  | 93.7537 | 104.7371 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  | Per MW-Mile files, 47.6% AEPW, 47.6% EES, 4.8 OKGE of 17.96 miles. | AEPW | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 AEPW | Rebuild 17.96 miles of 250 Copperweld with 1272 ACSR. | 285 | 335 | 335 | 335 | 17.96 | 30 | 15 |  | 0.00894 | 0.047018 | 0.02948 |  | 8520400 | 2006-07-17 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T7462212WP | FROM->TO |  | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 | EXP | ENTR | AEPW | EES-ARK | GRWDAECC | 0 | 99496 | 5DANVI 161.00 | 507195 | MAGZREC5 161.00 | 0 |  | 1 | 12WP | 127 | 148 |  | 93.7537 | 104.7371 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  | Per MW-Mile files, 47.6% AEPW, 47.6% EES, 4.8 OKGE of 17.96 miles. | AEPW | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 AEPW | Rebuild 17.96 miles of 250 Copperweld with 1272 ACSR. | 285 | 335 | 335 | 335 | 17.96 | 30 | 15 |  | 0.00894 | 0.047018 | 0.02948 |  | 8520400 | 2006-07-17 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T20512217SP | FROM->TO |  | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 | EXP | ENTR | AEPW | EES-ARK | GRWDAECC | 0 | 99496 | 5DANVI 161.00 | 507195 | MAGZREC5 161.00 | 0 |  | 1 | 17SP | 127 | 148 | 122.8 | 123.2319 | 134.2646 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  | Per MW-Mile files, 47.6% AEPW, 47.6% EES, 4.8 OKGE of 17.96 miles. | AEPW | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 AEPW | Rebuild 17.96 miles of 250 Copperweld with 1272 ACSR. | 285 | 335 | 335 | 335 | 17.96 | 30 | 15 |  | 0.00894 | 0.047018 | 0.02948 |  | 8520400 | 2006-07-17 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T20512217SP | FROM->TO |  | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 | EXP | ENTR | AEPW | EES-ARK | GRWDAECC | 0 | 99496 | 5DANVI 161.00 | 507195 | MAGZREC5 161.00 | 0 |  | 1 | 17SP | 127 | 148 | 122.8 | 123.2319 | 134.2646 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  | Per MW-Mile files, 47.6% AEPW, 47.6% EES, 4.8 OKGE of 17.96 miles. | AEPW | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 AEPW | Rebuild 17.96 miles of 250 Copperweld with 1272 ACSR. | 285 | 335 | 335 | 335 | 17.96 | 30 | 15 |  | 0.00894 | 0.047018 | 0.02948 |  | 8520400 | 2006-07-17 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T9452209SP | FROM->TO |  | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 | EXP | ENTR | AEPW | EES-ARK | GRWDAECC | 0 | 99496 | 5DANVI 161.00 | 507195 | MAGZREC5 161.00 | 0 |  | 1 | 09SP | 127 | 148 | 115.5 | 115.4683 | 124.2538 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  | Per MW-Mile files, 47.6% AEPW, 47.6% EES, 4.8 OKGE of 17.96 miles. | ENTR | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 ENTR | Rebuild 17.96 miles of 250 Copperweld with 1272 ACSR. | 285 | 335 | 335 | 335 | 17.96 | 30 | 15 |  | 0.00894 | 0.047018 | 0.02948 |  | 8520400 | 2006-07-17 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T9452209SP | FROM->TO |  | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 | EXP | ENTR | AEPW | EES-ARK | GRWDAECC | 0 | 99496 | 5DANVI 161.00 | 507195 | MAGZREC5 161.00 | 0 |  | 1 | 09SP | 127 | 148 | 115.5 | 115.4683 | 124.2538 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  | Per MW-Mile files, 47.6% AEPW, 47.6% EES, 4.8 OKGE of 17.96 miles. | ENTR | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 ENTR | Rebuild 17.96 miles of 250 Copperweld with 1272 ACSR. | 285 | 335 | 335 | 335 | 17.96 | 30 | 15 |  | 0.00894 | 0.047018 | 0.02948 |  | 8520400 | 2006-07-17 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T5802209WP | FROM->TO |  | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 | EXP | ENTR | AEPW | EES-ARK | GRWDAECC | 0 | 99496 | 5DANVI 161.00 | 507195 | MAGZREC5 161.00 | 0 |  | 1 | 09WP | 148 | 148 | 106.1 | 106.0918 | 114.8641 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  | Per MW-Mile files, 47.6% AEPW, 47.6% EES, 4.8 OKGE of 17.96 miles. | ENTR | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 ENTR | Rebuild 17.96 miles of 250 Copperweld with 1272 ACSR. | 285 | 335 | 335 | 335 | 17.96 | 30 | 15 |  | 0.00894 | 0.047018 | 0.02948 |  | 8520400 | 2006-07-17 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T5802209WP | FROM->TO |  | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 | EXP | ENTR | AEPW | EES-ARK | GRWDAECC | 0 | 99496 | 5DANVI 161.00 | 507195 | MAGZREC5 161.00 | 0 |  | 1 | 09WP | 148 | 148 | 106.1 | 106.0918 | 114.8641 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  | Per MW-Mile files, 47.6% AEPW, 47.6% EES, 4.8 OKGE of 17.96 miles. | ENTR | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 ENTR | Rebuild 17.96 miles of 250 Copperweld with 1272 ACSR. | 285 | 335 | 335 | 335 | 17.96 | 30 | 15 |  | 0.00894 | 0.047018 | 0.02948 |  | 8520400 | 2006-07-17 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T13562212SP | FROM->TO |  | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 | EXP | ENTR | AEPW | EES-ARK | GRWDAECC | 0 | 99496 | 5DANVI 161.00 | 507195 | MAGZREC5 161.00 | 0 |  | 1 | 12SP | 127 | 148 | 116.0 | 115.8848 | 127.7453 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  | Per MW-Mile files, 47.6% AEPW, 47.6% EES, 4.8 OKGE of 17.96 miles. | ENTR | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 ENTR | Rebuild 17.96 miles of 250 Copperweld with 1272 ACSR. | 285 | 335 | 335 | 335 | 17.96 | 30 | 15 |  | 0.00894 | 0.047018 | 0.02948 |  | 8520400 | 2006-07-17 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T13562212SP | FROM->TO |  | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 | EXP | ENTR | AEPW | EES-ARK | GRWDAECC | 0 | 99496 | 5DANVI 161.00 | 507195 | MAGZREC5 161.00 | 0 |  | 1 | 12SP | 127 | 148 | 116.0 | 115.8848 | 127.7453 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  | Per MW-Mile files, 47.6% AEPW, 47.6% EES, 4.8 OKGE of 17.96 miles. | ENTR | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 ENTR | Rebuild 17.96 miles of 250 Copperweld with 1272 ACSR. | 285 | 335 | 335 | 335 | 17.96 | 30 | 15 |  | 0.00894 | 0.047018 | 0.02948 |  | 8520400 | 2006-07-17 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T7462212WP | FROM->TO |  | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 | EXP | ENTR | AEPW | EES-ARK | GRWDAECC | 0 | 99496 | 5DANVI 161.00 | 507195 | MAGZREC5 161.00 | 0 |  | 1 | 12WP | 127 | 148 |  | 93.7537 | 104.7371 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  | Per MW-Mile files, 47.6% AEPW, 47.6% EES, 4.8 OKGE of 17.96 miles. | ENTR | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 ENTR | Rebuild 17.96 miles of 250 Copperweld with 1272 ACSR. | 285 | 335 | 335 | 335 | 17.96 | 30 | 15 |  | 0.00894 | 0.047018 | 0.02948 |  | 8520400 | 2006-07-17 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T7462212WP | FROM->TO |  | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 | EXP | ENTR | AEPW | EES-ARK | GRWDAECC | 0 | 99496 | 5DANVI 161.00 | 507195 | MAGZREC5 161.00 | 0 |  | 1 | 12WP | 127 | 148 |  | 93.7537 | 104.7371 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  | Per MW-Mile files, 47.6% AEPW, 47.6% EES, 4.8 OKGE of 17.96 miles. | ENTR | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 ENTR | Rebuild 17.96 miles of 250 Copperweld with 1272 ACSR. | 285 | 335 | 335 | 335 | 17.96 | 30 | 15 |  | 0.00894 | 0.047018 | 0.02948 |  | 8520400 | 2006-07-17 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T20512217SP | FROM->TO |  | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 | EXP | ENTR | AEPW | EES-ARK | GRWDAECC | 0 | 99496 | 5DANVI 161.00 | 507195 | MAGZREC5 161.00 | 0 |  | 1 | 17SP | 127 | 148 | 122.8 | 123.2319 | 134.2646 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  | Per MW-Mile files, 47.6% AEPW, 47.6% EES, 4.8 OKGE of 17.96 miles. | ENTR | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 ENTR | Rebuild 17.96 miles of 250 Copperweld with 1272 ACSR. | 285 | 335 | 335 | 335 | 17.96 | 30 | 15 |  | 0.00894 | 0.047018 | 0.02948 |  | 8520400 | 2006-07-17 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T20512217SP | FROM->TO |  | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 | EXP | ENTR | AEPW | EES-ARK | GRWDAECC | 0 | 99496 | 5DANVI 161.00 | 507195 | MAGZREC5 161.00 | 0 |  | 1 | 17SP | 127 | 148 | 122.8 | 123.2319 | 134.2646 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  | Per MW-Mile files, 47.6% AEPW, 47.6% EES, 4.8 OKGE of 17.96 miles. | ENTR | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 ENTR | Rebuild 17.96 miles of 250 Copperweld with 1272 ACSR. | 285 | 335 | 335 | 335 | 17.96 | 30 | 15 |  | 0.00894 | 0.047018 | 0.02948 |  | 8520400 | 2006-07-17 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T9452209SP | FROM->TO |  | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 | EXP | ENTR | AEPW | EES-ARK | GRWDAECC | 0 | 99496 | 5DANVI 161.00 | 507195 | MAGZREC5 161.00 | 0 |  | 1 | 09SP | 127 | 148 | 115.5 | 115.4683 | 124.2538 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  | Per MW-Mile files, 47.6% AEPW, 47.6% EES, 4.8 OKGE of 17.96 miles. | OKGE | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 OKGE | Rebuild 17.96 miles of 250 Copperweld with 1272 ACSR. | 285 | 335 | 335 | 335 | 17.96 | 30 | 15 |  | 0.00894 | 0.047018 | 0.02948 |  | 859200 | 2006-07-17 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T9452209SP | FROM->TO |  | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 | EXP | ENTR | AEPW | EES-ARK | GRWDAECC | 0 | 99496 | 5DANVI 161.00 | 507195 | MAGZREC5 161.00 | 0 |  | 1 | 09SP | 127 | 148 | 115.5 | 115.4683 | 124.2538 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  | Per MW-Mile files, 47.6% AEPW, 47.6% EES, 4.8 OKGE of 17.96 miles. | OKGE | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 OKGE | Rebuild 17.96 miles of 250 Copperweld with 1272 ACSR. | 285 | 335 | 335 | 335 | 17.96 | 30 | 15 |  | 0.00894 | 0.047018 | 0.02948 |  | 859200 | 2006-07-17 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T5802209WP | FROM->TO |  | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 | EXP | ENTR | AEPW | EES-ARK | GRWDAECC | 0 | 99496 | 5DANVI 161.00 | 507195 | MAGZREC5 161.00 | 0 |  | 1 | 09WP | 148 | 148 | 106.1 | 106.0918 | 114.8641 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  | Per MW-Mile files, 47.6% AEPW, 47.6% EES, 4.8 OKGE of 17.96 miles. | OKGE | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 OKGE | Rebuild 17.96 miles of 250 Copperweld with 1272 ACSR. | 285 | 335 | 335 | 335 | 17.96 | 30 | 15 |  | 0.00894 | 0.047018 | 0.02948 |  | 859200 | 2006-07-17 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T5802209WP | FROM->TO |  | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 | EXP | ENTR | AEPW | EES-ARK | GRWDAECC | 0 | 99496 | 5DANVI 161.00 | 507195 | MAGZREC5 161.00 | 0 |  | 1 | 09WP | 148 | 148 | 106.1 | 106.0918 | 114.8641 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  | Per MW-Mile files, 47.6% AEPW, 47.6% EES, 4.8 OKGE of 17.96 miles. | OKGE | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 OKGE | Rebuild 17.96 miles of 250 Copperweld with 1272 ACSR. | 285 | 335 | 335 | 335 | 17.96 | 30 | 15 |  | 0.00894 | 0.047018 | 0.02948 |  | 859200 | 2006-07-17 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T13562212SP | FROM->TO |  | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 | EXP | ENTR | AEPW | EES-ARK | GRWDAECC | 0 | 99496 | 5DANVI 161.00 | 507195 | MAGZREC5 161.00 | 0 |  | 1 | 12SP | 127 | 148 | 116.0 | 115.8848 | 127.7453 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  | Per MW-Mile files, 47.6% AEPW, 47.6% EES, 4.8 OKGE of 17.96 miles. | OKGE | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 OKGE | Rebuild 17.96 miles of 250 Copperweld with 1272 ACSR. | 285 | 335 | 335 | 335 | 17.96 | 30 | 15 |  | 0.00894 | 0.047018 | 0.02948 |  | 859200 | 2006-07-17 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T13562212SP | FROM->TO |  | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 | EXP | ENTR | AEPW | EES-ARK | GRWDAECC | 0 | 99496 | 5DANVI 161.00 | 507195 | MAGZREC5 161.00 | 0 |  | 1 | 12SP | 127 | 148 | 116.0 | 115.8848 | 127.7453 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  | Per MW-Mile files, 47.6% AEPW, 47.6% EES, 4.8 OKGE of 17.96 miles. | OKGE | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 OKGE | Rebuild 17.96 miles of 250 Copperweld with 1272 ACSR. | 285 | 335 | 335 | 335 | 17.96 | 30 | 15 |  | 0.00894 | 0.047018 | 0.02948 |  | 859200 | 2006-07-17 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T7462212WP | FROM->TO |  | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 | EXP | ENTR | AEPW | EES-ARK | GRWDAECC | 0 | 99496 | 5DANVI 161.00 | 507195 | MAGZREC5 161.00 | 0 |  | 1 | 12WP | 127 | 148 |  | 93.7537 | 104.7371 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  | Per MW-Mile files, 47.6% AEPW, 47.6% EES, 4.8 OKGE of 17.96 miles. | OKGE | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 OKGE | Rebuild 17.96 miles of 250 Copperweld with 1272 ACSR. | 285 | 335 | 335 | 335 | 17.96 | 30 | 15 |  | 0.00894 | 0.047018 | 0.02948 |  | 859200 | 2006-07-17 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T7462212WP | FROM->TO |  | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 | EXP | ENTR | AEPW | EES-ARK | GRWDAECC | 0 | 99496 | 5DANVI 161.00 | 507195 | MAGZREC5 161.00 | 0 |  | 1 | 12WP | 127 | 148 |  | 93.7537 | 104.7371 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  | Per MW-Mile files, 47.6% AEPW, 47.6% EES, 4.8 OKGE of 17.96 miles. | OKGE | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 OKGE | Rebuild 17.96 miles of 250 Copperweld with 1272 ACSR. | 285 | 335 | 335 | 335 | 17.96 | 30 | 15 |  | 0.00894 | 0.047018 | 0.02948 |  | 859200 | 2006-07-17 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T20512217SP | FROM->TO |  | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 | EXP | ENTR | AEPW | EES-ARK | GRWDAECC | 0 | 99496 | 5DANVI 161.00 | 507195 | MAGZREC5 161.00 | 0 |  | 1 | 17SP | 127 | 148 | 122.8 | 123.2319 | 134.2646 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  | Per MW-Mile files, 47.6% AEPW, 47.6% EES, 4.8 OKGE of 17.96 miles. | OKGE | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 OKGE | Rebuild 17.96 miles of 250 Copperweld with 1272 ACSR. | 285 | 335 | 335 | 335 | 17.96 | 30 | 15 |  | 0.00894 | 0.047018 | 0.02948 |  | 859200 | 2006-07-17 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T20512217SP | FROM->TO |  | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 | EXP | ENTR | AEPW | EES-ARK | GRWDAECC | 0 | 99496 | 5DANVI 161.00 | 507195 | MAGZREC5 161.00 | 0 |  | 1 | 17SP | 127 | 148 | 122.8 | 123.2319 | 134.2646 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  | Per MW-Mile files, 47.6% AEPW, 47.6% EES, 4.8 OKGE of 17.96 miles. | OKGE | DANVILLE (APL) - MAGAZINE REC 161KV CKT 1 OKGE | Rebuild 17.96 miles of 250 Copperweld with 1272 ACSR. | 285 | 335 | 335 | 335 | 17.96 | 30 | 15 |  | 0.00894 | 0.047018 | 0.02948 |  | 859200 | 2006-07-17 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T9442209SP | TO->FROM |  | DARDANELLE - RUSSELLVILLE SOUTH 161KV CKT 1 | S | ENTR | SWPA | EES-ARK | EMINTH | 0 | 99491 | 5RUSL-S 161.00 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 09SP | 335 | 335 |  | 97.183 | 104.953 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | DARDANELLE - RUSSELLVILLE SOUTH 161KV CKT 1 ENTR | Indeterminate | [37 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T13552212SP | TO->FROM |  | DARDANELLE - RUSSELLVILLE SOUTH 161KV CKT 1 | S | ENTR | SWPA | EES-ARK | EMINTH | 0 | 99491 | 5RUSL-S 161.00 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 12SP | 335 | 335 | 103.8 | 104.6725 | 114.0806 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | DARDANELLE - RUSSELLVILLE SOUTH 161KV CKT 1 ENTR | Indeterminate | [37 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T7452212WP | TO->FROM |  | DARDANELLE - RUSSELLVILLE SOUTH 161KV CKT 1 | S | ENTR | SWPA | EES-ARK | EMINTH | 0 | 99491 | 5RUSL-S 161.00 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 12WP | 335 | 335 |  | 91.2793 | 100.5973 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | DARDANELLE - RUSSELLVILLE SOUTH 161KV CKT 1 ENTR | Indeterminate | [37 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T20502217SP | TO->FROM |  | DARDANELLE - RUSSELLVILLE SOUTH 161KV CKT 1 | S | ENTR | SWPA | EES-ARK | EMINTH | 0 | 99491 | 5RUSL-S 161.00 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 17SP | 335 | 335 | 106.2 | 107.6879 | 116.2631 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | DARDANELLE - RUSSELLVILLE SOUTH 161KV CKT 1 ENTR | Indeterminate | [37 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T9442209SP | TO->FROM |  | DARDANELLE - RUSSELLVILLE SOUTH 161KV CKT 1 | EXP | ENTR | SWPA | EES-ARK | EMINTH | 0 | 99491 | 5RUSL-S 161.00 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 09SP | 335 | 335 |  | 97.183 | 104.953 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  |  | SWPA | DARDANELLE - RUSSELLVILLE SOUTH 161KV CKT 1 SWPA | Replace wave trap, disconnect switches, current transformers, and breaker. Bus will limit rating to 1340 amps. | 374 | 374 |  |  |  | 12 | 2 | [5 empty] | 325000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T13552212SP | TO->FROM |  | DARDANELLE - RUSSELLVILLE SOUTH 161KV CKT 1 | EXP | ENTR | SWPA | EES-ARK | EMINTH | 0 | 99491 | 5RUSL-S 161.00 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 12SP | 335 | 335 | 103.8 | 104.6725 | 114.0806 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  |  | SWPA | DARDANELLE - RUSSELLVILLE SOUTH 161KV CKT 1 SWPA | Replace wave trap, disconnect switches, current transformers, and breaker. Bus will limit rating to 1340 amps. | 374 | 374 |  |  |  | 12 | 2 | [5 empty] | 325000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T7452212WP | TO->FROM |  | DARDANELLE - RUSSELLVILLE SOUTH 161KV CKT 1 | EXP | ENTR | SWPA | EES-ARK | EMINTH | 0 | 99491 | 5RUSL-S 161.00 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 12WP | 335 | 335 |  | 91.2793 | 100.5973 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  |  | SWPA | DARDANELLE - RUSSELLVILLE SOUTH 161KV CKT 1 SWPA | Replace wave trap, disconnect switches, current transformers, and breaker. Bus will limit rating to 1340 amps. | 374 | 374 |  |  |  | 12 | 2 | [5 empty] | 325000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T20502217SP | TO->FROM |  | DARDANELLE - RUSSELLVILLE SOUTH 161KV CKT 1 | EXP | ENTR | SWPA | EES-ARK | EMINTH | 0 | 99491 | 5RUSL-S 161.00 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 17SP | 335 | 335 | 106.2 | 107.6879 | 116.2631 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  |  | SWPA | DARDANELLE - RUSSELLVILLE SOUTH 161KV CKT 1 SWPA | Replace wave trap, disconnect switches, current transformers, and breaker. Bus will limit rating to 1340 amps. | 374 | 374 |  |  |  | 12 | 2 | [5 empty] | 325000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T4194317SP | FROM->TO |  | MCDOWELL CREEK SWITCHING STATION - STAGG HILL 115KV CKT 1 | S | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533335 | MCDOWEL3 115.00 | 533341 | STAGGHL3 115.00 | 0 |  | 1 | 17SP | 181 | 181 | 110.5 | 111.0375 | 111.1181 | [6 empty] | CATEGORYB | SINGLE | EAST MANHATTAN - MATTERS CORNER 115KV CKT 1 | 0 | 533326 | EMANHAT3 115.00 | 533334 | MATTERS3 115.00 | 0 |  | 1 |  |  |  |  | WERE | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 Displacement | Uprate JEC- E.Manhattan 230 kV line to 100 deg C operation by raising structures | [12 empty] | 17085937.5 | 2008-01-01 | [23 empty] | 2013-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T4194317SP | FROM->TO |  | MCDOWELL CREEK SWITCHING STATION - STAGG HILL 115KV CKT 1 | S | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533335 | MCDOWEL3 115.00 | 533341 | STAGGHL3 115.00 | 0 |  | 1 | 17SP | 181 | 181 | 110.5 | 111.0375 | 111.1181 | [6 empty] | CATEGORYB | SINGLE | EAST MANHATTAN - MATTERS CORNER 115KV CKT 1 | 0 | 533326 | EMANHAT3 115.00 | 533334 | MATTERS3 115.00 | 0 |  | 1 |  |  |  |  | WERE | EAST MANHATTAN - NW MANHATTAN 230/115KV Displacement | Tap the Concordia - East Manhattan 230kV line and add a new substation"NW Manhattan"; Add a 230kV/115kV transformer and tap the KSU - Wildcat 115kV line into NW Manhattan | [12 empty] | 17437500 | 2008-01-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T4194317SP | FROM->TO |  | MCDOWELL CREEK SWITCHING STATION - STAGG HILL 115KV CKT 1 | S | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533335 | MCDOWEL3 115.00 | 533341 | STAGGHL3 115.00 | 0 |  | 1 | 17SP | 181 | 181 | 110.5 | 111.0375 | 111.1181 | [6 empty] | CATEGORYB | SINGLE | EAST MANHATTAN - MATTERS CORNER 115KV CKT 1 | 0 | 533326 | EMANHAT3 115.00 | 533334 | MATTERS3 115.00 | 0 |  | 1 |  |  |  |  | WERE | EAST MANHATTAN - NW MANHATTAN 230/115KV Displacement | Tap the Concordia - East Manhattan 230kV line and add a new substation"NW Manhattan"; Add a 230kV/115kV transformer and tap the KSU - Wildcat 115kV line into NW Manhattan | [12 empty] | 17437500 | 2008-01-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T4194317SP | FROM->TO |  | MCDOWELL CREEK SWITCHING STATION - STAGG HILL 115KV CKT 1 | S | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533335 | MCDOWEL3 115.00 | 533341 | STAGGHL3 115.00 | 0 |  | 1 | 17SP | 181 | 181 | 110.5 | 111.0375 | 111.1181 | [6 empty] | CATEGORYB | SINGLE | EAST MANHATTAN - MATTERS CORNER 115KV CKT 1 | 0 | 533326 | EMANHAT3 115.00 | 533334 | MATTERS3 115.00 | 0 |  | 1 |  |  |  |  | WERE | EAST MANHATTAN - NW MANHATTAN 230/115KV Displacement | Tap the Concordia - East Manhattan 230kV line and add a new substation"NW Manhattan"; Add a 230kV/115kV transformer and tap the KSU - Wildcat 115kV line into NW Manhattan | [12 empty] | 17437500 | 2008-01-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T4194317SP | FROM->TO |  | MCDOWELL CREEK SWITCHING STATION - STAGG HILL 115KV CKT 1 | S | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533335 | MCDOWEL3 115.00 | 533341 | STAGGHL3 115.00 | 0 |  | 1 | 17SP | 181 | 181 | 110.5 | 111.0375 | 111.1181 | [6 empty] | CATEGORYB | SINGLE | EAST MANHATTAN - MATTERS CORNER 115KV CKT 1 | 0 | 533326 | EMANHAT3 115.00 | 533334 | MATTERS3 115.00 | 0 |  | 1 |  |  |  |  | WERE | East Manhattan to Mcdowell 230 kV Displacement | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 |  | 1000000 | 2007-01-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T7052309SP | FROM->TO |  | LAKE ROAD 161/34.5KV TRANSFORMER CKT 1 | REL | MIPU | MIPU | FLA | FLA | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 1 | 09SP | 66.7 | 83.4 | 109.8 | 109.709 | 177.5051 | 540_Edmond Sub2 | [5 empty] | CATEGORYB | SINGLE | LAKE ROAD 161/34.5KV TRANSFORMER CKT 2 | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 2 |  |  |  |  | MIPU | EDMOND SUB | Add a new 161/34.5 kV Sub at Edmond tapping the Cook to Lake Road 161 kV line | [5 empty] | 18 | [31 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T7052309SP | FROM->TO |  | LAKE ROAD 161/34.5KV TRANSFORMER CKT 1 | REL | MIPU | MIPU | FLA | FLA | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 1 | 09SP | 66.7 | 83.4 | 109.8 | 109.709 | 177.5051 | 540_Edmond Sub2 | [5 empty] | CATEGORYB | SINGLE | LAKE ROAD 161/34.5KV TRANSFORMER CKT 2 | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 2 |  |  |  |  | MIPU | EDMOND SUB | Add a new 161/34.5 kV Sub at Edmond tapping the Cook to Lake Road 161 kV line | [5 empty] | 18 | [31 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T7042309SP | FROM->TO |  | LAKE ROAD 161/34.5KV TRANSFORMER CKT 2 | REL | MIPU | MIPU | FLA | FLA | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 2 | 09SP | 66.7 | 83.4 | 108.9 | 108.9475 | 174.8936 | 540_Edmond Sub2 | [5 empty] | CATEGORYB | SINGLE | LAKE ROAD 161/34.5KV TRANSFORMER CKT 1 | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 1 |  |  |  |  | MIPU | EDMOND SUB | Add a new 161/34.5 kV Sub at Edmond tapping the Cook to Lake Road 161 kV line | [5 empty] | 18 | [31 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T7042309SP | FROM->TO |  | LAKE ROAD 161/34.5KV TRANSFORMER CKT 2 | REL | MIPU | MIPU | FLA | FLA | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 2 | 09SP | 66.7 | 83.4 | 108.9 | 108.9475 | 174.8936 | 540_Edmond Sub2 | [5 empty] | CATEGORYB | SINGLE | LAKE ROAD 161/34.5KV TRANSFORMER CKT 1 | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 1 |  |  |  |  | MIPU | EDMOND SUB | Add a new 161/34.5 kV Sub at Edmond tapping the Cook to Lake Road 161 kV line | [5 empty] | 18 | [31 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T85509SP | FROM->TO |  | LAKE ROAD 161/34.5KV TRANSFORMER CKT 2 | REL | MIPU | MIPU | FLA | FLA | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 2 | 09SP | 66.7 | 83.4 |  | 65.308 | 100.2185 | 540_Edmond Sub2 | [5 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | MIPU | EDMOND SUB | Add a new 161/34.5 kV Sub at Edmond tapping the Cook to Lake Road 161 kV line | [5 empty] | 18 | [31 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T85509SP | FROM->TO |  | LAKE ROAD 161/34.5KV TRANSFORMER CKT 2 | REL | MIPU | MIPU | FLA | FLA | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 2 | 09SP | 66.7 | 83.4 |  | 65.308 | 100.2185 | 540_Edmond Sub2 | [5 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | MIPU | EDMOND SUB | Add a new 161/34.5 kV Sub at Edmond tapping the Cook to Lake Road 161 kV line | [5 empty] | 18 | [31 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T2212309WP | FROM->TO |  | LAKE ROAD 161/34.5KV TRANSFORMER CKT 1 | REL | MIPU | MIPU | FLA | FLA | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 1 | 09WP | 66.7 | 83.4 | 154.9 | 93.169 | 155.1319 | 540_Edmond Sub2 | [5 empty] | CATEGORYB | SINGLE | LAKE ROAD 161/34.5KV TRANSFORMER CKT 2 | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 2 |  |  |  |  | MIPU | EDMOND SUB | Add a new 161/34.5 kV Sub at Edmond tapping the Cook to Lake Road 161 kV line | [5 empty] | 18 | [31 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T2212309WP | FROM->TO |  | LAKE ROAD 161/34.5KV TRANSFORMER CKT 1 | REL | MIPU | MIPU | FLA | FLA | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 1 | 09WP | 66.7 | 83.4 | 154.9 | 93.169 | 155.1319 | 540_Edmond Sub2 | [5 empty] | CATEGORYB | SINGLE | LAKE ROAD 161/34.5KV TRANSFORMER CKT 2 | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 2 |  |  |  |  | MIPU | EDMOND SUB | Add a new 161/34.5 kV Sub at Edmond tapping the Cook to Lake Road 161 kV line | [5 empty] | 18 | [31 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T2202309WP | FROM->TO |  | LAKE ROAD 161/34.5KV TRANSFORMER CKT 2 | REL | MIPU | MIPU | FLA | FLA | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 2 | 09WP | 66.7 | 83.4 | 153.4 | 92.7596 | 153.5423 | 540_Edmond Sub2 | [5 empty] | CATEGORYB | SINGLE | LAKE ROAD 161/34.5KV TRANSFORMER CKT 1 | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 1 |  |  |  |  | MIPU | EDMOND SUB | Add a new 161/34.5 kV Sub at Edmond tapping the Cook to Lake Road 161 kV line | [5 empty] | 18 | [31 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T2202309WP | FROM->TO |  | LAKE ROAD 161/34.5KV TRANSFORMER CKT 2 | REL | MIPU | MIPU | FLA | FLA | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 2 | 09WP | 66.7 | 83.4 | 153.4 | 92.7596 | 153.5423 | 540_Edmond Sub2 | [5 empty] | CATEGORYB | SINGLE | LAKE ROAD 161/34.5KV TRANSFORMER CKT 1 | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 1 |  |  |  |  | MIPU | EDMOND SUB | Add a new 161/34.5 kV Sub at Edmond tapping the Cook to Lake Road 161 kV line | [5 empty] | 18 | [31 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T11062312SP | FROM->TO |  | LAKE ROAD 161/34.5KV TRANSFORMER CKT 1 | REL | MIPU | MIPU | FLA | FLA | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 1 | 12SP | 66.7 | 83.4 | 118.9 | 89.6341 | 190.3521 | 540_Edmond Sub2 | [5 empty] | CATEGORYB | SINGLE | LAKE ROAD 161/34.5KV TRANSFORMER CKT 2 | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 2 |  |  |  |  | MIPU | EDMOND SUB | Add a new 161/34.5 kV Sub at Edmond tapping the Cook to Lake Road 161 kV line | [5 empty] | 18 | [31 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T11062312SP | FROM->TO |  | LAKE ROAD 161/34.5KV TRANSFORMER CKT 1 | REL | MIPU | MIPU | FLA | FLA | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 1 | 12SP | 66.7 | 83.4 | 118.9 | 89.6341 | 190.3521 | 540_Edmond Sub2 | [5 empty] | CATEGORYB | SINGLE | LAKE ROAD 161/34.5KV TRANSFORMER CKT 2 | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 2 |  |  |  |  | MIPU | EDMOND SUB | Add a new 161/34.5 kV Sub at Edmond tapping the Cook to Lake Road 161 kV line | [5 empty] | 18 | [31 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T172312SP | FROM->TO |  | LAKE ROAD 161/34.5KV TRANSFORMER CKT 1 | REL | MIPU | MIPU | FLA | FLA | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 1 | 12SP | 66.7 | 83.4 |  | 52.8137 | 100.7979 | 540_Edmond Sub2 | [5 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | MIPU | EDMOND SUB | Add a new 161/34.5 kV Sub at Edmond tapping the Cook to Lake Road 161 kV line | [5 empty] | 18 | [31 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T172312SP | FROM->TO |  | LAKE ROAD 161/34.5KV TRANSFORMER CKT 1 | REL | MIPU | MIPU | FLA | FLA | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 1 | 12SP | 66.7 | 83.4 |  | 52.8137 | 100.7979 | 540_Edmond Sub2 | [5 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | MIPU | EDMOND SUB | Add a new 161/34.5 kV Sub at Edmond tapping the Cook to Lake Road 161 kV line | [5 empty] | 18 | [31 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T11052312SP | FROM->TO |  | LAKE ROAD 161/34.5KV TRANSFORMER CKT 2 | REL | MIPU | MIPU | FLA | FLA | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 2 | 12SP | 66.7 | 83.4 | 117.9 | 89.1207 | 186.9664 | 540_Edmond Sub2 | [5 empty] | CATEGORYB | SINGLE | LAKE ROAD 161/34.5KV TRANSFORMER CKT 1 | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 1 |  |  |  |  | MIPU | EDMOND SUB | Add a new 161/34.5 kV Sub at Edmond tapping the Cook to Lake Road 161 kV line | [5 empty] | 18 | [31 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T11052312SP | FROM->TO |  | LAKE ROAD 161/34.5KV TRANSFORMER CKT 2 | REL | MIPU | MIPU | FLA | FLA | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 2 | 12SP | 66.7 | 83.4 | 117.9 | 89.1207 | 186.9664 | 540_Edmond Sub2 | [5 empty] | CATEGORYB | SINGLE | LAKE ROAD 161/34.5KV TRANSFORMER CKT 1 | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 1 |  |  |  |  | MIPU | EDMOND SUB | Add a new 161/34.5 kV Sub at Edmond tapping the Cook to Lake Road 161 kV line | [5 empty] | 18 | [31 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T182312SP | FROM->TO |  | LAKE ROAD 161/34.5KV TRANSFORMER CKT 2 | REL | MIPU | MIPU | FLA | FLA | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 2 | 12SP | 66.7 | 83.4 |  | 55.3006 | 105.5444 | 540_Edmond Sub2 | [5 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | MIPU | EDMOND SUB | Add a new 161/34.5 kV Sub at Edmond tapping the Cook to Lake Road 161 kV line | [5 empty] | 18 | [31 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T182312SP | FROM->TO |  | LAKE ROAD 161/34.5KV TRANSFORMER CKT 2 | REL | MIPU | MIPU | FLA | FLA | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 2 | 12SP | 66.7 | 83.4 |  | 55.3006 | 105.5444 | 540_Edmond Sub2 | [5 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | MIPU | EDMOND SUB | Add a new 161/34.5 kV Sub at Edmond tapping the Cook to Lake Road 161 kV line | [5 empty] | 18 | [31 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T3154312WP | FROM->TO |  | LAKE ROAD 161/34.5KV TRANSFORMER CKT 1 | REL | MIPU | MIPU | FLA | FLA | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 1 | 12WP | 66.7 | 83.4 | 165.6 | 165.5538 | 165.6307 | 540_Edmond Sub2 | [5 empty] | CATEGORYB | SINGLE | LAKE ROAD 161/34.5KV TRANSFORMER CKT 2 | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 2 |  |  |  |  | MIPU | EDMOND SUB | Add a new 161/34.5 kV Sub at Edmond tapping the Cook to Lake Road 161 kV line | [5 empty] | 18 | [31 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T3154312WP | FROM->TO |  | LAKE ROAD 161/34.5KV TRANSFORMER CKT 1 | REL | MIPU | MIPU | FLA | FLA | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 1 | 12WP | 66.7 | 83.4 | 165.6 | 165.5538 | 165.6307 | 540_Edmond Sub2 | [5 empty] | CATEGORYB | SINGLE | LAKE ROAD 161/34.5KV TRANSFORMER CKT 2 | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 2 |  |  |  |  | MIPU | EDMOND SUB | Add a new 161/34.5 kV Sub at Edmond tapping the Cook to Lake Road 161 kV line | [5 empty] | 18 | [31 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T3144312WP | FROM->TO |  | LAKE ROAD 161/34.5KV TRANSFORMER CKT 2 | REL | MIPU | MIPU | FLA | FLA | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 2 | 12WP | 66.7 | 83.4 | 163.6 | 163.5939 | 163.6616 | 540_Edmond Sub2 | [5 empty] | CATEGORYB | SINGLE | LAKE ROAD 161/34.5KV TRANSFORMER CKT 1 | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 1 |  |  |  |  | MIPU | EDMOND SUB | Add a new 161/34.5 kV Sub at Edmond tapping the Cook to Lake Road 161 kV line | [5 empty] | 18 | [31 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T3144312WP | FROM->TO |  | LAKE ROAD 161/34.5KV TRANSFORMER CKT 2 | REL | MIPU | MIPU | FLA | FLA | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 2 | 12WP | 66.7 | 83.4 | 163.6 | 163.5939 | 163.6616 | 540_Edmond Sub2 | [5 empty] | CATEGORYB | SINGLE | LAKE ROAD 161/34.5KV TRANSFORMER CKT 1 | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 1 |  |  |  |  | MIPU | EDMOND SUB | Add a new 161/34.5 kV Sub at Edmond tapping the Cook to Lake Road 161 kV line | [5 empty] | 18 | [31 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T17422317SP | FROM->TO |  | LAKE ROAD 161/34.5KV TRANSFORMER CKT 1 | REL | MIPU | MIPU | FLA | FLA | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 1 | 17SP | 66.7 | 83.4 |  | 100.8689 | 130.6724 | 540_Edmond Sub2 | [5 empty] | CATEGORYB | SINGLE | LAKE ROAD 161/34.5KV TRANSFORMER CKT 2 | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 2 |  |  |  |  | MIPU | EDMOND SUB | Add a new 161/34.5 kV Sub at Edmond tapping the Cook to Lake Road 161 kV line | [5 empty] | 18 | [31 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T17422317SP | FROM->TO |  | LAKE ROAD 161/34.5KV TRANSFORMER CKT 1 | REL | MIPU | MIPU | FLA | FLA | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 1 | 17SP | 66.7 | 83.4 |  | 100.8689 | 130.6724 | 540_Edmond Sub2 | [5 empty] | CATEGORYB | SINGLE | LAKE ROAD 161/34.5KV TRANSFORMER CKT 2 | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 2 |  |  |  |  | MIPU | EDMOND SUB | Add a new 161/34.5 kV Sub at Edmond tapping the Cook to Lake Road 161 kV line | [5 empty] | 18 | [31 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T17412317SP | FROM->TO |  | LAKE ROAD 161/34.5KV TRANSFORMER CKT 2 | REL | MIPU | MIPU | FLA | FLA | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 2 | 17SP | 66.7 | 83.4 |  | 100.1891 | 129.3634 | 540_Edmond Sub2 | [5 empty] | CATEGORYB | SINGLE | LAKE ROAD 161/34.5KV TRANSFORMER CKT 1 | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 1 |  |  |  |  | MIPU | EDMOND SUB | Add a new 161/34.5 kV Sub at Edmond tapping the Cook to Lake Road 161 kV line | [5 empty] | 18 | [31 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T17412317SP | FROM->TO |  | LAKE ROAD 161/34.5KV TRANSFORMER CKT 2 | REL | MIPU | MIPU | FLA | FLA | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 2 | 17SP | 66.7 | 83.4 |  | 100.1891 | 129.3634 | 540_Edmond Sub2 | [5 empty] | CATEGORYB | SINGLE | LAKE ROAD 161/34.5KV TRANSFORMER CKT 1 | 0 | 541255 | LAKE RD5 161.00 | 541169 | LAKERD34 34.500 | 0 |  | 1 |  |  |  |  | MIPU | EDMOND SUB | Add a new 161/34.5 kV Sub at Edmond tapping the Cook to Lake Road 161 kV line | [5 empty] | 18 | [31 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T5032217SP | FROM->TO |  | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | EXP | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 | 17SP | 382 | 382 | 111.5 | 110.2383 | 111.0707 | [6 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 |  |  |  |  | WERE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 #2 | Reconductor 8.02 miles with Bundled 1192.5 ACSR | 534 | 586 | [6 empty] | 0.0017 | 0.01907 | 0.01433 | 380k per mile | 3050000 | 2007-01-01 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T28292217SP | FROM->TO |  | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | EXP | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 | 17SP | 382 | 382 | 103.2 | 101.9745 | 102.783 | [6 empty] | CATEGORYB | NONSINGLE | SPP-WERE-30 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 #2 | Reconductor 8.02 miles with Bundled 1192.5 ACSR | 534 | 586 | [6 empty] | 0.0017 | 0.01907 | 0.01433 | 380k per mile | 3050000 | 2007-01-01 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T4982217SP | FROM->TO |  | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | EXP | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 | 17SP | 382 | 382 | 101.6 | 100.6551 | 101.4729 | [6 empty] | CATEGORYB | SINGLE | CHISHOLM - EVANS ENERGY CENTER NORTH 138KV CKT 1 | 0 | 533035 | CHISHLM4 138.00 | 533040 | EVANS N4 138.00 | 0 |  | 1 |  |  |  |  | WERE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 #2 | Reconductor 8.02 miles with Bundled 1192.5 ACSR | 534 | 586 | [6 empty] | 0.0017 | 0.01907 | 0.01433 | 380k per mile | 3050000 | 2007-01-01 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T2344412SP | FROM->TO |  | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | S | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 | 12SP | 382 | 382 |  | 98.6325 | 100.7427 | [6 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 |  |  |  |  | WERE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 Displacement | Replace Disconnect Switches, Wavetrap, Breaker, Jumpers | 382 | 414 | 382 | 414 | [8 empty] | 200000 | 2007-01-01 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T5032217SP | FROM->TO |  | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | S | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 | 17SP | 382 | 382 | 111.5 | 110.2383 | 111.0707 | [6 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 |  |  |  |  | WERE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 Displacement | Replace Disconnect Switches, Wavetrap, Breaker, Jumpers | 382 | 414 | 382 | 414 | [8 empty] | 200000 | 2007-01-01 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T28292217SP | FROM->TO |  | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | S | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 | 17SP | 382 | 382 | 103.2 | 101.9745 | 102.783 | [6 empty] | CATEGORYB | NONSINGLE | SPP-WERE-30 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 Displacement | Replace Disconnect Switches, Wavetrap, Breaker, Jumpers | 382 | 414 | 382 | 414 | [8 empty] | 200000 | 2007-01-01 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T4982217SP | FROM->TO |  | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | S | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 | 17SP | 382 | 382 | 101.6 | 100.6551 | 101.4729 | [6 empty] | CATEGORYB | SINGLE | CHISHOLM - EVANS ENERGY CENTER NORTH 138KV CKT 1 | 0 | 533035 | CHISHLM4 138.00 | 533040 | EVANS N4 138.00 | 0 |  | 1 |  |  |  |  | WERE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 Displacement | Replace Disconnect Switches, Wavetrap, Breaker, Jumpers | 382 | 414 | 382 | 414 | [8 empty] | 200000 | 2007-01-01 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1862208WP | FROM->TO |  | EVERTON - HARRISON-EAST 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99843 | 5EVRTON 161.00 | 99811 | 5HARR-E 161.00 | 0 |  | 1 | 08WP | 167 | 167 | 108.1 | 107.069 | 109.8152 | [6 empty] | CATEGORYB | SINGLE | BULL SHOALS - BULL SHOALS 161KV CKT 1 | 0 | 505460 | BULL SH5 161.00 | 99802 | 5BULLSH* 161.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | EVERTON - HARRISON-EAST 161KV CKT 1 | Indeterminate | [37 empty] | 2008-12-01 | 2008-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1572208WP | FROM->TO |  | EVERTON - HARRISON-EAST 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99843 | 5EVRTON 161.00 | 99811 | 5HARR-E 161.00 | 0 |  | 1 | 08WP | 167 | 167 | 106.9 | 105.8448 | 108.6057 | [6 empty] | CATEGORYB | SINGLE | 5FLIPN - BULL SHOALS HES 161KV CKT 1 | 0 | 99802 | 5BULLSH* 161.00 | 99809 | 5FLIPN 161.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | EVERTON - HARRISON-EAST 161KV CKT 1 | Indeterminate | [37 empty] | 2008-12-01 | 2008-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1592208WP | FROM->TO |  | EVERTON - HARRISON-EAST 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99843 | 5EVRTON 161.00 | 99811 | 5HARR-E 161.00 | 0 |  | 1 | 08WP | 167 | 167 | 104.2 | 103.0898 | 105.8562 | [6 empty] | CATEGORYB | SINGLE | FLIPPIN - SUMMIT 161KV CKT 1 | 0 | 99809 | 5FLIPN 161.00 | 99837 | 5SUMMIT 161.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | EVERTON - HARRISON-EAST 161KV CKT 1 | Indeterminate | [37 empty] | 2008-12-01 | 2008-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T7622209SP | FROM->TO |  | EVERTON - HARRISON-EAST 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99843 | 5EVRTON 161.00 | 99811 | 5HARR-E 161.00 | 0 |  | 1 | 09SP | 167 | 167 | 111.6 | 110.263 | 120.2327 | [6 empty] | CATEGORYB | SINGLE | BULL SHOALS - BULL SHOALS 161KV CKT 1 | 0 | 505460 | BULL SH5 161.00 | 99802 | 5BULLSH* 161.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | EVERTON - HARRISON-EAST 161KV CKT 1 | Indeterminate | [37 empty] | 2008-12-01 | 2008-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T6882209SP | FROM->TO |  | EVERTON - HARRISON-EAST 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99843 | 5EVRTON 161.00 | 99811 | 5HARR-E 161.00 | 0 |  | 1 | 09SP | 167 | 167 | 110.0 | 108.799 | 118.5481 | [6 empty] | CATEGORYB | SINGLE | 5FLIPN - BULL SHOALS HES 161KV CKT 1 | 0 | 99802 | 5BULLSH* 161.00 | 99809 | 5FLIPN 161.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | EVERTON - HARRISON-EAST 161KV CKT 1 | Indeterminate | [37 empty] | 2008-12-01 | 2008-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T6952209SP | FROM->TO |  | EVERTON - HARRISON-EAST 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99843 | 5EVRTON 161.00 | 99811 | 5HARR-E 161.00 | 0 |  | 1 | 09SP | 167 | 167 | 106.4 | 105.1725 | 115.0519 | [6 empty] | CATEGORYB | SINGLE | FLIPPIN - SUMMIT 161KV CKT 1 | 0 | 99809 | 5FLIPN 161.00 | 99837 | 5SUMMIT 161.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | EVERTON - HARRISON-EAST 161KV CKT 1 | Indeterminate | [37 empty] | 2008-12-01 | 2008-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T4252209WP | FROM->TO |  | EVERTON - HARRISON-EAST 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99843 | 5EVRTON 161.00 | 99811 | 5HARR-E 161.00 | 0 |  | 1 | 09WP | 167 | 167 | 109.9 | 108.4606 | 117.9982 | [6 empty] | CATEGORYB | SINGLE | BULL SHOALS - BULL SHOALS 161KV CKT 1 | 0 | 505460 | BULL SH5 161.00 | 99802 | 5BULLSH* 161.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | EVERTON - HARRISON-EAST 161KV CKT 1 | Indeterminate | [37 empty] | 2008-12-01 | 2008-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T3412209WP | FROM->TO |  | EVERTON - HARRISON-EAST 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99843 | 5EVRTON 161.00 | 99811 | 5HARR-E 161.00 | 0 |  | 1 | 09WP | 167 | 167 | 108.7 | 107.2629 | 116.8179 | [6 empty] | CATEGORYB | SINGLE | 5FLIPN - BULL SHOALS HES 161KV CKT 1 | 0 | 99802 | 5BULLSH* 161.00 | 99809 | 5FLIPN 161.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | EVERTON - HARRISON-EAST 161KV CKT 1 | Indeterminate | [37 empty] | 2008-12-01 | 2008-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T3502209WP | FROM->TO |  | EVERTON - HARRISON-EAST 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99843 | 5EVRTON 161.00 | 99811 | 5HARR-E 161.00 | 0 |  | 1 | 09WP | 167 | 167 | 105.9 | 104.4391 | 114.07 | [6 empty] | CATEGORYB | SINGLE | FLIPPIN - SUMMIT 161KV CKT 1 | 0 | 99809 | 5FLIPN 161.00 | 99837 | 5SUMMIT 161.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | EVERTON - HARRISON-EAST 161KV CKT 1 | Indeterminate | [37 empty] | 2008-12-01 | 2008-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T11342212SP | FROM->TO |  | EVERTON - HARRISON-EAST 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99843 | 5EVRTON 161.00 | 99811 | 5HARR-E 161.00 | 0 |  | 1 | 12SP | 167 | 167 | 124.5 | 122.9389 | 135.007 | [6 empty] | CATEGORYB | SINGLE | BULL SHOALS - BULL SHOALS 161KV CKT 1 | 0 | 505460 | BULL SH5 161.00 | 99802 | 5BULLSH* 161.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | EVERTON - HARRISON-EAST 161KV CKT 1 | Indeterminate | [37 empty] | 2008-12-01 | 2008-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T10382212SP | FROM->TO |  | EVERTON - HARRISON-EAST 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99843 | 5EVRTON 161.00 | 99811 | 5HARR-E 161.00 | 0 |  | 1 | 12SP | 167 | 167 | 122.9 | 121.2927 | 133.3629 | [6 empty] | CATEGORYB | SINGLE | 5FLIPN - BULL SHOALS HES 161KV CKT 1 | 0 | 99802 | 5BULLSH* 161.00 | 99809 | 5FLIPN 161.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | EVERTON - HARRISON-EAST 161KV CKT 1 | Indeterminate | [37 empty] | 2008-12-01 | 2008-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T10502212SP | FROM->TO |  | EVERTON - HARRISON-EAST 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99843 | 5EVRTON 161.00 | 99811 | 5HARR-E 161.00 | 0 |  | 1 | 12SP | 167 | 167 | 118.7 | 117.1319 | 129.1597 | [6 empty] | CATEGORYB | SINGLE | FLIPPIN - SUMMIT 161KV CKT 1 | 0 | 99809 | 5FLIPN 161.00 | 99837 | 5SUMMIT 161.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | EVERTON - HARRISON-EAST 161KV CKT 1 | Indeterminate | [37 empty] | 2008-12-01 | 2008-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T5832212WP | FROM->TO |  | EVERTON - HARRISON-EAST 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99843 | 5EVRTON 161.00 | 99811 | 5HARR-E 161.00 | 0 |  | 1 | 12WP | 167 | 167 | 117.8 | 114.0705 | 125.2009 | [6 empty] | CATEGORYB | SINGLE | BULL SHOALS - BULL SHOALS 161KV CKT 1 | 0 | 505460 | BULL SH5 161.00 | 99802 | 5BULLSH* 161.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | EVERTON - HARRISON-EAST 161KV CKT 1 | Indeterminate | [37 empty] | 2008-12-01 | 2008-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T4992212WP | FROM->TO |  | EVERTON - HARRISON-EAST 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99843 | 5EVRTON 161.00 | 99811 | 5HARR-E 161.00 | 0 |  | 1 | 12WP | 167 | 167 | 116.6 | 112.8587 | 123.9756 | [6 empty] | CATEGORYB | SINGLE | 5FLIPN - BULL SHOALS HES 161KV CKT 1 | 0 | 99802 | 5BULLSH* 161.00 | 99809 | 5FLIPN 161.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | EVERTON - HARRISON-EAST 161KV CKT 1 | Indeterminate | [37 empty] | 2008-12-01 | 2008-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T5072212WP | FROM->TO |  | EVERTON - HARRISON-EAST 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99843 | 5EVRTON 161.00 | 99811 | 5HARR-E 161.00 | 0 |  | 1 | 12WP | 167 | 167 | 113.5 | 109.8011 | 120.872 | [6 empty] | CATEGORYB | SINGLE | FLIPPIN - SUMMIT 161KV CKT 1 | 0 | 99809 | 5FLIPN 161.00 | 99837 | 5SUMMIT 161.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | EVERTON - HARRISON-EAST 161KV CKT 1 | Indeterminate | [37 empty] | 2008-12-01 | 2008-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T17052417SP | FROM->TO |  | EVERTON - HARRISON-EAST 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99843 | 5EVRTON 161.00 | 99811 | 5HARR-E 161.00 | 0 |  | 1 | 17SP | 167 | 167 | 126.5 | 122.3 | 134.3246 | [6 empty] | CATEGORYB | SINGLE | BULL SHOALS - BULL SHOALS 161KV CKT 1 | 0 | 505460 | BULL SH5 161.00 | 99802 | 5BULLSH* 161.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | EVERTON - HARRISON-EAST 161KV CKT 1 | Indeterminate | [37 empty] | 2008-12-01 | 2008-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T16052417SP | FROM->TO |  | EVERTON - HARRISON-EAST 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99843 | 5EVRTON 161.00 | 99811 | 5HARR-E 161.00 | 0 |  | 1 | 17SP | 167 | 167 | 124.7 | 120.5507 | 132.4916 | [6 empty] | CATEGORYB | SINGLE | 5FLIPN - BULL SHOALS HES 161KV CKT 1 | 0 | 99802 | 5BULLSH* 161.00 | 99809 | 5FLIPN 161.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | EVERTON - HARRISON-EAST 161KV CKT 1 | Indeterminate | [37 empty] | 2008-12-01 | 2008-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T16162417SP | FROM->TO |  | EVERTON - HARRISON-EAST 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99843 | 5EVRTON 161.00 | 99811 | 5HARR-E 161.00 | 0 |  | 1 | 17SP | 167 | 167 | 119.9 | 115.9272 | 127.8345 | [6 empty] | CATEGORYB | SINGLE | FLIPPIN - SUMMIT 161KV CKT 1 | 0 | 99809 | 5FLIPN 161.00 | 99837 | 5SUMMIT 161.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | EVERTON - HARRISON-EAST 161KV CKT 1 | Indeterminate | [37 empty] | 2008-12-01 | 2008-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4522317SP | FROM->TO |  | FARMERS CONSUMER CO-OP - WAKARUSA JUNCTION SWITCHING STATION 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533236 | COOP 3 115.00 | 533277 | WAKARUS3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 106.1 | 105.7697 | 113.0438 | [6 empty] | CATEGORYB | SINGLE | SOUTHWEST LAWRENCE - WAKARUSA JUNCTION SWITCHING STATION 115KV CKT 1 | 0 | 533271 | SWLWRNC3 115.00 | 533277 | WAKARUS3 115.00 | 0 |  | 1 |  |  |  |  | WERE | FARMERS CONSUMER CO-OP - WAKARUSA JUNCTION SWITCHING STATION 115KV CKT 1 | Rebuild 1.53-mile Co-op-Wakarusa 115 kV line. | 223 | 240 | 223 | 240 | 1.53 | 12 | 5 |  | 0.00093 | 0.0085 | 0.00119 | Breaker and CT limit is 240 MVA. | 520000 | 2006-07-25 | [23 empty] | 2017-06-01 | 2017-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T14202212SP | FROM->TO |  | LITCHFIELD - PITNAC 69KV CKT 1 | EXP | WERE | WERE | SEAST | SEAST | 0 | 533765 | LITCH 2 69.000 | 533769 | PITNAC 2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | 90.6748 | 121.1532 | [6 empty] | CATEGORYB | SINGLE | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 |  |  |  |  | WERE | Fort Scott - SW Bourbon 161 kV | Tap Litchfield-Marmaton 161 kV with new SW Bourbon Sub to Ft Scott, and new 161/69 kV transformer at Ft Scott. | [5 empty] | 18 | 18 | [30 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T14212212SP | TO->FROM |  | MULBERRY - PITNAC 69KV CKT 1 | EXP | WERE | WERE | SEAST | SEAST | 0 | 533769 | PITNAC 2 69.000 | 533767 | MULBERY2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | 78.1767 | 108.1009 | [6 empty] | CATEGORYB | SINGLE | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 |  |  |  |  | WERE | Fort Scott - SW Bourbon 161 kV | Tap Litchfield-Marmaton 161 kV with new SW Bourbon Sub to Ft Scott, and new 161/69 kV transformer at Ft Scott. | [5 empty] | 18 | 18 | [30 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T21372217SP | FROM->TO |  | LITCHFIELD - PITNAC 69KV CKT 1 | EXP | WERE | WERE | SEAST | SEAST | 0 | 533765 | LITCH 2 69.000 | 533769 | PITNAC 2 69.000 | 0 |  | 1 | 17SP | 72 | 72 |  | 97.5972 | 120.7746 | [6 empty] | CATEGORYB | SINGLE | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 |  |  |  |  | WERE | Fort Scott - SW Bourbon 161 kV | Tap Litchfield-Marmaton 161 kV with new SW Bourbon Sub to Ft Scott, and new 161/69 kV transformer at Ft Scott. | [5 empty] | 18 | 18 | [30 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T21382217SP | TO->FROM |  | MULBERRY - PITNAC 69KV CKT 1 | EXP | WERE | WERE | SEAST | SEAST | 0 | 533769 | PITNAC 2 69.000 | 533767 | MULBERY2 69.000 | 0 |  | 1 | 17SP | 72 | 72 |  | 83.2407 | 106.2067 | [6 empty] | CATEGORYB | SINGLE | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 |  |  |  |  | WERE | Fort Scott - SW Bourbon 161 kV | Tap Litchfield-Marmaton 161 kV with new SW Bourbon Sub to Ft Scott, and new 161/69 kV transformer at Ft Scott. | [5 empty] | 18 | 18 | [30 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T4362117SP | FROM->TO |  | GILL ENERGY CENTER EAST - INTERSTATE 138KV CKT 1 | EXP | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533044 | GILL E 4 138.00 | 533051 | INTERST4 138.00 | 0 |  | 1 | 17SP | 191 | 210 | 104.4 | 104.4054 | 104.8552 | [6 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  |  | WERE | GILL ENERGY CENTER EAST - INTERSTATE 138KV CKT 1 | Replace wave trap | 232 | 232 | 232 | 232 |  | 6 | 1 | N | [29 empty] | 2016-06-01 | 2016-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T751108SH | TO->FROM |  | GRANDVIEW EAST - MARTIN CITY 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541210 | MARTCTY5 161.00 | 541223 | GRDVWE 5 161.00 | 0 |  | 1 | 08SH | 223 | 223 | 108.3 | 108.5772 | 111.6791 | 540_GRANDVIEW EAST - MARTIN CITY 161KV CKT 1-Reconductor | [5 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | GRANDVIEW EAST - MARTIN CITY 161KV CKT 1 #2 | Reconductor to Bundled Drake | 466 | 558 |  |  | 4.9 | 18 |  |  | 0.00121 | 0.01071 | 0.00937 |  | 4700000 | [24 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T5021108SH | TO->FROM |  | GRANDVIEW EAST - MARTIN CITY 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541210 | MARTCTY5 161.00 | 541223 | GRDVWE 5 161.00 | 0 |  | 1 | 08SH | 223 | 223 | 109.0 | 109.0635 | 110.9823 | 540_GRANDVIEW EAST - MARTIN CITY 161KV CKT 1-Reconductor | [5 empty] | CATEGORYB | SINGLE | PLEASANT HILL () 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 541200 | PHILL 7 345.00 | 541225 | PHILL 5 161.00 | 541361 | PHILL T 13.800 | 1 |  |  |  |  | MIPU | GRANDVIEW EAST - MARTIN CITY 161KV CKT 1 #2 | Reconductor to Bundled Drake | 466 | 558 |  |  | 4.9 | 18 |  |  | 0.00121 | 0.01071 | 0.00937 |  | 4700000 | [24 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T6875508SP | TO->FROM |  | GRANDVIEW EAST - MARTIN CITY 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541210 | MARTCTY5 161.00 | 541223 | GRDVWE 5 161.00 | 0 |  | 1 | 08SP | 223 | 223 | 112.9 | 113.7504 | 112.6331 | 540_GRANDVIEW EAST - MARTIN CITY 161KV CKT 1-Reconductor | [5 empty] | CATEGORYB | SINGLE | PLEASANT HILL () 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 541200 | PHILL 7 345.00 | 541225 | PHILL 5 161.00 | 541361 | PHILL T 13.800 | 1 |  |  |  |  | MIPU | GRANDVIEW EAST - MARTIN CITY 161KV CKT 1 #2 | Reconductor to Bundled Drake | 466 | 558 |  |  | 4.9 | 18 |  |  | 0.00121 | 0.01071 | 0.00937 |  | 4700000 | [24 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T2055508SP | TO->FROM |  | GRANDVIEW EAST - MARTIN CITY 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541210 | MARTCTY5 161.00 | 541223 | GRDVWE 5 161.00 | 0 |  | 1 | 08SP | 223 | 223 |  | 100.7239 | 101.0416 | 540_GRANDVIEW EAST - MARTIN CITY 161KV CKT 1-Reconductor | [5 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | GRANDVIEW EAST - MARTIN CITY 161KV CKT 1 #2 | Reconductor to Bundled Drake | 466 | 558 |  |  | 4.9 | 18 |  |  | 0.00121 | 0.01071 | 0.00937 |  | 4700000 | [24 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T2075508SP | TO->FROM |  | GRANDVIEW EAST - MARTIN CITY 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541210 | MARTCTY5 161.00 | 541223 | GRDVWE 5 161.00 | 0 |  | 1 | 08SP | 223 | 223 | 100.8 | 101.1983 | 100.6092 | 540_GRANDVIEW EAST - MARTIN CITY 161KV CKT 1-Reconductor | [5 empty] | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEY 161KV CKT 1 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | GRANDVIEW EAST - MARTIN CITY 161KV CKT 1 #2 | Reconductor to Bundled Drake | 466 | 558 |  |  | 4.9 | 18 |  |  | 0.00121 | 0.01071 | 0.00937 |  | 4700000 | [24 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T6742109SP | TO->FROM |  | GRANDVIEW EAST - MARTIN CITY 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541210 | MARTCTY5 161.00 | 541223 | GRDVWE 5 161.00 | 0 |  | 1 | 09SP | 223 | 223 |  | 84.5433 | 124.7698 | 540_GRANDVIEW EAST - MARTIN CITY 161KV CKT 1-Reconductor | [5 empty] | CATEGORYB | SINGLE | PLEASANT HILL () 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 541200 | PHILL 7 345.00 | 541225 | PHILL 5 161.00 | 541361 | PHILL T 13.800 | 1 |  |  |  |  | MIPU | GRANDVIEW EAST - MARTIN CITY 161KV CKT 1 #2 | Reconductor to Bundled Drake | 466 | 558 |  |  | 4.9 | 18 |  |  | 0.00121 | 0.01071 | 0.00937 |  | 4700000 | [24 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1732109SP | TO->FROM |  | GRANDVIEW EAST - MARTIN CITY 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541210 | MARTCTY5 161.00 | 541223 | GRDVWE 5 161.00 | 0 |  | 1 | 09SP | 223 | 223 |  | 92.7623 | 120.82 | 540_GRANDVIEW EAST - MARTIN CITY 161KV CKT 1-Reconductor | [5 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | GRANDVIEW EAST - MARTIN CITY 161KV CKT 1 #2 | Reconductor to Bundled Drake | 466 | 558 |  |  | 4.9 | 18 |  |  | 0.00121 | 0.01071 | 0.00937 |  | 4700000 | [24 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1772109SP | TO->FROM |  | GRANDVIEW EAST - MARTIN CITY 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541210 | MARTCTY5 161.00 | 541223 | GRDVWE 5 161.00 | 0 |  | 1 | 09SP | 223 | 223 |  | 79.0906 | 108.7443 | 540_GRANDVIEW EAST - MARTIN CITY 161KV CKT 1-Reconductor | [5 empty] | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEY 161KV CKT 1 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | GRANDVIEW EAST - MARTIN CITY 161KV CKT 1 #2 | Reconductor to Bundled Drake | 466 | 558 |  |  | 4.9 | 18 |  |  | 0.00121 | 0.01071 | 0.00937 |  | 4700000 | [24 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T9464312SP | TO->FROM |  | GRANDVIEW EAST - MARTIN CITY 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541210 | MARTCTY5 161.00 | 541223 | GRDVWE 5 161.00 | 0 |  | 1 | 12SP | 223 | 223 | 128.2 | 132.9719 | 136.0172 | 540_GRANDVIEW EAST - MARTIN CITY 161KV CKT 1-Reconductor | [5 empty] | CATEGORYB | SINGLE | PLEASANT HILL () 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 541200 | PHILL 7 345.00 | 541225 | PHILL 5 161.00 | 541361 | PHILL T 13.800 | 1 |  |  |  |  | MIPU | GRANDVIEW EAST - MARTIN CITY 161KV CKT 1 #2 | Reconductor to Bundled Drake | 466 | 558 |  |  | 4.9 | 18 |  |  | 0.00121 | 0.01071 | 0.00937 |  | 4700000 | [24 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T2934312SP | TO->FROM |  | GRANDVIEW EAST - MARTIN CITY 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541210 | MARTCTY5 161.00 | 541223 | GRDVWE 5 161.00 | 0 |  | 1 | 12SP | 223 | 223 | 114.5 | 117.2896 | 119.5001 | 540_GRANDVIEW EAST - MARTIN CITY 161KV CKT 1-Reconductor | [5 empty] | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEY 161KV CKT 1 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | GRANDVIEW EAST - MARTIN CITY 161KV CKT 1 #2 | Reconductor to Bundled Drake | 466 | 558 |  |  | 4.9 | 18 |  |  | 0.00121 | 0.01071 | 0.00937 |  | 4700000 | [24 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T2874312SP | TO->FROM |  | GRANDVIEW EAST - MARTIN CITY 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541210 | MARTCTY5 161.00 | 541223 | GRDVWE 5 161.00 | 0 |  | 1 | 12SP | 223 | 223 | 111.4 | 114.8523 | 118.9758 | 540_GRANDVIEW EAST - MARTIN CITY 161KV CKT 1-Reconductor | [5 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | GRANDVIEW EAST - MARTIN CITY 161KV CKT 1 #2 | Reconductor to Bundled Drake | 466 | 558 |  |  | 4.9 | 18 |  |  | 0.00121 | 0.01071 | 0.00937 |  | 4700000 | [24 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T3724112WP | TO->FROM |  | GRANDVIEW EAST - MARTIN CITY 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541210 | MARTCTY5 161.00 | 541223 | GRDVWE 5 161.00 | 0 |  | 1 | 12WP | 223 | 245 | 111.0 | 110.6456 | 112.7936 | 540_GRANDVIEW EAST - MARTIN CITY 161KV CKT 1-Reconductor | [5 empty] | CATEGORYB | SINGLE | PLEASANT HILL () 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 541200 | PHILL 7 345.00 | 541225 | PHILL 5 161.00 | 541361 | PHILL T 13.800 | 1 |  |  |  |  | MIPU | GRANDVIEW EAST - MARTIN CITY 161KV CKT 1 #2 | Reconductor to Bundled Drake | 466 | 558 |  |  | 4.9 | 18 |  |  | 0.00121 | 0.01071 | 0.00937 |  | 4700000 | [24 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T764112WP | TO->FROM |  | GRANDVIEW EAST - MARTIN CITY 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541210 | MARTCTY5 161.00 | 541223 | GRDVWE 5 161.00 | 0 |  | 1 | 12WP | 223 | 245 | 110.8 | 110.6222 | 112.7813 | 540_GRANDVIEW EAST - MARTIN CITY 161KV CKT 1-Reconductor | [5 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | GRANDVIEW EAST - MARTIN CITY 161KV CKT 1 #2 | Reconductor to Bundled Drake | 466 | 558 |  |  | 4.9 | 18 |  |  | 0.00121 | 0.01071 | 0.00937 |  | 4700000 | [24 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T17232317SP | TO->FROM |  | GRANDVIEW EAST - MARTIN CITY 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541210 | MARTCTY5 161.00 | 541223 | GRDVWE 5 161.00 | 0 |  | 1 | 17SP | 223 | 223 |  | 93.6935 | 138.3669 | 540_GRANDVIEW EAST - MARTIN CITY 161KV CKT 1-Reconductor | [5 empty] | CATEGORYB | SINGLE | PLEASANT HILL () 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 541200 | PHILL 7 345.00 | 541225 | PHILL 5 161.00 | 541361 | PHILL T 13.800 | 1 |  |  |  |  | MIPU | GRANDVIEW EAST - MARTIN CITY 161KV CKT 1 #2 | Reconductor to Bundled Drake | 466 | 558 |  |  | 4.9 | 18 |  |  | 0.00121 | 0.01071 | 0.00937 |  | 4700000 | [24 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T5442317SP | TO->FROM |  | GRANDVIEW EAST - MARTIN CITY 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541210 | MARTCTY5 161.00 | 541223 | GRDVWE 5 161.00 | 0 |  | 1 | 17SP | 223 | 223 |  | 86.838 | 122.9222 | 540_GRANDVIEW EAST - MARTIN CITY 161KV CKT 1-Reconductor | [5 empty] | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEY 161KV CKT 1 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | GRANDVIEW EAST - MARTIN CITY 161KV CKT 1 #2 | Reconductor to Bundled Drake | 466 | 558 |  |  | 4.9 | 18 |  |  | 0.00121 | 0.01071 | 0.00937 |  | 4700000 | [24 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T5662317SP | TO->FROM |  | GRANDVIEW EAST - MARTIN CITY 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541210 | MARTCTY5 161.00 | 541223 | GRDVWE 5 161.00 | 0 |  | 1 | 17SP | 223 | 223 | 105.6 | 92.192 | 121.2412 | 540_GRANDVIEW EAST - MARTIN CITY 161KV CKT 1-Reconductor | [5 empty] | CATEGORYB | SINGLE | LAKE WINNEBAGO - PLEASANT HILL 161KV CKT 1 | 0 | 541225 | PHILL 5 161.00 | 541243 | LKWINGB5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | GRANDVIEW EAST - MARTIN CITY 161KV CKT 1 #2 | Reconductor to Bundled Drake | 466 | 558 |  |  | 4.9 | 18 |  |  | 0.00121 | 0.01071 | 0.00937 |  | 4700000 | [24 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T6752109SP | FROM->TO |  | GRANDVIEW EAST - SAMPSON 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541223 | GRDVWE 5 161.00 | 541345 | SAMPSON5 161.00 | 0 |  | 1 | 09SP | 223 | 245 |  | 63.9117 | 100.2157 | 540_GRANDVIEW EAST - SAMPSON 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | PLEASANT HILL () 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 541200 | PHILL 7 345.00 | 541225 | PHILL 5 161.00 | 541361 | PHILL T 13.800 | 1 |  |  |  |  | MIPU | GRANDVIEW EAST - SAMPSON 161KV CKT 1 # 1 | Replace wavetraps | 233 | 265 | [10 empty] | 180000 | [24 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T6752109SP | FROM->TO |  | GRANDVIEW EAST - SAMPSON 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541223 | GRDVWE 5 161.00 | 541345 | SAMPSON5 161.00 | 0 |  | 1 | 09SP | 223 | 245 |  | 63.9117 | 100.2157 | 540_GRANDVIEW EAST - SAMPSON 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | PLEASANT HILL () 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 541200 | PHILL 7 345.00 | 541225 | PHILL 5 161.00 | 541361 | PHILL T 13.800 | 1 |  |  |  |  | MIPU | GRANDVIEW EAST - SAMPSON 161KV CKT 1 # 1 | Replace wavetraps | 233 | 265 | [10 empty] | 180000 | [24 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T9484312SP | FROM->TO |  | GRANDVIEW EAST - SAMPSON 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541223 | GRDVWE 5 161.00 | 541345 | SAMPSON5 161.00 | 0 |  | 1 | 12SP | 223 | 245 | 101.7 | 106.0536 | 108.8194 | 540_GRANDVIEW EAST - SAMPSON 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | PLEASANT HILL () 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 541200 | PHILL 7 345.00 | 541225 | PHILL 5 161.00 | 541361 | PHILL T 13.800 | 1 |  |  |  |  | MIPU | GRANDVIEW EAST - SAMPSON 161KV CKT 1 # 1 | Replace wavetraps | 233 | 265 | [10 empty] | 180000 | [24 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T9484312SP | FROM->TO |  | GRANDVIEW EAST - SAMPSON 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541223 | GRDVWE 5 161.00 | 541345 | SAMPSON5 161.00 | 0 |  | 1 | 12SP | 223 | 245 | 101.7 | 106.0536 | 108.8194 | 540_GRANDVIEW EAST - SAMPSON 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | PLEASANT HILL () 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 541200 | PHILL 7 345.00 | 541225 | PHILL 5 161.00 | 541361 | PHILL T 13.800 | 1 |  |  |  |  | MIPU | GRANDVIEW EAST - SAMPSON 161KV CKT 1 # 1 | Replace wavetraps | 233 | 265 | [10 empty] | 180000 | [24 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T784112WP | FROM->TO |  | GRANDVIEW EAST - SAMPSON 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541223 | GRDVWE 5 161.00 | 541345 | SAMPSON5 161.00 | 0 |  | 1 | 12WP | 223 | 245 | 100.5 | 100.32 | 102.4633 | 540_GRANDVIEW EAST - SAMPSON 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | GRANDVIEW EAST - SAMPSON 161KV CKT 1 # 1 | Replace wavetraps | 233 | 265 | [10 empty] | 180000 | [24 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T784112WP | FROM->TO |  | GRANDVIEW EAST - SAMPSON 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541223 | GRDVWE 5 161.00 | 541345 | SAMPSON5 161.00 | 0 |  | 1 | 12WP | 223 | 245 | 100.5 | 100.32 | 102.4633 | 540_GRANDVIEW EAST - SAMPSON 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | GRANDVIEW EAST - SAMPSON 161KV CKT 1 # 1 | Replace wavetraps | 233 | 265 | [10 empty] | 180000 | [24 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T3734112WP | FROM->TO |  | GRANDVIEW EAST - SAMPSON 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541223 | GRDVWE 5 161.00 | 541345 | SAMPSON5 161.00 | 0 |  | 1 | 12WP | 223 | 245 | 100.3 | 99.9581 | 102.0819 | 540_GRANDVIEW EAST - SAMPSON 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | PLEASANT HILL () 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 541200 | PHILL 7 345.00 | 541225 | PHILL 5 161.00 | 541361 | PHILL T 13.800 | 1 |  |  |  |  | MIPU | GRANDVIEW EAST - SAMPSON 161KV CKT 1 # 1 | Replace wavetraps | 233 | 265 | [10 empty] | 180000 | [24 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T3734112WP | FROM->TO |  | GRANDVIEW EAST - SAMPSON 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541223 | GRDVWE 5 161.00 | 541345 | SAMPSON5 161.00 | 0 |  | 1 | 12WP | 223 | 245 | 100.3 | 99.9581 | 102.0819 | 540_GRANDVIEW EAST - SAMPSON 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | PLEASANT HILL () 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 541200 | PHILL 7 345.00 | 541225 | PHILL 5 161.00 | 541361 | PHILL T 13.800 | 1 |  |  |  |  | MIPU | GRANDVIEW EAST - SAMPSON 161KV CKT 1 # 1 | Replace wavetraps | 233 | 265 | [10 empty] | 180000 | [24 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T17242317SP | FROM->TO |  | GRANDVIEW EAST - SAMPSON 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541223 | GRDVWE 5 161.00 | 541345 | SAMPSON5 161.00 | 0 |  | 1 | 17SP | 223 | 245 |  | 71.2897 | 108.8762 | 540_GRANDVIEW EAST - SAMPSON 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | PLEASANT HILL () 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 541200 | PHILL 7 345.00 | 541225 | PHILL 5 161.00 | 541361 | PHILL T 13.800 | 1 |  |  |  |  | MIPU | GRANDVIEW EAST - SAMPSON 161KV CKT 1 # 1 | Replace wavetraps | 233 | 265 | [10 empty] | 180000 | [24 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T17242317SP | FROM->TO |  | GRANDVIEW EAST - SAMPSON 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541223 | GRDVWE 5 161.00 | 541345 | SAMPSON5 161.00 | 0 |  | 1 | 17SP | 223 | 245 |  | 71.2897 | 108.8762 | 540_GRANDVIEW EAST - SAMPSON 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | PLEASANT HILL () 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 541200 | PHILL 7 345.00 | 541225 | PHILL 5 161.00 | 541361 | PHILL T 13.800 | 1 |  |  |  |  | MIPU | GRANDVIEW EAST - SAMPSON 161KV CKT 1 # 1 | Replace wavetraps | 233 | 265 | [10 empty] | 180000 | [24 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T1052408SH | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 08SH | 32 | 32 |  | 25.2998 | 101.9869 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1872208SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 08SP | 32 | 32 |  | 29.7355 | 122.0877 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1862208SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 08SP | 32 | 32 |  | 26.3121 | 118.4294 | [6 empty] | CATEGORYB | SINGLE | ORCHARD - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533643 | ORCHARD2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T1652308SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 08SP | 32 | 32 |  | 12.5859 | 111.7993 | [6 empty] | CATEGORYB | SINGLE | ATHENS SWITCHING STATION - OWL CREEK 69KV CKT 1 | 0 | 533623 | ATHENS 2 69.000 | 533642 | OWL CRK2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T1582408SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 08SP | 58 | 58 |  | 65.4461 | 103.802 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T1612408SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 08SP | 58 | 58 |  | 63.6438 | 101.879 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1492108SP | TO->FROM |  | LEHIGH TAP - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 08SP | 32 | 32 |  | 9.733 | 120.9169 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T1883309SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 09SP | 32 | 32 |  | 29.8705 | 124.2703 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T1873309SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 09SP | 32 | 32 |  | 26.4167 | 120.5106 | [6 empty] | CATEGORYB | SINGLE | ORCHARD - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533643 | ORCHARD2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T1833309SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 09SP | 32 | 32 |  | 12.6944 | 113.9161 | [6 empty] | CATEGORYB | SINGLE | ATHENS SWITCHING STATION - OWL CREEK 69KV CKT 1 | 0 | 533623 | ATHENS 2 69.000 | 533642 | OWL CRK2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T1794409SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 09SP | 58 | 58 |  | 65.5805 | 104.7422 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T1824409SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 09SP | 58 | 58 |  | 63.7171 | 102.7839 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T6324109SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 09SP | 58 | 58 |  | 72.8628 | 100.1831 | [6 empty] | CATEGORYB | SINGLE | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81T1751409SP | TO->FROM |  | LEHIGH TAP - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 09SP | 32 | 32 |  | 8.7892 | 124.0056 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2451112SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12SP | 32 | 32 |  | -999 | 185.4455 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T8991112SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12SP | 32 | 32 |  | -999 | 184.8256 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T2942112SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12SP | 32 | 32 |  | 31.8691 | 130.8571 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2461112SP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 157.4692 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T9001112SP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 156.7557 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2471112SP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 12SP | 108 | 108 |  | -999 | 170.7109 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T9011112SP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 12SP | 108 | 108 |  | -999 | 170.0226 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2792412SP | TO->FROM |  | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 56.0845 | 117.3039 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2912412SP | TO->FROM |  | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 55.5503 | 112.3373 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1582212SP | TO->FROM |  | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 72.3233 | 103.7043 | [6 empty] | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2782412SP | FROM->TO |  | ALTOONA - TIOGA 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 41.4013 | 157.0806 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T2972112SP | FROM->TO |  | ALTOONA - TIOGA 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 40.3416 | 153.9666 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T2772112SP | FROM->TO |  | ALTOONA - TIOGA 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 35.1642 | 128.815 | [6 empty] | CATEGORYB | SINGLE | ALLEN - ZILA JUNCTION 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | NCONV |  |  | FNSL-Blown up | FDNS-Blown up | 2 | 3 | 2008-12-01 | 2007AG1AFS84L32312SP |  |  | ALTOONA - TIOGA 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 25.1844 | 72.1214 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2812412SP | TO->FROM | Bidirectional | ARCO TAP - ENA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533634 | ENA 2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | 51.9299 | 110.5372 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2431112SP | FROM->TO | Bidirectional | ARCO TAP - ENA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533620 | ARCOTAP2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 108.209 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T8971112SP | FROM->TO | Bidirectional | ARCO TAP - ENA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533620 | ARCOTAP2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 107.7968 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2441112SP | TO->FROM | Bidirectional | ARCO TAP - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533641 | MONARCH2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 111.7972 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T8981112SP | TO->FROM | Bidirectional | ARCO TAP - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533641 | MONARCH2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 111.3621 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2822412SP | FROM->TO | Bidirectional | ARCO TAP - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533620 | ARCOTAP2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | 49.4684 | 107.2233 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2662412SP | FROM->TO |  | ATHENS SWITCHING STATION - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533623 | ATHENS 2 69.000 | 533642 | OWL CRK2 69.000 | 0 |  | 1 | 12SP | 41 | 41 |  | 10.1577 | 122.0473 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2832412SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12SP | 58 | 58 |  | 67.3281 | 140.9509 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T3022112SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12SP | 58 | 58 |  | 65.3825 | 136.6898 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2481112SP | FROM->TO | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533634 | ENA 2 69.000 | 533646 | TIOGA 2 69.000 | 0 |  | 1 | 12SP | 58 | 58 |  | -999 | 130.2259 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2672412SP | TO->FROM |  | LEHIGH TAP - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12SP | 32 | 32 |  | 9.2569 | 152.3867 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2491112SP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 12SP | 100 | 100 |  | -999 | 193.7517 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T9031112SP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 12SP | 100 | 100 |  | -999 | 192.9783 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2501112SP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 12SP | 108 | 108 |  | -999 | 178.3467 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T9041112SP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 12SP | 108 | 108 |  | -999 | 177.6278 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T572112WP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12WP | 32 | 32 |  | 24.6721 | 179.9951 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T3802112WP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12WP | 32 | 32 |  | 24.8481 | 179.8879 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T574312WP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12WP | 32 | 32 |  | 22.9815 | 100.7665 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T582112WP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 39.9857 | 150.9578 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T3812112WP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 40.0893 | 150.8733 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T553312WP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 12WP | 108 | 108 |  | 36.4684 | 159.2099 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T3843312WP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 12WP | 108 | 108 |  | 36.5782 | 159.1568 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T464112WP | FROM->TO | Bidirectional | ARCO TAP - ENA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533620 | ARCOTAP2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 9.7864 | 101.0901 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T3394112WP | FROM->TO | Bidirectional | ARCO TAP - ENA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533620 | ARCOTAP2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 10.0489 | 100.9961 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T474112WP | TO->FROM | Bidirectional | ARCO TAP - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533641 | MONARCH2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 11.0682 | 103.599 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T3404112WP | TO->FROM | Bidirectional | ARCO TAP - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533641 | MONARCH2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 11.2882 | 103.5055 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T514112WP | FROM->TO | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533634 | ENA 2 69.000 | 533646 | TIOGA 2 69.000 | 0 |  | 1 | 12WP | 58 | 58 |  | 10.7435 | 122.8447 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T3444112WP | FROM->TO | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533634 | ENA 2 69.000 | 533646 | TIOGA 2 69.000 | 0 |  | 1 | 12WP | 58 | 58 |  | 11.1297 | 122.7501 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81T964212WP | TO->FROM |  | LEHIGH TAP - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12WP | 32 | 32 |  | 7.335 | 100.4311 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T593312WP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 12WP | 100 | 100 |  | 44.6309 | 179.6932 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T3883312WP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 12WP | 100 | 100 |  | 44.776 | 179.5805 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T613312WP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 12WP | 108 | 108 |  | 40.4185 | 165.4322 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T3024312WP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 12WP | 108 | 108 |  | 40.5965 | 165.359 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4092317SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 17SP | 32 | 32 |  | 14.5581 | 132.3017 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16612317SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 17SP | 32 | 32 |  | 14.4858 | 131.4416 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4832317SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 17SP | 32 | 32 |  | 35.6597 | 126.9833 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4102317SP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 17SP | 72 | 72 |  | 23.268 | 100.8105 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16622317SP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 17SP | 72 | 72 |  | 23.1386 | 100.3044 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4112317SP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 17SP | 108 | 108 |  | 28.8307 | 116.5141 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16632317SP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 17SP | 108 | 108 |  | 28.7177 | 115.9243 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T6122417SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 17SP | 58 | 58 |  | 70.7819 | 101.4296 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T4742117SP | TO->FROM |  | LEHIGH TAP - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 17SP | 32 | 32 |  | 11.392 | 117.9501 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4122317SP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 17SP | 100 | 100 |  | 38.8083 | 133.7621 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16642317SP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 17SP | 100 | 100 |  | 38.688 | 133.0647 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4132317SP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 17SP | 108 | 108 |  | 34.6116 | 122.4871 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16652317SP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 17SP | 108 | 108 |  | 34.4969 | 121.8479 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Green to Vernon 69 kV | Rebuild 7.19 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 7.19 | 18 | 6 |  | 0.01517 | 0.10325 | 0.0022 | Terminal equipment limit | 2966229 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T10742212SP | TO->FROM |  | HARRISON-EAST - SUMMIT 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99837 | 5SUMMIT 161.00 | 99811 | 5HARR-E 161.00 | 0 |  | 1 | 12SP | 162 | 162 |  | 97.7925 | 107.396 | [6 empty] | CATEGORYB | SINGLE | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | 0 | 99843 | 5EVRTON 161.00 | 99860 | 5ST_JOE 161.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | HARRISON-EAST - SUMMIT 161KV CKT 1 | Indeterminate | [37 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T10542212SP | TO->FROM |  | HARRISON-EAST - SUMMIT 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99837 | 5SUMMIT 161.00 | 99811 | 5HARR-E 161.00 | 0 |  | 1 | 12SP | 162 | 162 |  | 95.8137 | 105.3681 | [6 empty] | CATEGORYB | SINGLE | EVERTON - HARRISON-EAST 161KV CKT 1 | 0 | 99811 | 5HARR-E 161.00 | 99843 | 5EVRTON 161.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | HARRISON-EAST - SUMMIT 161KV CKT 1 | Indeterminate | [37 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T16432417SP | TO->FROM |  | HARRISON-EAST - SUMMIT 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99837 | 5SUMMIT 161.00 | 99811 | 5HARR-E 161.00 | 0 |  | 1 | 17SP | 162 | 162 | 102.2 | 98.4702 | 108.3637 | [6 empty] | CATEGORYB | SINGLE | 5ST_JOE 161.00 - EVERTON 161KV CKT 1 | 0 | 99843 | 5EVRTON 161.00 | 99860 | 5ST_JOE 161.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | HARRISON-EAST - SUMMIT 161KV CKT 1 | Indeterminate | [37 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T16202417SP | TO->FROM |  | HARRISON-EAST - SUMMIT 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99837 | 5SUMMIT 161.00 | 99811 | 5HARR-E 161.00 | 0 |  | 1 | 17SP | 162 | 162 |  | 96.2154 | 106.011 | [6 empty] | CATEGORYB | SINGLE | EVERTON - HARRISON-EAST 161KV CKT 1 | 0 | 99811 | 5HARR-E 161.00 | 99843 | 5EVRTON 161.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | HARRISON-EAST - SUMMIT 161KV CKT 1 | Indeterminate | [37 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 4 | 2008-12-01 | 2007AG1AFS81T6953409WP | FROM->TO |  | HOLCOMB - PLYMELL 115KV CKT 1 | EXP | SUNC | SUNC | SEPC | PIONEER | 0 | 531448 | HOLCOMB3 115.00 | 531393 | PLYMELL3 115.00 | 0 |  | 1 | 09WP | 120 | 143 | 107.2 | 107.2716 | 107.3945 | [6 empty] | CATEGORYB | NONSINGLE | SPP-SUNC-05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | Rebuild Holcomb to Pioneer Tap, Reduce generation in area 534, increase generation in area 539 | SUNC | HOLCOMB - PLYMELL 115KV CKT 1 | Rebuild Holcomb to Plymell | 185 | 222 |  |  | 11 | 24 | 24 |  | 0.00821 | 0.06016 | 0.00862 |  | 1918400 | 2006-06-01 | [23 empty] | 2009-12-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 4 | 2008-12-01 | 2007AG1AFS81T803409WP | FROM->TO |  | HOLCOMB - PLYMELL 115KV CKT 1 | EXP | SUNC | SUNC | SEPC | PIONEER | 0 | 531448 | HOLCOMB3 115.00 | 531393 | PLYMELL3 115.00 | 0 |  | 1 | 09WP | 120 | 143 | 101.7 | 101.721 | 101.8542 | [6 empty] | CATEGORYB | SINGLE | FLETCHER - HOLCOMB 115KV CKT 1 | 0 | 531420 | FLETCHR3 115.00 | 531448 | HOLCOMB3 115.00 | 0 |  | 1 |  |  |  | Rebuild Holcomb to Pioneer Tap, Reduce generation in area 534, increase generation in area 539 | SUNC | HOLCOMB - PLYMELL 115KV CKT 1 | Rebuild Holcomb to Plymell | 185 | 222 |  |  | 11 | 24 | 24 |  | 0.00821 | 0.06016 | 0.00862 |  | 1918400 | 2006-06-01 | [23 empty] | 2009-12-01 | 2009-12-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FNSL | FDNS-Blown up | 3 | 3 | 2008-12-01 | 2007AG1AFS82T33312SP | FROM->TO |  | HOLCOMB - PLYMELL 115KV CKT 1 | EXP | SUNC | SUNC | SEPC | PIONEER | 0 | 531448 | HOLCOMB3 115.00 | 531393 | PLYMELL3 115.00 | 0 |  | 1 | 12SP | 120 | 143 | 126.1 | -999 | 126.0896 | [6 empty] | CATEGORYB | SINGLE | CUDAHY - JUDSON LARGE 115KV CKT 1 | 0 | 539659 | CUDAHY 3 115.00 | 539671 | JUD-LRG3 115.00 | 0 |  | 1 |  |  |  | Rebuild Holcomb to Pioneer Tap, Reduce generation in area 534, increase generation in area 539 | SUNC | HOLCOMB - PLYMELL 115KV CKT 1 | Rebuild Holcomb to Plymell | 185 | 222 |  |  | 11 | 24 | 24 |  | 0.00821 | 0.06016 | 0.00862 |  | 1918400 | 2006-06-01 | [23 empty] | 2009-12-01 | 2009-12-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FNSL | FDNS-Blown up | 3 | 2 | 2008-12-01 | 2007AG1AFS82T33212SP | FROM->TO |  | HOLCOMB - PLYMELL 115KV CKT 1 | EXP | SUNC | SUNC | SEPC | PIONEER | 0 | 531448 | HOLCOMB3 115.00 | 531393 | PLYMELL3 115.00 | 0 |  | 1 | 12SP | 120 | 143 | 117.7 | 117.6799 | 117.6926 | [6 empty] | CATEGORYB | SINGLE | CIMARRON RIVER TAP - CUDAHY 115KV CKT 1 | 0 | 539652 | CMRIVTP3 115.00 | 539659 | CUDAHY 3 115.00 | 0 |  | 1 |  |  |  | Rebuild Holcomb to Pioneer Tap, Reduce generation in area 534, increase generation in area 539 | SUNC | HOLCOMB - PLYMELL 115KV CKT 1 | Rebuild Holcomb to Plymell | 185 | 222 |  |  | 11 | 24 | 24 |  | 0.00821 | 0.06016 | 0.00862 |  | 1918400 | 2006-06-01 | [23 empty] | 2009-12-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T13795512SP | FROM->TO |  | HOLCOMB - PLYMELL 115KV CKT 1 | EXP | SUNC | SUNC | SEPC | PIONEER | 0 | 531448 | HOLCOMB3 115.00 | 531393 | PLYMELL3 115.00 | 0 |  | 1 | 12SP | 120 | 143 | 117.8 | 117.9313 | 117.3912 | [6 empty] | CATEGORYB | NONSINGLE | SPP-SUNC-05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | Rebuild Holcomb to Pioneer Tap, Reduce generation in area 534, increase generation in area 539 | SUNC | HOLCOMB - PLYMELL 115KV CKT 1 | Rebuild Holcomb to Plymell | 185 | 222 |  |  | 11 | 24 | 24 |  | 0.00821 | 0.06016 | 0.00862 |  | 1918400 | 2006-06-01 | [23 empty] | 2009-12-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 4 | 2008-12-01 | 2007AG1AFS81T7603412WP | FROM->TO |  | HOLCOMB - PLYMELL 115KV CKT 1 | EXP | SUNC | SUNC | SEPC | PIONEER | 0 | 531448 | HOLCOMB3 115.00 | 531393 | PLYMELL3 115.00 | 0 |  | 1 | 12WP | 120 | 143 | 105.5 | 105.8531 | 105.8611 | [6 empty] | CATEGORYB | NONSINGLE | SPP-SUNC-05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | Rebuild Holcomb to Pioneer Tap, Reduce generation in area 534, increase generation in area 539 | SUNC | HOLCOMB - PLYMELL 115KV CKT 1 | Rebuild Holcomb to Plymell | 185 | 222 |  |  | 11 | 24 | 24 |  | 0.00821 | 0.06016 | 0.00862 |  | 1918400 | 2006-06-01 | [23 empty] | 2009-12-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 4 | 2008-12-01 | 2007AG1AFS81T553412WP | FROM->TO |  | HOLCOMB - PLYMELL 115KV CKT 1 | EXP | SUNC | SUNC | SEPC | PIONEER | 0 | 531448 | HOLCOMB3 115.00 | 531393 | PLYMELL3 115.00 | 0 |  | 1 | 12WP | 120 | 143 | 100.2 | 100.543 | 100.6152 | [6 empty] | CATEGORYB | SINGLE | FLETCHER - HOLCOMB 115KV CKT 1 | 0 | 531420 | FLETCHR3 115.00 | 531448 | HOLCOMB3 115.00 | 0 |  | 1 |  |  |  | Rebuild Holcomb to Pioneer Tap, Reduce generation in area 534, increase generation in area 539 | SUNC | HOLCOMB - PLYMELL 115KV CKT 1 | Rebuild Holcomb to Plymell | 185 | 222 |  |  | 11 | 24 | 24 |  | 0.00821 | 0.06016 | 0.00862 |  | 1918400 | 2006-06-01 | [23 empty] | 2009-12-01 | 2009-12-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FNSL | FDNS-Iteration limit exceeded | 3 | 3 | 2008-12-01 | 2007AG1AFS82T23317SP | FROM->TO |  | HOLCOMB - PLYMELL 115KV CKT 1 | EXP | SUNC | SUNC | SEPC | PIONEER | 0 | 531448 | HOLCOMB3 115.00 | 531393 | PLYMELL3 115.00 | 0 |  | 1 | 17SP | 120 | 143 | 117.6 | 118.3176 | 118.5835 | [6 empty] | CATEGORYB | SINGLE | FLETCHER - HOLCOMB 115KV CKT 1 | 0 | 531420 | FLETCHR3 115.00 | 531448 | HOLCOMB3 115.00 | 0 |  | 1 |  |  |  | Rebuild Holcomb to Pioneer Tap, Reduce generation in area 534, increase generation in area 539 | SUNC | HOLCOMB - PLYMELL 115KV CKT 1 | Rebuild Holcomb to Plymell | 185 | 222 |  |  | 11 | 24 | 24 |  | 0.00821 | 0.06016 | 0.00862 |  | 1918400 | 2006-06-01 | [23 empty] | 2009-12-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T27033217SP | FROM->TO |  | HOLCOMB - PLYMELL 115KV CKT 1 | EXP | SUNC | SUNC | SEPC | PIONEER | 0 | 531448 | HOLCOMB3 115.00 | 531393 | PLYMELL3 115.00 | 0 |  | 1 | 17SP | 120 | 143 | 119.3 | 119.8044 | 120.0313 | [6 empty] | CATEGORYB | NONSINGLE | SPP-SUNC-05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | Rebuild Holcomb to Pioneer Tap, Reduce generation in area 534, increase generation in area 539 | SUNC | HOLCOMB - PLYMELL 115KV CKT 1 | Rebuild Holcomb to Plymell | 185 | 222 |  |  | 11 | 24 | 24 |  | 0.00821 | 0.06016 | 0.00862 |  | 1918400 | 2006-06-01 | [23 empty] | 2009-12-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T4763317SP | FROM->TO |  | HOLCOMB - PLYMELL 115KV CKT 1 | EXP | SUNC | SUNC | SEPC | PIONEER | 0 | 531448 | HOLCOMB3 115.00 | 531393 | PLYMELL3 115.00 | 0 |  | 1 | 17SP | 120 | 143 | 111.7 | 111.6915 | 111.7081 | [6 empty] | CATEGORYB | SINGLE | CUDAHY - JUDSON LARGE 115KV CKT 1 | 0 | 539659 | CUDAHY 3 115.00 | 539671 | JUD-LRG3 115.00 | 0 |  | 1 |  |  |  | Rebuild Holcomb to Pioneer Tap, Reduce generation in area 534, increase generation in area 539 | SUNC | HOLCOMB - PLYMELL 115KV CKT 1 | Rebuild Holcomb to Plymell | 185 | 222 |  |  | 11 | 24 | 24 |  | 0.00821 | 0.06016 | 0.00862 |  | 1918400 | 2006-06-01 | [23 empty] | 2009-12-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T6035517SP | FROM->TO |  | HUNTSVILLE - ST_JOHN 115KV CKT 1 | REL | MIDW | MIDW | REG E-IL | REG E-IL | 0 | 530618 | HUNTSVL3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 80 | 88 | 107.8 | 108.9262 | 105.8756 | [6 empty] | CATEGORYB | SINGLE | CIRCLE - MULLERGREN 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 |  |  |  |  | MIDW | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 MIDW | Tear down and rebuild 73.4% Ownership 28.79 mile HEC-Huntsville 115 kV line and replace CT, wavetrap and relays. | [11 empty] | 450k per miles | 9550000 | 2007-01-01 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T6165517SP | FROM->TO |  | HUNTSVILLE - ST_JOHN 115KV CKT 1 | REL | MIDW | MIDW | REG E-IL | REG E-IL | 0 | 530618 | HUNTSVL3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 80 | 88 | 106.2 | 107.361 | 105.0372 | [6 empty] | CATEGORYB | SINGLE | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 533045 | GILL W 4 138.00 | 0 |  | 1 |  |  |  |  | MIDW | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 MIDW | Tear down and rebuild 73.4% Ownership 28.79 mile HEC-Huntsville 115 kV line and replace CT, wavetrap and relays. | [11 empty] | 450k per miles | 9550000 | 2007-01-01 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T6205517SP | FROM->TO |  | HUNTSVILLE - ST_JOHN 115KV CKT 1 | REL | MIDW | MIDW | REG E-IL | REG E-IL | 0 | 530618 | HUNTSVL3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 80 | 88 | 104.6 | 105.7352 | 102.2569 | [6 empty] | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MIDW | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 MIDW | Tear down and rebuild 73.4% Ownership 28.79 mile HEC-Huntsville 115 kV line and replace CT, wavetrap and relays. | [11 empty] | 450k per miles | 9550000 | 2007-01-01 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T6045517SP | TO->FROM |  | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | REL | WERE | MIDW | WEST | REG E-IL | 0 | 533419 | HEC 3 115.00 | 530618 | HUNTSVL3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 108.5 | 109.5404 | 106.6121 | [6 empty] | CATEGORYB | SINGLE | CIRCLE - MULLERGREN 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 |  |  |  |  | MIDW | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 MIDW | Tear down and rebuild 73.4% Ownership 28.79 mile HEC-Huntsville 115 kV line and replace CT, wavetrap and relays. | [11 empty] | 450k per miles | 9550000 | 2007-01-01 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T6045517SP | TO->FROM |  | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | REL | WERE | MIDW | WEST | REG E-IL | 0 | 533419 | HEC 3 115.00 | 530618 | HUNTSVL3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 108.5 | 109.5404 | 106.6121 | [6 empty] | CATEGORYB | SINGLE | CIRCLE - MULLERGREN 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 |  |  |  |  | MIDW | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 MIDW | Tear down and rebuild 73.4% Ownership 28.79 mile HEC-Huntsville 115 kV line and replace CT, wavetrap and relays. | [11 empty] | 450k per miles | 9550000 | 2007-01-01 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T6175517SP | TO->FROM |  | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | REL | WERE | MIDW | WEST | REG E-IL | 0 | 533419 | HEC 3 115.00 | 530618 | HUNTSVL3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 107.0 | 108.18 | 105.8673 | [6 empty] | CATEGORYB | SINGLE | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 533045 | GILL W 4 138.00 | 0 |  | 1 |  |  |  |  | MIDW | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 MIDW | Tear down and rebuild 73.4% Ownership 28.79 mile HEC-Huntsville 115 kV line and replace CT, wavetrap and relays. | [11 empty] | 450k per miles | 9550000 | 2007-01-01 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T6175517SP | TO->FROM |  | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | REL | WERE | MIDW | WEST | REG E-IL | 0 | 533419 | HEC 3 115.00 | 530618 | HUNTSVL3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 107.0 | 108.18 | 105.8673 | [6 empty] | CATEGORYB | SINGLE | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 533045 | GILL W 4 138.00 | 0 |  | 1 |  |  |  |  | MIDW | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 MIDW | Tear down and rebuild 73.4% Ownership 28.79 mile HEC-Huntsville 115 kV line and replace CT, wavetrap and relays. | [11 empty] | 450k per miles | 9550000 | 2007-01-01 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T6215517SP | TO->FROM |  | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | REL | WERE | MIDW | WEST | REG E-IL | 0 | 533419 | HEC 3 115.00 | 530618 | HUNTSVL3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 105.8 | 106.8146 | 103.3232 | [6 empty] | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MIDW | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 MIDW | Tear down and rebuild 73.4% Ownership 28.79 mile HEC-Huntsville 115 kV line and replace CT, wavetrap and relays. | [11 empty] | 450k per miles | 9550000 | 2007-01-01 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T6215517SP | TO->FROM |  | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | REL | WERE | MIDW | WEST | REG E-IL | 0 | 533419 | HEC 3 115.00 | 530618 | HUNTSVL3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 105.8 | 106.8146 | 103.3232 | [6 empty] | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MIDW | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 MIDW | Tear down and rebuild 73.4% Ownership 28.79 mile HEC-Huntsville 115 kV line and replace CT, wavetrap and relays. | [11 empty] | 450k per miles | 9550000 | 2007-01-01 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T6175517SP | TO->FROM |  | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | REL | WERE | MIDW | WEST | REG E-IL | 0 | 533419 | HEC 3 115.00 | 530618 | HUNTSVL3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 107.0 | 108.18 | 105.8673 | [6 empty] | CATEGORYB | SINGLE | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 533045 | GILL W 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 WERE | Tear down and rebuild 26.6% Ownership 28.79 mile HEC-Huntsville 115 kV line and replace CT, wavetrap and relays. | [11 empty] | 450k per miles | 3450000 | 2007-01-01 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T6215517SP | TO->FROM |  | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | REL | WERE | MIDW | WEST | REG E-IL | 0 | 533419 | HEC 3 115.00 | 530618 | HUNTSVL3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 105.8 | 106.8146 | 103.3232 | [6 empty] | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | WERE | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 WERE | Tear down and rebuild 26.6% Ownership 28.79 mile HEC-Huntsville 115 kV line and replace CT, wavetrap and relays. | [11 empty] | 450k per miles | 3450000 | 2007-01-01 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T6215517SP | TO->FROM |  | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | REL | WERE | MIDW | WEST | REG E-IL | 0 | 533419 | HEC 3 115.00 | 530618 | HUNTSVL3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 105.8 | 106.8146 | 103.3232 | [6 empty] | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | WERE | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 WERE | Tear down and rebuild 26.6% Ownership 28.79 mile HEC-Huntsville 115 kV line and replace CT, wavetrap and relays. | [11 empty] | 450k per miles | 3450000 | 2007-01-01 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T6035517SP | FROM->TO |  | HUNTSVILLE - ST_JOHN 115KV CKT 1 | REL | MIDW | MIDW | REG E-IL | REG E-IL | 0 | 530618 | HUNTSVL3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 80 | 88 | 107.8 | 108.9262 | 105.8756 | [6 empty] | CATEGORYB | SINGLE | CIRCLE - MULLERGREN 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 |  |  |  |  | WERE | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 WERE | Tear down and rebuild 26.6% Ownership 28.79 mile HEC-Huntsville 115 kV line and replace CT, wavetrap and relays. | [11 empty] | 450k per miles | 3450000 | 2007-01-01 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T6165517SP | FROM->TO |  | HUNTSVILLE - ST_JOHN 115KV CKT 1 | REL | MIDW | MIDW | REG E-IL | REG E-IL | 0 | 530618 | HUNTSVL3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 80 | 88 | 106.2 | 107.361 | 105.0372 | [6 empty] | CATEGORYB | SINGLE | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 533045 | GILL W 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 WERE | Tear down and rebuild 26.6% Ownership 28.79 mile HEC-Huntsville 115 kV line and replace CT, wavetrap and relays. | [11 empty] | 450k per miles | 3450000 | 2007-01-01 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T6205517SP | FROM->TO |  | HUNTSVILLE - ST_JOHN 115KV CKT 1 | REL | MIDW | MIDW | REG E-IL | REG E-IL | 0 | 530618 | HUNTSVL3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 80 | 88 | 104.6 | 105.7352 | 102.2569 | [6 empty] | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | WERE | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 WERE | Tear down and rebuild 26.6% Ownership 28.79 mile HEC-Huntsville 115 kV line and replace CT, wavetrap and relays. | [11 empty] | 450k per miles | 3450000 | 2007-01-01 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T6045517SP | TO->FROM |  | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | REL | WERE | MIDW | WEST | REG E-IL | 0 | 533419 | HEC 3 115.00 | 530618 | HUNTSVL3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 108.5 | 109.5404 | 106.6121 | [6 empty] | CATEGORYB | SINGLE | CIRCLE - MULLERGREN 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 |  |  |  |  | WERE | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 WERE | Tear down and rebuild 26.6% Ownership 28.79 mile HEC-Huntsville 115 kV line and replace CT, wavetrap and relays. | [11 empty] | 450k per miles | 3450000 | 2007-01-01 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T6045517SP | TO->FROM |  | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | REL | WERE | MIDW | WEST | REG E-IL | 0 | 533419 | HEC 3 115.00 | 530618 | HUNTSVL3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 108.5 | 109.5404 | 106.6121 | [6 empty] | CATEGORYB | SINGLE | CIRCLE - MULLERGREN 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 |  |  |  |  | WERE | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 WERE | Tear down and rebuild 26.6% Ownership 28.79 mile HEC-Huntsville 115 kV line and replace CT, wavetrap and relays. | [11 empty] | 450k per miles | 3450000 | 2007-01-01 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T6175517SP | TO->FROM |  | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | REL | WERE | MIDW | WEST | REG E-IL | 0 | 533419 | HEC 3 115.00 | 530618 | HUNTSVL3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 107.0 | 108.18 | 105.8673 | [6 empty] | CATEGORYB | SINGLE | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 533045 | GILL W 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 WERE | Tear down and rebuild 26.6% Ownership 28.79 mile HEC-Huntsville 115 kV line and replace CT, wavetrap and relays. | [11 empty] | 450k per miles | 3450000 | 2007-01-01 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T6045517SP | TO->FROM |  | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | REL | WERE | MIDW | WEST | REG E-IL | 0 | 533419 | HEC 3 115.00 | 530618 | HUNTSVL3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 108.5 | 109.5404 | 106.6121 | [6 empty] | CATEGORYB | SINGLE | CIRCLE - MULLERGREN 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 |  |  |  |  | MIDW | HUNTSVILLE - ST_JOHN 115KV CKT 1 | Rebuild 26.5 miles Huntsville - St. John 115 kV line and replace CT, wavetrap, breakers, and relays. | [11 empty] | 450k per miles | 11925000 | 2007-01-01 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T6045517SP | TO->FROM |  | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | REL | WERE | MIDW | WEST | REG E-IL | 0 | 533419 | HEC 3 115.00 | 530618 | HUNTSVL3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 108.5 | 109.5404 | 106.6121 | [6 empty] | CATEGORYB | SINGLE | CIRCLE - MULLERGREN 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 |  |  |  |  | MIDW | HUNTSVILLE - ST_JOHN 115KV CKT 1 | Rebuild 26.5 miles Huntsville - St. John 115 kV line and replace CT, wavetrap, breakers, and relays. | [11 empty] | 450k per miles | 11925000 | 2007-01-01 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T6175517SP | TO->FROM |  | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | REL | WERE | MIDW | WEST | REG E-IL | 0 | 533419 | HEC 3 115.00 | 530618 | HUNTSVL3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 107.0 | 108.18 | 105.8673 | [6 empty] | CATEGORYB | SINGLE | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 533045 | GILL W 4 138.00 | 0 |  | 1 |  |  |  |  | MIDW | HUNTSVILLE - ST_JOHN 115KV CKT 1 | Rebuild 26.5 miles Huntsville - St. John 115 kV line and replace CT, wavetrap, breakers, and relays. | [11 empty] | 450k per miles | 11925000 | 2007-01-01 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T6175517SP | TO->FROM |  | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | REL | WERE | MIDW | WEST | REG E-IL | 0 | 533419 | HEC 3 115.00 | 530618 | HUNTSVL3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 107.0 | 108.18 | 105.8673 | [6 empty] | CATEGORYB | SINGLE | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 533045 | GILL W 4 138.00 | 0 |  | 1 |  |  |  |  | MIDW | HUNTSVILLE - ST_JOHN 115KV CKT 1 | Rebuild 26.5 miles Huntsville - St. John 115 kV line and replace CT, wavetrap, breakers, and relays. | [11 empty] | 450k per miles | 11925000 | 2007-01-01 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T6215517SP | TO->FROM |  | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | REL | WERE | MIDW | WEST | REG E-IL | 0 | 533419 | HEC 3 115.00 | 530618 | HUNTSVL3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 105.8 | 106.8146 | 103.3232 | [6 empty] | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MIDW | HUNTSVILLE - ST_JOHN 115KV CKT 1 | Rebuild 26.5 miles Huntsville - St. John 115 kV line and replace CT, wavetrap, breakers, and relays. | [11 empty] | 450k per miles | 11925000 | 2007-01-01 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T6215517SP | TO->FROM |  | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | REL | WERE | MIDW | WEST | REG E-IL | 0 | 533419 | HEC 3 115.00 | 530618 | HUNTSVL3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 105.8 | 106.8146 | 103.3232 | [6 empty] | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MIDW | HUNTSVILLE - ST_JOHN 115KV CKT 1 | Rebuild 26.5 miles Huntsville - St. John 115 kV line and replace CT, wavetrap, breakers, and relays. | [11 empty] | 450k per miles | 11925000 | 2007-01-01 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T6035517SP | FROM->TO |  | HUNTSVILLE - ST_JOHN 115KV CKT 1 | REL | MIDW | MIDW | REG E-IL | REG E-IL | 0 | 530618 | HUNTSVL3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 80 | 88 | 107.8 | 108.9262 | 105.8756 | [6 empty] | CATEGORYB | SINGLE | CIRCLE - MULLERGREN 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 |  |  |  |  | MIDW | HUNTSVILLE - ST_JOHN 115KV CKT 1 | Rebuild 26.5 miles Huntsville - St. John 115 kV line and replace CT, wavetrap, breakers, and relays. | [11 empty] | 450k per miles | 11925000 | 2007-01-01 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T6165517SP | FROM->TO |  | HUNTSVILLE - ST_JOHN 115KV CKT 1 | REL | MIDW | MIDW | REG E-IL | REG E-IL | 0 | 530618 | HUNTSVL3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 80 | 88 | 106.2 | 107.361 | 105.0372 | [6 empty] | CATEGORYB | SINGLE | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 533045 | GILL W 4 138.00 | 0 |  | 1 |  |  |  |  | MIDW | HUNTSVILLE - ST_JOHN 115KV CKT 1 | Rebuild 26.5 miles Huntsville - St. John 115 kV line and replace CT, wavetrap, breakers, and relays. | [11 empty] | 450k per miles | 11925000 | 2007-01-01 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T6205517SP | FROM->TO |  | HUNTSVILLE - ST_JOHN 115KV CKT 1 | REL | MIDW | MIDW | REG E-IL | REG E-IL | 0 | 530618 | HUNTSVL3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 80 | 88 | 104.6 | 105.7352 | 102.2569 | [6 empty] | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MIDW | HUNTSVILLE - ST_JOHN 115KV CKT 1 | Rebuild 26.5 miles Huntsville - St. John 115 kV line and replace CT, wavetrap, breakers, and relays. | [11 empty] | 450k per miles | 11925000 | 2007-01-01 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T7212417SP | FROM->TO |  | JAMES RIVER - TWIN OAKS 69KV CKT 1 | EXP | SPRM | SPRM | SPRM | SPRM | 0 | 549904 | JRPS 2 69.000 | 549933 | TWINOAK2 69.000 | 0 |  | 1 | 17SP | 103 | 108 | 105.9 | 71.4944 | 105.7928 | [6 empty] | CATEGORYB | SINGLE | KICKAPOO - SUNSET 69KV CKT 1 | 0 | 549906 | KICKAPO2 69.000 | 549907 | SUNSET 2 69.000 | 0 |  | 1 |  |  |  |  | SPRM | JAMES RIVER - TWIN OAKS 69KV CKT 1 | Reconductor 69kV Line 636 MCM ACSR to 762.8 kcmil ACSS/TW 3.103 miles. | 153 | 159 | 153 | 159 | 3 | 24 | 6 | Outage | 0.00851 | 0.0437 | 0.00095 |  | 979000 | 2007-04-19 | [23 empty] | 2015-06-01 | 2015-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T6102317SP | FROM->TO |  | JAMESVILLE - SUB 415 - BLACKHAWK JCT. 69KV CKT 1 | S | AECI | EMDE | KAMO | OZARK | 0 | 96673 | 2JAMESV 69.000 | 547604 | BHJ415 2 69.000 | 0 |  | 1 | 17SP | 54 | 65 | 106.9 | 91.4763 | 109.5839 | [6 empty] | CATEGORYB | SINGLE | OZARK SOUTH - SUB 434 - OZARK SOUTHEAST 69KV CKT 1 | 0 | 547442 | OZARKS 2 69.000 | 547609 | OZK434 2 69.000 | 0 |  | 1 | ASSIGN |  |  |  | AECI | JAMESVILLE - SUB 415 - BLACKHAWK JCT. 69KV CKT 1 AECI | Reset CT | [12 empty] | 1000 | [24 empty] | 2014-06-01 | 2014-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T17752317SP | FROM->TO |  | JAMESVILLE - SUB 415 - BLACKHAWK JCT. 69KV CKT 1 | S | AECI | EMDE | KAMO | OZARK | 0 | 96673 | 2JAMESV 69.000 | 547604 | BHJ415 2 69.000 | 0 |  | 1 | 17SP | 54 | 65 | 105.1 | 90.2384 | 107.9241 | [6 empty] | CATEGORYB | SINGLE | OZARKS (OZARK) 161/69/12.5KV TRANSFORMER CKT 1 | 1 | 547442 | OZARKS 2 69.000 | 547621 | OZARKS 5 161.00 | 547705 | OZARKST1 12.500 | 1 | ASSIGN |  |  |  | AECI | JAMESVILLE - SUB 415 - BLACKHAWK JCT. 69KV CKT 1 AECI | Reset CT | [12 empty] | 1000 | [24 empty] | 2014-06-01 | 2014-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T18152317SP | FROM->TO |  | JAMESVILLE - SUB 415 - BLACKHAWK JCT. 69KV CKT 1 | S | AECI | EMDE | KAMO | OZARK | 0 | 96673 | 2JAMESV 69.000 | 547604 | BHJ415 2 69.000 | 0 |  | 1 | 17SP | 54 | 65 | 104.9 | 90.2117 | 107.2662 | [6 empty] | CATEGORYB | SINGLE | OZARKS - RIVERDALE 161KV CKT 1 | 0 | 547621 | OZARKS 5 161.00 | 96726 | 5RIVRDL 161.00 | 0 |  | 1 | ASSIGN |  |  |  | AECI | JAMESVILLE - SUB 415 - BLACKHAWK JCT. 69KV CKT 1 AECI | Reset CT | [12 empty] | 1000 | [24 empty] | 2014-06-01 | 2014-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T6102317SP | FROM->TO |  | JAMESVILLE - SUB 415 - BLACKHAWK JCT. 69KV CKT 1 | EXP | AECI | EMDE | KAMO | OZARK | 0 | 96673 | 2JAMESV 69.000 | 547604 | BHJ415 2 69.000 | 0 |  | 1 | 17SP | 54 | 65 | 106.9 | 91.4763 | 109.5839 | [6 empty] | CATEGORYB | SINGLE | OZARK SOUTH - SUB 434 - OZARK SOUTHEAST 69KV CKT 1 | 0 | 547442 | OZARKS 2 69.000 | 547609 | OZK434 2 69.000 | 0 |  | 1 | ASSIGN |  |  |  | EMDE | JAMESVILLE - SUB 415 - BLACKHAWK JCT. 69KV CKT 1 EMDE | Replace Jumpers to breaker #6950 at Blackhawk Jct. | 73 | 89 | 96 | 96 |  | 12 | 6 | [5 empty] | 50000 | 2015-06-01 | [23 empty] | 2014-06-01 | 2014-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T17752317SP | FROM->TO |  | JAMESVILLE - SUB 415 - BLACKHAWK JCT. 69KV CKT 1 | EXP | AECI | EMDE | KAMO | OZARK | 0 | 96673 | 2JAMESV 69.000 | 547604 | BHJ415 2 69.000 | 0 |  | 1 | 17SP | 54 | 65 | 105.1 | 90.2384 | 107.9241 | [6 empty] | CATEGORYB | SINGLE | OZARKS (OZARK) 161/69/12.5KV TRANSFORMER CKT 1 | 1 | 547442 | OZARKS 2 69.000 | 547621 | OZARKS 5 161.00 | 547705 | OZARKST1 12.500 | 1 | ASSIGN |  |  |  | EMDE | JAMESVILLE - SUB 415 - BLACKHAWK JCT. 69KV CKT 1 EMDE | Replace Jumpers to breaker #6950 at Blackhawk Jct. | 73 | 89 | 96 | 96 |  | 12 | 6 | [5 empty] | 50000 | 2015-06-01 | [23 empty] | 2014-06-01 | 2014-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T18152317SP | FROM->TO |  | JAMESVILLE - SUB 415 - BLACKHAWK JCT. 69KV CKT 1 | EXP | AECI | EMDE | KAMO | OZARK | 0 | 96673 | 2JAMESV 69.000 | 547604 | BHJ415 2 69.000 | 0 |  | 1 | 17SP | 54 | 65 | 104.9 | 90.2117 | 107.2662 | [6 empty] | CATEGORYB | SINGLE | OZARKS - RIVERDALE 161KV CKT 1 | 0 | 547621 | OZARKS 5 161.00 | 96726 | 5RIVRDL 161.00 | 0 |  | 1 | ASSIGN |  |  |  | EMDE | JAMESVILLE - SUB 415 - BLACKHAWK JCT. 69KV CKT 1 EMDE | Replace Jumpers to breaker #6950 at Blackhawk Jct. | 73 | 89 | 96 | 96 |  | 12 | 6 | [5 empty] | 50000 | 2015-06-01 | [23 empty] | 2014-06-01 | 2014-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T7165517SP | FROM->TO |  | JEWELL 3 - SMITH CENTER 115KV CKT 1 | S | WEPL | WEPL |  |  | 0 | 539669 | JEWELL 3 115.00 | 539693 | SMITH-C3 115.00 | 0 |  | 1 | 17SP | 79.7 | 79.7 |  | 86.5264 | 102.3868 | [6 empty] | CATEGORYB | SINGLE | BELOIT - CONCORDIA 115KV CKT 1 | 0 | 539650 | BELOIT 3 115.00 | 539657 | CONCORD3 115.00 | 0 |  | 1 |  |  |  |  | MKEC | JEWELL 3 - SMITH CENTER 115KV CKT 1 | Rebuild 33.9 mile line | [11 empty] | $249,916.24 per mile | 8472161 | 2008-05-15 | [23 empty] | 2013-06-01 | 2013-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T3443312SP | TO->FROM |  | SUB 145 - JOPLIN WEST 7TH - SUB 439 - STATELINE 161KV CKT 1 | REL | EMDE | EMDE | JOPLIN | JOPLIN | 0 | 547498 | STL439 5 161.00 | 547470 | JOP145 5 161.00 | 0 |  | 1 | 12SP | 218 | 268 |  | 97.9312 | 101.2328 | [6 empty] | CATEGORYB | SINGLE | SUB 110 - ORONOGO JCT. - SUB 452 - RIVERTON 161KV CKT 1 | 0 | 547467 | ORO110 5 161.00 | 547469 | RIV4525 161.00 | 0 |  | 1 |  |  |  |  | EMDE | JOPLIN 59 - SUB 439 - STATELINE 161KV CKT 1 | Install new line from Sub #439 to new Sub Joplin 59. | [5 empty] | 48 | 48 | [5 empty] | 7182217 | 2007-01-01 | [23 empty] | 2012-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T5553317SP | TO->FROM |  | SUB 145 - JOPLIN WEST 7TH - SUB 439 - STATELINE 161KV CKT 1 | REL | EMDE | EMDE | JOPLIN | JOPLIN | 0 | 547498 | STL439 5 161.00 | 547470 | JOP145 5 161.00 | 0 |  | 1 | 17SP | 218 | 268 | 108.9 | 107.0874 | 108.8773 | [6 empty] | CATEGORYB | SINGLE | SUB 110 - ORONOGO JCT. - SUB 452 - RIVERTON 161KV CKT 1 | 0 | 547467 | ORO110 5 161.00 | 547469 | RIV4525 161.00 | 0 |  | 1 |  |  |  |  | EMDE | JOPLIN 59 - SUB 439 - STATELINE 161KV CKT 1 | Install new line from Sub #439 to new Sub Joplin 59. | [5 empty] | 48 | 48 | [5 empty] | 7182217 | 2007-01-01 | [23 empty] | 2012-06-01 | 2013-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T3443312SP | TO->FROM |  | SUB 145 - JOPLIN WEST 7TH - SUB 439 - STATELINE 161KV CKT 1 | REL | EMDE | EMDE | JOPLIN | JOPLIN | 0 | 547498 | STL439 5 161.00 | 547470 | JOP145 5 161.00 | 0 |  | 1 | 12SP | 218 | 268 |  | 97.9312 | 101.2328 | [6 empty] | CATEGORYB | SINGLE | SUB 110 - ORONOGO JCT. - SUB 452 - RIVERTON 161KV CKT 1 | 0 | 547467 | ORO110 5 161.00 | 547469 | RIV4525 161.00 | 0 |  | 1 |  |  |  |  | EMDE | JOPLIN 59 - SUB 59 - JOPLIN 26TH ST. 161/69kV TRANSFORMER CKT 1 | Install 3-wind transformer from 161 kV Joplin 59 bus to Sub #59 Joplin 26th St. | [5 empty] | 48 | 48 | [5 empty] | 9200000 | 2007-01-01 | [23 empty] | 2012-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T5553317SP | TO->FROM |  | SUB 145 - JOPLIN WEST 7TH - SUB 439 - STATELINE 161KV CKT 1 | REL | EMDE | EMDE | JOPLIN | JOPLIN | 0 | 547498 | STL439 5 161.00 | 547470 | JOP145 5 161.00 | 0 |  | 1 | 17SP | 218 | 268 | 108.9 | 107.0874 | 108.8773 | [6 empty] | CATEGORYB | SINGLE | SUB 110 - ORONOGO JCT. - SUB 452 - RIVERTON 161KV CKT 1 | 0 | 547467 | ORO110 5 161.00 | 547469 | RIV4525 161.00 | 0 |  | 1 |  |  |  |  | EMDE | JOPLIN 59 - SUB 59 - JOPLIN 26TH ST. 161/69kV TRANSFORMER CKT 1 | Install 3-wind transformer from 161 kV Joplin 59 bus to Sub #59 Joplin 26th St. | [5 empty] | 48 | 48 | [5 empty] | 9200000 | 2007-01-01 | [23 empty] | 2012-06-01 | 2013-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T292112WP | FROM->TO |  | KERR - PENSACOLA 115KV CKT 1 | EXP | GRDA | GRDA | GRDA-NEO | GRDA | 0 | 512634 | KERR GR3 115.00 | 512629 | PENSA 3 115.00 | 0 |  | 1 | 12WP | 76 | 97 |  | 100.9527 | 105.5731 | [6 empty] | CATEGORYB | SINGLE | MAID - PENSACOLA 161KV CKT 1 | 0 | 512648 | MAID 5 161.00 | 512654 | PENSA 5 161.00 | 0 |  | 1 |  |  |  |  | GRDA | KERR - PENSACOLA 115KV CKT 1 | Rebuild 22 miles of line from 4/0 Cu to 795 ACSR for 161kV | 162 | 186 | 194 | 214 | 22 | [7 empty] | 10450000 | 2007-04-16 | [23 empty] | 2012-12-01 | 2012-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T6932217SP | TO->FROM |  | KICKAPOO - SUNSET 69KV CKT 1 | EXP | SPRM | SPRM | SPRM | SPRM | 0 | 549907 | SUNSET 2 69.000 | 549906 | KICKAPO2 69.000 | 0 |  | 1 | 17SP | 103 | 108 | 107.2 | 72.7949 | 107.8767 | [6 empty] | CATEGORYB | SINGLE | JAMES RIVER - TWIN OAKS 69KV CKT 1 | 0 | 549904 | JRPS 2 69.000 | 549933 | TWINOAK2 69.000 | 0 |  | 1 |  |  |  |  | SPRM | KICKAPOO - SUNSET 69KV CKT 1 | Reconductor 69kV Line 636 MCM ACSR to 762.8 kcmil ACSS/TW 1.35 miles. | 153 | 159 | 153 | 159 | 1.35 | 24 | 2 | Outage | 0.0037 | 0.01887 | 0.00041 |  | 805000 | 2007-04-19 | [23 empty] | 2014-06-01 | 2014-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T5153217SP | FROM->TO |  | LAWRENCE HILL - MOCKINGBIRD HILL SWITCHING STATION 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533250 | LWRNCHL3 115.00 | 533253 | MOCKBRD3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 110.6 | 110.5852 | 109.9722 | [6 empty] | CATEGORYB | SINGLE | BISMARK JUNCTION SWITCHING STATION - FARMERS CONSUMER CO-OP 115KV CKT 1 | 0 | 533234 | BISMARK3 115.00 | 533236 | COOP 3 115.00 | 0 |  | 1 |  |  |  |  | WERE | LAWRENCE HILL - MOCKINGBIRD HILL SWITCHING STATION 115KV CKT 1 | Rebuild 5.49 mile line | [37 empty] | 2017-06-01 | 2017-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T27143217SP | FROM->TO |  | LAWRENCE HILL - MOCKINGBIRD HILL SWITCHING STATION 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533250 | LWRNCHL3 115.00 | 533253 | MOCKBRD3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 109.8 | 109.8461 | 109.2474 | [6 empty] | CATEGORYB | NONSINGLE | SPP-WERE-58 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | LAWRENCE HILL - MOCKINGBIRD HILL SWITCHING STATION 115KV CKT 1 | Rebuild 5.49 mile line | [37 empty] | 2017-06-01 | 2017-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T1052408SH | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 08SH | 32 | 32 |  | 25.2998 | 101.9869 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1872208SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 08SP | 32 | 32 |  | 29.7355 | 122.0877 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1862208SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 08SP | 32 | 32 |  | 26.3121 | 118.4294 | [6 empty] | CATEGORYB | SINGLE | ORCHARD - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533643 | ORCHARD2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T1652308SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 08SP | 32 | 32 |  | 12.5859 | 111.7993 | [6 empty] | CATEGORYB | SINGLE | ATHENS SWITCHING STATION - OWL CREEK 69KV CKT 1 | 0 | 533623 | ATHENS 2 69.000 | 533642 | OWL CRK2 69.000 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T1582408SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 08SP | 58 | 58 |  | 65.4461 | 103.802 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T1612408SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 08SP | 58 | 58 |  | 63.6438 | 101.879 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1492108SP | TO->FROM |  | LEHIGH TAP - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 08SP | 32 | 32 |  | 9.733 | 120.9169 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T1883309SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 09SP | 32 | 32 |  | 29.8705 | 124.2703 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T1873309SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 09SP | 32 | 32 |  | 26.4167 | 120.5106 | [6 empty] | CATEGORYB | SINGLE | ORCHARD - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533643 | ORCHARD2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T1833309SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 09SP | 32 | 32 |  | 12.6944 | 113.9161 | [6 empty] | CATEGORYB | SINGLE | ATHENS SWITCHING STATION - OWL CREEK 69KV CKT 1 | 0 | 533623 | ATHENS 2 69.000 | 533642 | OWL CRK2 69.000 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T1794409SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 09SP | 58 | 58 |  | 65.5805 | 104.7422 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T1824409SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 09SP | 58 | 58 |  | 63.7171 | 102.7839 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T6324109SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 09SP | 58 | 58 |  | 72.8628 | 100.1831 | [6 empty] | CATEGORYB | SINGLE | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81T1751409SP | TO->FROM |  | LEHIGH TAP - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 09SP | 32 | 32 |  | 8.7892 | 124.0056 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2451112SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12SP | 32 | 32 |  | -999 | 185.4455 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T8991112SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12SP | 32 | 32 |  | -999 | 184.8256 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T2942112SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12SP | 32 | 32 |  | 31.8691 | 130.8571 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2461112SP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 157.4692 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T9001112SP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 156.7557 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2471112SP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 12SP | 108 | 108 |  | -999 | 170.7109 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T9011112SP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 12SP | 108 | 108 |  | -999 | 170.0226 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2792412SP | TO->FROM |  | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 56.0845 | 117.3039 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2912412SP | TO->FROM |  | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 55.5503 | 112.3373 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1582212SP | TO->FROM |  | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 72.3233 | 103.7043 | [6 empty] | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2782412SP | FROM->TO |  | ALTOONA - TIOGA 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 41.4013 | 157.0806 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T2972112SP | FROM->TO |  | ALTOONA - TIOGA 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 40.3416 | 153.9666 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T2772112SP | FROM->TO |  | ALTOONA - TIOGA 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 35.1642 | 128.815 | [6 empty] | CATEGORYB | SINGLE | ALLEN - ZILA JUNCTION 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | NCONV |  |  | FNSL-Blown up | FDNS-Blown up | 2 | 3 | 2008-12-01 | 2007AG1AFS84L32312SP |  |  | ALTOONA - TIOGA 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 25.1844 | 72.1214 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2812412SP | TO->FROM | Bidirectional | ARCO TAP - ENA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533634 | ENA 2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | 51.9299 | 110.5372 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2431112SP | FROM->TO | Bidirectional | ARCO TAP - ENA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533620 | ARCOTAP2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 108.209 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T8971112SP | FROM->TO | Bidirectional | ARCO TAP - ENA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533620 | ARCOTAP2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 107.7968 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2441112SP | TO->FROM | Bidirectional | ARCO TAP - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533641 | MONARCH2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 111.7972 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T8981112SP | TO->FROM | Bidirectional | ARCO TAP - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533641 | MONARCH2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 111.3621 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2822412SP | FROM->TO | Bidirectional | ARCO TAP - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533620 | ARCOTAP2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | 49.4684 | 107.2233 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2662412SP | FROM->TO |  | ATHENS SWITCHING STATION - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533623 | ATHENS 2 69.000 | 533642 | OWL CRK2 69.000 | 0 |  | 1 | 12SP | 41 | 41 |  | 10.1577 | 122.0473 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2832412SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12SP | 58 | 58 |  | 67.3281 | 140.9509 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T3022112SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12SP | 58 | 58 |  | 65.3825 | 136.6898 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2481112SP | FROM->TO | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533634 | ENA 2 69.000 | 533646 | TIOGA 2 69.000 | 0 |  | 1 | 12SP | 58 | 58 |  | -999 | 130.2259 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2672412SP | TO->FROM |  | LEHIGH TAP - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12SP | 32 | 32 |  | 9.2569 | 152.3867 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2491112SP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 12SP | 100 | 100 |  | -999 | 193.7517 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T9031112SP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 12SP | 100 | 100 |  | -999 | 192.9783 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2501112SP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 12SP | 108 | 108 |  | -999 | 178.3467 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T9041112SP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 12SP | 108 | 108 |  | -999 | 177.6278 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T572112WP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12WP | 32 | 32 |  | 24.6721 | 179.9951 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T3802112WP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12WP | 32 | 32 |  | 24.8481 | 179.8879 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T574312WP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12WP | 32 | 32 |  | 22.9815 | 100.7665 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T582112WP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 39.9857 | 150.9578 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T3812112WP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 40.0893 | 150.8733 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T553312WP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 12WP | 108 | 108 |  | 36.4684 | 159.2099 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T3843312WP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 12WP | 108 | 108 |  | 36.5782 | 159.1568 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T464112WP | FROM->TO | Bidirectional | ARCO TAP - ENA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533620 | ARCOTAP2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 9.7864 | 101.0901 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T3394112WP | FROM->TO | Bidirectional | ARCO TAP - ENA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533620 | ARCOTAP2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 10.0489 | 100.9961 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T474112WP | TO->FROM | Bidirectional | ARCO TAP - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533641 | MONARCH2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 11.0682 | 103.599 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T3404112WP | TO->FROM | Bidirectional | ARCO TAP - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533641 | MONARCH2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 11.2882 | 103.5055 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T514112WP | FROM->TO | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533634 | ENA 2 69.000 | 533646 | TIOGA 2 69.000 | 0 |  | 1 | 12WP | 58 | 58 |  | 10.7435 | 122.8447 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T3444112WP | FROM->TO | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533634 | ENA 2 69.000 | 533646 | TIOGA 2 69.000 | 0 |  | 1 | 12WP | 58 | 58 |  | 11.1297 | 122.7501 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81T964212WP | TO->FROM |  | LEHIGH TAP - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12WP | 32 | 32 |  | 7.335 | 100.4311 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T593312WP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 12WP | 100 | 100 |  | 44.6309 | 179.6932 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T3883312WP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 12WP | 100 | 100 |  | 44.776 | 179.5805 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T613312WP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 12WP | 108 | 108 |  | 40.4185 | 165.4322 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T3024312WP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 12WP | 108 | 108 |  | 40.5965 | 165.359 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4092317SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 17SP | 32 | 32 |  | 14.5581 | 132.3017 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16612317SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 17SP | 32 | 32 |  | 14.4858 | 131.4416 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4832317SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 17SP | 32 | 32 |  | 35.6597 | 126.9833 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4102317SP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 17SP | 72 | 72 |  | 23.268 | 100.8105 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16622317SP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 17SP | 72 | 72 |  | 23.1386 | 100.3044 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4112317SP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 17SP | 108 | 108 |  | 28.8307 | 116.5141 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16632317SP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 17SP | 108 | 108 |  | 28.7177 | 115.9243 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T6122417SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 17SP | 58 | 58 |  | 70.7819 | 101.4296 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T4742117SP | TO->FROM |  | LEHIGH TAP - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 17SP | 32 | 32 |  | 11.392 | 117.9501 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4122317SP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 17SP | 100 | 100 |  | 38.8083 | 133.7621 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16642317SP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 17SP | 100 | 100 |  | 38.688 | 133.0647 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4132317SP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 17SP | 108 | 108 |  | 34.6116 | 122.4871 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16652317SP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 17SP | 108 | 108 |  | 34.4969 | 121.8479 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 3 | 2008-12-01 | 2007AG1AFS81T31308SP | FROM->TO |  | LEHIGH TAP - UNITED NO. 9 CONGER 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533638 | LEHIGTP2 69.000 | 533651 | UN9CONG2 69.000 | 0 |  | 1 | 08SP | 32 | 32 |  | 9.7113 | 105.3951 | [6 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | LEHIGH TAP - UNITED NO. 9 CONGER 69KV CKT 1 | Tear down / Rebuild 0.91-mile 69 kV line; 954 kcmiol ACSR | 72 | 72 | 72 | 72 | 0.91 | 12 | 6 |  | 0.002 | 0.014 | 0.00031 | 72 MVA limit is switches | 236391 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T31109SP | FROM->TO |  | LEHIGH TAP - UNITED NO. 9 CONGER 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533638 | LEHIGTP2 69.000 | 533651 | UN9CONG2 69.000 | 0 |  | 1 | 09SP | 32 | 32 |  | 9.8401 | 107.5866 | [6 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | LEHIGH TAP - UNITED NO. 9 CONGER 69KV CKT 1 | Tear down / Rebuild 0.91-mile 69 kV line; 954 kcmiol ACSR | 72 | 72 | 72 | 72 | 0.91 | 12 | 6 |  | 0.002 | 0.014 | 0.00031 | 72 MVA limit is switches | 236391 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 1 | 2008-12-01 | 2007AG1AFS81T14013112SP | FROM->TO |  | LEHIGH TAP - UNITED NO. 9 CONGER 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533638 | LEHIGTP2 69.000 | 533651 | UN9CONG2 69.000 | 0 |  | 1 | 12SP | 32 | 32 |  | 10.2292 | 112.0964 | [6 empty] | CATEGORYB | GENOUT | GEN533637 2-CITY OF IOLA | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | LEHIGH TAP - UNITED NO. 9 CONGER 69KV CKT 1 | Tear down / Rebuild 0.91-mile 69 kV line; 954 kcmiol ACSR | 72 | 72 | 72 | 72 | 0.91 | 12 | 6 |  | 0.002 | 0.014 | 0.00031 | 72 MVA limit is switches | 236391 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T82412SP | FROM->TO |  | LEHIGH TAP - UNITED NO. 9 CONGER 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533638 | LEHIGTP2 69.000 | 533651 | UN9CONG2 69.000 | 0 |  | 1 | 12SP | 32 | 32 |  | 10.2574 | 111.6966 | [6 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | LEHIGH TAP - UNITED NO. 9 CONGER 69KV CKT 1 | Tear down / Rebuild 0.91-mile 69 kV line; 954 kcmiol ACSR | 72 | 72 | 72 | 72 | 0.91 | 12 | 6 |  | 0.002 | 0.014 | 0.00031 | 72 MVA limit is switches | 236391 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T622112WP | FROM->TO |  | LEHIGH TAP - UNITED NO. 9 CONGER 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533638 | LEHIGTP2 69.000 | 533651 | UN9CONG2 69.000 | 0 |  | 1 | 12WP | 32 | 32 |  | 7.3147 | 139.5966 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | LEHIGH TAP - UNITED NO. 9 CONGER 69KV CKT 1 | Tear down / Rebuild 0.91-mile 69 kV line; 954 kcmiol ACSR | 72 | 72 | 72 | 72 | 0.91 | 12 | 6 |  | 0.002 | 0.014 | 0.00031 | 72 MVA limit is switches | 236391 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T3852112WP | FROM->TO |  | LEHIGH TAP - UNITED NO. 9 CONGER 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533638 | LEHIGTP2 69.000 | 533651 | UN9CONG2 69.000 | 0 |  | 1 | 12WP | 32 | 32 |  | 7.3465 | 139.5575 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | LEHIGH TAP - UNITED NO. 9 CONGER 69KV CKT 1 | Tear down / Rebuild 0.91-mile 69 kV line; 954 kcmiol ACSR | 72 | 72 | 72 | 72 | 0.91 | 12 | 6 |  | 0.002 | 0.014 | 0.00031 | 72 MVA limit is switches | 236391 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T32572217SP | FROM->TO |  | LEHIGH TAP - UNITED NO. 9 CONGER 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533638 | LEHIGTP2 69.000 | 533651 | UN9CONG2 69.000 | 0 |  | 1 | 17SP | 32 | 32 |  | 11.2847 | 121.4824 | [6 empty] | CATEGORYB | GENOUT | GEN533637 2-CITY OF IOLA | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | LEHIGH TAP - UNITED NO. 9 CONGER 69KV CKT 1 | Tear down / Rebuild 0.91-mile 69 kV line; 954 kcmiol ACSR | 72 | 72 | 72 | 72 | 0.91 | 12 | 6 |  | 0.002 | 0.014 | 0.00031 | 72 MVA limit is switches | 236391 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T142417SP | FROM->TO |  | LEHIGH TAP - UNITED NO. 9 CONGER 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533638 | LEHIGTP2 69.000 | 533651 | UN9CONG2 69.000 | 0 |  | 1 | 17SP | 32 | 32 |  | 11.2829 | 102.7238 | [6 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | LEHIGH TAP - UNITED NO. 9 CONGER 69KV CKT 1 | Tear down / Rebuild 0.91-mile 69 kV line; 954 kcmiol ACSR | 72 | 72 | 72 | 72 | 0.91 | 12 | 6 |  | 0.002 | 0.014 | 0.00031 | 72 MVA limit is switches | 236391 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T5683217SP | FROM->TO |  | AQUARIUS - HUDSON JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533756 | AQUARS 2 69.000 | 533764 | HUDSJCT2 69.000 | 0 |  | 1 | 17SP | 72 | 72 | 103.7 | 100.8002 | 111.1636 | [6 empty] | CATEGORYB | SINGLE | LITCHFIELD - ROUSE 69KV CKT 1 | 0 | 533765 | LITCH 2 69.000 | 533771 | ROUSE 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | LITCHFIELD - AQUARIUS - HUDSON JUNCTION 69KV CKT 1 Displacement | Replace 69 kV disconnect switches at Aquarius. | 80 | 80 | 80 | 80 | [8 empty] | 30000 | 2007-01-01 | [23 empty] | 2014-06-01 | 2014-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T5693217SP | TO->FROM |  | AQUARIUS - LITCHFIELD 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533765 | LITCH 2 69.000 | 533756 | AQUARS 2 69.000 | 0 |  | 1 | 17SP | 72 | 72 | 104.7 | 101.7829 | 112.1583 | [6 empty] | CATEGORYB | SINGLE | LITCHFIELD - ROUSE 69KV CKT 1 | 0 | 533765 | LITCH 2 69.000 | 533771 | ROUSE 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | LITCHFIELD - AQUARIUS - HUDSON JUNCTION 69KV CKT 1 Displacement | Replace 69 kV disconnect switches at Aquarius. | 80 | 80 | 80 | 80 | [8 empty] | 30000 | 2007-01-01 | [23 empty] | 2014-06-01 | 2014-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T6762109SP | TO->FROM |  | LONGVIEW - SAMPSON 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541345 | SAMPSON5 161.00 | 541224 | LNGVW 5 161.00 | 0 |  | 1 | 09SP | 223 | 245 |  | 63.926 | 100.2341 | [6 empty] | CATEGORYB | SINGLE | PLEASANT HILL () 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 541200 | PHILL 7 345.00 | 541225 | PHILL 5 161.00 | 541361 | PHILL T 13.800 | 1 |  |  |  | Replace the wavetraps on GrandviewEast-Longview | MIPU | LONGVIEW - SAMPSON 161KV CKT 1 | Increase the normal/emergency ratings to 233/265 MVA by replacing wave trapes | 233 | 265 | [10 empty] | 180000 | [24 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T6762109SP | TO->FROM |  | LONGVIEW - SAMPSON 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541345 | SAMPSON5 161.00 | 541224 | LNGVW 5 161.00 | 0 |  | 1 | 09SP | 223 | 245 |  | 63.926 | 100.2341 | [6 empty] | CATEGORYB | SINGLE | PLEASANT HILL () 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 541200 | PHILL 7 345.00 | 541225 | PHILL 5 161.00 | 541361 | PHILL T 13.800 | 1 |  |  |  | Replace the wavetraps on GrandviewEast-Longview | MIPU | LONGVIEW - SAMPSON 161KV CKT 1 | Increase the normal/emergency ratings to 233/265 MVA by replacing wave trapes | 233 | 265 | [10 empty] | 180000 | [24 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T9494312SP | TO->FROM |  | LONGVIEW - SAMPSON 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541345 | SAMPSON5 161.00 | 541224 | LNGVW 5 161.00 | 0 |  | 1 | 12SP | 223 | 245 |  | 102.7537 | 105.5207 | [6 empty] | CATEGORYB | SINGLE | PLEASANT HILL () 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 541200 | PHILL 7 345.00 | 541225 | PHILL 5 161.00 | 541361 | PHILL T 13.800 | 1 |  |  |  | Replace the wavetraps on GrandviewEast-Longview | MIPU | LONGVIEW - SAMPSON 161KV CKT 1 | Increase the normal/emergency ratings to 233/265 MVA by replacing wave trapes | 233 | 265 | [10 empty] | 180000 | [24 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T9494312SP | TO->FROM |  | LONGVIEW - SAMPSON 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541345 | SAMPSON5 161.00 | 541224 | LNGVW 5 161.00 | 0 |  | 1 | 12SP | 223 | 245 |  | 102.7537 | 105.5207 | [6 empty] | CATEGORYB | SINGLE | PLEASANT HILL () 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 541200 | PHILL 7 345.00 | 541225 | PHILL 5 161.00 | 541361 | PHILL T 13.800 | 1 |  |  |  | Replace the wavetraps on GrandviewEast-Longview | MIPU | LONGVIEW - SAMPSON 161KV CKT 1 | Increase the normal/emergency ratings to 233/265 MVA by replacing wave trapes | 233 | 265 | [10 empty] | 180000 | [24 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T794112WP | TO->FROM |  | LONGVIEW - SAMPSON 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541345 | SAMPSON5 161.00 | 541224 | LNGVW 5 161.00 | 0 |  | 1 | 12WP | 223 | 245 |  | 98.0812 | 100.2211 | [6 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 |  |  |  | Replace the wavetraps on GrandviewEast-Longview | MIPU | LONGVIEW - SAMPSON 161KV CKT 1 | Increase the normal/emergency ratings to 233/265 MVA by replacing wave trapes | 233 | 265 | [10 empty] | 180000 | [24 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T794112WP | TO->FROM |  | LONGVIEW - SAMPSON 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541345 | SAMPSON5 161.00 | 541224 | LNGVW 5 161.00 | 0 |  | 1 | 12WP | 223 | 245 |  | 98.0812 | 100.2211 | [6 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 |  |  |  | Replace the wavetraps on GrandviewEast-Longview | MIPU | LONGVIEW - SAMPSON 161KV CKT 1 | Increase the normal/emergency ratings to 233/265 MVA by replacing wave trapes | 233 | 265 | [10 empty] | 180000 | [24 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T17252317SP | TO->FROM |  | LONGVIEW - SAMPSON 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541345 | SAMPSON5 161.00 | 541224 | LNGVW 5 161.00 | 0 |  | 1 | 17SP | 223 | 245 |  | 68.2298 | 105.1094 | [6 empty] | CATEGORYB | SINGLE | PLEASANT HILL () 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 541200 | PHILL 7 345.00 | 541225 | PHILL 5 161.00 | 541361 | PHILL T 13.800 | 1 |  |  |  | Replace the wavetraps on GrandviewEast-Longview | MIPU | LONGVIEW - SAMPSON 161KV CKT 1 | Increase the normal/emergency ratings to 233/265 MVA by replacing wave trapes | 233 | 265 | [10 empty] | 180000 | [24 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T17252317SP | TO->FROM |  | LONGVIEW - SAMPSON 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541345 | SAMPSON5 161.00 | 541224 | LNGVW 5 161.00 | 0 |  | 1 | 17SP | 223 | 245 |  | 68.2298 | 105.1094 | [6 empty] | CATEGORYB | SINGLE | PLEASANT HILL () 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 541200 | PHILL 7 345.00 | 541225 | PHILL 5 161.00 | 541361 | PHILL T 13.800 | 1 |  |  |  | Replace the wavetraps on GrandviewEast-Longview | MIPU | LONGVIEW - SAMPSON 161KV CKT 1 | Increase the normal/emergency ratings to 233/265 MVA by replacing wave trapes | 233 | 265 | [10 empty] | 180000 | [24 empty] | 2009-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T9292209SP | FROM->TO |  | MAGAZINE REC - NORTH MAGAZINE 161KV CKT 1 | CP | AEPW | AEPW | GRWDAECC | GRENWOOD | 0 | 507195 | MAGZREC5 161.00 | 507190 | NMAGZIN5 161.00 | 0 |  | 1 | 09SP | 127 | 155 | 106.1 | 106.0974 | 114.4811 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 |  |  |  | Per MW-Mile files, 47.6% AEPW, 47.6% EES, 4.8 OKGE of 7.43 miles. | AEPW | MAGAZINE REC - NORTH MAGAZINE 161KV CKT 1 AEPW | Rebuild 7.43 miles of 250 CWC with 795 ACSR | 166 | 223 | 207 | 252 | 7.43 | 20 | 9 |  | 0.0037 | 0.020613 | 0.0114 | New limits will be jumpers @ N. Magazine. This line is an Arklahoma line. | 3522400 | 2007-09-18 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T9292209SP | FROM->TO |  | MAGAZINE REC - NORTH MAGAZINE 161KV CKT 1 | CP | AEPW | AEPW | GRWDAECC | GRENWOOD | 0 | 507195 | MAGZREC5 161.00 | 507190 | NMAGZIN5 161.00 | 0 |  | 1 | 09SP | 127 | 155 | 106.1 | 106.0974 | 114.4811 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 |  |  |  | Per MW-Mile files, 47.6% AEPW, 47.6% EES, 4.8 OKGE of 7.43 miles. | ENTR | MAGAZINE REC - NORTH MAGAZINE 161KV CKT 1 ENTR | Rebuild 7.43 miles of 250 CWC with 795 ACSR | 166 | 223 | 207 | 252 | 7.43 | 20 | 9 |  | 0.0037 | 0.020613 | 0.0114 | New limits will be jumpers @ N. Magazine. This line is an Arklahoma line. | 3522400 | 2007-09-18 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T9292209SP | FROM->TO |  | MAGAZINE REC - NORTH MAGAZINE 161KV CKT 1 | CP | AEPW | AEPW | GRWDAECC | GRENWOOD | 0 | 507195 | MAGZREC5 161.00 | 507190 | NMAGZIN5 161.00 | 0 |  | 1 | 09SP | 127 | 155 | 106.1 | 106.0974 | 114.4811 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 |  |  |  | Per MW-Mile files, 47.6% AEPW, 47.6% EES, 4.8 OKGE of 7.43 miles. | OKGE | MAGAZINE REC - NORTH MAGAZINE 161KV CKT 1 OKGE | Rebuild 7.43 miles of 250 CWC with 795 ACSR | 166 | 223 | 207 | 252 | 7.43 | 20 | 9 |  | 0.0037 | 0.020613 | 0.0114 | New limits will be jumpers @ N. Magazine. This line is an Arklahoma line. | 355200 | 2007-09-18 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T1962309SP | TO->FROM |  | MARTIN CITY - REDEL 161KV CKT 1 | S | KACP | KACP | JOCO | METRO | 0 | 543053 | REDEL 5 161.00 | 543002 | MARTCIT5 161.00 | 0 |  | 1 | 09SP | 293 | 335 |  | 91.4726 | 108.6632 | 541_MARTIN CITY - REDEL 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | PECULIAR - STILWELL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | KACP | MARTIN CITY - REDEL 161KV CKT 1 | Reconductor 1192 acss upgrade terminal equip 2000 amp | 558 | 558 | 558 | 558 | 4 | 24 | 4 | [5 empty] | 2000000 | 2008-02-21 | [23 empty] | 2009-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T3422312SP | TO->FROM |  | MARTIN CITY - REDEL 161KV CKT 1 | S | KACP | KACP | JOCO | METRO | 0 | 543053 | REDEL 5 161.00 | 543002 | MARTCIT5 161.00 | 0 |  | 1 | 12SP | 293 | 335 |  | 93.664 | 112.051 | 541_MARTIN CITY - REDEL 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | PECULIAR - STILWELL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | KACP | MARTIN CITY - REDEL 161KV CKT 1 | Reconductor 1192 acss upgrade terminal equip 2000 amp | 558 | 558 | 558 | 558 | 4 | 24 | 4 | [5 empty] | 2000000 | 2008-02-21 | [23 empty] | 2009-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T5362317SP | TO->FROM |  | MARTIN CITY - REDEL 161KV CKT 1 | S | KACP | KACP | JOCO | METRO | 0 | 543053 | REDEL 5 161.00 | 543002 | MARTCIT5 161.00 | 0 |  | 1 | 17SP | 293 | 335 |  | 79.503 | 102.4256 | 541_MARTIN CITY - REDEL 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | PECULIAR - STILWELL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | KACP | MARTIN CITY - REDEL 161KV CKT 1 | Reconductor 1192 acss upgrade terminal equip 2000 amp | 558 | 558 | 558 | 558 | 4 | 24 | 4 | [5 empty] | 2000000 | 2008-02-21 | [23 empty] | 2009-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T752108SH | TO->FROM |  | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541259 | TURNER 5 161.00 | 541210 | MARTCTY5 161.00 | 0 |  | 1 | 08SH | 233 | 250 | 108.8 | 109.2044 | 110.1035 | 540_MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | Upgrade to bundled 795 26/7 ACSR conductor | 466 | 558 |  |  | 5.5 | 24 |  |  | 0.00161 | 0.01357 | 0.01317 |  | 4244500 | 2006-06-01 | [23 empty] | 2008-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T752108SH | TO->FROM |  | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541259 | TURNER 5 161.00 | 541210 | MARTCTY5 161.00 | 0 |  | 1 | 08SH | 233 | 250 | 108.8 | 109.2044 | 110.1035 | 540_MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | Upgrade to bundled 795 26/7 ACSR conductor | 466 | 558 |  |  | 5.5 | 24 |  |  | 0.00161 | 0.01357 | 0.01317 |  | 4244500 | 2006-06-01 | [23 empty] | 2008-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1612108SP | TO->FROM |  | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541259 | TURNER 5 161.00 | 541210 | MARTCTY5 161.00 | 0 |  | 1 | 08SP | 233 | 250 | 110.4 | 110.7833 | 111.1457 | 540_MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | Upgrade to bundled 795 26/7 ACSR conductor | 466 | 558 |  |  | 5.5 | 24 |  |  | 0.00161 | 0.01357 | 0.01317 |  | 4244500 | 2006-06-01 | [23 empty] | 2008-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1612108SP | TO->FROM |  | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541259 | TURNER 5 161.00 | 541210 | MARTCTY5 161.00 | 0 |  | 1 | 08SP | 233 | 250 | 110.4 | 110.7833 | 111.1457 | 540_MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | Upgrade to bundled 795 26/7 ACSR conductor | 466 | 558 |  |  | 5.5 | 24 |  |  | 0.00161 | 0.01357 | 0.01317 |  | 4244500 | 2006-06-01 | [23 empty] | 2008-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1742109SP | TO->FROM |  | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541259 | TURNER 5 161.00 | 541210 | MARTCTY5 161.00 | 0 |  | 1 | 09SP | 233 | 250 | 113.6 | 113.8691 | 116.7901 | 540_MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | Upgrade to bundled 795 26/7 ACSR conductor | 466 | 558 |  |  | 5.5 | 24 |  |  | 0.00161 | 0.01357 | 0.01317 |  | 4244500 | 2006-06-01 | [23 empty] | 2008-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1742109SP | TO->FROM |  | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541259 | TURNER 5 161.00 | 541210 | MARTCTY5 161.00 | 0 |  | 1 | 09SP | 233 | 250 | 113.6 | 113.8691 | 116.7901 | 540_MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | Upgrade to bundled 795 26/7 ACSR conductor | 466 | 558 |  |  | 5.5 | 24 |  |  | 0.00161 | 0.01357 | 0.01317 |  | 4244500 | 2006-06-01 | [23 empty] | 2008-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1902109SP | TO->FROM |  | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541259 | TURNER 5 161.00 | 541210 | MARTCTY5 161.00 | 0 |  | 1 | 09SP | 233 | 250 | 101.2 | 101.4941 | 103.8892 | 540_MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | REDEL - STILWELL 161KV CKT 1 | 0 | 542969 | STILWEL5 161.00 | 543053 | REDEL 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | Upgrade to bundled 795 26/7 ACSR conductor | 466 | 558 |  |  | 5.5 | 24 |  |  | 0.00161 | 0.01357 | 0.01317 |  | 4244500 | 2006-06-01 | [23 empty] | 2008-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1902109SP | TO->FROM |  | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541259 | TURNER 5 161.00 | 541210 | MARTCTY5 161.00 | 0 |  | 1 | 09SP | 233 | 250 | 101.2 | 101.4941 | 103.8892 | 540_MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | REDEL - STILWELL 161KV CKT 1 | 0 | 542969 | STILWEL5 161.00 | 543053 | REDEL 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | Upgrade to bundled 795 26/7 ACSR conductor | 466 | 558 |  |  | 5.5 | 24 |  |  | 0.00161 | 0.01357 | 0.01317 |  | 4244500 | 2006-06-01 | [23 empty] | 2008-06-01 | 2013-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1912109SP | TO->FROM |  | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541259 | TURNER 5 161.00 | 541210 | MARTCTY5 161.00 | 0 |  | 1 | 09SP | 233 | 250 |  | 98.3936 | 100.7416 | 540_MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | MARTIN CITY - REDEL 161KV CKT 1 | 0 | 543002 | MARTCIT5 161.00 | 543053 | REDEL 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | Upgrade to bundled 795 26/7 ACSR conductor | 466 | 558 |  |  | 5.5 | 24 |  |  | 0.00161 | 0.01357 | 0.01317 |  | 4244500 | 2006-06-01 | [23 empty] | 2008-06-01 | 2013-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1912109SP | TO->FROM |  | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541259 | TURNER 5 161.00 | 541210 | MARTCTY5 161.00 | 0 |  | 1 | 09SP | 233 | 250 |  | 98.3936 | 100.7416 | 540_MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | MARTIN CITY - REDEL 161KV CKT 1 | 0 | 543002 | MARTCIT5 161.00 | 543053 | REDEL 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | Upgrade to bundled 795 26/7 ACSR conductor | 466 | 558 |  |  | 5.5 | 24 |  |  | 0.00161 | 0.01357 | 0.01317 |  | 4244500 | 2006-06-01 | [23 empty] | 2008-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T2884312SP | TO->FROM |  | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541259 | TURNER 5 161.00 | 541210 | MARTCTY5 161.00 | 0 |  | 1 | 12SP | 233 | 250 | 113.6 | 114.6627 | 116.7009 | 540_MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | Upgrade to bundled 795 26/7 ACSR conductor | 466 | 558 |  |  | 5.5 | 24 |  |  | 0.00161 | 0.01357 | 0.01317 |  | 4244500 | 2006-06-01 | [23 empty] | 2008-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T2884312SP | TO->FROM |  | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541259 | TURNER 5 161.00 | 541210 | MARTCTY5 161.00 | 0 |  | 1 | 12SP | 233 | 250 | 113.6 | 114.6627 | 116.7009 | 540_MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | Upgrade to bundled 795 26/7 ACSR conductor | 466 | 558 |  |  | 5.5 | 24 |  |  | 0.00161 | 0.01357 | 0.01317 |  | 4244500 | 2006-06-01 | [23 empty] | 2008-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T3164312SP | TO->FROM |  | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541259 | TURNER 5 161.00 | 541210 | MARTCTY5 161.00 | 0 |  | 1 | 12SP | 233 | 250 | 107.5 | 108.3088 | 109.1513 | 540_MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | REDEL - STILWELL 161KV CKT 1 | 0 | 542969 | STILWEL5 161.00 | 543053 | REDEL 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | Upgrade to bundled 795 26/7 ACSR conductor | 466 | 558 |  |  | 5.5 | 24 |  |  | 0.00161 | 0.01357 | 0.01317 |  | 4244500 | 2006-06-01 | [23 empty] | 2008-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T3164312SP | TO->FROM |  | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541259 | TURNER 5 161.00 | 541210 | MARTCTY5 161.00 | 0 |  | 1 | 12SP | 233 | 250 | 107.5 | 108.3088 | 109.1513 | 540_MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | REDEL - STILWELL 161KV CKT 1 | 0 | 542969 | STILWEL5 161.00 | 543053 | REDEL 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | Upgrade to bundled 795 26/7 ACSR conductor | 466 | 558 |  |  | 5.5 | 24 |  |  | 0.00161 | 0.01357 | 0.01317 |  | 4244500 | 2006-06-01 | [23 empty] | 2008-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T3094312SP | TO->FROM |  | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541259 | TURNER 5 161.00 | 541210 | MARTCTY5 161.00 | 0 |  | 1 | 12SP | 233 | 250 | 104.3 | 104.8655 | 105.938 | 540_MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | BELTON SOUTH 161/69KV TRANSFORMER CKT 1 | 0 | 541290 | BELTONS2 69.000 | 541340 | BELTONS5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | Upgrade to bundled 795 26/7 ACSR conductor | 466 | 558 |  |  | 5.5 | 24 |  |  | 0.00161 | 0.01357 | 0.01317 |  | 4244500 | 2006-06-01 | [23 empty] | 2008-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T3094312SP | TO->FROM |  | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541259 | TURNER 5 161.00 | 541210 | MARTCTY5 161.00 | 0 |  | 1 | 12SP | 233 | 250 | 104.3 | 104.8655 | 105.938 | 540_MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | BELTON SOUTH 161/69KV TRANSFORMER CKT 1 | 0 | 541290 | BELTONS2 69.000 | 541340 | BELTONS5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | Upgrade to bundled 795 26/7 ACSR conductor | 466 | 558 |  |  | 5.5 | 24 |  |  | 0.00161 | 0.01357 | 0.01317 |  | 4244500 | 2006-06-01 | [23 empty] | 2008-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T774112WP | TO->FROM |  | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541259 | TURNER 5 161.00 | 541210 | MARTCTY5 161.00 | 0 |  | 1 | 12WP | 233 | 250 | 110.1 | 110.3217 | 110.6953 | 540_MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | Upgrade to bundled 795 26/7 ACSR conductor | 466 | 558 |  |  | 5.5 | 24 |  |  | 0.00161 | 0.01357 | 0.01317 |  | 4244500 | 2006-06-01 | [23 empty] | 2008-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T774112WP | TO->FROM |  | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541259 | TURNER 5 161.00 | 541210 | MARTCTY5 161.00 | 0 |  | 1 | 12WP | 233 | 250 | 110.1 | 110.3217 | 110.6953 | 540_MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | Upgrade to bundled 795 26/7 ACSR conductor | 466 | 558 |  |  | 5.5 | 24 |  |  | 0.00161 | 0.01357 | 0.01317 |  | 4244500 | 2006-06-01 | [23 empty] | 2008-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T4784317SP | TO->FROM |  | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541259 | TURNER 5 161.00 | 541210 | MARTCTY5 161.00 | 0 |  | 1 | 17SP | 233 | 250 | 115.4 | 116.9061 | 116.2929 | 540_MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | Upgrade to bundled 795 26/7 ACSR conductor | 466 | 558 |  |  | 5.5 | 24 |  |  | 0.00161 | 0.01357 | 0.01317 |  | 4244500 | 2006-06-01 | [23 empty] | 2008-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T4784317SP | TO->FROM |  | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541259 | TURNER 5 161.00 | 541210 | MARTCTY5 161.00 | 0 |  | 1 | 17SP | 233 | 250 | 115.4 | 116.9061 | 116.2929 | 540_MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | Upgrade to bundled 795 26/7 ACSR conductor | 466 | 558 |  |  | 5.5 | 24 |  |  | 0.00161 | 0.01357 | 0.01317 |  | 4244500 | 2006-06-01 | [23 empty] | 2008-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T5074317SP | TO->FROM |  | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541259 | TURNER 5 161.00 | 541210 | MARTCTY5 161.00 | 0 |  | 1 | 17SP | 233 | 250 | 110.8 | 111.7503 | 110.4548 | 540_MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | REDEL - STILWELL 161KV CKT 1 | 0 | 542969 | STILWEL5 161.00 | 543053 | REDEL 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | Upgrade to bundled 795 26/7 ACSR conductor | 466 | 558 |  |  | 5.5 | 24 |  |  | 0.00161 | 0.01357 | 0.01317 |  | 4244500 | 2006-06-01 | [23 empty] | 2008-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T5074317SP | TO->FROM |  | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541259 | TURNER 5 161.00 | 541210 | MARTCTY5 161.00 | 0 |  | 1 | 17SP | 233 | 250 | 110.8 | 111.7503 | 110.4548 | 540_MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | REDEL - STILWELL 161KV CKT 1 | 0 | 542969 | STILWEL5 161.00 | 543053 | REDEL 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | Upgrade to bundled 795 26/7 ACSR conductor | 466 | 558 |  |  | 5.5 | 24 |  |  | 0.00161 | 0.01357 | 0.01317 |  | 4244500 | 2006-06-01 | [23 empty] | 2008-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T5144317SP | TO->FROM |  | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541259 | TURNER 5 161.00 | 541210 | MARTCTY5 161.00 | 0 |  | 1 | 17SP | 233 | 250 | 107.0 | 108.0073 | 106.7711 | 540_MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | MARTIN CITY - REDEL 161KV CKT 1 | 0 | 543002 | MARTCIT5 161.00 | 543053 | REDEL 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | Upgrade to bundled 795 26/7 ACSR conductor | 466 | 558 |  |  | 5.5 | 24 |  |  | 0.00161 | 0.01357 | 0.01317 |  | 4244500 | 2006-06-01 | [23 empty] | 2008-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T5144317SP | TO->FROM |  | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541259 | TURNER 5 161.00 | 541210 | MARTCTY5 161.00 | 0 |  | 1 | 17SP | 233 | 250 | 107.0 | 108.0073 | 106.7711 | 540_MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | MARTIN CITY - REDEL 161KV CKT 1 | 0 | 543002 | MARTCIT5 161.00 | 543053 | REDEL 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | Upgrade to bundled 795 26/7 ACSR conductor | 466 | 558 |  |  | 5.5 | 24 |  |  | 0.00161 | 0.01357 | 0.01317 |  | 4244500 | 2006-06-01 | [23 empty] | 2008-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T6022317SP | FROM->TO |  | MERRIAM - ROELAND PARK 161KV CKT 1 | EXP | KACP | KACP | JOCO | JOCO | 0 | 543032 | MERRIAM5 161.00 | 543040 | ROEPARK5 161.00 | 0 |  | 1 | 17SP | 187 | 212 | 101.8 | 101.005 | 101.6926 | 541_MERRIAM - ROELAND PARK 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | FOREST - SOUTHTOWN 161KV CKT 1 | 0 | 542993 | STHTOWN5 161.00 | 543001 | FOREST 5 161.00 | 0 |  | 1 |  |  |  |  | KACP | MERRIAM - ROELAND PARK 161KV CKT 1 | reconductor with 1192 acsr; upgrade term equip 1200 A | 293 | 335 | 335 | 335 | 4 | 24 | 4 | [5 empty] | 2200000 | 2008-02-21 | [23 empty] | 2017-06-01 | 2017-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T3973212SP | TO->FROM |  | NEERGARD - NORTON 69KV CKT 1 | EXP | SPRM | SPRM | SPRM | SPRM | 0 | 549928 | NORTON 2 69.000 | 549930 | NEERGRD2 69.000 | 0 |  | 1 | 12SP | 66 | 70 | 109.5 | 72.1863 | 110.241 | [6 empty] | CATEGORYB | SINGLE | MILL - PACKER 69KV CKT 1 | 0 | 549918 | MILL 2 69.000 | 549932 | PACKER 2 69.000 | 0 |  | 1 |  |  |  |  | SPRM | NEERGARD - NORTON 69KV CKT 1 | Transfer load & Reconductor 336.4 kcmil ACSR with 477 ACSS/TW | 111 | 115 | 111 | 115 | 2.6 | 24 | 2 | Outage | 0.01132 | 0.0367 | 0.00081 | SPRM will reconductor by 2010; Load will be transferred prior to project completion for short-term mitigation. | 1485000 | 2007-04-19 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T3973212SP | TO->FROM |  | NEERGARD - NORTON 69KV CKT 1 | EXP | SPRM | SPRM | SPRM | SPRM | 0 | 549928 | NORTON 2 69.000 | 549930 | NEERGRD2 69.000 | 0 |  | 1 | 12SP | 66 | 70 | 109.5 | 72.1863 | 110.241 | [6 empty] | CATEGORYB | SINGLE | MILL - PACKER 69KV CKT 1 | 0 | 549918 | MILL 2 69.000 | 549932 | PACKER 2 69.000 | 0 |  | 1 |  |  |  |  | SPRM | NEERGARD - NORTON 69KV CKT 1 | Transfer load & Reconductor 336.4 kcmil ACSR with 477 ACSS/TW | 111 | 115 | 111 | 115 | 2.6 | 24 | 2 | Outage | 0.01132 | 0.0367 | 0.00081 | SPRM will reconductor by 2010; Load will be transferred prior to project completion for short-term mitigation. | 1485000 | 2007-04-19 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T7222417SP | TO->FROM |  | NEERGARD - NORTON 69KV CKT 1 | EXP | SPRM | SPRM | SPRM | SPRM | 0 | 549928 | NORTON 2 69.000 | 549930 | NEERGRD2 69.000 | 0 |  | 1 | 17SP | 66 | 70 | 109.0 | 73.3886 | 108.5908 | [6 empty] | CATEGORYB | SINGLE | MILL - PACKER 69KV CKT 1 | 0 | 549918 | MILL 2 69.000 | 549932 | PACKER 2 69.000 | 0 |  | 1 |  |  |  |  | SPRM | NEERGARD - NORTON 69KV CKT 1 | Transfer load & Reconductor 336.4 kcmil ACSR with 477 ACSS/TW | 111 | 115 | 111 | 115 | 2.6 | 24 | 2 | Outage | 0.01132 | 0.0367 | 0.00081 | SPRM will reconductor by 2010; Load will be transferred prior to project completion for short-term mitigation. | 1485000 | 2007-04-19 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T7222417SP | TO->FROM |  | NEERGARD - NORTON 69KV CKT 1 | EXP | SPRM | SPRM | SPRM | SPRM | 0 | 549928 | NORTON 2 69.000 | 549930 | NEERGRD2 69.000 | 0 |  | 1 | 17SP | 66 | 70 | 109.0 | 73.3886 | 108.5908 | [6 empty] | CATEGORYB | SINGLE | MILL - PACKER 69KV CKT 1 | 0 | 549918 | MILL 2 69.000 | 549932 | PACKER 2 69.000 | 0 |  | 1 |  |  |  |  | SPRM | NEERGARD - NORTON 69KV CKT 1 | Transfer load & Reconductor 336.4 kcmil ACSR with 477 ACSS/TW | 111 | 115 | 111 | 115 | 2.6 | 24 | 2 | Outage | 0.01132 | 0.0367 | 0.00081 | SPRM will reconductor by 2010; Load will be transferred prior to project completion for short-term mitigation. | 1485000 | 2007-04-19 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T653309SP | FROM->TO |  | NEOSHO - NORTHEAST PARSONS 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533021 | NEOSHO 4 138.00 | 533005 | NEPARSN4 138.00 | 0 |  | 1 | 09SP | 159 | 159 |  | 87.3581 | 100.3403 | [6 empty] | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | NEOSHO - NORTHEAST PARSONS 138KV CKT 1 | Replace bus and Jumpers at NE Parsons 138 kV substation | 203 | 203 | 203 | 203 |  | 6 | 1 |  |  |  |  | 203 MVA is CT limit | 250000 | 2006-03-21 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2802412SP | FROM->TO |  | NEOSHO - NORTHEAST PARSONS 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533021 | NEOSHO 4 138.00 | 533005 | NEPARSN4 138.00 | 0 |  | 1 | 12SP | 159 | 159 |  | 76.0918 | 120.6632 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | NEOSHO - NORTHEAST PARSONS 138KV CKT 1 | Replace bus and Jumpers at NE Parsons 138 kV substation | 203 | 203 | 203 | 203 |  | 6 | 1 |  |  |  |  | 203 MVA is CT limit | 250000 | 2006-03-21 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2922412SP | FROM->TO |  | NEOSHO - NORTHEAST PARSONS 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533021 | NEOSHO 4 138.00 | 533005 | NEPARSN4 138.00 | 0 |  | 1 | 12SP | 159 | 159 |  | 75.6601 | 117.3259 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | NEOSHO - NORTHEAST PARSONS 138KV CKT 1 | Replace bus and Jumpers at NE Parsons 138 kV substation | 203 | 203 | 203 | 203 |  | 6 | 1 |  |  |  |  | 203 MVA is CT limit | 250000 | 2006-03-21 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T1553212SP | FROM->TO |  | NEOSHO - NORTHEAST PARSONS 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533021 | NEOSHO 4 138.00 | 533005 | NEPARSN4 138.00 | 0 |  | 1 | 12SP | 159 | 159 |  | 90.536 | 116.302 | [6 empty] | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | NEOSHO - NORTHEAST PARSONS 138KV CKT 1 | Replace bus and Jumpers at NE Parsons 138 kV substation | 203 | 203 | 203 | 203 |  | 6 | 1 |  |  |  |  | 203 MVA is CT limit | 250000 | 2006-03-21 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T2152217SP | FROM->TO |  | NEOSHO - NORTHEAST PARSONS 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533021 | NEOSHO 4 138.00 | 533005 | NEPARSN4 138.00 | 0 |  | 1 | 17SP | 159 | 159 |  | 91.4203 | 113.913 | [6 empty] | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | NEOSHO - NORTHEAST PARSONS 138KV CKT 1 | Replace bus and Jumpers at NE Parsons 138 kV substation | 203 | 203 | 203 | 203 |  | 6 | 1 |  |  |  |  | 203 MVA is CT limit | 250000 | 2006-03-21 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T5602217SP | FROM->TO |  | NEOSHO - NORTHEAST PARSONS 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533021 | NEOSHO 4 138.00 | 533005 | NEPARSN4 138.00 | 0 |  | 1 | 17SP | 159 | 159 |  | 78.8421 | 107.9068 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | NEOSHO - NORTHEAST PARSONS 138KV CKT 1 | Replace bus and Jumpers at NE Parsons 138 kV substation | 203 | 203 | 203 | 203 |  | 6 | 1 |  |  |  |  | 203 MVA is CT limit | 250000 | 2006-03-21 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T5672217SP | FROM->TO |  | NEOSHO - NORTHEAST PARSONS 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533021 | NEOSHO 4 138.00 | 533005 | NEPARSN4 138.00 | 0 |  | 1 | 17SP | 159 | 159 |  | 78.3559 | 107.3181 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | NEOSHO - NORTHEAST PARSONS 138KV CKT 1 | Replace bus and Jumpers at NE Parsons 138 kV substation | 203 | 203 | 203 | 203 |  | 6 | 1 |  |  |  |  | 203 MVA is CT limit | 250000 | 2006-03-21 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | NCONV | FNSL-Blown up | FDNS-Blown up | FNSL-Blown up | FDNS-Blown up | 3 | 2 | 2008-12-01 | 2007AG1AFS84L63212SP |  |  | PIONEER TAP - PLYMELL 115KV CKT 1 | EXP | SUNC | SUNC | PIONEER | PIONEER | 0 | 531393 | PLYMELL3 115.00 | 531392 | PIONTAP3 115.00 | 0 |  | 1 | 12SP | 120 | 143 | 95.98772 | 96.3223 | 96.4189 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | SUNC | NORTH CIMARRON CAPACITOR | Install 24 MVAR Capacitor bank at North Cimarron | [5 empty] | 18 | 18 | [5 empty] | 1400000 | 2006-07-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 | NCONV | FNSL-Blown up | FDNS-Blown up | FNSL-Blown up | FDNS-Blown up | 3 | 3 | 2008-12-01 | 2007AG1AFS84L83312SP |  |  | FLETCHER - HOLCOMB 115KV CKT 1 | EXP | SUNC | SUNC | SEPC | WHEATLAN | 0 | 531448 | HOLCOMB3 115.00 | 531420 | FLETCHR3 115.00 | 0 |  | 1 | 12SP | 165 | 198 | 62.88427 | 63.0275 | 63.2224 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | SUNC | NORTH CIMARRON CAPACITOR | Install 24 MVAR Capacitor bank at North Cimarron | [5 empty] | 18 | 18 | [5 empty] | 1400000 | 2006-07-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FNSL | FDNS-Blown up | 3 | 3 | 2008-12-01 | 2007AG1AFS82T43312SP | TO->FROM |  | CIMARRON RIVER PLANT - NORTH CIMARRON 115KV CKT 1 | EXP | SUNC | WEPL | SEPC |  | 0 | 531455 | NCIMARN3 115.00 | 539654 | CIM-PLT3 115.00 | 0 |  | 1 | 12SP | 120 | 143 | 107.6 | -999 | 107.6186 | [6 empty] | CATEGORYB | SINGLE | CUDAHY - JUDSON LARGE 115KV CKT 1 | 0 | 539659 | CUDAHY 3 115.00 | 539671 | JUD-LRG3 115.00 | 0 |  | 1 |  |  |  |  | SUNC | NORTH CIMARRON CAPACITOR | Install 24 MVAR Capacitor bank at North Cimarron | [5 empty] | 18 | 18 | [5 empty] | 1400000 | 2006-07-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FNSL | FDNS-Blown up | 3 | 3 | 2008-12-01 | 2007AG1AFS82T43312SP | TO->FROM |  | CIMARRON RIVER PLANT - NORTH CIMARRON 115KV CKT 1 | EXP | SUNC | WEPL | SEPC |  | 0 | 531455 | NCIMARN3 115.00 | 539654 | CIM-PLT3 115.00 | 0 |  | 1 | 12SP | 120 | 143 | 107.6 | -999 | 107.6186 | [6 empty] | CATEGORYB | SINGLE | CUDAHY - JUDSON LARGE 115KV CKT 1 | 0 | 539659 | CUDAHY 3 115.00 | 539671 | JUD-LRG3 115.00 | 0 |  | 1 |  |  |  |  | SUNC | NORTH CIMARRON CAPACITOR | Install 24 MVAR Capacitor bank at North Cimarron | [5 empty] | 18 | 18 | [5 empty] | 1400000 | 2006-07-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 | NCONV | FNSL-Blown up | FDNS-Blown up | FNSL-Blown up | FDNS-Iteration limit exceeded | 3 | 2 | 2008-12-01 | 2007AG1AFS84L93212SP |  |  | CIMARRON RIVER PLANT - NORTH CIMARRON 115KV CKT 1 | EXP | SUNC | WEPL | SEPC |  | 0 | 531455 | NCIMARN3 115.00 | 539654 | CIM-PLT3 115.00 | 0 |  | 1 | 12SP | 120 | 143 | 55.6476 | 56.181 | 56.3055 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | SUNC | NORTH CIMARRON CAPACITOR | Install 24 MVAR Capacitor bank at North Cimarron | [5 empty] | 18 | 18 | [5 empty] | 1400000 | 2006-07-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 | NCONV | FNSL-Singular jacobian or 0.0 voltage | FDNS-Blown up | FNSL-Blown up | FDNS-Blown up | 4 | 2 | 2008-12-01 | 2007AG1AFS84L114212SP |  |  | CUDAHY - JUDSON LARGE 115KV CKT 1 | EXP | WEPL | WEPL |  |  | 0 | 539671 | JUD-LRG3 115.00 | 539659 | CUDAHY 3 115.00 | 0 |  | 1 | 12SP | 120.7 | 129.5 | 57.70921 | 57.1273 | 57.6538 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | SUNC | NORTH CIMARRON CAPACITOR | Install 24 MVAR Capacitor bank at North Cimarron | [5 empty] | 18 | 18 | [5 empty] | 1400000 | 2006-07-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 | NCONV | FNSL-Blown up | FDNS-Blown up | FNSL-Blown up | FDNS-Blown up | 3 | 2 | 2008-12-01 | 2007AG1AFS84L73212SP |  |  | HOLCOMB - PLYMELL 115KV CKT 1 | EXP | SUNC | SUNC | SEPC | PIONEER | 0 | 531448 | HOLCOMB3 115.00 | 531393 | PLYMELL3 115.00 | 0 |  | 1 | 12SP | 120 | 143 | 100.3204 | 100.6549 | 100.7523 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | SUNC | NORTH CIMARRON CAPACITOR | Install 24 MVAR Capacitor bank at North Cimarron | [5 empty] | 18 | 18 | [5 empty] | 1400000 | 2006-07-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 | NCONV | FDNS |  | FNSL-Blown up | FDNS-Blown up | 3 | 2 | 2008-12-01 | 2007AG1AFS84L73212SP |  |  | HOLCOMB - PLYMELL 115KV CKT 1 | EXP | SUNC | SUNC | SEPC | PIONEER | 0 | 531448 | HOLCOMB3 115.00 | 531393 | PLYMELL3 115.00 | 0 |  | 1 | 12SP | 120 | 143 | 100.3 | 100.6549 | 100.7523 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | SUNC | NORTH CIMARRON CAPACITOR | Install 24 MVAR Capacitor bank at North Cimarron | [5 empty] | 18 | 18 | [5 empty] | 1400000 | 2006-07-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 | NCONV | FNSL-Blown up | FDNS-Iteration limit exceeded | FNSL-Blown up | FDNS-Blown up | 1 | 3 | 2008-12-01 | 2007AG1AFS84L121312SP |  |  | CIMARRON RIVER TAP - CUDAHY 115KV CKT 1 | EXP | WEPL | WEPL |  |  | 0 | 539659 | CUDAHY 3 115.00 | 539652 | CMRIVTP3 115.00 | 0 |  | 1 | 12SP | 120.7 | 129.5 | 53.92646 | 52.0047 | 53.0679 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | SUNC | NORTH CIMARRON CAPACITOR | Install 24 MVAR Capacitor bank at North Cimarron | [5 empty] | 18 | 18 | [5 empty] | 1400000 | 2006-07-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T772308SH | FROM->TO |  | OAK - RAINBOW 69KV CKT 1 | S | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533547 | OAK 2 69.000 | 533549 | RAINBOW2 69.000 | 0 |  | 1 | 08SH | 43 | 43 |  | 5.161 | 112.1025 | [6 empty] | CATEGORYB | SINGLE | OAK - STROTHER FIELD (CITY OF WINFIELD) 69KV CKT 1 | 0 | 533547 | OAK 2 69.000 | 533556 | STROTHR2 69.000 | 0 |  | 1 |  |  |  |  | WERE | OAK - RAINBOW 69KV CKT 1 | Tear down / Rebuild 5.10-mile Oak-Rainbow 69 kV using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 5.1 | 8 | 4 |  | 0.010721 | 0.0737 | 0.0015109 | Limit is conductor | 1900000 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01 | 2010-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 4 | 2008-12-01 | 2007AG1AFS81T6943409WP | TO->FROM |  | PIONEER TAP - PLYMELL 115KV CKT 1 | EXP | SUNC | SUNC | PIONEER | PIONEER | 0 | 531393 | PLYMELL3 115.00 | 531392 | PIONTAP3 115.00 | 0 |  | 1 | 09WP | 120 | 143 | 104.4 | 104.5064 | 104.63 | [6 empty] | CATEGORYB | NONSINGLE | SPP-SUNC-05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | Rebuild Holcomb to Pioneer Tap, Reduce generation in area 534, increase generation in area 539 | SUNC | PIONEER TAP - PLYMELL 115KV CKT 1 | Rebuild Plymell to Pioneer Tap | 185 | 222 |  |  | 14 | 24 | 24 |  | 0.01044 | 0.07657 | 0.01098 |  | 2380000 | 2006-06-01 | [23 empty] | 2009-12-01 | 2009-12-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FNSL | FDNS-Blown up | 3 | 3 | 2008-12-01 | 2007AG1AFS82T23312SP | TO->FROM |  | PIONEER TAP - PLYMELL 115KV CKT 1 | EXP | SUNC | SUNC | PIONEER | PIONEER | 0 | 531393 | PLYMELL3 115.00 | 531392 | PIONTAP3 115.00 | 0 |  | 1 | 12SP | 120 | 143 | 122.2 | -999 | 122.2487 | [6 empty] | CATEGORYB | SINGLE | CUDAHY - JUDSON LARGE 115KV CKT 1 | 0 | 539659 | CUDAHY 3 115.00 | 539671 | JUD-LRG3 115.00 | 0 |  | 1 |  |  |  | Rebuild Holcomb to Pioneer Tap, Reduce generation in area 534, increase generation in area 539 | SUNC | PIONEER TAP - PLYMELL 115KV CKT 1 | Rebuild Plymell to Pioneer Tap | 185 | 222 |  |  | 14 | 24 | 24 |  | 0.01044 | 0.07657 | 0.01098 |  | 2380000 | 2006-06-01 | [23 empty] | 2009-12-01 | 2009-12-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FNSL | FDNS-Blown up | 3 | 2 | 2008-12-01 | 2007AG1AFS82T23212SP | TO->FROM |  | PIONEER TAP - PLYMELL 115KV CKT 1 | EXP | SUNC | SUNC | PIONEER | PIONEER | 0 | 531393 | PLYMELL3 115.00 | 531392 | PIONTAP3 115.00 | 0 |  | 1 | 12SP | 120 | 143 | 113.9 | 113.8649 | 113.8776 | [6 empty] | CATEGORYB | SINGLE | CIMARRON RIVER TAP - CUDAHY 115KV CKT 1 | 0 | 539652 | CMRIVTP3 115.00 | 539659 | CUDAHY 3 115.00 | 0 |  | 1 |  |  |  | Rebuild Holcomb to Pioneer Tap, Reduce generation in area 534, increase generation in area 539 | SUNC | PIONEER TAP - PLYMELL 115KV CKT 1 | Rebuild Plymell to Pioneer Tap | 185 | 222 |  |  | 14 | 24 | 24 |  | 0.01044 | 0.07657 | 0.01098 |  | 2380000 | 2006-06-01 | [23 empty] | 2009-12-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T13785512SP | TO->FROM |  | PIONEER TAP - PLYMELL 115KV CKT 1 | EXP | SUNC | SUNC | PIONEER | PIONEER | 0 | 531393 | PLYMELL3 115.00 | 531392 | PIONTAP3 115.00 | 0 |  | 1 | 12SP | 120 | 143 | 114.1 | 114.2602 | 113.7334 | [6 empty] | CATEGORYB | NONSINGLE | SPP-SUNC-05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | Rebuild Holcomb to Pioneer Tap, Reduce generation in area 534, increase generation in area 539 | SUNC | PIONEER TAP - PLYMELL 115KV CKT 1 | Rebuild Plymell to Pioneer Tap | 185 | 222 |  |  | 14 | 24 | 24 |  | 0.01044 | 0.07657 | 0.01098 |  | 2380000 | 2006-06-01 | [23 empty] | 2009-12-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 4 | 2008-12-01 | 2007AG1AFS81T7593412WP | TO->FROM |  | PIONEER TAP - PLYMELL 115KV CKT 1 | EXP | SUNC | SUNC | PIONEER | PIONEER | 0 | 531393 | PLYMELL3 115.00 | 531392 | PIONTAP3 115.00 | 0 |  | 1 | 12WP | 120 | 143 | 102.6 | 103.0121 | 103.0199 | [6 empty] | CATEGORYB | NONSINGLE | SPP-SUNC-05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | Rebuild Holcomb to Pioneer Tap, Reduce generation in area 534, increase generation in area 539 | SUNC | PIONEER TAP - PLYMELL 115KV CKT 1 | Rebuild Plymell to Pioneer Tap | 185 | 222 |  |  | 14 | 24 | 24 |  | 0.01044 | 0.07657 | 0.01098 |  | 2380000 | 2006-06-01 | [23 empty] | 2009-12-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T27023217SP | TO->FROM |  | PIONEER TAP - PLYMELL 115KV CKT 1 | EXP | SUNC | SUNC | PIONEER | PIONEER | 0 | 531393 | PLYMELL3 115.00 | 531392 | PIONTAP3 115.00 | 0 |  | 1 | 17SP | 120 | 143 | 115.3 | 115.8094 | 116.0371 | [6 empty] | CATEGORYB | NONSINGLE | SPP-SUNC-05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | Rebuild Holcomb to Pioneer Tap, Reduce generation in area 534, increase generation in area 539 | SUNC | PIONEER TAP - PLYMELL 115KV CKT 1 | Rebuild Plymell to Pioneer Tap | 185 | 222 |  |  | 14 | 24 | 24 |  | 0.01044 | 0.07657 | 0.01098 |  | 2380000 | 2006-06-01 | [23 empty] | 2009-12-01 | 2009-12-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FNSL | FDNS-Iteration limit exceeded | 3 | 3 | 2008-12-01 | 2007AG1AFS82T13317SP | TO->FROM |  | PIONEER TAP - PLYMELL 115KV CKT 1 | EXP | SUNC | SUNC | PIONEER | PIONEER | 0 | 531393 | PLYMELL3 115.00 | 531392 | PIONTAP3 115.00 | 0 |  | 1 | 17SP | 120 | 143 | 113.5 | 114.2876 | 114.5522 | [6 empty] | CATEGORYB | SINGLE | FLETCHER - HOLCOMB 115KV CKT 1 | 0 | 531420 | FLETCHR3 115.00 | 531448 | HOLCOMB3 115.00 | 0 |  | 1 |  |  |  | Rebuild Holcomb to Pioneer Tap, Reduce generation in area 534, increase generation in area 539 | SUNC | PIONEER TAP - PLYMELL 115KV CKT 1 | Rebuild Plymell to Pioneer Tap | 185 | 222 |  |  | 14 | 24 | 24 |  | 0.01044 | 0.07657 | 0.01098 |  | 2380000 | 2006-06-01 | [23 empty] | 2009-12-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T4753317SP | TO->FROM |  | PIONEER TAP - PLYMELL 115KV CKT 1 | EXP | SUNC | SUNC | PIONEER | PIONEER | 0 | 531393 | PLYMELL3 115.00 | 531392 | PIONTAP3 115.00 | 0 |  | 1 | 17SP | 120 | 143 | 107.7 | 107.6984 | 107.7149 | [6 empty] | CATEGORYB | SINGLE | CUDAHY - JUDSON LARGE 115KV CKT 1 | 0 | 539659 | CUDAHY 3 115.00 | 539671 | JUD-LRG3 115.00 | 0 |  | 1 |  |  |  | Rebuild Holcomb to Pioneer Tap, Reduce generation in area 534, increase generation in area 539 | SUNC | PIONEER TAP - PLYMELL 115KV CKT 1 | Rebuild Plymell to Pioneer Tap | 185 | 222 |  |  | 14 | 24 | 24 |  | 0.01044 | 0.07657 | 0.01098 |  | 2380000 | 2006-06-01 | [23 empty] | 2009-12-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T6195517SP | TO->FROM |  | PRATT - ST JOHN 115KV CKT 1 | REL | WEPL | WEPL |  |  | 0 | 539696 | ST-JOHN3 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 | 17SP | 79.7 | 79.7 | 100.2 | 102.5049 | 102.08 | [6 empty] | CATEGORYB | SINGLE | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 533045 | GILL W 4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT - ST JOHN 115KV CKT 1 | Replace terminal equipment | [37 empty] | 2017-06-01 | 2017-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T875508SH | TO->FROM |  | REDEL - STILWELL 161KV CKT 1 | REL | KACP | KACP | JOCO | JOCO | 0 | 542969 | STILWEL5 161.00 | 543053 | REDEL 5 161.00 | 0 |  | 1 | 08SH | 293 | 335 |  | 99.9822 | 101.3917 | 541_REDEL - STILWELL 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | PECULIAR - STILWELL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  | reconductor with 1192 acss / 584 | KACP | REDEL - STILWELL 161KV CKT 1 | Reconductor line with 1192 ACSS and upgrade terminal equipment for 2000 amps | 558 | 558 |  |  |  | 24 | 4 | [5 empty] | 2200000 | 2008-02-21 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 3 | 2008-12-01 | 2007AG1AFS81T1731308SP | TO->FROM |  | REDEL - STILWELL 161KV CKT 1 | REL | KACP | KACP | JOCO | JOCO | 0 | 542969 | STILWEL5 161.00 | 543053 | REDEL 5 161.00 | 0 |  | 1 | 08SP | 293 | 335 |  | 100.3439 | 102.0646 | 541_REDEL - STILWELL 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | PECULIAR - STILWELL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  | reconductor with 1192 acss / 584 | KACP | REDEL - STILWELL 161KV CKT 1 | Reconductor line with 1192 ACSS and upgrade terminal equipment for 2000 amps | 558 | 558 |  |  |  | 24 | 4 | [5 empty] | 2200000 | 2008-02-21 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T1952309SP | TO->FROM |  | REDEL - STILWELL 161KV CKT 1 | REL | KACP | KACP | JOCO | JOCO | 0 | 542969 | STILWEL5 161.00 | 543053 | REDEL 5 161.00 | 0 |  | 1 | 09SP | 293 | 335 | 100.3 | 100.608 | 117.96 | 541_REDEL - STILWELL 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | PECULIAR - STILWELL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  | reconductor with 1192 acss / 584 | KACP | REDEL - STILWELL 161KV CKT 1 | Reconductor line with 1192 ACSS and upgrade terminal equipment for 2000 amps | 558 | 558 |  |  |  | 24 | 4 | [5 empty] | 2200000 | 2008-02-21 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T3412312SP | TO->FROM |  | REDEL - STILWELL 161KV CKT 1 | REL | KACP | KACP | JOCO | JOCO | 0 | 542969 | STILWEL5 161.00 | 543053 | REDEL 5 161.00 | 0 |  | 1 | 12SP | 293 | 335 |  | 103.3384 | 122.0253 | 541_REDEL - STILWELL 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | PECULIAR - STILWELL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  | reconductor with 1192 acss / 584 | KACP | REDEL - STILWELL 161KV CKT 1 | Reconductor line with 1192 ACSS and upgrade terminal equipment for 2000 amps | 558 | 558 |  |  |  | 24 | 4 | [5 empty] | 2200000 | 2008-02-21 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T10932312SP | TO->FROM |  | REDEL - STILWELL 161KV CKT 1 | REL | KACP | KACP | JOCO | JOCO | 0 | 542969 | STILWEL5 161.00 | 543053 | REDEL 5 161.00 | 0 |  | 1 | 12SP | 293 | 335 |  | 83.2427 | 101.7619 | 541_REDEL - STILWELL 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | PECULIAR () 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 541198 | PECULR 7 345.00 | 541342 | PECULR 5 161.00 | 541372 | PECULRT 13.800 | 1 |  |  |  | reconductor with 1192 acss / 584 | KACP | REDEL - STILWELL 161KV CKT 1 | Reconductor line with 1192 ACSS and upgrade terminal equipment for 2000 amps | 558 | 558 |  |  |  | 24 | 4 | [5 empty] | 2200000 | 2008-02-21 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T13074312SP | TO->FROM |  | REDEL - STILWELL 161KV CKT 1 | REL | KACP | KACP | JOCO | JOCO | 0 | 542969 | STILWEL5 161.00 | 543053 | REDEL 5 161.00 | 0 |  | 1 | 12SP | 293 | 335 |  | 100.945 | 101.3444 | 541_REDEL - STILWELL 161KV CKT 1 | [5 empty] | CATEGORYB | NONSINGLE | SPP-MIPU-01 | 0 | 0 |  | 0 |  | 0 | [5 empty] | reconductor with 1192 acss / 584 | KACP | REDEL - STILWELL 161KV CKT 1 | Reconductor line with 1192 ACSS and upgrade terminal equipment for 2000 amps | 558 | 558 |  |  |  | 24 | 4 | [5 empty] | 2200000 | 2008-02-21 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T5352317SP | TO->FROM |  | REDEL - STILWELL 161KV CKT 1 | REL | KACP | KACP | JOCO | JOCO | 0 | 542969 | STILWEL5 161.00 | 543053 | REDEL 5 161.00 | 0 |  | 1 | 17SP | 293 | 335 |  | 89.8683 | 113.0676 | 541_REDEL - STILWELL 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | PECULIAR - STILWELL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  | reconductor with 1192 acss / 584 | KACP | REDEL - STILWELL 161KV CKT 1 | Reconductor line with 1192 ACSS and upgrade terminal equipment for 2000 amps | 558 | 558 |  |  |  | 24 | 4 | [5 empty] | 2200000 | 2008-02-21 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T21922317SP | TO->FROM |  | REDEL - STILWELL 161KV CKT 1 | REL | KACP | KACP | JOCO | JOCO | 0 | 542969 | STILWEL5 161.00 | 543053 | REDEL 5 161.00 | 0 |  | 1 | 17SP | 293 | 335 |  | 96.4367 | 109.1272 | 541_REDEL - STILWELL 161KV CKT 1 | [5 empty] | CATEGORYB | NONSINGLE | SPP-MIPU-01 | 0 | 0 |  | 0 |  | 0 | [5 empty] | reconductor with 1192 acss / 584 | KACP | REDEL - STILWELL 161KV CKT 1 | Reconductor line with 1192 ACSS and upgrade terminal equipment for 2000 amps | 558 | 558 |  |  |  | 24 | 4 | [5 empty] | 2200000 | 2008-02-21 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T5872317SP | TO->FROM |  | REDEL - STILWELL 161KV CKT 1 | REL | KACP | KACP | JOCO | JOCO | 0 | 542969 | STILWEL5 161.00 | 543053 | REDEL 5 161.00 | 0 |  | 1 | 17SP | 293 | 335 |  | 95.1449 | 107.6762 | 541_REDEL - STILWELL 161KV CKT 1 | [5 empty] | CATEGORYB | SINGLE | BELTON SOUTH - PECULIAR 161KV CKT 1 | 0 | 541340 | BELTONS5 161.00 | 541342 | PECULR 5 161.00 | 0 |  | 1 |  |  |  | reconductor with 1192 acss / 584 | KACP | REDEL - STILWELL 161KV CKT 1 | Reconductor line with 1192 ACSS and upgrade terminal equipment for 2000 amps | 558 | 558 |  |  |  | 24 | 4 | [5 empty] | 2200000 | 2008-02-21 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T404408FA | TO->FROM |  | ROSE HILL JUNCTION - WEAVER 69KV CKT 1 | S | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533604 | WEAVER 2 69.000 | 533837 | RH JCT 2 69.000 | 0 |  | 1 | 08FA | 43 | 43 |  | 67.1424 | 105.8908 | [6 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | RICHLAND - ROSE HILL JUNCTION 69KV CKT 1 Displacement | Rebuild 5.43 mile Rose Hill Junction-Richland as a 138 kV line but operate at 69 kV. | 72 | 72 | 72 | 72 | 5.43 | 12 | 5 |  | 0.01146 | 0.07817 | 0.00166 | 72 MVA is CT and disconnect switch limit. | 2240142 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81T361408G | TO->FROM |  | RICHLAND - ROSE HILL JUNCTION 69KV CKT 1 | S | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533837 | RH JCT 2 69.000 | 533550 | RICHLAN2 69.000 | 0 |  | 1 | 08G | 43 | 43 |  | 68.5445 | 101.597 | [6 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | RICHLAND - ROSE HILL JUNCTION 69KV CKT 1 Displacement | Rebuild 5.43 mile Rose Hill Junction-Richland as a 138 kV line but operate at 69 kV. | 72 | 72 | 72 | 72 | 5.43 | 12 | 5 |  | 0.01146 | 0.07817 | 0.00166 | 72 MVA is CT and disconnect switch limit. | 2240142 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81T831408SH | TO->FROM |  | RICHLAND - ROSE HILL JUNCTION 69KV CKT 1 | S | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533837 | RH JCT 2 69.000 | 533550 | RICHLAN2 69.000 | 0 |  | 1 | 08SH | 43 | 43 |  | 61.4857 | 102.2452 | [6 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | RICHLAND - ROSE HILL JUNCTION 69KV CKT 1 Displacement | Rebuild 5.43 mile Rose Hill Junction-Richland as a 138 kV line but operate at 69 kV. | 72 | 72 | 72 | 72 | 5.43 | 12 | 5 |  | 0.01146 | 0.07817 | 0.00166 | 72 MVA is CT and disconnect switch limit. | 2240142 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81T841408SH | TO->FROM |  | ROSE HILL JUNCTION - WEAVER 69KV CKT 1 | S | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533604 | WEAVER 2 69.000 | 533837 | RH JCT 2 69.000 | 0 |  | 1 | 08SH | 43 | 43 |  | 74.4409 | 114.9701 | [6 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | RICHLAND - ROSE HILL JUNCTION 69KV CKT 1 Displacement | Rebuild 5.43 mile Rose Hill Junction-Richland as a 138 kV line but operate at 69 kV. | 72 | 72 | 72 | 72 | 5.43 | 12 | 5 |  | 0.01146 | 0.07817 | 0.00166 | 72 MVA is CT and disconnect switch limit. | 2240142 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81T871408SH | TO->FROM |  | ROSE HILL JUNCTION - WEAVER 69KV CKT 1 | S | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533604 | WEAVER 2 69.000 | 533837 | RH JCT 2 69.000 | 0 |  | 1 | 08SH | 43 | 43 |  | -999 | 107.4827 | [6 empty] | CATEGORYB | SINGLE | FARBER - SUMNER COUNTY NO. 10 BELLE PLAIN 138KV CKT 1 | 0 | 533042 | FARBER 4 138.00 | 533063 | SC10BEL4 138.00 | 0 |  | 1 |  |  |  |  | WERE | RICHLAND - ROSE HILL JUNCTION 69KV CKT 1 Displacement | Rebuild 5.43 mile Rose Hill Junction-Richland as a 138 kV line but operate at 69 kV. | 72 | 72 | 72 | 72 | 5.43 | 12 | 5 |  | 0.01146 | 0.07817 | 0.00166 | 72 MVA is CT and disconnect switch limit. | 2240142 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81T991408SH | TO->FROM |  | ROSE HILL JUNCTION - WEAVER 69KV CKT 1 | S | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533604 | WEAVER 2 69.000 | 533837 | RH JCT 2 69.000 | 0 |  | 1 | 08SH | 43 | 43 |  | 59.06 | 105.7616 | [6 empty] | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | RICHLAND - ROSE HILL JUNCTION 69KV CKT 1 Displacement | Rebuild 5.43 mile Rose Hill Junction-Richland as a 138 kV line but operate at 69 kV. | 72 | 72 | 72 | 72 | 5.43 | 12 | 5 |  | 0.01146 | 0.07817 | 0.00166 | 72 MVA is CT and disconnect switch limit. | 2240142 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T684409WP | TO->FROM |  | ROSE HILL JUNCTION - WEAVER 69KV CKT 1 | S | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533604 | WEAVER 2 69.000 | 533837 | RH JCT 2 69.000 | 0 |  | 1 | 09WP | 43 | 43 |  | 63.574 | 102.4914 | [6 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | RICHLAND - ROSE HILL JUNCTION 69KV CKT 1 Displacement | Rebuild 5.43 mile Rose Hill Junction-Richland as a 138 kV line but operate at 69 kV. | 72 | 72 | 72 | 72 | 5.43 | 12 | 5 |  | 0.01146 | 0.07817 | 0.00166 | 72 MVA is CT and disconnect switch limit. | 2240142 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T2354412SP | TO->FROM |  | ROSE HILL JUNCTION - WEAVER 69KV CKT 1 | S | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533604 | WEAVER 2 69.000 | 533837 | RH JCT 2 69.000 | 0 |  | 1 | 12SP | 43 | 43 | 103.2 | 76.6989 | 102.2917 | [6 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | RICHLAND - ROSE HILL JUNCTION 69KV CKT 1 Displacement | Rebuild 5.43 mile Rose Hill Junction-Richland as a 138 kV line but operate at 69 kV. | 72 | 72 | 72 | 72 | 5.43 | 12 | 5 |  | 0.01146 | 0.07817 | 0.00166 | 72 MVA is CT and disconnect switch limit. | 2240142 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T404408FA | TO->FROM |  | ROSE HILL JUNCTION - WEAVER 69KV CKT 1 | EXP | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533604 | WEAVER 2 69.000 | 533837 | RH JCT 2 69.000 | 0 |  | 1 | 08FA | 43 | 43 |  | 67.1424 | 105.8908 | [6 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ROSE HILL JUNCTION - WEAVER 69KV CKT 1 | Rebuild 5.73 mile Weaver-Rose Hill Junction as a 138 kV line but operate at 69 kV. | 116 | 128 | 116 | 128 | 5.73 | 12 | 5 |  | 0.01209 | 0.08228 | 0.001749 | MVA limit is conductor | 2300000 | 2006-07-25 | [23 empty] | 2008-06-01 | 2008-12-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81T361408G | TO->FROM |  | RICHLAND - ROSE HILL JUNCTION 69KV CKT 1 | EXP | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533837 | RH JCT 2 69.000 | 533550 | RICHLAN2 69.000 | 0 |  | 1 | 08G | 43 | 43 |  | 68.5445 | 101.597 | [6 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ROSE HILL JUNCTION - WEAVER 69KV CKT 1 | Rebuild 5.73 mile Weaver-Rose Hill Junction as a 138 kV line but operate at 69 kV. | 116 | 128 | 116 | 128 | 5.73 | 12 | 5 |  | 0.01209 | 0.08228 | 0.001749 | MVA limit is conductor | 2300000 | 2006-07-25 | [23 empty] | 2008-06-01 | 2008-12-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81T831408SH | TO->FROM |  | RICHLAND - ROSE HILL JUNCTION 69KV CKT 1 | EXP | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533837 | RH JCT 2 69.000 | 533550 | RICHLAN2 69.000 | 0 |  | 1 | 08SH | 43 | 43 |  | 61.4857 | 102.2452 | [6 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ROSE HILL JUNCTION - WEAVER 69KV CKT 1 | Rebuild 5.73 mile Weaver-Rose Hill Junction as a 138 kV line but operate at 69 kV. | 116 | 128 | 116 | 128 | 5.73 | 12 | 5 |  | 0.01209 | 0.08228 | 0.001749 | MVA limit is conductor | 2300000 | 2006-07-25 | [23 empty] | 2008-06-01 | 2008-12-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81T841408SH | TO->FROM |  | ROSE HILL JUNCTION - WEAVER 69KV CKT 1 | EXP | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533604 | WEAVER 2 69.000 | 533837 | RH JCT 2 69.000 | 0 |  | 1 | 08SH | 43 | 43 |  | 74.4409 | 114.9701 | [6 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ROSE HILL JUNCTION - WEAVER 69KV CKT 1 | Rebuild 5.73 mile Weaver-Rose Hill Junction as a 138 kV line but operate at 69 kV. | 116 | 128 | 116 | 128 | 5.73 | 12 | 5 |  | 0.01209 | 0.08228 | 0.001749 | MVA limit is conductor | 2300000 | 2006-07-25 | [23 empty] | 2008-06-01 | 2008-12-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81T871408SH | TO->FROM |  | ROSE HILL JUNCTION - WEAVER 69KV CKT 1 | EXP | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533604 | WEAVER 2 69.000 | 533837 | RH JCT 2 69.000 | 0 |  | 1 | 08SH | 43 | 43 |  | -999 | 107.4827 | [6 empty] | CATEGORYB | SINGLE | FARBER - SUMNER COUNTY NO. 10 BELLE PLAIN 138KV CKT 1 | 0 | 533042 | FARBER 4 138.00 | 533063 | SC10BEL4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ROSE HILL JUNCTION - WEAVER 69KV CKT 1 | Rebuild 5.73 mile Weaver-Rose Hill Junction as a 138 kV line but operate at 69 kV. | 116 | 128 | 116 | 128 | 5.73 | 12 | 5 |  | 0.01209 | 0.08228 | 0.001749 | MVA limit is conductor | 2300000 | 2006-07-25 | [23 empty] | 2008-06-01 | 2008-12-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81T991408SH | TO->FROM |  | ROSE HILL JUNCTION - WEAVER 69KV CKT 1 | EXP | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533604 | WEAVER 2 69.000 | 533837 | RH JCT 2 69.000 | 0 |  | 1 | 08SH | 43 | 43 |  | 59.06 | 105.7616 | [6 empty] | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ROSE HILL JUNCTION - WEAVER 69KV CKT 1 | Rebuild 5.73 mile Weaver-Rose Hill Junction as a 138 kV line but operate at 69 kV. | 116 | 128 | 116 | 128 | 5.73 | 12 | 5 |  | 0.01209 | 0.08228 | 0.001749 | MVA limit is conductor | 2300000 | 2006-07-25 | [23 empty] | 2008-06-01 | 2008-12-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T684409WP | TO->FROM |  | ROSE HILL JUNCTION - WEAVER 69KV CKT 1 | EXP | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533604 | WEAVER 2 69.000 | 533837 | RH JCT 2 69.000 | 0 |  | 1 | 09WP | 43 | 43 |  | 63.574 | 102.4914 | [6 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ROSE HILL JUNCTION - WEAVER 69KV CKT 1 | Rebuild 5.73 mile Weaver-Rose Hill Junction as a 138 kV line but operate at 69 kV. | 116 | 128 | 116 | 128 | 5.73 | 12 | 5 |  | 0.01209 | 0.08228 | 0.001749 | MVA limit is conductor | 2300000 | 2006-07-25 | [23 empty] | 2008-06-01 | 2008-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T2354412SP | TO->FROM |  | ROSE HILL JUNCTION - WEAVER 69KV CKT 1 | EXP | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533604 | WEAVER 2 69.000 | 533837 | RH JCT 2 69.000 | 0 |  | 1 | 12SP | 43 | 43 | 103.2 | 76.6989 | 102.2917 | [6 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ROSE HILL JUNCTION - WEAVER 69KV CKT 1 | Rebuild 5.73 mile Weaver-Rose Hill Junction as a 138 kV line but operate at 69 kV. | 116 | 128 | 116 | 128 | 5.73 | 12 | 5 |  | 0.01209 | 0.08228 | 0.001749 | MVA limit is conductor | 2300000 | 2006-07-25 | [23 empty] | 2008-06-01 | 2008-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T9352209SP | FROM->TO |  | RUSSELLVILLE EAST - RUSSELLVILLE SOUTH 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99490 | 5RUSL-E 161.00 | 99491 | 5RUSL-S 161.00 | 0 |  | 1 | 09SP | 335 | 335 | 120.1 | 120.1759 | 128.2288 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | RUSSELLVILLE EAST - RUSSELLVILLE SOUTH 161KV CKT 1 | Indeterminate | [37 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T5732209WP | FROM->TO |  | RUSSELLVILLE EAST - RUSSELLVILLE SOUTH 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99490 | 5RUSL-E 161.00 | 99491 | 5RUSL-S 161.00 | 0 |  | 1 | 09WP | 335 | 335 | 108.5 | 108.4619 | 116.2425 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | RUSSELLVILLE EAST - RUSSELLVILLE SOUTH 161KV CKT 1 | Indeterminate | [37 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T13452212SP | FROM->TO |  | RUSSELLVILLE EAST - RUSSELLVILLE SOUTH 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99490 | 5RUSL-E 161.00 | 99491 | 5RUSL-S 161.00 | 0 |  | 1 | 12SP | 335 | 335 | 129.7 | 130.5392 | 140.6396 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | RUSSELLVILLE EAST - RUSSELLVILLE SOUTH 161KV CKT 1 | Indeterminate | [37 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T7372212WP | FROM->TO |  | RUSSELLVILLE EAST - RUSSELLVILLE SOUTH 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99490 | 5RUSL-E 161.00 | 99491 | 5RUSL-S 161.00 | 0 |  | 1 | 12WP | 335 | 335 | 112.6 | 110.8085 | 120.418 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | RUSSELLVILLE EAST - RUSSELLVILLE SOUTH 161KV CKT 1 | Indeterminate | [37 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T20392217SP | FROM->TO |  | RUSSELLVILLE EAST - RUSSELLVILLE SOUTH 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99490 | 5RUSL-E 161.00 | 99491 | 5RUSL-S 161.00 | 0 |  | 1 | 17SP | 335 | 335 | 135.8 | 137.005 | 146.7527 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN |  |  |  | ENTR | RUSSELLVILLE EAST - RUSSELLVILLE SOUTH 161KV CKT 1 | Indeterminate | [37 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T232308SH | FROM->TO |  | BARTLESVILLE SOUTHEAST - NORTH BARTLESVILLE 138KV CKT 1 | CP | AEPW | AEPW | NORTHERN | TS-KAMO | 0 | 510391 | BV-SE--4 138.00 | 510386 | NBVILLE4 138.00 | 0 |  | 1 | 08SH | 202 | 235 |  | 97.9161 | 100.5716 | [6 empty] | CATEGORYB | SINGLE | DELAWARE - NORTHEAST STATION 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 510406 | N.E.S.-7 345.00 | 0 |  | 1 |  |  |  |  | OKGE | Sooner to Rose Hill 345 kV OKGE | New 345 kV line from Sooner to Oklahoma/Kansas | [37 empty] | 2008-06-01 | 2011-01-01 | 2010-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T502308SP | FROM->TO |  | BARTLESVILLE SOUTHEAST - NORTH BARTLESVILLE 138KV CKT 1 | CP | AEPW | AEPW | NORTHERN | TS-KAMO | 0 | 510391 | BV-SE--4 138.00 | 510386 | NBVILLE4 138.00 | 0 |  | 1 | 08SP | 202 | 235 |  | 97.952 | 101.1703 | [6 empty] | CATEGORYB | SINGLE | DELAWARE - NORTHEAST STATION 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 510406 | N.E.S.-7 345.00 | 0 |  | 1 |  |  |  |  | OKGE | Sooner to Rose Hill 345 kV OKGE | New 345 kV line from Sooner to Oklahoma/Kansas | [37 empty] | 2008-06-01 | 2011-01-01 | 2010-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T623309SP | FROM->TO |  | BARTLESVILLE SOUTHEAST - NORTH BARTLESVILLE 138KV CKT 1 | CP | AEPW | AEPW | NORTHERN | TS-KAMO | 0 | 510391 | BV-SE--4 138.00 | 510386 | NBVILLE4 138.00 | 0 |  | 1 | 09SP | 202 | 235 | 101.2 | 100.1216 | 108.1133 | [6 empty] | CATEGORYB | SINGLE | DELAWARE - NORTHEAST STATION 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 510406 | N.E.S.-7 345.00 | 0 |  | 1 |  |  |  |  | OKGE | Sooner to Rose Hill 345 kV OKGE | New 345 kV line from Sooner to Oklahoma/Kansas | [37 empty] | 2008-06-01 | 2011-01-01 | 2010-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T232308SH | FROM->TO |  | BARTLESVILLE SOUTHEAST - NORTH BARTLESVILLE 138KV CKT 1 | CP | AEPW | AEPW | NORTHERN | TS-KAMO | 0 | 510391 | BV-SE--4 138.00 | 510386 | NBVILLE4 138.00 | 0 |  | 1 | 08SH | 202 | 235 |  | 97.9161 | 100.5716 | [6 empty] | CATEGORYB | SINGLE | DELAWARE - NORTHEAST STATION 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 510406 | N.E.S.-7 345.00 | 0 |  | 1 |  |  |  |  | WERE | Sooner to Rose Hill 345 kV WERE | New 345 kV line from Oklahoma/Kansas Stateline to Rose Hill | [37 empty] | 2008-06-01 | 2011-01-01 | 2010-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T502308SP | FROM->TO |  | BARTLESVILLE SOUTHEAST - NORTH BARTLESVILLE 138KV CKT 1 | CP | AEPW | AEPW | NORTHERN | TS-KAMO | 0 | 510391 | BV-SE--4 138.00 | 510386 | NBVILLE4 138.00 | 0 |  | 1 | 08SP | 202 | 235 |  | 97.952 | 101.1703 | [6 empty] | CATEGORYB | SINGLE | DELAWARE - NORTHEAST STATION 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 510406 | N.E.S.-7 345.00 | 0 |  | 1 |  |  |  |  | WERE | Sooner to Rose Hill 345 kV WERE | New 345 kV line from Oklahoma/Kansas Stateline to Rose Hill | [37 empty] | 2008-06-01 | 2011-01-01 | 2010-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T623309SP | FROM->TO |  | BARTLESVILLE SOUTHEAST - NORTH BARTLESVILLE 138KV CKT 1 | CP | AEPW | AEPW | NORTHERN | TS-KAMO | 0 | 510391 | BV-SE--4 138.00 | 510386 | NBVILLE4 138.00 | 0 |  | 1 | 09SP | 202 | 235 | 101.2 | 100.1216 | 108.1133 | [6 empty] | CATEGORYB | SINGLE | DELAWARE - NORTHEAST STATION 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 510406 | N.E.S.-7 345.00 | 0 |  | 1 |  |  |  |  | WERE | Sooner to Rose Hill 345 kV WERE | New 345 kV line from Oklahoma/Kansas Stateline to Rose Hill | [37 empty] | 2008-06-01 | 2011-01-01 | 2010-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T802108SH | TO->FROM |  | ANACONDA - FREEMAN 69KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541291 | FREEMAN2 69.000 | 541292 | ANCONDA2 69.000 | 0 |  | 1 | 08SH | 30 | 32 | 113.7 | 113.8488 | 115.3885 | [6 empty] | CATEGORYB | SINGLE | BELTON SOUTH - PECULIAR 161KV CKT 1 | 0 | 541340 | BELTONS5 161.00 | 541342 | PECULR 5 161.00 | 0 |  | 1 |  |  |  | re-set the overcurrent relay at South Harper 69 kV Bus to open SouthHarper-Freeman 69 kV line | MIPU | South Harper - Freeman 69 kV | re-set the overcurrent relay at South Harper 69 kV Bus to open SouthHarper-Freeman 69 kV line | [37 empty] | 2008-06-01 | 2008-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T812108SH | FROM->TO |  | ANACONDA - HARRISONVILLE WEST 69KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541292 | ANCONDA2 69.000 | 541293 | HSNVLW 2 69.000 | 0 |  | 1 | 08SH | 30 | 32 | 111.2 | 111.3601 | 112.843 | [6 empty] | CATEGORYB | SINGLE | BELTON SOUTH - PECULIAR 161KV CKT 1 | 0 | 541340 | BELTONS5 161.00 | 541342 | PECULR 5 161.00 | 0 |  | 1 |  |  |  | re-set the overcurrent relay at South Harper 69 kV Bus to open SouthHarper-Freeman 69 kV line | MIPU | South Harper - Freeman 69 kV | re-set the overcurrent relay at South Harper 69 kV Bus to open SouthHarper-Freeman 69 kV line | [37 empty] | 2008-06-01 | 2008-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T1981208SP | TO->FROM |  | ANACONDA - FREEMAN 69KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541291 | FREEMAN2 69.000 | 541292 | ANCONDA2 69.000 | 0 |  | 1 | 08SP | 30 | 32 | 113.1 | 113.2287 | 113.9673 | [6 empty] | CATEGORYB | SINGLE | BELTON SOUTH - PECULIAR 161KV CKT 1 | 0 | 541340 | BELTONS5 161.00 | 541342 | PECULR 5 161.00 | 0 |  | 1 |  |  |  | re-set the overcurrent relay at South Harper 69 kV Bus to open SouthHarper-Freeman 69 kV line | MIPU | South Harper - Freeman 69 kV | re-set the overcurrent relay at South Harper 69 kV Bus to open SouthHarper-Freeman 69 kV line | [37 empty] | 2008-06-01 | 2008-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T1991208SP | FROM->TO |  | ANACONDA - HARRISONVILLE WEST 69KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541292 | ANCONDA2 69.000 | 541293 | HSNVLW 2 69.000 | 0 |  | 1 | 08SP | 30 | 32 | 110.0 | 110.174 | 110.9145 | [6 empty] | CATEGORYB | SINGLE | BELTON SOUTH - PECULIAR 161KV CKT 1 | 0 | 541340 | BELTONS5 161.00 | 541342 | PECULR 5 161.00 | 0 |  | 1 |  |  |  | re-set the overcurrent relay at South Harper 69 kV Bus to open SouthHarper-Freeman 69 kV line | MIPU | South Harper - Freeman 69 kV | re-set the overcurrent relay at South Harper 69 kV Bus to open SouthHarper-Freeman 69 kV line | [37 empty] | 2008-06-01 | 2008-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1872109SP | TO->FROM |  | ANACONDA - FREEMAN 69KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541291 | FREEMAN2 69.000 | 541292 | ANCONDA2 69.000 | 0 |  | 1 | 09SP | 30 | 32 | 104.4 | 104.3258 | 126.8763 | [6 empty] | CATEGORYB | SINGLE | BELTON SOUTH - PECULIAR 161KV CKT 1 | 0 | 541340 | BELTONS5 161.00 | 541342 | PECULR 5 161.00 | 0 |  | 1 |  |  |  | re-set the overcurrent relay at South Harper 69 kV Bus to open SouthHarper-Freeman 69 kV line | MIPU | South Harper - Freeman 69 kV | re-set the overcurrent relay at South Harper 69 kV Bus to open SouthHarper-Freeman 69 kV line | [37 empty] | 2008-06-01 | 2008-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1852109SP | TO->FROM |  | ANACONDA - FREEMAN 69KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541291 | FREEMAN2 69.000 | 541292 | ANCONDA2 69.000 | 0 |  | 1 | 09SP | 30 | 32 |  | 63.8749 | 116.8963 | [6 empty] | CATEGORYB | SINGLE | PLEASANT HILL - RALPH GREEN 69KV CKT 1 | 0 | 541279 | RGREEN 2 69.000 | 541280 | PHILL 2 69.000 | 0 |  | 1 |  |  |  | re-set the overcurrent relay at South Harper 69 kV Bus to open SouthHarper-Freeman 69 kV line | MIPU | South Harper - Freeman 69 kV | re-set the overcurrent relay at South Harper 69 kV Bus to open SouthHarper-Freeman 69 kV line | [37 empty] | 2008-06-01 | 2008-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1762109SP | TO->FROM |  | ANACONDA - FREEMAN 69KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541291 | FREEMAN2 69.000 | 541292 | ANCONDA2 69.000 | 0 |  | 1 | 09SP | 30 | 32 |  | 83.6442 | 106.7301 | [6 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 |  |  |  | re-set the overcurrent relay at South Harper 69 kV Bus to open SouthHarper-Freeman 69 kV line | MIPU | South Harper - Freeman 69 kV | re-set the overcurrent relay at South Harper 69 kV Bus to open SouthHarper-Freeman 69 kV line | [37 empty] | 2008-06-01 | 2008-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T3134312SP | TO->FROM |  | ANACONDA - FREEMAN 69KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541291 | FREEMAN2 69.000 | 541292 | ANCONDA2 69.000 | 0 |  | 1 | 12SP | 30 | 32 | 126.9 | 127.7789 | 130.4642 | [6 empty] | CATEGORYB | SINGLE | BELTON SOUTH - PECULIAR 161KV CKT 1 | 0 | 541340 | BELTONS5 161.00 | 541342 | PECULR 5 161.00 | 0 |  | 1 |  |  |  | re-set the overcurrent relay at South Harper 69 kV Bus to open SouthHarper-Freeman 69 kV line | MIPU | South Harper - Freeman 69 kV | re-set the overcurrent relay at South Harper 69 kV Bus to open SouthHarper-Freeman 69 kV line | [37 empty] | 2008-06-01 | 2008-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T3084312SP | TO->FROM |  | ANACONDA - FREEMAN 69KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541291 | FREEMAN2 69.000 | 541292 | ANCONDA2 69.000 | 0 |  | 1 | 12SP | 30 | 32 | 117.6 | 117.7465 | 120.6127 | [6 empty] | CATEGORYB | SINGLE | PLEASANT HILL - RALPH GREEN 69KV CKT 1 | 0 | 541279 | RGREEN 2 69.000 | 541280 | PHILL 2 69.000 | 0 |  | 1 |  |  |  | re-set the overcurrent relay at South Harper 69 kV Bus to open SouthHarper-Freeman 69 kV line | MIPU | South Harper - Freeman 69 kV | re-set the overcurrent relay at South Harper 69 kV Bus to open SouthHarper-Freeman 69 kV line | [37 empty] | 2008-06-01 | 2008-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T534117SP | FROM->TO |  | SOUTHWEST - SOUTHWEST DISPOSAL 161KV CKT 1 | PL | SPRM | SPRM | SPRM | SPRM | 0 | 549954 | SWPS 5 161.00 | 549960 | SWDISP 5 161.00 | 0 |  | 1 | 17SP | 340 | 358 |  | 71.0494 | 107.9411 | [6 empty] | CATEGORYB | SINGLE | BROOKLINE - SPRINGFIELD 161KV CKT 1 | 0 | 505492 | SPRGFLD5 161.00 | 549969 | BRKLNE 5 161.00 | 0 |  | 1 |  |  |  |  | SPRM | SOUTHWEST - SOUTHWEST DISPOSAL 161KV CKT 1 | SOUTHWEST - SOUTHWEST DISPOSAL 161KV CKT 1: Reconductor 161kV Line 1192 MCM AAC to 954 kcmil ACSS/TW 0.67 miles and Upgrade Teminal Equipment | 450 | 475 | 450 | 475 | 0.67 | 6 | 3 | Outage | 0.0003 | 0.0019 | 0.001 |  | 175000 | 2007-11-29 | [23 empty] | 2013-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4452317SP | FROM->TO |  | SOUTHWEST LAWRENCE - WAKARUSA JUNCTION SWITCHING STATION 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533271 | SWLWRNC3 115.00 | 533277 | WAKARUS3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 103.6 | 103.2422 | 109.8158 | [6 empty] | CATEGORYB | SINGLE | FARMERS CONSUMER CO-OP - WAKARUSA JUNCTION SWITCHING STATION 115KV CKT 1 | 0 | 533236 | COOP 3 115.00 | 533277 | WAKARUS3 115.00 | 0 |  | 1 |  |  |  |  | WERE | SOUTHWEST LAWRENCE - WAKARUSA JUNCTION SWITCHING STATION 115KV CKT 1 | Rebuild 4.09 mile SW Lawrence-Wakarusa 115 kV line | 223 | 240 | 223 | 240 | 4.09 | 12 | 5 |  | 0.0025 | 0.02271 | 0.00317 | Breaker and CT limit is 240 MVA. | 1400000 | 2006-07-25 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T10452312SP | TO->FROM |  | STULL SWITCHING STATION - TECUMSEH HILL 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533182 | TECHILE3 115.00 | 533270 | STULL T3 115.00 | 0 |  | 1 | 12SP | 92 | 92 | 119.0 | 116.5841 | 128.2356 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T10472312SP | TO->FROM |  | MOCKINGBIRD HILL SWITCHING STATION - STULL SWITCHING STATION 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533270 | STULL T3 115.00 | 533253 | MOCKBRD3 115.00 | 0 |  | 1 | 12SP | 92 | 92 | 113.2 | 110.7624 | 122.2646 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T17522312SP | TO->FROM |  | STULL SWITCHING STATION - TECUMSEH HILL 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533182 | TECHILE3 115.00 | 533270 | STULL T3 115.00 | 0 |  | 1 | 12SP | 92 | 92 | 100.2 | 99.9382 | 109.09 | [6 empty] | CATEGORYB | GENOUT | GEN532663 1-LAWRENCE ENERGY CENTER UNIT 5 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T17532312SP | TO->FROM |  | MOCKINGBIRD HILL SWITCHING STATION - STULL SWITCHING STATION 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533270 | STULL T3 115.00 | 533253 | MOCKBRD3 115.00 | 0 |  | 1 | 12SP | 92 | 92 |  | 94.1047 | 103.1988 | [6 empty] | CATEGORYB | GENOUT | GEN532663 1-LAWRENCE ENERGY CENTER UNIT 5 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16152317SP | TO->FROM |  | STULL SWITCHING STATION - TECUMSEH HILL 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533182 | TECHILE3 115.00 | 533270 | STULL T3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 141.1 | 138.7515 | 154.4691 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16162317SP | TO->FROM |  | JARBALO JUNCTION SWITCHING STATION - LAWRENCE ENERGY CENTER UNIT 4 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533249 | LEC U4 3 115.00 | 533244 | JARBALO3 115.00 | 0 |  | 1 | 17SP | 118 | 118 | 124.0 | 122.7828 | 131.2995 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16172317SP | TO->FROM |  | MOCKINGBIRD HILL SWITCHING STATION - STULL SWITCHING STATION 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533270 | STULL T3 115.00 | 533253 | MOCKBRD3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 134.1 | 131.7465 | 147.1824 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T25582317SP | TO->FROM |  | STULL SWITCHING STATION - TECUMSEH HILL 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533182 | TECHILE3 115.00 | 533270 | STULL T3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 112.5 | 112.3653 | 122.7168 | [6 empty] | CATEGORYB | GENOUT | GEN532663 1-LAWRENCE ENERGY CENTER UNIT 5 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T25592317SP | TO->FROM |  | MOCKINGBIRD HILL SWITCHING STATION - STULL SWITCHING STATION 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533270 | STULL T3 115.00 | 533253 | MOCKBRD3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 105.7 | 105.6225 | 115.8784 | [6 empty] | CATEGORYB | GENOUT | GEN532663 1-LAWRENCE ENERGY CENTER UNIT 5 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 | TOD 803 | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T3712317SP | TO->FROM |  | STULL SWITCHING STATION - TECUMSEH HILL 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533182 | TECHILE3 115.00 | 533270 | STULL T3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 107.7 | 105.8644 | 121.8628 | [6 empty] | CATEGORYB | SINGLE | HOYT - STRANGER CREEK 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532772 | STRANGR7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0803 - Hoyt - Stranger 345kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T3722317SP | TO->FROM |  | MOCKINGBIRD HILL SWITCHING STATION - STULL SWITCHING STATION 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533270 | STULL T3 115.00 | 533253 | MOCKBRD3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 101.2 | 99.3413 | 115.2132 | [6 empty] | CATEGORYB | SINGLE | HOYT - STRANGER CREEK 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532772 | STRANGR7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T5213217SP | TO->FROM |  | JARBALO JUNCTION SWITCHING STATION - STRANGER CREEK 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533268 | STRANGR3 115.00 | 533244 | JARBALO3 115.00 | 0 |  | 1 | 17SP | 223 | 240 | 100.6 | 101.3954 | 101.7726 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK - THORNTON STREET 115KV CKT 1 | 0 | 533268 | STRANGR3 115.00 | 533272 | THORNTN3 115.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T10582109SP | TO->FROM |  | STULL SWITCHING STATION - TECUMSEH HILL 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533182 | TECHILE3 115.00 | 533270 | STULL T3 115.00 | 0 |  | 1 | 09SP | 92 | 92 |  | 94.4355 | 100.3677 | [6 empty] | CATEGORYB | GENOUT | GEN532663 1-LAWRENCE ENERGY CENTER UNIT 5 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | TOD 803 | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1352109SP | TO->FROM |  | STULL SWITCHING STATION - TECUMSEH HILL 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533182 | TECHILE3 115.00 | 533270 | STULL T3 115.00 | 0 |  | 1 | 09SP | 92 | 92 | 110.9 | 110.7065 | 120.9977 | [6 empty] | CATEGORYB | SINGLE | HOYT - STRANGER CREEK 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532772 | STRANGR7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0803 - Hoyt - Stranger 345kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1362109SP | TO->FROM |  | MOCKINGBIRD HILL SWITCHING STATION - STULL SWITCHING STATION 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533270 | STULL T3 115.00 | 533253 | MOCKBRD3 115.00 | 0 |  | 1 | 09SP | 92 | 92 | 105.8 | 105.5577 | 115.8121 | [6 empty] | CATEGORYB | SINGLE | HOYT - STRANGER CREEK 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532772 | STRANGR7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T6682309SP | TO->FROM |  | STULL SWITCHING STATION - TECUMSEH HILL 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533182 | TECHILE3 115.00 | 533270 | STULL T3 115.00 | 0 |  | 1 | 09SP | 92 | 92 |  | 95.5645 | 102.0707 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T10452312SP | TO->FROM |  | STULL SWITCHING STATION - TECUMSEH HILL 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533182 | TECHILE3 115.00 | 533270 | STULL T3 115.00 | 0 |  | 1 | 12SP | 92 | 92 | 119.0 | 116.5841 | 128.2356 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T10472312SP | TO->FROM |  | MOCKINGBIRD HILL SWITCHING STATION - STULL SWITCHING STATION 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533270 | STULL T3 115.00 | 533253 | MOCKBRD3 115.00 | 0 |  | 1 | 12SP | 92 | 92 | 113.2 | 110.7624 | 122.2646 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T17522312SP | TO->FROM |  | STULL SWITCHING STATION - TECUMSEH HILL 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533182 | TECHILE3 115.00 | 533270 | STULL T3 115.00 | 0 |  | 1 | 12SP | 92 | 92 | 100.2 | 99.9382 | 109.09 | [6 empty] | CATEGORYB | GENOUT | GEN532663 1-LAWRENCE ENERGY CENTER UNIT 5 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T17532312SP | TO->FROM |  | MOCKINGBIRD HILL SWITCHING STATION - STULL SWITCHING STATION 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533270 | STULL T3 115.00 | 533253 | MOCKBRD3 115.00 | 0 |  | 1 | 12SP | 92 | 92 |  | 94.1047 | 103.1988 | [6 empty] | CATEGORYB | GENOUT | GEN532663 1-LAWRENCE ENERGY CENTER UNIT 5 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16152317SP | TO->FROM |  | STULL SWITCHING STATION - TECUMSEH HILL 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533182 | TECHILE3 115.00 | 533270 | STULL T3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 141.1 | 138.7515 | 154.4691 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16162317SP | TO->FROM |  | JARBALO JUNCTION SWITCHING STATION - LAWRENCE ENERGY CENTER UNIT 4 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533249 | LEC U4 3 115.00 | 533244 | JARBALO3 115.00 | 0 |  | 1 | 17SP | 118 | 118 | 124.0 | 122.7828 | 131.2995 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16172317SP | TO->FROM |  | MOCKINGBIRD HILL SWITCHING STATION - STULL SWITCHING STATION 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533270 | STULL T3 115.00 | 533253 | MOCKBRD3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 134.1 | 131.7465 | 147.1824 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T25582317SP | TO->FROM |  | STULL SWITCHING STATION - TECUMSEH HILL 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533182 | TECHILE3 115.00 | 533270 | STULL T3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 112.5 | 112.3653 | 122.7168 | [6 empty] | CATEGORYB | GENOUT | GEN532663 1-LAWRENCE ENERGY CENTER UNIT 5 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T25592317SP | TO->FROM |  | MOCKINGBIRD HILL SWITCHING STATION - STULL SWITCHING STATION 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533270 | STULL T3 115.00 | 533253 | MOCKBRD3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 105.7 | 105.6225 | 115.8784 | [6 empty] | CATEGORYB | GENOUT | GEN532663 1-LAWRENCE ENERGY CENTER UNIT 5 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | TOD 803 | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T3712317SP | TO->FROM |  | STULL SWITCHING STATION - TECUMSEH HILL 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533182 | TECHILE3 115.00 | 533270 | STULL T3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 107.7 | 105.8644 | 121.8628 | [6 empty] | CATEGORYB | SINGLE | HOYT - STRANGER CREEK 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532772 | STRANGR7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0803 - Hoyt - Stranger 345kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T3722317SP | TO->FROM |  | MOCKINGBIRD HILL SWITCHING STATION - STULL SWITCHING STATION 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533270 | STULL T3 115.00 | 533253 | MOCKBRD3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 101.2 | 99.3413 | 115.2132 | [6 empty] | CATEGORYB | SINGLE | HOYT - STRANGER CREEK 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532772 | STRANGR7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T5213217SP | TO->FROM |  | JARBALO JUNCTION SWITCHING STATION - STRANGER CREEK 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533268 | STRANGR3 115.00 | 533244 | JARBALO3 115.00 | 0 |  | 1 | 17SP | 223 | 240 | 100.6 | 101.3954 | 101.7726 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK - THORNTON STREET 115KV CKT 1 | 0 | 533268 | STRANGR3 115.00 | 533272 | THORNTN3 115.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T7234409SP | FROM->TO |  | SUB 124 - AURORA H.T. - SUB 152 - MONETT H.T. 69KV CKT 1 | REL | EMDE | EMDE | AURORA | AURORA | 0 | 547537 | AUR124 2 69.000 | 547540 | MON152 2 69.000 | 0 |  | 1 | 09SP | 48 | 48 | 100.2 | 93.7975 | 101.5253 | [6 empty] | CATEGORYB | SINGLE | SUB 383 - MONETT (MONETT) 161/69/12.5KV TRANSFORMER CKT 1 | 1 | 547480 | MON383 5 161.00 | 547591 | MON383 2 69.000 | 547712 | MON383 1 12.500 | 1 |  |  |  |  | EMDE | SUB 124 - AURORA H.T. - SUB 152 - MONETT H.T. 69KV CKT 1 | Change CT Ratio on breaker #6936 at Aurora #124 | 54 | 65 | 83 | 90 |  | 6 | 6 | [5 empty] | 5000 | 2011-06-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T11462412SP | FROM->TO |  | SUB 124 - AURORA H.T. - SUB 152 - MONETT H.T. 69KV CKT 1 | REL | EMDE | EMDE | AURORA | AURORA | 0 | 547537 | AUR124 2 69.000 | 547540 | MON152 2 69.000 | 0 |  | 1 | 12SP | 48 | 48 | 105.7 | 99.5055 | 107.7375 | [6 empty] | CATEGORYB | SINGLE | SUB 383 - MONETT (MONETT) 161/69/12.5KV TRANSFORMER CKT 1 | 1 | 547480 | MON383 5 161.00 | 547591 | MON383 2 69.000 | 547712 | MON383 1 12.500 | 1 |  |  |  |  | EMDE | SUB 124 - AURORA H.T. - SUB 152 - MONETT H.T. 69KV CKT 1 | Change CT Ratio on breaker #6936 at Aurora #124 | 54 | 65 | 83 | 90 |  | 6 | 6 | [5 empty] | 5000 | 2011-06-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T22482417SP | FROM->TO |  | SUB 124 - AURORA H.T. - SUB 152 - MONETT H.T. 69KV CKT 1 | REL | EMDE | EMDE | AURORA | AURORA | 0 | 547537 | AUR124 2 69.000 | 547540 | MON152 2 69.000 | 0 |  | 1 | 17SP | 48 | 48 | 115.1 | 109.5625 | 117.3841 | [6 empty] | CATEGORYB | SINGLE | SUB 383 - MONETT (MONETT) 161/69/12.5KV TRANSFORMER CKT 1 | 1 | 547480 | MON383 5 161.00 | 547591 | MON383 2 69.000 | 547712 | MON383 1 12.500 | 1 |  |  |  |  | EMDE | SUB 124 - AURORA H.T. - SUB 152 - MONETT H.T. 69KV CKT 1 | Change CT Ratio on breaker #6936 at Aurora #124 | 54 | 65 | 83 | 90 |  | 6 | 6 | [5 empty] | 5000 | 2011-06-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 3 | 2008-12-01 | 2007AG1AFS81T15701317SP | TO->FROM |  | SUB 124 - AURORA H.T. - SUB 383 - MONETT 161KV CKT 1 | REL | EMDE | EMDE | AURORA | AURORA | 0 | 547480 | MON383 5 161.00 | 547468 | AUR124 5 161.00 | 0 |  | 1 | 17SP | 219 | 223 | 104.5 | 100.576 | 101.1561 | [6 empty] | CATEGORYB | SINGLE | SUB 383 - MONETT (MONETT) 161/69/12.5KV TRANSFORMER CKT 1 | 1 | 547480 | MON383 5 161.00 | 547591 | MON383 2 69.000 | 547712 | MON383 1 12.500 | 1 |  |  |  |  | EMDE | SUB 124 - AURORA H.T. - SUB 383 - MONETT 161KV CKT 1 | Change CT Ratio at Sub #383 on Breaker #16186 for 268 MVA Rate B | 218 | 268 | 335 | 335 |  | 6 | 6 | [5 empty] | 5000 | 2017-06-01 | [23 empty] | 2017-06-01 | 2017-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 3 | 2008-12-01 | 2007AG1AFS81T9931312SP | FROM->TO |  | SUB 145 - JOPLIN WEST 7TH - SUB 64 - JOPLIN 10TH ST. 69KV CKT 1 | REL | EMDE | EMDE | JOPLIN | JOPLIN | 0 | 547539 | JOP145 2 69.000 | 547526 | JOP 64 2 69.000 | 0 |  | 1 | 12SP | 63 | 72 | 101.3 | 101.3378 | 101.1379 | [6 empty] | CATEGORYB | SINGLE | SUB 389 - JOPLIN SOUTHWEST (JOPLINSW) 161/69/12.5KV TRANSFORMER CKT 1 | 1 | 547483 | JOP389 5 161.00 | 547592 | JOP389 2 69.000 | 547713 | JOP389 1 12.500 | 1 |  |  |  |  | EMDE | SUB 145 - JOPLIN WEST 7TH - SUB 64 - JOPLIN 10TH ST. 69KV CKT 1 | Replace Disconnect Switches and Leads on Breaker #6965 at Sub #64 and #6932 at Sub #145 | 86 | 104 | 129 | 129 |  | 12 | 6 | [5 empty] | 55000 | 2011-06-01 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T15611117SP | FROM->TO |  | SUB 145 - JOPLIN WEST 7TH - SUB 64 - JOPLIN 10TH ST. 69KV CKT 1 | REL | EMDE | EMDE | JOPLIN | JOPLIN | 0 | 547539 | JOP145 2 69.000 | 547526 | JOP 64 2 69.000 | 0 |  | 1 | 17SP | 63 | 72 | 110.6 | 109.1511 | 108.9296 | [6 empty] | CATEGORYB | SINGLE | SUB 389 - JOPLIN SOUTHWEST (JOPLINSW) 161/69/12.5KV TRANSFORMER CKT 1 | 1 | 547483 | JOP389 5 161.00 | 547592 | JOP389 2 69.000 | 547713 | JOP389 1 12.500 | 1 |  |  |  |  | EMDE | SUB 145 - JOPLIN WEST 7TH - SUB 64 - JOPLIN 10TH ST. 69KV CKT 1 | Replace Disconnect Switches and Leads on Breaker #6965 at Sub #64 and #6932 at Sub #145 | 86 | 104 | 129 | 129 |  | 12 | 6 | [5 empty] | 55000 | 2011-06-01 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T5231117SP | FROM->TO |  | SUB 145 - JOPLIN WEST 7TH - SUB 64 - JOPLIN 10TH ST. 69KV CKT 1 | REL | EMDE | EMDE | JOPLIN | JOPLIN | 0 | 547539 | JOP145 2 69.000 | 547526 | JOP 64 2 69.000 | 0 |  | 1 | 17SP | 63 | 72 | 108.9 | 106.994 | 106.8246 | [6 empty] | CATEGORYB | SINGLE | SUB 167 - RIVERTON - SUB 59 - JOPLIN 26TH ST. 69KV CKT 1 | 0 | 547525 | JOP 59 2 69.000 | 547541 | RIV167 2 69.000 | 0 |  | 1 |  |  |  |  | EMDE | SUB 145 - JOPLIN WEST 7TH - SUB 64 - JOPLIN 10TH ST. 69KV CKT 1 | Replace Disconnect Switches and Leads on Breaker #6965 at Sub #64 and #6932 at Sub #145 | 86 | 104 | 129 | 129 |  | 12 | 6 | [5 empty] | 55000 | 2011-06-01 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T5061117SP | FROM->TO |  | SUB 145 - JOPLIN WEST 7TH - SUB 64 - JOPLIN 10TH ST. 69KV CKT 1 | REL | EMDE | EMDE | JOPLIN | JOPLIN | 0 | 547539 | JOP145 2 69.000 | 547526 | JOP 64 2 69.000 | 0 |  | 1 | 17SP | 63 | 72 | 107.2 | 105.2913 | 105.2201 | [6 empty] | CATEGORYB | SINGLE | SUB 110 - ORONOGO JCT. - SUB 432 - JOPLIN OAKLAND NORTH 161KV CKT 1 | 0 | 547467 | ORO110 5 161.00 | 547494 | OAK432 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 145 - JOPLIN WEST 7TH - SUB 64 - JOPLIN 10TH ST. 69KV CKT 1 | Replace Disconnect Switches and Leads on Breaker #6965 at Sub #64 and #6932 at Sub #145 | 86 | 104 | 129 | 129 |  | 12 | 6 | [5 empty] | 55000 | 2011-06-01 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T4192212SP | FROM->TO |  | SUB 170 - NICHOLS ST. - SUB 80 - MARSHFIELD JCT. 69KV CKT 1 | REL | EMDE | EMDE | OZARK | OZARK | 0 | 547542 | NIC170 2 69.000 | 547529 | SED 80 2 69.000 | 0 |  | 1 | 12SP | 33 | 39 | 105.7 | -999 | 107.2273 | [6 empty] | CATEGORYB | SINGLE | SUB 368 - DADEVILLE EAST - SUB 431 - BOLIVAR SOUTH 161KV CKT 1 | 0 | 547478 | DAD368 5 161.00 | 547493 | BOL431 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 170 - NICHOLS ST. - SUB 80 - MARSHFIELD JCT. 69KV CKT 1 | Reconductor line from Sub #80 to Sub #170 from 1/0 CU to 556 ACSR and replace Jumpers in Sub #80 | 48 | 48 | 48 | 48 |  | 24 | 12 |  | 0.03113 | 0.1238 | 0.00277 |  | 3000000 | 2007-07-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T6252317SP | FROM->TO |  | SUB 170 - NICHOLS ST. - SUB 80 - MARSHFIELD JCT. 69KV CKT 1 | REL | EMDE | EMDE | OZARK | OZARK | 0 | 547542 | NIC170 2 69.000 | 547529 | SED 80 2 69.000 | 0 |  | 1 | 17SP | 33 | 39 | 104.7 | -999 | 114.1779 | [6 empty] | CATEGORYB | SINGLE | SUB 368 - DADEVILLE EAST - SUB 431 - BOLIVAR SOUTH 161KV CKT 1 | 0 | 547478 | DAD368 5 161.00 | 547493 | BOL431 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 170 - NICHOLS ST. - SUB 80 - MARSHFIELD JCT. 69KV CKT 1 | Reconductor line from Sub #80 to Sub #170 from 1/0 CU to 556 ACSR and replace Jumpers in Sub #80 | 48 | 48 | 48 | 48 |  | 24 | 12 |  | 0.03113 | 0.1238 | 0.00277 |  | 3000000 | 2007-07-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T22442417SP | FROM->TO |  | SUB 170 - NICHOLS ST. - SUB 80 - MARSHFIELD JCT. 69KV CKT 1 | REL | EMDE | EMDE | OZARK | OZARK | 0 | 547542 | NIC170 2 69.000 | 547529 | SED 80 2 69.000 | 0 |  | 1 | 17SP | 33 | 39 |  | 98.3932 | 102.202 | [6 empty] | CATEGORYB | SINGLE | MORGAN - SUB 368 - DADEVILLE EAST 161KV CKT 1 | 0 | 547478 | DAD368 5 161.00 | 96101 | 5MORGAN 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 170 - NICHOLS ST. - SUB 80 - MARSHFIELD JCT. 69KV CKT 1 | Reconductor line from Sub #80 to Sub #170 from 1/0 CU to 556 ACSR and replace Jumpers in Sub #80 | 48 | 48 | 48 | 48 |  | 24 | 12 |  | 0.03113 | 0.1238 | 0.00277 |  | 3000000 | 2007-07-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T374108WP | TO->FROM |  | SUB 271 - BAXTER SPRINGS WEST - SUB 404 - HOCKERVILLE 69KV CKT 1 | S | EMDE | EMDE | BAXTER | BAXTER | 0 | 547601 | HOC404 2 69.000 | 547554 | BAX271 2 69.000 | 0 |  | 1 | 08WP | 48 | 48 |  | 96.4394 | 102.3367 | [6 empty] | CATEGORYB | SINGLE | SUB 404 - HOCKERVILLE - SUB 452 - RIVERTON 161KV CKT 1 | 0 | 547469 | RIV4525 161.00 | 547487 | HOC404 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 271 - BAXTER SPRINGS WEST - SUB 404 - HOCKERVILLE 69KV CKT 1 Displacement | Change CT setting on Breaker #6973 at Baxter #271 | 51 | 61 | 66 | 66 |  | 3 | 3 | [5 empty] | 10000 | 2011-10-01 | [23 empty] | 2008-12-01 | 2009-04-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1002112WP | TO->FROM |  | SUB 271 - BAXTER SPRINGS WEST - SUB 404 - HOCKERVILLE 69KV CKT 1 | S | EMDE | EMDE | BAXTER | BAXTER | 0 | 547601 | HOC404 2 69.000 | 547554 | BAX271 2 69.000 | 0 |  | 1 | 12WP | 48 | 48 |  | 93.2851 | 103.6486 | [6 empty] | CATEGORYB | SINGLE | SUB 404 - HOCKERVILLE - SUB 452 - RIVERTON 161KV CKT 1 | 0 | 547469 | RIV4525 161.00 | 547487 | HOC404 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 271 - BAXTER SPRINGS WEST - SUB 404 - HOCKERVILLE 69KV CKT 1 Displacement | Change CT setting on Breaker #6973 at Baxter #271 | 51 | 61 | 66 | 66 |  | 3 | 3 | [5 empty] | 10000 | 2011-10-01 | [23 empty] | 2008-12-01 | 2009-04-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T2175508SP | FROM->TO |  | SUB 389 - JOPLIN SOUTHWEST - SUB 422 - JOPLIN 24TH & CONNECTICUT 161KV CKT 1 | EXP | EMDE | EMDE | JOPLIN | JOPLIN | 0 | 547483 | JOP389 5 161.00 | 547607 | JOP422 5 161.00 | 0 |  | 1 | 08SP | 218 | 223 |  | 99.5225 | 100.1908 | [6 empty] | CATEGORYB | SINGLE | SUB 292 - TIPTON FORD - SUB 389 - JOPLIN SOUTHWEST 161KV CKT 1 | 0 | 547472 | TIP292 5 161.00 | 547483 | JOP389 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 389 - JOPLIN SOUTHWEST - SUB 422 - JOPLIN 24TH & CONNECTICUT 161KV CKT 1 | Change CT Ratio at Sub #389 on Breaker #16170 for 268 MVA Rate B | 268 | 268 |  |  |  | 6 | 6 | [5 empty] | 10000 | 2006-09-01 | [23 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 3 | 2008-12-01 | 2007AG1AFS81T1961309SP | FROM->TO |  | SUB 389 - JOPLIN SOUTHWEST - SUB 422 - JOPLIN 24TH & CONNECTICUT 161KV CKT 1 | EXP | EMDE | EMDE | JOPLIN | JOPLIN | 0 | 547483 | JOP389 5 161.00 | 547607 | JOP422 5 161.00 | 0 |  | 1 | 09SP | 218 | 223 |  | 99.728 | 100.4387 | [6 empty] | CATEGORYB | SINGLE | SUB 292 - TIPTON FORD - SUB 389 - JOPLIN SOUTHWEST 161KV CKT 1 | 0 | 547472 | TIP292 5 161.00 | 547483 | JOP389 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 389 - JOPLIN SOUTHWEST - SUB 422 - JOPLIN 24TH & CONNECTICUT 161KV CKT 1 | Change CT Ratio at Sub #389 on Breaker #16170 for 268 MVA Rate B | 268 | 268 |  |  |  | 6 | 6 | [5 empty] | 10000 | 2006-09-01 | [23 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 3 | 2008-12-01 | 2007AG1AFS81T3191312SP | FROM->TO |  | SUB 389 - JOPLIN SOUTHWEST - SUB 422 - JOPLIN 24TH & CONNECTICUT 161KV CKT 1 | EXP | EMDE | EMDE | JOPLIN | JOPLIN | 0 | 547483 | JOP389 5 161.00 | 547607 | JOP422 5 161.00 | 0 |  | 1 | 12SP | 218 | 223 | 103.2 | 103.3615 | 103.3713 | [6 empty] | CATEGORYB | SINGLE | SUB 292 - TIPTON FORD - SUB 389 - JOPLIN SOUTHWEST 161KV CKT 1 | 0 | 547472 | TIP292 5 161.00 | 547483 | JOP389 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 389 - JOPLIN SOUTHWEST - SUB 422 - JOPLIN 24TH & CONNECTICUT 161KV CKT 1 | Change CT Ratio at Sub #389 on Breaker #16170 for 268 MVA Rate B | 268 | 268 |  |  |  | 6 | 6 | [5 empty] | 10000 | 2006-09-01 | [23 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T5121117SP | FROM->TO |  | SUB 389 - JOPLIN SOUTHWEST - SUB 422 - JOPLIN 24TH & CONNECTICUT 161KV CKT 1 | EXP | EMDE | EMDE | JOPLIN | JOPLIN | 0 | 547483 | JOP389 5 161.00 | 547607 | JOP422 5 161.00 | 0 |  | 1 | 17SP | 218 | 223 | 114.7 | 112.437 | 112.2412 | [6 empty] | CATEGORYB | SINGLE | SUB 292 - TIPTON FORD - SUB 389 - JOPLIN SOUTHWEST 161KV CKT 1 | 0 | 547472 | TIP292 5 161.00 | 547483 | JOP389 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 389 - JOPLIN SOUTHWEST - SUB 422 - JOPLIN 24TH & CONNECTICUT 161KV CKT 1 | Change CT Ratio at Sub #389 on Breaker #16170 for 268 MVA Rate B | 268 | 268 |  |  |  | 6 | 6 | [5 empty] | 10000 | 2006-09-01 | [23 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T3115512SP | FROM->TO |  | SUBSTATION M 161/69KV TRANSFORMER CKT 1 | REL | INDN | INDN | INDN | INDN | 0 | 548814 | SUB M-161 161.00 | 548815 | SUB M 69.000 | 0 |  | 1 | 12SP | 100 | 112 | 104.8 | 103.5595 | 108.5777 | 545_SUBSTATION M 161-69KV TRANSFORMER CKT 2 | [5 empty] | CATEGORYB | SINGLE | BLUE MILLS - ECKLES 161KV CKT 1 | 0 | 543004 | BLUMILS5 161.00 | 548808 | ECKLES-161 161.00 | 0 |  | 1 |  |  |  |  | INDN | SUBSTATION M 161/69KV TRANSFORMER CKT 2 | Add second 100 MVA xfr at Subsation M | 100 | 112 |  |  |  | 18 | [6 empty] | 6600000 | [24 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T3115512SP | FROM->TO |  | SUBSTATION M 161/69KV TRANSFORMER CKT 1 | REL | INDN | INDN | INDN | INDN | 0 | 548814 | SUB M-161 161.00 | 548815 | SUB M 69.000 | 0 |  | 1 | 12SP | 100 | 112 | 104.8 | 103.5595 | 108.5777 | 545_SUBSTATION M 161-69KV TRANSFORMER CKT 2 | [5 empty] | CATEGORYB | SINGLE | BLUE MILLS - ECKLES 161KV CKT 1 | 0 | 543004 | BLUMILS5 161.00 | 548808 | ECKLES-161 161.00 | 0 |  | 1 |  |  |  |  | INDN | SUBSTATION M 161/69KV TRANSFORMER CKT 2 | Add second 100 MVA xfr at Subsation M | 100 | 112 |  |  |  | 18 | [6 empty] | 6600000 | [24 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T3383312SP | FROM->TO |  | SUBSTATION M 161/69KV TRANSFORMER CKT 1 | REL | INDN | INDN | INDN | INDN | 0 | 548814 | SUB M-161 161.00 | 548815 | SUB M 69.000 | 0 |  | 1 | 12SP | 100 | 112 | 100.7 | 98.8406 | 104.5106 | 545_SUBSTATION M 161-69KV TRANSFORMER CKT 2 | [5 empty] | CATEGORYB | SINGLE | BLUE MILLS - BLUE VALLEY 161KV CKT 1 | 0 | 543004 | BLUMILS5 161.00 | 548807 | BLUVLY-161 161.00 | 0 |  | 1 |  |  |  |  | INDN | SUBSTATION M 161/69KV TRANSFORMER CKT 2 | Add second 100 MVA xfr at Subsation M | 100 | 112 |  |  |  | 18 | [6 empty] | 6600000 | [24 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T3383312SP | FROM->TO |  | SUBSTATION M 161/69KV TRANSFORMER CKT 1 | REL | INDN | INDN | INDN | INDN | 0 | 548814 | SUB M-161 161.00 | 548815 | SUB M 69.000 | 0 |  | 1 | 12SP | 100 | 112 | 100.7 | 98.8406 | 104.5106 | 545_SUBSTATION M 161-69KV TRANSFORMER CKT 2 | [5 empty] | CATEGORYB | SINGLE | BLUE MILLS - BLUE VALLEY 161KV CKT 1 | 0 | 543004 | BLUMILS5 161.00 | 548807 | BLUVLY-161 161.00 | 0 |  | 1 |  |  |  |  | INDN | SUBSTATION M 161/69KV TRANSFORMER CKT 2 | Add second 100 MVA xfr at Subsation M | 100 | 112 |  |  |  | 18 | [6 empty] | 6600000 | [24 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T7605517SP | FROM->TO |  | HAWTHORN 161/69KV TRANSFORMER CKT 11 | REL | KACP | KACP | METRO | 69KV | 0 | 542973 | HAWTHRN5 161.00 | 543080 | HAWTH 2 69.000 | 0 |  | 11 | 17SP | 30 | 33 | 105.0 | 103.8468 | 105.622 | 545_SUBSTATION M 161-69KV TRANSFORMER CKT 2 | [5 empty] | CATEGORYB | SINGLE | BLUE MILLS - ECKLES 161KV CKT 1 | 0 | 543004 | BLUMILS5 161.00 | 548808 | ECKLES-161 161.00 | 0 |  | 1 |  |  |  |  | INDN | SUBSTATION M 161/69KV TRANSFORMER CKT 2 | Add second 100 MVA xfr at Subsation M | 100 | 112 |  |  |  | 18 | [6 empty] | 6600000 | [24 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T7605517SP | FROM->TO |  | HAWTHORN 161/69KV TRANSFORMER CKT 11 | REL | KACP | KACP | METRO | 69KV | 0 | 542973 | HAWTHRN5 161.00 | 543080 | HAWTH 2 69.000 | 0 |  | 11 | 17SP | 30 | 33 | 105.0 | 103.8468 | 105.622 | 545_SUBSTATION M 161-69KV TRANSFORMER CKT 2 | [5 empty] | CATEGORYB | SINGLE | BLUE MILLS - ECKLES 161KV CKT 1 | 0 | 543004 | BLUMILS5 161.00 | 548808 | ECKLES-161 161.00 | 0 |  | 1 |  |  |  |  | INDN | SUBSTATION M 161/69KV TRANSFORMER CKT 2 | Add second 100 MVA xfr at Subsation M | 100 | 112 |  |  |  | 18 | [6 empty] | 6600000 | [24 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T7585517SP | FROM->TO |  | HAWTHORN 161/69KV TRANSFORMER CKT 11 | REL | KACP | KACP | METRO | 69KV | 0 | 542973 | HAWTHRN5 161.00 | 543080 | HAWTH 2 69.000 | 0 |  | 11 | 17SP | 30 | 33 | 101.6 | 100.445 | 103.1495 | 545_SUBSTATION M 161-69KV TRANSFORMER CKT 2 | [5 empty] | CATEGORYB | SINGLE | BLUE MILLS - BLUE VALLEY 161KV CKT 1 | 0 | 543004 | BLUMILS5 161.00 | 548807 | BLUVLY-161 161.00 | 0 |  | 1 |  |  |  |  | INDN | SUBSTATION M 161/69KV TRANSFORMER CKT 2 | Add second 100 MVA xfr at Subsation M | 100 | 112 |  |  |  | 18 | [6 empty] | 6600000 | [24 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T7585517SP | FROM->TO |  | HAWTHORN 161/69KV TRANSFORMER CKT 11 | REL | KACP | KACP | METRO | 69KV | 0 | 542973 | HAWTHRN5 161.00 | 543080 | HAWTH 2 69.000 | 0 |  | 11 | 17SP | 30 | 33 | 101.6 | 100.445 | 103.1495 | 545_SUBSTATION M 161-69KV TRANSFORMER CKT 2 | [5 empty] | CATEGORYB | SINGLE | BLUE MILLS - BLUE VALLEY 161KV CKT 1 | 0 | 543004 | BLUMILS5 161.00 | 548807 | BLUVLY-161 161.00 | 0 |  | 1 |  |  |  |  | INDN | SUBSTATION M 161/69KV TRANSFORMER CKT 2 | Add second 100 MVA xfr at Subsation M | 100 | 112 |  |  |  | 18 | [6 empty] | 6600000 | [24 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T5484117SP | FROM->TO |  | HAWTHORN 161/69KV TRANSFORMER CKT 11 | REL | KACP | KACP | METRO | 69KV | 0 | 542973 | HAWTHRN5 161.00 | 543080 | HAWTH 2 69.000 | 0 |  | 11 | 17SP | 30 | 33 | 102.2 | 102.6083 | 102.3384 | 545_SUBSTATION M 161-69KV TRANSFORMER CKT 2 | [5 empty] | CATEGORYB | SINGLE | SUBSTATION M 161/69KV TRANSFORMER CKT 1 | 0 | 548814 | SUB M-161 161.00 | 548815 | SUB M 69.000 | 0 |  | 1 |  |  |  |  | INDN | SUBSTATION M 161/69KV TRANSFORMER CKT 2 | Add second 100 MVA xfr at Subsation M | 100 | 112 |  |  |  | 18 | [6 empty] | 6600000 | [24 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T5484117SP | FROM->TO |  | HAWTHORN 161/69KV TRANSFORMER CKT 11 | REL | KACP | KACP | METRO | 69KV | 0 | 542973 | HAWTHRN5 161.00 | 543080 | HAWTH 2 69.000 | 0 |  | 11 | 17SP | 30 | 33 | 102.2 | 102.6083 | 102.3384 | 545_SUBSTATION M 161-69KV TRANSFORMER CKT 2 | [5 empty] | CATEGORYB | SINGLE | SUBSTATION M 161/69KV TRANSFORMER CKT 1 | 0 | 548814 | SUB M-161 161.00 | 548815 | SUB M 69.000 | 0 |  | 1 |  |  |  |  | INDN | SUBSTATION M 161/69KV TRANSFORMER CKT 2 | Add second 100 MVA xfr at Subsation M | 100 | 112 |  |  |  | 18 | [6 empty] | 6600000 | [24 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T5972117SP | FROM->TO |  | SUBSTATION M 161/69KV TRANSFORMER CKT 1 | REL | INDN | INDN | INDN | INDN | 0 | 548814 | SUB M-161 161.00 | 548815 | SUB M 69.000 | 0 |  | 1 | 17SP | 100 | 112 | 115.8 | 114.3199 | 118.6604 | 545_SUBSTATION M 161-69KV TRANSFORMER CKT 2 | [5 empty] | CATEGORYB | SINGLE | BLUE MILLS - ECKLES 161KV CKT 1 | 0 | 543004 | BLUMILS5 161.00 | 548808 | ECKLES-161 161.00 | 0 |  | 1 |  |  |  |  | INDN | SUBSTATION M 161/69KV TRANSFORMER CKT 2 | Add second 100 MVA xfr at Subsation M | 100 | 112 |  |  |  | 18 | [6 empty] | 6600000 | [24 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T5972117SP | FROM->TO |  | SUBSTATION M 161/69KV TRANSFORMER CKT 1 | REL | INDN | INDN | INDN | INDN | 0 | 548814 | SUB M-161 161.00 | 548815 | SUB M 69.000 | 0 |  | 1 | 17SP | 100 | 112 | 115.8 | 114.3199 | 118.6604 | 545_SUBSTATION M 161-69KV TRANSFORMER CKT 2 | [5 empty] | CATEGORYB | SINGLE | BLUE MILLS - ECKLES 161KV CKT 1 | 0 | 543004 | BLUMILS5 161.00 | 548808 | ECKLES-161 161.00 | 0 |  | 1 |  |  |  |  | INDN | SUBSTATION M 161/69KV TRANSFORMER CKT 2 | Add second 100 MVA xfr at Subsation M | 100 | 112 |  |  |  | 18 | [6 empty] | 6600000 | [24 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T5952117SP | FROM->TO |  | SUBSTATION M 161/69KV TRANSFORMER CKT 1 | REL | INDN | INDN | INDN | INDN | 0 | 548814 | SUB M-161 161.00 | 548815 | SUB M 69.000 | 0 |  | 1 | 17SP | 100 | 112 | 110.4 | 108.9548 | 115.9967 | 545_SUBSTATION M 161-69KV TRANSFORMER CKT 2 | [5 empty] | CATEGORYB | SINGLE | BLUE MILLS - BLUE VALLEY 161KV CKT 1 | 0 | 543004 | BLUMILS5 161.00 | 548807 | BLUVLY-161 161.00 | 0 |  | 1 |  |  |  |  | INDN | SUBSTATION M 161/69KV TRANSFORMER CKT 2 | Add second 100 MVA xfr at Subsation M | 100 | 112 |  |  |  | 18 | [6 empty] | 6600000 | [24 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T5952117SP | FROM->TO |  | SUBSTATION M 161/69KV TRANSFORMER CKT 1 | REL | INDN | INDN | INDN | INDN | 0 | 548814 | SUB M-161 161.00 | 548815 | SUB M 69.000 | 0 |  | 1 | 17SP | 100 | 112 | 110.4 | 108.9548 | 115.9967 | 545_SUBSTATION M 161-69KV TRANSFORMER CKT 2 | [5 empty] | CATEGORYB | SINGLE | BLUE MILLS - BLUE VALLEY 161KV CKT 1 | 0 | 543004 | BLUMILS5 161.00 | 548807 | BLUVLY-161 161.00 | 0 |  | 1 |  |  |  |  | INDN | SUBSTATION M 161/69KV TRANSFORMER CKT 2 | Add second 100 MVA xfr at Subsation M | 100 | 112 |  |  |  | 18 | [6 empty] | 6600000 | [24 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T583208FA | FROM->TO |  | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533368 | EXIDE J3 115.00 | 533372 | PHILIPS3 115.00 | 0 |  | 1 | 08FA | 181 | 196 |  | 105.4532 | 100.1058 | [6 empty] | CATEGORYB | SINGLE | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 0 | 532872 | EMCPHER6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T593208FA | TO->FROM |  | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533368 | EXIDE J3 115.00 | 0 |  | 1 | 08FA | 181 | 196 | 103.7 | 110.454 | 105.1422 | [6 empty] | CATEGORYB | SINGLE | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 0 | 532872 | EMCPHER6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T733208FA | TO->FROM |  | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533368 | EXIDE J3 115.00 | 0 |  | 1 | 08FA | 181 | 196 | 100.1 | 102.9237 | 102.9297 | [6 empty] | CATEGORYB | SINGLE | NORTHVIEW - SUMMIT 115KV CKT 1 | 0 | 533371 | NORTHVW3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T583208FA | FROM->TO |  | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533368 | EXIDE J3 115.00 | 533372 | PHILIPS3 115.00 | 0 |  | 1 | 08FA | 181 | 196 |  | 105.4532 | 100.1058 | [6 empty] | CATEGORYB | SINGLE | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 0 | 532872 | EMCPHER6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T593208FA | TO->FROM |  | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533368 | EXIDE J3 115.00 | 0 |  | 1 | 08FA | 181 | 196 | 103.7 | 110.454 | 105.1422 | [6 empty] | CATEGORYB | SINGLE | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 0 | 532872 | EMCPHER6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T733208FA | TO->FROM |  | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533368 | EXIDE J3 115.00 | 0 |  | 1 | 08FA | 181 | 196 | 100.1 | 102.9237 | 102.9297 | [6 empty] | CATEGORYB | SINGLE | NORTHVIEW - SUMMIT 115KV CKT 1 | 0 | 533371 | NORTHVW3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T582208G | TO->FROM |  | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533368 | EXIDE J3 115.00 | 0 |  | 1 | 08G | 181 | 196 |  | 98.874 | 102.125 | [6 empty] | CATEGORYB | SINGLE | NORTHVIEW - SUMMIT 115KV CKT 1 | 0 | 533371 | NORTHVW3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  |  |  | FNSL | FDNS-Iteration limit exceeded | 2 | 2 | 2008-12-01 | 2007AG1AFS82T12208G | TO->FROM |  | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533368 | EXIDE J3 115.00 | 0 |  | 1 | 08G | 181 | 196 |  | 99.6081 | 101.9374 | [6 empty] | CATEGORYB | SINGLE | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 0 | 532872 | EMCPHER6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T582208G | TO->FROM |  | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533368 | EXIDE J3 115.00 | 0 |  | 1 | 08G | 181 | 196 |  | 98.874 | 102.125 | [6 empty] | CATEGORYB | SINGLE | NORTHVIEW - SUMMIT 115KV CKT 1 | 0 | 533371 | NORTHVW3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  |  |  | FNSL | FDNS-Iteration limit exceeded | 2 | 2 | 2008-12-01 | 2007AG1AFS82T12208G | TO->FROM |  | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533368 | EXIDE J3 115.00 | 0 |  | 1 | 08G | 181 | 196 |  | 99.6081 | 101.9374 | [6 empty] | CATEGORYB | SINGLE | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 0 | 532872 | EMCPHER6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T892208SH | FROM->TO |  | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533368 | EXIDE J3 115.00 | 533372 | PHILIPS3 115.00 | 0 |  | 1 | 08SH | 181 | 196 | 107.1 | 109.5222 | 113.4067 | [6 empty] | CATEGORYB | SINGLE | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 0 | 532872 | EMCPHER6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1132208SH | FROM->TO |  | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533368 | EXIDE J3 115.00 | 533372 | PHILIPS3 115.00 | 0 |  | 1 | 08SH | 181 | 196 | 106.7 | 107.3845 | 110.9819 | [6 empty] | CATEGORYB | SINGLE | NORTHVIEW - SUMMIT 115KV CKT 1 | 0 | 533371 | NORTHVW3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T902208SH | TO->FROM |  | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533368 | EXIDE J3 115.00 | 0 |  | 1 | 08SH | 181 | 196 | 112.5 | 114.9518 | 118.5636 | [6 empty] | CATEGORYB | SINGLE | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 0 | 532872 | EMCPHER6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1142208SH | TO->FROM |  | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533368 | EXIDE J3 115.00 | 0 |  | 1 | 08SH | 181 | 196 | 111.7 | 112.5176 | 116.1554 | [6 empty] | CATEGORYB | SINGLE | NORTHVIEW - SUMMIT 115KV CKT 1 | 0 | 533371 | NORTHVW3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1122208SH | TO->FROM |  | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 08SH | 181 | 181 | 107.8 | 108.4387 | 112.1381 | [6 empty] | CATEGORYB | SINGLE | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | 0 | 533368 | EXIDE J3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T9612208SH | TO->FROM |  | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 08SH | 181 | 181 | 105.1 | 105.6697 | 109.3269 | [6 empty] | CATEGORYB | NONSINGLE | SPP-WERE-73 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1112208SH | TO->FROM |  | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 08SH | 181 | 181 | 104.0 | 104.5398 | 108.2305 | [6 empty] | CATEGORYB | SINGLE | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | 0 | 533368 | EXIDE J3 115.00 | 533372 | PHILIPS3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T892208SH | FROM->TO |  | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533368 | EXIDE J3 115.00 | 533372 | PHILIPS3 115.00 | 0 |  | 1 | 08SH | 181 | 196 | 107.1 | 109.5222 | 113.4067 | [6 empty] | CATEGORYB | SINGLE | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 0 | 532872 | EMCPHER6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1132208SH | FROM->TO |  | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533368 | EXIDE J3 115.00 | 533372 | PHILIPS3 115.00 | 0 |  | 1 | 08SH | 181 | 196 | 106.7 | 107.3845 | 110.9819 | [6 empty] | CATEGORYB | SINGLE | NORTHVIEW - SUMMIT 115KV CKT 1 | 0 | 533371 | NORTHVW3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T902208SH | TO->FROM |  | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533368 | EXIDE J3 115.00 | 0 |  | 1 | 08SH | 181 | 196 | 112.5 | 114.9518 | 118.5636 | [6 empty] | CATEGORYB | SINGLE | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 0 | 532872 | EMCPHER6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1142208SH | TO->FROM |  | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533368 | EXIDE J3 115.00 | 0 |  | 1 | 08SH | 181 | 196 | 111.7 | 112.5176 | 116.1554 | [6 empty] | CATEGORYB | SINGLE | NORTHVIEW - SUMMIT 115KV CKT 1 | 0 | 533371 | NORTHVW3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1122208SH | TO->FROM |  | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 08SH | 181 | 181 | 107.8 | 108.4387 | 112.1381 | [6 empty] | CATEGORYB | SINGLE | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | 0 | 533368 | EXIDE J3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T9612208SH | TO->FROM |  | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 08SH | 181 | 181 | 105.1 | 105.6697 | 109.3269 | [6 empty] | CATEGORYB | NONSINGLE | SPP-WERE-73 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1112208SH | TO->FROM |  | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 08SH | 181 | 181 | 104.0 | 104.5398 | 108.2305 | [6 empty] | CATEGORYB | SINGLE | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | 0 | 533368 | EXIDE J3 115.00 | 533372 | PHILIPS3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1742208SP | FROM->TO |  | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533368 | EXIDE J3 115.00 | 533372 | PHILIPS3 115.00 | 0 |  | 1 | 08SP | 181 | 196 | 112.1 | 110.9061 | 104.9002 | [6 empty] | CATEGORYB | SINGLE | NORTHVIEW - SUMMIT 115KV CKT 1 | 0 | 533371 | NORTHVW3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1752208SP | TO->FROM |  | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533368 | EXIDE J3 115.00 | 0 |  | 1 | 08SP | 181 | 196 | 117.1 | 115.9769 | 109.9847 | [6 empty] | CATEGORYB | SINGLE | NORTHVIEW - SUMMIT 115KV CKT 1 | 0 | 533371 | NORTHVW3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1482208SP | TO->FROM |  | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533368 | EXIDE J3 115.00 | 0 |  | 1 | 08SP | 181 | 196 | 108.5 | 108.1004 | 102.7947 | [6 empty] | CATEGORYB | SINGLE | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 0 | 532872 | EMCPHER6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1732208SP | TO->FROM |  | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 08SP | 181 | 181 | 114.1 | 112.8126 | 106.675 | [6 empty] | CATEGORYB | SINGLE | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | 0 | 533368 | EXIDE J3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T11082208SP | TO->FROM |  | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 08SP | 181 | 181 | 111.3 | 110.0295 | 103.938 | [6 empty] | CATEGORYB | NONSINGLE | SPP-WERE-73 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1722208SP | TO->FROM |  | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 08SP | 181 | 181 | 110.3 | 108.9413 | 102.8254 | [6 empty] | CATEGORYB | SINGLE | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | 0 | 533368 | EXIDE J3 115.00 | 533372 | PHILIPS3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1742208SP | FROM->TO |  | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533368 | EXIDE J3 115.00 | 533372 | PHILIPS3 115.00 | 0 |  | 1 | 08SP | 181 | 196 | 112.1 | 110.9061 | 104.9002 | [6 empty] | CATEGORYB | SINGLE | NORTHVIEW - SUMMIT 115KV CKT 1 | 0 | 533371 | NORTHVW3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1752208SP | TO->FROM |  | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533368 | EXIDE J3 115.00 | 0 |  | 1 | 08SP | 181 | 196 | 117.1 | 115.9769 | 109.9847 | [6 empty] | CATEGORYB | SINGLE | NORTHVIEW - SUMMIT 115KV CKT 1 | 0 | 533371 | NORTHVW3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1482208SP | TO->FROM |  | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533368 | EXIDE J3 115.00 | 0 |  | 1 | 08SP | 181 | 196 | 108.5 | 108.1004 | 102.7947 | [6 empty] | CATEGORYB | SINGLE | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 0 | 532872 | EMCPHER6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1732208SP | TO->FROM |  | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 08SP | 181 | 181 | 114.1 | 112.8126 | 106.675 | [6 empty] | CATEGORYB | SINGLE | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | 0 | 533368 | EXIDE J3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T11082208SP | TO->FROM |  | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 08SP | 181 | 181 | 111.3 | 110.0295 | 103.938 | [6 empty] | CATEGORYB | NONSINGLE | SPP-WERE-73 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1722208SP | TO->FROM |  | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 08SP | 181 | 181 | 110.3 | 108.9413 | 102.8254 | [6 empty] | CATEGORYB | SINGLE | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | 0 | 533368 | EXIDE J3 115.00 | 533372 | PHILIPS3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T643208WP | TO->FROM |  | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533368 | EXIDE J3 115.00 | 0 |  | 1 | 08WP | 181 | 196 | 102.3 | 98.8727 | 100.9928 | [6 empty] | CATEGORYB | SINGLE | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 0 | 532872 | EMCPHER6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T643208WP | TO->FROM |  | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533368 | EXIDE J3 115.00 | 0 |  | 1 | 08WP | 181 | 196 | 102.3 | 98.8727 | 100.9928 | [6 empty] | CATEGORYB | SINGLE | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 0 | 532872 | EMCPHER6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T2383209SP | FROM->TO |  | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533368 | EXIDE J3 115.00 | 533372 | PHILIPS3 115.00 | 0 |  | 1 | 09SP | 181 | 196 | 116.0 | 115.6636 | 118.4537 | [6 empty] | CATEGORYB | SINGLE | NORTHVIEW - SUMMIT 115KV CKT 1 | 0 | 533371 | NORTHVW3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T2393209SP | TO->FROM |  | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533368 | EXIDE J3 115.00 | 0 |  | 1 | 09SP | 181 | 196 | 121.3 | 121.0332 | 123.8824 | [6 empty] | CATEGORYB | SINGLE | NORTHVIEW - SUMMIT 115KV CKT 1 | 0 | 533371 | NORTHVW3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T2202209SP | TO->FROM |  | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533368 | EXIDE J3 115.00 | 0 |  | 1 | 09SP | 181 | 196 | 100.9 | 100.3273 | 102.6122 | [6 empty] | CATEGORYB | SINGLE | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 0 | 532872 | EMCPHER6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T2373209SP | TO->FROM |  | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 09SP | 181 | 181 | 118.7 | 118.4441 | 121.532 | [6 empty] | CATEGORYB | SINGLE | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | 0 | 533368 | EXIDE J3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T14343209SP | TO->FROM |  | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 09SP | 181 | 181 | 115.9 | 115.6067 | 118.6495 | [6 empty] | CATEGORYB | NONSINGLE | SPP-WERE-73 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T2363209SP | TO->FROM |  | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 09SP | 181 | 181 | 114.7 | 114.3562 | 117.3901 | [6 empty] | CATEGORYB | SINGLE | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | 0 | 533368 | EXIDE J3 115.00 | 533372 | PHILIPS3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T2383209SP | FROM->TO |  | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533368 | EXIDE J3 115.00 | 533372 | PHILIPS3 115.00 | 0 |  | 1 | 09SP | 181 | 196 | 116.0 | 115.6636 | 118.4537 | [6 empty] | CATEGORYB | SINGLE | NORTHVIEW - SUMMIT 115KV CKT 1 | 0 | 533371 | NORTHVW3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T2393209SP | TO->FROM |  | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533368 | EXIDE J3 115.00 | 0 |  | 1 | 09SP | 181 | 196 | 121.3 | 121.0332 | 123.8824 | [6 empty] | CATEGORYB | SINGLE | NORTHVIEW - SUMMIT 115KV CKT 1 | 0 | 533371 | NORTHVW3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T2202209SP | TO->FROM |  | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533368 | EXIDE J3 115.00 | 0 |  | 1 | 09SP | 181 | 196 | 100.9 | 100.3273 | 102.6122 | [6 empty] | CATEGORYB | SINGLE | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 0 | 532872 | EMCPHER6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T2373209SP | TO->FROM |  | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 09SP | 181 | 181 | 118.7 | 118.4441 | 121.532 | [6 empty] | CATEGORYB | SINGLE | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | 0 | 533368 | EXIDE J3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T14343209SP | TO->FROM |  | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 09SP | 181 | 181 | 115.9 | 115.6067 | 118.6495 | [6 empty] | CATEGORYB | NONSINGLE | SPP-WERE-73 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T2363209SP | TO->FROM |  | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 09SP | 181 | 181 | 114.7 | 114.3562 | 117.3901 | [6 empty] | CATEGORYB | SINGLE | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | 0 | 533368 | EXIDE J3 115.00 | 533372 | PHILIPS3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 1 | 2008-12-01 | 2007AG1AFS81T2553112SP | FROM->TO |  | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533368 | EXIDE J3 115.00 | 533372 | PHILIPS3 115.00 | 0 |  | 1 | 12SP | 181 | 196 | 105.9 | 104.8826 | 108.1927 | [6 empty] | CATEGORYB | SINGLE | NORTHVIEW - SUMMIT 115KV CKT 1 | 0 | 533371 | NORTHVW3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 1 | 2008-12-01 | 2007AG1AFS81T2563112SP | TO->FROM |  | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533368 | EXIDE J3 115.00 | 0 |  | 1 | 12SP | 181 | 196 | 111.6 | 110.5919 | 113.9755 | [6 empty] | CATEGORYB | SINGLE | NORTHVIEW - SUMMIT 115KV CKT 1 | 0 | 533371 | NORTHVW3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 1 | 2008-12-01 | 2007AG1AFS81T2543112SP | TO->FROM |  | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 12SP | 181 | 181 | 120.8 | 119.7323 | 123.5092 | [6 empty] | CATEGORYB | SINGLE | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | 0 | 533368 | EXIDE J3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 1 | 2008-12-01 | 2007AG1AFS81T13653112SP | TO->FROM |  | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 12SP | 181 | 181 | 115.6 | 114.4294 | 118.1774 | [6 empty] | CATEGORYB | NONSINGLE | SPP-WERE-73 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 1 | 2008-12-01 | 2007AG1AFS81T2533112SP | TO->FROM |  | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 12SP | 181 | 181 | 114.9 | 113.8004 | 117.5314 | [6 empty] | CATEGORYB | SINGLE | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | 0 | 533368 | EXIDE J3 115.00 | 533372 | PHILIPS3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 1 | 2008-12-01 | 2007AG1AFS81T2553112SP | FROM->TO |  | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533368 | EXIDE J3 115.00 | 533372 | PHILIPS3 115.00 | 0 |  | 1 | 12SP | 181 | 196 | 105.9 | 104.8826 | 108.1927 | [6 empty] | CATEGORYB | SINGLE | NORTHVIEW - SUMMIT 115KV CKT 1 | 0 | 533371 | NORTHVW3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 1 | 2008-12-01 | 2007AG1AFS81T2563112SP | TO->FROM |  | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533368 | EXIDE J3 115.00 | 0 |  | 1 | 12SP | 181 | 196 | 111.6 | 110.5919 | 113.9755 | [6 empty] | CATEGORYB | SINGLE | NORTHVIEW - SUMMIT 115KV CKT 1 | 0 | 533371 | NORTHVW3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 1 | 2008-12-01 | 2007AG1AFS81T2543112SP | TO->FROM |  | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 12SP | 181 | 181 | 120.8 | 119.7323 | 123.5092 | [6 empty] | CATEGORYB | SINGLE | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | 0 | 533368 | EXIDE J3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 1 | 2008-12-01 | 2007AG1AFS81T13653112SP | TO->FROM |  | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 12SP | 181 | 181 | 115.6 | 114.4294 | 118.1774 | [6 empty] | CATEGORYB | NONSINGLE | SPP-WERE-73 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 1 | 2008-12-01 | 2007AG1AFS81T2533112SP | TO->FROM |  | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 12SP | 181 | 181 | 114.9 | 113.8004 | 117.5314 | [6 empty] | CATEGORYB | SINGLE | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | 0 | 533368 | EXIDE J3 115.00 | 533372 | PHILIPS3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 1 | 2008-12-01 | 2007AG1AFS81T4473117SP | FROM->TO |  | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533368 | EXIDE J3 115.00 | 533372 | PHILIPS3 115.00 | 0 |  | 1 | 17SP | 181 | 196 | 121.9 | 121.8237 | 124.2057 | [6 empty] | CATEGORYB | SINGLE | NORTHVIEW - SUMMIT 115KV CKT 1 | 0 | 533371 | NORTHVW3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 1 | 2008-12-01 | 2007AG1AFS81T4483117SP | TO->FROM |  | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533368 | EXIDE J3 115.00 | 0 |  | 1 | 17SP | 181 | 196 | 127.7 | 127.6362 | 130.0332 | [6 empty] | CATEGORYB | SINGLE | NORTHVIEW - SUMMIT 115KV CKT 1 | 0 | 533371 | NORTHVW3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 1 | 2008-12-01 | 2007AG1AFS81T4463117SP | TO->FROM |  | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 17SP | 181 | 181 | 138.5 | 138.4958 | 141.1367 | [6 empty] | CATEGORYB | SINGLE | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | 0 | 533368 | EXIDE J3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 1 | 2008-12-01 | 2007AG1AFS81T20943117SP | TO->FROM |  | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 17SP | 181 | 181 | 133.0 | 132.9141 | 135.5972 | [6 empty] | CATEGORYB | NONSINGLE | SPP-WERE-73 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 1 | 2008-12-01 | 2007AG1AFS81T4453117SP | TO->FROM |  | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 17SP | 181 | 181 | 132.4 | 132.3227 | 134.9848 | [6 empty] | CATEGORYB | SINGLE | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | 0 | 533368 | EXIDE J3 115.00 | 533372 | PHILIPS3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 1 | 2008-12-01 | 2007AG1AFS81T4473117SP | FROM->TO |  | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533368 | EXIDE J3 115.00 | 533372 | PHILIPS3 115.00 | 0 |  | 1 | 17SP | 181 | 196 | 121.9 | 121.8237 | 124.2057 | [6 empty] | CATEGORYB | SINGLE | NORTHVIEW - SUMMIT 115KV CKT 1 | 0 | 533371 | NORTHVW3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 1 | 2008-12-01 | 2007AG1AFS81T4483117SP | TO->FROM |  | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533368 | EXIDE J3 115.00 | 0 |  | 1 | 17SP | 181 | 196 | 127.7 | 127.6362 | 130.0332 | [6 empty] | CATEGORYB | SINGLE | NORTHVIEW - SUMMIT 115KV CKT 1 | 0 | 533371 | NORTHVW3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 1 | 2008-12-01 | 2007AG1AFS81T4463117SP | TO->FROM |  | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 17SP | 181 | 181 | 138.5 | 138.4958 | 141.1367 | [6 empty] | CATEGORYB | SINGLE | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | 0 | 533368 | EXIDE J3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 1 | 2008-12-01 | 2007AG1AFS81T20943117SP | TO->FROM |  | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 17SP | 181 | 181 | 133.0 | 132.9141 | 135.5972 | [6 empty] | CATEGORYB | NONSINGLE | SPP-WERE-73 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 1 | 2008-12-01 | 2007AG1AFS81T4453117SP | TO->FROM |  | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 17SP | 181 | 181 | 132.4 | 132.3227 | 134.9848 | [6 empty] | CATEGORYB | SINGLE | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | 0 | 533368 | EXIDE J3 115.00 | 533372 | PHILIPS3 115.00 | 0 |  | 1 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2008-04-01 | 2009-12-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T10582109SP | TO->FROM |  | STULL SWITCHING STATION - TECUMSEH HILL 115KV CKT 1 | S | WERE | WERE | NEAST | NEAST | 0 | 533182 | TECHILE3 115.00 | 533270 | STULL T3 115.00 | 0 |  | 1 | 09SP | 92 | 92 |  | 94.4355 | 100.3677 | [6 empty] | CATEGORYB | GENOUT | GEN532663 1-LAWRENCE ENERGY CENTER UNIT 5 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | TOD 803 | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1352109SP | TO->FROM |  | STULL SWITCHING STATION - TECUMSEH HILL 115KV CKT 1 | S | WERE | WERE | NEAST | NEAST | 0 | 533182 | TECHILE3 115.00 | 533270 | STULL T3 115.00 | 0 |  | 1 | 09SP | 92 | 92 | 110.9 | 110.7065 | 120.9977 | [6 empty] | CATEGORYB | SINGLE | HOYT - STRANGER CREEK 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532772 | STRANGR7 345.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0803 - Hoyt - Stranger 345kV | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1362109SP | TO->FROM |  | MOCKINGBIRD HILL SWITCHING STATION - STULL SWITCHING STATION 115KV CKT 1 | S | WERE | WERE | NEAST | NEAST | 0 | 533270 | STULL T3 115.00 | 533253 | MOCKBRD3 115.00 | 0 |  | 1 | 09SP | 92 | 92 | 105.8 | 105.5577 | 115.8121 | [6 empty] | CATEGORYB | SINGLE | HOYT - STRANGER CREEK 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532772 | STRANGR7 345.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T6682309SP | TO->FROM |  | STULL SWITCHING STATION - TECUMSEH HILL 115KV CKT 1 | S | WERE | WERE | NEAST | NEAST | 0 | 533182 | TECHILE3 115.00 | 533270 | STULL T3 115.00 | 0 |  | 1 | 09SP | 92 | 92 |  | 95.5645 | 102.0707 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T10452312SP | TO->FROM |  | STULL SWITCHING STATION - TECUMSEH HILL 115KV CKT 1 | S | WERE | WERE | NEAST | NEAST | 0 | 533182 | TECHILE3 115.00 | 533270 | STULL T3 115.00 | 0 |  | 1 | 12SP | 92 | 92 | 119.0 | 116.5841 | 128.2356 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T10472312SP | TO->FROM |  | MOCKINGBIRD HILL SWITCHING STATION - STULL SWITCHING STATION 115KV CKT 1 | S | WERE | WERE | NEAST | NEAST | 0 | 533270 | STULL T3 115.00 | 533253 | MOCKBRD3 115.00 | 0 |  | 1 | 12SP | 92 | 92 | 113.2 | 110.7624 | 122.2646 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T17522312SP | TO->FROM |  | STULL SWITCHING STATION - TECUMSEH HILL 115KV CKT 1 | S | WERE | WERE | NEAST | NEAST | 0 | 533182 | TECHILE3 115.00 | 533270 | STULL T3 115.00 | 0 |  | 1 | 12SP | 92 | 92 | 100.2 | 99.9382 | 109.09 | [6 empty] | CATEGORYB | GENOUT | GEN532663 1-LAWRENCE ENERGY CENTER UNIT 5 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T17532312SP | TO->FROM |  | MOCKINGBIRD HILL SWITCHING STATION - STULL SWITCHING STATION 115KV CKT 1 | S | WERE | WERE | NEAST | NEAST | 0 | 533270 | STULL T3 115.00 | 533253 | MOCKBRD3 115.00 | 0 |  | 1 | 12SP | 92 | 92 |  | 94.1047 | 103.1988 | [6 empty] | CATEGORYB | GENOUT | GEN532663 1-LAWRENCE ENERGY CENTER UNIT 5 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16152317SP | TO->FROM |  | STULL SWITCHING STATION - TECUMSEH HILL 115KV CKT 1 | S | WERE | WERE | NEAST | NEAST | 0 | 533182 | TECHILE3 115.00 | 533270 | STULL T3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 141.1 | 138.7515 | 154.4691 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16162317SP | TO->FROM |  | JARBALO JUNCTION SWITCHING STATION - LAWRENCE ENERGY CENTER UNIT 4 115KV CKT 1 | S | WERE | WERE | NEAST | NEAST | 0 | 533249 | LEC U4 3 115.00 | 533244 | JARBALO3 115.00 | 0 |  | 1 | 17SP | 118 | 118 | 124.0 | 122.7828 | 131.2995 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16172317SP | TO->FROM |  | MOCKINGBIRD HILL SWITCHING STATION - STULL SWITCHING STATION 115KV CKT 1 | S | WERE | WERE | NEAST | NEAST | 0 | 533270 | STULL T3 115.00 | 533253 | MOCKBRD3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 134.1 | 131.7465 | 147.1824 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T25582317SP | TO->FROM |  | STULL SWITCHING STATION - TECUMSEH HILL 115KV CKT 1 | S | WERE | WERE | NEAST | NEAST | 0 | 533182 | TECHILE3 115.00 | 533270 | STULL T3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 112.5 | 112.3653 | 122.7168 | [6 empty] | CATEGORYB | GENOUT | GEN532663 1-LAWRENCE ENERGY CENTER UNIT 5 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T25592317SP | TO->FROM |  | MOCKINGBIRD HILL SWITCHING STATION - STULL SWITCHING STATION 115KV CKT 1 | S | WERE | WERE | NEAST | NEAST | 0 | 533270 | STULL T3 115.00 | 533253 | MOCKBRD3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 105.7 | 105.6225 | 115.8784 | [6 empty] | CATEGORYB | GENOUT | GEN532663 1-LAWRENCE ENERGY CENTER UNIT 5 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T3702317SP | FROM->TO |  | TECUMSEH ENERGY CENTER - TECUMSEH HILL 115KV CKT 1 | S | WERE | WERE | NEAST | NEAST | 0 | 533180 | TEC E 3 115.00 | 533182 | TECHILE3 115.00 | 0 |  | 1 | 17SP | 236 | 236 | 106.0 | 104.5506 | 110.2136 | [6 empty] | CATEGORYB | SINGLE | HOYT - STRANGER CREEK 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532772 | STRANGR7 345.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T3702317SP | FROM->TO |  | TECUMSEH ENERGY CENTER - TECUMSEH HILL 115KV CKT 1 | S | WERE | WERE | NEAST | NEAST | 0 | 533180 | TEC E 3 115.00 | 533182 | TECHILE3 115.00 | 0 |  | 1 | 17SP | 236 | 236 | 106.0 | 104.5506 | 110.2136 | [6 empty] | CATEGORYB | SINGLE | HOYT - STRANGER CREEK 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532772 | STRANGR7 345.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | TOD 803 | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T3712317SP | TO->FROM |  | STULL SWITCHING STATION - TECUMSEH HILL 115KV CKT 1 | S | WERE | WERE | NEAST | NEAST | 0 | 533182 | TECHILE3 115.00 | 533270 | STULL T3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 107.7 | 105.8644 | 121.8628 | [6 empty] | CATEGORYB | SINGLE | HOYT - STRANGER CREEK 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532772 | STRANGR7 345.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 | 0803 - Hoyt - Stranger 345kV | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T3722317SP | TO->FROM |  | MOCKINGBIRD HILL SWITCHING STATION - STULL SWITCHING STATION 115KV CKT 1 | S | WERE | WERE | NEAST | NEAST | 0 | 533270 | STULL T3 115.00 | 533253 | MOCKBRD3 115.00 | 0 |  | 1 | 17SP | 92 | 92 | 101.2 | 99.3413 | 115.2132 | [6 empty] | CATEGORYB | SINGLE | HOYT - STRANGER CREEK 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532772 | STRANGR7 345.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T5213217SP | TO->FROM |  | JARBALO JUNCTION SWITCHING STATION - STRANGER CREEK 115KV CKT 1 | S | WERE | WERE | NEAST | NEAST | 0 | 533268 | STRANGR3 115.00 | 533244 | JARBALO3 115.00 | 0 |  | 1 | 17SP | 223 | 240 | 100.6 | 101.3954 | 101.7726 | [6 empty] | CATEGORYB | SINGLE | STRANGER CREEK - THORNTON STREET 115KV CKT 1 | 0 | 533268 | STRANGR3 115.00 | 533272 | THORNTN3 115.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T1052408SH | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 08SH | 32 | 32 |  | 25.2998 | 101.9869 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1872208SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 08SP | 32 | 32 |  | 29.7355 | 122.0877 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1862208SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 08SP | 32 | 32 |  | 26.3121 | 118.4294 | [6 empty] | CATEGORYB | SINGLE | ORCHARD - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533643 | ORCHARD2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T1652308SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 08SP | 32 | 32 |  | 12.5859 | 111.7993 | [6 empty] | CATEGORYB | SINGLE | ATHENS SWITCHING STATION - OWL CREEK 69KV CKT 1 | 0 | 533623 | ATHENS 2 69.000 | 533642 | OWL CRK2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T1582408SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 08SP | 58 | 58 |  | 65.4461 | 103.802 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T1612408SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 08SP | 58 | 58 |  | 63.6438 | 101.879 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T1492108SP | TO->FROM |  | LEHIGH TAP - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 08SP | 32 | 32 |  | 9.733 | 120.9169 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T1883309SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 09SP | 32 | 32 |  | 29.8705 | 124.2703 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T1873309SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 09SP | 32 | 32 |  | 26.4167 | 120.5106 | [6 empty] | CATEGORYB | SINGLE | ORCHARD - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533643 | ORCHARD2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T1833309SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 09SP | 32 | 32 |  | 12.6944 | 113.9161 | [6 empty] | CATEGORYB | SINGLE | ATHENS SWITCHING STATION - OWL CREEK 69KV CKT 1 | 0 | 533623 | ATHENS 2 69.000 | 533642 | OWL CRK2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T1794409SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 09SP | 58 | 58 |  | 65.5805 | 104.7422 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81T1824409SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 09SP | 58 | 58 |  | 63.7171 | 102.7839 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T6324109SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 09SP | 58 | 58 |  | 72.8628 | 100.1831 | [6 empty] | CATEGORYB | SINGLE | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81T1751409SP | TO->FROM |  | LEHIGH TAP - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 09SP | 32 | 32 |  | 8.7892 | 124.0056 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2451112SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12SP | 32 | 32 |  | -999 | 185.4455 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T8991112SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12SP | 32 | 32 |  | -999 | 184.8256 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T2942112SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12SP | 32 | 32 |  | 31.8691 | 130.8571 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2461112SP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 157.4692 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T9001112SP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 156.7557 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2471112SP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 12SP | 108 | 108 |  | -999 | 170.7109 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T9011112SP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 12SP | 108 | 108 |  | -999 | 170.0226 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2792412SP | TO->FROM |  | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 56.0845 | 117.3039 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2912412SP | TO->FROM |  | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 55.5503 | 112.3373 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T1582212SP | TO->FROM |  | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 72.3233 | 103.7043 | [6 empty] | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2782412SP | FROM->TO |  | ALTOONA - TIOGA 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 41.4013 | 157.0806 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T2972112SP | FROM->TO |  | ALTOONA - TIOGA 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 40.3416 | 153.9666 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T2772112SP | FROM->TO |  | ALTOONA - TIOGA 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 35.1642 | 128.815 | [6 empty] | CATEGORYB | SINGLE | ALLEN - ZILA JUNCTION 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | NCONV |  |  | FNSL-Blown up | FDNS-Blown up | 2 | 3 | 2008-12-01 | 2007AG1AFS84L32312SP |  |  | ALTOONA - TIOGA 138KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 | 12SP | 143 | 143 |  | 25.1844 | 72.1214 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2812412SP | TO->FROM | Bidirectional | ARCO TAP - ENA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533634 | ENA 2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | 51.9299 | 110.5372 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2431112SP | FROM->TO | Bidirectional | ARCO TAP - ENA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533620 | ARCOTAP2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 108.209 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T8971112SP | FROM->TO | Bidirectional | ARCO TAP - ENA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533620 | ARCOTAP2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 107.7968 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2441112SP | TO->FROM | Bidirectional | ARCO TAP - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533641 | MONARCH2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 111.7972 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T8981112SP | TO->FROM | Bidirectional | ARCO TAP - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533641 | MONARCH2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | -999 | 111.3621 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2822412SP | FROM->TO | Bidirectional | ARCO TAP - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533620 | ARCOTAP2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 12SP | 72 | 72 |  | 49.4684 | 107.2233 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2662412SP | FROM->TO |  | ATHENS SWITCHING STATION - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533623 | ATHENS 2 69.000 | 533642 | OWL CRK2 69.000 | 0 |  | 1 | 12SP | 41 | 41 |  | 10.1577 | 122.0473 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2832412SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12SP | 58 | 58 |  | 67.3281 | 140.9509 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T3022112SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12SP | 58 | 58 |  | 65.3825 | 136.6898 | [6 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2481112SP | FROM->TO | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533634 | ENA 2 69.000 | 533646 | TIOGA 2 69.000 | 0 |  | 1 | 12SP | 58 | 58 |  | -999 | 130.2259 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T2672412SP | TO->FROM |  | LEHIGH TAP - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12SP | 32 | 32 |  | 9.2569 | 152.3867 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2491112SP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 12SP | 100 | 100 |  | -999 | 193.7517 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T9031112SP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 12SP | 100 | 100 |  | -999 | 192.9783 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T2501112SP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 12SP | 108 | 108 |  | -999 | 178.3467 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T9041112SP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 12SP | 108 | 108 |  | -999 | 177.6278 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T572112WP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12WP | 32 | 32 |  | 24.6721 | 179.9951 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T3802112WP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12WP | 32 | 32 |  | 24.8481 | 179.8879 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T574312WP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12WP | 32 | 32 |  | 22.9815 | 100.7665 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T582112WP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 39.9857 | 150.9578 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T3812112WP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 40.0893 | 150.8733 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T553312WP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 12WP | 108 | 108 |  | 36.4684 | 159.2099 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T3843312WP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 12WP | 108 | 108 |  | 36.5782 | 159.1568 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T464112WP | FROM->TO | Bidirectional | ARCO TAP - ENA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533620 | ARCOTAP2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 9.7864 | 101.0901 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T3394112WP | FROM->TO | Bidirectional | ARCO TAP - ENA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533620 | ARCOTAP2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 10.0489 | 100.9961 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T474112WP | TO->FROM | Bidirectional | ARCO TAP - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533641 | MONARCH2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 11.0682 | 103.599 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T3404112WP | TO->FROM | Bidirectional | ARCO TAP - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533641 | MONARCH2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 | 12WP | 72 | 72 |  | 11.2882 | 103.5055 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T514112WP | FROM->TO | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533634 | ENA 2 69.000 | 533646 | TIOGA 2 69.000 | 0 |  | 1 | 12WP | 58 | 58 |  | 10.7435 | 122.8447 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81T3444112WP | FROM->TO | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533634 | ENA 2 69.000 | 533646 | TIOGA 2 69.000 | 0 |  | 1 | 12WP | 58 | 58 |  | 11.1297 | 122.7501 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81T964212WP | TO->FROM |  | LEHIGH TAP - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 12WP | 32 | 32 |  | 7.335 | 100.4311 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T593312WP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 12WP | 100 | 100 |  | 44.6309 | 179.6932 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T3883312WP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 12WP | 100 | 100 |  | 44.776 | 179.5805 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81T613312WP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 12WP | 108 | 108 |  | 40.4185 | 165.4322 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 4 | 3 | 2008-12-01 | 2007AG1AFS81T3024312WP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 12WP | 108 | 108 |  | 40.5965 | 165.359 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4092317SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 17SP | 32 | 32 |  | 14.5581 | 132.3017 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16612317SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 17SP | 32 | 32 |  | 14.4858 | 131.4416 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4832317SP | FROM->TO |  | ALLEN - LEHIGH TAP 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 17SP | 32 | 32 |  | 35.6597 | 126.9833 | [6 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4102317SP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 17SP | 72 | 72 |  | 23.268 | 100.8105 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16622317SP | FROM->TO |  | ALLEN - MONARCH 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533641 | MONARCH2 69.000 | 0 |  | 1 | 17SP | 72 | 72 |  | 23.1386 | 100.3044 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4112317SP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 17SP | 108 | 108 |  | 28.8307 | 116.5141 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16632317SP | TO->FROM |  | ALLEN - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533654 | ZILAJCT2 69.000 | 533621 | ALLEN 2 69.000 | 0 |  | 1 | 17SP | 108 | 108 |  | 28.7177 | 115.9243 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T6122417SP | TO->FROM | Bidirectional | ENA - TIOGA 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 | 17SP | 58 | 58 |  | 70.7819 | 101.4296 | [6 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81T4742117SP | TO->FROM |  | LEHIGH TAP - OWL CREEK 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 17SP | 32 | 32 |  | 11.392 | 117.9501 | [6 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4122317SP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 17SP | 100 | 100 |  | 38.8083 | 133.7621 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16642317SP | FROM->TO |  | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 | 17SP | 100 | 100 |  | 38.688 | 133.0647 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 1102 - Altoona - Tioga 138kV |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T4132317SP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 17SP | 108 | 108 |  | 34.6116 | 122.4871 | [6 empty] | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 532996 | TIOGA 4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 | 0614 - Tioga 138-69kV XFMR |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81T16652317SP | FROM->TO |  | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 | 17SP | 108 | 108 |  | 34.4969 | 121.8479 | [6 empty] | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Vernon to Athens 69 kV | Rebuild 5.17 miles Green to Vernon 69 kV (138kV/69kV Operation) | 72 | 72 | 72 | 72 | 5.17 | 18 | 6 |  | 0.01091 | 0.07424 | 0.00158 | Terminal equipment limit | 2132879 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81T351408AP | TO->FROM |  | MIDIAN - WILLIAMS BROTHERS PIPELINE 161KV CKT 1 | PL | WERE | WERE | NEAST | SCENTRAL | 0 | 532921 | WM BROS5 161.00 | 532936 | MIDIAN 5 161.00 | 0 |  | 1 | 08AP | 84 | 84 |  | 96.4989 | 101.3431 | [6 empty] | CATEGORYB | SINGLE | LANG - WICHITA 345KV CKT 1 | 0 | 532769 | LANG 7 345.00 | 532796 | WICHITA7 345.00 | 0 |  | 1 |  |  |  |  | WERE | WICHITA - RENO 345KV | Build 345kV from Wichita to Reno Co | 1383 | 1468 | 1383 | 1468 | 40 | 54 | 6 | Y | 0.0014 | 0.01998 | 0.32792 |  | 42000000 | 2005-09-09 | [23 empty] | 2008-04-01 | 2008-12-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T371208AP | FROM->TO |  | NORTH AMERICAN PHILIPS JUNCTION (SOUTH) - WEST MCPHERSON 115KV CKT 1 | PL | WERE | WERE | WEST | WEST | 0 | 533374 | SPHILPJ3 115.00 | 533438 | WMCPHER3 115.00 | 0 |  | 1 | 08AP | 68 | 68 |  | -999 | 100.3201 | [6 empty] | CATEGORYB | SINGLE | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 0 | 532872 | EMCPHER6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | WICHITA - RENO 345KV | Build 345kV from Wichita to Reno Co | 1383 | 1468 | 1383 | 1468 | 40 | 54 | 6 | Y | 0.0014 | 0.01998 | 0.32792 |  | 42000000 | 2005-09-09 | [23 empty] | 2008-04-01 | 2008-12-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81T371208AP | FROM->TO |  | NORTH AMERICAN PHILIPS JUNCTION (SOUTH) - WEST MCPHERSON 115KV CKT 1 | PL | WERE | WERE | WEST | WEST | 0 | 533374 | SPHILPJ3 115.00 | 533438 | WMCPHER3 115.00 | 0 |  | 1 | 08AP | 68 | 68 |  | -999 | 100.3201 | [6 empty] | CATEGORYB | SINGLE | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 0 | 532872 | EMCPHER6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | WICHITA - RENO 345KV | Build 345kV from Wichita to Reno Co | 1383 | 1468 | 1383 | 1468 | 40 | 54 | 6 | Y | 0.0014 | 0.01998 | 0.32792 |  | 42000000 | 2005-09-09 | [23 empty] | 2008-04-01 | 2008-12-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81T341408AP | FROM->TO |  | TECUMSEH HILL - WILLIAMS BROTHERS PIPELINE 161KV CKT 1 | PL | WERE | WERE | NEAST | NEAST | 0 | 532920 | TECHILL5 161.00 | 532921 | WM BROS5 161.00 | 0 |  | 1 | 08AP | 84 | 84 |  | 96.5127 | 101.6266 | [6 empty] | CATEGORYB | SINGLE | LANG - WICHITA 345KV CKT 1 | 0 | 532769 | LANG 7 345.00 | 532796 | WICHITA7 345.00 | 0 |  | 1 |  |  |  |  | WERE | WICHITA - RENO 345KV | Build 345kV from Wichita to Reno Co | 1383 | 1468 | 1383 | 1468 | 40 | 54 | 6 | Y | 0.0014 | 0.01998 | 0.32792 |  | 42000000 | 2005-09-09 | [23 empty] | 2008-04-01 | 2008-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T603208FA | FROM->TO |  | NORTH AMERICAN PHILIPS - NORTH AMERICAN PHILIPS JUNCTION (SOUTH) 115KV CKT 1 | PL | WERE | WERE | WEST | WEST | 0 | 533372 | PHILIPS3 115.00 | 533374 | SPHILPJ3 115.00 | 0 |  | 1 | 08FA | 160 | 160 | 104.8 | 119.5872 | 104.4798 | [6 empty] | CATEGORYB | SINGLE | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 0 | 532872 | EMCPHER6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | WICHITA - RENO 345KV | Build 345kV from Wichita to Reno Co | 1383 | 1468 | 1383 | 1468 | 40 | 54 | 6 | Y | 0.0014 | 0.01998 | 0.32792 |  | 42000000 | 2005-09-09 | [23 empty] | 2008-04-01 | 2008-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T603208FA | FROM->TO |  | NORTH AMERICAN PHILIPS - NORTH AMERICAN PHILIPS JUNCTION (SOUTH) 115KV CKT 1 | PL | WERE | WERE | WEST | WEST | 0 | 533372 | PHILIPS3 115.00 | 533374 | SPHILPJ3 115.00 | 0 |  | 1 | 08FA | 160 | 160 | 104.8 | 119.5872 | 104.4798 | [6 empty] | CATEGORYB | SINGLE | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 0 | 532872 | EMCPHER6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | WICHITA - RENO 345KV | Build 345kV from Wichita to Reno Co | 1383 | 1468 | 1383 | 1468 | 40 | 54 | 6 | Y | 0.0014 | 0.01998 | 0.32792 |  | 42000000 | 2005-09-09 | [23 empty] | 2008-04-01 | 2008-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T613208FA | FROM->TO |  | NORTH AMERICAN PHILIPS JUNCTION (SOUTH) - WEST MCPHERSON 115KV CKT 1 | PL | WERE | WERE | WEST | WEST | 0 | 533374 | SPHILPJ3 115.00 | 533438 | WMCPHER3 115.00 | 0 |  | 1 | 08FA | 68 | 68 | 113.2 | 129.0865 | 112.7855 | [6 empty] | CATEGORYB | SINGLE | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 0 | 532872 | EMCPHER6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | WICHITA - RENO 345KV | Build 345kV from Wichita to Reno Co | 1383 | 1468 | 1383 | 1468 | 40 | 54 | 6 | Y | 0.0014 | 0.01998 | 0.32792 |  | 42000000 | 2005-09-09 | [23 empty] | 2008-04-01 | 2008-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T613208FA | FROM->TO |  | NORTH AMERICAN PHILIPS JUNCTION (SOUTH) - WEST MCPHERSON 115KV CKT 1 | PL | WERE | WERE | WEST | WEST | 0 | 533374 | SPHILPJ3 115.00 | 533438 | WMCPHER3 115.00 | 0 |  | 1 | 08FA | 68 | 68 | 113.2 | 129.0865 | 112.7855 | [6 empty] | CATEGORYB | SINGLE | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 0 | 532872 | EMCPHER6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | WICHITA - RENO 345KV | Build 345kV from Wichita to Reno Co | 1383 | 1468 | 1383 | 1468 | 40 | 54 | 6 | Y | 0.0014 | 0.01998 | 0.32792 |  | 42000000 | 2005-09-09 | [23 empty] | 2008-04-01 | 2008-12-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Iteration limit exceeded | FNSL | FDNS-Iteration limit exceeded | 1 | 2 | 2008-12-01 | 2007AG1AFS82T21208G | FROM->TO |  | NORTH AMERICAN PHILIPS JUNCTION (SOUTH) - WEST MCPHERSON 115KV CKT 1 | PL | WERE | WERE | WEST | WEST | 0 | 533374 | SPHILPJ3 115.00 | 533438 | WMCPHER3 115.00 | 0 |  | 1 | 08G | 68 | 68 | 100.8 | 104.4363 | 106.2095 | [6 empty] | CATEGORYB | SINGLE | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 0 | 532872 | EMCPHER6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | WICHITA - RENO 345KV | Build 345kV from Wichita to Reno Co | 1383 | 1468 | 1383 | 1468 | 40 | 54 | 6 | Y | 0.0014 | 0.01998 | 0.32792 |  | 42000000 | 2005-09-09 | [23 empty] | 2008-04-01 | 2008-12-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Iteration limit exceeded | FNSL | FDNS-Iteration limit exceeded | 1 | 2 | 2008-12-01 | 2007AG1AFS82T21208G | FROM->TO |  | NORTH AMERICAN PHILIPS JUNCTION (SOUTH) - WEST MCPHERSON 115KV CKT 1 | PL | WERE | WERE | WEST | WEST | 0 | 533374 | SPHILPJ3 115.00 | 533438 | WMCPHER3 115.00 | 0 |  | 1 | 08G | 68 | 68 | 100.8 | 104.4363 | 106.2095 | [6 empty] | CATEGORYB | SINGLE | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 0 | 532872 | EMCPHER6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | WICHITA - RENO 345KV | Build 345kV from Wichita to Reno Co | 1383 | 1468 | 1383 | 1468 | 40 | 54 | 6 | Y | 0.0014 | 0.01998 | 0.32792 |  | 42000000 | 2005-09-09 | [23 empty] | 2008-04-01 | 2008-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T912208SH | FROM->TO |  | NORTH AMERICAN PHILIPS - NORTH AMERICAN PHILIPS JUNCTION (SOUTH) 115KV CKT 1 | PL | WERE | WERE | WEST | WEST | 0 | 533372 | PHILIPS3 115.00 | 533374 | SPHILPJ3 115.00 | 0 |  | 1 | 08SH | 160 | 160 | 107.8 | 112.9768 | 117.9181 | [6 empty] | CATEGORYB | SINGLE | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 0 | 532872 | EMCPHER6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | WICHITA - RENO 345KV | Build 345kV from Wichita to Reno Co | 1383 | 1468 | 1383 | 1468 | 40 | 54 | 6 | Y | 0.0014 | 0.01998 | 0.32792 |  | 42000000 | 2005-09-09 | [23 empty] | 2008-04-01 | 2008-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T912208SH | FROM->TO |  | NORTH AMERICAN PHILIPS - NORTH AMERICAN PHILIPS JUNCTION (SOUTH) 115KV CKT 1 | PL | WERE | WERE | WEST | WEST | 0 | 533372 | PHILIPS3 115.00 | 533374 | SPHILPJ3 115.00 | 0 |  | 1 | 08SH | 160 | 160 | 107.8 | 112.9768 | 117.9181 | [6 empty] | CATEGORYB | SINGLE | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 0 | 532872 | EMCPHER6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | WICHITA - RENO 345KV | Build 345kV from Wichita to Reno Co | 1383 | 1468 | 1383 | 1468 | 40 | 54 | 6 | Y | 0.0014 | 0.01998 | 0.32792 |  | 42000000 | 2005-09-09 | [23 empty] | 2008-04-01 | 2008-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T922208SH | FROM->TO |  | NORTH AMERICAN PHILIPS JUNCTION (SOUTH) - WEST MCPHERSON 115KV CKT 1 | PL | WERE | WERE | WEST | WEST | 0 | 533374 | SPHILPJ3 115.00 | 533438 | WMCPHER3 115.00 | 0 |  | 1 | 08SH | 68 | 68 | 116.3 | 121.951 | 127.2859 | [6 empty] | CATEGORYB | SINGLE | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 0 | 532872 | EMCPHER6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | WICHITA - RENO 345KV | Build 345kV from Wichita to Reno Co | 1383 | 1468 | 1383 | 1468 | 40 | 54 | 6 | Y | 0.0014 | 0.01998 | 0.32792 |  | 42000000 | 2005-09-09 | [23 empty] | 2008-04-01 | 2008-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T922208SH | FROM->TO |  | NORTH AMERICAN PHILIPS JUNCTION (SOUTH) - WEST MCPHERSON 115KV CKT 1 | PL | WERE | WERE | WEST | WEST | 0 | 533374 | SPHILPJ3 115.00 | 533438 | WMCPHER3 115.00 | 0 |  | 1 | 08SH | 68 | 68 | 116.3 | 121.951 | 127.2859 | [6 empty] | CATEGORYB | SINGLE | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 0 | 532872 | EMCPHER6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | WICHITA - RENO 345KV | Build 345kV from Wichita to Reno Co | 1383 | 1468 | 1383 | 1468 | 40 | 54 | 6 | Y | 0.0014 | 0.01998 | 0.32792 |  | 42000000 | 2005-09-09 | [23 empty] | 2008-04-01 | 2008-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T932208SH | FROM->TO |  | NORTH AMERICAN PHILIPS JUNCTION (SOUTH) - WEST MCPHERSON 115KV CKT 2 | PL | WERE | WERE | WEST | WEST | 0 | 533374 | SPHILPJ3 115.00 | 533438 | WMCPHER3 115.00 | 0 |  | 2 | 08SH | 92 | 92 | 101.5 | 106.405 | 111.0538 | [6 empty] | CATEGORYB | SINGLE | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 0 | 532872 | EMCPHER6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | WICHITA - RENO 345KV | Build 345kV from Wichita to Reno Co | 1383 | 1468 | 1383 | 1468 | 40 | 54 | 6 | Y | 0.0014 | 0.01998 | 0.32792 |  | 42000000 | 2005-09-09 | [23 empty] | 2008-04-01 | 2008-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T932208SH | FROM->TO |  | NORTH AMERICAN PHILIPS JUNCTION (SOUTH) - WEST MCPHERSON 115KV CKT 2 | PL | WERE | WERE | WEST | WEST | 0 | 533374 | SPHILPJ3 115.00 | 533438 | WMCPHER3 115.00 | 0 |  | 2 | 08SH | 92 | 92 | 101.5 | 106.405 | 111.0538 | [6 empty] | CATEGORYB | SINGLE | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 0 | 532872 | EMCPHER6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | WICHITA - RENO 345KV | Build 345kV from Wichita to Reno Co | 1383 | 1468 | 1383 | 1468 | 40 | 54 | 6 | Y | 0.0014 | 0.01998 | 0.32792 |  | 42000000 | 2005-09-09 | [23 empty] | 2008-04-01 | 2008-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T653208WP | FROM->TO |  | NORTH AMERICAN PHILIPS - NORTH AMERICAN PHILIPS JUNCTION (SOUTH) 115KV CKT 1 | PL | WERE | WERE | WEST | WEST | 0 | 533372 | PHILIPS3 115.00 | 533374 | SPHILPJ3 115.00 | 0 |  | 1 | 08WP | 160 | 160 | 110.2 | 104.5969 | 105.2551 | [6 empty] | CATEGORYB | SINGLE | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 0 | 532872 | EMCPHER6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | WICHITA - RENO 345KV | Build 345kV from Wichita to Reno Co | 1383 | 1468 | 1383 | 1468 | 40 | 54 | 6 | Y | 0.0014 | 0.01998 | 0.32792 |  | 42000000 | 2005-09-09 | [23 empty] | 2008-04-01 | 2008-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T653208WP | FROM->TO |  | NORTH AMERICAN PHILIPS - NORTH AMERICAN PHILIPS JUNCTION (SOUTH) 115KV CKT 1 | PL | WERE | WERE | WEST | WEST | 0 | 533372 | PHILIPS3 115.00 | 533374 | SPHILPJ3 115.00 | 0 |  | 1 | 08WP | 160 | 160 | 110.2 | 104.5969 | 105.2551 | [6 empty] | CATEGORYB | SINGLE | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 0 | 532872 | EMCPHER6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | WICHITA - RENO 345KV | Build 345kV from Wichita to Reno Co | 1383 | 1468 | 1383 | 1468 | 40 | 54 | 6 | Y | 0.0014 | 0.01998 | 0.32792 |  | 42000000 | 2005-09-09 | [23 empty] | 2008-04-01 | 2008-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T663208WP | FROM->TO |  | NORTH AMERICAN PHILIPS JUNCTION (SOUTH) - WEST MCPHERSON 115KV CKT 1 | PL | WERE | WERE | WEST | WEST | 0 | 533374 | SPHILPJ3 115.00 | 533438 | WMCPHER3 115.00 | 0 |  | 1 | 08WP | 68 | 68 | 119.0 | 112.9156 | 113.6227 | [6 empty] | CATEGORYB | SINGLE | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 0 | 532872 | EMCPHER6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | WICHITA - RENO 345KV | Build 345kV from Wichita to Reno Co | 1383 | 1468 | 1383 | 1468 | 40 | 54 | 6 | Y | 0.0014 | 0.01998 | 0.32792 |  | 42000000 | 2005-09-09 | [23 empty] | 2008-04-01 | 2008-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T663208WP | FROM->TO |  | NORTH AMERICAN PHILIPS JUNCTION (SOUTH) - WEST MCPHERSON 115KV CKT 1 | PL | WERE | WERE | WEST | WEST | 0 | 533374 | SPHILPJ3 115.00 | 533438 | WMCPHER3 115.00 | 0 |  | 1 | 08WP | 68 | 68 | 119.0 | 112.9156 | 113.6227 | [6 empty] | CATEGORYB | SINGLE | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 0 | 532872 | EMCPHER6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 |  |  |  |  | WERE | WICHITA - RENO 345KV | Build 345kV from Wichita to Reno Co | 1383 | 1468 | 1383 | 1468 | 40 | 54 | 6 | Y | 0.0014 | 0.01998 | 0.32792 |  | 42000000 | 2005-09-09 | [23 empty] | 2008-04-01 | 2008-12-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T1971108AP | TO->FROM |  | FRONT STREET - SLIDELL 230KV CKT 1 | S | ENTR | CELE | EES-ASNO | CLE_EAST | 0 | 98492 | 6SLIDEL 230.00 | 500360 | FRONTST6 230.00 | 0 |  | 1 | 08AP | 641 | 641 |  | 99.5329 | 100.5402 | [6 empty] | CATEGORYB | SINGLE | 8DANIEL 500.00 - MCKNIGHT 500KV CKT 1 | 0 | 98235 | 8MCKNT 500.00 | 15021 | 8DANIEL 500.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2008-04-01 | 2008-04-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T1995508AP | TO->FROM |  | WATERFORD - WILLOW GLEN 500KV CKT 1 | S | ENTR | ENTR | EES-GSLA | EES-ASNO | 0 | 98246 | 8WGLEN 500.00 | 98539 | 8WATERFO 500.00 | 0 |  | 1 | 08AP | 1200 | 1200 | 105.8 | 105.9566 | 106.0744 | [6 empty] | CATEGORYB | GENOUT | GEN 98538 1-WATERFORD UNIT#3 | 0 | 0 |  | 0 |  | 0 |  |  | ASSIGN | [43 empty] | 2008-04-01 | 2008-04-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T2005508AP | FROM->TO |  | WATERFORD 500/230KV TRANSFORMER CKT 1 | S | ENTR | ENTR | EES-ASNO | EES-ASNO | 0 | 98539 | 8WATERFO 500.00 | 98537 | 6WATFRD 230.00 | 0 |  | 1 | 08AP | 1200 | 1200 | 102.7 | 102.9296 | 103.1321 | [6 empty] | CATEGORYB | GENOUT | GEN 98538 1-WATERFORD UNIT#3 | 0 | 0 |  | 0 |  | 0 |  |  | ASSIGN | [43 empty] | 2008-04-01 | 2008-04-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81T871108G | FROM->TO |  | ADAMS CREEK - BOGALUSA 230KV CKT 2 | S | ENTR | ENTR | EES-ASNO | EES-ASNO | 0 | 98497 | 6ADMSCRK 230.00 | 98488 | 6BOGALUS 230.00 | 0 |  | 2 | 08G | 637 | 637 | 100.0 | 99.9973 | 102.0142 | [6 empty] | CATEGORYB | SINGLE | ADAMS CREEK - BOGALUSA 230KV CKT 1 | 0 | 98488 | 6BOGALUS 230.00 | 98497 | 6ADMSCRK 230.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2008-04-01 | 2008-04-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T4075508G | TO->FROM |  | WATERFORD - WILLOW GLEN 500KV CKT 1 | S | ENTR | ENTR | EES-GSLA | EES-ASNO | 0 | 98246 | 8WGLEN 500.00 | 98539 | 8WATERFO 500.00 | 0 |  | 1 | 08G | 1200 | 1200 |  | 98.9842 | 100.7101 | [6 empty] | CATEGORYB | GENOUT | GEN 98538 1-WATERFORD UNIT#3 | 0 | 0 |  | 0 |  | 0 |  |  | ASSIGN | [43 empty] | 2008-04-01 | 2008-04-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T715508WP | TO->FROM |  | 6VIGNES 230.00 - COLY 230KV CKT 1 | S | ENTR | LAGN | EES-GSLA | LAGN | 0 | 98391 | 6COLY 2 230.00 | 97331 | 6VIGNES 230.00 | 0 |  | 1 | 08WP | 462 | 462 | 103.4 | 103.4087 | 104.4133 | [6 empty] | CATEGORYB | SINGLE | 6STGABTP 230.00 - WILLOW GLEN 230KV CKT 1 | 0 | 98247 | 6WGLEN 230.00 | 98438 | 6STGABTP 230.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2008-12-01 | 2008-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T755508WP | TO->FROM |  | 6VIGNES 230.00 - COLY 230KV CKT 1 | S | ENTR | LAGN | EES-GSLA | LAGN | 0 | 98391 | 6COLY 2 230.00 | 97331 | 6VIGNES 230.00 | 0 |  | 1 | 08WP | 462 | 462 | 101.4 | 101.4193 | 102.4249 | [6 empty] | CATEGORYB | SINGLE | AAC CORP - POLSCAR 230KV CKT 1 | 0 | 98249 | 6A.A.C. 230.00 | 98434 | 6POLSCAR 230.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2008-12-01 | 2008-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81T825508WP | TO->FROM |  | 6VIGNES 230.00 - COLY 230KV CKT 1 | S | ENTR | LAGN | EES-GSLA | LAGN | 0 | 98391 | 6COLY 2 230.00 | 97331 | 6VIGNES 230.00 | 0 |  | 1 | 08WP | 462 | 462 | 101.4 | 101.4183 | 102.424 | [6 empty] | CATEGORYB | SINGLE | 6STGABTP 230.00 - POLSCAR 230KV CKT 1 | 0 | 98434 | 6POLSCAR 230.00 | 98438 | 6STGABTP 230.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2008-12-01 | 2008-12-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 1 | 2008-12-01 | 2007AG1AFS81T3323109SP | TO->FROM |  | 3CLEVND 115.00 - DELTA SES 115KV CKT 1 | S | ENTR | ENTR | EES-MISS | EES-MISS | 0 | 98737 | 3DELTA 115.00 | 98726 | 3CLEVND 115.00 | 0 |  | 1 | 09SP | 120 | 120 |  | 91.7995 | 102.1751 | [6 empty] | CATEGORYB | SINGLE | INDIANOLA 230/115KV TRANSFORMER CKT 1 | 0 | 98769 | 6INDOLA 230.00 | 98770 | 3INDIAN 115.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81T4233209SP | TO->FROM |  | 3SARDIS 115.00 - BATESVILLE 115KV CKT 1 | S | ENTR | ENTR | EES-MISS | EES-MISS | 0 | 98730 | 3BATESV 115.00 | 98716 | 3SARDIS 115.00 | 0 |  | 1 | 09SP | 160 | 160 |  | 98.0799 | 103.4019 | [6 empty] | CATEGORYB | SINGLE | FREEPORT - HORN LAKE 230KV CKT 1 | 0 | 98701 | 6HN LAK 230.00 | 98707 | 6FRPORT 230.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T9372209SP | TO->FROM |  | 5BEE BR - QUITMAN 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99519 | 5QUITMN 161.00 | 99799 | 5BEE BR 161.00 | 0 |  | 1 | 09SP | 167 | 167 |  | 98.5498 | 107.1074 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T7832209SP | TO->FROM |  | 5BEE BR - QUITMAN 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99519 | 5QUITMN 161.00 | 99799 | 5BEE BR 161.00 | 0 |  | 1 | 09SP | 167 | 167 |  | 92.2722 | 100.3835 | [6 empty] | CATEGORYB | SINGLE | 5HILLTOP 161.00 - DARDANELLE 161KV CKT 1 | 0 | 505508 | DARDANE5 161.00 | 99679 | 5HILLTOP 161.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T9342209SP | FROM->TO |  | ARKANSAS NUCLEAR ONE 161 - RUSSELLVILLE NORTH 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99487 | 5ANO 16 161.00 | 99492 | 5RUSL-N 161.00 | 0 |  | 1 | 09SP | 396 | 396 | 114.7 | 114.7925 | 119.4664 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T6532209SP | TO->FROM | Bidirectional | CALICO ROCK - MELBOURNE 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99824 | 5MELBRN 161.00 | 99803 | 5CALCR 161.00 | 0 |  | 1 | 09SP | 148 | 148 | 113.6 | 113.1181 | 120.5765 | [6 empty] | CATEGORYB | SINGLE | DELL - INDEPENDENCE 500KV CKT 1 | 0 | 99742 | 8DELL 5 500.00 | 99818 | 8ISES 5 500.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T9382209SP | TO->FROM | Bidirectional | CALICO ROCK - MELBOURNE 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99824 | 5MELBRN 161.00 | 99803 | 5CALCR 161.00 | 0 |  | 1 | 09SP | 148 | 148 | 107.2 | 106.6017 | 115.1577 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T16392209SP | TO->FROM | Bidirectional | CALICO ROCK - MELBOURNE 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99824 | 5MELBRN 161.00 | 99803 | 5CALCR 161.00 | 0 |  | 1 | 09SP | 148 | 148 | 105.3 | 104.5592 | 112.0031 | [6 empty] | CATEGORYB | GENOUT | GEN532751 1-WOLF CREEK GENERATING STATION UNIT 1 | 0 | 0 |  | 0 |  | 0 |  |  | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T6542209SP | TO->FROM |  | MELBOURNE - SAGE SS 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99834 | 5SAGE * 161.00 | 99824 | 5MELBRN 161.00 | 0 |  | 1 | 09SP | 148 | 148 | 118.7 | 118.2494 | 125.763 | [6 empty] | CATEGORYB | SINGLE | DELL - INDEPENDENCE 500KV CKT 1 | 0 | 99742 | 8DELL 5 500.00 | 99818 | 8ISES 5 500.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T9402209SP | TO->FROM |  | MELBOURNE - SAGE SS 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99834 | 5SAGE * 161.00 | 99824 | 5MELBRN 161.00 | 0 |  | 1 | 09SP | 148 | 148 | 112.4 | 111.8195 | 120.456 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T16412209SP | TO->FROM |  | MELBOURNE - SAGE SS 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99834 | 5SAGE * 161.00 | 99824 | 5MELBRN 161.00 | 0 |  | 1 | 09SP | 148 | 148 | 110.5 | 109.7401 | 117.2534 | [6 empty] | CATEGORYB | GENOUT | GEN532751 1-WOLF CREEK GENERATING STATION UNIT 1 | 0 | 0 |  | 0 |  | 0 |  |  | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T4672209SP | FROM->TO |  | MEPS CLARKESDALE 230/115KV TRANSFORMER CKT 1 | S | ENTR | ENTR | EES-MISS | EES-MISS | 0 | 98854 | 6MEPSCLK 230.00 | 98723 | 3CLARKD 115.00 | 0 |  | 1 | 09SP | 250 | 250 |  | 3.425 | 122.0914 | [6 empty] | CATEGORYB | SINGLE | MEPS CLARKESDALE - RITCHIE BATESVILLE TAP 230KV CKT 1 | 0 | 98854 | 6MEPSCLK 230.00 | 99680 | 6MOONLAK 230.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T9362209SP | TO->FROM |  | RUSSELLVILLE EAST - RUSSELLVILLE NORTH 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99492 | 5RUSL-N 161.00 | 99490 | 5RUSL-E 161.00 | 0 |  | 1 | 09SP | 396 | 396 | 106.6 | 106.7616 | 111.361 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T5742209WP | TO->FROM |  | 5BEE BR - QUITMAN 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99519 | 5QUITMN 161.00 | 99799 | 5BEE BR 161.00 | 0 |  | 1 | 09WP | 167 | 167 | 100.5 | 99.8747 | 108.3742 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T4512209WP | TO->FROM |  | 5BEE BR - QUITMAN 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99519 | 5QUITMN 161.00 | 99799 | 5BEE BR 161.00 | 0 |  | 1 | 09WP | 167 | 167 |  | 95.7199 | 103.6965 | [6 empty] | CATEGORYB | SINGLE | 5HILLTOP 161.00 - DARDANELLE 161KV CKT 1 | 0 | 505508 | DARDANE5 161.00 | 99679 | 5HILLTOP 161.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T5722209WP | FROM->TO |  | ARKANSAS NUCLEAR ONE 161 - RUSSELLVILLE NORTH 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99487 | 5ANO 16 161.00 | 99492 | 5RUSL-N 161.00 | 0 |  | 1 | 09WP | 396 | 396 |  | 99.817 | 104.2093 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T3062209WP | TO->FROM | Bidirectional | CALICO ROCK - MELBOURNE 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99824 | 5MELBRN 161.00 | 99803 | 5CALCR 161.00 | 0 |  | 1 | 09WP | 148 | 148 | 118.0 | 117.5643 | 124.8428 | [6 empty] | CATEGORYB | SINGLE | DELL - INDEPENDENCE 500KV CKT 1 | 0 | 99742 | 8DELL 5 500.00 | 99818 | 8ISES 5 500.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T5752209WP | TO->FROM | Bidirectional | CALICO ROCK - MELBOURNE 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99824 | 5MELBRN 161.00 | 99803 | 5CALCR 161.00 | 0 |  | 1 | 09WP | 148 | 148 | 110.7 | 110.324 | 118.5975 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T11042209WP | TO->FROM | Bidirectional | CALICO ROCK - MELBOURNE 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99824 | 5MELBRN 161.00 | 99803 | 5CALCR 161.00 | 0 |  | 1 | 09WP | 148 | 148 | 107.6 | 109.3596 | 116.7496 | [6 empty] | CATEGORYB | GENOUT | GEN532751 1-WOLF CREEK GENERATING STATION UNIT 1 | 0 | 0 |  | 0 |  | 0 |  |  | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T3072209WP | TO->FROM |  | MELBOURNE - SAGE SS 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99834 | 5SAGE * 161.00 | 99824 | 5MELBRN 161.00 | 0 |  | 1 | 09WP | 148 | 148 | 121.9 | 121.495 | 128.8161 | [6 empty] | CATEGORYB | SINGLE | DELL - INDEPENDENCE 500KV CKT 1 | 0 | 99742 | 8DELL 5 500.00 | 99818 | 8ISES 5 500.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T5772209WP | TO->FROM |  | MELBOURNE - SAGE SS 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99834 | 5SAGE * 161.00 | 99824 | 5MELBRN 161.00 | 0 |  | 1 | 09WP | 148 | 148 | 114.7 | 114.3022 | 122.6307 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T11062209WP | TO->FROM |  | MELBOURNE - SAGE SS 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99834 | 5SAGE * 161.00 | 99824 | 5MELBRN 161.00 | 0 |  | 1 | 09WP | 148 | 148 | 111.6 | 113.3246 | 120.7635 | [6 empty] | CATEGORYB | GENOUT | GEN532751 1-WOLF CREEK GENERATING STATION UNIT 1 | 0 | 0 |  | 0 |  | 0 |  |  | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T2372209WP | FROM->TO |  | MEPS CLARKESDALE 230/115KV TRANSFORMER CKT 1 | S | ENTR | ENTR | EES-MISS | EES-MISS | 0 | 98854 | 6MEPSCLK 230.00 | 98723 | 3CLARKD 115.00 | 0 |  | 1 | 09WP | 250 | 250 |  | 0.00039496 | 121.9652 | [6 empty] | CATEGORYB | SINGLE | MEPS CLARKESDALE - RITCHIE BATESVILLE TAP 230KV CKT 1 | 0 | 98854 | 6MEPSCLK 230.00 | 99680 | 6MOONLAK 230.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T13472212SP | TO->FROM |  | 5BEE BR - QUITMAN 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99519 | 5QUITMN 161.00 | 99799 | 5BEE BR 161.00 | 0 |  | 1 | 12SP | 167 | 167 |  | 100.0302 | 109.6875 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T11672212SP | TO->FROM |  | 5BEE BR - QUITMAN 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99519 | 5QUITMN 161.00 | 99799 | 5BEE BR 161.00 | 0 |  | 1 | 12SP | 167 | 167 |  | 92.6282 | 101.3445 | [6 empty] | CATEGORYB | SINGLE | 5HILLTOP 161.00 - DARDANELLE 161KV CKT 1 | 0 | 505508 | DARDANE5 161.00 | 99679 | 5HILLTOP 161.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T13492212SP | FROM->TO |  | 5CLINTN - CLINTON WEST (AECC) 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99807 | 5CLINTON 161.00 | 99806 | 5CLIN-W# 161.00 | 0 |  | 1 | 12SP | 167 | 167 |  | 91.1379 | 100.5796 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T13442212SP | FROM->TO |  | ARKANSAS NUCLEAR ONE 161 - RUSSELLVILLE NORTH 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99487 | 5ANO 16 161.00 | 99492 | 5RUSL-N 161.00 | 0 |  | 1 | 12SP | 396 | 396 | 122.4 | 123.0226 | 128.9964 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T9912212SP | TO->FROM | Bidirectional | CALICO ROCK - MELBOURNE 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99824 | 5MELBRN 161.00 | 99803 | 5CALCR 161.00 | 0 |  | 1 | 12SP | 148 | 148 | 110.0 | 110.4767 | 117.6361 | [6 empty] | CATEGORYB | SINGLE | DELL - INDEPENDENCE 500KV CKT 1 | 0 | 99742 | 8DELL 5 500.00 | 99818 | 8ISES 5 500.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T13482212SP | TO->FROM | Bidirectional | CALICO ROCK - MELBOURNE 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99824 | 5MELBRN 161.00 | 99803 | 5CALCR 161.00 | 0 |  | 1 | 12SP | 148 | 148 | 107.9 | 108.457 | 116.9555 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T23562212SP | TO->FROM | Bidirectional | CALICO ROCK - MELBOURNE 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99824 | 5MELBRN 161.00 | 99803 | 5CALCR 161.00 | 0 |  | 1 | 12SP | 148 | 148 | 104.4 | 104.9325 | 112.1714 | [6 empty] | CATEGORYB | GENOUT | GEN532751 1-WOLF CREEK GENERATING STATION UNIT 1 | 0 | 0 |  | 0 |  | 0 |  |  | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T9932212SP | TO->FROM |  | MELBOURNE - SAGE SS 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99834 | 5SAGE * 161.00 | 99824 | 5MELBRN 161.00 | 0 |  | 1 | 12SP | 148 | 148 | 115.4 | 115.8581 | 123.1169 | [6 empty] | CATEGORYB | SINGLE | DELL - INDEPENDENCE 500KV CKT 1 | 0 | 99742 | 8DELL 5 500.00 | 99818 | 8ISES 5 500.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T13512212SP | TO->FROM |  | MELBOURNE - SAGE SS 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99834 | 5SAGE * 161.00 | 99824 | 5MELBRN 161.00 | 0 |  | 1 | 12SP | 148 | 148 | 113.4 | 113.985 | 122.6408 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T23582212SP | TO->FROM |  | MELBOURNE - SAGE SS 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99834 | 5SAGE * 161.00 | 99824 | 5MELBRN 161.00 | 0 |  | 1 | 12SP | 148 | 148 | 109.9 | 110.3892 | 117.7601 | [6 empty] | CATEGORYB | GENOUT | GEN532751 1-WOLF CREEK GENERATING STATION UNIT 1 | 0 | 0 |  | 0 |  | 0 |  |  | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T6942412SP | FROM->TO |  | MEPS CLARKESDALE 230/115KV TRANSFORMER CKT 1 | S | ENTR | ENTR | EES-MISS | EES-MISS | 0 | 98854 | 6MEPSCLK 230.00 | 98723 | 3CLARKD 115.00 | 0 |  | 1 | 12SP | 250 | 250 |  | 7.7868 | 120.3097 | [6 empty] | CATEGORYB | SINGLE | MEPS CLARKESDALE - RITCHIE BATESVILLE TAP 230KV CKT 1 | 0 | 98854 | 6MEPSCLK 230.00 | 99680 | 6MOONLAK 230.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T13462212SP | TO->FROM |  | RUSSELLVILLE EAST - RUSSELLVILLE NORTH 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99492 | 5RUSL-N 161.00 | 99490 | 5RUSL-E 161.00 | 0 |  | 1 | 12SP | 396 | 396 | 113.3 | 113.9271 | 119.735 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T7392212WP | TO->FROM |  | 5BEE BR - QUITMAN 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99519 | 5QUITMN 161.00 | 99799 | 5BEE BR 161.00 | 0 |  | 1 | 12WP | 167 | 167 | 100.4 | 98.3517 | 107.7161 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T6152212WP | TO->FROM |  | 5BEE BR - QUITMAN 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99519 | 5QUITMN 161.00 | 99799 | 5BEE BR 161.00 | 0 |  | 1 | 12WP | 167 | 167 |  | 95.6165 | 103.9531 | [6 empty] | CATEGORYB | SINGLE | 5HILLTOP 161.00 - DARDANELLE 161KV CKT 1 | 0 | 505508 | DARDANE5 161.00 | 99679 | 5HILLTOP 161.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T7362212WP | FROM->TO |  | ARKANSAS NUCLEAR ONE 161 - RUSSELLVILLE NORTH 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99487 | 5ANO 16 161.00 | 99492 | 5RUSL-N 161.00 | 0 |  | 1 | 12WP | 396 | 396 | 104.2 | 103.2162 | 108.6271 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T4652212WP | TO->FROM | Bidirectional | CALICO ROCK - MELBOURNE 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99824 | 5MELBRN 161.00 | 99803 | 5CALCR 161.00 | 0 |  | 1 | 12WP | 148 | 148 | 113.6 | 113.3234 | 120.3455 | [6 empty] | CATEGORYB | SINGLE | DELL - INDEPENDENCE 500KV CKT 1 | 0 | 99742 | 8DELL 5 500.00 | 99818 | 8ISES 5 500.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T7402212WP | TO->FROM | Bidirectional | CALICO ROCK - MELBOURNE 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99824 | 5MELBRN 161.00 | 99803 | 5CALCR 161.00 | 0 |  | 1 | 12WP | 148 | 148 | 107.0 | 105.9941 | 114.257 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T3372212WP | TO->FROM | Bidirectional | CALICO ROCK - MELBOURNE 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99824 | 5MELBRN 161.00 | 99803 | 5CALCR 161.00 | 0 |  | 1 | 12WP | 148 | 148 | 103.3 | 102.2856 | 109.8789 | [6 empty] | CATEGORYB | SINGLE | WHITEWATER EAST - WILHELMINA 345KV CKT 1 | 0 | 96051 | 7WILHLM 345.00 | 96054 | 7GOBKNO 345.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T4672212WP | TO->FROM |  | MELBOURNE - SAGE SS 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99834 | 5SAGE * 161.00 | 99824 | 5MELBRN 161.00 | 0 |  | 1 | 12WP | 148 | 148 | 117.8 | 117.4381 | 124.5169 | [6 empty] | CATEGORYB | SINGLE | DELL - INDEPENDENCE 500KV CKT 1 | 0 | 99742 | 8DELL 5 500.00 | 99818 | 8ISES 5 500.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T7422212WP | TO->FROM |  | MELBOURNE - SAGE SS 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99834 | 5SAGE * 161.00 | 99824 | 5MELBRN 161.00 | 0 |  | 1 | 12WP | 148 | 148 | 111.2 | 110.163 | 118.5007 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T3392212WP | TO->FROM |  | MELBOURNE - SAGE SS 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99834 | 5SAGE * 161.00 | 99824 | 5MELBRN 161.00 | 0 |  | 1 | 12WP | 148 | 148 | 107.5 | 106.4389 | 114.0936 | [6 empty] | CATEGORYB | SINGLE | WHITEWATER EAST - WILHELMINA 345KV CKT 1 | 0 | 96051 | 7WILHLM 345.00 | 96054 | 7GOBKNO 345.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T3942212WP | FROM->TO |  | MEPS CLARKESDALE 230/115KV TRANSFORMER CKT 1 | S | ENTR | ENTR | EES-MISS | EES-MISS | 0 | 98854 | 6MEPSCLK 230.00 | 98723 | 3CLARKD 115.00 | 0 |  | 1 | 12WP | 250 | 250 |  | 2.36e-06 | 120.4723 | [6 empty] | CATEGORYB | SINGLE | MEPS CLARKESDALE - RITCHIE BATESVILLE TAP 230KV CKT 1 | 0 | 98854 | 6MEPSCLK 230.00 | 99680 | 6MOONLAK 230.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T7382212WP | TO->FROM |  | RUSSELLVILLE EAST - RUSSELLVILLE NORTH 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99492 | 5RUSL-N 161.00 | 99490 | 5RUSL-E 161.00 | 0 |  | 1 | 12WP | 396 | 396 |  | 96.4122 | 101.7558 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T20412217SP | TO->FROM |  | 5BEE BR - QUITMAN 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99519 | 5QUITMN 161.00 | 99799 | 5BEE BR 161.00 | 0 |  | 1 | 17SP | 167 | 167 | 104.4 | 103.5964 | 113.7359 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T17822217SP | TO->FROM |  | 5BEE BR - QUITMAN 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99519 | 5QUITMN 161.00 | 99799 | 5BEE BR 161.00 | 0 |  | 1 | 17SP | 167 | 167 |  | 94.8686 | 103.7608 | [6 empty] | CATEGORYB | SINGLE | 5HILLTOP 161.00 - DARDANELLE 161KV CKT 1 | 0 | 505508 | DARDANE5 161.00 | 99679 | 5HILLTOP 161.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T20432217SP | FROM->TO |  | 5CLINTN - CLINTON WEST (AECC) 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99807 | 5CLINTON 161.00 | 99806 | 5CLIN-W# 161.00 | 0 |  | 1 | 17SP | 167 | 167 |  | 92.328 | 102.151 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T15292417SP | TO->FROM |  | 5MORFLD - INDEPENDENCE 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99817 | 5ISES 1 161.00 | 99826 | 5MORFLD 161.00 | 0 |  | 1 | 17SP | 310 | 310 | 100.1 | 99.6833 | 103.0412 | [6 empty] | CATEGORYB | SINGLE | DELL - INDEPENDENCE 500KV CKT 1 | 0 | 99742 | 8DELL 5 500.00 | 99818 | 8ISES 5 500.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2013-06-01 | 2013-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T20452217SP | TO->FROM |  | 5MORFLD - INDEPENDENCE 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99817 | 5ISES 1 161.00 | 99826 | 5MORFLD 161.00 | 0 |  | 1 | 17SP | 310 | 310 |  | 98.0379 | 102.6231 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2013-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T20382217SP | FROM->TO |  | ARKANSAS NUCLEAR ONE 161 - RUSSELLVILLE NORTH 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99487 | 5ANO 16 161.00 | 99492 | 5RUSL-N 161.00 | 0 |  | 1 | 17SP | 396 | 396 | 130.4 | 131.2118 | 137.212 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T15282417SP | TO->FROM | Bidirectional | CALICO ROCK - MELBOURNE 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99824 | 5MELBRN 161.00 | 99803 | 5CALCR 161.00 | 0 |  | 1 | 17SP | 148 | 148 | 115.1 | 114.415 | 121.1359 | [6 empty] | CATEGORYB | SINGLE | DELL - INDEPENDENCE 500KV CKT 1 | 0 | 99742 | 8DELL 5 500.00 | 99818 | 8ISES 5 500.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T20422217SP | TO->FROM | Bidirectional | CALICO ROCK - MELBOURNE 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99824 | 5MELBRN 161.00 | 99803 | 5CALCR 161.00 | 0 |  | 1 | 17SP | 148 | 148 | 111.0 | 110.7846 | 120.055 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T32502217SP | TO->FROM | Bidirectional | CALICO ROCK - MELBOURNE 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99824 | 5MELBRN 161.00 | 99803 | 5CALCR 161.00 | 0 |  | 1 | 17SP | 148 | 148 | 106.2 | 105.1352 | 113.1903 | [6 empty] | CATEGORYB | GENOUT | GEN532751 1-WOLF CREEK GENERATING STATION UNIT 1 | 0 | 0 |  | 0 |  | 0 |  |  | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T27442417SP | TO->FROM |  | FORREST CITY NORTH SS - MOSES 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99637 | 5MOSES 161.00 | 99614 | 5FCTY-N* 161.00 | 0 |  | 1 | 17SP | 148 | 148 |  | 96.011 | 102.9132 | [6 empty] | CATEGORYB | SINGLE | WEST MEMPHIS - WEST MEMPHIS POLK AVE 161KV CKT 1 | 0 | 99787 | 5WM-EHV 161.00 | 99792 | 5WM-POK 161.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2013-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T15302417SP | TO->FROM |  | MELBOURNE - SAGE SS 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99834 | 5SAGE * 161.00 | 99824 | 5MELBRN 161.00 | 0 |  | 1 | 17SP | 148 | 148 | 120.9 | 120.0729 | 126.9306 | [6 empty] | CATEGORYB | SINGLE | DELL - INDEPENDENCE 500KV CKT 1 | 0 | 99742 | 8DELL 5 500.00 | 99818 | 8ISES 5 500.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T20462217SP | TO->FROM |  | MELBOURNE - SAGE SS 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99834 | 5SAGE * 161.00 | 99824 | 5MELBRN 161.00 | 0 |  | 1 | 17SP | 148 | 148 | 116.9 | 116.5998 | 126.0257 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T32522217SP | TO->FROM |  | MELBOURNE - SAGE SS 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99834 | 5SAGE * 161.00 | 99824 | 5MELBRN 161.00 | 0 |  | 1 | 17SP | 148 | 148 | 112.1 | 110.8495 | 119.0936 | [6 empty] | CATEGORYB | GENOUT | GEN532751 1-WOLF CREEK GENERATING STATION UNIT 1 | 0 | 0 |  | 0 |  | 0 |  |  | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81T12502417SP | FROM->TO |  | MEPS CLARKESDALE 230/115KV TRANSFORMER CKT 1 | S | ENTR | ENTR | EES-MISS | EES-MISS | 0 | 98854 | 6MEPSCLK 230.00 | 98723 | 3CLARKD 115.00 | 0 |  | 1 | 17SP | 250 | 250 |  | 8.9366 | 120.8921 | [6 empty] | CATEGORYB | SINGLE | MEPS CLARKESDALE - RITCHIE BATESVILLE TAP 230KV CKT 1 | 0 | 98854 | 6MEPSCLK 230.00 | 99680 | 6MOONLAK 230.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81T20402217SP | TO->FROM |  | RUSSELLVILLE EAST - RUSSELLVILLE NORTH 161KV CKT 1 | S | ENTR | ENTR | EES-ARK | EES-ARK | 0 | 99492 | 5RUSL-N 161.00 | 99490 | 5RUSL-E 161.00 | 0 |  | 1 | 17SP | 396 | 396 | 120.1 | 120.968 | 126.7085 | [6 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 99486 | 8ANO 50 500.00 | 0 |  | 1 | ASSIGN | [43 empty] | 2009-06-01 | 2009-06-01
GEN-2001-024 | Mattison | [8 empty] | 506957506927012SP | TO->FROM |  | DYESS - TONTITOWN 161KV CKT 1 | U | AEPW | AEPW | FAYETTEV | FAYETTEV | 0 | 506957 | TONTITN5 161.00 | 506927 | DYESS 5 161.00 | 0 |  | 1 |  | 451 | 592 |  |  | 238.5 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | AEPW | DYESS - TONTITOWN 161KV CKT 1 | Add one 161KV terminal for Tontitown | [12 empty] | 537700 | [24 empty] | 2008-06-01 | 2008-06-01
GEN-2001-024 | Mattison | [8 empty] | 506957504010012SP | TO->FROM |  | ELMSPRGS 5 161.00 - TONTITOWN 161KV CKT 1 | U | AEPW | AEPW | FAYETTEV | FAYTAECC | 0 | 506957 | TONTITN5 161.00 | 504010 | ELMSPRGS 5 161.00 | 0 |  | 1 |  | 451 | 592 |  |  | 362.25 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | AEPW | ELMSPRGS 5 161.00 - TONTITOWN 161KV CKT 1 | Add one 161KV terminal for Tontitown | [12 empty] | 537700 | [24 empty] | 2008-06-01 | 2008-06-01
GEN-2001-024 | Mattison | [8 empty] | 506957506938012SP | TO->FROM |  | LOWELL 5 - TONTITOWN 161KV CKT 1 | U | AEPW | AEPW | FAYETTEV | FAYETTEV | 0 | 506957 | TONTITN5 161.00 | 506938 | LOWELL 5 161.00 | 0 |  | 1 |  | 373 | 443 |  |  | 167.5 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | AEPW | LOWELL 5 - TONTITOWN 161KV CKT 1 | Add one 161KV terminal for Tontitown | [12 empty] | 537700 | [24 empty] | 2008-06-01 | 2008-06-01
GEN-2004-014 | Spearville2 | [8 empty] | 539695539679012SP | TO->FROM |  | MULLERGREN - SPEARVILLE 230KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539695 | SPEARVL6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 |  | 330.3 | 355.3 |  |  | 116.6 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | MULLERGREN - SPEARVILLE 230KV CKT 1 | 230kv line terminal at Spearville | [12 empty] | 650000 | [24 empty] | 2009-12-31 | 2009-12-31
GEN-2006-010 | Turk | [8 empty] | 507428507402012SP | TO->FROM |  | ASHDOWN REC (MILLWOOD) - OKAY 138KV CKT 1 | U | AEPW | AEPW | SARK | SARKAECC | 0 | 507428 | OKAY 4 138.00 | 507402 | ASHDWNR4 138.00 | 0 |  | 1 |  | 368 | 512 |  |  | 116 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | AEPW | ASHDOWN REC (MILLWOOD) - OKAY 138KV CKT 1 | Recunductor and convert line to 138 kV and replace switches at Ashdown REC | [11 empty] | 11100000 | 11100000 | [24 empty] | 2012-07-01 | 2012-07-01
GEN-2006-010 | Turk | [8 empty] | 507402507431012SP | FROM->TO |  | ASHDOWN REC (MILLWOOD) - PATTERSON 138KV CKT 1 | U | AEPW | AEPW | SARKAECC | SARK | 0 | 507402 | ASHDWNR4 138.00 | 507431 | PATTERS4 138.00 | 0 |  | 1 |  | 368 | 512 |  |  | 108.5 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | AEPW | ASHDOWN REC (MILLWOOD) - PATTERSON 138KV CKT 1 | Reconductor Line & Convert Line to 138 kV and convert Patterson station to breaker-and-a half cofiguration | [11 empty] | 6670000 | 6670000 | [24 empty] | 2012-07-01 | 2012-07-01
GEN-2006-010 | Turk | [8 empty] | 508054508075012SP | FROM->TO |  | BANN - RED SPRINGS REC 138KV CKT 1 | U | AEPW | AEPW | TEXARK | TXARNTEC | 0 | 508054 | BANN 4 138.00 | 508075 | REDSPRG4 138.00 | 0 |  | 1 |  | 224 | 261 |  |  | 72.8 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | AEPW | BANN - RED SPRINGS REC 138KV CKT 1 | Replace 138 kV breakers 3300 & 3310 | [11 empty] | 300000 | 300000 | [24 empty] | 2012-07-01 | 2012-07-01
GEN-2006-010 | Turk | [8 empty] | 504122507456012SP | FROM->TO |  | MCNAB REC - TURK 115KV CKT 1 | U | AEPW | AEPW | SARK | SARKAECC | 0 | 504122 | MCNAB 3 115.00 | 507456 | HEMPSTD3 115.00 | 0 |  | 1 |  | 150 | 174 |  |  | 47.9 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | AEPW | MCNAB REC - TURK 115KV CKT 1 | Build a new two mile, 138 kV, 1590 ACSR line section (operated at 115 kV) from Turk Substation to the existing Okay- Hope 115 kV line to form a Turk - Hope 115 kV line. | [11 empty] | 1520000 | 1520000 | [24 empty] | 2012-07-01 | 2012-07-01
GEN-2006-010 | Turk | [8 empty] | 507454507428012SP | TO->FROM |  | OKAY - TURK 138KV CKT 1 | U | AEPW | AEPW | SARK | SARK | 0 | 507454 | HEMPSTD4 138.00 | 507428 | OKAY 4 138.00 | 0 |  | 1 |  | 368 | 512 |  |  | 175.2 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | AEPW | OKAY - TURK 138KV CKT 1 | Build two mile, 138 kV, 1590ACSR line section from Turk Sub to existing Okay-Hope 115 kV line and rebuild twelve miles of 115 kV line to Okay Sub to 138 kV, 1590 ACSR , to form a Turk-Okay 138 kV line | [11 empty] | 9190000 | 9190000 | [24 empty] | 2012-07-01 | 2012-07-01
GEN-2006-010 | Turk | [8 empty] | 507454508078012SP | TO->FROM |  | SE TEXARKANA - TURK 138KV CKT 1 | U | AEPW | AEPW | SARK | TEXARK | 0 | 507454 | HEMPSTD4 138.00 | 508078 | SETEXAR4 138.00 | 0 |  | 1 |  | 368 | 512 |  |  | 125.3 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | AEPW | SE TEXARKANA - TURK 138KV CKT 1 | Build new Turk-SE Texarkana 138 kV line and add SE Texarkana 138 kV terminal. | [11 empty] | 26850000 | 26850000 | [24 empty] | 2012-07-01 | 2012-07-01
GEN-2006-010 | Turk | [8 empty] | 507454508080012SP | TO->FROM |  | SUGAR HILL - TURK 138KV CKT 1 | U | AEPW | AEPW | SARK | TEXARK | 0 | 507454 | HEMPSTD4 138.00 | 508080 | SUGARHL4 138.00 | 0 |  | 1 |  | 368 | 512 |  |  | 159.6 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | AEPW | SUGAR HILL - TURK 138KV CKT 1 | Build new Turk-Sugar Hill 138 kV line and add Sugar Hill 138 kV terminal. | [11 empty] | 19700000 | 19700000 | [24 empty] | 2012-07-01 | 2012-07-01
GEN-2006-010 | Turk | [8 empty] | 509416507454012SP | FROM->TO |  | TURK 138/24.0KV TRANSFORMER CKT 1 | U | AEPW | AEPW | SARK | SARK | 0 | 509416 | TURKCOAL 24.000 | 507454 | HEMPSTD4 138.00 | 0 |  | 1 |  | 750 | 750 |  |  | 618 | [7 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | AEPW | TURK 138/24.0KV TRANSFORMER CKT 1 | Install a GSU transformer at Turk | [11 empty] | 0 | 0 | [24 empty] | 2012-07-01 | 2012-07-01
NA | [9 empty] | NAKACP5429815429651 |  |  | LACYGNE - WEST GARDNER 345KV CKT 1 | U | KACP | KACP |  |  | 0 | 542981 | LACYGNE7 | 542965 | W.GRDNR7 | 0 |  | 1 | [27 empty] | KACP | LACYGNE - WEST GARDNER 345KV CKT 1 | KCPL Sponsored Project to Reconductor Line to be In-Service by 6/1/2006 | [37 empty] | 2006-06-01 | 2006-06-01
NA | [9 empty] | NAWERE5327735327711 |  |  | SUMMIT - RENO 345KV | U | WERE | WERE |  |  | 0 | 532773 | SUMMIT 7 345.0 | 532771 | RENO 7 345.00 |  |  | 1 | [27 empty] | WERE | SUMMIT - RENO 345KV | Install new 50.55-mile 345 kV line from Reno county to Summit; 31 miles of 115 kV line between Circle and S Philips would be rebuilt as double circuit with the 345 kV line to minimize ROW impacts; Substation work required at Summit for new 345 kV terminal and completion of ring bus. | [37 empty] | 2010-06-01 | 2010-06-01
NA | [9 empty] | NAWERE5327965327711 |  |  | WICHITA - RENO 345KV | U | WERE | WERE |  |  | 0 | 532796 | WICHITA7 345.0 | 532771 | RENO 7 345.00 |  |  | 1 | [27 empty] | WERE | WICHITA - RENO 345KV | 40 mile 345 kV transmission line from existing Wichita 345 kV substation to a new 345-115 kV substation in Reno County east northeast of Hutchinson (Wichita to Reno) | [37 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V3602108AP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08AP | [6 empty] | 1.0133 | 0.8986 | 0.94789 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V3622108AP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08AP | [6 empty] | 1.0133 | 0.9157 | 0.96407 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V3612108AP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08AP | [6 empty] | 1.0133 | 0.91888 | 0.96708 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V3531108AP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08AP | [6 empty] | 0.95794 | 0.92052 | 0.94425 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V4721108AP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08AP | [6 empty] | 0.95806 | 0.92058 | 0.94425 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81V1365508AP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08AP | [6 empty] | 0.94863 | 0.92418 | 0.94905 | 0.95 | 1.05 | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V3531208AP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08AP | [6 empty] | 0.99424 | 0.93133 | 0.95309 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V3561208AP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08AP | [6 empty] | 0.99421 | 0.93137 | 0.95309 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V3351208AP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 08AP | [6 empty] | 0.96678 | 0.94393 | 0.9833 | 0.95 | 1.05 | CATEGORYB | SINGLE | DEARING - MONTGOMERY 138KV CKT 1 | 0 | 533002 | DEARING4 138.00 | 533004 | MONTGOM4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V2862408AP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 08AP | [6 empty] | 0.97555 | 0.94533 | 0.97004 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V3361208AP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 08AP | [6 empty] | 0.96785 | 0.94533 | 0.98215 | 0.95 | 1.05 | CATEGORYB | SINGLE | DEARING - MONTGOMERY 138KV CKT 1 | 0 | 533002 | DEARING4 138.00 | 533004 | MONTGOM4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V3371208AP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 08AP | [6 empty] | 0.96788 | 0.94535 | 0.98217 | 0.95 | 1.05 | CATEGORYB | SINGLE | DEARING - MONTGOMERY 138KV CKT 1 | 0 | 533002 | DEARING4 138.00 | 533004 | MONTGOM4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V4052408AP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 08AP | [6 empty] | 0.97571 | 0.9456 | 0.97004 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V3541208AP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08AP | [6 empty] | 0.99421 | 0.9478 | 0.96918 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V3571208AP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08AP | [6 empty] | 0.99418 | 0.94784 | 0.96918 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V6063308FA |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08FA | [6 empty] | 0.99922 | 0.87127 | 0.94183 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V6083308FA |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08FA | [6 empty] | 0.99919 | 0.88942 | 0.95853 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V6073308FA |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08FA | [6 empty] | 0.99942 | 0.89294 | 0.96177 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V3154408FA |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08FA | [6 empty] | 0.9635 | 0.92212 | 0.95452 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V3434108FA |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08FA | [6 empty] | 0.98653 | 0.92213 | 0.9442 | 0.95 | 1.05 | CATEGORYB | SINGLE | ARCO TAP - ENA 69KV CKT 1 | 0 | 533634 | ENA 2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V3164408FA |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08FA | [6 empty] | 0.96385 | 0.92253 | 0.95452 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V3001108FA |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08FA | [6 empty] | 0.97138 | 0.92255 | 0.95449 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81V6403208FA |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08FA | [6 empty] | 0.98865 | 0.92277 | 0.94289 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V3454108FA |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08FA | [6 empty] | 0.98651 | 0.93919 | 0.96086 | 0.95 | 1.05 | CATEGORYB | SINGLE | ARCO TAP - ENA 69KV CKT 1 | 0 | 533634 | ENA 2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V6172208FA |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08FA | [6 empty] | 0.98582 | 0.93987 | 0.96001 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V3144408FA |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 08FA | [6 empty] | 0.99563 | 0.94239 | 0.9779 | 0.95 | 1.05 | CATEGORYB | SINGLE | ATHENS SWITCHING STATION - OWL CREEK 69KV CKT 1 | 0 | 533623 | ATHENS 2 69.000 | 533642 | OWL CRK2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V3444108FA |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08FA | [6 empty] | 0.98673 | 0.9425 | 0.9641 | 0.95 | 1.05 | CATEGORYB | SINGLE | ARCO TAP - ENA 69KV CKT 1 | 0 | 533634 | ENA 2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V6162208FA |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08FA | [6 empty] | 0.98605 | 0.94318 | 0.96324 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V2744408FA |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 08FA | [6 empty] | 0.98469 | 0.94579 | 0.97556 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V4794408FA |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 08FA | [6 empty] | 0.98311 | 0.94602 | 0.97556 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V1541408G |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08G | [6 empty] | 0.99837 | 0.87792 | 0.9443 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V1561408G |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08G | [6 empty] | 0.99834 | 0.89541 | 0.96054 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V1551408G |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08G | [6 empty] | 0.99857 | 0.89881 | 0.9637 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V1351108G |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08G | [6 empty] | 0.95625 | 0.91484 | 0.94864 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V1981108G |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08G | [6 empty] | 0.9568 | 0.91537 | 0.94864 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V1591408G |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08G | [6 empty] | 0.95217 | 0.91965 | 0.94887 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V1791108G |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08G | [6 empty] | 0.98612 | 0.92338 | 0.94374 | 0.95 | 1.05 | CATEGORYB | SINGLE | ENA - TIOGA 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V1601408G |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08G | [6 empty] | 0.98548 | 0.92382 | 0.9443 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V1361108G |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 08G | [6 empty] | 0.97037 | 0.93744 | 0.97027 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V1851408G |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 08G | [6 empty] | 0.96997 | 0.93817 | 0.96979 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V1621408G |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08G | [6 empty] | 0.98545 | 0.94042 | 0.96054 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V2532308G |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08G | [6 empty] | 0.98671 | 0.94056 | 0.96233 | 0.95 | 1.05 | CATEGORYB | SINGLE | ARCO TAP - ENA 69KV CKT 1 | 0 | 533634 | ENA 2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V1781108G |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 08G | [6 empty] | 0.99364 | 0.94316 | 0.97873 | 0.95 | 1.05 | CATEGORYB | SINGLE | ATHENS SWITCHING STATION - OWL CREEK 69KV CKT 1 | 0 | 533623 | ATHENS 2 69.000 | 533642 | OWL CRK2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V1611408G |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08G | [6 empty] | 0.98568 | 0.94365 | 0.9637 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V2522308G |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08G | [6 empty] | 0.98694 | 0.94378 | 0.96549 | 0.95 | 1.05 | CATEGORYB | SINGLE | ARCO TAP - ENA 69KV CKT 1 | 0 | 533634 | ENA 2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 3 | 2008-12-01 | 2007AG1AFS81V3731308SH |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08SH | [6 empty] | 0.99621 | 0.86184 | 0.9398 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 3 | 2008-12-01 | 2007AG1AFS81V3761308SH |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08SH | [6 empty] | 0.99618 | 0.8804 | 0.95673 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 3 | 2008-12-01 | 2007AG1AFS81V3741308SH |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08SH | [6 empty] | 0.99647 | 0.88407 | 0.96008 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V2831108SH |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08SH | [6 empty] | 0.94857 | 0.91022 | 0.94459 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V4841108SH |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08SH | [6 empty] | 0.94875 | 0.91028 | 0.94459 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V4201108SH |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08SH | [6 empty] | 0.95384 | 0.91473 | 0.94459 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V4021408SH |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08SH | [6 empty] | 0.98421 | 0.91607 | 0.93991 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V4061408SH |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08SH | [6 empty] | 0.98506 | 0.91684 | 0.93991 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V2841108SH |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 08SH | [6 empty] | 0.96242 | 0.93044 | 0.9679 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V4851108SH |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 08SH | [6 empty] | 0.96279 | 0.9307 | 0.9679 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V3361408SH |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 08SH | [6 empty] | 0.9582 | 0.93193 | 0.97651 | 0.95 | 1.05 | CATEGORYB | SINGLE | DEARING - MONTGOMERY 138KV CKT 1 | 0 | 533002 | DEARING4 138.00 | 533004 | MONTGOM4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V3371408SH |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 08SH | [6 empty] | 0.95919 | 0.93312 | 0.97499 | 0.95 | 1.05 | CATEGORYB | SINGLE | DEARING - MONTGOMERY 138KV CKT 1 | 0 | 533002 | DEARING4 138.00 | 533004 | MONTGOM4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V3381408SH |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 08SH | [6 empty] | 0.95926 | 0.9332 | 0.97506 | 0.95 | 1.05 | CATEGORYB | SINGLE | DEARING - MONTGOMERY 138KV CKT 1 | 0 | 533002 | DEARING4 138.00 | 533004 | MONTGOM4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V4041408SH |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08SH | [6 empty] | 0.98418 | 0.93345 | 0.95684 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V4081408SH |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08SH | [6 empty] | 0.98503 | 0.9342 | 0.95684 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V4211108SH |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 08SH | [6 empty] | 0.96848 | 0.93597 | 0.9679 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V4031408SH |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08SH | [6 empty] | 0.98448 | 0.93689 | 0.96019 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V4071408SH |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08SH | [6 empty] | 0.98533 | 0.93763 | 0.96019 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V4432308SH |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 08SH | [6 empty] | 0.96573 | 0.94072 | 0.97111 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V4442308SH |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 08SH | [6 empty] | 0.9658 | 0.94079 | 0.97118 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V4412308SH |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 08SH | [6 empty] | 0.96534 | 0.94142 | 0.97197 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 3 | 2008-12-01 | 2007AG1AFS81V3751308SH |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 08SH | [6 empty] | 1.001 | 0.94363 | 0.97647 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V5632108SP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08SP | [6 empty] | 0.99181 | 0.80904 | 0.92862 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V5662108SP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08SP | [6 empty] | 0.99178 | 0.83233 | 0.94881 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V5642108SP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08SP | [6 empty] | 0.99213 | 0.83693 | 0.95281 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V6412408SP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08SP | [6 empty] | 0.98111 | 0.89687 | 0.92889 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V6492408SP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08SP | [6 empty] | 0.98184 | 0.8978 | 0.92889 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V6741108SP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.94537 | 0.90732 | 0.93288 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V5191408SP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.95007 | 0.90782 | 0.93661 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V8171408SP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.94595 | 0.90788 | 0.93661 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V5652108SP |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 08SP | [6 empty] | 0.99755 | 0.91193 | 0.97173 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V6452408SP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08SP | [6 empty] | 0.98108 | 0.91778 | 0.94907 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V6522408SP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08SP | [6 empty] | 0.98182 | 0.91869 | 0.94907 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V6422408SP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08SP | [6 empty] | 0.98143 | 0.92192 | 0.95306 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V6502408SP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08SP | [6 empty] | 0.98217 | 0.92282 | 0.95306 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V6751108SP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 08SP | [6 empty] | 0.95906 | 0.92502 | 0.95977 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V5201408SP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 08SP | [6 empty] | 0.96363 | 0.92682 | 0.96213 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V8181408SP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 08SP | [6 empty] | 0.96041 | 0.92697 | 0.96213 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V5622108SP |  |  | ATHENS SWITCHING STATION 69KV | S | WERE |  | SEAST |  |  | 533623 | ATHENS 2 69.000 | [5 empty] | 08SP | [6 empty] | 0.99907 | 0.93047 | 0.97668 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V7612308SP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.96101 | 0.93257 | 0.97246 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V7622308SP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 08SP | [6 empty] | 0.96109 | 0.93265 | 0.97254 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V7592308SP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 08SP | [6 empty] | 0.96115 | 0.93377 | 0.97397 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V6442408SP |  |  | UNITED NO. 8 HUMBOLDT 69KV | S | WERE |  | SEAST |  |  | 533650 | UN8HUMB2 69.000 | [5 empty] | 08SP | [6 empty] | 0.97317 | 0.93955 | 0.98621 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V7572308SP |  |  | DEARING 138KV | S | WERE |  | SEAST |  |  | 533002 | DEARING4 138.00 | [5 empty] | 08SP | [6 empty] | 0.96349 | 0.94071 | 0.98072 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V6512408SP |  |  | UNITED NO. 8 HUMBOLDT 69KV | S | WERE |  | SEAST |  |  | 533650 | UN8HUMB2 69.000 | [5 empty] | 08SP | [6 empty] | 0.97423 | 0.94079 | 0.98621 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V6432408SP |  |  | UNITED NO. 1 ELSMORE 69KV | S | WERE |  | SEAST |  |  | 533647 | UN1ELSM2 69.000 | [5 empty] | 08SP | [6 empty] | 0.97597 | 0.94244 | 1.00474 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V6462408SP |  |  | ZILA JUNCTION 69KV | S | WERE |  | SEAST |  |  | 533654 | ZILAJCT2 69.000 | [5 empty] | 08SP | [6 empty] | 0.97632 | 0.94281 | 0.98932 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V4901108SP |  |  | NORTHEAST PARSONS 138KV | S | WERE |  | SEAST |  |  | 533005 | NEPARSN4 138.00 | [5 empty] | 08SP | [6 empty] | 0.98296 | 0.94298 | 0.98661 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533021 | NEOSHO 4 138.00 | 533005 | NEPARSN4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V5402208SP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.97056 | 0.94335 | 0.97494 | 0.95 | 1.05 | CATEGORYB | SINGLE | DEARING - MONTGOMERY 138KV CKT 1 | 0 | 533002 | DEARING4 138.00 | 533004 | MONTGOM4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V5412208SP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 08SP | [6 empty] | 0.97064 | 0.94344 | 0.97502 | 0.95 | 1.05 | CATEGORYB | SINGLE | DEARING - MONTGOMERY 138KV CKT 1 | 0 | 533002 | DEARING4 138.00 | 533004 | MONTGOM4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V5392208SP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 08SP | [6 empty] | 0.97079 | 0.94361 | 0.97683 | 0.95 | 1.05 | CATEGORYB | SINGLE | DEARING - MONTGOMERY 138KV CKT 1 | 0 | 533002 | DEARING4 138.00 | 533004 | MONTGOM4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V6532408SP |  |  | ZILA JUNCTION 69KV | S | WERE |  | SEAST |  |  | 533654 | ZILAJCT2 69.000 | [5 empty] | 08SP | [6 empty] | 0.97738 | 0.94405 | 0.98932 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V8812208SP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.9718 | 0.94506 | 0.97494 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-20 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V8822208SP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 08SP | [6 empty] | 0.97188 | 0.94515 | 0.97502 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-20 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V6402408SP |  |  | ALLEN 69KV | S | WERE |  | SEAST |  |  | 533621 | ALLEN 2 69.000 | [5 empty] | 08SP | [6 empty] | 0.97867 | 0.94527 | 0.98256 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V6482408SP |  |  | ALLEN 69KV | S | WERE |  | SEAST |  |  | 533621 | ALLEN 2 69.000 | [5 empty] | 08SP | [6 empty] | 0.97959 | 0.94634 | 0.98256 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V6891108SP |  |  | UNITED NO. 8 HUMBOLDT 69KV | S | WERE |  | SEAST |  |  | 533650 | UN8HUMB2 69.000 | [5 empty] | 08SP | [6 empty] | 0.97446 | 0.94847 | 0.98523 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V1211408WP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08WP | [6 empty] | 1.0023 | 0.87229 | 0.94225 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V1231408WP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08WP | [6 empty] | 1.0023 | 0.89035 | 0.95894 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V1221408WP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08WP | [6 empty] | 1.0025 | 0.89388 | 0.9622 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 1 | 2008-12-01 | 2007AG1AFS81V1433108WP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08WP | [6 empty] | 0.98507 | 0.92126 | 0.94257 | 0.95 | 1.05 | CATEGORYB | SINGLE | ENA - TIOGA 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V1642108WP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08WP | [6 empty] | 0.98626 | 0.92165 | 0.94214 | 0.95 | 1.05 | CATEGORYB | SINGLE | ARCO TAP - ENA 69KV CKT 1 | 0 | 533634 | ENA 2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V1384108WP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08WP | [6 empty] | 0.96856 | 0.92242 | 0.95455 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V1261408WP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08WP | [6 empty] | 0.96145 | 0.92283 | 0.95476 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V1271408WP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08WP | [6 empty] | 0.9617 | 0.92312 | 0.95476 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 1 | 2008-12-01 | 2007AG1AFS81V1453108WP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08WP | [6 empty] | 0.98504 | 0.93834 | 0.95926 | 0.95 | 1.05 | CATEGORYB | SINGLE | ENA - TIOGA 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V1662108WP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08WP | [6 empty] | 0.98624 | 0.93872 | 0.95884 | 0.95 | 1.05 | CATEGORYB | SINGLE | ARCO TAP - ENA 69KV CKT 1 | 0 | 533634 | ENA 2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 1 | 2008-12-01 | 2007AG1AFS81V1443108WP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08WP | [6 empty] | 0.98529 | 0.94167 | 0.96252 | 0.95 | 1.05 | CATEGORYB | SINGLE | ENA - TIOGA 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V1652108WP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08WP | [6 empty] | 0.98649 | 0.94205 | 0.9621 | 0.95 | 1.05 | CATEGORYB | SINGLE | ARCO TAP - ENA 69KV CKT 1 | 0 | 533634 | ENA 2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 1 | 2008-12-01 | 2007AG1AFS81V1423108WP |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 08WP | [6 empty] | 0.99825 | 0.94323 | 0.97902 | 0.95 | 1.05 | CATEGORYB | SINGLE | ATHENS SWITCHING STATION - OWL CREEK 69KV CKT 1 | 0 | 533623 | ATHENS 2 69.000 | 533642 | OWL CRK2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V1394108WP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 08WP | [6 empty] | 0.98252 | 0.94609 | 0.9771 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V2304108WP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 08WP | [6 empty] | 0.98063 | 0.94821 | 0.9771 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V5831409SP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 09SP | [6 empty] | 0.99267 | 0.80256 | 0.92634 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V5871409SP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 09SP | [6 empty] | 0.99264 | 0.82642 | 0.94695 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V5841409SP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 09SP | [6 empty] | 0.99299 | 0.83114 | 0.95103 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5894409SP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 09SP | [6 empty] | 0.98089 | 0.89457 | 0.92826 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5974409SP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 09SP | [6 empty] | 0.98165 | 0.89554 | 0.92826 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V7134109SP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 09SP | [6 empty] | 0.93638 | 0.90346 | 0.92884 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V8342109SP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 09SP | [6 empty] | 0.93998 | 0.9043 | 0.93181 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V5452109SP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 09SP | [6 empty] | 0.93942 | 0.90466 | 0.93181 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V5851409SP |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 09SP | [6 empty] | 0.99796 | 0.90811 | 0.96948 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5934409SP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 09SP | [6 empty] | 0.98086 | 0.91593 | 0.94883 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V6004409SP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 09SP | [6 empty] | 0.98162 | 0.91687 | 0.94883 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V7144109SP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 09SP | [6 empty] | 0.95069 | 0.9187 | 0.95683 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5904409SP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 09SP | [6 empty] | 0.98121 | 0.92015 | 0.9529 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5984409SP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 09SP | [6 empty] | 0.98198 | 0.92109 | 0.9529 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V8352109SP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 09SP | [6 empty] | 0.9548 | 0.92237 | 0.95863 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V5462109SP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 09SP | [6 empty] | 0.95412 | 0.92294 | 0.95863 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8872309SP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 09SP | [6 empty] | 0.95426 | 0.92539 | 0.96836 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8882309SP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 09SP | [6 empty] | 0.95435 | 0.92548 | 0.96844 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8852309SP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 09SP | [6 empty] | 0.95427 | 0.92624 | 0.96964 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V5821409SP |  |  | ATHENS SWITCHING STATION 69KV | S | WERE |  | SEAST |  |  | 533623 | ATHENS 2 69.000 | [5 empty] | 09SP | [6 empty] | 0.99942 | 0.92714 | 0.97442 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8832309SP |  |  | DEARING 138KV | S | WERE |  | SEAST |  |  | 533002 | DEARING4 138.00 | [5 empty] | 09SP | [6 empty] | 0.95631 | 0.93232 | 0.97588 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V5404109SP |  |  | NORTHEAST PARSONS 138KV | S | WERE |  | SEAST |  |  | 533005 | NEPARSN4 138.00 | [5 empty] | 09SP | [6 empty] | 0.97987 | 0.9377 | 0.98649 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533021 | NEOSHO 4 138.00 | 533005 | NEPARSN4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5924409SP |  |  | UNITED NO. 8 HUMBOLDT 69KV | S | WERE |  | SEAST |  |  | 533650 | UN8HUMB2 69.000 | [5 empty] | 09SP | [6 empty] | 0.97298 | 0.93836 | 0.98616 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5994409SP |  |  | UNITED NO. 8 HUMBOLDT 69KV | S | WERE |  | SEAST |  |  | 533650 | UN8HUMB2 69.000 | [5 empty] | 09SP | [6 empty] | 0.97408 | 0.93964 | 0.98616 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5384409SP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 09SP | [6 empty] | 0.97014 | 0.94085 | 0.97185 | 0.95 | 1.05 | CATEGORYB | SINGLE | DEARING - MONTGOMERY 138KV CKT 1 | 0 | 533002 | DEARING4 138.00 | 533004 | MONTGOM4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5394409SP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 09SP | [6 empty] | 0.97022 | 0.94094 | 0.97193 | 0.95 | 1.05 | CATEGORYB | SINGLE | DEARING - MONTGOMERY 138KV CKT 1 | 0 | 533002 | DEARING4 138.00 | 533004 | MONTGOM4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5374409SP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 09SP | [6 empty] | 0.97041 | 0.94114 | 0.97395 | 0.95 | 1.05 | CATEGORYB | SINGLE | DEARING - MONTGOMERY 138KV CKT 1 | 0 | 533002 | DEARING4 138.00 | 533004 | MONTGOM4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5914409SP |  |  | UNITED NO. 1 ELSMORE 69KV | S | WERE |  | SEAST |  |  | 533647 | UN1ELSM2 69.000 | [5 empty] | 09SP | [6 empty] | 0.97577 | 0.94125 | 1.00421 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5944409SP |  |  | ZILA JUNCTION 69KV | S | WERE |  | SEAST |  |  | 533654 | ZILAJCT2 69.000 | [5 empty] | 09SP | [6 empty] | 0.97613 | 0.94163 | 0.98927 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V6014409SP |  |  | ZILA JUNCTION 69KV | S | WERE |  | SEAST |  |  | 533654 | ZILAJCT2 69.000 | [5 empty] | 09SP | [6 empty] | 0.97723 | 0.9429 | 0.98927 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5884409SP |  |  | ALLEN 69KV | S | WERE |  | SEAST |  |  | 533621 | ALLEN 2 69.000 | [5 empty] | 09SP | [6 empty] | 0.97849 | 0.9441 | 0.98284 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5964409SP |  |  | ALLEN 69KV | S | WERE |  | SEAST |  |  | 533621 | ALLEN 2 69.000 | [5 empty] | 09SP | [6 empty] | 0.97943 | 0.9452 | 0.98284 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V7902409SP |  |  | UNITED NO. 8 HUMBOLDT 69KV | S | WERE |  | SEAST |  |  | 533650 | UN8HUMB2 69.000 | [5 empty] | 09SP | [6 empty] | 0.97478 | 0.94705 | 0.98465 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V9942309SP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 09SP | [6 empty] | 0.96845 | 0.94773 | 0.96964 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V5861409SP |  |  | ORCHARD 69KV | S | WERE |  | SEAST |  |  | 533643 | ORCHARD2 69.000 | [5 empty] | 09SP | [6 empty] | 1.0014 | 0.94866 | 0.98299 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1503309WP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 09WP | [6 empty] | 0.99737 | 0.87101 | 0.94188 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1523309WP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 09WP | [6 empty] | 0.99734 | 0.88906 | 0.95855 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1513309WP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 09WP | [6 empty] | 0.9976 | 0.8926 | 0.96182 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V1594109WP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 09WP | [6 empty] | 0.9636 | 0.91758 | 0.95107 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 4 | 2008-12-01 | 2007AG1AFS81V1063409WP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 09WP | [6 empty] | 0.96419 | 0.91899 | 0.95082 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V1162409WP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 09WP | [6 empty] | 0.95983 | 0.92166 | 0.95281 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V1172409WP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 09WP | [6 empty] | 0.98648 | 0.92199 | 0.94308 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V1212409WP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 09WP | [6 empty] | 0.98738 | 0.92242 | 0.94308 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V1192409WP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 09WP | [6 empty] | 0.98646 | 0.93903 | 0.95973 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V1232409WP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 09WP | [6 empty] | 0.98735 | 0.93945 | 0.95973 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V1724409WP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 09WP | [6 empty] | 0.97866 | 0.94093 | 0.97431 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V1182409WP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 09WP | [6 empty] | 0.98672 | 0.94237 | 0.963 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 4 | 2008-12-01 | 2007AG1AFS81V1073409WP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 09WP | [6 empty] | 0.97799 | 0.94251 | 0.97352 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V1222409WP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 09WP | [6 empty] | 0.98762 | 0.94279 | 0.963 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V8961112SP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.56419 | 0.94109 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9031112SP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.58308 | 0.95815 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12491112SP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.58852 | 0.95815 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9171112SP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.60886 | 0.97512 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9081112SP |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.61007 | 0.99865 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9001112SP |  |  | ATHENS SWITCHING STATION 69KV | S | WERE |  | SEAST |  |  | 533623 | ATHENS 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.61276 | 1.00456 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9041112SP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.61412 | 0.97857 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12631112SP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.61425 | 0.97512 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12541112SP |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.61573 | 0.99865 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9091112SP |  |  | ORCHARD 69KV | S | WERE |  | SEAST |  |  | 533643 | ORCHARD2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.61729 | 1.00395 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12461112SP |  |  | ATHENS SWITCHING STATION 69KV | S | WERE |  | SEAST |  |  | 533623 | ATHENS 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.61848 | 1.00456 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12501112SP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.6195 | 0.97857 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9271112SP |  |  | CHANUTE PLANT3 69KV | S | WERE |  | SEAST |  |  | 533665 | CHANP3 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.62259 | 0.9955 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9251112SP |  |  | CHANUTE PLANT1 69KV | S | WERE |  | SEAST |  |  | 533663 | CHANP1 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.62293 | 0.99572 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9261112SP |  |  | CHANUTE PLANT2 69KV | S | WERE |  | SEAST |  |  | 533664 | CHANP2 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.62293 | 0.99572 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12551112SP |  |  | ORCHARD 69KV | S | WERE |  | SEAST |  |  | 533643 | ORCHARD2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.62303 | 1.00395 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9191112SP |  |  | ASH GROVE1 69KV | S | WERE |  | SEAST |  |  | 533657 | ASHGRV12 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.62622 | 0.99784 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9151112SP |  |  | UNITED NO. 7 ROSE 69KV | S | WERE |  | SEAST |  |  | 533649 | UN7ROSE2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.6268 | 1.00579 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9211112SP |  |  | ASH GROVE JCT1 69KV | S | WERE |  | SEAST |  |  | 533659 | ASHGRJ12 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.62699 | 0.99833 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9231112SP |  |  | CHANUTE GENERATION TAP 69KV | S | WERE |  | SEAST |  |  | 533661 | CGENTAP2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.62722 | 0.99848 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9201112SP |  |  | ASH GROVE2 69KV | S | WERE |  | SEAST |  |  | 533658 | ASHGRV22 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.62751 | 0.99949 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9221112SP |  |  | ASH GROVE JCT2 69KV | S | WERE |  | SEAST |  |  | 533660 | ASHGRJ22 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.62828 | 0.99998 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12731112SP |  |  | CHANUTE PLANT3 69KV | S | WERE |  | SEAST |  |  | 533665 | CHANP3 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.62832 | 0.9955 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12711112SP |  |  | CHANUTE PLANT1 69KV | S | WERE |  | SEAST |  |  | 533663 | CHANP1 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.62866 | 0.99572 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12721112SP |  |  | CHANUTE PLANT2 69KV | S | WERE |  | SEAST |  |  | 533664 | CHANP2 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.62866 | 0.99572 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9241112SP |  |  | CHANUTE GENERATION SUB 69KV | S | WERE |  | SEAST |  |  | 533662 | CGENSUB2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.62959 | 1.0 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9281112SP |  |  | CHANUTE TAP 69KV | S | WERE |  | SEAST |  |  | 533666 | CHANTAP2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.63161 | 1.00181 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12651112SP |  |  | ASH GROVE1 69KV | S | WERE |  | SEAST |  |  | 533657 | ASHGRV12 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.63193 | 0.99784 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12611112SP |  |  | UNITED NO. 7 ROSE 69KV | S | WERE |  | SEAST |  |  | 533649 | UN7ROSE2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.63254 | 1.00579 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12671112SP |  |  | ASH GROVE JCT1 69KV | S | WERE |  | SEAST |  |  | 533659 | ASHGRJ12 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.63269 | 0.99833 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12691112SP |  |  | CHANUTE GENERATION TAP 69KV | S | WERE |  | SEAST |  |  | 533661 | CGENTAP2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.63292 | 0.99848 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12661112SP |  |  | ASH GROVE2 69KV | S | WERE |  | SEAST |  |  | 533658 | ASHGRV22 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.63323 | 0.99949 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12681112SP |  |  | ASH GROVE JCT2 69KV | S | WERE |  | SEAST |  |  | 533660 | ASHGRJ22 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.63399 | 0.99998 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9121112SP |  |  | TIOGA 69KV | S | WERE |  | SEAST |  |  | 533646 | TIOGA 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.63506 | 1.0078 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12701112SP |  |  | CHANUTE GENERATION SUB 69KV | S | WERE |  | SEAST |  |  | 533662 | CGENSUB2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.63529 | 1.0 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12741112SP |  |  | CHANUTE TAP 69KV | S | WERE |  | SEAST |  |  | 533666 | CHANTAP2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.6373 | 1.00181 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12581112SP |  |  | TIOGA 69KV | S | WERE |  | SEAST |  |  | 533646 | TIOGA 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.64078 | 1.0078 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9141112SP |  |  | UNITED NO. 6 URBANA 69KV | S | WERE |  | SEAST |  |  | 533648 | UN6URBA2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.65044 | 1.01031 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V10972412SP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 12SP | [6 empty] | 0.97877 | 0.65045 | 0.94092 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9011112SP |  |  | ENA 69KV | S | WERE |  | SEAST |  |  | 533634 | ENA 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.65276 | 0.9995 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V8971112SP |  |  | ARCO 69KV | S | WERE |  | SEAST |  |  | 533619 | ARCO 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.65372 | 0.99907 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V8981112SP |  |  | ARCO TAP 69KV | S | WERE |  | SEAST |  |  | 533620 | ARCOTAP2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.65392 | 0.9992 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12601112SP |  |  | UNITED NO. 6 URBANA 69KV | S | WERE |  | SEAST |  |  | 533648 | UN6URBA2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.65597 | 1.01031 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9071112SP |  |  | MONARCH 69KV | S | WERE |  | SEAST |  |  | 533641 | MONARCH2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.65598 | 0.99879 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12471112SP |  |  | ENA 69KV | S | WERE |  | SEAST |  |  | 533634 | ENA 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.65809 | 0.9995 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12431112SP |  |  | ARCO 69KV | S | WERE |  | SEAST |  |  | 533619 | ARCO 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.65904 | 0.99907 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12441112SP |  |  | ARCO TAP 69KV | S | WERE |  | SEAST |  |  | 533620 | ARCOTAP2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.65924 | 0.9992 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12531112SP |  |  | MONARCH 69KV | S | WERE |  | SEAST |  |  | 533641 | MONARCH2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.66126 | 0.99879 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9291112SP |  |  | CITY OF ERIE 69KV | S | WERE |  | SEAST |  |  | 533760 | ERIE 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.67095 | 1.02 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V8991112SP |  |  | ALLEN 69KV | S | WERE |  | SEAST |  |  | 533621 | ALLEN 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.67363 | 1.00104 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12751112SP |  |  | CITY OF ERIE 69KV | S | WERE |  | SEAST |  |  | 533760 | ERIE 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.67632 | 1.02 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12451112SP |  |  | ALLEN 69KV | S | WERE |  | SEAST |  |  | 533621 | ALLEN 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.67868 | 1.00104 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11072412SP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 12SP | [6 empty] | 0.97874 | 0.68133 | 0.96239 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V10982412SP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 12SP | [6 empty] | 0.97911 | 0.68744 | 0.96663 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11062412SP |  |  | UNITED NO. 8 HUMBOLDT 69KV | S | WERE |  | SEAST |  |  | 533650 | UN8HUMB2 69.000 | [5 empty] | 12SP | [6 empty] | 0.9709 | 0.71327 | 0.99719 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11032412SP |  |  | UNITED NO. 1 ELSMORE 69KV | S | WERE |  | SEAST |  |  | 533647 | UN1ELSM2 69.000 | [5 empty] | 12SP | [6 empty] | 0.97368 | 0.717 | 1.01321 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9161112SP |  |  | UNITED NO. 8 HUMBOLDT 69KV | S | WERE |  | SEAST |  |  | 533650 | UN8HUMB2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.71715 | 0.99944 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11082412SP |  |  | ZILA JUNCTION 69KV | S | WERE |  | SEAST |  |  | 533654 | ZILAJCT2 69.000 | [5 empty] | 12SP | [6 empty] | 0.97406 | 0.71761 | 1.00027 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V10942412SP |  |  | ALLEN 69KV | S | WERE |  | SEAST |  |  | 533621 | ALLEN 2 69.000 | [5 empty] | 12SP | [6 empty] | 0.97643 | 0.72105 | 0.9963 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9181112SP |  |  | ZILA JUNCTION 69KV | S | WERE |  | SEAST |  |  | 533654 | ZILAJCT2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.72146 | 1.00251 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12621112SP |  |  | UNITED NO. 8 HUMBOLDT 69KV | S | WERE |  | SEAST |  |  | 533650 | UN8HUMB2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.72148 | 0.99944 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12641112SP |  |  | ZILA JUNCTION 69KV | S | WERE |  | SEAST |  |  | 533654 | ZILAJCT2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.72576 | 1.00251 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V10992412SP |  |  | MONARCH 69KV | S | WERE |  | SEAST |  |  | 533641 | MONARCH2 69.000 | [5 empty] | 12SP | [6 empty] | 0.97891 | 0.72923 | 0.99397 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V10922412SP |  |  | ARCO 69KV | S | WERE |  | SEAST |  |  | 533619 | ARCO 2 69.000 | [5 empty] | 12SP | [6 empty] | 0.98021 | 0.73208 | 0.99424 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V10932412SP |  |  | ARCO TAP 69KV | S | WERE |  | SEAST |  |  | 533620 | ARCOTAP2 69.000 | [5 empty] | 12SP | [6 empty] | 0.98034 | 0.73226 | 0.99438 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11002412SP |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 12SP | [6 empty] | 0.98913 | 0.73409 | 0.98839 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V10962412SP |  |  | ENA 69KV | S | WERE |  | SEAST |  |  | 533634 | ENA 2 69.000 | [5 empty] | 12SP | [6 empty] | 0.98128 | 0.73421 | 0.99467 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V10952412SP |  |  | ATHENS SWITCHING STATION 69KV | S | WERE |  | SEAST |  |  | 533623 | ATHENS 2 69.000 | [5 empty] | 12SP | [6 empty] | 0.99162 | 0.74577 | 0.99487 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11012412SP |  |  | ORCHARD 69KV | S | WERE |  | SEAST |  |  | 533643 | ORCHARD2 69.000 | [5 empty] | 12SP | [6 empty] | 0.99464 | 0.75613 | 0.99581 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11172412SP |  |  | CHANUTE PLANT3 69KV | S | WERE |  | SEAST |  |  | 533665 | CHANP3 2 69.000 | [5 empty] | 12SP | [6 empty] | 1.0056 | 0.76372 | 0.98304 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11152412SP |  |  | CHANUTE PLANT1 69KV | S | WERE |  | SEAST |  |  | 533663 | CHANP1 2 69.000 | [5 empty] | 12SP | [6 empty] | 1.0056 | 0.76401 | 0.98327 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11162412SP |  |  | CHANUTE PLANT2 69KV | S | WERE |  | SEAST |  |  | 533664 | CHANP2 2 69.000 | [5 empty] | 12SP | [6 empty] | 1.0056 | 0.76402 | 0.98327 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11192412SP |  |  | CITY OF ERIE 69KV | S | WERE |  | SEAST |  |  | 533760 | ERIE 2 69.000 | [5 empty] | 12SP | [6 empty] | 1.0038 | 0.76455 | 0.98401 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11092412SP |  |  | ASH GROVE1 69KV | S | WERE |  | SEAST |  |  | 533657 | ASHGRV12 69.000 | [5 empty] | 12SP | [6 empty] | 1.0056 | 0.76685 | 0.98546 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11042412SP |  |  | UNITED NO. 6 URBANA 69KV | S | WERE |  | SEAST |  |  | 533648 | UN6URBA2 69.000 | [5 empty] | 12SP | [6 empty] | 1.0036 | 0.76688 | 0.98574 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11112412SP |  |  | ASH GROVE JCT1 69KV | S | WERE |  | SEAST |  |  | 533659 | ASHGRJ12 69.000 | [5 empty] | 12SP | [6 empty] | 1.0056 | 0.7675 | 0.98597 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11132412SP |  |  | CHANUTE GENERATION TAP 69KV | S | WERE |  | SEAST |  |  | 533661 | CGENTAP2 69.000 | [5 empty] | 12SP | [6 empty] | 1.0056 | 0.7677 | 0.98613 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11142412SP |  |  | CHANUTE GENERATION SUB 69KV | S | WERE |  | SEAST |  |  | 533662 | CGENSUB2 69.000 | [5 empty] | 12SP | [6 empty] | 1.0056 | 0.76974 | 0.9877 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11102412SP |  |  | ASH GROVE2 69KV | S | WERE |  | SEAST |  |  | 533658 | ASHGRV22 69.000 | [5 empty] | 12SP | [6 empty] | 1.0057 | 0.77051 | 0.98827 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11122412SP |  |  | ASH GROVE JCT2 69KV | S | WERE |  | SEAST |  |  | 533660 | ASHGRJ22 69.000 | [5 empty] | 12SP | [6 empty] | 1.0057 | 0.77117 | 0.98878 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11182412SP |  |  | CHANUTE TAP 69KV | S | WERE |  | SEAST |  |  | 533666 | CHANTAP2 69.000 | [5 empty] | 12SP | [6 empty] | 1.0056 | 0.77259 | 0.98991 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11052412SP |  |  | UNITED NO. 7 ROSE 69KV | S | WERE |  | SEAST |  |  | 533649 | UN7ROSE2 69.000 | [5 empty] | 12SP | [6 empty] | 1.0008 | 0.77383 | 0.99946 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V10872412SP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 12SP | [6 empty] | 0.95969 | 0.77845 | 0.9212 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V10752112SP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 12SP | [6 empty] | 0.96022 | 0.78132 | 0.91953 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11022412SP |  |  | TIOGA 69KV | S | WERE |  | SEAST |  |  | 533646 | TIOGA 2 69.000 | [5 empty] | 12SP | [6 empty] | 1.0061 | 0.78951 | 1.00284 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9131112SP |  |  | UNITED NO. 1 ELSMORE 69KV | S | WERE |  | SEAST |  |  | 533647 | UN1ELSM2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.84414 | 1.01051 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12591112SP |  |  | UNITED NO. 1 ELSMORE 69KV | S | WERE |  | SEAST |  |  | 533647 | UN1ELSM2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.84687 | 1.01051 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9051112SP |  |  | MARMATON 69KV | S | WERE |  | SEAST |  |  | 533639 | MARMATN2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.872 | 1.01246 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12511112SP |  |  | MARMATON 69KV | S | WERE |  | SEAST |  |  | 533639 | MARMATN2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.87442 | 1.01246 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V10762112SP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 12SP | [6 empty] | 0.97968 | 0.89271 | 0.95606 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V10882412SP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 12SP | [6 empty] | 0.97966 | 0.89336 | 0.95637 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V14572412SP |  |  | MARMATON 69KV | S | WERE |  | SEAST |  |  | 533639 | MARMATN2 69.000 | [5 empty] | 12SP | [6 empty] | 0.9757 | 0.89612 | 1.01623 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V13302112SP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 12SP | [6 empty] | 0.95963 | 0.89804 | 0.95606 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15102312SP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 12SP | [6 empty] | 0.9556 | 0.90129 | 0.96206 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15112312SP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 12SP | [6 empty] | 0.9557 | 0.90139 | 0.96215 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15082312SP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 12SP | [6 empty] | 0.95478 | 0.90206 | 0.96306 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15062312SP |  |  | DEARING 138KV | S | WERE |  | SEAST |  |  | 533002 | DEARING4 138.00 | [5 empty] | 12SP | [6 empty] | 0.95342 | 0.90925 | 0.96833 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V8951112SP |  |  | MARMTNE5 161KV | S | WERE |  | SEAST |  |  | 532934 | MARMTNE5 161.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.91678 | 0.99744 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12421112SP |  |  | MARMTNE5 161KV | S | WERE |  | SEAST |  |  | 532934 | MARMTNE5 161.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.91761 | 0.99744 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V11312312SP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 12SP | [6 empty] | 0.97943 | 0.92227 | 0.96206 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V11322312SP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 12SP | [6 empty] | 0.97952 | 0.92237 | 0.96215 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V10792112SP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 12SP | [6 empty] | 0.98045 | 0.92308 | 0.96441 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V10802112SP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 12SP | [6 empty] | 0.98054 | 0.92318 | 0.9645 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V9162112SP |  |  | NORTHEAST PARSONS 138KV | S | WERE |  | SEAST |  |  | 533005 | NEPARSN4 138.00 | [5 empty] | 12SP | [6 empty] | 1.0066 | 0.92618 | 0.98581 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533021 | NEOSHO 4 138.00 | 533005 | NEPARSN4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V11302312SP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 12SP | [6 empty] | 0.97934 | 0.92661 | 0.96306 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V10782112SP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 12SP | [6 empty] | 0.98065 | 0.92767 | 0.96573 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V1162412SP |  |  | DEARING 138KV | S | WERE |  | SEAST |  |  | 533002 | DEARING4 138.00 | [5 empty] | 12SP | [6 empty] | 0.95484 | 0.93271 | 0.97492 | 0.95 | 1.05 | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V11292312SP |  |  | DEARING 138KV | S | WERE |  | SEAST |  |  | 533002 | DEARING4 138.00 | [5 empty] | 12SP | [6 empty] | 0.9807 | 0.94632 | 0.96833 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1823312WP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 12WP | [6 empty] | 0.8913 | 0.45704 | 0.95214 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2133312WP |  |  | CHANUTE PLANT3 69KV | S | WERE |  | SEAST |  |  | 533665 | CHANP3 2 69.000 | [5 empty] | 12WP | [6 empty] | 1.003 | 0.49095 | 1.00517 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2113312WP |  |  | CHANUTE PLANT1 69KV | S | WERE |  | SEAST |  |  | 533663 | CHANP1 2 69.000 | [5 empty] | 12WP | [6 empty] | 1.003 | 0.49122 | 1.00533 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2123312WP |  |  | CHANUTE PLANT2 69KV | S | WERE |  | SEAST |  |  | 533664 | CHANP2 2 69.000 | [5 empty] | 12WP | [6 empty] | 1.003 | 0.49122 | 1.00533 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3713312WP |  |  | CHANUTE PLANT3 69KV | S | WERE |  | SEAST |  |  | 533665 | CHANP3 2 69.000 | [5 empty] | 12WP | [6 empty] | 0.99925 | 0.49237 | 1.00517 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3693312WP |  |  | CHANUTE PLANT1 69KV | S | WERE |  | SEAST |  |  | 533663 | CHANP1 2 69.000 | [5 empty] | 12WP | [6 empty] | 0.99925 | 0.49264 | 1.00533 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3703312WP |  |  | CHANUTE PLANT2 69KV | S | WERE |  | SEAST |  |  | 533664 | CHANP2 2 69.000 | [5 empty] | 12WP | [6 empty] | 0.99925 | 0.49264 | 1.00533 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2053312WP |  |  | ASH GROVE1 69KV | S | WERE |  | SEAST |  |  | 533657 | ASHGRV12 69.000 | [5 empty] | 12WP | [6 empty] | 1.003 | 0.49385 | 1.00693 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2073312WP |  |  | ASH GROVE JCT1 69KV | S | WERE |  | SEAST |  |  | 533659 | ASHGRJ12 69.000 | [5 empty] | 12WP | [6 empty] | 1.003 | 0.49447 | 1.00731 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2093312WP |  |  | CHANUTE GENERATION TAP 69KV | S | WERE |  | SEAST |  |  | 533661 | CGENTAP2 69.000 | [5 empty] | 12WP | [6 empty] | 1.003 | 0.49466 | 1.00742 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3633312WP |  |  | ASH GROVE1 69KV | S | WERE |  | SEAST |  |  | 533657 | ASHGRV12 69.000 | [5 empty] | 12WP | [6 empty] | 0.99925 | 0.49528 | 1.00693 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3653312WP |  |  | ASH GROVE JCT1 69KV | S | WERE |  | SEAST |  |  | 533659 | ASHGRJ12 69.000 | [5 empty] | 12WP | [6 empty] | 0.99925 | 0.49589 | 1.00731 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3673312WP |  |  | CHANUTE GENERATION TAP 69KV | S | WERE |  | SEAST |  |  | 533661 | CGENTAP2 69.000 | [5 empty] | 12WP | [6 empty] | 0.99925 | 0.49608 | 1.00742 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2103312WP |  |  | CHANUTE GENERATION SUB 69KV | S | WERE |  | SEAST |  |  | 533662 | CGENSUB2 69.000 | [5 empty] | 12WP | [6 empty] | 1.003 | 0.49656 | 1.00857 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2003312WP |  |  | UNITED NO. 6 URBANA 69KV | S | WERE |  | SEAST |  |  | 533648 | UN6URBA2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0016 | 0.49668 | 1.0087 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2153312WP |  |  | CITY OF ERIE 69KV | S | WERE |  | SEAST |  |  | 533760 | ERIE 2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0018 | 0.49709 | 1.00873 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2063312WP |  |  | ASH GROVE2 69KV | S | WERE |  | SEAST |  |  | 533658 | ASHGRV22 69.000 | [5 empty] | 12WP | [6 empty] | 1.0031 | 0.49721 | 1.00894 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2083312WP |  |  | ASH GROVE JCT2 69KV | S | WERE |  | SEAST |  |  | 533660 | ASHGRJ22 69.000 | [5 empty] | 12WP | [6 empty] | 1.0031 | 0.49783 | 1.00932 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3683312WP |  |  | CHANUTE GENERATION SUB 69KV | S | WERE |  | SEAST |  |  | 533662 | CGENSUB2 69.000 | [5 empty] | 12WP | [6 empty] | 0.99925 | 0.49799 | 1.00857 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3583312WP |  |  | UNITED NO. 6 URBANA 69KV | S | WERE |  | SEAST |  |  | 533648 | UN6URBA2 69.000 | [5 empty] | 12WP | [6 empty] | 0.99784 | 0.4981 | 1.0087 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3733312WP |  |  | CITY OF ERIE 69KV | S | WERE |  | SEAST |  |  | 533760 | ERIE 2 69.000 | [5 empty] | 12WP | [6 empty] | 0.99802 | 0.4985 | 1.00873 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3643312WP |  |  | ASH GROVE2 69KV | S | WERE |  | SEAST |  |  | 533658 | ASHGRV22 69.000 | [5 empty] | 12WP | [6 empty] | 0.99927 | 0.49864 | 1.00894 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3663312WP |  |  | ASH GROVE JCT2 69KV | S | WERE |  | SEAST |  |  | 533660 | ASHGRJ22 69.000 | [5 empty] | 12WP | [6 empty] | 0.99927 | 0.49925 | 1.00932 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2143312WP |  |  | CHANUTE TAP 69KV | S | WERE |  | SEAST |  |  | 533666 | CHANTAP2 69.000 | [5 empty] | 12WP | [6 empty] | 1.003 | 0.49929 | 1.01023 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3723312WP |  |  | CHANUTE TAP 69KV | S | WERE |  | SEAST |  |  | 533666 | CHANTAP2 69.000 | [5 empty] | 12WP | [6 empty] | 0.99924 | 0.50072 | 1.01023 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1893312WP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 12WP | [6 empty] | 1.006 | 0.51044 | 0.97067 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3473312WP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0017 | 0.51157 | 0.97067 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1983312WP |  |  | TIOGA 69KV | S | WERE |  | SEAST |  |  | 533646 | TIOGA 2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0033 | 0.51454 | 1.01926 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3563312WP |  |  | TIOGA 69KV | S | WERE |  | SEAST |  |  | 533646 | TIOGA 2 69.000 | [5 empty] | 12WP | [6 empty] | 0.99955 | 0.51596 | 1.01926 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2013312WP |  |  | UNITED NO. 7 ROSE 69KV | S | WERE |  | SEAST |  |  | 533649 | UN7ROSE2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0066 | 0.51642 | 1.01829 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3593312WP |  |  | UNITED NO. 7 ROSE 69KV | S | WERE |  | SEAST |  |  | 533649 | UN7ROSE2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0027 | 0.5178 | 1.01829 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1953312WP |  |  | ORCHARD 69KV | S | WERE |  | SEAST |  |  | 533643 | ORCHARD2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0111 | 0.51997 | 1.01745 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3533312WP |  |  | ORCHARD 69KV | S | WERE |  | SEAST |  |  | 533643 | ORCHARD2 69.000 | [5 empty] | 12WP | [6 empty] | 1.007 | 0.52128 | 1.01745 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1863312WP |  |  | ATHENS SWITCHING STATION 69KV | S | WERE |  | SEAST |  |  | 533623 | ATHENS 2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0161 | 0.52546 | 1.01811 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3443312WP |  |  | ATHENS SWITCHING STATION 69KV | S | WERE |  | SEAST |  |  | 533623 | ATHENS 2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0119 | 0.52673 | 1.01811 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1943312WP |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0131 | 0.52726 | 1.01213 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3523312WP |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0089 | 0.52849 | 1.01213 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2033312WP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0059 | 0.53769 | 0.98773 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3613312WP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0016 | 0.53881 | 0.98773 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1903312WP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0062 | 0.54304 | 0.99107 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3483312WP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0019 | 0.54416 | 0.99107 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1873312WP |  |  | ENA 69KV | S | WERE |  | SEAST |  |  | 533634 | ENA 2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0004 | 0.57422 | 1.01069 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3453312WP |  |  | ENA 69KV | S | WERE |  | SEAST |  |  | 533634 | ENA 2 69.000 | [5 empty] | 12WP | [6 empty] | 0.9962 | 0.57536 | 1.01069 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1833312WP |  |  | ARCO 69KV | S | WERE |  | SEAST |  |  | 533619 | ARCO 2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0002 | 0.57673 | 1.01028 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1843312WP |  |  | ARCO TAP 69KV | S | WERE |  | SEAST |  |  | 533620 | ARCOTAP2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0003 | 0.57687 | 1.01036 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3413312WP |  |  | ARCO 69KV | S | WERE |  | SEAST |  |  | 533619 | ARCO 2 69.000 | [5 empty] | 12WP | [6 empty] | 0.99601 | 0.57785 | 1.01028 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3423312WP |  |  | ARCO TAP 69KV | S | WERE |  | SEAST |  |  | 533620 | ARCOTAP2 69.000 | [5 empty] | 12WP | [6 empty] | 0.99609 | 0.57799 | 1.01036 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1933312WP |  |  | MONARCH 69KV | S | WERE |  | SEAST |  |  | 533641 | MONARCH2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0002 | 0.58129 | 1.00988 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3513312WP |  |  | MONARCH 69KV | S | WERE |  | SEAST |  |  | 533641 | MONARCH2 69.000 | [5 empty] | 12WP | [6 empty] | 0.99598 | 0.5824 | 1.00988 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1853312WP |  |  | ALLEN 69KV | S | WERE |  | SEAST |  |  | 533621 | ALLEN 2 69.000 | [5 empty] | 12WP | [6 empty] | 1.004 | 0.61001 | 1.01178 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3433312WP |  |  | ALLEN 69KV | S | WERE |  | SEAST |  |  | 533621 | ALLEN 2 69.000 | [5 empty] | 12WP | [6 empty] | 0.9997 | 0.61103 | 1.01178 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2023312WP |  |  | UNITED NO. 8 HUMBOLDT 69KV | S | WERE |  | SEAST |  |  | 533650 | UN8HUMB2 69.000 | [5 empty] | 12WP | [6 empty] | 1.004 | 0.67852 | 1.00982 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3603312WP |  |  | UNITED NO. 8 HUMBOLDT 69KV | S | WERE |  | SEAST |  |  | 533650 | UN8HUMB2 69.000 | [5 empty] | 12WP | [6 empty] | 0.99942 | 0.67933 | 1.00982 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2043312WP |  |  | ZILA JUNCTION 69KV | S | WERE |  | SEAST |  |  | 533654 | ZILAJCT2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0062 | 0.68187 | 1.01207 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3623312WP |  |  | ZILA JUNCTION 69KV | S | WERE |  | SEAST |  |  | 533654 | ZILAJCT2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0017 | 0.68268 | 1.01207 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1993312WP |  |  | UNITED NO. 1 ELSMORE 69KV | S | WERE |  | SEAST |  |  | 533647 | UN1ELSM2 69.000 | [5 empty] | 12WP | [6 empty] | 1.014 | 0.82823 | 1.01655 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3573312WP |  |  | UNITED NO. 1 ELSMORE 69KV | S | WERE |  | SEAST |  |  | 533647 | UN1ELSM2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0091 | 0.82872 | 1.01655 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V2014212WP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0033 | 0.85015 | 0.95731 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1913312WP |  |  | MARMATON 69KV | S | WERE |  | SEAST |  |  | 533639 | MARMATN2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0157 | 0.85884 | 1.01769 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3493312WP |  |  | MARMATON 69KV | S | WERE |  | SEAST |  |  | 533639 | MARMATN2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0108 | 0.85927 | 1.01769 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V2044212WP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0033 | 0.86966 | 0.97462 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V2024212WP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0035 | 0.87348 | 0.97801 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V3594112WP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 12WP | [6 empty] | 0.97193 | 0.89516 | 0.93711 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V1994112WP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 12WP | [6 empty] | 0.97312 | 0.89543 | 0.93711 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1813312WP |  |  | MARMTNE5 161KV | S | WERE |  | SEAST |  |  | 532934 | MARMTNE5 161.00 | [5 empty] | 12WP | [6 empty] | 1.0044 | 0.91209 | 0.99823 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3403312WP |  |  | MARMTNE5 161KV | S | WERE |  | SEAST |  |  | 532934 | MARMTNE5 161.00 | [5 empty] | 12WP | [6 empty] | 1.0049 | 0.91227 | 0.99823 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V3604112WP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 12WP | [6 empty] | 0.98023 | 0.92191 | 0.96479 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V2004112WP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 12WP | [6 empty] | 0.98137 | 0.92197 | 0.96479 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V2974112WP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 12WP | [6 empty] | 0.98347 | 0.93505 | 0.96479 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V2034212WP |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0076 | 0.93555 | 0.99734 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V614112WP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 12WP | [6 empty] | 0.96701 | 0.94498 | 0.97736 | 0.95 | 1.05 | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V624112WP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 12WP | [6 empty] | 0.96707 | 0.94504 | 0.97742 | 0.95 | 1.05 | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V522212WP |  |  | DEARING 138KV | S | WERE |  | SEAST |  |  | 533002 | DEARING4 138.00 | [5 empty] | 12WP | [6 empty] | 0.96698 | 0.94566 | 0.98584 | 0.95 | 1.05 | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V532212WP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 12WP | [6 empty] | 0.97048 | 0.94578 | 0.98117 | 0.95 | 1.05 | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V3002112WP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 12WP | [6 empty] | 0.98481 | 0.94764 | 0.97773 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V3012112WP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 12WP | [6 empty] | 0.98487 | 0.9477 | 0.97779 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V3614112WP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 12WP | [6 empty] | 0.98626 | 0.94853 | 0.97736 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-20 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V3624112WP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 12WP | [6 empty] | 0.98632 | 0.94859 | 0.97742 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-20 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V2992112WP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 12WP | [6 empty] | 0.98494 | 0.94942 | 0.97947 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12752317SP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 17SP | [6 empty] | 0.8767 | 0.81369 | 0.94449 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V14982117SP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.98247 | 0.81534 | 0.93789 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V15022117SP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 17SP | [6 empty] | 0.98244 | 0.83702 | 0.95669 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V14992117SP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 17SP | [6 empty] | 0.98284 | 0.84142 | 0.96051 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12812317SP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97705 | 0.86198 | 0.93855 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21052317SP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97757 | 0.86724 | 0.93855 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12902317SP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97702 | 0.88246 | 0.95734 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12822317SP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97743 | 0.88662 | 0.96116 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21142317SP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97754 | 0.8876 | 0.95734 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21062317SP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97795 | 0.89173 | 0.96116 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V19902117SP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 17SP | [6 empty] | 0.95113 | 0.89265 | 0.94414 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12842317SP |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97733 | 0.89539 | 0.98575 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12792317SP |  |  | ATHENS SWITCHING STATION 69KV | S | WERE |  | SEAST |  |  | 533623 | ATHENS 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97793 | 0.90032 | 0.99287 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21082317SP |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 17SP | [6 empty] | 0.9779 | 0.90078 | 0.98575 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12852317SP |  |  | ORCHARD 69KV | S | WERE |  | SEAST |  |  | 533643 | ORCHARD2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97912 | 0.90355 | 0.99461 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21032317SP |  |  | ATHENS SWITCHING STATION 69KV | S | WERE |  | SEAST |  |  | 533623 | ATHENS 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97852 | 0.90579 | 0.99287 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V19942417SP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 17SP | [6 empty] | 0.96338 | 0.907 | 0.94771 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V18283317SP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 17SP | [6 empty] | 0.95278 | 0.90724 | 0.96581 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V13002317SP |  |  | CHANUTE PLANT3 69KV | S | WERE |  | SEAST |  |  | 533665 | CHANP3 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.99002 | 0.90728 | 0.99482 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V18303317SP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 17SP | [6 empty] | 0.95421 | 0.90748 | 0.96565 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12982317SP |  |  | CHANUTE PLANT1 69KV | S | WERE |  | SEAST |  |  | 533663 | CHANP1 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.99002 | 0.90755 | 0.99506 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12992317SP |  |  | CHANUTE PLANT2 69KV | S | WERE |  | SEAST |  |  | 533664 | CHANP2 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.99002 | 0.90755 | 0.99506 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V18313317SP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 17SP | [6 empty] | 0.95432 | 0.9076 | 0.96576 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21092317SP |  |  | ORCHARD 69KV | S | WERE |  | SEAST |  |  | 533643 | ORCHARD2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97973 | 0.9091 | 0.99461 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 1 | 2008-12-01 | 2007AG1AFS81V18823117SP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 17SP | [6 empty] | 0.95846 | 0.90946 | 0.96537 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12922317SP |  |  | ASH GROVE1 69KV | S | WERE |  | SEAST |  |  | 533657 | ASHGRV12 69.000 | [5 empty] | 17SP | [6 empty] | 0.99002 | 0.91009 | 0.99738 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12882317SP |  |  | UNITED NO. 7 ROSE 69KV | S | WERE |  | SEAST |  |  | 533649 | UN7ROSE2 69.000 | [5 empty] | 17SP | [6 empty] | 0.98326 | 0.91031 | 0.9997 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12942317SP |  |  | ASH GROVE JCT1 69KV | S | WERE |  | SEAST |  |  | 533659 | ASHGRJ12 69.000 | [5 empty] | 17SP | [6 empty] | 0.99002 | 0.91068 | 0.99792 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12962317SP |  |  | CHANUTE GENERATION TAP 69KV | S | WERE |  | SEAST |  |  | 533661 | CGENTAP2 69.000 | [5 empty] | 17SP | [6 empty] | 0.99002 | 0.91086 | 0.99808 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V18263317SP |  |  | DEARING 138KV | S | WERE |  | SEAST |  |  | 533002 | DEARING4 138.00 | [5 empty] | 17SP | [6 empty] | 0.9489 | 0.91118 | 0.96684 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12932317SP |  |  | ASH GROVE2 69KV | S | WERE |  | SEAST |  |  | 533658 | ASHGRV22 69.000 | [5 empty] | 17SP | [6 empty] | 0.98966 | 0.91118 | 0.99866 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12952317SP |  |  | ASH GROVE JCT2 69KV | S | WERE |  | SEAST |  |  | 533660 | ASHGRJ22 69.000 | [5 empty] | 17SP | [6 empty] | 0.98966 | 0.91178 | 0.99921 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12972317SP |  |  | CHANUTE GENERATION SUB 69KV | S | WERE |  | SEAST |  |  | 533662 | CGENSUB2 69.000 | [5 empty] | 17SP | [6 empty] | 0.99002 | 0.9127 | 0.99975 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21242317SP |  |  | CHANUTE PLANT3 69KV | S | WERE |  | SEAST |  |  | 533665 | CHANP3 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.99062 | 0.913 | 0.99482 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21222317SP |  |  | CHANUTE PLANT1 69KV | S | WERE |  | SEAST |  |  | 533663 | CHANP1 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.99062 | 0.91327 | 0.99506 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21232317SP |  |  | CHANUTE PLANT2 69KV | S | WERE |  | SEAST |  |  | 533664 | CHANP2 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.99062 | 0.91327 | 0.99506 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V15002117SP |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 17SP | [6 empty] | 0.98925 | 0.91331 | 0.9853 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V13012317SP |  |  | CHANUTE TAP 69KV | S | WERE |  | SEAST |  |  | 533666 | CHANTAP2 69.000 | [5 empty] | 17SP | [6 empty] | 0.99038 | 0.91441 | 1.001 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21162317SP |  |  | ASH GROVE1 69KV | S | WERE |  | SEAST |  |  | 533657 | ASHGRV12 69.000 | [5 empty] | 17SP | [6 empty] | 0.99062 | 0.9158 | 0.99738 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21122317SP |  |  | UNITED NO. 7 ROSE 69KV | S | WERE |  | SEAST |  |  | 533649 | UN7ROSE2 69.000 | [5 empty] | 17SP | [6 empty] | 0.98389 | 0.91592 | 0.9997 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12862317SP |  |  | TIOGA 69KV | S | WERE |  | SEAST |  |  | 533646 | TIOGA 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.98695 | 0.91602 | 1.00434 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21182317SP |  |  | ASH GROVE JCT1 69KV | S | WERE |  | SEAST |  |  | 533659 | ASHGRJ12 69.000 | [5 empty] | 17SP | [6 empty] | 0.99062 | 0.91639 | 0.99792 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21202317SP |  |  | CHANUTE GENERATION TAP 69KV | S | WERE |  | SEAST |  |  | 533661 | CGENTAP2 69.000 | [5 empty] | 17SP | [6 empty] | 0.99062 | 0.91656 | 0.99808 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12802317SP |  |  | ENA 69KV | S | WERE |  | SEAST |  |  | 533634 | ENA 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97937 | 0.91664 | 0.98667 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12762317SP |  |  | ARCO 69KV | S | WERE |  | SEAST |  |  | 533619 | ARCO 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97896 | 0.91669 | 0.98586 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12772317SP |  |  | ARCO TAP 69KV | S | WERE |  | SEAST |  |  | 533620 | ARCOTAP2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97911 | 0.91685 | 0.98601 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21172317SP |  |  | ASH GROVE2 69KV | S | WERE |  | SEAST |  |  | 533658 | ASHGRV22 69.000 | [5 empty] | 17SP | [6 empty] | 0.99026 | 0.91688 | 0.99866 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12832317SP |  |  | MONARCH 69KV | S | WERE |  | SEAST |  |  | 533641 | MONARCH2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97876 | 0.91731 | 0.98501 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21192317SP |  |  | ASH GROVE JCT2 69KV | S | WERE |  | SEAST |  |  | 533660 | ASHGRJ22 69.000 | [5 empty] | 17SP | [6 empty] | 0.99026 | 0.91747 | 0.99921 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21212317SP |  |  | CHANUTE GENERATION SUB 69KV | S | WERE |  | SEAST |  |  | 533662 | CGENSUB2 69.000 | [5 empty] | 17SP | [6 empty] | 0.99062 | 0.91839 | 0.99975 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21252317SP |  |  | CHANUTE TAP 69KV | S | WERE |  | SEAST |  |  | 533666 | CHANTAP2 69.000 | [5 empty] | 17SP | [6 empty] | 0.99096 | 0.92009 | 1.001 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21042317SP |  |  | ENA 69KV | S | WERE |  | SEAST |  |  | 533634 | ENA 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97991 | 0.92161 | 0.98667 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21002317SP |  |  | ARCO 69KV | S | WERE |  | SEAST |  |  | 533619 | ARCO 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97949 | 0.92164 | 0.98586 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21102317SP |  |  | TIOGA 69KV | S | WERE |  | SEAST |  |  | 533646 | TIOGA 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.9876 | 0.92168 | 1.00434 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21012317SP |  |  | ARCO TAP 69KV | S | WERE |  | SEAST |  |  | 533620 | ARCOTAP2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97964 | 0.9218 | 0.98601 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21072317SP |  |  | MONARCH 69KV | S | WERE |  | SEAST |  |  | 533641 | MONARCH2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97929 | 0.9222 | 0.98501 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12782317SP |  |  | ALLEN 69KV | S | WERE |  | SEAST |  |  | 533621 | ALLEN 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.98144 | 0.92452 | 0.98459 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21022317SP |  |  | ALLEN 69KV | S | WERE |  | SEAST |  |  | 533621 | ALLEN 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.98193 | 0.92916 | 0.98459 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V14972117SP |  |  | ATHENS SWITCHING STATION 69KV | S | WERE |  | SEAST |  |  | 533623 | ATHENS 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.99112 | 0.93108 | 0.99245 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V2122217SP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 17SP | [6 empty] | 0.95535 | 0.93316 | 0.96942 | 0.95 | 1.05 | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 1 | 2008-12-01 | 2007AG1AFS81V13373117SP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 17SP | [6 empty] | 0.98867 | 0.9335 | 0.96537 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 4 | 2008-12-01 | 2007AG1AFS81V19823417SP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 17SP | [6 empty] | 0.98545 | 0.93376 | 0.96537 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12872317SP |  |  | UNITED NO. 6 URBANA 69KV | S | WERE |  | SEAST |  |  | 533648 | UN6URBA2 69.000 | [5 empty] | 17SP | [6 empty] | 1.0044 | 0.9338 | 1.00954 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V2132217SP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 17SP | [6 empty] | 0.95682 | 0.9339 | 0.96907 | 0.95 | 1.05 | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V2142217SP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 17SP | [6 empty] | 0.95693 | 0.93401 | 0.96918 | 0.95 | 1.05 | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12892317SP |  |  | UNITED NO. 8 HUMBOLDT 69KV | S | WERE |  | SEAST |  |  | 533650 | UN8HUMB2 69.000 | [5 empty] | 17SP | [6 empty] | 0.98413 | 0.93422 | 0.98603 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12912317SP |  |  | ZILA JUNCTION 69KV | S | WERE |  | SEAST |  |  | 533654 | ZILAJCT2 69.000 | [5 empty] | 17SP | [6 empty] | 0.98725 | 0.9375 | 0.98914 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21132317SP |  |  | UNITED NO. 8 HUMBOLDT 69KV | S | WERE |  | SEAST |  |  | 533650 | UN8HUMB2 69.000 | [5 empty] | 17SP | [6 empty] | 0.98455 | 0.93815 | 0.98603 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21112317SP |  |  | UNITED NO. 6 URBANA 69KV | S | WERE |  | SEAST |  |  | 533648 | UN6URBA2 69.000 | [5 empty] | 17SP | [6 empty] | 1.0047 | 0.93939 | 1.00954 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21152317SP |  |  | ZILA JUNCTION 69KV | S | WERE |  | SEAST |  |  | 533654 | ZILAJCT2 69.000 | [5 empty] | 17SP | [6 empty] | 0.98766 | 0.94142 | 0.98914 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V20033317SP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 17SP | [6 empty] | 0.97016 | 0.94495 | 0.96581 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-19 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V11663317SP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 17SP | [6 empty] | 0.98445 | 0.94496 | 0.96565 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V11673317SP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 17SP | [6 empty] | 0.98455 | 0.94508 | 0.96576 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12742317SP |  |  | MARMTNE5 161KV | S | WERE |  | SEAST |  |  | 532934 | MARMTNE5 161.00 | [5 empty] | 17SP | [6 empty] | 0.99345 | 0.94916 | 0.98255 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ALLEN 69KV Capacitor | Allen 69 kV 15 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V5031408SH |  |  | ARGO 69KV | S | WERE |  | SEAST |  |  | 533675 | ARGO 2 69.000 | [5 empty] | 08SH | [6 empty] | 0.98993 | 0.93855 | 0.98604 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA (ALTOON3X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 533001 | ALTOONA4 138.00 | 533673 | ALTOO E2 69.000 | 533087 | ALTOO3 1 13.200 | 1 |  |  |  |  | WERE | ALTOONA EAST 69KV Capacitor | ALTOONA EAST 69KV 6 MVAR Capacitor Addition | [5 empty] | 18 | [6 empty] | 240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V5041408SH |  |  | CITY OF NEODESHA 69KV | S | WERE |  | SEAST |  |  | 533699 | NEODESH2 69.000 | [5 empty] | 08SH | [6 empty] | 0.98993 | 0.93855 | 0.98604 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA (ALTOON3X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 533001 | ALTOONA4 138.00 | 533673 | ALTOO E2 69.000 | 533087 | ALTOO3 1 13.200 | 1 |  |  |  |  | WERE | ALTOONA EAST 69KV Capacitor | ALTOONA EAST 69KV 6 MVAR Capacitor Addition | [5 empty] | 18 | [6 empty] | 240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 3 | 2008-12-01 | 2007AG1AFS81V3941308SH |  |  | ARGO 69KV | S | WERE |  | SEAST |  |  | 533675 | ARGO 2 69.000 | [5 empty] | 08SH | [6 empty] | 0.99356 | 0.94271 | 0.98448 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA EAST - NOEDESHA JUNCTION 69KV CKT 1 | 0 | 533673 | ALTOO E2 69.000 | 533700 | NEODJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALTOONA EAST 69KV Capacitor | ALTOONA EAST 69KV 6 MVAR Capacitor Addition | [5 empty] | 18 | [6 empty] | 240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 3 | 2008-12-01 | 2007AG1AFS81V3951308SH |  |  | CITY OF NEODESHA 69KV | S | WERE |  | SEAST |  |  | 533699 | NEODESH2 69.000 | [5 empty] | 08SH | [6 empty] | 0.99356 | 0.94271 | 0.98448 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA EAST - NOEDESHA JUNCTION 69KV CKT 1 | 0 | 533673 | ALTOO E2 69.000 | 533700 | NEODJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALTOONA EAST 69KV Capacitor | ALTOONA EAST 69KV 6 MVAR Capacitor Addition | [5 empty] | 18 | [6 empty] | 240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V5061408SH |  |  | RADIANT NO. 5 HIGH PRAIRIE 69KV | S | WERE |  | SEAST |  |  | 533706 | RA5HIPR2 69.000 | [5 empty] | 08SH | [6 empty] | 0.98936 | 0.94713 | 0.99981 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA (ALTOON3X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 533001 | ALTOONA4 138.00 | 533673 | ALTOO E2 69.000 | 533087 | ALTOO3 1 13.200 | 1 |  |  |  |  | WERE | ALTOONA EAST 69KV Capacitor | ALTOONA EAST 69KV 6 MVAR Capacitor Addition | [5 empty] | 18 | [6 empty] | 240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V5021408SH |  |  | ALTOONA EAST 69KV | S | WERE |  | SEAST |  |  | 533673 | ALTOO E2 69.000 | [5 empty] | 08SH | [6 empty] | 0.98937 | 0.94713 | 0.99982 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA (ALTOON3X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 533001 | ALTOONA4 138.00 | 533673 | ALTOO E2 69.000 | 533087 | ALTOO3 1 13.200 | 1 |  |  |  |  | WERE | ALTOONA EAST 69KV Capacitor | ALTOONA EAST 69KV 6 MVAR Capacitor Addition | [5 empty] | 18 | [6 empty] | 240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V5051408SH |  |  | NOEDESHA JUNCTION 69KV | S | WERE |  | SEAST |  |  | 533700 | NEODJCT2 69.000 | [5 empty] | 08SH | [6 empty] | 0.98989 | 0.94771 | 0.99475 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA (ALTOON3X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 533001 | ALTOONA4 138.00 | 533673 | ALTOO E2 69.000 | 533087 | ALTOO3 1 13.200 | 1 |  |  |  |  | WERE | ALTOONA EAST 69KV Capacitor | ALTOONA EAST 69KV 6 MVAR Capacitor Addition | [5 empty] | 18 | [6 empty] | 240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V7751408SP |  |  | ARGO 69KV | S | WERE |  | SEAST |  |  | 533675 | ARGO 2 69.000 | [5 empty] | 08SP | [6 empty] | 0.98415 | 0.9265 | 0.98278 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA (ALTOON3X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 533001 | ALTOONA4 138.00 | 533673 | ALTOO E2 69.000 | 533087 | ALTOO3 1 13.200 | 1 |  |  |  |  | WERE | ALTOONA EAST 69KV Capacitor | ALTOONA EAST 69KV 6 MVAR Capacitor Addition | [5 empty] | 18 | [6 empty] | 240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V7761408SP |  |  | CITY OF NEODESHA 69KV | S | WERE |  | SEAST |  |  | 533699 | NEODESH2 69.000 | [5 empty] | 08SP | [6 empty] | 0.98415 | 0.9265 | 0.98278 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA (ALTOON3X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 533001 | ALTOONA4 138.00 | 533673 | ALTOO E2 69.000 | 533087 | ALTOO3 1 13.200 | 1 |  |  |  |  | WERE | ALTOONA EAST 69KV Capacitor | ALTOONA EAST 69KV 6 MVAR Capacitor Addition | [5 empty] | 18 | [6 empty] | 240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V6421408SP |  |  | ARGO 69KV | S | WERE |  | SEAST |  |  | 533675 | ARGO 2 69.000 | [5 empty] | 08SP | [6 empty] | 0.98941 | 0.9329 | 0.98278 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA EAST - NOEDESHA JUNCTION 69KV CKT 1 | 0 | 533673 | ALTOO E2 69.000 | 533700 | NEODJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALTOONA EAST 69KV Capacitor | ALTOONA EAST 69KV 6 MVAR Capacitor Addition | [5 empty] | 18 | [6 empty] | 240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V6431408SP |  |  | CITY OF NEODESHA 69KV | S | WERE |  | SEAST |  |  | 533699 | NEODESH2 69.000 | [5 empty] | 08SP | [6 empty] | 0.98941 | 0.9329 | 0.98278 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA EAST - NOEDESHA JUNCTION 69KV CKT 1 | 0 | 533673 | ALTOO E2 69.000 | 533700 | NEODJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALTOONA EAST 69KV Capacitor | ALTOONA EAST 69KV 6 MVAR Capacitor Addition | [5 empty] | 18 | [6 empty] | 240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V7781408SP |  |  | RADIANT NO. 5 HIGH PRAIRIE 69KV | S | WERE |  | SEAST |  |  | 533706 | RA5HIPR2 69.000 | [5 empty] | 08SP | [6 empty] | 0.98338 | 0.93673 | 0.99934 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA (ALTOON3X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 533001 | ALTOONA4 138.00 | 533673 | ALTOO E2 69.000 | 533087 | ALTOO3 1 13.200 | 1 |  |  |  |  | WERE | ALTOONA EAST 69KV Capacitor | ALTOONA EAST 69KV 6 MVAR Capacitor Addition | [5 empty] | 18 | [6 empty] | 240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V7741408SP |  |  | ALTOONA EAST 69KV | S | WERE |  | SEAST |  |  | 533673 | ALTOO E2 69.000 | [5 empty] | 08SP | [6 empty] | 0.98338 | 0.93674 | 0.99935 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA (ALTOON3X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 533001 | ALTOONA4 138.00 | 533673 | ALTOO E2 69.000 | 533087 | ALTOO3 1 13.200 | 1 |  |  |  |  | WERE | ALTOONA EAST 69KV Capacitor | ALTOONA EAST 69KV 6 MVAR Capacitor Addition | [5 empty] | 18 | [6 empty] | 240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V7771408SP |  |  | NOEDESHA JUNCTION 69KV | S | WERE |  | SEAST |  |  | 533700 | NEODJCT2 69.000 | [5 empty] | 08SP | [6 empty] | 0.98411 | 0.93744 | 0.99308 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA (ALTOON3X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 533001 | ALTOONA4 138.00 | 533673 | ALTOO E2 69.000 | 533087 | ALTOO3 1 13.200 | 1 |  |  |  |  | WERE | ALTOONA EAST 69KV Capacitor | ALTOONA EAST 69KV 6 MVAR Capacitor Addition | [5 empty] | 18 | [6 empty] | 240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V6441408SP |  |  | NOEDESHA JUNCTION 69KV | S | WERE |  | SEAST |  |  | 533700 | NEODJCT2 69.000 | [5 empty] | 08SP | [6 empty] | 0.98936 | 0.94376 | 0.99308 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA EAST - NOEDESHA JUNCTION 69KV CKT 1 | 0 | 533673 | ALTOO E2 69.000 | 533700 | NEODJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALTOONA EAST 69KV Capacitor | ALTOONA EAST 69KV 6 MVAR Capacitor Addition | [5 empty] | 18 | [6 empty] | 240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V8052209SP |  |  | ARGO 69KV | S | WERE |  | SEAST |  |  | 533675 | ARGO 2 69.000 | [5 empty] | 09SP | [6 empty] | 0.98533 | 0.92573 | 0.98399 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA (ALTOON3X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 533001 | ALTOONA4 138.00 | 533673 | ALTOO E2 69.000 | 533087 | ALTOO3 1 13.200 | 1 |  |  |  |  | WERE | ALTOONA EAST 69KV Capacitor | ALTOONA EAST 69KV 6 MVAR Capacitor Addition | [5 empty] | 18 | [6 empty] | 240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V8062209SP |  |  | CITY OF NEODESHA 69KV | S | WERE |  | SEAST |  |  | 533699 | NEODESH2 69.000 | [5 empty] | 09SP | [6 empty] | 0.98533 | 0.92573 | 0.98399 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA (ALTOON3X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 533001 | ALTOONA4 138.00 | 533673 | ALTOO E2 69.000 | 533087 | ALTOO3 1 13.200 | 1 |  |  |  |  | WERE | ALTOONA EAST 69KV Capacitor | ALTOONA EAST 69KV 6 MVAR Capacitor Addition | [5 empty] | 18 | [6 empty] | 240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V6532209SP |  |  | ARGO 69KV | S | WERE |  | SEAST |  |  | 533675 | ARGO 2 69.000 | [5 empty] | 09SP | [6 empty] | 0.99051 | 0.93225 | 0.98399 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA EAST - NOEDESHA JUNCTION 69KV CKT 1 | 0 | 533673 | ALTOO E2 69.000 | 533700 | NEODJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALTOONA EAST 69KV Capacitor | ALTOONA EAST 69KV 6 MVAR Capacitor Addition | [5 empty] | 18 | [6 empty] | 240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V6542209SP |  |  | CITY OF NEODESHA 69KV | S | WERE |  | SEAST |  |  | 533699 | NEODESH2 69.000 | [5 empty] | 09SP | [6 empty] | 0.99051 | 0.93225 | 0.98399 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA EAST - NOEDESHA JUNCTION 69KV CKT 1 | 0 | 533673 | ALTOO E2 69.000 | 533700 | NEODJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALTOONA EAST 69KV Capacitor | ALTOONA EAST 69KV 6 MVAR Capacitor Addition | [5 empty] | 18 | [6 empty] | 240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V8082209SP |  |  | RADIANT NO. 5 HIGH PRAIRIE 69KV | S | WERE |  | SEAST |  |  | 533706 | RA5HIPR2 69.000 | [5 empty] | 09SP | [6 empty] | 0.9846 | 0.93605 | 1.00071 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA (ALTOON3X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 533001 | ALTOONA4 138.00 | 533673 | ALTOO E2 69.000 | 533087 | ALTOO3 1 13.200 | 1 |  |  |  |  | WERE | ALTOONA EAST 69KV Capacitor | ALTOONA EAST 69KV 6 MVAR Capacitor Addition | [5 empty] | 18 | [6 empty] | 240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V8042209SP |  |  | ALTOONA EAST 69KV | S | WERE |  | SEAST |  |  | 533673 | ALTOO E2 69.000 | [5 empty] | 09SP | [6 empty] | 0.98461 | 0.93606 | 1.00072 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA (ALTOON3X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 533001 | ALTOONA4 138.00 | 533673 | ALTOO E2 69.000 | 533087 | ALTOO3 1 13.200 | 1 |  |  |  |  | WERE | ALTOONA EAST 69KV Capacitor | ALTOONA EAST 69KV 6 MVAR Capacitor Addition | [5 empty] | 18 | [6 empty] | 240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V8072209SP |  |  | NOEDESHA JUNCTION 69KV | S | WERE |  | SEAST |  |  | 533700 | NEODJCT2 69.000 | [5 empty] | 09SP | [6 empty] | 0.98528 | 0.93677 | 0.99437 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA (ALTOON3X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 533001 | ALTOONA4 138.00 | 533673 | ALTOO E2 69.000 | 533087 | ALTOO3 1 13.200 | 1 |  |  |  |  | WERE | ALTOONA EAST 69KV Capacitor | ALTOONA EAST 69KV 6 MVAR Capacitor Addition | [5 empty] | 18 | [6 empty] | 240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V6552209SP |  |  | NOEDESHA JUNCTION 69KV | S | WERE |  | SEAST |  |  | 533700 | NEODJCT2 69.000 | [5 empty] | 09SP | [6 empty] | 0.99047 | 0.94321 | 0.99437 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA EAST - NOEDESHA JUNCTION 69KV CKT 1 | 0 | 533673 | ALTOO E2 69.000 | 533700 | NEODJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ALTOONA EAST 69KV Capacitor | ALTOONA EAST 69KV 6 MVAR Capacitor Addition | [5 empty] | 18 | [6 empty] | 240000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V3602108AP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08AP | [6 empty] | 1.0133 | 0.8986 | 0.94789 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V3622108AP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08AP | [6 empty] | 1.0133 | 0.9157 | 0.96407 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V3612108AP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08AP | [6 empty] | 1.0133 | 0.91888 | 0.96708 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V3531108AP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08AP | [6 empty] | 0.95794 | 0.92052 | 0.94425 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V4721108AP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08AP | [6 empty] | 0.95806 | 0.92058 | 0.94425 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81V1365508AP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08AP | [6 empty] | 0.94863 | 0.92418 | 0.94905 | 0.95 | 1.05 | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V3531208AP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08AP | [6 empty] | 0.99424 | 0.93133 | 0.95309 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V3561208AP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08AP | [6 empty] | 0.99421 | 0.93137 | 0.95309 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V3351208AP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 08AP | [6 empty] | 0.96678 | 0.94393 | 0.9833 | 0.95 | 1.05 | CATEGORYB | SINGLE | DEARING - MONTGOMERY 138KV CKT 1 | 0 | 533002 | DEARING4 138.00 | 533004 | MONTGOM4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V2862408AP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 08AP | [6 empty] | 0.97555 | 0.94533 | 0.97004 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V3361208AP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 08AP | [6 empty] | 0.96785 | 0.94533 | 0.98215 | 0.95 | 1.05 | CATEGORYB | SINGLE | DEARING - MONTGOMERY 138KV CKT 1 | 0 | 533002 | DEARING4 138.00 | 533004 | MONTGOM4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V3371208AP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 08AP | [6 empty] | 0.96788 | 0.94535 | 0.98217 | 0.95 | 1.05 | CATEGORYB | SINGLE | DEARING - MONTGOMERY 138KV CKT 1 | 0 | 533002 | DEARING4 138.00 | 533004 | MONTGOM4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V4052408AP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 08AP | [6 empty] | 0.97571 | 0.9456 | 0.97004 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V3541208AP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08AP | [6 empty] | 0.99421 | 0.9478 | 0.96918 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V3571208AP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08AP | [6 empty] | 0.99418 | 0.94784 | 0.96918 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V6063308FA |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08FA | [6 empty] | 0.99922 | 0.87127 | 0.94183 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V6083308FA |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08FA | [6 empty] | 0.99919 | 0.88942 | 0.95853 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V6073308FA |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08FA | [6 empty] | 0.99942 | 0.89294 | 0.96177 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V3154408FA |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08FA | [6 empty] | 0.9635 | 0.92212 | 0.95452 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V3434108FA |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08FA | [6 empty] | 0.98653 | 0.92213 | 0.9442 | 0.95 | 1.05 | CATEGORYB | SINGLE | ARCO TAP - ENA 69KV CKT 1 | 0 | 533634 | ENA 2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V3164408FA |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08FA | [6 empty] | 0.96385 | 0.92253 | 0.95452 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V3001108FA |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08FA | [6 empty] | 0.97138 | 0.92255 | 0.95449 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81V6403208FA |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08FA | [6 empty] | 0.98865 | 0.92277 | 0.94289 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V3454108FA |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08FA | [6 empty] | 0.98651 | 0.93919 | 0.96086 | 0.95 | 1.05 | CATEGORYB | SINGLE | ARCO TAP - ENA 69KV CKT 1 | 0 | 533634 | ENA 2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V6172208FA |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08FA | [6 empty] | 0.98582 | 0.93987 | 0.96001 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V3144408FA |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 08FA | [6 empty] | 0.99563 | 0.94239 | 0.9779 | 0.95 | 1.05 | CATEGORYB | SINGLE | ATHENS SWITCHING STATION - OWL CREEK 69KV CKT 1 | 0 | 533623 | ATHENS 2 69.000 | 533642 | OWL CRK2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V3444108FA |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08FA | [6 empty] | 0.98673 | 0.9425 | 0.9641 | 0.95 | 1.05 | CATEGORYB | SINGLE | ARCO TAP - ENA 69KV CKT 1 | 0 | 533634 | ENA 2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V6162208FA |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08FA | [6 empty] | 0.98605 | 0.94318 | 0.96324 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V2744408FA |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 08FA | [6 empty] | 0.98469 | 0.94579 | 0.97556 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V4794408FA |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 08FA | [6 empty] | 0.98311 | 0.94602 | 0.97556 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V1541408G |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08G | [6 empty] | 0.99837 | 0.87792 | 0.9443 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V1561408G |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08G | [6 empty] | 0.99834 | 0.89541 | 0.96054 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V1551408G |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08G | [6 empty] | 0.99857 | 0.89881 | 0.9637 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V1351108G |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08G | [6 empty] | 0.95625 | 0.91484 | 0.94864 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V1981108G |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08G | [6 empty] | 0.9568 | 0.91537 | 0.94864 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V1591408G |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08G | [6 empty] | 0.95217 | 0.91965 | 0.94887 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V1791108G |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08G | [6 empty] | 0.98612 | 0.92338 | 0.94374 | 0.95 | 1.05 | CATEGORYB | SINGLE | ENA - TIOGA 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V1601408G |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08G | [6 empty] | 0.98548 | 0.92382 | 0.9443 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V1361108G |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 08G | [6 empty] | 0.97037 | 0.93744 | 0.97027 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V1851408G |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 08G | [6 empty] | 0.96997 | 0.93817 | 0.96979 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V1621408G |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08G | [6 empty] | 0.98545 | 0.94042 | 0.96054 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V2532308G |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08G | [6 empty] | 0.98671 | 0.94056 | 0.96233 | 0.95 | 1.05 | CATEGORYB | SINGLE | ARCO TAP - ENA 69KV CKT 1 | 0 | 533634 | ENA 2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V1781108G |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 08G | [6 empty] | 0.99364 | 0.94316 | 0.97873 | 0.95 | 1.05 | CATEGORYB | SINGLE | ATHENS SWITCHING STATION - OWL CREEK 69KV CKT 1 | 0 | 533623 | ATHENS 2 69.000 | 533642 | OWL CRK2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V1611408G |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08G | [6 empty] | 0.98568 | 0.94365 | 0.9637 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V2522308G |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08G | [6 empty] | 0.98694 | 0.94378 | 0.96549 | 0.95 | 1.05 | CATEGORYB | SINGLE | ARCO TAP - ENA 69KV CKT 1 | 0 | 533634 | ENA 2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 3 | 2008-12-01 | 2007AG1AFS81V3731308SH |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08SH | [6 empty] | 0.99621 | 0.86184 | 0.9398 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 3 | 2008-12-01 | 2007AG1AFS81V3761308SH |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08SH | [6 empty] | 0.99618 | 0.8804 | 0.95673 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 3 | 2008-12-01 | 2007AG1AFS81V3741308SH |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08SH | [6 empty] | 0.99647 | 0.88407 | 0.96008 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V2831108SH |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08SH | [6 empty] | 0.94857 | 0.91022 | 0.94459 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V4841108SH |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08SH | [6 empty] | 0.94875 | 0.91028 | 0.94459 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V4201108SH |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08SH | [6 empty] | 0.95384 | 0.91473 | 0.94459 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V4021408SH |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08SH | [6 empty] | 0.98421 | 0.91607 | 0.93991 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V4061408SH |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08SH | [6 empty] | 0.98506 | 0.91684 | 0.93991 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V2841108SH |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 08SH | [6 empty] | 0.96242 | 0.93044 | 0.9679 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V4851108SH |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 08SH | [6 empty] | 0.96279 | 0.9307 | 0.9679 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V3361408SH |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 08SH | [6 empty] | 0.9582 | 0.93193 | 0.97651 | 0.95 | 1.05 | CATEGORYB | SINGLE | DEARING - MONTGOMERY 138KV CKT 1 | 0 | 533002 | DEARING4 138.00 | 533004 | MONTGOM4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V3371408SH |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 08SH | [6 empty] | 0.95919 | 0.93312 | 0.97499 | 0.95 | 1.05 | CATEGORYB | SINGLE | DEARING - MONTGOMERY 138KV CKT 1 | 0 | 533002 | DEARING4 138.00 | 533004 | MONTGOM4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V3381408SH |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 08SH | [6 empty] | 0.95926 | 0.9332 | 0.97506 | 0.95 | 1.05 | CATEGORYB | SINGLE | DEARING - MONTGOMERY 138KV CKT 1 | 0 | 533002 | DEARING4 138.00 | 533004 | MONTGOM4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V4041408SH |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08SH | [6 empty] | 0.98418 | 0.93345 | 0.95684 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V4081408SH |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08SH | [6 empty] | 0.98503 | 0.9342 | 0.95684 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V4211108SH |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 08SH | [6 empty] | 0.96848 | 0.93597 | 0.9679 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V4031408SH |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08SH | [6 empty] | 0.98448 | 0.93689 | 0.96019 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V4071408SH |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08SH | [6 empty] | 0.98533 | 0.93763 | 0.96019 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V4432308SH |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 08SH | [6 empty] | 0.96573 | 0.94072 | 0.97111 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V4442308SH |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 08SH | [6 empty] | 0.9658 | 0.94079 | 0.97118 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V4412308SH |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 08SH | [6 empty] | 0.96534 | 0.94142 | 0.97197 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 3 | 2008-12-01 | 2007AG1AFS81V3751308SH |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 08SH | [6 empty] | 1.001 | 0.94363 | 0.97647 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V5632108SP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08SP | [6 empty] | 0.99181 | 0.80904 | 0.92862 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V5662108SP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08SP | [6 empty] | 0.99178 | 0.83233 | 0.94881 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V5642108SP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08SP | [6 empty] | 0.99213 | 0.83693 | 0.95281 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V6412408SP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08SP | [6 empty] | 0.98111 | 0.89687 | 0.92889 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V6492408SP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08SP | [6 empty] | 0.98184 | 0.8978 | 0.92889 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V6741108SP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.94537 | 0.90732 | 0.93288 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V5191408SP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.95007 | 0.90782 | 0.93661 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V8171408SP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.94595 | 0.90788 | 0.93661 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V5652108SP |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 08SP | [6 empty] | 0.99755 | 0.91193 | 0.97173 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V6452408SP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08SP | [6 empty] | 0.98108 | 0.91778 | 0.94907 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V6522408SP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08SP | [6 empty] | 0.98182 | 0.91869 | 0.94907 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V6422408SP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08SP | [6 empty] | 0.98143 | 0.92192 | 0.95306 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V6502408SP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08SP | [6 empty] | 0.98217 | 0.92282 | 0.95306 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V6751108SP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 08SP | [6 empty] | 0.95906 | 0.92502 | 0.95977 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V5201408SP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 08SP | [6 empty] | 0.96363 | 0.92682 | 0.96213 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V8181408SP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 08SP | [6 empty] | 0.96041 | 0.92697 | 0.96213 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V5622108SP |  |  | ATHENS SWITCHING STATION 69KV | S | WERE |  | SEAST |  |  | 533623 | ATHENS 2 69.000 | [5 empty] | 08SP | [6 empty] | 0.99907 | 0.93047 | 0.97668 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V7612308SP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.96101 | 0.93257 | 0.97246 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V7622308SP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 08SP | [6 empty] | 0.96109 | 0.93265 | 0.97254 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V7592308SP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 08SP | [6 empty] | 0.96115 | 0.93377 | 0.97397 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V6442408SP |  |  | UNITED NO. 8 HUMBOLDT 69KV | S | WERE |  | SEAST |  |  | 533650 | UN8HUMB2 69.000 | [5 empty] | 08SP | [6 empty] | 0.97317 | 0.93955 | 0.98621 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V7572308SP |  |  | DEARING 138KV | S | WERE |  | SEAST |  |  | 533002 | DEARING4 138.00 | [5 empty] | 08SP | [6 empty] | 0.96349 | 0.94071 | 0.98072 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V6512408SP |  |  | UNITED NO. 8 HUMBOLDT 69KV | S | WERE |  | SEAST |  |  | 533650 | UN8HUMB2 69.000 | [5 empty] | 08SP | [6 empty] | 0.97423 | 0.94079 | 0.98621 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V6432408SP |  |  | UNITED NO. 1 ELSMORE 69KV | S | WERE |  | SEAST |  |  | 533647 | UN1ELSM2 69.000 | [5 empty] | 08SP | [6 empty] | 0.97597 | 0.94244 | 1.00474 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V6462408SP |  |  | ZILA JUNCTION 69KV | S | WERE |  | SEAST |  |  | 533654 | ZILAJCT2 69.000 | [5 empty] | 08SP | [6 empty] | 0.97632 | 0.94281 | 0.98932 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V4901108SP |  |  | NORTHEAST PARSONS 138KV | S | WERE |  | SEAST |  |  | 533005 | NEPARSN4 138.00 | [5 empty] | 08SP | [6 empty] | 0.98296 | 0.94298 | 0.98661 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533021 | NEOSHO 4 138.00 | 533005 | NEPARSN4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V5402208SP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.97056 | 0.94335 | 0.97494 | 0.95 | 1.05 | CATEGORYB | SINGLE | DEARING - MONTGOMERY 138KV CKT 1 | 0 | 533002 | DEARING4 138.00 | 533004 | MONTGOM4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V5412208SP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 08SP | [6 empty] | 0.97064 | 0.94344 | 0.97502 | 0.95 | 1.05 | CATEGORYB | SINGLE | DEARING - MONTGOMERY 138KV CKT 1 | 0 | 533002 | DEARING4 138.00 | 533004 | MONTGOM4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V5392208SP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 08SP | [6 empty] | 0.97079 | 0.94361 | 0.97683 | 0.95 | 1.05 | CATEGORYB | SINGLE | DEARING - MONTGOMERY 138KV CKT 1 | 0 | 533002 | DEARING4 138.00 | 533004 | MONTGOM4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V6532408SP |  |  | ZILA JUNCTION 69KV | S | WERE |  | SEAST |  |  | 533654 | ZILAJCT2 69.000 | [5 empty] | 08SP | [6 empty] | 0.97738 | 0.94405 | 0.98932 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V8812208SP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.9718 | 0.94506 | 0.97494 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-20 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V8822208SP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 08SP | [6 empty] | 0.97188 | 0.94515 | 0.97502 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-20 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V6402408SP |  |  | ALLEN 69KV | S | WERE |  | SEAST |  |  | 533621 | ALLEN 2 69.000 | [5 empty] | 08SP | [6 empty] | 0.97867 | 0.94527 | 0.98256 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V6482408SP |  |  | ALLEN 69KV | S | WERE |  | SEAST |  |  | 533621 | ALLEN 2 69.000 | [5 empty] | 08SP | [6 empty] | 0.97959 | 0.94634 | 0.98256 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V6891108SP |  |  | UNITED NO. 8 HUMBOLDT 69KV | S | WERE |  | SEAST |  |  | 533650 | UN8HUMB2 69.000 | [5 empty] | 08SP | [6 empty] | 0.97446 | 0.94847 | 0.98523 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V1211408WP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08WP | [6 empty] | 1.0023 | 0.87229 | 0.94225 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V1231408WP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08WP | [6 empty] | 1.0023 | 0.89035 | 0.95894 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V1221408WP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08WP | [6 empty] | 1.0025 | 0.89388 | 0.9622 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 1 | 2008-12-01 | 2007AG1AFS81V1433108WP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08WP | [6 empty] | 0.98507 | 0.92126 | 0.94257 | 0.95 | 1.05 | CATEGORYB | SINGLE | ENA - TIOGA 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V1642108WP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08WP | [6 empty] | 0.98626 | 0.92165 | 0.94214 | 0.95 | 1.05 | CATEGORYB | SINGLE | ARCO TAP - ENA 69KV CKT 1 | 0 | 533634 | ENA 2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V1384108WP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08WP | [6 empty] | 0.96856 | 0.92242 | 0.95455 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V1261408WP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08WP | [6 empty] | 0.96145 | 0.92283 | 0.95476 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V1271408WP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08WP | [6 empty] | 0.9617 | 0.92312 | 0.95476 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 1 | 2008-12-01 | 2007AG1AFS81V1453108WP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08WP | [6 empty] | 0.98504 | 0.93834 | 0.95926 | 0.95 | 1.05 | CATEGORYB | SINGLE | ENA - TIOGA 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V1662108WP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08WP | [6 empty] | 0.98624 | 0.93872 | 0.95884 | 0.95 | 1.05 | CATEGORYB | SINGLE | ARCO TAP - ENA 69KV CKT 1 | 0 | 533634 | ENA 2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 1 | 2008-12-01 | 2007AG1AFS81V1443108WP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08WP | [6 empty] | 0.98529 | 0.94167 | 0.96252 | 0.95 | 1.05 | CATEGORYB | SINGLE | ENA - TIOGA 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V1652108WP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08WP | [6 empty] | 0.98649 | 0.94205 | 0.9621 | 0.95 | 1.05 | CATEGORYB | SINGLE | ARCO TAP - ENA 69KV CKT 1 | 0 | 533634 | ENA 2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 1 | 2008-12-01 | 2007AG1AFS81V1423108WP |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 08WP | [6 empty] | 0.99825 | 0.94323 | 0.97902 | 0.95 | 1.05 | CATEGORYB | SINGLE | ATHENS SWITCHING STATION - OWL CREEK 69KV CKT 1 | 0 | 533623 | ATHENS 2 69.000 | 533642 | OWL CRK2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V1394108WP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 08WP | [6 empty] | 0.98252 | 0.94609 | 0.9771 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V2304108WP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 08WP | [6 empty] | 0.98063 | 0.94821 | 0.9771 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V5831409SP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 09SP | [6 empty] | 0.99267 | 0.80256 | 0.92634 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V5871409SP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 09SP | [6 empty] | 0.99264 | 0.82642 | 0.94695 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V5841409SP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 09SP | [6 empty] | 0.99299 | 0.83114 | 0.95103 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5894409SP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 09SP | [6 empty] | 0.98089 | 0.89457 | 0.92826 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5974409SP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 09SP | [6 empty] | 0.98165 | 0.89554 | 0.92826 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V7134109SP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 09SP | [6 empty] | 0.93638 | 0.90346 | 0.92884 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V8342109SP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 09SP | [6 empty] | 0.93998 | 0.9043 | 0.93181 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V5452109SP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 09SP | [6 empty] | 0.93942 | 0.90466 | 0.93181 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V5851409SP |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 09SP | [6 empty] | 0.99796 | 0.90811 | 0.96948 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5934409SP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 09SP | [6 empty] | 0.98086 | 0.91593 | 0.94883 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V6004409SP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 09SP | [6 empty] | 0.98162 | 0.91687 | 0.94883 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V7144109SP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 09SP | [6 empty] | 0.95069 | 0.9187 | 0.95683 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5904409SP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 09SP | [6 empty] | 0.98121 | 0.92015 | 0.9529 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5984409SP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 09SP | [6 empty] | 0.98198 | 0.92109 | 0.9529 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V8352109SP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 09SP | [6 empty] | 0.9548 | 0.92237 | 0.95863 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V5462109SP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 09SP | [6 empty] | 0.95412 | 0.92294 | 0.95863 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8872309SP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 09SP | [6 empty] | 0.95426 | 0.92539 | 0.96836 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8882309SP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 09SP | [6 empty] | 0.95435 | 0.92548 | 0.96844 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8852309SP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 09SP | [6 empty] | 0.95427 | 0.92624 | 0.96964 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V5821409SP |  |  | ATHENS SWITCHING STATION 69KV | S | WERE |  | SEAST |  |  | 533623 | ATHENS 2 69.000 | [5 empty] | 09SP | [6 empty] | 0.99942 | 0.92714 | 0.97442 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8832309SP |  |  | DEARING 138KV | S | WERE |  | SEAST |  |  | 533002 | DEARING4 138.00 | [5 empty] | 09SP | [6 empty] | 0.95631 | 0.93232 | 0.97588 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V5404109SP |  |  | NORTHEAST PARSONS 138KV | S | WERE |  | SEAST |  |  | 533005 | NEPARSN4 138.00 | [5 empty] | 09SP | [6 empty] | 0.97987 | 0.9377 | 0.98649 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533021 | NEOSHO 4 138.00 | 533005 | NEPARSN4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5924409SP |  |  | UNITED NO. 8 HUMBOLDT 69KV | S | WERE |  | SEAST |  |  | 533650 | UN8HUMB2 69.000 | [5 empty] | 09SP | [6 empty] | 0.97298 | 0.93836 | 0.98616 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5994409SP |  |  | UNITED NO. 8 HUMBOLDT 69KV | S | WERE |  | SEAST |  |  | 533650 | UN8HUMB2 69.000 | [5 empty] | 09SP | [6 empty] | 0.97408 | 0.93964 | 0.98616 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5384409SP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 09SP | [6 empty] | 0.97014 | 0.94085 | 0.97185 | 0.95 | 1.05 | CATEGORYB | SINGLE | DEARING - MONTGOMERY 138KV CKT 1 | 0 | 533002 | DEARING4 138.00 | 533004 | MONTGOM4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5394409SP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 09SP | [6 empty] | 0.97022 | 0.94094 | 0.97193 | 0.95 | 1.05 | CATEGORYB | SINGLE | DEARING - MONTGOMERY 138KV CKT 1 | 0 | 533002 | DEARING4 138.00 | 533004 | MONTGOM4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5374409SP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 09SP | [6 empty] | 0.97041 | 0.94114 | 0.97395 | 0.95 | 1.05 | CATEGORYB | SINGLE | DEARING - MONTGOMERY 138KV CKT 1 | 0 | 533002 | DEARING4 138.00 | 533004 | MONTGOM4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5914409SP |  |  | UNITED NO. 1 ELSMORE 69KV | S | WERE |  | SEAST |  |  | 533647 | UN1ELSM2 69.000 | [5 empty] | 09SP | [6 empty] | 0.97577 | 0.94125 | 1.00421 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5944409SP |  |  | ZILA JUNCTION 69KV | S | WERE |  | SEAST |  |  | 533654 | ZILAJCT2 69.000 | [5 empty] | 09SP | [6 empty] | 0.97613 | 0.94163 | 0.98927 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V6014409SP |  |  | ZILA JUNCTION 69KV | S | WERE |  | SEAST |  |  | 533654 | ZILAJCT2 69.000 | [5 empty] | 09SP | [6 empty] | 0.97723 | 0.9429 | 0.98927 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5884409SP |  |  | ALLEN 69KV | S | WERE |  | SEAST |  |  | 533621 | ALLEN 2 69.000 | [5 empty] | 09SP | [6 empty] | 0.97849 | 0.9441 | 0.98284 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5964409SP |  |  | ALLEN 69KV | S | WERE |  | SEAST |  |  | 533621 | ALLEN 2 69.000 | [5 empty] | 09SP | [6 empty] | 0.97943 | 0.9452 | 0.98284 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V7902409SP |  |  | UNITED NO. 8 HUMBOLDT 69KV | S | WERE |  | SEAST |  |  | 533650 | UN8HUMB2 69.000 | [5 empty] | 09SP | [6 empty] | 0.97478 | 0.94705 | 0.98465 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V9942309SP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 09SP | [6 empty] | 0.96845 | 0.94773 | 0.96964 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V5861409SP |  |  | ORCHARD 69KV | S | WERE |  | SEAST |  |  | 533643 | ORCHARD2 69.000 | [5 empty] | 09SP | [6 empty] | 1.0014 | 0.94866 | 0.98299 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1503309WP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 09WP | [6 empty] | 0.99737 | 0.87101 | 0.94188 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1523309WP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 09WP | [6 empty] | 0.99734 | 0.88906 | 0.95855 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1513309WP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 09WP | [6 empty] | 0.9976 | 0.8926 | 0.96182 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V1594109WP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 09WP | [6 empty] | 0.9636 | 0.91758 | 0.95107 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 4 | 2008-12-01 | 2007AG1AFS81V1063409WP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 09WP | [6 empty] | 0.96419 | 0.91899 | 0.95082 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V1162409WP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 09WP | [6 empty] | 0.95983 | 0.92166 | 0.95281 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V1172409WP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 09WP | [6 empty] | 0.98648 | 0.92199 | 0.94308 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V1212409WP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 09WP | [6 empty] | 0.98738 | 0.92242 | 0.94308 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V1192409WP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 09WP | [6 empty] | 0.98646 | 0.93903 | 0.95973 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V1232409WP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 09WP | [6 empty] | 0.98735 | 0.93945 | 0.95973 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V1724409WP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 09WP | [6 empty] | 0.97866 | 0.94093 | 0.97431 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V1182409WP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 09WP | [6 empty] | 0.98672 | 0.94237 | 0.963 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 4 | 2008-12-01 | 2007AG1AFS81V1073409WP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 09WP | [6 empty] | 0.97799 | 0.94251 | 0.97352 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V1222409WP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 09WP | [6 empty] | 0.98762 | 0.94279 | 0.963 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V8961112SP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.56419 | 0.94109 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9031112SP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.58308 | 0.95815 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12491112SP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.58852 | 0.95815 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9171112SP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.60886 | 0.97512 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9081112SP |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.61007 | 0.99865 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9001112SP |  |  | ATHENS SWITCHING STATION 69KV | S | WERE |  | SEAST |  |  | 533623 | ATHENS 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.61276 | 1.00456 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9041112SP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.61412 | 0.97857 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12631112SP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.61425 | 0.97512 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12541112SP |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.61573 | 0.99865 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9091112SP |  |  | ORCHARD 69KV | S | WERE |  | SEAST |  |  | 533643 | ORCHARD2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.61729 | 1.00395 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12461112SP |  |  | ATHENS SWITCHING STATION 69KV | S | WERE |  | SEAST |  |  | 533623 | ATHENS 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.61848 | 1.00456 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12501112SP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.6195 | 0.97857 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9271112SP |  |  | CHANUTE PLANT3 69KV | S | WERE |  | SEAST |  |  | 533665 | CHANP3 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.62259 | 0.9955 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9251112SP |  |  | CHANUTE PLANT1 69KV | S | WERE |  | SEAST |  |  | 533663 | CHANP1 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.62293 | 0.99572 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9261112SP |  |  | CHANUTE PLANT2 69KV | S | WERE |  | SEAST |  |  | 533664 | CHANP2 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.62293 | 0.99572 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12551112SP |  |  | ORCHARD 69KV | S | WERE |  | SEAST |  |  | 533643 | ORCHARD2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.62303 | 1.00395 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9191112SP |  |  | ASH GROVE1 69KV | S | WERE |  | SEAST |  |  | 533657 | ASHGRV12 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.62622 | 0.99784 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9151112SP |  |  | UNITED NO. 7 ROSE 69KV | S | WERE |  | SEAST |  |  | 533649 | UN7ROSE2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.6268 | 1.00579 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9211112SP |  |  | ASH GROVE JCT1 69KV | S | WERE |  | SEAST |  |  | 533659 | ASHGRJ12 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.62699 | 0.99833 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9231112SP |  |  | CHANUTE GENERATION TAP 69KV | S | WERE |  | SEAST |  |  | 533661 | CGENTAP2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.62722 | 0.99848 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9201112SP |  |  | ASH GROVE2 69KV | S | WERE |  | SEAST |  |  | 533658 | ASHGRV22 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.62751 | 0.99949 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9221112SP |  |  | ASH GROVE JCT2 69KV | S | WERE |  | SEAST |  |  | 533660 | ASHGRJ22 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.62828 | 0.99998 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12731112SP |  |  | CHANUTE PLANT3 69KV | S | WERE |  | SEAST |  |  | 533665 | CHANP3 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.62832 | 0.9955 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12711112SP |  |  | CHANUTE PLANT1 69KV | S | WERE |  | SEAST |  |  | 533663 | CHANP1 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.62866 | 0.99572 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12721112SP |  |  | CHANUTE PLANT2 69KV | S | WERE |  | SEAST |  |  | 533664 | CHANP2 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.62866 | 0.99572 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9241112SP |  |  | CHANUTE GENERATION SUB 69KV | S | WERE |  | SEAST |  |  | 533662 | CGENSUB2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.62959 | 1.0 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9281112SP |  |  | CHANUTE TAP 69KV | S | WERE |  | SEAST |  |  | 533666 | CHANTAP2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.63161 | 1.00181 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12651112SP |  |  | ASH GROVE1 69KV | S | WERE |  | SEAST |  |  | 533657 | ASHGRV12 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.63193 | 0.99784 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12611112SP |  |  | UNITED NO. 7 ROSE 69KV | S | WERE |  | SEAST |  |  | 533649 | UN7ROSE2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.63254 | 1.00579 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12671112SP |  |  | ASH GROVE JCT1 69KV | S | WERE |  | SEAST |  |  | 533659 | ASHGRJ12 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.63269 | 0.99833 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12691112SP |  |  | CHANUTE GENERATION TAP 69KV | S | WERE |  | SEAST |  |  | 533661 | CGENTAP2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.63292 | 0.99848 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12661112SP |  |  | ASH GROVE2 69KV | S | WERE |  | SEAST |  |  | 533658 | ASHGRV22 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.63323 | 0.99949 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12681112SP |  |  | ASH GROVE JCT2 69KV | S | WERE |  | SEAST |  |  | 533660 | ASHGRJ22 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.63399 | 0.99998 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9121112SP |  |  | TIOGA 69KV | S | WERE |  | SEAST |  |  | 533646 | TIOGA 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.63506 | 1.0078 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12701112SP |  |  | CHANUTE GENERATION SUB 69KV | S | WERE |  | SEAST |  |  | 533662 | CGENSUB2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.63529 | 1.0 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12741112SP |  |  | CHANUTE TAP 69KV | S | WERE |  | SEAST |  |  | 533666 | CHANTAP2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.6373 | 1.00181 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12581112SP |  |  | TIOGA 69KV | S | WERE |  | SEAST |  |  | 533646 | TIOGA 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.64078 | 1.0078 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9141112SP |  |  | UNITED NO. 6 URBANA 69KV | S | WERE |  | SEAST |  |  | 533648 | UN6URBA2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.65044 | 1.01031 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V10972412SP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 12SP | [6 empty] | 0.97877 | 0.65045 | 0.94092 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9011112SP |  |  | ENA 69KV | S | WERE |  | SEAST |  |  | 533634 | ENA 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.65276 | 0.9995 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V8971112SP |  |  | ARCO 69KV | S | WERE |  | SEAST |  |  | 533619 | ARCO 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.65372 | 0.99907 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V8981112SP |  |  | ARCO TAP 69KV | S | WERE |  | SEAST |  |  | 533620 | ARCOTAP2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.65392 | 0.9992 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12601112SP |  |  | UNITED NO. 6 URBANA 69KV | S | WERE |  | SEAST |  |  | 533648 | UN6URBA2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.65597 | 1.01031 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9071112SP |  |  | MONARCH 69KV | S | WERE |  | SEAST |  |  | 533641 | MONARCH2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.65598 | 0.99879 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12471112SP |  |  | ENA 69KV | S | WERE |  | SEAST |  |  | 533634 | ENA 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.65809 | 0.9995 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12431112SP |  |  | ARCO 69KV | S | WERE |  | SEAST |  |  | 533619 | ARCO 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.65904 | 0.99907 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12441112SP |  |  | ARCO TAP 69KV | S | WERE |  | SEAST |  |  | 533620 | ARCOTAP2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.65924 | 0.9992 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12531112SP |  |  | MONARCH 69KV | S | WERE |  | SEAST |  |  | 533641 | MONARCH2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.66126 | 0.99879 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9291112SP |  |  | CITY OF ERIE 69KV | S | WERE |  | SEAST |  |  | 533760 | ERIE 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.67095 | 1.02 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V8991112SP |  |  | ALLEN 69KV | S | WERE |  | SEAST |  |  | 533621 | ALLEN 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.67363 | 1.00104 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12751112SP |  |  | CITY OF ERIE 69KV | S | WERE |  | SEAST |  |  | 533760 | ERIE 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.67632 | 1.02 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12451112SP |  |  | ALLEN 69KV | S | WERE |  | SEAST |  |  | 533621 | ALLEN 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.67868 | 1.00104 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11072412SP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 12SP | [6 empty] | 0.97874 | 0.68133 | 0.96239 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V10982412SP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 12SP | [6 empty] | 0.97911 | 0.68744 | 0.96663 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11062412SP |  |  | UNITED NO. 8 HUMBOLDT 69KV | S | WERE |  | SEAST |  |  | 533650 | UN8HUMB2 69.000 | [5 empty] | 12SP | [6 empty] | 0.9709 | 0.71327 | 0.99719 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11032412SP |  |  | UNITED NO. 1 ELSMORE 69KV | S | WERE |  | SEAST |  |  | 533647 | UN1ELSM2 69.000 | [5 empty] | 12SP | [6 empty] | 0.97368 | 0.717 | 1.01321 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9161112SP |  |  | UNITED NO. 8 HUMBOLDT 69KV | S | WERE |  | SEAST |  |  | 533650 | UN8HUMB2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.71715 | 0.99944 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11082412SP |  |  | ZILA JUNCTION 69KV | S | WERE |  | SEAST |  |  | 533654 | ZILAJCT2 69.000 | [5 empty] | 12SP | [6 empty] | 0.97406 | 0.71761 | 1.00027 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V10942412SP |  |  | ALLEN 69KV | S | WERE |  | SEAST |  |  | 533621 | ALLEN 2 69.000 | [5 empty] | 12SP | [6 empty] | 0.97643 | 0.72105 | 0.9963 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9181112SP |  |  | ZILA JUNCTION 69KV | S | WERE |  | SEAST |  |  | 533654 | ZILAJCT2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.72146 | 1.00251 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12621112SP |  |  | UNITED NO. 8 HUMBOLDT 69KV | S | WERE |  | SEAST |  |  | 533650 | UN8HUMB2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.72148 | 0.99944 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12641112SP |  |  | ZILA JUNCTION 69KV | S | WERE |  | SEAST |  |  | 533654 | ZILAJCT2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.72576 | 1.00251 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V10992412SP |  |  | MONARCH 69KV | S | WERE |  | SEAST |  |  | 533641 | MONARCH2 69.000 | [5 empty] | 12SP | [6 empty] | 0.97891 | 0.72923 | 0.99397 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V10922412SP |  |  | ARCO 69KV | S | WERE |  | SEAST |  |  | 533619 | ARCO 2 69.000 | [5 empty] | 12SP | [6 empty] | 0.98021 | 0.73208 | 0.99424 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V10932412SP |  |  | ARCO TAP 69KV | S | WERE |  | SEAST |  |  | 533620 | ARCOTAP2 69.000 | [5 empty] | 12SP | [6 empty] | 0.98034 | 0.73226 | 0.99438 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11002412SP |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 12SP | [6 empty] | 0.98913 | 0.73409 | 0.98839 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V10962412SP |  |  | ENA 69KV | S | WERE |  | SEAST |  |  | 533634 | ENA 2 69.000 | [5 empty] | 12SP | [6 empty] | 0.98128 | 0.73421 | 0.99467 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V10952412SP |  |  | ATHENS SWITCHING STATION 69KV | S | WERE |  | SEAST |  |  | 533623 | ATHENS 2 69.000 | [5 empty] | 12SP | [6 empty] | 0.99162 | 0.74577 | 0.99487 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11012412SP |  |  | ORCHARD 69KV | S | WERE |  | SEAST |  |  | 533643 | ORCHARD2 69.000 | [5 empty] | 12SP | [6 empty] | 0.99464 | 0.75613 | 0.99581 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11172412SP |  |  | CHANUTE PLANT3 69KV | S | WERE |  | SEAST |  |  | 533665 | CHANP3 2 69.000 | [5 empty] | 12SP | [6 empty] | 1.0056 | 0.76372 | 0.98304 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11152412SP |  |  | CHANUTE PLANT1 69KV | S | WERE |  | SEAST |  |  | 533663 | CHANP1 2 69.000 | [5 empty] | 12SP | [6 empty] | 1.0056 | 0.76401 | 0.98327 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11162412SP |  |  | CHANUTE PLANT2 69KV | S | WERE |  | SEAST |  |  | 533664 | CHANP2 2 69.000 | [5 empty] | 12SP | [6 empty] | 1.0056 | 0.76402 | 0.98327 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11192412SP |  |  | CITY OF ERIE 69KV | S | WERE |  | SEAST |  |  | 533760 | ERIE 2 69.000 | [5 empty] | 12SP | [6 empty] | 1.0038 | 0.76455 | 0.98401 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11092412SP |  |  | ASH GROVE1 69KV | S | WERE |  | SEAST |  |  | 533657 | ASHGRV12 69.000 | [5 empty] | 12SP | [6 empty] | 1.0056 | 0.76685 | 0.98546 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11042412SP |  |  | UNITED NO. 6 URBANA 69KV | S | WERE |  | SEAST |  |  | 533648 | UN6URBA2 69.000 | [5 empty] | 12SP | [6 empty] | 1.0036 | 0.76688 | 0.98574 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11112412SP |  |  | ASH GROVE JCT1 69KV | S | WERE |  | SEAST |  |  | 533659 | ASHGRJ12 69.000 | [5 empty] | 12SP | [6 empty] | 1.0056 | 0.7675 | 0.98597 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11132412SP |  |  | CHANUTE GENERATION TAP 69KV | S | WERE |  | SEAST |  |  | 533661 | CGENTAP2 69.000 | [5 empty] | 12SP | [6 empty] | 1.0056 | 0.7677 | 0.98613 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11142412SP |  |  | CHANUTE GENERATION SUB 69KV | S | WERE |  | SEAST |  |  | 533662 | CGENSUB2 69.000 | [5 empty] | 12SP | [6 empty] | 1.0056 | 0.76974 | 0.9877 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11102412SP |  |  | ASH GROVE2 69KV | S | WERE |  | SEAST |  |  | 533658 | ASHGRV22 69.000 | [5 empty] | 12SP | [6 empty] | 1.0057 | 0.77051 | 0.98827 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11122412SP |  |  | ASH GROVE JCT2 69KV | S | WERE |  | SEAST |  |  | 533660 | ASHGRJ22 69.000 | [5 empty] | 12SP | [6 empty] | 1.0057 | 0.77117 | 0.98878 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11182412SP |  |  | CHANUTE TAP 69KV | S | WERE |  | SEAST |  |  | 533666 | CHANTAP2 69.000 | [5 empty] | 12SP | [6 empty] | 1.0056 | 0.77259 | 0.98991 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11052412SP |  |  | UNITED NO. 7 ROSE 69KV | S | WERE |  | SEAST |  |  | 533649 | UN7ROSE2 69.000 | [5 empty] | 12SP | [6 empty] | 1.0008 | 0.77383 | 0.99946 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V10872412SP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 12SP | [6 empty] | 0.95969 | 0.77845 | 0.9212 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V10752112SP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 12SP | [6 empty] | 0.96022 | 0.78132 | 0.91953 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11022412SP |  |  | TIOGA 69KV | S | WERE |  | SEAST |  |  | 533646 | TIOGA 2 69.000 | [5 empty] | 12SP | [6 empty] | 1.0061 | 0.78951 | 1.00284 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9131112SP |  |  | UNITED NO. 1 ELSMORE 69KV | S | WERE |  | SEAST |  |  | 533647 | UN1ELSM2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.84414 | 1.01051 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12591112SP |  |  | UNITED NO. 1 ELSMORE 69KV | S | WERE |  | SEAST |  |  | 533647 | UN1ELSM2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.84687 | 1.01051 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9051112SP |  |  | MARMATON 69KV | S | WERE |  | SEAST |  |  | 533639 | MARMATN2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.872 | 1.01246 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12511112SP |  |  | MARMATON 69KV | S | WERE |  | SEAST |  |  | 533639 | MARMATN2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.87442 | 1.01246 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V10762112SP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 12SP | [6 empty] | 0.97968 | 0.89271 | 0.95606 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V10882412SP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 12SP | [6 empty] | 0.97966 | 0.89336 | 0.95637 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V14572412SP |  |  | MARMATON 69KV | S | WERE |  | SEAST |  |  | 533639 | MARMATN2 69.000 | [5 empty] | 12SP | [6 empty] | 0.9757 | 0.89612 | 1.01623 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V13302112SP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 12SP | [6 empty] | 0.95963 | 0.89804 | 0.95606 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15102312SP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 12SP | [6 empty] | 0.9556 | 0.90129 | 0.96206 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15112312SP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 12SP | [6 empty] | 0.9557 | 0.90139 | 0.96215 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15082312SP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 12SP | [6 empty] | 0.95478 | 0.90206 | 0.96306 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15062312SP |  |  | DEARING 138KV | S | WERE |  | SEAST |  |  | 533002 | DEARING4 138.00 | [5 empty] | 12SP | [6 empty] | 0.95342 | 0.90925 | 0.96833 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V8951112SP |  |  | MARMTNE5 161KV | S | WERE |  | SEAST |  |  | 532934 | MARMTNE5 161.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.91678 | 0.99744 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12421112SP |  |  | MARMTNE5 161KV | S | WERE |  | SEAST |  |  | 532934 | MARMTNE5 161.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.91761 | 0.99744 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V11312312SP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 12SP | [6 empty] | 0.97943 | 0.92227 | 0.96206 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V11322312SP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 12SP | [6 empty] | 0.97952 | 0.92237 | 0.96215 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V10792112SP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 12SP | [6 empty] | 0.98045 | 0.92308 | 0.96441 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V10802112SP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 12SP | [6 empty] | 0.98054 | 0.92318 | 0.9645 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V9162112SP |  |  | NORTHEAST PARSONS 138KV | S | WERE |  | SEAST |  |  | 533005 | NEPARSN4 138.00 | [5 empty] | 12SP | [6 empty] | 1.0066 | 0.92618 | 0.98581 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533021 | NEOSHO 4 138.00 | 533005 | NEPARSN4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V11302312SP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 12SP | [6 empty] | 0.97934 | 0.92661 | 0.96306 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V10782112SP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 12SP | [6 empty] | 0.98065 | 0.92767 | 0.96573 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V1162412SP |  |  | DEARING 138KV | S | WERE |  | SEAST |  |  | 533002 | DEARING4 138.00 | [5 empty] | 12SP | [6 empty] | 0.95484 | 0.93271 | 0.97492 | 0.95 | 1.05 | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V11292312SP |  |  | DEARING 138KV | S | WERE |  | SEAST |  |  | 533002 | DEARING4 138.00 | [5 empty] | 12SP | [6 empty] | 0.9807 | 0.94632 | 0.96833 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1823312WP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 12WP | [6 empty] | 0.8913 | 0.45704 | 0.95214 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2133312WP |  |  | CHANUTE PLANT3 69KV | S | WERE |  | SEAST |  |  | 533665 | CHANP3 2 69.000 | [5 empty] | 12WP | [6 empty] | 1.003 | 0.49095 | 1.00517 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2113312WP |  |  | CHANUTE PLANT1 69KV | S | WERE |  | SEAST |  |  | 533663 | CHANP1 2 69.000 | [5 empty] | 12WP | [6 empty] | 1.003 | 0.49122 | 1.00533 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2123312WP |  |  | CHANUTE PLANT2 69KV | S | WERE |  | SEAST |  |  | 533664 | CHANP2 2 69.000 | [5 empty] | 12WP | [6 empty] | 1.003 | 0.49122 | 1.00533 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3713312WP |  |  | CHANUTE PLANT3 69KV | S | WERE |  | SEAST |  |  | 533665 | CHANP3 2 69.000 | [5 empty] | 12WP | [6 empty] | 0.99925 | 0.49237 | 1.00517 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3693312WP |  |  | CHANUTE PLANT1 69KV | S | WERE |  | SEAST |  |  | 533663 | CHANP1 2 69.000 | [5 empty] | 12WP | [6 empty] | 0.99925 | 0.49264 | 1.00533 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3703312WP |  |  | CHANUTE PLANT2 69KV | S | WERE |  | SEAST |  |  | 533664 | CHANP2 2 69.000 | [5 empty] | 12WP | [6 empty] | 0.99925 | 0.49264 | 1.00533 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2053312WP |  |  | ASH GROVE1 69KV | S | WERE |  | SEAST |  |  | 533657 | ASHGRV12 69.000 | [5 empty] | 12WP | [6 empty] | 1.003 | 0.49385 | 1.00693 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2073312WP |  |  | ASH GROVE JCT1 69KV | S | WERE |  | SEAST |  |  | 533659 | ASHGRJ12 69.000 | [5 empty] | 12WP | [6 empty] | 1.003 | 0.49447 | 1.00731 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2093312WP |  |  | CHANUTE GENERATION TAP 69KV | S | WERE |  | SEAST |  |  | 533661 | CGENTAP2 69.000 | [5 empty] | 12WP | [6 empty] | 1.003 | 0.49466 | 1.00742 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3633312WP |  |  | ASH GROVE1 69KV | S | WERE |  | SEAST |  |  | 533657 | ASHGRV12 69.000 | [5 empty] | 12WP | [6 empty] | 0.99925 | 0.49528 | 1.00693 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3653312WP |  |  | ASH GROVE JCT1 69KV | S | WERE |  | SEAST |  |  | 533659 | ASHGRJ12 69.000 | [5 empty] | 12WP | [6 empty] | 0.99925 | 0.49589 | 1.00731 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3673312WP |  |  | CHANUTE GENERATION TAP 69KV | S | WERE |  | SEAST |  |  | 533661 | CGENTAP2 69.000 | [5 empty] | 12WP | [6 empty] | 0.99925 | 0.49608 | 1.00742 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2103312WP |  |  | CHANUTE GENERATION SUB 69KV | S | WERE |  | SEAST |  |  | 533662 | CGENSUB2 69.000 | [5 empty] | 12WP | [6 empty] | 1.003 | 0.49656 | 1.00857 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2003312WP |  |  | UNITED NO. 6 URBANA 69KV | S | WERE |  | SEAST |  |  | 533648 | UN6URBA2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0016 | 0.49668 | 1.0087 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2153312WP |  |  | CITY OF ERIE 69KV | S | WERE |  | SEAST |  |  | 533760 | ERIE 2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0018 | 0.49709 | 1.00873 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2063312WP |  |  | ASH GROVE2 69KV | S | WERE |  | SEAST |  |  | 533658 | ASHGRV22 69.000 | [5 empty] | 12WP | [6 empty] | 1.0031 | 0.49721 | 1.00894 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2083312WP |  |  | ASH GROVE JCT2 69KV | S | WERE |  | SEAST |  |  | 533660 | ASHGRJ22 69.000 | [5 empty] | 12WP | [6 empty] | 1.0031 | 0.49783 | 1.00932 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3683312WP |  |  | CHANUTE GENERATION SUB 69KV | S | WERE |  | SEAST |  |  | 533662 | CGENSUB2 69.000 | [5 empty] | 12WP | [6 empty] | 0.99925 | 0.49799 | 1.00857 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3583312WP |  |  | UNITED NO. 6 URBANA 69KV | S | WERE |  | SEAST |  |  | 533648 | UN6URBA2 69.000 | [5 empty] | 12WP | [6 empty] | 0.99784 | 0.4981 | 1.0087 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3733312WP |  |  | CITY OF ERIE 69KV | S | WERE |  | SEAST |  |  | 533760 | ERIE 2 69.000 | [5 empty] | 12WP | [6 empty] | 0.99802 | 0.4985 | 1.00873 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3643312WP |  |  | ASH GROVE2 69KV | S | WERE |  | SEAST |  |  | 533658 | ASHGRV22 69.000 | [5 empty] | 12WP | [6 empty] | 0.99927 | 0.49864 | 1.00894 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3663312WP |  |  | ASH GROVE JCT2 69KV | S | WERE |  | SEAST |  |  | 533660 | ASHGRJ22 69.000 | [5 empty] | 12WP | [6 empty] | 0.99927 | 0.49925 | 1.00932 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2143312WP |  |  | CHANUTE TAP 69KV | S | WERE |  | SEAST |  |  | 533666 | CHANTAP2 69.000 | [5 empty] | 12WP | [6 empty] | 1.003 | 0.49929 | 1.01023 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3723312WP |  |  | CHANUTE TAP 69KV | S | WERE |  | SEAST |  |  | 533666 | CHANTAP2 69.000 | [5 empty] | 12WP | [6 empty] | 0.99924 | 0.50072 | 1.01023 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1893312WP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 12WP | [6 empty] | 1.006 | 0.51044 | 0.97067 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3473312WP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0017 | 0.51157 | 0.97067 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1983312WP |  |  | TIOGA 69KV | S | WERE |  | SEAST |  |  | 533646 | TIOGA 2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0033 | 0.51454 | 1.01926 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3563312WP |  |  | TIOGA 69KV | S | WERE |  | SEAST |  |  | 533646 | TIOGA 2 69.000 | [5 empty] | 12WP | [6 empty] | 0.99955 | 0.51596 | 1.01926 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2013312WP |  |  | UNITED NO. 7 ROSE 69KV | S | WERE |  | SEAST |  |  | 533649 | UN7ROSE2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0066 | 0.51642 | 1.01829 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3593312WP |  |  | UNITED NO. 7 ROSE 69KV | S | WERE |  | SEAST |  |  | 533649 | UN7ROSE2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0027 | 0.5178 | 1.01829 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1953312WP |  |  | ORCHARD 69KV | S | WERE |  | SEAST |  |  | 533643 | ORCHARD2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0111 | 0.51997 | 1.01745 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3533312WP |  |  | ORCHARD 69KV | S | WERE |  | SEAST |  |  | 533643 | ORCHARD2 69.000 | [5 empty] | 12WP | [6 empty] | 1.007 | 0.52128 | 1.01745 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1863312WP |  |  | ATHENS SWITCHING STATION 69KV | S | WERE |  | SEAST |  |  | 533623 | ATHENS 2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0161 | 0.52546 | 1.01811 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3443312WP |  |  | ATHENS SWITCHING STATION 69KV | S | WERE |  | SEAST |  |  | 533623 | ATHENS 2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0119 | 0.52673 | 1.01811 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1943312WP |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0131 | 0.52726 | 1.01213 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3523312WP |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0089 | 0.52849 | 1.01213 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2033312WP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0059 | 0.53769 | 0.98773 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3613312WP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0016 | 0.53881 | 0.98773 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1903312WP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0062 | 0.54304 | 0.99107 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3483312WP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0019 | 0.54416 | 0.99107 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1873312WP |  |  | ENA 69KV | S | WERE |  | SEAST |  |  | 533634 | ENA 2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0004 | 0.57422 | 1.01069 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3453312WP |  |  | ENA 69KV | S | WERE |  | SEAST |  |  | 533634 | ENA 2 69.000 | [5 empty] | 12WP | [6 empty] | 0.9962 | 0.57536 | 1.01069 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1833312WP |  |  | ARCO 69KV | S | WERE |  | SEAST |  |  | 533619 | ARCO 2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0002 | 0.57673 | 1.01028 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1843312WP |  |  | ARCO TAP 69KV | S | WERE |  | SEAST |  |  | 533620 | ARCOTAP2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0003 | 0.57687 | 1.01036 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3413312WP |  |  | ARCO 69KV | S | WERE |  | SEAST |  |  | 533619 | ARCO 2 69.000 | [5 empty] | 12WP | [6 empty] | 0.99601 | 0.57785 | 1.01028 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3423312WP |  |  | ARCO TAP 69KV | S | WERE |  | SEAST |  |  | 533620 | ARCOTAP2 69.000 | [5 empty] | 12WP | [6 empty] | 0.99609 | 0.57799 | 1.01036 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1933312WP |  |  | MONARCH 69KV | S | WERE |  | SEAST |  |  | 533641 | MONARCH2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0002 | 0.58129 | 1.00988 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3513312WP |  |  | MONARCH 69KV | S | WERE |  | SEAST |  |  | 533641 | MONARCH2 69.000 | [5 empty] | 12WP | [6 empty] | 0.99598 | 0.5824 | 1.00988 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1853312WP |  |  | ALLEN 69KV | S | WERE |  | SEAST |  |  | 533621 | ALLEN 2 69.000 | [5 empty] | 12WP | [6 empty] | 1.004 | 0.61001 | 1.01178 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3433312WP |  |  | ALLEN 69KV | S | WERE |  | SEAST |  |  | 533621 | ALLEN 2 69.000 | [5 empty] | 12WP | [6 empty] | 0.9997 | 0.61103 | 1.01178 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2023312WP |  |  | UNITED NO. 8 HUMBOLDT 69KV | S | WERE |  | SEAST |  |  | 533650 | UN8HUMB2 69.000 | [5 empty] | 12WP | [6 empty] | 1.004 | 0.67852 | 1.00982 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3603312WP |  |  | UNITED NO. 8 HUMBOLDT 69KV | S | WERE |  | SEAST |  |  | 533650 | UN8HUMB2 69.000 | [5 empty] | 12WP | [6 empty] | 0.99942 | 0.67933 | 1.00982 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2043312WP |  |  | ZILA JUNCTION 69KV | S | WERE |  | SEAST |  |  | 533654 | ZILAJCT2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0062 | 0.68187 | 1.01207 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3623312WP |  |  | ZILA JUNCTION 69KV | S | WERE |  | SEAST |  |  | 533654 | ZILAJCT2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0017 | 0.68268 | 1.01207 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1993312WP |  |  | UNITED NO. 1 ELSMORE 69KV | S | WERE |  | SEAST |  |  | 533647 | UN1ELSM2 69.000 | [5 empty] | 12WP | [6 empty] | 1.014 | 0.82823 | 1.01655 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3573312WP |  |  | UNITED NO. 1 ELSMORE 69KV | S | WERE |  | SEAST |  |  | 533647 | UN1ELSM2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0091 | 0.82872 | 1.01655 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V2014212WP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0033 | 0.85015 | 0.95731 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1913312WP |  |  | MARMATON 69KV | S | WERE |  | SEAST |  |  | 533639 | MARMATN2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0157 | 0.85884 | 1.01769 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3493312WP |  |  | MARMATON 69KV | S | WERE |  | SEAST |  |  | 533639 | MARMATN2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0108 | 0.85927 | 1.01769 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V2044212WP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0033 | 0.86966 | 0.97462 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V2024212WP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0035 | 0.87348 | 0.97801 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V3594112WP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 12WP | [6 empty] | 0.97193 | 0.89516 | 0.93711 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V1994112WP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 12WP | [6 empty] | 0.97312 | 0.89543 | 0.93711 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1813312WP |  |  | MARMTNE5 161KV | S | WERE |  | SEAST |  |  | 532934 | MARMTNE5 161.00 | [5 empty] | 12WP | [6 empty] | 1.0044 | 0.91209 | 0.99823 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3403312WP |  |  | MARMTNE5 161KV | S | WERE |  | SEAST |  |  | 532934 | MARMTNE5 161.00 | [5 empty] | 12WP | [6 empty] | 1.0049 | 0.91227 | 0.99823 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V3604112WP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 12WP | [6 empty] | 0.98023 | 0.92191 | 0.96479 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V2004112WP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 12WP | [6 empty] | 0.98137 | 0.92197 | 0.96479 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V2974112WP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 12WP | [6 empty] | 0.98347 | 0.93505 | 0.96479 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V2034212WP |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0076 | 0.93555 | 0.99734 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V614112WP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 12WP | [6 empty] | 0.96701 | 0.94498 | 0.97736 | 0.95 | 1.05 | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V624112WP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 12WP | [6 empty] | 0.96707 | 0.94504 | 0.97742 | 0.95 | 1.05 | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V522212WP |  |  | DEARING 138KV | S | WERE |  | SEAST |  |  | 533002 | DEARING4 138.00 | [5 empty] | 12WP | [6 empty] | 0.96698 | 0.94566 | 0.98584 | 0.95 | 1.05 | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V532212WP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 12WP | [6 empty] | 0.97048 | 0.94578 | 0.98117 | 0.95 | 1.05 | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V3002112WP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 12WP | [6 empty] | 0.98481 | 0.94764 | 0.97773 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V3012112WP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 12WP | [6 empty] | 0.98487 | 0.9477 | 0.97779 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V3614112WP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 12WP | [6 empty] | 0.98626 | 0.94853 | 0.97736 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-20 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V3624112WP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 12WP | [6 empty] | 0.98632 | 0.94859 | 0.97742 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-20 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V2992112WP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 12WP | [6 empty] | 0.98494 | 0.94942 | 0.97947 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12752317SP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 17SP | [6 empty] | 0.8767 | 0.81369 | 0.94449 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V14982117SP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.98247 | 0.81534 | 0.93789 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V15022117SP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 17SP | [6 empty] | 0.98244 | 0.83702 | 0.95669 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V14992117SP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 17SP | [6 empty] | 0.98284 | 0.84142 | 0.96051 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12812317SP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97705 | 0.86198 | 0.93855 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21052317SP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97757 | 0.86724 | 0.93855 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12902317SP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97702 | 0.88246 | 0.95734 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12822317SP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97743 | 0.88662 | 0.96116 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21142317SP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97754 | 0.8876 | 0.95734 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21062317SP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97795 | 0.89173 | 0.96116 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V19902117SP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 17SP | [6 empty] | 0.95113 | 0.89265 | 0.94414 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12842317SP |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97733 | 0.89539 | 0.98575 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12792317SP |  |  | ATHENS SWITCHING STATION 69KV | S | WERE |  | SEAST |  |  | 533623 | ATHENS 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97793 | 0.90032 | 0.99287 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21082317SP |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 17SP | [6 empty] | 0.9779 | 0.90078 | 0.98575 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12852317SP |  |  | ORCHARD 69KV | S | WERE |  | SEAST |  |  | 533643 | ORCHARD2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97912 | 0.90355 | 0.99461 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21032317SP |  |  | ATHENS SWITCHING STATION 69KV | S | WERE |  | SEAST |  |  | 533623 | ATHENS 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97852 | 0.90579 | 0.99287 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V19942417SP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 17SP | [6 empty] | 0.96338 | 0.907 | 0.94771 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V18283317SP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 17SP | [6 empty] | 0.95278 | 0.90724 | 0.96581 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V13002317SP |  |  | CHANUTE PLANT3 69KV | S | WERE |  | SEAST |  |  | 533665 | CHANP3 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.99002 | 0.90728 | 0.99482 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V18303317SP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 17SP | [6 empty] | 0.95421 | 0.90748 | 0.96565 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12982317SP |  |  | CHANUTE PLANT1 69KV | S | WERE |  | SEAST |  |  | 533663 | CHANP1 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.99002 | 0.90755 | 0.99506 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12992317SP |  |  | CHANUTE PLANT2 69KV | S | WERE |  | SEAST |  |  | 533664 | CHANP2 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.99002 | 0.90755 | 0.99506 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V18313317SP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 17SP | [6 empty] | 0.95432 | 0.9076 | 0.96576 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21092317SP |  |  | ORCHARD 69KV | S | WERE |  | SEAST |  |  | 533643 | ORCHARD2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97973 | 0.9091 | 0.99461 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 1 | 2008-12-01 | 2007AG1AFS81V18823117SP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 17SP | [6 empty] | 0.95846 | 0.90946 | 0.96537 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12922317SP |  |  | ASH GROVE1 69KV | S | WERE |  | SEAST |  |  | 533657 | ASHGRV12 69.000 | [5 empty] | 17SP | [6 empty] | 0.99002 | 0.91009 | 0.99738 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12882317SP |  |  | UNITED NO. 7 ROSE 69KV | S | WERE |  | SEAST |  |  | 533649 | UN7ROSE2 69.000 | [5 empty] | 17SP | [6 empty] | 0.98326 | 0.91031 | 0.9997 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12942317SP |  |  | ASH GROVE JCT1 69KV | S | WERE |  | SEAST |  |  | 533659 | ASHGRJ12 69.000 | [5 empty] | 17SP | [6 empty] | 0.99002 | 0.91068 | 0.99792 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12962317SP |  |  | CHANUTE GENERATION TAP 69KV | S | WERE |  | SEAST |  |  | 533661 | CGENTAP2 69.000 | [5 empty] | 17SP | [6 empty] | 0.99002 | 0.91086 | 0.99808 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V18263317SP |  |  | DEARING 138KV | S | WERE |  | SEAST |  |  | 533002 | DEARING4 138.00 | [5 empty] | 17SP | [6 empty] | 0.9489 | 0.91118 | 0.96684 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12932317SP |  |  | ASH GROVE2 69KV | S | WERE |  | SEAST |  |  | 533658 | ASHGRV22 69.000 | [5 empty] | 17SP | [6 empty] | 0.98966 | 0.91118 | 0.99866 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12952317SP |  |  | ASH GROVE JCT2 69KV | S | WERE |  | SEAST |  |  | 533660 | ASHGRJ22 69.000 | [5 empty] | 17SP | [6 empty] | 0.98966 | 0.91178 | 0.99921 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12972317SP |  |  | CHANUTE GENERATION SUB 69KV | S | WERE |  | SEAST |  |  | 533662 | CGENSUB2 69.000 | [5 empty] | 17SP | [6 empty] | 0.99002 | 0.9127 | 0.99975 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21242317SP |  |  | CHANUTE PLANT3 69KV | S | WERE |  | SEAST |  |  | 533665 | CHANP3 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.99062 | 0.913 | 0.99482 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21222317SP |  |  | CHANUTE PLANT1 69KV | S | WERE |  | SEAST |  |  | 533663 | CHANP1 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.99062 | 0.91327 | 0.99506 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21232317SP |  |  | CHANUTE PLANT2 69KV | S | WERE |  | SEAST |  |  | 533664 | CHANP2 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.99062 | 0.91327 | 0.99506 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V15002117SP |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 17SP | [6 empty] | 0.98925 | 0.91331 | 0.9853 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V13012317SP |  |  | CHANUTE TAP 69KV | S | WERE |  | SEAST |  |  | 533666 | CHANTAP2 69.000 | [5 empty] | 17SP | [6 empty] | 0.99038 | 0.91441 | 1.001 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21162317SP |  |  | ASH GROVE1 69KV | S | WERE |  | SEAST |  |  | 533657 | ASHGRV12 69.000 | [5 empty] | 17SP | [6 empty] | 0.99062 | 0.9158 | 0.99738 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21122317SP |  |  | UNITED NO. 7 ROSE 69KV | S | WERE |  | SEAST |  |  | 533649 | UN7ROSE2 69.000 | [5 empty] | 17SP | [6 empty] | 0.98389 | 0.91592 | 0.9997 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12862317SP |  |  | TIOGA 69KV | S | WERE |  | SEAST |  |  | 533646 | TIOGA 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.98695 | 0.91602 | 1.00434 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21182317SP |  |  | ASH GROVE JCT1 69KV | S | WERE |  | SEAST |  |  | 533659 | ASHGRJ12 69.000 | [5 empty] | 17SP | [6 empty] | 0.99062 | 0.91639 | 0.99792 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21202317SP |  |  | CHANUTE GENERATION TAP 69KV | S | WERE |  | SEAST |  |  | 533661 | CGENTAP2 69.000 | [5 empty] | 17SP | [6 empty] | 0.99062 | 0.91656 | 0.99808 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12802317SP |  |  | ENA 69KV | S | WERE |  | SEAST |  |  | 533634 | ENA 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97937 | 0.91664 | 0.98667 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12762317SP |  |  | ARCO 69KV | S | WERE |  | SEAST |  |  | 533619 | ARCO 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97896 | 0.91669 | 0.98586 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12772317SP |  |  | ARCO TAP 69KV | S | WERE |  | SEAST |  |  | 533620 | ARCOTAP2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97911 | 0.91685 | 0.98601 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21172317SP |  |  | ASH GROVE2 69KV | S | WERE |  | SEAST |  |  | 533658 | ASHGRV22 69.000 | [5 empty] | 17SP | [6 empty] | 0.99026 | 0.91688 | 0.99866 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12832317SP |  |  | MONARCH 69KV | S | WERE |  | SEAST |  |  | 533641 | MONARCH2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97876 | 0.91731 | 0.98501 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21192317SP |  |  | ASH GROVE JCT2 69KV | S | WERE |  | SEAST |  |  | 533660 | ASHGRJ22 69.000 | [5 empty] | 17SP | [6 empty] | 0.99026 | 0.91747 | 0.99921 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21212317SP |  |  | CHANUTE GENERATION SUB 69KV | S | WERE |  | SEAST |  |  | 533662 | CGENSUB2 69.000 | [5 empty] | 17SP | [6 empty] | 0.99062 | 0.91839 | 0.99975 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21252317SP |  |  | CHANUTE TAP 69KV | S | WERE |  | SEAST |  |  | 533666 | CHANTAP2 69.000 | [5 empty] | 17SP | [6 empty] | 0.99096 | 0.92009 | 1.001 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21042317SP |  |  | ENA 69KV | S | WERE |  | SEAST |  |  | 533634 | ENA 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97991 | 0.92161 | 0.98667 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21002317SP |  |  | ARCO 69KV | S | WERE |  | SEAST |  |  | 533619 | ARCO 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97949 | 0.92164 | 0.98586 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21102317SP |  |  | TIOGA 69KV | S | WERE |  | SEAST |  |  | 533646 | TIOGA 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.9876 | 0.92168 | 1.00434 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21012317SP |  |  | ARCO TAP 69KV | S | WERE |  | SEAST |  |  | 533620 | ARCOTAP2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97964 | 0.9218 | 0.98601 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21072317SP |  |  | MONARCH 69KV | S | WERE |  | SEAST |  |  | 533641 | MONARCH2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97929 | 0.9222 | 0.98501 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12782317SP |  |  | ALLEN 69KV | S | WERE |  | SEAST |  |  | 533621 | ALLEN 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.98144 | 0.92452 | 0.98459 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21022317SP |  |  | ALLEN 69KV | S | WERE |  | SEAST |  |  | 533621 | ALLEN 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.98193 | 0.92916 | 0.98459 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V14972117SP |  |  | ATHENS SWITCHING STATION 69KV | S | WERE |  | SEAST |  |  | 533623 | ATHENS 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.99112 | 0.93108 | 0.99245 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V2122217SP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 17SP | [6 empty] | 0.95535 | 0.93316 | 0.96942 | 0.95 | 1.05 | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 1 | 2008-12-01 | 2007AG1AFS81V13373117SP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 17SP | [6 empty] | 0.98867 | 0.9335 | 0.96537 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 4 | 2008-12-01 | 2007AG1AFS81V19823417SP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 17SP | [6 empty] | 0.98545 | 0.93376 | 0.96537 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12872317SP |  |  | UNITED NO. 6 URBANA 69KV | S | WERE |  | SEAST |  |  | 533648 | UN6URBA2 69.000 | [5 empty] | 17SP | [6 empty] | 1.0044 | 0.9338 | 1.00954 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V2132217SP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 17SP | [6 empty] | 0.95682 | 0.9339 | 0.96907 | 0.95 | 1.05 | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V2142217SP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 17SP | [6 empty] | 0.95693 | 0.93401 | 0.96918 | 0.95 | 1.05 | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12892317SP |  |  | UNITED NO. 8 HUMBOLDT 69KV | S | WERE |  | SEAST |  |  | 533650 | UN8HUMB2 69.000 | [5 empty] | 17SP | [6 empty] | 0.98413 | 0.93422 | 0.98603 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12912317SP |  |  | ZILA JUNCTION 69KV | S | WERE |  | SEAST |  |  | 533654 | ZILAJCT2 69.000 | [5 empty] | 17SP | [6 empty] | 0.98725 | 0.9375 | 0.98914 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21132317SP |  |  | UNITED NO. 8 HUMBOLDT 69KV | S | WERE |  | SEAST |  |  | 533650 | UN8HUMB2 69.000 | [5 empty] | 17SP | [6 empty] | 0.98455 | 0.93815 | 0.98603 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21112317SP |  |  | UNITED NO. 6 URBANA 69KV | S | WERE |  | SEAST |  |  | 533648 | UN6URBA2 69.000 | [5 empty] | 17SP | [6 empty] | 1.0047 | 0.93939 | 1.00954 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21152317SP |  |  | ZILA JUNCTION 69KV | S | WERE |  | SEAST |  |  | 533654 | ZILAJCT2 69.000 | [5 empty] | 17SP | [6 empty] | 0.98766 | 0.94142 | 0.98914 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V20033317SP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 17SP | [6 empty] | 0.97016 | 0.94495 | 0.96581 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-19 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V11663317SP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 17SP | [6 empty] | 0.98445 | 0.94496 | 0.96565 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V11673317SP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 17SP | [6 empty] | 0.98455 | 0.94508 | 0.96576 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12742317SP |  |  | MARMTNE5 161KV | S | WERE |  | SEAST |  |  | 532934 | MARMTNE5 161.00 | [5 empty] | 17SP | [6 empty] | 0.99345 | 0.94916 | 0.98255 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | ATHENS 69KV Capacitor | Athens 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12482312SP |  |  | DUNCAN ROAD 161KV | REL | MIPU |  |  |  |  | 541235 | DUNCAN 5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.91289 | 0.87604 | 0.94034 | 0.9 | 1.1 | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEY 161KV CKT 1 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12492312SP |  |  | BLUE SPRINGS WEST 161KV | REL | MIPU |  |  |  |  | 541237 | BLSPW 5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.91465 | 0.87642 | 0.92934 | 0.9 | 1.1 | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEY 161KV CKT 1 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12382312SP |  |  | BLUE SPRINGS EAST 161KV | REL | MIPU |  |  |  |  | 541205 | BLSPE 5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.91446 | 0.87744 | 0.9352 | 0.9 | 1.1 | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEY 161KV CKT 1 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12502312SP |  |  | LAKEWOOD 161KV | REL | MIPU |  |  |  |  | 541238 | LKWOOD 5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.91764 | 0.87863 | 0.92576 | 0.9 | 1.1 | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEY 161KV CKT 1 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12402312SP |  |  | BLUE SPRING SOUTH 161KV | REL | MIPU |  |  |  |  | 541211 | BLSPS 5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.91648 | 0.87933 | 0.93241 | 0.9 | 1.1 | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEY 161KV CKT 1 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12422312SP |  |  | RAYTOWN 161KV | REL | MIPU |  |  |  |  | 541219 | RAYTOWN5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.92184 | 0.88269 | 0.92531 | 0.9 | 1.1 | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEY 161KV CKT 1 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12392312SP |  |  | PRAIRIE LEE 161KV | REL | MIPU |  |  |  |  | 541206 | PRALEE 5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.92483 | 0.88795 | 0.92666 | 0.9 | 1.1 | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEY 161KV CKT 1 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12432312SP |  |  | FROST ROAD 161KV | REL | MIPU |  |  |  |  | 541220 | FROSTRD5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.92706 | 0.8882 | 0.92689 | 0.9 | 1.1 | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEY 161KV CKT 1 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12612312SP |  |  | BLUE SPRINGS WEST 161KV | REL | MIPU |  |  |  |  | 541237 | BLSPW 5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.92699 | 0.88887 | 0.92934 | 0.9 | 1.1 | CATEGORYB | SINGLE | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | 0 | 541235 | DUNCAN 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12462312SP |  |  | GRAIN VALLEY 161KV | REL | MIPU |  |  |  |  | 541226 | GRAINVL5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.92088 | 0.88938 | 0.93683 | 0.9 | 1.1 | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEY 161KV CKT 1 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12622312SP |  |  | LAKEWOOD 161KV | REL | MIPU |  |  |  |  | 541238 | LKWOOD 5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.92863 | 0.88983 | 0.92576 | 0.9 | 1.1 | CATEGORYB | SINGLE | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | 0 | 541235 | DUNCAN 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12522312SP |  |  | STROTHERS ROAD 161KV | REL | MIPU |  |  |  |  | 541246 | STROTHR5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.92761 | 0.88991 | 0.92531 | 0.9 | 1.1 | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEY 161KV CKT 1 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12552312SP |  |  | BLUE SPRINGS EAST 161KV | REL | MIPU |  |  |  |  | 541205 | BLSPE 5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.92791 | 0.89092 | 0.9352 | 0.9 | 1.1 | CATEGORYB | SINGLE | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | 0 | 541235 | DUNCAN 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12872312SP |  |  | WESTERN ELECTRIC 161KV | REL | MIPU |  |  |  |  | 541222 | WSTELEC5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93294 | 0.89092 | 0.92519 | 0.9 | 1.1 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12472312SP |  |  | LEES SUMMIT EAST 161KV | REL | MIPU |  |  |  |  | 541233 | LEESUM 5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.92731 | 0.89111 | 0.92632 | 0.9 | 1.1 | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEY 161KV CKT 1 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12942312SP |  |  | STROTHERS ROAD 161KV | REL | MIPU |  |  |  |  | 541246 | STROTHR5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93275 | 0.89161 | 0.92531 | 0.9 | 1.1 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12572312SP |  |  | BLUE SPRING SOUTH 161KV | REL | MIPU |  |  |  |  | 541211 | BLSPS 5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.92885 | 0.89181 | 0.93241 | 0.9 | 1.1 | CATEGORYB | SINGLE | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | 0 | 541235 | DUNCAN 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12852312SP |  |  | RAYTOWN 161KV | REL | MIPU |  |  |  |  | 541219 | RAYTOWN5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93347 | 0.89184 | 0.92531 | 0.9 | 1.1 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12512312SP |  |  | KC SOUTH 161KV | REL | MIPU |  |  |  |  | 541245 | KCSOUTH5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93006 | 0.8922 | 0.92623 | 0.9 | 1.1 | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEY 161KV CKT 1 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12932312SP |  |  | KC SOUTH 161KV | REL | MIPU |  |  |  |  | 541245 | KCSOUTH5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93379 | 0.89225 | 0.92623 | 0.9 | 1.1 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12442312SP |  |  | WESTERN ELECTRIC 161KV | REL | MIPU |  |  |  |  | 541222 | WSTELEC5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.9307 | 0.89253 | 0.92519 | 0.9 | 1.1 | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEY 161KV CKT 1 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12912312SP |  |  | LAKEWOOD 161KV | REL | MIPU |  |  |  |  | 541238 | LKWOOD 5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93372 | 0.89286 | 0.92576 | 0.9 | 1.1 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12582312SP |  |  | RAYTOWN 161KV | REL | MIPU |  |  |  |  | 541219 | RAYTOWN5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93178 | 0.8929 | 0.92531 | 0.9 | 1.1 | CATEGORYB | SINGLE | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | 0 | 541235 | DUNCAN 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12862312SP |  |  | FROST ROAD 161KV | REL | MIPU |  |  |  |  | 541220 | FROSTRD5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93489 | 0.89301 | 0.92689 | 0.9 | 1.1 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12882312SP |  |  | LONGVIEW 161KV | REL | MIPU |  |  |  |  | 541224 | LNGVW 5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.9343 | 0.89331 | 0.92753 | 0.9 | 1.1 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12892312SP |  |  | LEES SUMMIT EAST 161KV | REL | MIPU |  |  |  |  | 541233 | LEESUM 5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93292 | 0.89335 | 0.92632 | 0.9 | 1.1 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V9452312SP |  |  | WESTERN ELECTRIC 161KV | REL | MIPU |  |  |  |  | 541222 | WSTELEC5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93461 | 0.89337 | 0.92519 | 0.9 | 1.1 | CATEGORYB | SINGLE | CRAIG - STRANGER CREEK 345KV CKT 1 | 0 | 532772 | STRANGR7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12832312SP |  |  | PRAIRIE LEE 161KV | REL | MIPU |  |  |  |  | 541206 | PRALEE 5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93356 | 0.89375 | 0.92666 | 0.9 | 1.1 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V9522312SP |  |  | STROTHERS ROAD 161KV | REL | MIPU |  |  |  |  | 541246 | STROTHR5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.9344 | 0.89407 | 0.92531 | 0.9 | 1.1 | CATEGORYB | SINGLE | CRAIG - STRANGER CREEK 345KV CKT 1 | 0 | 532772 | STRANGR7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12952312SP |  |  | HOOK ROAD 161KV | REL | MIPU |  |  |  |  | 541249 | HOOKRD 5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93425 | 0.89412 | 0.92797 | 0.9 | 1.1 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V9512312SP |  |  | KC SOUTH 161KV | REL | MIPU |  |  |  |  | 541245 | KCSOUTH5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93533 | 0.89453 | 0.92623 | 0.9 | 1.1 | CATEGORYB | SINGLE | CRAIG - STRANGER CREEK 345KV CKT 1 | 0 | 532772 | STRANGR7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V9442312SP |  |  | FROST ROAD 161KV | REL | MIPU |  |  |  |  | 541220 | FROSTRD5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93633 | 0.89521 | 0.92689 | 0.9 | 1.1 | CATEGORYB | SINGLE | CRAIG - STRANGER CREEK 345KV CKT 1 | 0 | 532772 | STRANGR7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V9462312SP |  |  | LONGVIEW 161KV | REL | MIPU |  |  |  |  | 541224 | LNGVW 5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93596 | 0.89571 | 0.92753 | 0.9 | 1.1 | CATEGORYB | SINGLE | CRAIG - STRANGER CREEK 345KV CKT 1 | 0 | 532772 | STRANGR7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V9472312SP |  |  | LEES SUMMIT EAST 161KV | REL | MIPU |  |  |  |  | 541233 | LEESUM 5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93475 | 0.89605 | 0.92632 | 0.9 | 1.1 | CATEGORYB | SINGLE | CRAIG - STRANGER CREEK 345KV CKT 1 | 0 | 532772 | STRANGR7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12922312SP |  |  | LAKE WINNEBAGO 161KV | REL | MIPU |  |  |  |  | 541243 | LKWINGB5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93517 | 0.89613 | 0.9296 | 0.9 | 1.1 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V9412312SP |  |  | PRAIRIE LEE 161KV | REL | MIPU |  |  |  |  | 541206 | PRALEE 5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93521 | 0.89624 | 0.92666 | 0.9 | 1.1 | CATEGORYB | SINGLE | CRAIG - STRANGER CREEK 345KV CKT 1 | 0 | 532772 | STRANGR7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12972312SP |  |  | LONE JACK 161KV | REL | MIPU |  |  |  |  | 541316 | LONEJACK 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93497 | 0.89643 | 0.92939 | 0.9 | 1.1 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12842312SP |  |  | GREENWOOD ENERGY CENTER 161KV | REL | MIPU |  |  |  |  | 541218 | GRNWD 5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93522 | 0.89673 | 0.92968 | 0.9 | 1.1 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V9532312SP |  |  | HOOK ROAD 161KV | REL | MIPU |  |  |  |  | 541249 | HOOKRD 5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.9361 | 0.89677 | 0.92797 | 0.9 | 1.1 | CATEGORYB | SINGLE | CRAIG - STRANGER CREEK 345KV CKT 1 | 0 | 532772 | STRANGR7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12982312SP |  |  | SAMPSON 161KV | REL | MIPU |  |  |  |  | 541345 | SAMPSON5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.937 | 0.89678 | 0.93132 | 0.9 | 1.1 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12452312SP |  |  | LONGVIEW 161KV | REL | MIPU |  |  |  |  | 541224 | LNGVW 5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93409 | 0.89718 | 0.92753 | 0.9 | 1.1 | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEY 161KV CKT 1 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12962312SP |  |  | HARRIS ROAD 161KV | REL | MIPU |  |  |  |  | 541313 | HARRIS 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93608 | 0.89801 | 0.93095 | 0.9 | 1.1 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V9552312SP |  |  | SAMPSON 161KV | REL | MIPU |  |  |  |  | 541345 | SAMPSON5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93829 | 0.89878 | 0.93132 | 0.9 | 1.1 | CATEGORYB | SINGLE | CRAIG - STRANGER CREEK 345KV CKT 1 | 0 | 532772 | STRANGR7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V9502312SP |  |  | LAKE WINNEBAGO 161KV | REL | MIPU |  |  |  |  | 541243 | LKWINGB5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93724 | 0.89907 | 0.9296 | 0.9 | 1.1 | CATEGORYB | SINGLE | CRAIG - STRANGER CREEK 345KV CKT 1 | 0 | 532772 | STRANGR7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12532312SP |  |  | HOOK ROAD 161KV | REL | MIPU |  |  |  |  | 541249 | HOOKRD 5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93509 | 0.89922 | 0.92797 | 0.9 | 1.1 | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEY 161KV CKT 1 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12542312SP |  |  | LONE JACK 161KV | REL | MIPU |  |  |  |  | 541316 | LONEJACK 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93379 | 0.89925 | 0.92939 | 0.9 | 1.1 | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEY 161KV CKT 1 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V9542312SP |  |  | LONE JACK 161KV | REL | MIPU |  |  |  |  | 541316 | LONEJACK 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93707 | 0.89944 | 0.92939 | 0.9 | 1.1 | CATEGORYB | SINGLE | CRAIG - STRANGER CREEK 345KV CKT 1 | 0 | 532772 | STRANGR7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12412312SP |  |  | GREENWOOD ENERGY CENTER 161KV | REL | MIPU |  |  |  |  | 541218 | GRNWD 5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93403 | 0.89955 | 0.92968 | 0.9 | 1.1 | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEY 161KV CKT 1 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V9422312SP |  |  | GREENWOOD ENERGY CENTER 161KV | REL | MIPU |  |  |  |  | 541218 | GRNWD 5 161.00 | [5 empty] | 12SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93731 | 0.89974 | 0.92968 | 0.9 | 1.1 | CATEGORYB | SINGLE | CRAIG - STRANGER CREEK 345KV CKT 1 | 0 | 532772 | STRANGR7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15462317SP |  |  | DUNCAN ROAD 161KV | REL | MIPU |  |  |  |  | 541235 | DUNCAN 5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.91009 | 0.86414 | 0.93328 | 0.9 | 1.1 | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEY 161KV CKT 1 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15472317SP |  |  | BLUE SPRINGS WEST 161KV | REL | MIPU |  |  |  |  | 541237 | BLSPW 5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.91186 | 0.8645 | 0.92205 | 0.9 | 1.1 | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEY 161KV CKT 1 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15352317SP |  |  | BLUE SPRINGS EAST 161KV | REL | MIPU |  |  |  |  | 541205 | BLSPE 5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.91183 | 0.86557 | 0.92806 | 0.9 | 1.1 | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEY 161KV CKT 1 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15482317SP |  |  | LAKEWOOD 161KV | REL | MIPU |  |  |  |  | 541238 | LKWOOD 5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.91501 | 0.86709 | 0.91872 | 0.9 | 1.1 | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEY 161KV CKT 1 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15372317SP |  |  | BLUE SPRING SOUTH 161KV | REL | MIPU |  |  |  |  | 541211 | BLSPS 5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.91482 | 0.86794 | 0.92559 | 0.9 | 1.1 | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEY 161KV CKT 1 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15392317SP |  |  | RAYTOWN 161KV | REL | MIPU |  |  |  |  | 541219 | RAYTOWN5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.9196 | 0.87175 | 0.91875 | 0.9 | 1.1 | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEY 161KV CKT 1 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15432317SP |  |  | GRAIN VALLEY 161KV | REL | MIPU |  |  |  |  | 541226 | GRAINVL5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.91533 | 0.87683 | 0.92806 | 0.9 | 1.1 | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEY 161KV CKT 1 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15652317SP |  |  | BLUE SPRINGS WEST 161KV | REL | MIPU |  |  |  |  | 541237 | BLSPW 5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.92561 | 0.87783 | 0.92205 | 0.9 | 1.1 | CATEGORYB | SINGLE | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | 0 | 541235 | DUNCAN 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15402317SP |  |  | FROST ROAD 161KV | REL | MIPU |  |  |  |  | 541220 | FROSTRD5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.9254 | 0.87803 | 0.92095 | 0.9 | 1.1 | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEY 161KV CKT 1 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15362317SP |  |  | PRAIRIE LEE 161KV | REL | MIPU |  |  |  |  | 541206 | PRALEE 5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.9265 | 0.87851 | 0.92135 | 0.9 | 1.1 | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEY 161KV CKT 1 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15662317SP |  |  | LAKEWOOD 161KV | REL | MIPU |  |  |  |  | 541238 | LKWOOD 5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.92725 | 0.87916 | 0.91872 | 0.9 | 1.1 | CATEGORYB | SINGLE | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | 0 | 541235 | DUNCAN 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15562317SP |  |  | BLUE SPRINGS EAST 161KV | REL | MIPU |  |  |  |  | 541205 | BLSPE 5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.92683 | 0.87992 | 0.92806 | 0.9 | 1.1 | CATEGORYB | SINGLE | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | 0 | 541235 | DUNCAN 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15512317SP |  |  | STROTHERS ROAD 161KV | REL | MIPU |  |  |  |  | 541246 | STROTHR5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.92821 | 0.88066 | 0.92006 | 0.9 | 1.1 | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEY 161KV CKT 1 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15582317SP |  |  | BLUE SPRING SOUTH 161KV | REL | MIPU |  |  |  |  | 541211 | BLSPS 5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.92863 | 0.88128 | 0.92559 | 0.9 | 1.1 | CATEGORYB | SINGLE | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | 0 | 541235 | DUNCAN 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15452317SP |  |  | LEES SUMMIT EAST 161KV | REL | MIPU |  |  |  |  | 541233 | LEESUM 5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93071 | 0.88243 | 0.92159 | 0.9 | 1.1 | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEY 161KV CKT 1 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15592317SP |  |  | RAYTOWN 161KV | REL | MIPU |  |  |  |  | 541219 | RAYTOWN5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93065 | 0.88281 | 0.91875 | 0.9 | 1.1 | CATEGORYB | SINGLE | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | 0 | 541235 | DUNCAN 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15502317SP |  |  | KC SOUTH 161KV | REL | MIPU |  |  |  |  | 541245 | KCSOUTH5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.92928 | 0.88327 | 0.92134 | 0.9 | 1.1 | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEY 161KV CKT 1 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16212317SP |  |  | RAYTOWN 161KV | REL | MIPU |  |  |  |  | 541219 | RAYTOWN5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93503 | 0.8834 | 0.91875 | 0.9 | 1.1 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15412317SP |  |  | WESTERN ELECTRIC 161KV | REL | MIPU |  |  |  |  | 541222 | WSTELEC5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93055 | 0.88356 | 0.92014 | 0.9 | 1.1 | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEY 161KV CKT 1 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16232317SP |  |  | WESTERN ELECTRIC 161KV | REL | MIPU |  |  |  |  | 541222 | WSTELEC5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93671 | 0.88384 | 0.92014 | 0.9 | 1.1 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16302317SP |  |  | LAKEWOOD 161KV | REL | MIPU |  |  |  |  | 541238 | LKWOOD 5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93475 | 0.88405 | 0.91872 | 0.9 | 1.1 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16332317SP |  |  | STROTHERS ROAD 161KV | REL | MIPU |  |  |  |  | 541246 | STROTHR5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93718 | 0.88441 | 0.92006 | 0.9 | 1.1 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16222317SP |  |  | FROST ROAD 161KV | REL | MIPU |  |  |  |  | 541220 | FROSTRD5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93711 | 0.88513 | 0.92095 | 0.9 | 1.1 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16322317SP |  |  | KC SOUTH 161KV | REL | MIPU |  |  |  |  | 541245 | KCSOUTH5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93687 | 0.88537 | 0.92134 | 0.9 | 1.1 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16182317SP |  |  | PRAIRIE LEE 161KV | REL | MIPU |  |  |  |  | 541206 | PRALEE 5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93897 | 0.88657 | 0.92135 | 0.9 | 1.1 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16282317SP |  |  | LEES SUMMIT EAST 161KV | REL | MIPU |  |  |  |  | 541233 | LEESUM 5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.94 | 0.8867 | 0.92159 | 0.9 | 1.1 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16252317SP |  |  | LONGVIEW 161KV | REL | MIPU |  |  |  |  | 541224 | LNGVW 5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93834 | 0.88723 | 0.92344 | 0.9 | 1.1 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15602317SP |  |  | FROST ROAD 161KV | REL | MIPU |  |  |  |  | 541220 | FROSTRD5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93541 | 0.88821 | 0.92095 | 0.9 | 1.1 | CATEGORYB | SINGLE | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | 0 | 541235 | DUNCAN 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16342317SP |  |  | HOOK ROAD 161KV | REL | MIPU |  |  |  |  | 541249 | HOOKRD 5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93906 | 0.88845 | 0.92431 | 0.9 | 1.1 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15572317SP |  |  | PRAIRIE LEE 161KV | REL | MIPU |  |  |  |  | 541206 | PRALEE 5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93647 | 0.88862 | 0.92135 | 0.9 | 1.1 | CATEGORYB | SINGLE | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | 0 | 541235 | DUNCAN 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12302317SP |  |  | WESTERN ELECTRIC 161KV | REL | MIPU |  |  |  |  | 541222 | WSTELEC5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93783 | 0.88874 | 0.92014 | 0.9 | 1.1 | CATEGORYB | SINGLE | CRAIG - STRANGER CREEK 345KV CKT 1 | 0 | 532772 | STRANGR7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15632317SP |  |  | GRAIN VALLEY 161KV | REL | MIPU |  |  |  |  | 541226 | GRAINVL5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.92789 | 0.88893 | 0.92806 | 0.9 | 1.1 | CATEGORYB | SINGLE | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | 0 | 541235 | DUNCAN 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12372317SP |  |  | STROTHERS ROAD 161KV | REL | MIPU |  |  |  |  | 541246 | STROTHR5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93832 | 0.88925 | 0.92006 | 0.9 | 1.1 | CATEGORYB | SINGLE | CRAIG - STRANGER CREEK 345KV CKT 1 | 0 | 532772 | STRANGR7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15422317SP |  |  | LONGVIEW 161KV | REL | MIPU |  |  |  |  | 541224 | LNGVW 5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93418 | 0.88935 | 0.92344 | 0.9 | 1.1 | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEY 161KV CKT 1 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12362317SP |  |  | KC SOUTH 161KV | REL | MIPU |  |  |  |  | 541245 | KCSOUTH5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93787 | 0.89009 | 0.92134 | 0.9 | 1.1 | CATEGORYB | SINGLE | CRAIG - STRANGER CREEK 345KV CKT 1 | 0 | 532772 | STRANGR7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16362317SP |  |  | LONE JACK 161KV | REL | MIPU |  |  |  |  | 541316 | LONEJACK 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.94482 | 0.89096 | 0.92588 | 0.9 | 1.1 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16312317SP |  |  | LAKE WINNEBAGO 161KV | REL | MIPU |  |  |  |  | 541243 | LKWINGB5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.9409 | 0.89102 | 0.9265 | 0.9 | 1.1 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16202317SP |  |  | GREENWOOD ENERGY CENTER 161KV | REL | MIPU |  |  |  |  | 541218 | GRNWD 5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.94509 | 0.89129 | 0.9262 | 0.9 | 1.1 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15822317SP |  |  | GRANDVIEW EAST 161KV | REL | MIPU |  |  |  |  | 541223 | GRDVWE 5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93853 | 0.8916 | 0.93544 | 0.9 | 1.1 | CATEGORYB | SINGLE | GRANDVIEW EAST - MARTIN CITY 161KV CKT 1 | 0 | 541210 | MARTCTY5 161.00 | 541223 | GRDVWE 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V24092317SP |  |  | BLUE SPRING SOUTH 161KV | REL | MIPU |  |  |  |  | 541211 | BLSPS 5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93132 | 0.89168 | 0.92559 | 0.9 | 1.1 | CATEGORYB | GENOUT | GEN541151 3-SIBLEY GENERATING UNIT #3 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12322317SP |  |  | LEES SUMMIT EAST 161KV | REL | MIPU |  |  |  |  | 541233 | LEESUM 5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.94136 | 0.89171 | 0.92159 | 0.9 | 1.1 | CATEGORYB | SINGLE | CRAIG - STRANGER CREEK 345KV CKT 1 | 0 | 532772 | STRANGR7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16372317SP |  |  | SAMPSON 161KV | REL | MIPU |  |  |  |  | 541345 | SAMPSON5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.94119 | 0.89196 | 0.92849 | 0.9 | 1.1 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15522317SP |  |  | HOOK ROAD 161KV | REL | MIPU |  |  |  |  | 541249 | HOOKRD 5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93613 | 0.89196 | 0.92431 | 0.9 | 1.1 | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEY 161KV CKT 1 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12312317SP |  |  | LONGVIEW 161KV | REL | MIPU |  |  |  |  | 541224 | LNGVW 5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93944 | 0.89209 | 0.92344 | 0.9 | 1.1 | CATEGORYB | SINGLE | CRAIG - STRANGER CREEK 345KV CKT 1 | 0 | 532772 | STRANGR7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15542317SP |  |  | LONE JACK 161KV | REL | MIPU |  |  |  |  | 541316 | LONEJACK 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.94015 | 0.89212 | 0.92588 | 0.9 | 1.1 | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEY 161KV CKT 1 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15442317SP |  |  | OAK GROVE 161KV | REL | MIPU |  |  |  |  | 541227 | OAKGRV 5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.92213 | 0.89225 | 0.93186 | 0.9 | 1.1 | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEY 161KV CKT 1 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15382317SP |  |  | GREENWOOD ENERGY CENTER 161KV | REL | MIPU |  |  |  |  | 541218 | GRNWD 5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.94042 | 0.89245 | 0.9262 | 0.9 | 1.1 | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEY 161KV CKT 1 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V24072317SP |  |  | BLUE SPRINGS EAST 161KV | REL | MIPU |  |  |  |  | 541205 | BLSPE 5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.931 | 0.89297 | 0.92806 | 0.9 | 1.1 | CATEGORYB | GENOUT | GEN541151 3-SIBLEY GENERATING UNIT #3 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16352317SP |  |  | HARRIS ROAD 161KV | REL | MIPU |  |  |  |  | 541313 | HARRIS 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.94498 | 0.89301 | 0.92792 | 0.9 | 1.1 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12382317SP |  |  | HOOK ROAD 161KV | REL | MIPU |  |  |  |  | 541249 | HOOKRD 5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.94039 | 0.89353 | 0.92431 | 0.9 | 1.1 | CATEGORYB | SINGLE | CRAIG - STRANGER CREEK 345KV CKT 1 | 0 | 532772 | STRANGR7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15882317SP |  |  | SAMPSON 161KV | REL | MIPU |  |  |  |  | 541345 | SAMPSON5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.94016 | 0.89361 | 0.92849 | 0.9 | 1.1 | CATEGORYB | SINGLE | GRANDVIEW EAST - MARTIN CITY 161KV CKT 1 | 0 | 541210 | MARTCTY5 161.00 | 541223 | GRDVWE 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V24152317SP |  |  | GRAIN VALLEY 161KV | REL | MIPU |  |  |  |  | 541226 | GRAINVL5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.92636 | 0.89446 | 0.92806 | 0.9 | 1.1 | CATEGORYB | GENOUT | GEN541151 3-SIBLEY GENERATING UNIT #3 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15782317SP |  |  | WHITEMAN AIR FORCE BASE 161KV | REL | MIPU |  |  |  |  | 541234 | WAFB 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.93905 | 0.8945 | 0.97209 | 0.9 | 1.1 | CATEGORYB | SINGLE | SEDALIA - WHITEMAN AIR FORCE BASE 161KV CKT 1 | 0 | 541209 | SEDALIA5 161.00 | 541234 | WAFB 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15492317SP |  |  | LAKE WINNEBAGO 161KV | REL | MIPU |  |  |  |  | 541243 | LKWINGB5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93923 | 0.89594 | 0.9265 | 0.9 | 1.1 | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEY 161KV CKT 1 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15532317SP |  |  | HARRIS ROAD 161KV | REL | MIPU |  |  |  |  | 541313 | HARRIS 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.94198 | 0.89614 | 0.92792 | 0.9 | 1.1 | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEY 161KV CKT 1 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21622317SP |  |  | LONE JACK 161KV | REL | MIPU |  |  |  |  | 541316 | LONEJACK 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.95094 | 0.89618 | 0.92588 | 0.9 | 1.1 | CATEGORYB | SINGLE | PLEASANT HILL () 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 541200 | PHILL 7 345.00 | 541225 | PHILL 5 161.00 | 541361 | PHILL T 13.800 | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16262317SP |  |  | PLEASANT HILL 161KV | REL | MIPU |  |  |  |  | 541225 | PHILL 5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.94484 | 0.89625 | 0.93118 | 0.9 | 1.1 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12352317SP |  |  | LAKE WINNEBAGO 161KV | REL | MIPU |  |  |  |  | 541243 | LKWINGB5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.94249 | 0.89635 | 0.9265 | 0.9 | 1.1 | CATEGORYB | SINGLE | CRAIG - STRANGER CREEK 345KV CKT 1 | 0 | 532772 | STRANGR7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12412317SP |  |  | SAMPSON 161KV | REL | MIPU |  |  |  |  | 541345 | SAMPSON5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.94197 | 0.89649 | 0.92849 | 0.9 | 1.1 | CATEGORYB | SINGLE | CRAIG - STRANGER CREEK 345KV CKT 1 | 0 | 532772 | STRANGR7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21492317SP |  |  | GREENWOOD ENERGY CENTER 161KV | REL | MIPU |  |  |  |  | 541218 | GRNWD 5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.95121 | 0.89651 | 0.9262 | 0.9 | 1.1 | CATEGORYB | SINGLE | PLEASANT HILL () 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 541200 | PHILL 7 345.00 | 541225 | PHILL 5 161.00 | 541361 | PHILL T 13.800 | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V24182317SP |  |  | DUNCAN ROAD 161KV | REL | MIPU |  |  |  |  | 541235 | DUNCAN 5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.93335 | 0.89676 | 0.93328 | 0.9 | 1.1 | CATEGORYB | GENOUT | GEN541151 3-SIBLEY GENERATING UNIT #3 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21612317SP |  |  | HARRIS ROAD 161KV | REL | MIPU |  |  |  |  | 541313 | HARRIS 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.95074 | 0.89753 | 0.92792 | 0.9 | 1.1 | CATEGORYB | SINGLE | PLEASANT HILL () 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 541200 | PHILL 7 345.00 | 541225 | PHILL 5 161.00 | 541361 | PHILL T 13.800 | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15772317SP |  |  | WARRENSBURG EAST 161KV | REL | MIPU |  |  |  |  | 541228 | WBURGE 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.94186 | 0.89797 | 0.96416 | 0.9 | 1.1 | CATEGORYB | SINGLE | SEDALIA - WHITEMAN AIR FORCE BASE 161KV CKT 1 | 0 | 541209 | SEDALIA5 161.00 | 541234 | WAFB 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16242317SP |  |  | GRANDVIEW EAST 161KV | REL | MIPU |  |  |  |  | 541223 | GRDVWE 5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.94521 | 0.89852 | 0.93544 | 0.9 | 1.1 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21542317SP |  |  | PLEASANT HILL 161KV | REL | MIPU |  |  |  |  | 541225 | PHILL 5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.94996 | 0.89947 | 0.93118 | 0.9 | 1.1 | CATEGORYB | SINGLE | PLEASANT HILL () 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 541200 | PHILL 7 345.00 | 541225 | PHILL 5 161.00 | 541361 | PHILL T 13.800 | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V24162317SP |  |  | OAK GROVE 161KV | REL | MIPU |  |  |  |  | 541227 | OAKGRV 5 161.00 | [5 empty] | 17SP | [5 empty] | 540_BLUE SPRINGS EAST CAP BANK | 0.9251 | 0.89989 | 0.93186 | 0.9 | 1.1 | CATEGORYB | GENOUT | GEN541151 3-SIBLEY GENERATING UNIT #3 | 0 | 541202 | SIBLEY 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  |  | MIPU | BLUE SPRINGS EAST CAP BANK | Add 50 MVAR cap bank at Blue Springs East | [5 empty] | 18 | [6 empty] | 1400000 | 2007-08-22 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V17222217SP |  |  | EXCELSIOR 69KV | EXP | AEPW |  | GRENWOOD |  |  | 507185 | EXCELSR2 69.000 | [5 empty] | 17SP | [6 empty] | 0.9008 | 0.87963 | 0.94017 | 0.9 | 1.05 | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 99486 | 8ANO 50 500.00 | 515305 | FTSMITH8 500.00 | 0 |  | 1 |  |  |  |  | AEPW | BONANZA - NORTH HUNTINGTON 69KV | Convert from 69KV to 161KV | [37 empty] | 2014-06-01 | 2014-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V17232217SP |  |  | WALDRON 69KV | EXP | AEPW |  | GRENWOOD |  |  | 507191 | WALDRON2 69.000 | [5 empty] | 17SP | [6 empty] | 0.90985 | 0.88775 | 0.95398 | 0.9 | 1.05 | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 99486 | 8ANO 50 500.00 | 515305 | FTSMITH8 500.00 | 0 |  | 1 |  |  |  |  | AEPW | BONANZA - NORTH HUNTINGTON 69KV | Convert from 69KV to 161KV | [37 empty] | 2014-06-01 | 2014-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V17242217SP |  |  | SUGRLFTP 69.000 69KV | EXP | AEPW |  | GRWDAECC |  |  | 507201 | SUGRLFTP 69.000 | [5 empty] | 17SP | [6 empty] | 0.91293 | 0.89207 | 0.95179 | 0.9 | 1.05 | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE 500 - FT SMITH 500 500KV CKT 1 | 0 | 99486 | 8ANO 50 500.00 | 515305 | FTSMITH8 500.00 | 0 |  | 1 |  |  |  |  | AEPW | BONANZA - NORTH HUNTINGTON 69KV | Convert from 69KV to 161KV | [37 empty] | 2014-06-01 | 2014-06-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FNSL | FDNS-Blown up | 3 | 3 | 2008-12-01 | 2007AG1AFS82V23312SP |  |  | WALKEMEYER 115KV | EXP | SUNC |  | PIONEER |  |  | 531405 | WALKMYR3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.87453 | 0.97357 | 0.9 | 1.1 | CATEGORYB | SINGLE | CUDAHY - JUDSON LARGE 115KV CKT 1 | 0 | 539671 | JUD-LRG3 115.00 | 539659 | CUDAHY 3 115.00 | 0 |  | 1 |  |  |  |  | MKEC | Cimarron Plant Substation Expansion | Integrate SUNC North Cimarron Top into reconfigured WEPL Cimarron Plant Sub | [12 empty] | 2500000 | 2006-06-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V10084412SP |  |  | ROSE HILL 69KV | S | WERE |  | SCENTRAL |  |  | 533836 | ROSEHIL2 69.000 | [5 empty] | 12SP | [6 empty] | 0.97764 | 0.92884 | 1.01405 | 0.95 | 1.05 | CATEGORYB | SINGLE | ROSE HILL JUNCTION - WEAVER 69KV CKT 1 | 0 | 533604 | WEAVER 2 69.000 | 533837 | RH JCT 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | CITY OF WINFIELD - RAINBOW 69KV CKT 1 | Rebuild 3.99-mile Rainbow-Winfield 69 kV line, 954 ACSR | 72 | 72 | 72 | 72 | 3.99 | 12 | 4 | N | 0.00841 | 0.05727 | 0.00122 | Line switches limit to 72 MVA | 1645279 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V10084412SP |  |  | ROSE HILL 69KV | S | WERE |  | SCENTRAL |  |  | 533836 | ROSEHIL2 69.000 | [5 empty] | 12SP | [6 empty] | 0.97764 | 0.92884 | 1.01405 | 0.95 | 1.05 | CATEGORYB | SINGLE | ROSE HILL JUNCTION - WEAVER 69KV CKT 1 | 0 | 533604 | WEAVER 2 69.000 | 533837 | RH JCT 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | CITY OF WINFIELD - RAINBOW 69KV CKT 1 | Rebuild 3.99-mile Rainbow-Winfield 69 kV line, 954 ACSR | 72 | 72 | 72 | 72 | 3.99 | 12 | 4 | N | 0.00841 | 0.05727 | 0.00122 | Line switches limit to 72 MVA | 1645279 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V10084412SP |  |  | ROSE HILL 69KV | S | WERE |  | SCENTRAL |  |  | 533836 | ROSEHIL2 69.000 | [5 empty] | 12SP | [6 empty] | 0.97764 | 0.92884 | 1.01405 | 0.95 | 1.05 | CATEGORYB | SINGLE | ROSE HILL JUNCTION - WEAVER 69KV CKT 1 | 0 | 533604 | WEAVER 2 69.000 | 533837 | RH JCT 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | CITY OF WINFIELD - RAINBOW 69KV CKT 1 | Rebuild 3.99-mile Rainbow-Winfield 69 kV line, 954 ACSR | 72 | 72 | 72 | 72 | 3.99 | 12 | 4 | N | 0.00841 | 0.05727 | 0.00122 | Line switches limit to 72 MVA | 1645279 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V10084412SP |  |  | ROSE HILL 69KV | S | WERE |  | SCENTRAL |  |  | 533836 | ROSEHIL2 69.000 | [5 empty] | 12SP | [6 empty] | 0.97764 | 0.92884 | 1.01405 | 0.95 | 1.05 | CATEGORYB | SINGLE | ROSE HILL JUNCTION - WEAVER 69KV CKT 1 | 0 | 533604 | WEAVER 2 69.000 | 533837 | RH JCT 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | CITY OF WINFIELD - RAINBOW 69KV CKT 1 | Rebuild 3.99-mile Rainbow-Winfield 69 kV line, 954 ACSR | 72 | 72 | 72 | 72 | 3.99 | 12 | 4 | N | 0.00841 | 0.05727 | 0.00122 | Line switches limit to 72 MVA | 1645279 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V9572312SP |  |  | CRAIG 345KV | S | KACP |  | KACP |  |  | 542977 | CRAIG 7 345.00 | [5 empty] | 12SP | [6 empty] | 0.90501 | 0.87623 | 0.93668 | 0.9 | 1.05 | CATEGORYB | SINGLE | CRAIG - STRANGER CREEK 345KV CKT 1 | 0 | 532772 | STRANGR7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  |  |  |  | KACP | Craig 161kV 20MVar Cap Bank Upgrade | Additional 20 MVAR to make a total of 70 MVAR at Craig 542978 | [5 empty] | 18 | [6 empty] | 50000 | [24 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V9562312SP |  |  | WEST GARDNER 345KV | S | KACP |  | KACP |  |  | 542965 | W.GRDNR7 345.00 | [5 empty] | 12SP | [6 empty] | 0.92026 | 0.89216 | 0.9468 | 0.9 | 1.05 | CATEGORYB | SINGLE | CRAIG - STRANGER CREEK 345KV CKT 1 | 0 | 532772 | STRANGR7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  |  |  |  | KACP | Craig 161kV 20MVar Cap Bank Upgrade | Additional 20 MVAR to make a total of 70 MVAR at Craig 542978 | [5 empty] | 18 | [6 empty] | 50000 | [24 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V472312SP |  |  | SPRINT #2 161KV | S | KACP |  | JOCO |  |  | 543075 | SPRINT25 161.00 | [5 empty] | 12SP | [6 empty] | 0.96923 | 0.94862 | 0.94862 | 0.95 | 1.05 | CATEGORYA | BASECASE | BASE CASE | 0 | 532772 | STRANGR7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  |  |  |  | KACP | Craig 161kV 20MVar Cap Bank Upgrade | Additional 20 MVAR to make a total of 70 MVAR at Craig 542978 | [5 empty] | 18 | [6 empty] | 50000 | [24 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V462312SP |  |  | RILEY 161KV | S | KACP |  | JOCO |  |  | 543051 | RILEY 5 161.00 | [5 empty] | 12SP | [6 empty] | 0.96937 | 0.94876 | 0.94876 | 0.95 | 1.05 | CATEGORYA | BASECASE | BASE CASE | 0 | 532772 | STRANGR7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  |  |  |  | KACP | Craig 161kV 20MVar Cap Bank Upgrade | Additional 20 MVAR to make a total of 70 MVAR at Craig 542978 | [5 empty] | 18 | [6 empty] | 50000 | [24 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12432317SP |  |  | CRAIG 345KV | S | KACP |  | KACP |  |  | 542977 | CRAIG 7 345.00 | [5 empty] | 17SP | [6 empty] | 0.90739 | 0.87807 | 0.93534 | 0.9 | 1.05 | CATEGORYB | SINGLE | CRAIG - STRANGER CREEK 345KV CKT 1 | 0 | 532772 | STRANGR7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  |  |  |  | KACP | Craig 161kV 20MVar Cap Bank Upgrade | Additional 20 MVAR to make a total of 70 MVAR at Craig 542978 | [5 empty] | 18 | [6 empty] | 50000 | [24 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12422317SP |  |  | WEST GARDNER 345KV | S | KACP |  | KACP |  |  | 542965 | W.GRDNR7 345.00 | [5 empty] | 17SP | [6 empty] | 0.92456 | 0.89592 | 0.94771 | 0.9 | 1.05 | CATEGORYB | SINGLE | CRAIG - STRANGER CREEK 345KV CKT 1 | 0 | 532772 | STRANGR7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  |  |  |  | KACP | Craig 161kV 20MVar Cap Bank Upgrade | Additional 20 MVAR to make a total of 70 MVAR at Craig 542978 | [5 empty] | 18 | [6 empty] | 50000 | [24 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12452317SP |  |  | SPRINT #2 161KV | S | KACP |  | JOCO |  |  | 543075 | SPRINT25 161.00 | [5 empty] | 17SP | [6 empty] | 0.93123 | 0.89936 | 0.94558 | 0.9 | 1.05 | CATEGORYB | SINGLE | CRAIG - STRANGER CREEK 345KV CKT 1 | 0 | 532772 | STRANGR7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  |  |  |  | KACP | Craig 161kV 20MVar Cap Bank Upgrade | Additional 20 MVAR to make a total of 70 MVAR at Craig 542978 | [5 empty] | 18 | [6 empty] | 50000 | [24 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12442317SP |  |  | RILEY 161KV | S | KACP |  | JOCO |  |  | 543051 | RILEY 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.93139 | 0.89953 | 0.94573 | 0.9 | 1.05 | CATEGORYB | SINGLE | CRAIG - STRANGER CREEK 345KV CKT 1 | 0 | 532772 | STRANGR7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  |  |  |  | KACP | Craig 161kV 20MVar Cap Bank Upgrade | Additional 20 MVAR to make a total of 70 MVAR at Craig 542978 | [5 empty] | 18 | [6 empty] | 50000 | [24 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V614112WP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 12WP | [6 empty] | 0.96701 | 0.94498 | 0.97736 | 0.95 | 1.05 | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | DEARING 138KV Capacitor Displacement | Dearing 138 kV 20 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 810000 | 2008-01-01 | [23 empty] | 2012-12-01 | 2012-12-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V624112WP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 12WP | [6 empty] | 0.96707 | 0.94504 | 0.97742 | 0.95 | 1.05 | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | DEARING 138KV Capacitor Displacement | Dearing 138 kV 20 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 810000 | 2008-01-01 | [23 empty] | 2012-12-01 | 2012-12-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V522212WP |  |  | DEARING 138KV | S | WERE |  | SEAST |  |  | 533002 | DEARING4 138.00 | [5 empty] | 12WP | [6 empty] | 0.96698 | 0.94566 | 0.98584 | 0.95 | 1.05 | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | DEARING 138KV Capacitor Displacement | Dearing 138 kV 20 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 810000 | 2008-01-01 | [23 empty] | 2012-12-01 | 2012-12-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V532212WP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 12WP | [6 empty] | 0.97048 | 0.94578 | 0.98117 | 0.95 | 1.05 | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | DEARING 138KV Capacitor Displacement | Dearing 138 kV 20 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 810000 | 2008-01-01 | [23 empty] | 2012-12-01 | 2012-12-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V3614112WP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 12WP | [6 empty] | 0.98626 | 0.94853 | 0.97736 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-20 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | DEARING 138KV Capacitor Displacement | Dearing 138 kV 20 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 810000 | 2008-01-01 | [23 empty] | 2012-12-01 | 2012-12-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V3624112WP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 12WP | [6 empty] | 0.98632 | 0.94859 | 0.97742 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-20 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | DEARING 138KV Capacitor Displacement | Dearing 138 kV 20 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 810000 | 2008-01-01 | [23 empty] | 2012-12-01 | 2012-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V2122217SP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 17SP | [6 empty] | 0.95535 | 0.93316 | 0.96942 | 0.95 | 1.05 | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | DEARING 138KV Capacitor Displacement | Dearing 138 kV 20 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 810000 | 2008-01-01 | [23 empty] | 2012-12-01 | 2012-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V2132217SP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 17SP | [6 empty] | 0.95682 | 0.9339 | 0.96907 | 0.95 | 1.05 | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | DEARING 138KV Capacitor Displacement | Dearing 138 kV 20 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 810000 | 2008-01-01 | [23 empty] | 2012-12-01 | 2012-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V2142217SP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 17SP | [6 empty] | 0.95693 | 0.93401 | 0.96918 | 0.95 | 1.05 | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | DEARING 138KV Capacitor Displacement | Dearing 138 kV 20 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 810000 | 2008-01-01 | [23 empty] | 2012-12-01 | 2012-12-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V20033317SP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 17SP | [6 empty] | 0.97016 | 0.94495 | 0.96581 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-19 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | DEARING 138KV Capacitor Displacement | Dearing 138 kV 20 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 810000 | 2008-01-01 | [23 empty] | 2012-12-01 | 2012-12-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V11663317SP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 17SP | [6 empty] | 0.98445 | 0.94496 | 0.96565 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | DEARING 138KV Capacitor Displacement | Dearing 138 kV 20 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 810000 | 2008-01-01 | [23 empty] | 2012-12-01 | 2012-12-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V11673317SP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 17SP | [6 empty] | 0.98455 | 0.94508 | 0.96576 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | DEARING 138KV Capacitor Displacement | Dearing 138 kV 20 MVAR Capacitor Addition | [5 empty] | 18 | 18 | [5 empty] | 810000 | 2008-01-01 | [23 empty] | 2012-12-01 | 2012-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V7942309SP |  |  | WOODBINE 161KV | EXP | MIPU |  | FLA |  |  | 541258 | WOODBIN5 161.00 | [5 empty] | 09SP | [6 empty] | 0.89252 | 0.87113 | 0.97647 | 0.9 | 1.1 | CATEGORYB | SINGLE | ST JOE - WOODBINE 161KV CKT 1 | 0 | 541253 | ST JOE 5 161.00 | 541258 | WOODBIN5 161.00 | 0 |  | 1 |  |  |  |  | SJLP | EAST 20MVAR CAPACITOR # 1 | Add 20MVAR capacitor at East 161kV | [5 empty] | 12 | [6 empty] | 600000 | [24 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V7922309SP |  |  | EAST 161KV | EXP | MIPU |  | FLA |  |  | 541254 | EAST 5 161.00 | [5 empty] | 09SP | [6 empty] | 0.89314 | 0.87177 | 0.97203 | 0.9 | 1.1 | CATEGORYB | SINGLE | ST JOE - WOODBINE 161KV CKT 1 | 0 | 541253 | ST JOE 5 161.00 | 541258 | WOODBIN5 161.00 | 0 |  | 1 |  |  |  |  | SJLP | EAST 20MVAR CAPACITOR # 1 | Add 20MVAR capacitor at East 161kV | [5 empty] | 12 | [6 empty] | 600000 | [24 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V7932309SP |  |  | INDUSTRIAL PARK 161KV | EXP | MIPU |  | FLA |  |  | 541256 | IND PRK5 161.00 | [5 empty] | 09SP | [6 empty] | 0.90174 | 0.8806 | 0.96785 | 0.9 | 1.1 | CATEGORYB | SINGLE | ST JOE - WOODBINE 161KV CKT 1 | 0 | 541253 | ST JOE 5 161.00 | 541258 | WOODBIN5 161.00 | 0 |  | 1 |  |  |  |  | SJLP | EAST 20MVAR CAPACITOR # 1 | Add 20MVAR capacitor at East 161kV | [5 empty] | 12 | [6 empty] | 600000 | [24 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V7952309SP |  |  | EAST 161KV | EXP | MIPU |  | FLA |  |  | 541254 | EAST 5 161.00 | [5 empty] | 09SP | [6 empty] | 0.90637 | 0.88597 | 0.97203 | 0.9 | 1.1 | CATEGORYB | SINGLE | EAST - WOODBINE 161KV CKT 1 | 0 | 541258 | WOODBIN5 161.00 | 541254 | EAST 5 161.00 | 0 |  | 1 |  |  |  |  | SJLP | EAST 20MVAR CAPACITOR # 1 | Add 20MVAR capacitor at East 161kV | [5 empty] | 12 | [6 empty] | 600000 | [24 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V7962309SP |  |  | INDUSTRIAL PARK 161KV | EXP | MIPU |  | FLA |  |  | 541256 | IND PRK5 161.00 | [5 empty] | 09SP | [6 empty] | 0.91329 | 0.89307 | 0.96785 | 0.9 | 1.1 | CATEGORYB | SINGLE | EAST - WOODBINE 161KV CKT 1 | 0 | 541258 | WOODBIN5 161.00 | 541254 | EAST 5 161.00 | 0 |  | 1 |  |  |  |  | SJLP | EAST 20MVAR CAPACITOR # 1 | Add 20MVAR capacitor at East 161kV | [5 empty] | 12 | [6 empty] | 600000 | [24 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12712312SP |  |  | WOODBINE 161KV | EXP | MIPU |  | FLA |  |  | 541258 | WOODBIN5 161.00 | [5 empty] | 12SP | [6 empty] | 0.91909 | 0.85982 | 0.97703 | 0.9 | 1.1 | CATEGORYB | SINGLE | ST JOE - WOODBINE 161KV CKT 1 | 0 | 541253 | ST JOE 5 161.00 | 541258 | WOODBIN5 161.00 | 0 |  | 1 |  |  |  |  | SJLP | EAST 20MVAR CAPACITOR # 1 | Add 20MVAR capacitor at East 161kV | [5 empty] | 12 | [6 empty] | 600000 | [24 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12692312SP |  |  | EAST 161KV | EXP | MIPU |  | FLA |  |  | 541254 | EAST 5 161.00 | [5 empty] | 12SP | [6 empty] | 0.91963 | 0.86051 | 0.97231 | 0.9 | 1.1 | CATEGORYB | SINGLE | ST JOE - WOODBINE 161KV CKT 1 | 0 | 541253 | ST JOE 5 161.00 | 541258 | WOODBIN5 161.00 | 0 |  | 1 |  |  |  |  | SJLP | EAST 20MVAR CAPACITOR # 1 | Add 20MVAR capacitor at East 161kV | [5 empty] | 12 | [6 empty] | 600000 | [24 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12702312SP |  |  | INDUSTRIAL PARK 161KV | EXP | MIPU |  | FLA |  |  | 541256 | IND PRK5 161.00 | [5 empty] | 12SP | [6 empty] | 0.927 | 0.86992 | 0.96785 | 0.9 | 1.1 | CATEGORYB | SINGLE | ST JOE - WOODBINE 161KV CKT 1 | 0 | 541253 | ST JOE 5 161.00 | 541258 | WOODBIN5 161.00 | 0 |  | 1 |  |  |  |  | SJLP | EAST 20MVAR CAPACITOR # 1 | Add 20MVAR capacitor at East 161kV | [5 empty] | 12 | [6 empty] | 600000 | [24 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12722312SP |  |  | EAST 161KV | EXP | MIPU |  | FLA |  |  | 541254 | EAST 5 161.00 | [5 empty] | 12SP | [6 empty] | 0.92957 | 0.87603 | 0.97231 | 0.9 | 1.1 | CATEGORYB | SINGLE | EAST - WOODBINE 161KV CKT 1 | 0 | 541258 | WOODBIN5 161.00 | 541254 | EAST 5 161.00 | 0 |  | 1 |  |  |  |  | SJLP | EAST 20MVAR CAPACITOR # 1 | Add 20MVAR capacitor at East 161kV | [5 empty] | 12 | [6 empty] | 600000 | [24 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12732312SP |  |  | INDUSTRIAL PARK 161KV | EXP | MIPU |  | FLA |  |  | 541256 | IND PRK5 161.00 | [5 empty] | 12SP | [6 empty] | 0.93556 | 0.88358 | 0.96785 | 0.9 | 1.1 | CATEGORYB | SINGLE | EAST - WOODBINE 161KV CKT 1 | 0 | 541258 | WOODBIN5 161.00 | 541254 | EAST 5 161.00 | 0 |  | 1 |  |  |  |  | SJLP | EAST 20MVAR CAPACITOR # 1 | Add 20MVAR capacitor at East 161kV | [5 empty] | 12 | [6 empty] | 600000 | [24 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V13642312SP |  |  | NEVADA 161KV | EXP | MIPU |  |  |  |  | 541208 | NEVADA 5 161.00 | [5 empty] | 12SP | [6 empty] | 0.92344 | 0.89928 | 0.93681 | 0.9 | 1.1 | CATEGORYB | SINGLE | STOCKTON - STOCKTON AECI 161KV CKT 1 | 0 | 505498 | STOCKTN5 161.00 | 96118 | 5STKAEC 161.00 | 0 |  | 1 |  |  |  |  | SJLP | EAST 20MVAR CAPACITOR # 1 | Add 20MVAR capacitor at East 161kV | [5 empty] | 12 | [6 empty] | 600000 | [24 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V13642312SP |  |  | NEVADA 161KV | EXP | MIPU |  |  |  |  | 541208 | NEVADA 5 161.00 | [5 empty] | 12SP | [6 empty] | 0.92344 | 0.89928 | 0.93681 | 0.9 | 1.1 | CATEGORYB | SINGLE | STOCKTON - STOCKTON AECI 161KV CKT 1 | 0 | 505498 | STOCKTN5 161.00 | 96118 | 5STKAEC 161.00 | 0 |  | 1 |  |  |  |  | SJLP | EAST 20MVAR CAPACITOR # 1 | Add 20MVAR capacitor at East 161kV | [5 empty] | 12 | [6 empty] | 600000 | [24 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15952317SP |  |  | WOODBINE 161KV | EXP | MIPU |  | FLA |  |  | 541258 | WOODBIN5 161.00 | [5 empty] | 17SP | [6 empty] | 0.90327 | 0.859 | 0.97671 | 0.9 | 1.1 | CATEGORYB | SINGLE | ST JOE - WOODBINE 161KV CKT 1 | 0 | 541253 | ST JOE 5 161.00 | 541258 | WOODBIN5 161.00 | 0 |  | 1 |  |  |  |  | SJLP | EAST 20MVAR CAPACITOR # 1 | Add 20MVAR capacitor at East 161kV | [5 empty] | 12 | [6 empty] | 600000 | [24 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15932317SP |  |  | EAST 161KV | EXP | MIPU |  | FLA |  |  | 541254 | EAST 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.90386 | 0.85972 | 0.97183 | 0.9 | 1.1 | CATEGORYB | SINGLE | ST JOE - WOODBINE 161KV CKT 1 | 0 | 541253 | ST JOE 5 161.00 | 541258 | WOODBIN5 161.00 | 0 |  | 1 |  |  |  |  | SJLP | EAST 20MVAR CAPACITOR # 1 | Add 20MVAR capacitor at East 161kV | [5 empty] | 12 | [6 empty] | 600000 | [24 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15942317SP |  |  | INDUSTRIAL PARK 161KV | EXP | MIPU |  | FLA |  |  | 541256 | IND PRK5 161.00 | [5 empty] | 17SP | [6 empty] | 0.91192 | 0.86967 | 0.96733 | 0.9 | 1.1 | CATEGORYB | SINGLE | ST JOE - WOODBINE 161KV CKT 1 | 0 | 541253 | ST JOE 5 161.00 | 541258 | WOODBIN5 161.00 | 0 |  | 1 |  |  |  |  | SJLP | EAST 20MVAR CAPACITOR # 1 | Add 20MVAR capacitor at East 161kV | [5 empty] | 12 | [6 empty] | 600000 | [24 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15962317SP |  |  | EAST 161KV | EXP | MIPU |  | FLA |  |  | 541254 | EAST 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.91541 | 0.87603 | 0.97183 | 0.9 | 1.1 | CATEGORYB | SINGLE | EAST - WOODBINE 161KV CKT 1 | 0 | 541258 | WOODBIN5 161.00 | 541254 | EAST 5 161.00 | 0 |  | 1 |  |  |  |  | SJLP | EAST 20MVAR CAPACITOR # 1 | Add 20MVAR capacitor at East 161kV | [5 empty] | 12 | [6 empty] | 600000 | [24 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15972317SP |  |  | INDUSTRIAL PARK 161KV | EXP | MIPU |  | FLA |  |  | 541256 | IND PRK5 161.00 | [5 empty] | 17SP | [6 empty] | 0.92193 | 0.88399 | 0.96733 | 0.9 | 1.1 | CATEGORYB | SINGLE | EAST - WOODBINE 161KV CKT 1 | 0 | 541258 | WOODBIN5 161.00 | 541254 | EAST 5 161.00 | 0 |  | 1 |  |  |  |  | SJLP | EAST 20MVAR CAPACITOR # 1 | Add 20MVAR capacitor at East 161kV | [5 empty] | 12 | [6 empty] | 600000 | [24 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V14582217SP |  |  | BUTLER 161KV | EXP | MIPU |  |  |  |  | 541216 | BUTLER_5 161.00 | [5 empty] | 17SP | [6 empty] | 0.9313 | 0.89082 | 0.95934 | 0.9 | 1.1 | CATEGORYB | SINGLE | ADRIAN - BUTLER 161KV CKT 1 | 0 | 541240 | ADRIAN 5 161.00 | 541216 | BUTLER_5 161.00 | 0 |  | 1 |  |  |  |  | SJLP | EAST 20MVAR CAPACITOR # 1 | Add 20MVAR capacitor at East 161kV | [5 empty] | 12 | [6 empty] | 600000 | [24 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V14582217SP |  |  | BUTLER 161KV | EXP | MIPU |  |  |  |  | 541216 | BUTLER_5 161.00 | [5 empty] | 17SP | [6 empty] | 0.9313 | 0.89082 | 0.95934 | 0.9 | 1.1 | CATEGORYB | SINGLE | ADRIAN - BUTLER 161KV CKT 1 | 0 | 541240 | ADRIAN 5 161.00 | 541216 | BUTLER_5 161.00 | 0 |  | 1 |  |  |  |  | SJLP | EAST 20MVAR CAPACITOR # 1 | Add 20MVAR capacitor at East 161kV | [5 empty] | 12 | [6 empty] | 600000 | [24 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V14582217SP |  |  | BUTLER 161KV | EXP | MIPU |  |  |  |  | 541216 | BUTLER_5 161.00 | [5 empty] | 17SP | [6 empty] | 0.9313 | 0.89082 | 0.95934 | 0.9 | 1.1 | CATEGORYB | SINGLE | ADRIAN - BUTLER 161KV CKT 1 | 0 | 541240 | ADRIAN 5 161.00 | 541216 | BUTLER_5 161.00 | 0 |  | 1 |  |  |  |  | SJLP | EAST 20MVAR CAPACITOR # 1 | Add 20MVAR capacitor at East 161kV | [5 empty] | 12 | [6 empty] | 600000 | [24 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V14572217SP |  |  | NEVADA 161KV | EXP | MIPU |  |  |  |  | 541208 | NEVADA 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.94016 | 0.89527 | 0.9481 | 0.9 | 1.1 | CATEGORYB | SINGLE | ADRIAN - BUTLER 161KV CKT 1 | 0 | 541240 | ADRIAN 5 161.00 | 541216 | BUTLER_5 161.00 | 0 |  | 1 |  |  |  |  | SJLP | EAST 20MVAR CAPACITOR # 1 | Add 20MVAR capacitor at East 161kV | [5 empty] | 12 | [6 empty] | 600000 | [24 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V14572217SP |  |  | NEVADA 161KV | EXP | MIPU |  |  |  |  | 541208 | NEVADA 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.94016 | 0.89527 | 0.9481 | 0.9 | 1.1 | CATEGORYB | SINGLE | ADRIAN - BUTLER 161KV CKT 1 | 0 | 541240 | ADRIAN 5 161.00 | 541216 | BUTLER_5 161.00 | 0 |  | 1 |  |  |  |  | SJLP | EAST 20MVAR CAPACITOR # 1 | Add 20MVAR capacitor at East 161kV | [5 empty] | 12 | [6 empty] | 600000 | [24 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V9362312SP |  |  | EDWARDSVILLE 161KV | REL | WERE |  | NEAST |  |  | 532912 | EDWRDVL5 161.00 | [5 empty] | 12SP | [6 empty] | 0.94188 | 0.91608 | 0.95199 | 0.95 | 1.05 | CATEGORYB | SINGLE | CRAIG - STRANGER CREEK 345KV CKT 1 | 0 | 532772 | STRANGR7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | EDWARDSVILLE 115KV Capacitor | Install 30 Mvar cap at Edwardsville 115 kV | [37 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12762312SP |  |  | EDWARDSVILLE 161KV | REL | WERE |  | NEAST |  |  | 532912 | EDWRDVL5 161.00 | [5 empty] | 12SP | [6 empty] | 0.94908 | 0.92371 | 0.95199 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | EDWARDSVILLE 115KV Capacitor | Install 30 Mvar cap at Edwardsville 115 kV | [37 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16772312SP |  |  | EDWARDSVILLE 161KV | REL | WERE |  | NEAST |  |  | 532912 | EDWRDVL5 161.00 | [5 empty] | 12SP | [6 empty] | 0.95085 | 0.92612 | 0.95199 | 0.95 | 1.05 | CATEGORYB | GENOUT | GEN542951 5-HAWTHORN UNIT #5 | 0 | 532772 | STRANGR7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | EDWARDSVILLE 115KV Capacitor | Install 30 Mvar cap at Edwardsville 115 kV | [37 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12142317SP |  |  | EDWARDSVILLE 161KV | REL | WERE |  | NEAST |  |  | 532912 | EDWRDVL5 161.00 | [5 empty] | 17SP | [6 empty] | 0.93988 | 0.91418 | 0.94628 | 0.95 | 1.05 | CATEGORYB | SINGLE | CRAIG - STRANGER CREEK 345KV CKT 1 | 0 | 532772 | STRANGR7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | EDWARDSVILLE 115KV Capacitor | Install 30 Mvar cap at Edwardsville 115 kV | [37 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16022317SP |  |  | EDWARDSVILLE 161KV | REL | WERE |  | NEAST |  |  | 532912 | EDWRDVL5 161.00 | [5 empty] | 17SP | [6 empty] | 0.94445 | 0.91849 | 0.94628 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | EDWARDSVILLE 115KV Capacitor | Install 30 Mvar cap at Edwardsville 115 kV | [37 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19732317SP |  |  | EDWARDSVILLE 161KV | REL | WERE |  | NEAST |  |  | 532912 | EDWRDVL5 161.00 | [5 empty] | 17SP | [6 empty] | 0.94455 | 0.92101 | 0.94628 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | EDWARDSVILLE 115KV Capacitor | Install 30 Mvar cap at Edwardsville 115 kV | [37 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V952217SP |  |  | EUREKA SPRINGS 161KV | EXP | AEPW |  | FAYETTEV |  |  | 506932 | EUREKA 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.88344 | 0.86264 | 0.94585 | 0.9 | 1.05 | CATEGORYB | SINGLE | BEAVER - EUREKA SPRINGS 161KV CKT 1 | 0 | 505480 | BEAVER 5 161.00 | 506932 | EUREKA 5 161.00 | 0 |  | 1 |  |  |  |  | AEPW | FLINT CREEK - SHIPE ROAD - EAST ROGERS - OSAGE 345KV | Install new 345kV line from FLINT CREEK - SHIPE ROAD - EAST ROGERS - OSAGE | [37 empty] | 2017-06-01 | 2017-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81V1345517SP |  |  | AVOCA 161KV | EXP | AEPW |  | FAYTAECC |  |  | 506966 | AVOCA--5 161.00 | [5 empty] | 17SP | [6 empty] | 0.9099 | 0.88906 | 0.96398 | 0.9 | 1.05 | CATEGORYB | SINGLE | AVOCA - EAST ROGERS 161KV CKT 1 | 0 | 506931 | EROGERS5 161.00 | 506966 | AVOCA--5 161.00 | 0 |  | 1 |  |  |  |  | AEPW | FLINT CREEK - SHIPE ROAD - EAST ROGERS - OSAGE 345KV | Install new 345kV line from FLINT CREEK - SHIPE ROAD - EAST ROGERS - OSAGE | [37 empty] | 2017-06-01 | 2017-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81V1325517SP |  |  | AVOCA_1 69.000 69KV | EXP | AEPW |  | GRWDAECC |  |  | 504001 | AVOCA_1 69.000 | [5 empty] | 17SP | [6 empty] | 0.9099 | 0.88906 | 0.96398 | 0.9 | 1.05 | CATEGORYB | SINGLE | AVOCA - EAST ROGERS 161KV CKT 1 | 0 | 506931 | EROGERS5 161.00 | 506966 | AVOCA--5 161.00 | 0 |  | 1 |  |  |  |  | AEPW | FLINT CREEK - SHIPE ROAD - EAST ROGERS - OSAGE 345KV | Install new 345kV line from FLINT CREEK - SHIPE ROAD - EAST ROGERS - OSAGE | [37 empty] | 2017-06-01 | 2017-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V1084417SP |  |  | EUREKA SPRINGS 161KV | EXP | AEPW |  | FAYETTEV |  |  | 506932 | EUREKA 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.9174 | 0.89703 | 0.94659 | 0.9 | 1.05 | CATEGORYB | SINGLE | AVOCA - EAST ROGERS 161KV CKT 1 | 0 | 506931 | EROGERS5 161.00 | 506966 | AVOCA--5 161.00 | 0 |  | 1 |  |  |  |  | AEPW | FLINT CREEK - SHIPE ROAD - EAST ROGERS - OSAGE 345KV | Install new 345kV line from FLINT CREEK - SHIPE ROAD - EAST ROGERS - OSAGE | [37 empty] | 2017-06-01 | 2017-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9061112SP |  |  | MCKEE 69KV | EXP | WERE |  | SEAST |  |  | 533640 | MCKEE 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.89638 | 1.01253 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Fort Scott - SW Bourbon 161 kV | Tap Litchfield-Marmaton 161 kV with new SW Bourbon Sub to Ft Scott, and new 161/69 kV transformer at Ft Scott. | [5 empty] | 18 | 18 | [30 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12521112SP |  |  | MCKEE 69KV | EXP | WERE |  | SEAST |  |  | 533640 | MCKEE 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.89843 | 1.01253 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Fort Scott - SW Bourbon 161 kV | Tap Litchfield-Marmaton 161 kV with new SW Bourbon Sub to Ft Scott, and new 161/69 kV transformer at Ft Scott. | [5 empty] | 18 | 18 | [30 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V13682212SP |  |  | MCKEE 69KV | EXP | WERE |  | SEAST |  |  | 533640 | MCKEE 2 69.000 | [5 empty] | 12SP | [6 empty] | 0.97719 | 0.90537 | 1.01753 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 |  |  |  |  | WERE | Fort Scott - SW Bourbon 161 kV | Tap Litchfield-Marmaton 161 kV with new SW Bourbon Sub to Ft Scott, and new 161/69 kV transformer at Ft Scott. | [5 empty] | 18 | 18 | [30 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9111112SP |  |  | SEKAN NO. 9 HIATTVILLE 69KV | EXP | WERE |  | SEAST |  |  | 533645 | SE9HIAT2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.90641 | 1.01303 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Fort Scott - SW Bourbon 161 kV | Tap Litchfield-Marmaton 161 kV with new SW Bourbon Sub to Ft Scott, and new 161/69 kV transformer at Ft Scott. | [5 empty] | 18 | 18 | [30 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12571112SP |  |  | SEKAN NO. 9 HIATTVILLE 69KV | EXP | WERE |  | SEAST |  |  | 533645 | SE9HIAT2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.90832 | 1.01303 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Fort Scott - SW Bourbon 161 kV | Tap Litchfield-Marmaton 161 kV with new SW Bourbon Sub to Ft Scott, and new 161/69 kV transformer at Ft Scott. | [5 empty] | 18 | 18 | [30 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9101112SP |  |  | SEKAN NO. 4 DEVON 69KV | EXP | WERE |  | SEAST |  |  | 533644 | SE4DEVO2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.90876 | 1.01331 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Fort Scott - SW Bourbon 161 kV | Tap Litchfield-Marmaton 161 kV with new SW Bourbon Sub to Ft Scott, and new 161/69 kV transformer at Ft Scott. | [5 empty] | 18 | 18 | [30 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V13732212SP |  |  | SEKAN NO. 9 HIATTVILLE 69KV | EXP | WERE |  | SEAST |  |  | 533645 | SE9HIAT2 69.000 | [5 empty] | 12SP | [6 empty] | 0.97872 | 0.90966 | 1.01707 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 |  |  |  |  | WERE | Fort Scott - SW Bourbon 161 kV | Tap Litchfield-Marmaton 161 kV with new SW Bourbon Sub to Ft Scott, and new 161/69 kV transformer at Ft Scott. | [5 empty] | 18 | 18 | [30 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12561112SP |  |  | SEKAN NO. 4 DEVON 69KV | EXP | WERE |  | SEAST |  |  | 533644 | SE4DEVO2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.91063 | 1.01331 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Fort Scott - SW Bourbon 161 kV | Tap Litchfield-Marmaton 161 kV with new SW Bourbon Sub to Ft Scott, and new 161/69 kV transformer at Ft Scott. | [5 empty] | 18 | 18 | [30 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V13722212SP |  |  | SEKAN NO. 4 DEVON 69KV | EXP | WERE |  | SEAST |  |  | 533644 | SE4DEVO2 69.000 | [5 empty] | 12SP | [6 empty] | 0.97922 | 0.91081 | 1.01714 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 |  |  |  |  | WERE | Fort Scott - SW Bourbon 161 kV | Tap Litchfield-Marmaton 161 kV with new SW Bourbon Sub to Ft Scott, and new 161/69 kV transformer at Ft Scott. | [5 empty] | 18 | 18 | [30 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V13642212SP |  |  | FORT SCOTT 69KV | EXP | WERE |  | SEAST |  |  | 533635 | FTSCOTT2 69.000 | [5 empty] | 12SP | [6 empty] | 0.98476 | 0.92267 | 1.01894 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 |  |  |  |  | WERE | Fort Scott - SW Bourbon 161 kV | Tap Litchfield-Marmaton 161 kV with new SW Bourbon Sub to Ft Scott, and new 161/69 kV transformer at Ft Scott. | [5 empty] | 18 | 18 | [30 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9021112SP |  |  | FORT SCOTT 69KV | EXP | WERE |  | SEAST |  |  | 533635 | FTSCOTT2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.93021 | 1.01706 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Fort Scott - SW Bourbon 161 kV | Tap Litchfield-Marmaton 161 kV with new SW Bourbon Sub to Ft Scott, and new 161/69 kV transformer at Ft Scott. | [5 empty] | 18 | 18 | [30 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12481112SP |  |  | FORT SCOTT 69KV | EXP | WERE |  | SEAST |  |  | 533635 | FTSCOTT2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.9318 | 1.01706 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Fort Scott - SW Bourbon 161 kV | Tap Litchfield-Marmaton 161 kV with new SW Bourbon Sub to Ft Scott, and new 161/69 kV transformer at Ft Scott. | [5 empty] | 18 | 18 | [30 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1923312WP |  |  | MCKEE 69KV | EXP | WERE |  | SEAST |  |  | 533640 | MCKEE 2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0191 | 0.88761 | 1.01972 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Fort Scott - SW Bourbon 161 kV | Tap Litchfield-Marmaton 161 kV with new SW Bourbon Sub to Ft Scott, and new 161/69 kV transformer at Ft Scott. | [5 empty] | 18 | 18 | [30 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3503312WP |  |  | MCKEE 69KV | EXP | WERE |  | SEAST |  |  | 533640 | MCKEE 2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0151 | 0.88799 | 1.01972 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Fort Scott - SW Bourbon 161 kV | Tap Litchfield-Marmaton 161 kV with new SW Bourbon Sub to Ft Scott, and new 161/69 kV transformer at Ft Scott. | [5 empty] | 18 | 18 | [30 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1973312WP |  |  | SEKAN NO. 9 HIATTVILLE 69KV | EXP | WERE |  | SEAST |  |  | 533645 | SE9HIAT2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0206 | 0.89933 | 1.02064 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Fort Scott - SW Bourbon 161 kV | Tap Litchfield-Marmaton 161 kV with new SW Bourbon Sub to Ft Scott, and new 161/69 kV transformer at Ft Scott. | [5 empty] | 18 | 18 | [30 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3553312WP |  |  | SEKAN NO. 9 HIATTVILLE 69KV | EXP | WERE |  | SEAST |  |  | 533645 | SE9HIAT2 69.000 | [5 empty] | 12WP | [6 empty] | 1.017 | 0.89968 | 1.02064 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Fort Scott - SW Bourbon 161 kV | Tap Litchfield-Marmaton 161 kV with new SW Bourbon Sub to Ft Scott, and new 161/69 kV transformer at Ft Scott. | [5 empty] | 18 | 18 | [30 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1963312WP |  |  | SEKAN NO. 4 DEVON 69KV | EXP | WERE |  | SEAST |  |  | 533644 | SE4DEVO2 69.000 | [5 empty] | 12WP | [6 empty] | 1.021 | 0.902 | 1.02096 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Fort Scott - SW Bourbon 161 kV | Tap Litchfield-Marmaton 161 kV with new SW Bourbon Sub to Ft Scott, and new 161/69 kV transformer at Ft Scott. | [5 empty] | 18 | 18 | [30 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3543312WP |  |  | SEKAN NO. 4 DEVON 69KV | EXP | WERE |  | SEAST |  |  | 533644 | SE4DEVO2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0175 | 0.90234 | 1.02096 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Fort Scott - SW Bourbon 161 kV | Tap Litchfield-Marmaton 161 kV with new SW Bourbon Sub to Ft Scott, and new 161/69 kV transformer at Ft Scott. | [5 empty] | 18 | 18 | [30 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1883312WP |  |  | FORT SCOTT 69KV | EXP | WERE |  | SEAST |  |  | 533635 | FTSCOTT2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0255 | 0.92591 | 1.02445 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | Fort Scott - SW Bourbon 161 kV | Tap Litchfield-Marmaton 161 kV with new SW Bourbon Sub to Ft Scott, and new 161/69 kV transformer at Ft Scott. | [5 empty] | 18 | 18 | [30 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3463312WP |  |  | FORT SCOTT 69KV | EXP | WERE |  | SEAST |  |  | 533635 | FTSCOTT2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0227 | 0.92621 | 1.02445 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | Fort Scott - SW Bourbon 161 kV | Tap Litchfield-Marmaton 161 kV with new SW Bourbon Sub to Ft Scott, and new 161/69 kV transformer at Ft Scott. | [5 empty] | 18 | 18 | [30 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V4301408SH |  |  | PRATT 115KV | EXP | WEPL |  |  |  |  | 539687 | PRATT 3 115.00 | [5 empty] | 08SH | [6 empty] | 0.92099 | 0.89812 | 0.94243 | 0.9 | 1.1 | CATEGORYB | SINGLE | SEWARD - ST JOHN 115KV CKT 1 | 0 | 539692 | SEWARD 3 115.00 | 539696 | ST-JOHN3 115.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V5732308SP |  |  | MILAN 4 138KV | EXP | WEPL |  |  |  |  | 539676 | MILAN 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.87784 | 0.85203 | 0.99597 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V5732308SP |  |  | MILAN 4 138KV | EXP | WEPL |  |  |  |  | 539676 | MILAN 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.87784 | 0.85203 | 0.99597 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V5732308SP |  |  | MILAN 4 138KV | EXP | WEPL |  |  |  |  | 539676 | MILAN 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.87784 | 0.85203 | 0.99597 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V5732308SP |  |  | MILAN 4 138KV | EXP | WEPL |  |  |  |  | 539676 | MILAN 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.87784 | 0.85203 | 0.99597 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8682308SP |  |  | MILAN 4 138KV | EXP | WEPL |  |  |  |  | 539676 | MILAN 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.87893 | 0.85271 | 0.99597 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WEPL-03A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8682308SP |  |  | MILAN 4 138KV | EXP | WEPL |  |  |  |  | 539676 | MILAN 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.87893 | 0.85271 | 0.99597 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WEPL-03A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8682308SP |  |  | MILAN 4 138KV | EXP | WEPL |  |  |  |  | 539676 | MILAN 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.87893 | 0.85271 | 0.99597 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WEPL-03A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8682308SP |  |  | MILAN 4 138KV | EXP | WEPL |  |  |  |  | 539676 | MILAN 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.87893 | 0.85271 | 0.99597 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WEPL-03A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V5722308SP |  |  | MILAN TAP 138KV | EXP | WEPL |  |  |  |  | 539675 | MILANTP4 138.00 | [5 empty] | 08SP | [6 empty] | 0.8797 | 0.85424 | 0.99834 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V5722308SP |  |  | MILAN TAP 138KV | EXP | WEPL |  |  |  |  | 539675 | MILANTP4 138.00 | [5 empty] | 08SP | [6 empty] | 0.8797 | 0.85424 | 0.99834 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V5722308SP |  |  | MILAN TAP 138KV | EXP | WEPL |  |  |  |  | 539675 | MILANTP4 138.00 | [5 empty] | 08SP | [6 empty] | 0.8797 | 0.85424 | 0.99834 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V5722308SP |  |  | MILAN TAP 138KV | EXP | WEPL |  |  |  |  | 539675 | MILANTP4 138.00 | [5 empty] | 08SP | [6 empty] | 0.8797 | 0.85424 | 0.99834 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8672308SP |  |  | MILAN TAP 138KV | EXP | WEPL |  |  |  |  | 539675 | MILANTP4 138.00 | [5 empty] | 08SP | [6 empty] | 0.88078 | 0.85491 | 0.99834 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WEPL-03A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8672308SP |  |  | MILAN TAP 138KV | EXP | WEPL |  |  |  |  | 539675 | MILANTP4 138.00 | [5 empty] | 08SP | [6 empty] | 0.88078 | 0.85491 | 0.99834 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WEPL-03A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8672308SP |  |  | MILAN TAP 138KV | EXP | WEPL |  |  |  |  | 539675 | MILANTP4 138.00 | [5 empty] | 08SP | [6 empty] | 0.88078 | 0.85491 | 0.99834 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WEPL-03A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8672308SP |  |  | MILAN TAP 138KV | EXP | WEPL |  |  |  |  | 539675 | MILANTP4 138.00 | [5 empty] | 08SP | [6 empty] | 0.88078 | 0.85491 | 0.99834 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WEPL-03A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V5692308SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.88205 | 0.85729 | 0.97943 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V5692308SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.88205 | 0.85729 | 0.97943 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V5692308SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.88205 | 0.85729 | 0.97943 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V5692308SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.88205 | 0.85729 | 0.97943 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V5692308SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.88205 | 0.85729 | 0.97943 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8642308SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.88309 | 0.85794 | 0.97943 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WEPL-03A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8642308SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.88309 | 0.85794 | 0.97943 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WEPL-03A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8642308SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.88309 | 0.85794 | 0.97943 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WEPL-03A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8642308SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.88309 | 0.85794 | 0.97943 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WEPL-03A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8642308SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.88309 | 0.85794 | 0.97943 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WEPL-03A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V6091108SP |  |  | PRATT 115KV | EXP | WEPL |  |  |  |  | 539687 | PRATT 3 115.00 | [5 empty] | 08SP | [6 empty] | 0.90095 | 0.88014 | 0.93137 | 0.9 | 1.1 | CATEGORYB | SINGLE | PRATT - ST JOHN 115KV CKT 1 | 0 | 539696 | ST-JOHN3 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8662308SP |  |  | MEDICINE LODGE 138KV | EXP | WEPL |  |  |  |  | 539674 | MED-LDG4 138.00 | [5 empty] | 08SP | [6 empty] | 0.90458 | 0.88448 | 0.9675 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WEPL-03A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8662308SP |  |  | MEDICINE LODGE 138KV | EXP | WEPL |  |  |  |  | 539674 | MED-LDG4 138.00 | [5 empty] | 08SP | [6 empty] | 0.90458 | 0.88448 | 0.9675 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WEPL-03A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8662308SP |  |  | MEDICINE LODGE 138KV | EXP | WEPL |  |  |  |  | 539674 | MED-LDG4 138.00 | [5 empty] | 08SP | [6 empty] | 0.90458 | 0.88448 | 0.9675 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WEPL-03A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8662308SP |  |  | MEDICINE LODGE 138KV | EXP | WEPL |  |  |  |  | 539674 | MED-LDG4 138.00 | [5 empty] | 08SP | [6 empty] | 0.90458 | 0.88448 | 0.9675 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WEPL-03A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 3 | 2008-12-01 | 2007AG1AFS81V6721309SP |  |  | MILAN 4 138KV | EXP | WEPL |  |  |  |  | 539676 | MILAN 4 138.00 | [5 empty] | 09SP | [6 empty] | 0.85258 | 0.83191 | 0.99414 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 3 | 2008-12-01 | 2007AG1AFS81V6721309SP |  |  | MILAN 4 138KV | EXP | WEPL |  |  |  |  | 539676 | MILAN 4 138.00 | [5 empty] | 09SP | [6 empty] | 0.85258 | 0.83191 | 0.99414 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 3 | 2008-12-01 | 2007AG1AFS81V6721309SP |  |  | MILAN 4 138KV | EXP | WEPL |  |  |  |  | 539676 | MILAN 4 138.00 | [5 empty] | 09SP | [6 empty] | 0.85258 | 0.83191 | 0.99414 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 3 | 2008-12-01 | 2007AG1AFS81V6721309SP |  |  | MILAN 4 138KV | EXP | WEPL |  |  |  |  | 539676 | MILAN 4 138.00 | [5 empty] | 09SP | [6 empty] | 0.85258 | 0.83191 | 0.99414 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 3 | 2008-12-01 | 2007AG1AFS81V6711309SP |  |  | MILAN TAP 138KV | EXP | WEPL |  |  |  |  | 539675 | MILANTP4 138.00 | [5 empty] | 09SP | [6 empty] | 0.85484 | 0.83447 | 0.99658 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 3 | 2008-12-01 | 2007AG1AFS81V6711309SP |  |  | MILAN TAP 138KV | EXP | WEPL |  |  |  |  | 539675 | MILANTP4 138.00 | [5 empty] | 09SP | [6 empty] | 0.85484 | 0.83447 | 0.99658 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 3 | 2008-12-01 | 2007AG1AFS81V6711309SP |  |  | MILAN TAP 138KV | EXP | WEPL |  |  |  |  | 539675 | MILANTP4 138.00 | [5 empty] | 09SP | [6 empty] | 0.85484 | 0.83447 | 0.99658 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 3 | 2008-12-01 | 2007AG1AFS81V6711309SP |  |  | MILAN TAP 138KV | EXP | WEPL |  |  |  |  | 539675 | MILANTP4 138.00 | [5 empty] | 09SP | [6 empty] | 0.85484 | 0.83447 | 0.99658 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V5784209SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 09SP | [6 empty] | 0.86079 | 0.83988 | 0.97353 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V5784209SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 09SP | [6 empty] | 0.86079 | 0.83988 | 0.97353 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V5784209SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 09SP | [6 empty] | 0.86079 | 0.83988 | 0.97353 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V5784209SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 09SP | [6 empty] | 0.86079 | 0.83988 | 0.97353 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V5784209SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 09SP | [6 empty] | 0.86079 | 0.83988 | 0.97353 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V5714209SP |  |  | PRATT 115KV | EXP | WEPL |  |  |  |  | 539687 | PRATT 3 115.00 | [5 empty] | 09SP | [6 empty] | 1 | 0.89883 | 0.92078 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | 0 | 533045 | GILL W 4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V12081212SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.87742 | 0.97111 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WERE-34A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V12081212SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.87742 | 0.97111 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WERE-34A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V12081212SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.87742 | 0.97111 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WERE-34A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V12081212SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.87742 | 0.97111 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WERE-34A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V12081212SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.87742 | 0.97111 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WERE-34A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V9474212SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.87813 | 0.97139 | 0.9 | 1.1 | CATEGORYB | SINGLE | HARPER - MILAN TAP 138KV CKT 1 | 0 | 539675 | MILANTP4 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V9474212SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.87813 | 0.97139 | 0.9 | 1.1 | CATEGORYB | SINGLE | HARPER - MILAN TAP 138KV CKT 1 | 0 | 539675 | MILANTP4 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V9474212SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.87813 | 0.97139 | 0.9 | 1.1 | CATEGORYB | SINGLE | HARPER - MILAN TAP 138KV CKT 1 | 0 | 539675 | MILANTP4 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V9474212SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.87813 | 0.97139 | 0.9 | 1.1 | CATEGORYB | SINGLE | HARPER - MILAN TAP 138KV CKT 1 | 0 | 539675 | MILANTP4 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V9474212SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.87813 | 0.97139 | 0.9 | 1.1 | CATEGORYB | SINGLE | HARPER - MILAN TAP 138KV CKT 1 | 0 | 539675 | MILANTP4 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V12111212SP |  |  | PRATT 115KV | EXP | WEPL |  |  |  |  | 539687 | PRATT 3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.88006 | 0.91434 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WERE-34A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V9504212SP |  |  | PRATT 115KV | EXP | WEPL |  |  |  |  | 539687 | PRATT 3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.88078 | 0.91426 | 0.9 | 1.1 | CATEGORYB | SINGLE | HARPER - MILAN TAP 138KV CKT 1 | 0 | 539675 | MILANTP4 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V12041212SP |  |  | PAWNEE 115KV | EXP | MIDW |  | REG E-IL |  |  | 530621 | PAWNEE 3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.88345 | 0.90566 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WERE-34A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V9434212SP |  |  | PAWNEE 115KV | EXP | MIDW |  | REG E-IL |  |  | 530621 | PAWNEE 3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.88418 | 0.90552 | 0.9 | 1.1 | CATEGORYB | SINGLE | HARPER - MILAN TAP 138KV CKT 1 | 0 | 539675 | MILANTP4 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V12031212SP |  |  | KINSLEY 115KV | EXP | MIDW |  | REG E-IL |  |  | 530619 | KINSLEY3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.88538 | 0.90754 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WERE-34A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V9424212SP |  |  | KINSLEY 115KV | EXP | MIDW |  | REG E-IL |  |  | 530619 | KINSLEY3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.8861 | 0.9074 | 0.9 | 1.1 | CATEGORYB | SINGLE | HARPER - MILAN TAP 138KV CKT 1 | 0 | 539675 | MILANTP4 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V12051212SP |  |  | PAWNEE-EDWARDS_JCT 115KV | EXP | MIDW |  | REG E-IL |  |  | 530622 | PAWN-ED3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.88993 | 0.91196 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WERE-34A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V9444212SP |  |  | PAWNEE-EDWARDS_JCT 115KV | EXP | MIDW |  | REG E-IL |  |  | 530622 | PAWN-ED3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.89065 | 0.91182 | 0.9 | 1.1 | CATEGORYB | SINGLE | HARPER - MILAN TAP 138KV CKT 1 | 0 | 539675 | MILANTP4 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V12021212SP |  |  | EDWARDS 115KV | EXP | MIDW |  | REG E-IL |  |  | 530617 | EDWARDS3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.89219 | 0.91414 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WERE-34A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V9414212SP |  |  | EDWARDS 115KV | EXP | MIDW |  | REG E-IL |  |  | 530617 | EDWARDS3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.8929 | 0.914 | 0.9 | 1.1 | CATEGORYB | SINGLE | HARPER - MILAN TAP 138KV CKT 1 | 0 | 539675 | MILANTP4 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V12101212SP |  |  | MEDICINE LODGE 138KV | EXP | WEPL |  |  |  |  | 539674 | MED-LDG4 138.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.89382 | 0.95446 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WERE-34A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V12101212SP |  |  | MEDICINE LODGE 138KV | EXP | WEPL |  |  |  |  | 539674 | MED-LDG4 138.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.89382 | 0.95446 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WERE-34A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V12101212SP |  |  | MEDICINE LODGE 138KV | EXP | WEPL |  |  |  |  | 539674 | MED-LDG4 138.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.89382 | 0.95446 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WERE-34A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V12101212SP |  |  | MEDICINE LODGE 138KV | EXP | WEPL |  |  |  |  | 539674 | MED-LDG4 138.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.89382 | 0.95446 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WERE-34A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V9494212SP |  |  | MEDICINE LODGE 138KV | EXP | WEPL |  |  |  |  | 539674 | MED-LDG4 138.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.8945 | 0.9548 | 0.9 | 1.1 | CATEGORYB | SINGLE | HARPER - MILAN TAP 138KV CKT 1 | 0 | 539675 | MILANTP4 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V9494212SP |  |  | MEDICINE LODGE 138KV | EXP | WEPL |  |  |  |  | 539674 | MED-LDG4 138.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.8945 | 0.9548 | 0.9 | 1.1 | CATEGORYB | SINGLE | HARPER - MILAN TAP 138KV CKT 1 | 0 | 539675 | MILANTP4 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V9494212SP |  |  | MEDICINE LODGE 138KV | EXP | WEPL |  |  |  |  | 539674 | MED-LDG4 138.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.8945 | 0.9548 | 0.9 | 1.1 | CATEGORYB | SINGLE | HARPER - MILAN TAP 138KV CKT 1 | 0 | 539675 | MILANTP4 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V9494212SP |  |  | MEDICINE LODGE 138KV | EXP | WEPL |  |  |  |  | 539674 | MED-LDG4 138.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.8945 | 0.9548 | 0.9 | 1.1 | CATEGORYB | SINGLE | HARPER - MILAN TAP 138KV CKT 1 | 0 | 539675 | MILANTP4 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V12091212SP |  |  | MEDICINE LODGE 115KV | EXP | WEPL |  |  |  |  | 539673 | MED-LDG3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.89549 | 0.95083 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WERE-34A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V12091212SP |  |  | MEDICINE LODGE 115KV | EXP | WEPL |  |  |  |  | 539673 | MED-LDG3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.89549 | 0.95083 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WERE-34A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V9484212SP |  |  | MEDICINE LODGE 115KV | EXP | WEPL |  |  |  |  | 539673 | MED-LDG3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.89615 | 0.95085 | 0.9 | 1.1 | CATEGORYB | SINGLE | HARPER - MILAN TAP 138KV CKT 1 | 0 | 539675 | MILANTP4 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V9484212SP |  |  | MEDICINE LODGE 115KV | EXP | WEPL |  |  |  |  | 539673 | MED-LDG3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.89615 | 0.95085 | 0.9 | 1.1 | CATEGORYB | SINGLE | HARPER - MILAN TAP 138KV CKT 1 | 0 | 539675 | MILANTP4 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V13484417SP |  |  | PAWNEE 115KV | EXP | MIDW |  | REG E-IL |  |  | 530621 | PAWNEE 3 115.00 | [5 empty] | 17SP | [6 empty] | 1 | 0.87206 | 0.89467 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | 0 | 533045 | GILL W 4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V13474417SP |  |  | KINSLEY 115KV | EXP | MIDW |  | REG E-IL |  |  | 530619 | KINSLEY3 115.00 | [5 empty] | 17SP | [6 empty] | 1 | 0.87409 | 0.89666 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | 0 | 533045 | GILL W 4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V13504417SP |  |  | PRATT 115KV | EXP | WEPL |  |  |  |  | 539687 | PRATT 3 115.00 | [5 empty] | 17SP | [6 empty] | 1 | 0.87559 | 0.90538 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | 0 | 533045 | GILL W 4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V13494417SP |  |  | PAWNEE-EDWARDS_JCT 115KV | EXP | MIDW |  | REG E-IL |  |  | 530622 | PAWN-ED3 115.00 | [5 empty] | 17SP | [6 empty] | 1 | 0.87895 | 0.90137 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | 0 | 533045 | GILL W 4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Iteration limit exceeded | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V13184217SP |  |  | PRATT 115KV | EXP | WEPL |  |  |  |  | 539687 | PRATT 3 115.00 | [5 empty] | 17SP | [6 empty] | 1 | 0.88031 | 0.90163 | 0.9 | 1.1 | CATEGORYB | SINGLE | GREENSBURG - JUDSON LARGE 115KV CKT 1 | 0 | 539671 | JUD-LRG3 115.00 | 539664 | GRNBURG3 115.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V13464417SP |  |  | EDWARDS 115KV | EXP | MIDW |  | REG E-IL |  |  | 530617 | EDWARDS3 115.00 | [5 empty] | 17SP | [6 empty] | 1 | 0.88138 | 0.90371 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | 0 | 533045 | GILL W 4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | HARPER 138KV Capacitor | Install 1 - 20 MVar capacitor bank | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V22192417SP |  |  | NIXA 161KV | EXP | SWPA |  | EMINTH |  |  | 505496 | NIXA 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.96096 | 0.89775 | 0.94046 | 0.9 | 1.1 | CATEGORYB | GENOUT | GEN549893 2-SOUTHWEST 2 | 0 | 505492 | SPRGFLD5 161.00 | 505496 | NIXA 5 161.00 | 0 |  | 1 |  |  |  |  | SWPA | NIXA 161KV CAP BANK | 25Mvar Cap at Nixa | [12 empty] | 675000 | [24 empty] | 2013-06-01 | 2013-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V1002417SP |  |  | NIXA 161KV | EXP | SWPA |  | EMINTH |  |  | 505496 | NIXA 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.92424 | 0.89998 | 0.94046 | 0.9 | 1.1 | CATEGORYB | SINGLE | NIXA - SPRINGFIELD 161KV CKT 1 | 0 | 505492 | SPRGFLD5 161.00 | 505496 | NIXA 5 161.00 | 0 |  | 1 |  |  |  |  | SWPA | NIXA 161KV CAP BANK | 25Mvar Cap at Nixa | [12 empty] | 675000 | [24 empty] | 2013-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V42417SP |  |  | NIXA 161KV | EXP | SWPA |  | EMINTH |  |  | 505496 | NIXA 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.96096 | 0.94046 | 0.94046 | 0.95 | 1.1 | CATEGORYA | BASECASE | BASE CASE | 0 | 505492 | SPRGFLD5 161.00 | 505496 | NIXA 5 161.00 | 0 |  | 1 |  |  |  |  | SWPA | NIXA 161KV CAP BANK | 25Mvar Cap at Nixa | [12 empty] | 675000 | [24 empty] | 2013-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FNSL | FDNS-Blown up | 3 | 3 | 2008-12-01 | 2007AG1AFS82V113312SP |  |  | CUDAHY 115KV | EXP | WEPL |  |  |  |  | 539659 | CUDAHY 3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.83539 | 0.9669 | 0.9 | 1.1 | CATEGORYB | SINGLE | CUDAHY - JUDSON LARGE 115KV CKT 1 | 0 | 539671 | JUD-LRG3 115.00 | 539659 | CUDAHY 3 115.00 | 0 |  | 1 |  |  |  |  | SUNC | NORTH CIMARRON CAPACITOR | Install 24 MVAR Capacitor bank at North Cimarron | [5 empty] | 18 | 18 | [5 empty] | 1400000 | 2006-07-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FNSL | FDNS-Blown up | 3 | 3 | 2008-12-01 | 2007AG1AFS82V163312SP |  |  | LIBERAL WESTERN AVENUE 115KV | EXP | WEPL |  |  |  |  | 539700 | W-LIBER3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.83706 | 0.95241 | 0.9 | 1.1 | CATEGORYB | SINGLE | CUDAHY - JUDSON LARGE 115KV CKT 1 | 0 | 539671 | JUD-LRG3 115.00 | 539659 | CUDAHY 3 115.00 | 0 |  | 1 |  |  |  |  | SUNC | NORTH CIMARRON CAPACITOR | Install 24 MVAR Capacitor bank at North Cimarron | [5 empty] | 18 | 18 | [5 empty] | 1400000 | 2006-07-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FNSL | FDNS-Blown up | 3 | 3 | 2008-12-01 | 2007AG1AFS82V173312SP |  |  | NORTH LIBERAL 115KV | EXP | WEPL |  |  |  |  | 539737 | NLIB 3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.84067 | 0.95479 | 0.9 | 1.1 | CATEGORYB | SINGLE | CUDAHY - JUDSON LARGE 115KV CKT 1 | 0 | 539671 | JUD-LRG3 115.00 | 539659 | CUDAHY 3 115.00 | 0 |  | 1 |  |  |  |  | SUNC | NORTH CIMARRON CAPACITOR | Install 24 MVAR Capacitor bank at North Cimarron | [5 empty] | 18 | 18 | [5 empty] | 1400000 | 2006-07-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FNSL | FDNS-Blown up | 3 | 3 | 2008-12-01 | 2007AG1AFS82V133312SP |  |  | NORTH LIBERAL TAP 115KV | EXP | WEPL |  |  |  |  | 539682 | NLIBTAP3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.84397 | 0.95725 | 0.9 | 1.1 | CATEGORYB | SINGLE | CUDAHY - JUDSON LARGE 115KV CKT 1 | 0 | 539671 | JUD-LRG3 115.00 | 539659 | CUDAHY 3 115.00 | 0 |  | 1 |  |  |  |  | SUNC | NORTH CIMARRON CAPACITOR | Install 24 MVAR Capacitor bank at North Cimarron | [5 empty] | 18 | 18 | [5 empty] | 1400000 | 2006-07-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FNSL | FDNS-Blown up | 3 | 3 | 2008-12-01 | 2007AG1AFS82V143312SP |  |  | LIBERAL PINE STREET 115KV | EXP | WEPL |  |  |  |  | 539690 | S-LIBER3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.84454 | 0.95757 | 0.9 | 1.1 | CATEGORYB | SINGLE | CUDAHY - JUDSON LARGE 115KV CKT 1 | 0 | 539671 | JUD-LRG3 115.00 | 539659 | CUDAHY 3 115.00 | 0 |  | 1 |  |  |  |  | SUNC | NORTH CIMARRON CAPACITOR | Install 24 MVAR Capacitor bank at North Cimarron | [5 empty] | 18 | 18 | [5 empty] | 1400000 | 2006-07-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FNSL | FDNS-Blown up | 3 | 3 | 2008-12-01 | 2007AG1AFS82V93312SP |  |  | CIMARRON RIVER TAP 115KV | EXP | WEPL |  |  |  |  | 539652 | CMRIVTP3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.84517 | 0.961 | 0.9 | 1.1 | CATEGORYB | SINGLE | CUDAHY - JUDSON LARGE 115KV CKT 1 | 0 | 539671 | JUD-LRG3 115.00 | 539659 | CUDAHY 3 115.00 | 0 |  | 1 |  |  |  |  | SUNC | NORTH CIMARRON CAPACITOR | Install 24 MVAR Capacitor bank at North Cimarron | [5 empty] | 18 | 18 | [5 empty] | 1400000 | 2006-07-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FNSL | FDNS-Blown up | 3 | 3 | 2008-12-01 | 2007AG1AFS82V123312SP |  |  | EAST LIBERAL 115KV | EXP | WEPL |  |  |  |  | 539672 | E-LIBER3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.84626 | 0.95881 | 0.9 | 1.1 | CATEGORYB | SINGLE | CUDAHY - JUDSON LARGE 115KV CKT 1 | 0 | 539671 | JUD-LRG3 115.00 | 539659 | CUDAHY 3 115.00 | 0 |  | 1 |  |  |  |  | SUNC | NORTH CIMARRON CAPACITOR | Install 24 MVAR Capacitor bank at North Cimarron | [5 empty] | 18 | 18 | [5 empty] | 1400000 | 2006-07-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FNSL | FDNS-Blown up | 3 | 3 | 2008-12-01 | 2007AG1AFS82V103312SP |  |  | CIMARRON RIVER PLANT 115KV | EXP | WEPL |  |  |  |  | 539654 | CIM-PLT3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.8491 | 0.96133 | 0.9 | 1.1 | CATEGORYB | SINGLE | CUDAHY - JUDSON LARGE 115KV CKT 1 | 0 | 539671 | JUD-LRG3 115.00 | 539659 | CUDAHY 3 115.00 | 0 |  | 1 |  |  |  |  | SUNC | NORTH CIMARRON CAPACITOR | Install 24 MVAR Capacitor bank at North Cimarron | [5 empty] | 18 | 18 | [5 empty] | 1400000 | 2006-07-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FNSL | FDNS-Blown up | 3 | 3 | 2008-12-01 | 2007AG1AFS82V43312SP |  |  | NORTH CIMARRON 115KV | EXP | SUNC |  | SEPC |  |  | 531455 | NCIMARN3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.84939 | 0.96143 | 0.9 | 1.1 | CATEGORYB | SINGLE | CUDAHY - JUDSON LARGE 115KV CKT 1 | 0 | 539671 | JUD-LRG3 115.00 | 539659 | CUDAHY 3 115.00 | 0 |  | 1 |  |  |  |  | SUNC | NORTH CIMARRON CAPACITOR | Install 24 MVAR Capacitor bank at North Cimarron | [5 empty] | 18 | 18 | [5 empty] | 1400000 | 2006-07-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FNSL | FDNS-Blown up | 3 | 3 | 2008-12-01 | 2007AG1AFS82V53312SP |  |  | SEWARD-3 115KV | EXP | SUNC |  | SEPC |  |  | 531467 | SEWARD-3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.85853 | 0.96079 | 0.9 | 1.1 | CATEGORYB | SINGLE | CUDAHY - JUDSON LARGE 115KV CKT 1 | 0 | 539671 | JUD-LRG3 115.00 | 539659 | CUDAHY 3 115.00 | 0 |  | 1 |  |  |  |  | SUNC | NORTH CIMARRON CAPACITOR | Install 24 MVAR Capacitor bank at North Cimarron | [5 empty] | 18 | 18 | [5 empty] | 1400000 | 2006-07-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FNSL | FDNS-Blown up | 3 | 3 | 2008-12-01 | 2007AG1AFS82V13312SP |  |  | HASKELL 115KV | EXP | SUNC |  | PIONEER |  |  | 531374 | HASKELL3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.86786 | 0.96322 | 0.9 | 1.1 | CATEGORYB | SINGLE | CUDAHY - JUDSON LARGE 115KV CKT 1 | 0 | 539671 | JUD-LRG3 115.00 | 539659 | CUDAHY 3 115.00 | 0 |  | 1 |  |  |  |  | SUNC | NORTH CIMARRON CAPACITOR | Install 24 MVAR Capacitor bank at North Cimarron | [5 empty] | 18 | 18 | [5 empty] | 1400000 | 2006-07-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FNSL | FDNS-Blown up | 3 | 3 | 2008-12-01 | 2007AG1AFS82V153312SP |  |  | SATANTA 115KV | EXP | WEPL |  |  |  |  | 539691 | SATANTA3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.86973 | 0.96372 | 0.9 | 1.1 | CATEGORYB | SINGLE | CUDAHY - JUDSON LARGE 115KV CKT 1 | 0 | 539671 | JUD-LRG3 115.00 | 539659 | CUDAHY 3 115.00 | 0 |  | 1 |  |  |  |  | SUNC | NORTH CIMARRON CAPACITOR | Install 24 MVAR Capacitor bank at North Cimarron | [5 empty] | 18 | 18 | [5 empty] | 1400000 | 2006-07-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FNSL | FDNS-Blown up | 3 | 3 | 2008-12-01 | 2007AG1AFS82V33312SP |  |  | CTU SUBLETTE 115KV | EXP | SUNC |  | SEPC |  |  | 531442 | CTUSUBL3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.86974 | 0.96373 | 0.9 | 1.1 | CATEGORYB | SINGLE | CUDAHY - JUDSON LARGE 115KV CKT 1 | 0 | 539671 | JUD-LRG3 115.00 | 539659 | CUDAHY 3 115.00 | 0 |  | 1 |  |  |  |  | SUNC | NORTH CIMARRON CAPACITOR | Install 24 MVAR Capacitor bank at North Cimarron | [5 empty] | 18 | 18 | [5 empty] | 1400000 | 2006-07-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FNSL | FDNS-Blown up | 3 | 3 | 2008-12-01 | 2007AG1AFS82V23312SP |  |  | WALKEMEYER 115KV | EXP | SUNC |  | PIONEER |  |  | 531405 | WALKMYR3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.87453 | 0.97357 | 0.9 | 1.1 | CATEGORYB | SINGLE | CUDAHY - JUDSON LARGE 115KV CKT 1 | 0 | 539671 | JUD-LRG3 115.00 | 539659 | CUDAHY 3 115.00 | 0 |  | 1 |  |  |  |  | SUNC | NORTH CIMARRON CAPACITOR | Install 24 MVAR Capacitor bank at North Cimarron | [5 empty] | 18 | 18 | [5 empty] | 1400000 | 2006-07-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FNSL | FDNS-Blown up | 3 | 3 | 2008-12-01 | 2007AG1AFS82V63312SP |  |  | HUGOTON SUBSTATION 115KV | EXP | SUNC |  | PIONEER |  |  | 531481 | HUGOTON3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.88041 | 0.97444 | 0.9 | 1.1 | CATEGORYB | SINGLE | CUDAHY - JUDSON LARGE 115KV CKT 1 | 0 | 539671 | JUD-LRG3 115.00 | 539659 | CUDAHY 3 115.00 | 0 |  | 1 |  |  |  |  | SUNC | NORTH CIMARRON CAPACITOR | Install 24 MVAR Capacitor bank at North Cimarron | [5 empty] | 18 | 18 | [5 empty] | 1400000 | 2006-07-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FNSL | FDNS-Blown up | 3 | 3 | 2008-12-01 | 2007AG1AFS82V83312SP |  |  | PIONEER NATURAL RESOURCES 115KV | EXP | SUNC |  | PIONEER |  |  | 531484 | PION NR 3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.89697 | 0.97991 | 0.9 | 1.1 | CATEGORYB | SINGLE | CUDAHY - JUDSON LARGE 115KV CKT 1 | 0 | 539671 | JUD-LRG3 115.00 | 539659 | CUDAHY 3 115.00 | 0 |  | 1 |  |  |  |  | SUNC | NORTH CIMARRON CAPACITOR | Install 24 MVAR Capacitor bank at North Cimarron | [5 empty] | 18 | 18 | [5 empty] | 1400000 | 2006-07-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Blown up | FNSL | FDNS-Blown up | 3 | 3 | 2008-12-01 | 2007AG1AFS82V73312SP |  |  | PIONEER NATURAL RESOURCES TAP 115KV | EXP | SUNC |  | PIONEER |  |  | 531483 | PION NRT3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.8974 | 0.9803 | 0.9 | 1.1 | CATEGORYB | SINGLE | CUDAHY - JUDSON LARGE 115KV CKT 1 | 0 | 539671 | JUD-LRG3 115.00 | 539659 | CUDAHY 3 115.00 | 0 |  | 1 |  |  |  |  | SUNC | NORTH CIMARRON CAPACITOR | Install 24 MVAR Capacitor bank at North Cimarron | [5 empty] | 18 | 18 | [5 empty] | 1400000 | 2006-07-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V13174217SP |  |  | GREENSBURG 115KV | EXP | WEPL |  |  |  |  | 539664 | GRNBURG3 115.00 | [5 empty] | 17SP | [6 empty] | 1 | 0.89863 | 0.97426 | 0.9 | 1.1 | CATEGORYB | SINGLE | GREENSBURG - JUDSON LARGE 115KV CKT 1 | 0 | 539671 | JUD-LRG3 115.00 | 539664 | GRNBURG3 115.00 | 0 |  | 1 |  |  |  |  | SUNC | NORTH CIMARRON CAPACITOR | Install 24 MVAR Capacitor bank at North Cimarron | [5 empty] | 18 | 18 | [5 empty] | 1400000 | 2006-07-01 | [23 empty] | 2012-06-01 | 2012-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V10084412SP |  |  | ROSE HILL 69KV | S | WERE |  | SCENTRAL |  |  | 533836 | ROSEHIL2 69.000 | [5 empty] | 12SP | [6 empty] | 0.97764 | 0.92884 | 1.01405 | 0.95 | 1.05 | CATEGORYB | SINGLE | ROSE HILL JUNCTION - WEAVER 69KV CKT 1 | 0 | 533604 | WEAVER 2 69.000 | 533837 | RH JCT 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | OAK - RAINBOW 69KV CKT 1 | Tear down / Rebuild 5.10-mile Oak-Rainbow 69 kV using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 5.1 | 8 | 4 |  | 0.010721 | 0.0737 | 0.0015109 | Limit is conductor | 1900000 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01 | 2010-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V10084412SP |  |  | ROSE HILL 69KV | S | WERE |  | SCENTRAL |  |  | 533836 | ROSEHIL2 69.000 | [5 empty] | 12SP | [6 empty] | 0.97764 | 0.92884 | 1.01405 | 0.95 | 1.05 | CATEGORYB | SINGLE | ROSE HILL JUNCTION - WEAVER 69KV CKT 1 | 0 | 533604 | WEAVER 2 69.000 | 533837 | RH JCT 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | OAK - RAINBOW 69KV CKT 1 | Tear down / Rebuild 5.10-mile Oak-Rainbow 69 kV using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 5.1 | 8 | 4 |  | 0.010721 | 0.0737 | 0.0015109 | Limit is conductor | 1900000 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01 | 2010-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V2914408FA |  |  | FARBER 138KV | S | WERE |  | SCENTRAL |  |  | 533042 | FARBER 4 138.00 | [5 empty] | 08FA | [6 empty] | 1.0163 | 0.94978 | 1.02108 | 0.95 | 1.05 | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | OXFORD 138KV Capacitor Displacement | Install 30 MVAR Capacitor Bank at Oxford 138 kV | [5 empty] | 18 | 18 | [5 empty] | 1215000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 3 | 2008-12-01 | 2007AG1AFS81V3321308SH |  |  | FARBER 138KV | S | WERE |  | SCENTRAL |  |  | 533042 | FARBER 4 138.00 | [5 empty] | 08SH | [6 empty] | 1.0113 | 0.91382 | 1.02103 | 0.95 | 1.05 | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | OXFORD 138KV Capacitor Displacement | Install 30 MVAR Capacitor Bank at Oxford 138 kV | [5 empty] | 18 | 18 | [5 empty] | 1215000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 3 | 2008-12-01 | 2007AG1AFS81V3331308SH |  |  | SUMNER COUNTY NO. 10 BELLE PLAIN 138KV | S | WERE |  | SCENTRAL |  |  | 533063 | SC10BEL4 138.00 | [5 empty] | 08SH | [6 empty] | 1.0137 | 0.91653 | 1.01269 | 0.95 | 1.05 | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | OXFORD 138KV Capacitor Displacement | Install 30 MVAR Capacitor Bank at Oxford 138 kV | [5 empty] | 18 | 18 | [5 empty] | 1215000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 3 | 2008-12-01 | 2007AG1AFS81V3311308SH |  |  | OXFORD 138KV | S | WERE |  | SCENTRAL |  |  | 532982 | OXFORD 4 138.00 | [5 empty] | 08SH | [6 empty] | 1.0164 | 0.91964 | 1.00542 | 0.95 | 1.05 | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | OXFORD 138KV Capacitor Displacement | Install 30 MVAR Capacitor Bank at Oxford 138 kV | [5 empty] | 18 | 18 | [5 empty] | 1215000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 3 | 2008-12-01 | 2007AG1AFS81V3301308SH |  |  | CRESWELL 138KV | S | WERE |  | SCENTRAL |  |  | 532981 | CRESWLN4 138.00 | [5 empty] | 08SH | [6 empty] | 1.0214 | 0.92668 | 0.99463 | 0.95 | 1.05 | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | OXFORD 138KV Capacitor Displacement | Install 30 MVAR Capacitor Bank at Oxford 138 kV | [5 empty] | 18 | 18 | [5 empty] | 1215000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V3341108SH |  |  | SUMNER COUNTY NO. 10 BELLE PLAIN 138KV | S | WERE |  | SCENTRAL |  |  | 533063 | SC10BEL4 138.00 | [5 empty] | 08SH | [6 empty] | 1 | 0.93937 | 1.01175 | 0.95 | 1.05 | CATEGORYB | SINGLE | FARBER - SUMNER COUNTY NO. 10 BELLE PLAIN 138KV CKT 1 | 0 | 533042 | FARBER 4 138.00 | 533063 | SC10BEL4 138.00 | 0 |  | 1 |  |  |  |  | WERE | OXFORD 138KV Capacitor Displacement | Install 30 MVAR Capacitor Bank at Oxford 138 kV | [5 empty] | 18 | 18 | [5 empty] | 1215000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V3331108SH |  |  | OXFORD 138KV | S | WERE |  | SCENTRAL |  |  | 532982 | OXFORD 4 138.00 | [5 empty] | 08SH | [6 empty] | 1 | 0.94002 | 1.00402 | 0.95 | 1.05 | CATEGORYB | SINGLE | FARBER - SUMNER COUNTY NO. 10 BELLE PLAIN 138KV CKT 1 | 0 | 533042 | FARBER 4 138.00 | 533063 | SC10BEL4 138.00 | 0 |  | 1 |  |  |  |  | WERE | OXFORD 138KV Capacitor Displacement | Install 30 MVAR Capacitor Bank at Oxford 138 kV | [5 empty] | 18 | 18 | [5 empty] | 1215000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V3321108SH |  |  | CRESWELL 138KV | S | WERE |  | SCENTRAL |  |  | 532981 | CRESWLN4 138.00 | [5 empty] | 08SH | [6 empty] | 1 | 0.94263 | 0.99324 | 0.95 | 1.05 | CATEGORYB | SINGLE | FARBER - SUMNER COUNTY NO. 10 BELLE PLAIN 138KV CKT 1 | 0 | 533042 | FARBER 4 138.00 | 533063 | SC10BEL4 138.00 | 0 |  | 1 |  |  |  |  | WERE | OXFORD 138KV Capacitor Displacement | Install 30 MVAR Capacitor Bank at Oxford 138 kV | [5 empty] | 18 | 18 | [5 empty] | 1215000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V3301408SH |  |  | OXFORD 138KV | S | WERE |  | SCENTRAL |  |  | 532982 | OXFORD 4 138.00 | [5 empty] | 08SH | [6 empty] | 1 | 0.94305 | 1.00414 | 0.95 | 1.05 | CATEGORYB | SINGLE | OXFORD - SUMNER COUNTY NO. 10 BELLE PLAIN 138KV CKT 1 | 0 | 533063 | SC10BEL4 138.00 | 532982 | OXFORD 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | OXFORD 138KV Capacitor Displacement | Install 30 MVAR Capacitor Bank at Oxford 138 kV | [5 empty] | 18 | 18 | [5 empty] | 1215000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V3291408SH |  |  | CRESWELL 138KV | S | WERE |  | SCENTRAL |  |  | 532981 | CRESWLN4 138.00 | [5 empty] | 08SH | [6 empty] | 1 | 0.94483 | 0.99327 | 0.95 | 1.05 | CATEGORYB | SINGLE | OXFORD - SUMNER COUNTY NO. 10 BELLE PLAIN 138KV CKT 1 | 0 | 533063 | SC10BEL4 138.00 | 532982 | OXFORD 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | OXFORD 138KV Capacitor Displacement | Install 30 MVAR Capacitor Bank at Oxford 138 kV | [5 empty] | 18 | 18 | [5 empty] | 1215000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V5211108SP |  |  | FARBER 138KV | S | WERE |  | SCENTRAL |  |  | 533042 | FARBER 4 138.00 | [5 empty] | 08SP | [6 empty] | 1.0002 | 0.93393 | 1.02059 | 0.95 | 1.05 | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | OXFORD 138KV Capacitor Displacement | Install 30 MVAR Capacitor Bank at Oxford 138 kV | [5 empty] | 18 | 18 | [5 empty] | 1215000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V5221108SP |  |  | SUMNER COUNTY NO. 10 BELLE PLAIN 138KV | S | WERE |  | SCENTRAL |  |  | 533063 | SC10BEL4 138.00 | [5 empty] | 08SP | [6 empty] | 1.0031 | 0.93709 | 1.01602 | 0.95 | 1.05 | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | OXFORD 138KV Capacitor Displacement | Install 30 MVAR Capacitor Bank at Oxford 138 kV | [5 empty] | 18 | 18 | [5 empty] | 1215000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V5201108SP |  |  | OXFORD 138KV | S | WERE |  | SCENTRAL |  |  | 532982 | OXFORD 4 138.00 | [5 empty] | 08SP | [6 empty] | 1.0064 | 0.94074 | 1.01252 | 0.95 | 1.05 | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | OXFORD 138KV Capacitor Displacement | Install 30 MVAR Capacitor Bank at Oxford 138 kV | [5 empty] | 18 | 18 | [5 empty] | 1215000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V5191108SP |  |  | CRESWELL 138KV | S | WERE |  | SCENTRAL |  |  | 532981 | CRESWLN4 138.00 | [5 empty] | 08SP | [6 empty] | 1.0128 | 0.94916 | 1.00871 | 0.95 | 1.05 | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | OXFORD 138KV Capacitor Displacement | Install 30 MVAR Capacitor Bank at Oxford 138 kV | [5 empty] | 18 | 18 | [5 empty] | 1215000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5594409SP |  |  | FARBER 138KV | S | WERE |  | SCENTRAL |  |  | 533042 | FARBER 4 138.00 | [5 empty] | 09SP | [6 empty] | 0.98586 | 0.92517 | 1.02007 | 0.95 | 1.05 | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | OXFORD 138KV Capacitor Displacement | Install 30 MVAR Capacitor Bank at Oxford 138 kV | [5 empty] | 18 | 18 | [5 empty] | 1215000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5604409SP |  |  | SUMNER COUNTY NO. 10 BELLE PLAIN 138KV | S | WERE |  | SCENTRAL |  |  | 533063 | SC10BEL4 138.00 | [5 empty] | 09SP | [6 empty] | 0.98893 | 0.92848 | 1.01487 | 0.95 | 1.05 | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | OXFORD 138KV Capacitor Displacement | Install 30 MVAR Capacitor Bank at Oxford 138 kV | [5 empty] | 18 | 18 | [5 empty] | 1215000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5584409SP |  |  | OXFORD 138KV | S | WERE |  | SCENTRAL |  |  | 532982 | OXFORD 4 138.00 | [5 empty] | 09SP | [6 empty] | 0.99245 | 0.93231 | 1.01089 | 0.95 | 1.05 | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | OXFORD 138KV Capacitor Displacement | Install 30 MVAR Capacitor Bank at Oxford 138 kV | [5 empty] | 18 | 18 | [5 empty] | 1215000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5574409SP |  |  | CRESWELL 138KV | S | WERE |  | SCENTRAL |  |  | 532981 | CRESWLN4 138.00 | [5 empty] | 09SP | [6 empty] | 0.99924 | 0.94114 | 1.00653 | 0.95 | 1.05 | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | OXFORD 138KV Capacitor Displacement | Install 30 MVAR Capacitor Bank at Oxford 138 kV | [5 empty] | 18 | 18 | [5 empty] | 1215000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V9584412SP |  |  | FARBER 138KV | S | WERE |  | SCENTRAL |  |  | 533042 | FARBER 4 138.00 | [5 empty] | 12SP | [6 empty] | 0.98795 | 0.91649 | 1.02199 | 0.95 | 1.05 | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | OXFORD 138KV Capacitor Displacement | Install 30 MVAR Capacitor Bank at Oxford 138 kV | [5 empty] | 18 | 18 | [5 empty] | 1215000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V9594412SP |  |  | SUMNER COUNTY NO. 10 BELLE PLAIN 138KV | S | WERE |  | SCENTRAL |  |  | 533063 | SC10BEL4 138.00 | [5 empty] | 12SP | [6 empty] | 0.99128 | 0.92012 | 1.01585 | 0.95 | 1.05 | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | OXFORD 138KV Capacitor Displacement | Install 30 MVAR Capacitor Bank at Oxford 138 kV | [5 empty] | 18 | 18 | [5 empty] | 1215000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V9574412SP |  |  | OXFORD 138KV | S | WERE |  | SCENTRAL |  |  | 532982 | OXFORD 4 138.00 | [5 empty] | 12SP | [6 empty] | 0.99511 | 0.92436 | 1.01104 | 0.95 | 1.05 | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | OXFORD 138KV Capacitor Displacement | Install 30 MVAR Capacitor Bank at Oxford 138 kV | [5 empty] | 18 | 18 | [5 empty] | 1215000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V10084412SP |  |  | ROSE HILL 69KV | S | WERE |  | SCENTRAL |  |  | 533836 | ROSEHIL2 69.000 | [5 empty] | 12SP | [6 empty] | 0.97764 | 0.92884 | 1.01405 | 0.95 | 1.05 | CATEGORYB | SINGLE | ROSE HILL JUNCTION - WEAVER 69KV CKT 1 | 0 | 533604 | WEAVER 2 69.000 | 533837 | RH JCT 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | OXFORD 138KV Capacitor Displacement | Install 30 MVAR Capacitor Bank at Oxford 138 kV | [5 empty] | 18 | 18 | [5 empty] | 1215000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V10084412SP |  |  | ROSE HILL 69KV | S | WERE |  | SCENTRAL |  |  | 533836 | ROSEHIL2 69.000 | [5 empty] | 12SP | [6 empty] | 0.97764 | 0.92884 | 1.01405 | 0.95 | 1.05 | CATEGORYB | SINGLE | ROSE HILL JUNCTION - WEAVER 69KV CKT 1 | 0 | 533604 | WEAVER 2 69.000 | 533837 | RH JCT 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | OXFORD 138KV Capacitor Displacement | Install 30 MVAR Capacitor Bank at Oxford 138 kV | [5 empty] | 18 | 18 | [5 empty] | 1215000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V10084412SP |  |  | ROSE HILL 69KV | S | WERE |  | SCENTRAL |  |  | 533836 | ROSEHIL2 69.000 | [5 empty] | 12SP | [6 empty] | 0.97764 | 0.92884 | 1.01405 | 0.95 | 1.05 | CATEGORYB | SINGLE | ROSE HILL JUNCTION - WEAVER 69KV CKT 1 | 0 | 533604 | WEAVER 2 69.000 | 533837 | RH JCT 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | OXFORD 138KV Capacitor Displacement | Install 30 MVAR Capacitor Bank at Oxford 138 kV | [5 empty] | 18 | 18 | [5 empty] | 1215000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V10084412SP |  |  | ROSE HILL 69KV | S | WERE |  | SCENTRAL |  |  | 533836 | ROSEHIL2 69.000 | [5 empty] | 12SP | [6 empty] | 0.97764 | 0.92884 | 1.01405 | 0.95 | 1.05 | CATEGORYB | SINGLE | ROSE HILL JUNCTION - WEAVER 69KV CKT 1 | 0 | 533604 | WEAVER 2 69.000 | 533837 | RH JCT 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | OXFORD 138KV Capacitor Displacement | Install 30 MVAR Capacitor Bank at Oxford 138 kV | [5 empty] | 18 | 18 | [5 empty] | 1215000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V9564412SP |  |  | CRESWELL 138KV | S | WERE |  | SCENTRAL |  |  | 532981 | CRESWLN4 138.00 | [5 empty] | 12SP | [6 empty] | 1.0025 | 0.9321 | 1.00363 | 0.95 | 1.05 | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | OXFORD 138KV Capacitor Displacement | Install 30 MVAR Capacitor Bank at Oxford 138 kV | [5 empty] | 18 | 18 | [5 empty] | 1215000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V2064412WP |  |  | FARBER 138KV | S | WERE |  | SCENTRAL |  |  | 533042 | FARBER 4 138.00 | [5 empty] | 12WP | [6 empty] | 1.0121 | 0.93953 | 1.01842 | 0.95 | 1.05 | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | OXFORD 138KV Capacitor Displacement | Install 30 MVAR Capacitor Bank at Oxford 138 kV | [5 empty] | 18 | 18 | [5 empty] | 1215000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V2074412WP |  |  | SUMNER COUNTY NO. 10 BELLE PLAIN 138KV | S | WERE |  | SCENTRAL |  |  | 533063 | SC10BEL4 138.00 | [5 empty] | 12WP | [6 empty] | 1.0142 | 0.94182 | 1.00473 | 0.95 | 1.05 | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | OXFORD 138KV Capacitor Displacement | Install 30 MVAR Capacitor Bank at Oxford 138 kV | [5 empty] | 18 | 18 | [5 empty] | 1215000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V2054412WP |  |  | OXFORD 138KV | S | WERE |  | SCENTRAL |  |  | 532982 | OXFORD 4 138.00 | [5 empty] | 12WP | [6 empty] | 1.0166 | 0.94442 | 0.99279 | 0.95 | 1.05 | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | OXFORD 138KV Capacitor Displacement | Install 30 MVAR Capacitor Bank at Oxford 138 kV | [5 empty] | 18 | 18 | [5 empty] | 1215000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V13744417SP |  |  | FARBER 138KV | S | WERE |  | SCENTRAL |  |  | 533042 | FARBER 4 138.00 | [5 empty] | 17SP | [6 empty] | 0.96427 | 0.8964 | 1.01535 | 0.95 | 1.05 | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | OXFORD 138KV Capacitor Displacement | Install 30 MVAR Capacitor Bank at Oxford 138 kV | [5 empty] | 18 | 18 | [5 empty] | 1215000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V13754417SP |  |  | SUMNER COUNTY NO. 10 BELLE PLAIN 138KV | S | WERE |  | SCENTRAL |  |  | 533063 | SC10BEL4 138.00 | [5 empty] | 17SP | [6 empty] | 0.9682 | 0.90067 | 1.00741 | 0.95 | 1.05 | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | OXFORD 138KV Capacitor Displacement | Install 30 MVAR Capacitor Bank at Oxford 138 kV | [5 empty] | 18 | 18 | [5 empty] | 1215000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V13734417SP |  |  | OXFORD 138KV | S | WERE |  | SCENTRAL |  |  | 532982 | OXFORD 4 138.00 | [5 empty] | 17SP | [6 empty] | 0.97279 | 0.90573 | 1.00108 | 0.95 | 1.05 | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | OXFORD 138KV Capacitor Displacement | Install 30 MVAR Capacitor Bank at Oxford 138 kV | [5 empty] | 18 | 18 | [5 empty] | 1215000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V13724417SP |  |  | CRESWELL 138KV | S | WERE |  | SCENTRAL |  |  | 532981 | CRESWLN4 138.00 | [5 empty] | 17SP | [6 empty] | 0.98184 | 0.91535 | 0.99138 | 0.95 | 1.05 | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | OXFORD 138KV Capacitor Displacement | Install 30 MVAR Capacitor Bank at Oxford 138 kV | [5 empty] | 18 | 18 | [5 empty] | 1215000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V13854417SP |  |  | SUMNER COUNTY NO. 10 BELLE PLAIN 138KV | S | WERE |  | SCENTRAL |  |  | 533063 | SC10BEL4 138.00 | [5 empty] | 17SP | [6 empty] | 1.0075 | 0.93355 | 1.00741 | 0.95 | 1.05 | CATEGORYB | SINGLE | FARBER - SUMNER COUNTY NO. 10 BELLE PLAIN 138KV CKT 1 | 0 | 533042 | FARBER 4 138.00 | 533063 | SC10BEL4 138.00 | 0 |  | 1 |  |  |  |  | WERE | OXFORD 138KV Capacitor Displacement | Install 30 MVAR Capacitor Bank at Oxford 138 kV | [5 empty] | 18 | 18 | [5 empty] | 1215000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V13844417SP |  |  | OXFORD 138KV | S | WERE |  | SCENTRAL |  |  | 532982 | OXFORD 4 138.00 | [5 empty] | 17SP | [6 empty] | 1.0084 | 0.93456 | 1.00108 | 0.95 | 1.05 | CATEGORYB | SINGLE | FARBER - SUMNER COUNTY NO. 10 BELLE PLAIN 138KV CKT 1 | 0 | 533042 | FARBER 4 138.00 | 533063 | SC10BEL4 138.00 | 0 |  | 1 |  |  |  |  | WERE | OXFORD 138KV Capacitor Displacement | Install 30 MVAR Capacitor Bank at Oxford 138 kV | [5 empty] | 18 | 18 | [5 empty] | 1215000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V13834417SP |  |  | CRESWELL 138KV | S | WERE |  | SCENTRAL |  |  | 532981 | CRESWLN4 138.00 | [5 empty] | 17SP | [6 empty] | 1.0107 | 0.9368 | 0.99138 | 0.95 | 1.05 | CATEGORYB | SINGLE | FARBER - SUMNER COUNTY NO. 10 BELLE PLAIN 138KV CKT 1 | 0 | 533042 | FARBER 4 138.00 | 533063 | SC10BEL4 138.00 | 0 |  | 1 |  |  |  |  | WERE | OXFORD 138KV Capacitor Displacement | Install 30 MVAR Capacitor Bank at Oxford 138 kV | [5 empty] | 18 | 18 | [5 empty] | 1215000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V13394417SP |  |  | OXFORD 138KV | S | WERE |  | SCENTRAL |  |  | 532982 | OXFORD 4 138.00 | [5 empty] | 17SP | [6 empty] | 1.0131 | 0.94167 | 1.00108 | 0.95 | 1.05 | CATEGORYB | SINGLE | OXFORD - SUMNER COUNTY NO. 10 BELLE PLAIN 138KV CKT 1 | 0 | 533063 | SC10BEL4 138.00 | 532982 | OXFORD 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | OXFORD 138KV Capacitor Displacement | Install 30 MVAR Capacitor Bank at Oxford 138 kV | [5 empty] | 18 | 18 | [5 empty] | 1215000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V13384417SP |  |  | CRESWELL 138KV | S | WERE |  | SCENTRAL |  |  | 532981 | CRESWLN4 138.00 | [5 empty] | 17SP | [6 empty] | 1.0142 | 0.94246 | 0.99138 | 0.95 | 1.05 | CATEGORYB | SINGLE | OXFORD - SUMNER COUNTY NO. 10 BELLE PLAIN 138KV CKT 1 | 0 | 533063 | SC10BEL4 138.00 | 532982 | OXFORD 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | OXFORD 138KV Capacitor Displacement | Install 30 MVAR Capacitor Bank at Oxford 138 kV | [5 empty] | 18 | 18 | [5 empty] | 1215000 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V4751208SP |  |  | BEMIS 115KV | EXP | MIDW |  | REG E-IL |  |  | 530590 | BEMIS 3 115.00 | [5 empty] | 08SP | [6 empty] | 0.78058 | 0.77779 | 0.99263 | 0.9 | 1.1 | CATEGORYB | SINGLE | KNOLL - SALINE RIVER 115KV CKT 1 | 0 | 530561 | KNOLL 3 115.00 | 530551 | SALINE 3 115.00 | 0 |  | 1 |  |  |  | Capacitor banks at 56378, 56391 should on at 24 MVAR. Reactors at 56452, 56468 should be off 0 MVAR. Line reactor on Mingo to Setab line 56451- 56465 should be switched off. | SUNC | PHILLIPSBURG - RHOADES 115 kV | Install 35 miles 115 kV from Phillipsburgsubstion to Rhoades | [37 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V4741208SP |  |  | SALINE RIVER 115KV | EXP | MIDW |  | REG E-IL |  |  | 530551 | SALINE 3 115.00 | [5 empty] | 08SP | [6 empty] | 0.78219 | 0.7794 | 0.99388 | 0.9 | 1.1 | CATEGORYB | SINGLE | KNOLL - SALINE RIVER 115KV CKT 1 | 0 | 530561 | KNOLL 3 115.00 | 530551 | SALINE 3 115.00 | 0 |  | 1 |  |  |  | Capacitor banks at 56378, 56391 should on at 24 MVAR. Reactors at 56452, 56468 should be off 0 MVAR. Line reactor on Mingo to Setab line 56451- 56465 should be switched off. | SUNC | PHILLIPSBURG - RHOADES 115 kV | Install 35 miles 115 kV from Phillipsburgsubstion to Rhoades | [37 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V4771208SP |  |  | PLAINVILLE 115KV | EXP | WEPL |  |  |  |  | 539686 | PLAINVL3 115.00 | [5 empty] | 08SP | [6 empty] | 0.78568 | 0.7829 | 0.9906 | 0.9 | 1.1 | CATEGORYB | SINGLE | KNOLL - SALINE RIVER 115KV CKT 1 | 0 | 530561 | KNOLL 3 115.00 | 530551 | SALINE 3 115.00 | 0 |  | 1 |  |  |  | Capacitor banks at 56378, 56391 should on at 24 MVAR. Reactors at 56452, 56468 should be off 0 MVAR. Line reactor on Mingo to Setab line 56451- 56465 should be switched off. | SUNC | PHILLIPSBURG - RHOADES 115 kV | Install 35 miles 115 kV from Phillipsburgsubstion to Rhoades | [37 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V4301408SH |  |  | PRATT 115KV | EXP | WEPL |  |  |  |  | 539687 | PRATT 3 115.00 | [5 empty] | 08SH | [6 empty] | 0.92099 | 0.89812 | 0.94243 | 0.9 | 1.1 | CATEGORYB | SINGLE | SEWARD - ST JOHN 115KV CKT 1 | 0 | 539692 | SEWARD 3 115.00 | 539696 | ST-JOHN3 115.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V5732308SP |  |  | MILAN 4 138KV | EXP | WEPL |  |  |  |  | 539676 | MILAN 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.87784 | 0.85203 | 0.99597 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V5732308SP |  |  | MILAN 4 138KV | EXP | WEPL |  |  |  |  | 539676 | MILAN 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.87784 | 0.85203 | 0.99597 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V5732308SP |  |  | MILAN 4 138KV | EXP | WEPL |  |  |  |  | 539676 | MILAN 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.87784 | 0.85203 | 0.99597 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V5732308SP |  |  | MILAN 4 138KV | EXP | WEPL |  |  |  |  | 539676 | MILAN 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.87784 | 0.85203 | 0.99597 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8682308SP |  |  | MILAN 4 138KV | EXP | WEPL |  |  |  |  | 539676 | MILAN 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.87893 | 0.85271 | 0.99597 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WEPL-03A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8682308SP |  |  | MILAN 4 138KV | EXP | WEPL |  |  |  |  | 539676 | MILAN 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.87893 | 0.85271 | 0.99597 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WEPL-03A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8682308SP |  |  | MILAN 4 138KV | EXP | WEPL |  |  |  |  | 539676 | MILAN 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.87893 | 0.85271 | 0.99597 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WEPL-03A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8682308SP |  |  | MILAN 4 138KV | EXP | WEPL |  |  |  |  | 539676 | MILAN 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.87893 | 0.85271 | 0.99597 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WEPL-03A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V5722308SP |  |  | MILAN TAP 138KV | EXP | WEPL |  |  |  |  | 539675 | MILANTP4 138.00 | [5 empty] | 08SP | [6 empty] | 0.8797 | 0.85424 | 0.99834 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V5722308SP |  |  | MILAN TAP 138KV | EXP | WEPL |  |  |  |  | 539675 | MILANTP4 138.00 | [5 empty] | 08SP | [6 empty] | 0.8797 | 0.85424 | 0.99834 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V5722308SP |  |  | MILAN TAP 138KV | EXP | WEPL |  |  |  |  | 539675 | MILANTP4 138.00 | [5 empty] | 08SP | [6 empty] | 0.8797 | 0.85424 | 0.99834 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V5722308SP |  |  | MILAN TAP 138KV | EXP | WEPL |  |  |  |  | 539675 | MILANTP4 138.00 | [5 empty] | 08SP | [6 empty] | 0.8797 | 0.85424 | 0.99834 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8672308SP |  |  | MILAN TAP 138KV | EXP | WEPL |  |  |  |  | 539675 | MILANTP4 138.00 | [5 empty] | 08SP | [6 empty] | 0.88078 | 0.85491 | 0.99834 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WEPL-03A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8672308SP |  |  | MILAN TAP 138KV | EXP | WEPL |  |  |  |  | 539675 | MILANTP4 138.00 | [5 empty] | 08SP | [6 empty] | 0.88078 | 0.85491 | 0.99834 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WEPL-03A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8672308SP |  |  | MILAN TAP 138KV | EXP | WEPL |  |  |  |  | 539675 | MILANTP4 138.00 | [5 empty] | 08SP | [6 empty] | 0.88078 | 0.85491 | 0.99834 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WEPL-03A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8672308SP |  |  | MILAN TAP 138KV | EXP | WEPL |  |  |  |  | 539675 | MILANTP4 138.00 | [5 empty] | 08SP | [6 empty] | 0.88078 | 0.85491 | 0.99834 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WEPL-03A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V5692308SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.88205 | 0.85729 | 0.97943 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V5692308SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.88205 | 0.85729 | 0.97943 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V5692308SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.88205 | 0.85729 | 0.97943 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V5692308SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.88205 | 0.85729 | 0.97943 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V5692308SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.88205 | 0.85729 | 0.97943 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8642308SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.88309 | 0.85794 | 0.97943 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WEPL-03A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8642308SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.88309 | 0.85794 | 0.97943 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WEPL-03A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8642308SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.88309 | 0.85794 | 0.97943 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WEPL-03A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8642308SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.88309 | 0.85794 | 0.97943 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WEPL-03A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8642308SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.88309 | 0.85794 | 0.97943 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WEPL-03A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V6091108SP |  |  | PRATT 115KV | EXP | WEPL |  |  |  |  | 539687 | PRATT 3 115.00 | [5 empty] | 08SP | [6 empty] | 0.90095 | 0.88014 | 0.93137 | 0.9 | 1.1 | CATEGORYB | SINGLE | PRATT - ST JOHN 115KV CKT 1 | 0 | 539696 | ST-JOHN3 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8662308SP |  |  | MEDICINE LODGE 138KV | EXP | WEPL |  |  |  |  | 539674 | MED-LDG4 138.00 | [5 empty] | 08SP | [6 empty] | 0.90458 | 0.88448 | 0.9675 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WEPL-03A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8662308SP |  |  | MEDICINE LODGE 138KV | EXP | WEPL |  |  |  |  | 539674 | MED-LDG4 138.00 | [5 empty] | 08SP | [6 empty] | 0.90458 | 0.88448 | 0.9675 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WEPL-03A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8662308SP |  |  | MEDICINE LODGE 138KV | EXP | WEPL |  |  |  |  | 539674 | MED-LDG4 138.00 | [5 empty] | 08SP | [6 empty] | 0.90458 | 0.88448 | 0.9675 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WEPL-03A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8662308SP |  |  | MEDICINE LODGE 138KV | EXP | WEPL |  |  |  |  | 539674 | MED-LDG4 138.00 | [5 empty] | 08SP | [6 empty] | 0.90458 | 0.88448 | 0.9675 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WEPL-03A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 3 | 2008-12-01 | 2007AG1AFS81V6721309SP |  |  | MILAN 4 138KV | EXP | WEPL |  |  |  |  | 539676 | MILAN 4 138.00 | [5 empty] | 09SP | [6 empty] | 0.85258 | 0.83191 | 0.99414 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 3 | 2008-12-01 | 2007AG1AFS81V6721309SP |  |  | MILAN 4 138KV | EXP | WEPL |  |  |  |  | 539676 | MILAN 4 138.00 | [5 empty] | 09SP | [6 empty] | 0.85258 | 0.83191 | 0.99414 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 3 | 2008-12-01 | 2007AG1AFS81V6721309SP |  |  | MILAN 4 138KV | EXP | WEPL |  |  |  |  | 539676 | MILAN 4 138.00 | [5 empty] | 09SP | [6 empty] | 0.85258 | 0.83191 | 0.99414 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 3 | 2008-12-01 | 2007AG1AFS81V6721309SP |  |  | MILAN 4 138KV | EXP | WEPL |  |  |  |  | 539676 | MILAN 4 138.00 | [5 empty] | 09SP | [6 empty] | 0.85258 | 0.83191 | 0.99414 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 3 | 2008-12-01 | 2007AG1AFS81V6711309SP |  |  | MILAN TAP 138KV | EXP | WEPL |  |  |  |  | 539675 | MILANTP4 138.00 | [5 empty] | 09SP | [6 empty] | 0.85484 | 0.83447 | 0.99658 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 3 | 2008-12-01 | 2007AG1AFS81V6711309SP |  |  | MILAN TAP 138KV | EXP | WEPL |  |  |  |  | 539675 | MILANTP4 138.00 | [5 empty] | 09SP | [6 empty] | 0.85484 | 0.83447 | 0.99658 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 3 | 2008-12-01 | 2007AG1AFS81V6711309SP |  |  | MILAN TAP 138KV | EXP | WEPL |  |  |  |  | 539675 | MILANTP4 138.00 | [5 empty] | 09SP | [6 empty] | 0.85484 | 0.83447 | 0.99658 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 3 | 2008-12-01 | 2007AG1AFS81V6711309SP |  |  | MILAN TAP 138KV | EXP | WEPL |  |  |  |  | 539675 | MILANTP4 138.00 | [5 empty] | 09SP | [6 empty] | 0.85484 | 0.83447 | 0.99658 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V5784209SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 09SP | [6 empty] | 0.86079 | 0.83988 | 0.97353 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V5784209SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 09SP | [6 empty] | 0.86079 | 0.83988 | 0.97353 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V5784209SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 09SP | [6 empty] | 0.86079 | 0.83988 | 0.97353 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V5784209SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 09SP | [6 empty] | 0.86079 | 0.83988 | 0.97353 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V5784209SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 09SP | [6 empty] | 0.86079 | 0.83988 | 0.97353 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V5714209SP |  |  | PRATT 115KV | EXP | WEPL |  |  |  |  | 539687 | PRATT 3 115.00 | [5 empty] | 09SP | [6 empty] | 1 | 0.89883 | 0.92078 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | 0 | 533045 | GILL W 4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V12081212SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.87742 | 0.97111 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WERE-34A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V12081212SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.87742 | 0.97111 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WERE-34A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V12081212SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.87742 | 0.97111 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WERE-34A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V12081212SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.87742 | 0.97111 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WERE-34A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V12081212SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.87742 | 0.97111 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WERE-34A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V9474212SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.87813 | 0.97139 | 0.9 | 1.1 | CATEGORYB | SINGLE | HARPER - MILAN TAP 138KV CKT 1 | 0 | 539675 | MILANTP4 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V9474212SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.87813 | 0.97139 | 0.9 | 1.1 | CATEGORYB | SINGLE | HARPER - MILAN TAP 138KV CKT 1 | 0 | 539675 | MILANTP4 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V9474212SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.87813 | 0.97139 | 0.9 | 1.1 | CATEGORYB | SINGLE | HARPER - MILAN TAP 138KV CKT 1 | 0 | 539675 | MILANTP4 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V9474212SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.87813 | 0.97139 | 0.9 | 1.1 | CATEGORYB | SINGLE | HARPER - MILAN TAP 138KV CKT 1 | 0 | 539675 | MILANTP4 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V9474212SP |  |  | HARPER 138KV | EXP | WEPL |  |  |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.87813 | 0.97139 | 0.9 | 1.1 | CATEGORYB | SINGLE | HARPER - MILAN TAP 138KV CKT 1 | 0 | 539675 | MILANTP4 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V12111212SP |  |  | PRATT 115KV | EXP | WEPL |  |  |  |  | 539687 | PRATT 3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.88006 | 0.91434 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WERE-34A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V9504212SP |  |  | PRATT 115KV | EXP | WEPL |  |  |  |  | 539687 | PRATT 3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.88078 | 0.91426 | 0.9 | 1.1 | CATEGORYB | SINGLE | HARPER - MILAN TAP 138KV CKT 1 | 0 | 539675 | MILANTP4 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V12041212SP |  |  | PAWNEE 115KV | EXP | MIDW |  | REG E-IL |  |  | 530621 | PAWNEE 3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.88345 | 0.90566 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WERE-34A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V9434212SP |  |  | PAWNEE 115KV | EXP | MIDW |  | REG E-IL |  |  | 530621 | PAWNEE 3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.88418 | 0.90552 | 0.9 | 1.1 | CATEGORYB | SINGLE | HARPER - MILAN TAP 138KV CKT 1 | 0 | 539675 | MILANTP4 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V12031212SP |  |  | KINSLEY 115KV | EXP | MIDW |  | REG E-IL |  |  | 530619 | KINSLEY3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.88538 | 0.90754 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WERE-34A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V9424212SP |  |  | KINSLEY 115KV | EXP | MIDW |  | REG E-IL |  |  | 530619 | KINSLEY3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.8861 | 0.9074 | 0.9 | 1.1 | CATEGORYB | SINGLE | HARPER - MILAN TAP 138KV CKT 1 | 0 | 539675 | MILANTP4 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V12051212SP |  |  | PAWNEE-EDWARDS_JCT 115KV | EXP | MIDW |  | REG E-IL |  |  | 530622 | PAWN-ED3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.88993 | 0.91196 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WERE-34A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V9444212SP |  |  | PAWNEE-EDWARDS_JCT 115KV | EXP | MIDW |  | REG E-IL |  |  | 530622 | PAWN-ED3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.89065 | 0.91182 | 0.9 | 1.1 | CATEGORYB | SINGLE | HARPER - MILAN TAP 138KV CKT 1 | 0 | 539675 | MILANTP4 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V12021212SP |  |  | EDWARDS 115KV | EXP | MIDW |  | REG E-IL |  |  | 530617 | EDWARDS3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.89219 | 0.91414 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WERE-34A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V9414212SP |  |  | EDWARDS 115KV | EXP | MIDW |  | REG E-IL |  |  | 530617 | EDWARDS3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.8929 | 0.914 | 0.9 | 1.1 | CATEGORYB | SINGLE | HARPER - MILAN TAP 138KV CKT 1 | 0 | 539675 | MILANTP4 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V12101212SP |  |  | MEDICINE LODGE 138KV | EXP | WEPL |  |  |  |  | 539674 | MED-LDG4 138.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.89382 | 0.95446 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WERE-34A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V12101212SP |  |  | MEDICINE LODGE 138KV | EXP | WEPL |  |  |  |  | 539674 | MED-LDG4 138.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.89382 | 0.95446 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WERE-34A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V12101212SP |  |  | MEDICINE LODGE 138KV | EXP | WEPL |  |  |  |  | 539674 | MED-LDG4 138.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.89382 | 0.95446 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WERE-34A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V12101212SP |  |  | MEDICINE LODGE 138KV | EXP | WEPL |  |  |  |  | 539674 | MED-LDG4 138.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.89382 | 0.95446 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WERE-34A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V9494212SP |  |  | MEDICINE LODGE 138KV | EXP | WEPL |  |  |  |  | 539674 | MED-LDG4 138.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.8945 | 0.9548 | 0.9 | 1.1 | CATEGORYB | SINGLE | HARPER - MILAN TAP 138KV CKT 1 | 0 | 539675 | MILANTP4 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V9494212SP |  |  | MEDICINE LODGE 138KV | EXP | WEPL |  |  |  |  | 539674 | MED-LDG4 138.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.8945 | 0.9548 | 0.9 | 1.1 | CATEGORYB | SINGLE | HARPER - MILAN TAP 138KV CKT 1 | 0 | 539675 | MILANTP4 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V9494212SP |  |  | MEDICINE LODGE 138KV | EXP | WEPL |  |  |  |  | 539674 | MED-LDG4 138.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.8945 | 0.9548 | 0.9 | 1.1 | CATEGORYB | SINGLE | HARPER - MILAN TAP 138KV CKT 1 | 0 | 539675 | MILANTP4 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V9494212SP |  |  | MEDICINE LODGE 138KV | EXP | WEPL |  |  |  |  | 539674 | MED-LDG4 138.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.8945 | 0.9548 | 0.9 | 1.1 | CATEGORYB | SINGLE | HARPER - MILAN TAP 138KV CKT 1 | 0 | 539675 | MILANTP4 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V12091212SP |  |  | MEDICINE LODGE 115KV | EXP | WEPL |  |  |  |  | 539673 | MED-LDG3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.89549 | 0.95083 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WERE-34A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V12091212SP |  |  | MEDICINE LODGE 115KV | EXP | WEPL |  |  |  |  | 539673 | MED-LDG3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.89549 | 0.95083 | 0.9 | 1.1 | CATEGORYB | NONSINGLE | SPP-WERE-34A | 0 | 0 |  | 0 |  | 0 | [6 empty] | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V9484212SP |  |  | MEDICINE LODGE 115KV | EXP | WEPL |  |  |  |  | 539673 | MED-LDG3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.89615 | 0.95085 | 0.9 | 1.1 | CATEGORYB | SINGLE | HARPER - MILAN TAP 138KV CKT 1 | 0 | 539675 | MILANTP4 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V9484212SP |  |  | MEDICINE LODGE 115KV | EXP | WEPL |  |  |  |  | 539673 | MED-LDG3 115.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.89615 | 0.95085 | 0.9 | 1.1 | CATEGORYB | SINGLE | HARPER - MILAN TAP 138KV CKT 1 | 0 | 539675 | MILANTP4 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  |  |  | FNSL-CHECK-TC | FDNS-Iteration limit exceeded | 4 | 3 | 2008-12-01 | 2007AG1AFS82V14312WP |  |  | CLEARWATER 138KV | EXP | WERE |  | SCENTRAL |  |  | 533036 | CLEARWT4 138.00 | [5 empty] | 12WP | [6 empty] | 0.96064 | 0.91058 | 1.01815 | 0.95 | 1.05 | CATEGORYB | SINGLE | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | 0 | 533045 | GILL W 4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V13484417SP |  |  | PAWNEE 115KV | EXP | MIDW |  | REG E-IL |  |  | 530621 | PAWNEE 3 115.00 | [5 empty] | 17SP | [6 empty] | 1 | 0.87206 | 0.89467 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | 0 | 533045 | GILL W 4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V13474417SP |  |  | KINSLEY 115KV | EXP | MIDW |  | REG E-IL |  |  | 530619 | KINSLEY3 115.00 | [5 empty] | 17SP | [6 empty] | 1 | 0.87409 | 0.89666 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | 0 | 533045 | GILL W 4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V13504417SP |  |  | PRATT 115KV | EXP | WEPL |  |  |  |  | 539687 | PRATT 3 115.00 | [5 empty] | 17SP | [6 empty] | 1 | 0.87559 | 0.90538 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | 0 | 533045 | GILL W 4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V13494417SP |  |  | PAWNEE-EDWARDS_JCT 115KV | EXP | MIDW |  | REG E-IL |  |  | 530622 | PAWN-ED3 115.00 | [5 empty] | 17SP | [6 empty] | 1 | 0.87895 | 0.90137 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | 0 | 533045 | GILL W 4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FNSL | FDNS-Iteration limit exceeded | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V13184217SP |  |  | PRATT 115KV | EXP | WEPL |  |  |  |  | 539687 | PRATT 3 115.00 | [5 empty] | 17SP | [6 empty] | 1 | 0.88031 | 0.90163 | 0.9 | 1.1 | CATEGORYB | SINGLE | GREENSBURG - JUDSON LARGE 115KV CKT 1 | 0 | 539671 | JUD-LRG3 115.00 | 539664 | GRNBURG3 115.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V13464417SP |  |  | EDWARDS 115KV | EXP | MIDW |  | REG E-IL |  |  | 530617 | EDWARDS3 115.00 | [5 empty] | 17SP | [6 empty] | 1 | 0.88138 | 0.90371 | 0.9 | 1.1 | CATEGORYB | SINGLE | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | 0 | 533045 | GILL W 4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 |  |  |  |  | MKEC | PRATT 115KV Capacitor | Install (2) 12 Mvar cap banks at Pratt 115kV | [5 empty] | 12 | 12 | [30 empty] | 2008-06-01 | 2009-06-01 | 2008-10-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12742312SP |  |  | RALPH GREEN 69KV | REL | MIPU |  |  |  |  | 541279 | RGREEN 2 69.000 | [5 empty] | 12SP | [5 empty] | 540_Ralph Green 12MVar Cap | 0.92431 | 0.89331 | 0.98061 | 0.9 | 1.1 | CATEGORYB | SINGLE | PLEASANT HILL - RALPH GREEN 69KV CKT 1 | 0 | 541280 | PHILL 2 69.000 | 541279 | RGREEN 2 69.000 | 0 |  | 1 |  |  |  |  | MIPU | RALPH GREEN 12MVAR CAPACITOR | 12MVAR at Ralph Green | [5 empty] | 12 | [7 empty] | 2006-06-01 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15992317SP |  |  | RALPH GREEN 69KV | REL | MIPU |  |  |  |  | 541279 | RGREEN 2 69.000 | [5 empty] | 17SP | [5 empty] | 540_Ralph Green 12MVar Cap | 0.8974 | 0.87224 | 0.97356 | 0.9 | 1.1 | CATEGORYB | SINGLE | PLEASANT HILL - RALPH GREEN 69KV CKT 1 | 0 | 541280 | PHILL 2 69.000 | 541279 | RGREEN 2 69.000 | 0 |  | 1 |  |  |  |  | MIPU | RALPH GREEN 12MVAR CAPACITOR | 12MVAR at Ralph Green | [5 empty] | 12 | [7 empty] | 2006-06-01 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15982317SP |  |  | HOLDEN 69KV | REL | MIPU |  |  |  |  | 541278 | HOLDEN 2 69.000 | [5 empty] | 17SP | [5 empty] | 540_Ralph Green 12MVar Cap | 0.92176 | 0.89646 | 0.9594 | 0.9 | 1.1 | CATEGORYB | SINGLE | PLEASANT HILL - RALPH GREEN 69KV CKT 1 | 0 | 541280 | PHILL 2 69.000 | 541279 | RGREEN 2 69.000 | 0 |  | 1 |  |  |  |  | MIPU | RALPH GREEN 12MVAR CAPACITOR | 12MVAR at Ralph Green | [5 empty] | 12 | [7 empty] | 2006-06-01 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V3871408SH |  |  | CITY OF WINFIELD 69KV | S | WERE |  | SCENTRAL |  |  | 533561 | WINFLD 2 69.000 | [5 empty] | 08SH | [6 empty] | 1.0026 | 0.92774 | 0.97359 | 0.95 | 1.05 | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | RICHLAND - ROSE HILL JUNCTION 69KV CKT 1 Displacement | Rebuild 5.43 mile Rose Hill Junction-Richland as a 138 kV line but operate at 69 kV. | 72 | 72 | 72 | 72 | 5.43 | 12 | 5 |  | 0.01146 | 0.07817 | 0.00166 | 72 MVA is CT and disconnect switch limit. | 2240142 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V3871408SH |  |  | CITY OF WINFIELD 69KV | S | WERE |  | SCENTRAL |  |  | 533561 | WINFLD 2 69.000 | [5 empty] | 08SH | [6 empty] | 1.0026 | 0.92774 | 0.97359 | 0.95 | 1.05 | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | RICHLAND - ROSE HILL JUNCTION 69KV CKT 1 Displacement | Rebuild 5.43 mile Rose Hill Junction-Richland as a 138 kV line but operate at 69 kV. | 72 | 72 | 72 | 72 | 5.43 | 12 | 5 |  | 0.01146 | 0.07817 | 0.00166 | 72 MVA is CT and disconnect switch limit. | 2240142 | 2008-03-14 | [23 empty] | 2008-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V3871408SH |  |  | CITY OF WINFIELD 69KV | EXP | WERE |  | SCENTRAL |  |  | 533561 | WINFLD 2 69.000 | [5 empty] | 08SH | [6 empty] | 1.0026 | 0.92774 | 0.97359 | 0.95 | 1.05 | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ROSE HILL JUNCTION - WEAVER 69KV CKT 1 | Rebuild 5.73 mile Weaver-Rose Hill Junction as a 138 kV line but operate at 69 kV. | 116 | 128 | 116 | 128 | 5.73 | 12 | 5 |  | 0.01209 | 0.08228 | 0.001749 | MVA limit is conductor | 2300000 | 2006-07-25 | [23 empty] | 2008-06-01 | 2008-12-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V3871408SH |  |  | CITY OF WINFIELD 69KV | EXP | WERE |  | SCENTRAL |  |  | 533561 | WINFLD 2 69.000 | [5 empty] | 08SH | [6 empty] | 1.0026 | 0.92774 | 0.97359 | 0.95 | 1.05 | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | ROSE HILL JUNCTION - WEAVER 69KV CKT 1 | Rebuild 5.73 mile Weaver-Rose Hill Junction as a 138 kV line but operate at 69 kV. | 116 | 128 | 116 | 128 | 5.73 | 12 | 5 |  | 0.01209 | 0.08228 | 0.001749 | MVA limit is conductor | 2300000 | 2006-07-25 | [23 empty] | 2008-06-01 | 2008-12-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15032312SP |  |  | WATHENA 69KV | EXP | WERE |  | NEAST |  |  | 533485 | WATHENA2 69.000 | [5 empty] | 12SP | [6 empty] | 0.88434 | 0.8519 | 0.93789 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15032312SP |  |  | WATHENA 69KV | EXP | WERE |  | NEAST |  |  | 533485 | WATHENA2 69.000 | [5 empty] | 12SP | [6 empty] | 0.88434 | 0.8519 | 0.93789 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14922312SP |  |  | ATCHISON CASTINGS 69KV | EXP | WERE |  | NEAST |  |  | 533474 | ATCHCST2 69.000 | [5 empty] | 12SP | [6 empty] | 0.91812 | 0.88723 | 0.96955 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14952312SP |  |  | MIDWEST GRAIN 69KV | EXP | WERE |  | NEAST |  |  | 533477 | MW SOLV2 69.000 | [5 empty] | 12SP | [6 empty] | 0.92188 | 0.89112 | 0.97316 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14912312SP |  |  | ATCHISON JCT2 69KV | EXP | WERE |  | NEAST |  |  | 533473 | ATCH J22 69.000 | [5 empty] | 12SP | [6 empty] | 0.92258 | 0.89185 | 0.97382 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14902312SP |  |  | ATCHISON JCT1 69KV | EXP | WERE |  | NEAST |  |  | 533472 | ATCH J12 69.000 | [5 empty] | 12SP | [6 empty] | 0.92263 | 0.89189 | 0.97382 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14962312SP |  |  | MIDWEST GRAIN SOLVENTS JCT1 69KV | EXP | WERE |  | NEAST |  |  | 533478 | MWSOLJ12 69.000 | [5 empty] | 12SP | [6 empty] | 0.9227 | 0.89197 | 0.97389 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15022312SP |  |  | WALNUT STREET 69KV | EXP | WERE |  | NEAST |  |  | 533484 | WALNUT 2 69.000 | [5 empty] | 12SP | [6 empty] | 0.92429 | 0.89356 | 0.9754 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14942312SP |  |  | MAUR HILL 69KV | EXP | WERE |  | NEAST |  |  | 533476 | MAUR HL2 69.000 | [5 empty] | 12SP | [6 empty] | 0.92448 | 0.89385 | 0.97575 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14972312SP |  |  | MIDWEST GRAIN SOLVENTS JCT2 69KV | EXP | WERE |  | NEAST |  |  | 533479 | MWSOLJ22 69.000 | [5 empty] | 12SP | [6 empty] | 0.92519 | 0.89456 | 0.97609 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14932312SP |  |  | KEREFORD JUNCTION 69KV | EXP | WERE |  | NEAST |  |  | 533475 | KERFORD2 69.000 | [5 empty] | 12SP | [6 empty] | 0.92938 | 0.89897 | 0.98057 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14682312SP |  |  | WALNUT STREET 115KV | EXP | WERE |  | NEAST |  |  | 533220 | WALNUT 3 115.00 | [5 empty] | 12SP | [6 empty] | 0.92929 | 0.89956 | 0.97745 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14682312SP |  |  | WALNUT STREET 115KV | EXP | WERE |  | NEAST |  |  | 533220 | WALNUT 3 115.00 | [5 empty] | 12SP | [6 empty] | 0.92929 | 0.89956 | 0.97745 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14662312SP |  |  | PARALLEL 115KV | EXP | WERE |  | NEAST |  |  | 533218 | PARALEL3 115.00 | [5 empty] | 12SP | [6 empty] | 0.93108 | 0.90149 | 0.97901 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14892312SP |  |  | ARNOLD 69KV | EXP | WERE |  | NEAST |  |  | 533471 | ARNOLD 2 69.000 | [5 empty] | 12SP | [6 empty] | 0.93501 | 0.90478 | 0.98468 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14642312SP |  |  | ARNOLD 115KV | EXP | WERE |  | NEAST |  |  | 533211 | ARNOLD 3 115.00 | [5 empty] | 12SP | [6 empty] | 0.93571 | 0.9064 | 0.98329 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14652312SP |  |  | KEREFORD JUNCTION 115KV | EXP | WERE |  | NEAST |  |  | 533216 | KERFORD3 115.00 | [5 empty] | 12SP | [6 empty] | 0.93781 | 0.90868 | 0.98529 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14982312SP |  |  | MUSCOTAH 69KV | EXP | WERE |  | NEAST |  |  | 533480 | MUSCOTA2 69.000 | [5 empty] | 12SP | [6 empty] | 0.94761 | 0.91972 | 0.96454 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14982312SP |  |  | MUSCOTAH 69KV | EXP | WERE |  | NEAST |  |  | 533480 | MUSCOTA2 69.000 | [5 empty] | 12SP | [6 empty] | 0.94761 | 0.91972 | 0.96454 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14982312SP |  |  | MUSCOTAH 69KV | EXP | WERE |  | NEAST |  |  | 533480 | MUSCOTA2 69.000 | [5 empty] | 12SP | [6 empty] | 0.94761 | 0.91972 | 0.96454 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14982312SP |  |  | MUSCOTAH 69KV | EXP | WERE |  | NEAST |  |  | 533480 | MUSCOTA2 69.000 | [5 empty] | 12SP | [6 empty] | 0.94761 | 0.91972 | 0.96454 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14982312SP |  |  | MUSCOTAH 69KV | EXP | WERE |  | NEAST |  |  | 533480 | MUSCOTA2 69.000 | [5 empty] | 12SP | [6 empty] | 0.94761 | 0.91972 | 0.96454 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14822312SP |  |  | SPRUCE STREET 115KV | EXP | WERE |  | NEAST |  |  | 533266 | SPRUCE 3 115.00 | [5 empty] | 12SP | [6 empty] | 0.95018 | 0.9226 | 0.99588 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14852312SP |  |  | THORNTON STREET 115KV | EXP | WERE |  | NEAST |  |  | 533272 | THORNTN3 115.00 | [5 empty] | 12SP | [6 empty] | 0.9502 | 0.92269 | 0.99589 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14732312SP |  |  | HALLMARK 115KV | EXP | WERE |  | NEAST |  |  | 533242 | HALLMRK3 115.00 | [5 empty] | 12SP | [6 empty] | 0.9509 | 0.92353 | 0.99437 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14792312SP |  |  | NORTHWEST LEAVENWORTH 115KV | EXP | WERE |  | NEAST |  |  | 533259 | NW LEAV3 115.00 | [5 empty] | 12SP | [6 empty] | 0.9535 | 0.92568 | 0.9993 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14762312SP |  |  | LANSING3 115.00 115KV | EXP | WERE |  | NEAST |  |  | 533246 | LANSING3 115.00 | [5 empty] | 12SP | [6 empty] | 0.9552 | 0.92818 | 0.99696 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14992312SP |  |  | NORTONVILLE 69KV | EXP | WERE |  | NEAST |  |  | 533481 | NORTONV2 69.000 | [5 empty] | 12SP | [6 empty] | 0.95609 | 0.92849 | 0.97286 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14842312SP |  |  | STRANGER CREEK 115KV | EXP | WERE |  | NEAST |  |  | 533268 | STRANGR3 115.00 | [5 empty] | 12SP | [6 empty] | 0.95608 | 0.92894 | 1.003 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15012312SP |  |  | VALLEY FALLS 69KV | EXP | WERE |  | NEAST |  |  | 533483 | VALLEY22 69.000 | [5 empty] | 12SP | [6 empty] | 0.96124 | 0.93669 | 0.97769 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15012312SP |  |  | VALLEY FALLS 69KV | EXP | WERE |  | NEAST |  |  | 533483 | VALLEY22 69.000 | [5 empty] | 12SP | [6 empty] | 0.96124 | 0.93669 | 0.97769 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14772312SP |  |  | MOONLIGHT 115KV | EXP | WERE |  | NEAST |  |  | 533254 | MOONLIT3 115.00 | [5 empty] | 12SP | [6 empty] | 0.96432 | 0.93941 | 0.97251 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14882312SP |  |  | 95TH & WAVERLY 115KV | EXP | WERE |  | NEAST |  |  | 533278 | WAVERLY3 115.00 | [5 empty] | 12SP | [6 empty] | 0.96371 | 0.93974 | 0.97737 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12812312SP |  |  | NEW SPRING HILL 115KV | EXP | WERE |  | NEAST |  |  | 533267 | SPRINGH3 115.00 | [5 empty] | 12SP | [6 empty] | 0.96726 | 0.93985 | 0.97259 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14712312SP |  |  | EAST S.A.A.P. JCT 115KV | EXP | WERE |  | NEAST |  |  | 533239 | ESAAPJ 3 115.00 | [5 empty] | 12SP | [6 empty] | 0.96413 | 0.93994 | 0.9766 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14782312SP |  |  | MOONLIGHT JUNCTION SWITCHING STATION 115KV | EXP | WERE |  | NEAST |  |  | 533255 | MOONLTJ3 115.00 | [5 empty] | 12SP | [6 empty] | 0.96582 | 0.94095 | 0.974 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12792312SP |  |  | 160TH STREET 115KV | EXP | WERE |  | NEAST |  |  | 533262 | 160TH 3 115.00 | [5 empty] | 12SP | [6 empty] | 0.96832 | 0.94254 | 0.97259 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14752312SP |  |  | JARBALO JUNCTION SWITCHING STATION 115KV | EXP | WERE |  | NEAST |  |  | 533244 | JARBALO3 115.00 | [5 empty] | 12SP | [6 empty] | 0.96888 | 0.94286 | 1.00546 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14812312SP |  |  | SOUTHTOWN 115KV | EXP | WERE |  | NEAST |  |  | 533265 | SOUTHTN3 115.00 | [5 empty] | 12SP | [6 empty] | 0.96862 | 0.94344 | 0.97319 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14672312SP |  |  | TONGA TAP 115KV | EXP | WERE |  | NEAST |  |  | 533219 | TONGATP3 115.00 | [5 empty] | 12SP | [6 empty] | 0.96875 | 0.94382 | 1.00336 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V9402312SP |  |  | NEW SPRING HILL 115KV | EXP | WERE |  | NEAST |  |  | 533267 | SPRINGH3 115.00 | [5 empty] | 12SP | [6 empty] | 0.9711 | 0.94404 | 0.97259 | 0.95 | 1.05 | CATEGORYB | SINGLE | CRAIG - STRANGER CREEK 345KV CKT 1 | 0 | 532772 | STRANGR7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14692312SP |  |  | 166TH STREET 115KV | EXP | WERE |  | NEAST |  |  | 533233 | 166TH 3 115.00 | [5 empty] | 12SP | [6 empty] | 0.96984 | 0.94475 | 0.99465 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14862312SP |  |  | TIMBERLANE 115KV | EXP | WERE |  | NEAST |  |  | 533273 | TIMBRLN3 115.00 | [5 empty] | 12SP | [6 empty] | 0.96996 | 0.94501 | 0.9769 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12772312SP |  |  | MOONLIGHT 115KV | EXP | WERE |  | NEAST |  |  | 533254 | MOONLIT3 115.00 | [5 empty] | 12SP | [6 empty] | 0.96914 | 0.94523 | 0.97251 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14702312SP |  |  | CAPTAIN JUNCTION 115KV | EXP | WERE |  | NEAST |  |  | 533235 | CAPTAIN3 115.00 | [5 empty] | 12SP | [6 empty] | 0.96972 | 0.94673 | 0.98736 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12782312SP |  |  | MOONLIGHT JUNCTION SWITCHING STATION 115KV | EXP | WERE |  | NEAST |  |  | 533255 | MOONLTJ3 115.00 | [5 empty] | 12SP | [6 empty] | 0.97063 | 0.94676 | 0.974 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14722312SP |  |  | EUDORA TOWNSHIP 115KV | EXP | WERE |  | NEAST |  |  | 533240 | EUDORA 3 115.00 | [5 empty] | 12SP | [6 empty] | 0.96977 | 0.94707 | 0.98899 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14742312SP |  |  | JAGGARD JUNCTION 115KV | EXP | WERE |  | NEAST |  |  | 533243 | JAGGARD3 115.00 | [5 empty] | 12SP | [6 empty] | 0.97213 | 0.94777 | 0.9898 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14872312SP |  |  | WAKARUSA JUNCTION SWITCHING STATION 115KV | EXP | WERE |  | NEAST |  |  | 533277 | WAKARUS3 115.00 | [5 empty] | 12SP | [6 empty] | 0.97129 | 0.94909 | 0.99267 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12822312SP |  |  | TIMBERLANE 115KV | EXP | WERE |  | NEAST |  |  | 533273 | TIMBRLN3 115.00 | [5 empty] | 12SP | [6 empty] | 0.97358 | 0.9495 | 0.9769 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V9372312SP |  |  | MOONLIGHT 115KV | EXP | WERE |  | NEAST |  |  | 533254 | MOONLIT3 115.00 | [5 empty] | 12SP | [6 empty] | 0.97338 | 0.94972 | 0.97251 | 0.95 | 1.05 | CATEGORYB | SINGLE | CRAIG - STRANGER CREEK 345KV CKT 1 | 0 | 532772 | STRANGR7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20352317SP |  |  | WATHENA 69KV | EXP | WERE |  | NEAST |  |  | 533485 | WATHENA2 69.000 | [5 empty] | 17SP | [6 empty] | 0.82937 | 0.76196 | 0.93811 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20352317SP |  |  | WATHENA 69KV | EXP | WERE |  | NEAST |  |  | 533485 | WATHENA2 69.000 | [5 empty] | 17SP | [6 empty] | 0.82937 | 0.76196 | 0.93811 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19782317SP |  |  | WALNUT STREET 115KV | EXP | WERE |  | NEAST |  |  | 533220 | WALNUT 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.84913 | 0.79126 | 0.94755 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19782317SP |  |  | WALNUT STREET 115KV | EXP | WERE |  | NEAST |  |  | 533220 | WALNUT 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.84913 | 0.79126 | 0.94755 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19762317SP |  |  | PARALLEL 115KV | EXP | WERE |  | NEAST |  |  | 533218 | PARALEL3 115.00 | [5 empty] | 17SP | [6 empty] | 0.85229 | 0.79471 | 0.9508 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19742317SP |  |  | ARNOLD 115KV | EXP | WERE |  | NEAST |  |  | 533211 | ARNOLD 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.8596 | 0.80265 | 0.95809 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19752317SP |  |  | KEREFORD JUNCTION 115KV | EXP | WERE |  | NEAST |  |  | 533216 | KERFORD3 115.00 | [5 empty] | 17SP | [6 empty] | 0.86208 | 0.80564 | 0.96045 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20242317SP |  |  | ATCHISON CASTINGS 69KV | EXP | WERE |  | NEAST |  |  | 533474 | ATCHCST2 69.000 | [5 empty] | 17SP | [6 empty] | 0.87015 | 0.80739 | 0.97491 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20272317SP |  |  | MIDWEST GRAIN 69KV | EXP | WERE |  | NEAST |  |  | 533477 | MW SOLV2 69.000 | [5 empty] | 17SP | [6 empty] | 0.87445 | 0.81196 | 0.97873 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20222317SP |  |  | ATCHISON JCT1 69KV | EXP | WERE |  | NEAST |  |  | 533472 | ATCH J12 69.000 | [5 empty] | 17SP | [6 empty] | 0.87491 | 0.81251 | 0.97915 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20282317SP |  |  | MIDWEST GRAIN SOLVENTS JCT1 69KV | EXP | WERE |  | NEAST |  |  | 533478 | MWSOLJ12 69.000 | [5 empty] | 17SP | [6 empty] | 0.875 | 0.81261 | 0.97924 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20232317SP |  |  | ATCHISON JCT2 69KV | EXP | WERE |  | NEAST |  |  | 533473 | ATCH J22 69.000 | [5 empty] | 17SP | [6 empty] | 0.87519 | 0.81276 | 0.97939 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20292317SP |  |  | MIDWEST GRAIN SOLVENTS JCT2 69KV | EXP | WERE |  | NEAST |  |  | 533479 | MWSOLJ22 69.000 | [5 empty] | 17SP | [6 empty] | 0.87717 | 0.81504 | 0.98109 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20342317SP |  |  | WALNUT STREET 69KV | EXP | WERE |  | NEAST |  |  | 533484 | WALNUT 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.87838 | 0.81579 | 0.98097 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20262317SP |  |  | MAUR HILL 69KV | EXP | WERE |  | NEAST |  |  | 533476 | MAUR HL2 69.000 | [5 empty] | 17SP | [6 empty] | 0.87802 | 0.81583 | 0.98258 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20252317SP |  |  | KEREFORD JUNCTION 69KV | EXP | WERE |  | NEAST |  |  | 533475 | KERFORD2 69.000 | [5 empty] | 17SP | [6 empty] | 0.88481 | 0.82317 | 0.98967 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20212317SP |  |  | ARNOLD 69KV | EXP | WERE |  | NEAST |  |  | 533471 | ARNOLD 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.88582 | 0.82474 | 0.98834 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20072317SP |  |  | SPRUCE STREET 115KV | EXP | WERE |  | NEAST |  |  | 533266 | SPRUCE 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.88194 | 0.82954 | 0.98008 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20132317SP |  |  | THORNTON STREET 115KV | EXP | WERE |  | NEAST |  |  | 533272 | THORNTN3 115.00 | [5 empty] | 17SP | [6 empty] | 0.8823 | 0.83007 | 0.98053 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20022317SP |  |  | NORTHWEST LEAVENWORTH 115KV | EXP | WERE |  | NEAST |  |  | 533259 | NW LEAV3 115.00 | [5 empty] | 17SP | [6 empty] | 0.88436 | 0.83137 | 0.98179 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19882317SP |  |  | HALLMARK 115KV | EXP | WERE |  | NEAST |  |  | 533242 | HALLMRK3 115.00 | [5 empty] | 17SP | [6 empty] | 0.88371 | 0.83186 | 0.97889 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19922317SP |  |  | LANSING3 115.00 115KV | EXP | WERE |  | NEAST |  |  | 533246 | LANSING3 115.00 | [5 empty] | 17SP | [6 empty] | 0.88996 | 0.839 | 0.98202 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20092317SP |  |  | STRANGER CREEK 115KV | EXP | WERE |  | NEAST |  |  | 533268 | STRANGR3 115.00 | [5 empty] | 17SP | [6 empty] | 0.89049 | 0.83918 | 0.99206 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20302317SP |  |  | MUSCOTAH 69KV | EXP | WERE |  | NEAST |  |  | 533480 | MUSCOTA2 69.000 | [5 empty] | 17SP | [6 empty] | 0.89898 | 0.84172 | 0.96362 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20302317SP |  |  | MUSCOTAH 69KV | EXP | WERE |  | NEAST |  |  | 533480 | MUSCOTA2 69.000 | [5 empty] | 17SP | [6 empty] | 0.89898 | 0.84172 | 0.96362 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20302317SP |  |  | MUSCOTAH 69KV | EXP | WERE |  | NEAST |  |  | 533480 | MUSCOTA2 69.000 | [5 empty] | 17SP | [6 empty] | 0.89898 | 0.84172 | 0.96362 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20302317SP |  |  | MUSCOTAH 69KV | EXP | WERE |  | NEAST |  |  | 533480 | MUSCOTA2 69.000 | [5 empty] | 17SP | [6 empty] | 0.89898 | 0.84172 | 0.96362 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20302317SP |  |  | MUSCOTAH 69KV | EXP | WERE |  | NEAST |  |  | 533480 | MUSCOTA2 69.000 | [5 empty] | 17SP | [6 empty] | 0.89898 | 0.84172 | 0.96362 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20312317SP |  |  | NORTONVILLE 69KV | EXP | WERE |  | NEAST |  |  | 533481 | NORTONV2 69.000 | [5 empty] | 17SP | [6 empty] | 0.90941 | 0.85293 | 0.9733 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19902317SP |  |  | JARBALO JUNCTION SWITCHING STATION 115KV | EXP | WERE |  | NEAST |  |  | 533244 | JARBALO3 115.00 | [5 empty] | 17SP | [6 empty] | 0.90942 | 0.86106 | 0.99222 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19772317SP |  |  | TONGA TAP 115KV | EXP | WERE |  | NEAST |  |  | 533219 | TONGATP3 115.00 | [5 empty] | 17SP | [6 empty] | 0.91322 | 0.86721 | 0.98979 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20332317SP |  |  | VALLEY FALLS 69KV | EXP | WERE |  | NEAST |  |  | 533483 | VALLEY22 69.000 | [5 empty] | 17SP | [6 empty] | 0.92127 | 0.87091 | 0.9784 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20332317SP |  |  | VALLEY FALLS 69KV | EXP | WERE |  | NEAST |  |  | 533483 | VALLEY22 69.000 | [5 empty] | 17SP | [6 empty] | 0.92127 | 0.87091 | 0.9784 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20332317SP |  |  | VALLEY FALLS 69KV | EXP | WERE |  | NEAST |  |  | 533483 | VALLEY22 69.000 | [5 empty] | 17SP | [6 empty] | 0.92127 | 0.87091 | 0.9784 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20332317SP |  |  | VALLEY FALLS 69KV | EXP | WERE |  | NEAST |  |  | 533483 | VALLEY22 69.000 | [5 empty] | 17SP | [6 empty] | 0.92127 | 0.87091 | 0.9784 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19802317SP |  |  | 166TH STREET 115KV | EXP | WERE |  | NEAST |  |  | 533233 | 166TH 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.91737 | 0.87214 | 0.9833 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20162317SP |  |  | 95TH & WAVERLY 115KV | EXP | WERE |  | NEAST |  |  | 533278 | WAVERLY3 115.00 | [5 empty] | 17SP | [6 empty] | 0.92146 | 0.8812 | 0.9649 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19892317SP |  |  | JAGGARD JUNCTION 115KV | EXP | WERE |  | NEAST |  |  | 533243 | JAGGARD3 115.00 | [5 empty] | 17SP | [6 empty] | 0.92496 | 0.88205 | 0.98018 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19852317SP |  |  | EAST S.A.A.P. JCT 115KV | EXP | WERE |  | NEAST |  |  | 533239 | ESAAPJ 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.92259 | 0.88235 | 0.96473 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19982317SP |  |  | MOONLIGHT 115KV | EXP | WERE |  | NEAST |  |  | 533254 | MOONLIT3 115.00 | [5 empty] | 17SP | [6 empty] | 0.92549 | 0.8854 | 0.96299 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19862317SP |  |  | EUDORA TOWNSHIP 115KV | EXP | WERE |  | NEAST |  |  | 533240 | EUDORA 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.92596 | 0.8862 | 0.97507 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19822317SP |  |  | CAPTAIN JUNCTION 115KV | EXP | WERE |  | NEAST |  |  | 533235 | CAPTAIN3 115.00 | [5 empty] | 17SP | [6 empty] | 0.92655 | 0.88679 | 0.97404 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19992317SP |  |  | MOONLIGHT JUNCTION SWITCHING STATION 115KV | EXP | WERE |  | NEAST |  |  | 533255 | MOONLTJ3 115.00 | [5 empty] | 17SP | [6 empty] | 0.92703 | 0.88701 | 0.96446 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20152317SP |  |  | WAKARUSA JUNCTION SWITCHING STATION 115KV | EXP | WERE |  | NEAST |  |  | 533277 | WAKARUS3 115.00 | [5 empty] | 17SP | [6 empty] | 0.92701 | 0.88747 | 0.97826 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19832317SP |  |  | FARMERS CONSUMER CO-OP 115KV | EXP | WERE |  | NEAST |  |  | 533236 | COOP 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.92839 | 0.88894 | 0.98071 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20002317SP |  |  | 19TH STREET 115KV | EXP | WERE |  | NEAST |  |  | 533256 | 19THST 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.92898 | 0.88985 | 0.98089 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19912317SP |  |  | KU CAMPUS 115KV | EXP | WERE |  | NEAST |  |  | 533245 | KU CAMP3 115.00 | [5 empty] | 17SP | [6 empty] | 0.92971 | 0.89067 | 0.9815 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20012317SP |  |  | 19TH STREET JUNCTION 115KV | EXP | WERE |  | NEAST |  |  | 533257 | 19THSTJ3 115.00 | [5 empty] | 17SP | [6 empty] | 0.93039 | 0.89144 | 0.98208 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20142317SP |  |  | TIMBERLANE 115KV | EXP | WERE |  | NEAST |  |  | 533273 | TIMBRLN3 115.00 | [5 empty] | 17SP | [6 empty] | 0.93207 | 0.89231 | 0.96803 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20122317SP |  |  | SOUTHWEST LAWRENCE 115KV | EXP | WERE |  | NEAST |  |  | 533271 | SWLWRNC3 115.00 | [5 empty] | 17SP | [6 empty] | 0.93261 | 0.89392 | 0.98397 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19812317SP |  |  | BISMARK JUNCTION SWITCHING STATION 115KV | EXP | WERE |  | NEAST |  |  | 533234 | BISMARK3 115.00 | [5 empty] | 17SP | [6 empty] | 0.93358 | 0.89408 | 0.9878 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20062317SP |  |  | SOUTHTOWN 115KV | EXP | WERE |  | NEAST |  |  | 533265 | SOUTHTN3 115.00 | [5 empty] | 17SP | [6 empty] | 0.93342 | 0.89464 | 0.96492 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19872317SP |  |  | FMC 115KV | EXP | WERE |  | NEAST |  |  | 533241 | FMC 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.93457 | 0.89508 | 0.98908 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20182317SP |  |  | MONTICELLO 115KV | EXP | WERE |  | NEAST |  |  | 533281 | MNTCLLO3 115.00 | [5 empty] | 17SP | [6 empty] | 0.93641 | 0.89658 | 0.97665 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20052317SP |  |  | 6TH STREET 115KV | EXP | WERE |  | NEAST |  |  | 533264 | 6TH ST 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.9368 | 0.89738 | 0.99157 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19972317SP |  |  | MOCKINGBIRD HILL SWITCHING STATION 115KV | EXP | WERE |  | NEAST |  |  | 533253 | MOCKBRD3 115.00 | [5 empty] | 17SP | [6 empty] | 0.93653 | 0.89867 | 0.98682 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19962317SP |  |  | MIDLAND JUNCTION 115KV | EXP | WERE |  | NEAST |  |  | 533252 | MIDLAND3 115.00 | [5 empty] | 17SP | [6 empty] | 0.93851 | 0.89884 | 0.99504 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20042317SP |  |  | 160TH STREET 115KV | EXP | WERE |  | NEAST |  |  | 533262 | 160TH 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.93733 | 0.89942 | 0.96514 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20032317SP |  |  | PENTAGON 115KV | EXP | WERE |  | NEAST |  |  | 533261 | PENTAGN3 115.00 | [5 empty] | 17SP | [6 empty] | 0.93935 | 0.89955 | 0.98142 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19792317SP |  |  | BALDWIN CREEK 115KV | EXP | WERE |  | NEAST |  |  | 533232 | BALDCRK3 115.00 | [5 empty] | 17SP | [6 empty] | 0.93886 | 0.89988 | 0.99234 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20172317SP |  |  | WREN 115KV | EXP | WERE |  | NEAST |  |  | 533280 | WREN 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.9412 | 0.90193 | 0.99639 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20202317SP |  |  | ROCK CREEK 69KV | EXP | WERE |  | NEAST |  |  | 533458 | ROCKCRK2 69.000 | [5 empty] | 17SP | [6 empty] | 0.94658 | 0.90464 | 0.99031 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20202317SP |  |  | ROCK CREEK 69KV | EXP | WERE |  | NEAST |  |  | 533458 | ROCKCRK2 69.000 | [5 empty] | 17SP | [6 empty] | 0.94658 | 0.90464 | 0.99031 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20202317SP |  |  | ROCK CREEK 69KV | EXP | WERE |  | NEAST |  |  | 533458 | ROCKCRK2 69.000 | [5 empty] | 17SP | [6 empty] | 0.94658 | 0.90464 | 0.99031 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19932317SP |  |  | LAWRENCE ENERGY CENTER UNIT 3 115KV | EXP | WERE |  | NEAST |  |  | 533248 | LEC U3 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.94395 | 0.90474 | 0.99918 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19952317SP |  |  | LAWRENCE HILL 115KV | EXP | WERE |  | NEAST |  |  | 533250 | LWRNCHL3 115.00 | [5 empty] | 17SP | [6 empty] | 0.94447 | 0.90536 | 0.99949 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19942317SP |  |  | LAWRENCE ENERGY CENTER UNIT 4 115KV | EXP | WERE |  | NEAST |  |  | 533249 | LEC U4 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.94492 | 0.90561 | 1.00077 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19722317SP |  |  | MIDLAND JUNCTION 230KV | EXP | WERE |  | NEAST |  |  | 532855 | MIDLAND6 230.00 | [5 empty] | 17SP | [6 empty] | 0.94759 | 0.9123 | 0.99553 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20082317SP |  |  | NEW SPRING HILL 115KV | EXP | WERE |  | NEAST |  |  | 533267 | SPRINGH3 115.00 | [5 empty] | 17SP | [6 empty] | 0.94913 | 0.91334 | 0.96738 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19702317SP |  |  | LAWRENCE HILL 230KV | EXP | WERE |  | NEAST |  |  | 532853 | LAWHILL6 230.00 | [5 empty] | 17SP | [6 empty] | 0.95061 | 0.916 | 0.99682 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19712317SP |  |  | LAWRENCE ENERGY CENTER UNIT 5 230KV | EXP | WERE |  | NEAST |  |  | 532854 | LEC U5 6 230.00 | [5 empty] | 17SP | [6 empty] | 0.95128 | 0.91668 | 0.99747 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20192317SP |  |  | MUND 115KV | EXP | WERE |  | NEAST |  |  | 533282 | MUND 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.95473 | 0.91692 | 0.98963 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20102317SP |  |  | STULL (KAW VALLEY R.E.C.) 115KV | EXP | WERE |  | NEAST |  |  | 533269 | STULL 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.95807 | 0.926 | 0.99486 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20112317SP |  |  | STULL SWITCHING STATION 115KV | EXP | WERE |  | NEAST |  |  | 533270 | STULL T3 115.00 | [5 empty] | 17SP | [6 empty] | 0.95809 | 0.92601 | 0.99488 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16072317SP |  |  | MOONLIGHT 115KV | EXP | WERE |  | NEAST |  |  | 533254 | MOONLIT3 115.00 | [5 empty] | 17SP | [6 empty] | 0.96004 | 0.92758 | 0.96299 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16102317SP |  |  | 160TH STREET 115KV | EXP | WERE |  | NEAST |  |  | 533262 | 160TH 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.96196 | 0.92825 | 0.96514 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16112317SP |  |  | SOUTHTOWN 115KV | EXP | WERE |  | NEAST |  |  | 533265 | SOUTHTN3 115.00 | [5 empty] | 17SP | [6 empty] | 0.96186 | 0.92856 | 0.96492 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16082317SP |  |  | MOONLIGHT JUNCTION SWITCHING STATION 115KV | EXP | WERE |  | NEAST |  |  | 533255 | MOONLTJ3 115.00 | [5 empty] | 17SP | [6 empty] | 0.96152 | 0.92912 | 0.96446 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16122317SP |  |  | NEW SPRING HILL 115KV | EXP | WERE |  | NEAST |  |  | 533267 | SPRINGH3 115.00 | [5 empty] | 17SP | [6 empty] | 0.96381 | 0.92916 | 0.96738 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16042317SP |  |  | EAST S.A.A.P. JCT 115KV | EXP | WERE |  | NEAST |  |  | 533239 | ESAAPJ 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.9618 | 0.93079 | 0.96473 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16152317SP |  |  | 95TH & WAVERLY 115KV | EXP | WERE |  | NEAST |  |  | 533278 | WAVERLY3 115.00 | [5 empty] | 17SP | [6 empty] | 0.96198 | 0.93139 | 0.9649 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12132317SP |  |  | 95TH & WAVERLY 115KV | EXP | WERE |  | NEAST |  |  | 533278 | WAVERLY3 115.00 | [5 empty] | 17SP | [6 empty] | 0.96043 | 0.93429 | 0.9649 | 0.95 | 1.05 | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12012317SP |  |  | EAST S.A.A.P. JCT 115KV | EXP | WERE |  | NEAST |  |  | 533239 | ESAAPJ 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.96088 | 0.93463 | 0.96473 | 0.95 | 1.05 | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19842317SP |  |  | EDWARDSVILLE 115KV | EXP | WERE |  | NEAST |  |  | 533238 | EDWARVL3 115.00 | [5 empty] | 17SP | [6 empty] | 0.97579 | 0.94044 | 1.00191 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V11992317SP |  |  | CAPTAIN JUNCTION 115KV | EXP | WERE |  | NEAST |  |  | 533235 | CAPTAIN3 115.00 | [5 empty] | 17SP | [6 empty] | 0.96765 | 0.9423 | 0.97404 | 0.95 | 1.05 | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12022317SP |  |  | EUDORA TOWNSHIP 115KV | EXP | WERE |  | NEAST |  |  | 533240 | EUDORA 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.96762 | 0.94243 | 0.97507 | 0.95 | 1.05 | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16032317SP |  |  | CAPTAIN JUNCTION 115KV | EXP | WERE |  | NEAST |  |  | 533235 | CAPTAIN3 115.00 | [5 empty] | 17SP | [6 empty] | 0.97122 | 0.94246 | 0.97404 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16162317SP |  |  | MONTICELLO 115KV | EXP | WERE |  | NEAST |  |  | 533281 | MNTCLLO3 115.00 | [5 empty] | 17SP | [6 empty] | 0.97393 | 0.94312 | 0.97665 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16052317SP |  |  | EUDORA TOWNSHIP 115KV | EXP | WERE |  | NEAST |  |  | 533240 | EUDORA 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.97225 | 0.94417 | 0.97507 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12122317SP |  |  | WAKARUSA JUNCTION SWITCHING STATION 115KV | EXP | WERE |  | NEAST |  |  | 533277 | WAKARUS3 115.00 | [5 empty] | 17SP | [6 empty] | 0.96948 | 0.94469 | 0.97826 | 0.95 | 1.05 | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12002317SP |  |  | FARMERS CONSUMER CO-OP 115KV | EXP | WERE |  | NEAST |  |  | 533236 | COOP 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.97176 | 0.94719 | 0.98071 | 0.95 | 1.05 | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12062317SP |  |  | 19TH STREET 115KV | EXP | WERE |  | NEAST |  |  | 533256 | 19THST 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.97175 | 0.94734 | 0.98089 | 0.95 | 1.05 | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12032317SP |  |  | KU CAMPUS 115KV | EXP | WERE |  | NEAST |  |  | 533245 | KU CAMP3 115.00 | [5 empty] | 17SP | [6 empty] | 0.97232 | 0.94796 | 0.9815 | 0.95 | 1.05 | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16142317SP |  |  | WAKARUSA JUNCTION SWITCHING STATION 115KV | EXP | WERE |  | NEAST |  |  | 533277 | WAKARUS3 115.00 | [5 empty] | 17SP | [6 empty] | 0.97545 | 0.94847 | 0.97826 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12072317SP |  |  | 19TH STREET JUNCTION 115KV | EXP | WERE |  | NEAST |  |  | 533257 | 19THSTJ3 115.00 | [5 empty] | 17SP | [6 empty] | 0.97288 | 0.94856 | 0.98208 | 0.95 | 1.05 | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16092317SP |  |  | PENTAGON 115KV | EXP | WERE |  | NEAST |  |  | 533261 | PENTAGN3 115.00 | [5 empty] | 17SP | [6 empty] | 0.97888 | 0.9489 | 0.98142 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16062317SP |  |  | JAGGARD JUNCTION 115KV | EXP | WERE |  | NEAST |  |  | 533243 | JAGGARD3 115.00 | [5 empty] | 17SP | [6 empty] | 0.97764 | 0.94938 | 0.98018 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15032312SP |  |  | WATHENA 69KV | EXP | WERE |  | NEAST |  |  | 533485 | WATHENA2 69.000 | [5 empty] | 12SP | [6 empty] | 0.88434 | 0.8519 | 0.93789 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15032312SP |  |  | WATHENA 69KV | EXP | WERE |  | NEAST |  |  | 533485 | WATHENA2 69.000 | [5 empty] | 12SP | [6 empty] | 0.88434 | 0.8519 | 0.93789 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14922312SP |  |  | ATCHISON CASTINGS 69KV | EXP | WERE |  | NEAST |  |  | 533474 | ATCHCST2 69.000 | [5 empty] | 12SP | [6 empty] | 0.91812 | 0.88723 | 0.96955 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14952312SP |  |  | MIDWEST GRAIN 69KV | EXP | WERE |  | NEAST |  |  | 533477 | MW SOLV2 69.000 | [5 empty] | 12SP | [6 empty] | 0.92188 | 0.89112 | 0.97316 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14912312SP |  |  | ATCHISON JCT2 69KV | EXP | WERE |  | NEAST |  |  | 533473 | ATCH J22 69.000 | [5 empty] | 12SP | [6 empty] | 0.92258 | 0.89185 | 0.97382 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14902312SP |  |  | ATCHISON JCT1 69KV | EXP | WERE |  | NEAST |  |  | 533472 | ATCH J12 69.000 | [5 empty] | 12SP | [6 empty] | 0.92263 | 0.89189 | 0.97382 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14962312SP |  |  | MIDWEST GRAIN SOLVENTS JCT1 69KV | EXP | WERE |  | NEAST |  |  | 533478 | MWSOLJ12 69.000 | [5 empty] | 12SP | [6 empty] | 0.9227 | 0.89197 | 0.97389 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15022312SP |  |  | WALNUT STREET 69KV | EXP | WERE |  | NEAST |  |  | 533484 | WALNUT 2 69.000 | [5 empty] | 12SP | [6 empty] | 0.92429 | 0.89356 | 0.9754 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14942312SP |  |  | MAUR HILL 69KV | EXP | WERE |  | NEAST |  |  | 533476 | MAUR HL2 69.000 | [5 empty] | 12SP | [6 empty] | 0.92448 | 0.89385 | 0.97575 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14972312SP |  |  | MIDWEST GRAIN SOLVENTS JCT2 69KV | EXP | WERE |  | NEAST |  |  | 533479 | MWSOLJ22 69.000 | [5 empty] | 12SP | [6 empty] | 0.92519 | 0.89456 | 0.97609 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14932312SP |  |  | KEREFORD JUNCTION 69KV | EXP | WERE |  | NEAST |  |  | 533475 | KERFORD2 69.000 | [5 empty] | 12SP | [6 empty] | 0.92938 | 0.89897 | 0.98057 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14682312SP |  |  | WALNUT STREET 115KV | EXP | WERE |  | NEAST |  |  | 533220 | WALNUT 3 115.00 | [5 empty] | 12SP | [6 empty] | 0.92929 | 0.89956 | 0.97745 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14682312SP |  |  | WALNUT STREET 115KV | EXP | WERE |  | NEAST |  |  | 533220 | WALNUT 3 115.00 | [5 empty] | 12SP | [6 empty] | 0.92929 | 0.89956 | 0.97745 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14662312SP |  |  | PARALLEL 115KV | EXP | WERE |  | NEAST |  |  | 533218 | PARALEL3 115.00 | [5 empty] | 12SP | [6 empty] | 0.93108 | 0.90149 | 0.97901 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14892312SP |  |  | ARNOLD 69KV | EXP | WERE |  | NEAST |  |  | 533471 | ARNOLD 2 69.000 | [5 empty] | 12SP | [6 empty] | 0.93501 | 0.90478 | 0.98468 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14642312SP |  |  | ARNOLD 115KV | EXP | WERE |  | NEAST |  |  | 533211 | ARNOLD 3 115.00 | [5 empty] | 12SP | [6 empty] | 0.93571 | 0.9064 | 0.98329 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14652312SP |  |  | KEREFORD JUNCTION 115KV | EXP | WERE |  | NEAST |  |  | 533216 | KERFORD3 115.00 | [5 empty] | 12SP | [6 empty] | 0.93781 | 0.90868 | 0.98529 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14982312SP |  |  | MUSCOTAH 69KV | EXP | WERE |  | NEAST |  |  | 533480 | MUSCOTA2 69.000 | [5 empty] | 12SP | [6 empty] | 0.94761 | 0.91972 | 0.96454 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14982312SP |  |  | MUSCOTAH 69KV | EXP | WERE |  | NEAST |  |  | 533480 | MUSCOTA2 69.000 | [5 empty] | 12SP | [6 empty] | 0.94761 | 0.91972 | 0.96454 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14982312SP |  |  | MUSCOTAH 69KV | EXP | WERE |  | NEAST |  |  | 533480 | MUSCOTA2 69.000 | [5 empty] | 12SP | [6 empty] | 0.94761 | 0.91972 | 0.96454 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14982312SP |  |  | MUSCOTAH 69KV | EXP | WERE |  | NEAST |  |  | 533480 | MUSCOTA2 69.000 | [5 empty] | 12SP | [6 empty] | 0.94761 | 0.91972 | 0.96454 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14982312SP |  |  | MUSCOTAH 69KV | EXP | WERE |  | NEAST |  |  | 533480 | MUSCOTA2 69.000 | [5 empty] | 12SP | [6 empty] | 0.94761 | 0.91972 | 0.96454 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14822312SP |  |  | SPRUCE STREET 115KV | EXP | WERE |  | NEAST |  |  | 533266 | SPRUCE 3 115.00 | [5 empty] | 12SP | [6 empty] | 0.95018 | 0.9226 | 0.99588 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14852312SP |  |  | THORNTON STREET 115KV | EXP | WERE |  | NEAST |  |  | 533272 | THORNTN3 115.00 | [5 empty] | 12SP | [6 empty] | 0.9502 | 0.92269 | 0.99589 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14732312SP |  |  | HALLMARK 115KV | EXP | WERE |  | NEAST |  |  | 533242 | HALLMRK3 115.00 | [5 empty] | 12SP | [6 empty] | 0.9509 | 0.92353 | 0.99437 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14792312SP |  |  | NORTHWEST LEAVENWORTH 115KV | EXP | WERE |  | NEAST |  |  | 533259 | NW LEAV3 115.00 | [5 empty] | 12SP | [6 empty] | 0.9535 | 0.92568 | 0.9993 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14762312SP |  |  | LANSING3 115.00 115KV | EXP | WERE |  | NEAST |  |  | 533246 | LANSING3 115.00 | [5 empty] | 12SP | [6 empty] | 0.9552 | 0.92818 | 0.99696 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14992312SP |  |  | NORTONVILLE 69KV | EXP | WERE |  | NEAST |  |  | 533481 | NORTONV2 69.000 | [5 empty] | 12SP | [6 empty] | 0.95609 | 0.92849 | 0.97286 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14842312SP |  |  | STRANGER CREEK 115KV | EXP | WERE |  | NEAST |  |  | 533268 | STRANGR3 115.00 | [5 empty] | 12SP | [6 empty] | 0.95608 | 0.92894 | 1.003 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15012312SP |  |  | VALLEY FALLS 69KV | EXP | WERE |  | NEAST |  |  | 533483 | VALLEY22 69.000 | [5 empty] | 12SP | [6 empty] | 0.96124 | 0.93669 | 0.97769 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15012312SP |  |  | VALLEY FALLS 69KV | EXP | WERE |  | NEAST |  |  | 533483 | VALLEY22 69.000 | [5 empty] | 12SP | [6 empty] | 0.96124 | 0.93669 | 0.97769 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14772312SP |  |  | MOONLIGHT 115KV | EXP | WERE |  | NEAST |  |  | 533254 | MOONLIT3 115.00 | [5 empty] | 12SP | [6 empty] | 0.96432 | 0.93941 | 0.97251 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14882312SP |  |  | 95TH & WAVERLY 115KV | EXP | WERE |  | NEAST |  |  | 533278 | WAVERLY3 115.00 | [5 empty] | 12SP | [6 empty] | 0.96371 | 0.93974 | 0.97737 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12812312SP |  |  | NEW SPRING HILL 115KV | EXP | WERE |  | NEAST |  |  | 533267 | SPRINGH3 115.00 | [5 empty] | 12SP | [6 empty] | 0.96726 | 0.93985 | 0.97259 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14712312SP |  |  | EAST S.A.A.P. JCT 115KV | EXP | WERE |  | NEAST |  |  | 533239 | ESAAPJ 3 115.00 | [5 empty] | 12SP | [6 empty] | 0.96413 | 0.93994 | 0.9766 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14782312SP |  |  | MOONLIGHT JUNCTION SWITCHING STATION 115KV | EXP | WERE |  | NEAST |  |  | 533255 | MOONLTJ3 115.00 | [5 empty] | 12SP | [6 empty] | 0.96582 | 0.94095 | 0.974 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12792312SP |  |  | 160TH STREET 115KV | EXP | WERE |  | NEAST |  |  | 533262 | 160TH 3 115.00 | [5 empty] | 12SP | [6 empty] | 0.96832 | 0.94254 | 0.97259 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14752312SP |  |  | JARBALO JUNCTION SWITCHING STATION 115KV | EXP | WERE |  | NEAST |  |  | 533244 | JARBALO3 115.00 | [5 empty] | 12SP | [6 empty] | 0.96888 | 0.94286 | 1.00546 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14812312SP |  |  | SOUTHTOWN 115KV | EXP | WERE |  | NEAST |  |  | 533265 | SOUTHTN3 115.00 | [5 empty] | 12SP | [6 empty] | 0.96862 | 0.94344 | 0.97319 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14672312SP |  |  | TONGA TAP 115KV | EXP | WERE |  | NEAST |  |  | 533219 | TONGATP3 115.00 | [5 empty] | 12SP | [6 empty] | 0.96875 | 0.94382 | 1.00336 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V9402312SP |  |  | NEW SPRING HILL 115KV | EXP | WERE |  | NEAST |  |  | 533267 | SPRINGH3 115.00 | [5 empty] | 12SP | [6 empty] | 0.9711 | 0.94404 | 0.97259 | 0.95 | 1.05 | CATEGORYB | SINGLE | CRAIG - STRANGER CREEK 345KV CKT 1 | 0 | 532772 | STRANGR7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14692312SP |  |  | 166TH STREET 115KV | EXP | WERE |  | NEAST |  |  | 533233 | 166TH 3 115.00 | [5 empty] | 12SP | [6 empty] | 0.96984 | 0.94475 | 0.99465 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14862312SP |  |  | TIMBERLANE 115KV | EXP | WERE |  | NEAST |  |  | 533273 | TIMBRLN3 115.00 | [5 empty] | 12SP | [6 empty] | 0.96996 | 0.94501 | 0.9769 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12772312SP |  |  | MOONLIGHT 115KV | EXP | WERE |  | NEAST |  |  | 533254 | MOONLIT3 115.00 | [5 empty] | 12SP | [6 empty] | 0.96914 | 0.94523 | 0.97251 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14702312SP |  |  | CAPTAIN JUNCTION 115KV | EXP | WERE |  | NEAST |  |  | 533235 | CAPTAIN3 115.00 | [5 empty] | 12SP | [6 empty] | 0.96972 | 0.94673 | 0.98736 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12782312SP |  |  | MOONLIGHT JUNCTION SWITCHING STATION 115KV | EXP | WERE |  | NEAST |  |  | 533255 | MOONLTJ3 115.00 | [5 empty] | 12SP | [6 empty] | 0.97063 | 0.94676 | 0.974 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14722312SP |  |  | EUDORA TOWNSHIP 115KV | EXP | WERE |  | NEAST |  |  | 533240 | EUDORA 3 115.00 | [5 empty] | 12SP | [6 empty] | 0.96977 | 0.94707 | 0.98899 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14742312SP |  |  | JAGGARD JUNCTION 115KV | EXP | WERE |  | NEAST |  |  | 533243 | JAGGARD3 115.00 | [5 empty] | 12SP | [6 empty] | 0.97213 | 0.94777 | 0.9898 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14872312SP |  |  | WAKARUSA JUNCTION SWITCHING STATION 115KV | EXP | WERE |  | NEAST |  |  | 533277 | WAKARUS3 115.00 | [5 empty] | 12SP | [6 empty] | 0.97129 | 0.94909 | 0.99267 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12822312SP |  |  | TIMBERLANE 115KV | EXP | WERE |  | NEAST |  |  | 533273 | TIMBRLN3 115.00 | [5 empty] | 12SP | [6 empty] | 0.97358 | 0.9495 | 0.9769 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V9372312SP |  |  | MOONLIGHT 115KV | EXP | WERE |  | NEAST |  |  | 533254 | MOONLIT3 115.00 | [5 empty] | 12SP | [6 empty] | 0.97338 | 0.94972 | 0.97251 | 0.95 | 1.05 | CATEGORYB | SINGLE | CRAIG - STRANGER CREEK 345KV CKT 1 | 0 | 532772 | STRANGR7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20352317SP |  |  | WATHENA 69KV | EXP | WERE |  | NEAST |  |  | 533485 | WATHENA2 69.000 | [5 empty] | 17SP | [6 empty] | 0.82937 | 0.76196 | 0.93811 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20352317SP |  |  | WATHENA 69KV | EXP | WERE |  | NEAST |  |  | 533485 | WATHENA2 69.000 | [5 empty] | 17SP | [6 empty] | 0.82937 | 0.76196 | 0.93811 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19782317SP |  |  | WALNUT STREET 115KV | EXP | WERE |  | NEAST |  |  | 533220 | WALNUT 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.84913 | 0.79126 | 0.94755 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19782317SP |  |  | WALNUT STREET 115KV | EXP | WERE |  | NEAST |  |  | 533220 | WALNUT 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.84913 | 0.79126 | 0.94755 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19762317SP |  |  | PARALLEL 115KV | EXP | WERE |  | NEAST |  |  | 533218 | PARALEL3 115.00 | [5 empty] | 17SP | [6 empty] | 0.85229 | 0.79471 | 0.9508 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19742317SP |  |  | ARNOLD 115KV | EXP | WERE |  | NEAST |  |  | 533211 | ARNOLD 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.8596 | 0.80265 | 0.95809 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19752317SP |  |  | KEREFORD JUNCTION 115KV | EXP | WERE |  | NEAST |  |  | 533216 | KERFORD3 115.00 | [5 empty] | 17SP | [6 empty] | 0.86208 | 0.80564 | 0.96045 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20242317SP |  |  | ATCHISON CASTINGS 69KV | EXP | WERE |  | NEAST |  |  | 533474 | ATCHCST2 69.000 | [5 empty] | 17SP | [6 empty] | 0.87015 | 0.80739 | 0.97491 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20272317SP |  |  | MIDWEST GRAIN 69KV | EXP | WERE |  | NEAST |  |  | 533477 | MW SOLV2 69.000 | [5 empty] | 17SP | [6 empty] | 0.87445 | 0.81196 | 0.97873 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20222317SP |  |  | ATCHISON JCT1 69KV | EXP | WERE |  | NEAST |  |  | 533472 | ATCH J12 69.000 | [5 empty] | 17SP | [6 empty] | 0.87491 | 0.81251 | 0.97915 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20282317SP |  |  | MIDWEST GRAIN SOLVENTS JCT1 69KV | EXP | WERE |  | NEAST |  |  | 533478 | MWSOLJ12 69.000 | [5 empty] | 17SP | [6 empty] | 0.875 | 0.81261 | 0.97924 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20232317SP |  |  | ATCHISON JCT2 69KV | EXP | WERE |  | NEAST |  |  | 533473 | ATCH J22 69.000 | [5 empty] | 17SP | [6 empty] | 0.87519 | 0.81276 | 0.97939 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20292317SP |  |  | MIDWEST GRAIN SOLVENTS JCT2 69KV | EXP | WERE |  | NEAST |  |  | 533479 | MWSOLJ22 69.000 | [5 empty] | 17SP | [6 empty] | 0.87717 | 0.81504 | 0.98109 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20342317SP |  |  | WALNUT STREET 69KV | EXP | WERE |  | NEAST |  |  | 533484 | WALNUT 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.87838 | 0.81579 | 0.98097 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20262317SP |  |  | MAUR HILL 69KV | EXP | WERE |  | NEAST |  |  | 533476 | MAUR HL2 69.000 | [5 empty] | 17SP | [6 empty] | 0.87802 | 0.81583 | 0.98258 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20252317SP |  |  | KEREFORD JUNCTION 69KV | EXP | WERE |  | NEAST |  |  | 533475 | KERFORD2 69.000 | [5 empty] | 17SP | [6 empty] | 0.88481 | 0.82317 | 0.98967 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20212317SP |  |  | ARNOLD 69KV | EXP | WERE |  | NEAST |  |  | 533471 | ARNOLD 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.88582 | 0.82474 | 0.98834 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20072317SP |  |  | SPRUCE STREET 115KV | EXP | WERE |  | NEAST |  |  | 533266 | SPRUCE 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.88194 | 0.82954 | 0.98008 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20132317SP |  |  | THORNTON STREET 115KV | EXP | WERE |  | NEAST |  |  | 533272 | THORNTN3 115.00 | [5 empty] | 17SP | [6 empty] | 0.8823 | 0.83007 | 0.98053 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20022317SP |  |  | NORTHWEST LEAVENWORTH 115KV | EXP | WERE |  | NEAST |  |  | 533259 | NW LEAV3 115.00 | [5 empty] | 17SP | [6 empty] | 0.88436 | 0.83137 | 0.98179 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19882317SP |  |  | HALLMARK 115KV | EXP | WERE |  | NEAST |  |  | 533242 | HALLMRK3 115.00 | [5 empty] | 17SP | [6 empty] | 0.88371 | 0.83186 | 0.97889 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19922317SP |  |  | LANSING3 115.00 115KV | EXP | WERE |  | NEAST |  |  | 533246 | LANSING3 115.00 | [5 empty] | 17SP | [6 empty] | 0.88996 | 0.839 | 0.98202 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20092317SP |  |  | STRANGER CREEK 115KV | EXP | WERE |  | NEAST |  |  | 533268 | STRANGR3 115.00 | [5 empty] | 17SP | [6 empty] | 0.89049 | 0.83918 | 0.99206 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20302317SP |  |  | MUSCOTAH 69KV | EXP | WERE |  | NEAST |  |  | 533480 | MUSCOTA2 69.000 | [5 empty] | 17SP | [6 empty] | 0.89898 | 0.84172 | 0.96362 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20302317SP |  |  | MUSCOTAH 69KV | EXP | WERE |  | NEAST |  |  | 533480 | MUSCOTA2 69.000 | [5 empty] | 17SP | [6 empty] | 0.89898 | 0.84172 | 0.96362 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20302317SP |  |  | MUSCOTAH 69KV | EXP | WERE |  | NEAST |  |  | 533480 | MUSCOTA2 69.000 | [5 empty] | 17SP | [6 empty] | 0.89898 | 0.84172 | 0.96362 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20302317SP |  |  | MUSCOTAH 69KV | EXP | WERE |  | NEAST |  |  | 533480 | MUSCOTA2 69.000 | [5 empty] | 17SP | [6 empty] | 0.89898 | 0.84172 | 0.96362 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20302317SP |  |  | MUSCOTAH 69KV | EXP | WERE |  | NEAST |  |  | 533480 | MUSCOTA2 69.000 | [5 empty] | 17SP | [6 empty] | 0.89898 | 0.84172 | 0.96362 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20312317SP |  |  | NORTONVILLE 69KV | EXP | WERE |  | NEAST |  |  | 533481 | NORTONV2 69.000 | [5 empty] | 17SP | [6 empty] | 0.90941 | 0.85293 | 0.9733 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19902317SP |  |  | JARBALO JUNCTION SWITCHING STATION 115KV | EXP | WERE |  | NEAST |  |  | 533244 | JARBALO3 115.00 | [5 empty] | 17SP | [6 empty] | 0.90942 | 0.86106 | 0.99222 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19772317SP |  |  | TONGA TAP 115KV | EXP | WERE |  | NEAST |  |  | 533219 | TONGATP3 115.00 | [5 empty] | 17SP | [6 empty] | 0.91322 | 0.86721 | 0.98979 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20332317SP |  |  | VALLEY FALLS 69KV | EXP | WERE |  | NEAST |  |  | 533483 | VALLEY22 69.000 | [5 empty] | 17SP | [6 empty] | 0.92127 | 0.87091 | 0.9784 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20332317SP |  |  | VALLEY FALLS 69KV | EXP | WERE |  | NEAST |  |  | 533483 | VALLEY22 69.000 | [5 empty] | 17SP | [6 empty] | 0.92127 | 0.87091 | 0.9784 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20332317SP |  |  | VALLEY FALLS 69KV | EXP | WERE |  | NEAST |  |  | 533483 | VALLEY22 69.000 | [5 empty] | 17SP | [6 empty] | 0.92127 | 0.87091 | 0.9784 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20332317SP |  |  | VALLEY FALLS 69KV | EXP | WERE |  | NEAST |  |  | 533483 | VALLEY22 69.000 | [5 empty] | 17SP | [6 empty] | 0.92127 | 0.87091 | 0.9784 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19802317SP |  |  | 166TH STREET 115KV | EXP | WERE |  | NEAST |  |  | 533233 | 166TH 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.91737 | 0.87214 | 0.9833 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20162317SP |  |  | 95TH & WAVERLY 115KV | EXP | WERE |  | NEAST |  |  | 533278 | WAVERLY3 115.00 | [5 empty] | 17SP | [6 empty] | 0.92146 | 0.8812 | 0.9649 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19892317SP |  |  | JAGGARD JUNCTION 115KV | EXP | WERE |  | NEAST |  |  | 533243 | JAGGARD3 115.00 | [5 empty] | 17SP | [6 empty] | 0.92496 | 0.88205 | 0.98018 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19852317SP |  |  | EAST S.A.A.P. JCT 115KV | EXP | WERE |  | NEAST |  |  | 533239 | ESAAPJ 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.92259 | 0.88235 | 0.96473 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19982317SP |  |  | MOONLIGHT 115KV | EXP | WERE |  | NEAST |  |  | 533254 | MOONLIT3 115.00 | [5 empty] | 17SP | [6 empty] | 0.92549 | 0.8854 | 0.96299 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19862317SP |  |  | EUDORA TOWNSHIP 115KV | EXP | WERE |  | NEAST |  |  | 533240 | EUDORA 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.92596 | 0.8862 | 0.97507 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19822317SP |  |  | CAPTAIN JUNCTION 115KV | EXP | WERE |  | NEAST |  |  | 533235 | CAPTAIN3 115.00 | [5 empty] | 17SP | [6 empty] | 0.92655 | 0.88679 | 0.97404 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19992317SP |  |  | MOONLIGHT JUNCTION SWITCHING STATION 115KV | EXP | WERE |  | NEAST |  |  | 533255 | MOONLTJ3 115.00 | [5 empty] | 17SP | [6 empty] | 0.92703 | 0.88701 | 0.96446 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20152317SP |  |  | WAKARUSA JUNCTION SWITCHING STATION 115KV | EXP | WERE |  | NEAST |  |  | 533277 | WAKARUS3 115.00 | [5 empty] | 17SP | [6 empty] | 0.92701 | 0.88747 | 0.97826 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19832317SP |  |  | FARMERS CONSUMER CO-OP 115KV | EXP | WERE |  | NEAST |  |  | 533236 | COOP 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.92839 | 0.88894 | 0.98071 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20002317SP |  |  | 19TH STREET 115KV | EXP | WERE |  | NEAST |  |  | 533256 | 19THST 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.92898 | 0.88985 | 0.98089 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19912317SP |  |  | KU CAMPUS 115KV | EXP | WERE |  | NEAST |  |  | 533245 | KU CAMP3 115.00 | [5 empty] | 17SP | [6 empty] | 0.92971 | 0.89067 | 0.9815 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20012317SP |  |  | 19TH STREET JUNCTION 115KV | EXP | WERE |  | NEAST |  |  | 533257 | 19THSTJ3 115.00 | [5 empty] | 17SP | [6 empty] | 0.93039 | 0.89144 | 0.98208 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20142317SP |  |  | TIMBERLANE 115KV | EXP | WERE |  | NEAST |  |  | 533273 | TIMBRLN3 115.00 | [5 empty] | 17SP | [6 empty] | 0.93207 | 0.89231 | 0.96803 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20122317SP |  |  | SOUTHWEST LAWRENCE 115KV | EXP | WERE |  | NEAST |  |  | 533271 | SWLWRNC3 115.00 | [5 empty] | 17SP | [6 empty] | 0.93261 | 0.89392 | 0.98397 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19812317SP |  |  | BISMARK JUNCTION SWITCHING STATION 115KV | EXP | WERE |  | NEAST |  |  | 533234 | BISMARK3 115.00 | [5 empty] | 17SP | [6 empty] | 0.93358 | 0.89408 | 0.9878 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20062317SP |  |  | SOUTHTOWN 115KV | EXP | WERE |  | NEAST |  |  | 533265 | SOUTHTN3 115.00 | [5 empty] | 17SP | [6 empty] | 0.93342 | 0.89464 | 0.96492 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19872317SP |  |  | FMC 115KV | EXP | WERE |  | NEAST |  |  | 533241 | FMC 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.93457 | 0.89508 | 0.98908 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20182317SP |  |  | MONTICELLO 115KV | EXP | WERE |  | NEAST |  |  | 533281 | MNTCLLO3 115.00 | [5 empty] | 17SP | [6 empty] | 0.93641 | 0.89658 | 0.97665 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20052317SP |  |  | 6TH STREET 115KV | EXP | WERE |  | NEAST |  |  | 533264 | 6TH ST 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.9368 | 0.89738 | 0.99157 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19972317SP |  |  | MOCKINGBIRD HILL SWITCHING STATION 115KV | EXP | WERE |  | NEAST |  |  | 533253 | MOCKBRD3 115.00 | [5 empty] | 17SP | [6 empty] | 0.93653 | 0.89867 | 0.98682 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19962317SP |  |  | MIDLAND JUNCTION 115KV | EXP | WERE |  | NEAST |  |  | 533252 | MIDLAND3 115.00 | [5 empty] | 17SP | [6 empty] | 0.93851 | 0.89884 | 0.99504 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20042317SP |  |  | 160TH STREET 115KV | EXP | WERE |  | NEAST |  |  | 533262 | 160TH 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.93733 | 0.89942 | 0.96514 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20032317SP |  |  | PENTAGON 115KV | EXP | WERE |  | NEAST |  |  | 533261 | PENTAGN3 115.00 | [5 empty] | 17SP | [6 empty] | 0.93935 | 0.89955 | 0.98142 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19792317SP |  |  | BALDWIN CREEK 115KV | EXP | WERE |  | NEAST |  |  | 533232 | BALDCRK3 115.00 | [5 empty] | 17SP | [6 empty] | 0.93886 | 0.89988 | 0.99234 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20172317SP |  |  | WREN 115KV | EXP | WERE |  | NEAST |  |  | 533280 | WREN 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.9412 | 0.90193 | 0.99639 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20202317SP |  |  | ROCK CREEK 69KV | EXP | WERE |  | NEAST |  |  | 533458 | ROCKCRK2 69.000 | [5 empty] | 17SP | [6 empty] | 0.94658 | 0.90464 | 0.99031 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20202317SP |  |  | ROCK CREEK 69KV | EXP | WERE |  | NEAST |  |  | 533458 | ROCKCRK2 69.000 | [5 empty] | 17SP | [6 empty] | 0.94658 | 0.90464 | 0.99031 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20202317SP |  |  | ROCK CREEK 69KV | EXP | WERE |  | NEAST |  |  | 533458 | ROCKCRK2 69.000 | [5 empty] | 17SP | [6 empty] | 0.94658 | 0.90464 | 0.99031 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19932317SP |  |  | LAWRENCE ENERGY CENTER UNIT 3 115KV | EXP | WERE |  | NEAST |  |  | 533248 | LEC U3 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.94395 | 0.90474 | 0.99918 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19952317SP |  |  | LAWRENCE HILL 115KV | EXP | WERE |  | NEAST |  |  | 533250 | LWRNCHL3 115.00 | [5 empty] | 17SP | [6 empty] | 0.94447 | 0.90536 | 0.99949 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19942317SP |  |  | LAWRENCE ENERGY CENTER UNIT 4 115KV | EXP | WERE |  | NEAST |  |  | 533249 | LEC U4 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.94492 | 0.90561 | 1.00077 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19722317SP |  |  | MIDLAND JUNCTION 230KV | EXP | WERE |  | NEAST |  |  | 532855 | MIDLAND6 230.00 | [5 empty] | 17SP | [6 empty] | 0.94759 | 0.9123 | 0.99553 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20082317SP |  |  | NEW SPRING HILL 115KV | EXP | WERE |  | NEAST |  |  | 533267 | SPRINGH3 115.00 | [5 empty] | 17SP | [6 empty] | 0.94913 | 0.91334 | 0.96738 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19702317SP |  |  | LAWRENCE HILL 230KV | EXP | WERE |  | NEAST |  |  | 532853 | LAWHILL6 230.00 | [5 empty] | 17SP | [6 empty] | 0.95061 | 0.916 | 0.99682 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19712317SP |  |  | LAWRENCE ENERGY CENTER UNIT 5 230KV | EXP | WERE |  | NEAST |  |  | 532854 | LEC U5 6 230.00 | [5 empty] | 17SP | [6 empty] | 0.95128 | 0.91668 | 0.99747 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20192317SP |  |  | MUND 115KV | EXP | WERE |  | NEAST |  |  | 533282 | MUND 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.95473 | 0.91692 | 0.98963 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20102317SP |  |  | STULL (KAW VALLEY R.E.C.) 115KV | EXP | WERE |  | NEAST |  |  | 533269 | STULL 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.95807 | 0.926 | 0.99486 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20112317SP |  |  | STULL SWITCHING STATION 115KV | EXP | WERE |  | NEAST |  |  | 533270 | STULL T3 115.00 | [5 empty] | 17SP | [6 empty] | 0.95809 | 0.92601 | 0.99488 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16072317SP |  |  | MOONLIGHT 115KV | EXP | WERE |  | NEAST |  |  | 533254 | MOONLIT3 115.00 | [5 empty] | 17SP | [6 empty] | 0.96004 | 0.92758 | 0.96299 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16102317SP |  |  | 160TH STREET 115KV | EXP | WERE |  | NEAST |  |  | 533262 | 160TH 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.96196 | 0.92825 | 0.96514 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16112317SP |  |  | SOUTHTOWN 115KV | EXP | WERE |  | NEAST |  |  | 533265 | SOUTHTN3 115.00 | [5 empty] | 17SP | [6 empty] | 0.96186 | 0.92856 | 0.96492 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16082317SP |  |  | MOONLIGHT JUNCTION SWITCHING STATION 115KV | EXP | WERE |  | NEAST |  |  | 533255 | MOONLTJ3 115.00 | [5 empty] | 17SP | [6 empty] | 0.96152 | 0.92912 | 0.96446 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16122317SP |  |  | NEW SPRING HILL 115KV | EXP | WERE |  | NEAST |  |  | 533267 | SPRINGH3 115.00 | [5 empty] | 17SP | [6 empty] | 0.96381 | 0.92916 | 0.96738 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16042317SP |  |  | EAST S.A.A.P. JCT 115KV | EXP | WERE |  | NEAST |  |  | 533239 | ESAAPJ 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.9618 | 0.93079 | 0.96473 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16152317SP |  |  | 95TH & WAVERLY 115KV | EXP | WERE |  | NEAST |  |  | 533278 | WAVERLY3 115.00 | [5 empty] | 17SP | [6 empty] | 0.96198 | 0.93139 | 0.9649 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12132317SP |  |  | 95TH & WAVERLY 115KV | EXP | WERE |  | NEAST |  |  | 533278 | WAVERLY3 115.00 | [5 empty] | 17SP | [6 empty] | 0.96043 | 0.93429 | 0.9649 | 0.95 | 1.05 | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12012317SP |  |  | EAST S.A.A.P. JCT 115KV | EXP | WERE |  | NEAST |  |  | 533239 | ESAAPJ 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.96088 | 0.93463 | 0.96473 | 0.95 | 1.05 | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19842317SP |  |  | EDWARDSVILLE 115KV | EXP | WERE |  | NEAST |  |  | 533238 | EDWARVL3 115.00 | [5 empty] | 17SP | [6 empty] | 0.97579 | 0.94044 | 1.00191 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V11992317SP |  |  | CAPTAIN JUNCTION 115KV | EXP | WERE |  | NEAST |  |  | 533235 | CAPTAIN3 115.00 | [5 empty] | 17SP | [6 empty] | 0.96765 | 0.9423 | 0.97404 | 0.95 | 1.05 | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12022317SP |  |  | EUDORA TOWNSHIP 115KV | EXP | WERE |  | NEAST |  |  | 533240 | EUDORA 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.96762 | 0.94243 | 0.97507 | 0.95 | 1.05 | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16032317SP |  |  | CAPTAIN JUNCTION 115KV | EXP | WERE |  | NEAST |  |  | 533235 | CAPTAIN3 115.00 | [5 empty] | 17SP | [6 empty] | 0.97122 | 0.94246 | 0.97404 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16162317SP |  |  | MONTICELLO 115KV | EXP | WERE |  | NEAST |  |  | 533281 | MNTCLLO3 115.00 | [5 empty] | 17SP | [6 empty] | 0.97393 | 0.94312 | 0.97665 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16052317SP |  |  | EUDORA TOWNSHIP 115KV | EXP | WERE |  | NEAST |  |  | 533240 | EUDORA 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.97225 | 0.94417 | 0.97507 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12122317SP |  |  | WAKARUSA JUNCTION SWITCHING STATION 115KV | EXP | WERE |  | NEAST |  |  | 533277 | WAKARUS3 115.00 | [5 empty] | 17SP | [6 empty] | 0.96948 | 0.94469 | 0.97826 | 0.95 | 1.05 | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12002317SP |  |  | FARMERS CONSUMER CO-OP 115KV | EXP | WERE |  | NEAST |  |  | 533236 | COOP 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.97176 | 0.94719 | 0.98071 | 0.95 | 1.05 | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12062317SP |  |  | 19TH STREET 115KV | EXP | WERE |  | NEAST |  |  | 533256 | 19THST 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.97175 | 0.94734 | 0.98089 | 0.95 | 1.05 | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12032317SP |  |  | KU CAMPUS 115KV | EXP | WERE |  | NEAST |  |  | 533245 | KU CAMP3 115.00 | [5 empty] | 17SP | [6 empty] | 0.97232 | 0.94796 | 0.9815 | 0.95 | 1.05 | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16142317SP |  |  | WAKARUSA JUNCTION SWITCHING STATION 115KV | EXP | WERE |  | NEAST |  |  | 533277 | WAKARUS3 115.00 | [5 empty] | 17SP | [6 empty] | 0.97545 | 0.94847 | 0.97826 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12072317SP |  |  | 19TH STREET JUNCTION 115KV | EXP | WERE |  | NEAST |  |  | 533257 | 19THSTJ3 115.00 | [5 empty] | 17SP | [6 empty] | 0.97288 | 0.94856 | 0.98208 | 0.95 | 1.05 | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16092317SP |  |  | PENTAGON 115KV | EXP | WERE |  | NEAST |  |  | 533261 | PENTAGN3 115.00 | [5 empty] | 17SP | [6 empty] | 0.97888 | 0.9489 | 0.98142 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16062317SP |  |  | JAGGARD JUNCTION 115KV | EXP | WERE |  | NEAST |  |  | 533243 | JAGGARD3 115.00 | [5 empty] | 17SP | [6 empty] | 0.97764 | 0.94938 | 0.98018 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | STRANGER CREEK TRANSFORMER CKT 2 | Install second Stranger Creek 345-115 transformer | 560 | 616 | 560 | 616 |  | 18 | 9 | Y | [29 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81V935517SP |  |  | SUB 424 - AEC REEDS SPRING 161KV | REL | EMDE |  | BRANSON |  |  | 547492 | RDS424 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.89516 | 0.87247 | 0.92162 | 0.92 | 1.05 | CATEGORYB | SINGLE | SUB 438 - RIVERSIDE - TABLE ROCK 161KV CKT 1 | 0 | 505472 | TABLE R5 161.00 | 547497 | RVS438 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 124 - AURORA H.T. 161KV | Install 3 - stages of 22 MVAR each for total of 66 MVAR capacitor bank at Aurora Sub #124 bus# 547537 | [5 empty] | 12 | 12 | [30 empty] | 2013-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81V875517SP |  |  | SUB 295 - REEDS SPRING 161KV | REL | EMDE |  | BRANSON |  |  | 547473 | RDS295 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.89884 | 0.87675 | 0.9226 | 0.92 | 1.05 | CATEGORYB | SINGLE | SUB 438 - RIVERSIDE - TABLE ROCK 161KV CKT 1 | 0 | 505472 | TABLE R5 161.00 | 547497 | RVS438 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 124 - AURORA H.T. 161KV | Install 3 - stages of 22 MVAR each for total of 66 MVAR capacitor bank at Aurora Sub #124 bus# 547537 | [5 empty] | 12 | 12 | [30 empty] | 2013-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V16072417SP |  |  | SUB 424 - AEC REEDS SPRING 161KV | REL | EMDE |  | BRANSON |  |  | 547492 | RDS424 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.91285 | 0.88095 | 0.91241 | 0.92 | 1.05 | CATEGORYB | SINGLE | SUB 412 - BRANSON NORTHWEST - SUB 424 - AEC REEDS SPRING 161KV CKT 1 | 0 | 547488 | BRN412 5 161.00 | 547492 | RDS424 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 124 - AURORA H.T. 161KV | Install 3 - stages of 22 MVAR each for total of 66 MVAR capacitor bank at Aurora Sub #124 bus# 547537 | [5 empty] | 12 | 12 | [30 empty] | 2013-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V16062417SP |  |  | SUB 295 - REEDS SPRING 161KV | REL | EMDE |  | BRANSON |  |  | 547473 | RDS295 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.9155 | 0.88472 | 0.91387 | 0.92 | 1.05 | CATEGORYB | SINGLE | SUB 412 - BRANSON NORTHWEST - SUB 424 - AEC REEDS SPRING 161KV CKT 1 | 0 | 547488 | BRN412 5 161.00 | 547492 | RDS424 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 124 - AURORA H.T. 161KV | Install 3 - stages of 22 MVAR each for total of 66 MVAR capacitor bank at Aurora Sub #124 bus# 547537 | [5 empty] | 12 | 12 | [30 empty] | 2013-06-01 | 2013-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V22212417SP |  |  | SUB 295 - REEDS SPRING 161KV | REL | EMDE |  | BRANSON |  |  | 547473 | RDS295 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.93539 | 0.88521 | 0.91387 | 0.92 | 1.05 | CATEGORYB | GENOUT | GEN549893 2-SOUTHWEST 2 | 0 | 506935 | FLINTCR7 345.00 | 547481 | MON383 7 345.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 124 - AURORA H.T. 161KV | Install 3 - stages of 22 MVAR each for total of 66 MVAR capacitor bank at Aurora Sub #124 bus# 547537 | [5 empty] | 12 | 12 | [30 empty] | 2013-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V14712217SP |  |  | SUB 124 - AURORA H.T. 161KV | REL | EMDE |  | AURORA |  |  | 547468 | AUR124 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.91339 | 0.88584 | 0.92839 | 0.92 | 1.05 | CATEGORYB | SINGLE | SUB 124 - AURORA H.T. - SUB 383 - MONETT 161KV CKT 1 | 0 | 547480 | MON383 5 161.00 | 547468 | AUR124 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 124 - AURORA H.T. 161KV | Install 3 - stages of 22 MVAR each for total of 66 MVAR capacitor bank at Aurora Sub #124 bus# 547537 | [5 empty] | 12 | 12 | [30 empty] | 2013-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V14762217SP |  |  | SUB 446 - CHESAPEAKE 161KV | REL | EMDE |  | AURORA |  |  | 547499 | CPK446 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.92109 | 0.89353 | 0.92737 | 0.92 | 1.05 | CATEGORYB | SINGLE | SUB 124 - AURORA H.T. - SUB 383 - MONETT 161KV CKT 1 | 0 | 547480 | MON383 5 161.00 | 547468 | AUR124 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 124 - AURORA H.T. 161KV | Install 3 - stages of 22 MVAR each for total of 66 MVAR capacitor bank at Aurora Sub #124 bus# 547537 | [5 empty] | 12 | 12 | [30 empty] | 2013-06-01 | 2013-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V22332417SP |  |  | SUB 446 - CHESAPEAKE 161KV | REL | EMDE |  | AURORA |  |  | 547499 | CPK446 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.94474 | 0.89642 | 0.92547 | 0.92 | 1.05 | CATEGORYB | GENOUT | GEN549893 2-SOUTHWEST 2 | 0 | 96101 | 5MORGAN 161.00 | 547478 | DAD368 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 124 - AURORA H.T. 161KV | Install 3 - stages of 22 MVAR each for total of 66 MVAR capacitor bank at Aurora Sub #124 bus# 547537 | [5 empty] | 12 | 12 | [30 empty] | 2013-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V22972417SP |  |  | SUB 73 - BOLIVAR BURNS 161KV | REL | EMDE |  | BOLIVAR |  |  | 547464 | BOL 73 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.92068 | 0.89735 | 0.96665 | 0.92 | 1.05 | CATEGORYB | SWSHUNT | SUB 73 - BOLIVAR BURNS 161KV SWITCHED SHUNT | 0 | 96101 | 5MORGAN 161.00 | 547478 | DAD368 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 124 - AURORA H.T. 161KV | Install 3 - stages of 22 MVAR each for total of 66 MVAR capacitor bank at Aurora Sub #124 bus# 547537 | [5 empty] | 12 | 12 | [30 empty] | 2013-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V20332417SP |  |  | SUB 446 - CHESAPEAKE 161KV | REL | EMDE |  | AURORA |  |  | 547499 | CPK446 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.92571 | 0.89758 | 0.92547 | 0.92 | 1.05 | CATEGORYB | SINGLE | MORGAN - SUB 368 - DADEVILLE EAST 161KV CKT 1 | 0 | 96101 | 5MORGAN 161.00 | 547478 | DAD368 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 124 - AURORA H.T. 161KV | Install 3 - stages of 22 MVAR each for total of 66 MVAR capacitor bank at Aurora Sub #124 bus# 547537 | [5 empty] | 12 | 12 | [30 empty] | 2013-06-01 | 2013-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V22202417SP |  |  | SUB 124 - AURORA H.T. 161KV | REL | EMDE |  | AURORA |  |  | 547468 | AUR124 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.94518 | 0.89977 | 0.92654 | 0.92 | 1.05 | CATEGORYB | GENOUT | GEN549893 2-SOUTHWEST 2 | 0 | 547480 | MON383 5 161.00 | 547468 | AUR124 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 124 - AURORA H.T. 161KV | Install 3 - stages of 22 MVAR each for total of 66 MVAR capacitor bank at Aurora Sub #124 bus# 547537 | [5 empty] | 12 | 12 | [30 empty] | 2013-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V20312417SP |  |  | SUB 368 - DADEVILLE EAST 161KV | REL | EMDE |  | BOLIVAR |  |  | 547478 | DAD368 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.93346 | 0.9011 | 0.94061 | 0.92 | 1.05 | CATEGORYB | SINGLE | MORGAN - SUB 368 - DADEVILLE EAST 161KV CKT 1 | 0 | 96101 | 5MORGAN 161.00 | 547478 | DAD368 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 124 - AURORA H.T. 161KV | Install 3 - stages of 22 MVAR each for total of 66 MVAR capacitor bank at Aurora Sub #124 bus# 547537 | [5 empty] | 12 | 12 | [30 empty] | 2013-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V22992417SP |  |  | SUB 431 - BOLIVAR SOUTH 161KV | REL | EMDE |  | BOLIVAR |  |  | 547493 | BOL431 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.92473 | 0.90162 | 0.95749 | 0.92 | 1.05 | CATEGORYB | SWSHUNT | SUB 73 - BOLIVAR BURNS 161KV SWITCHED SHUNT | 0 | 96101 | 5MORGAN 161.00 | 547478 | DAD368 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 124 - AURORA H.T. 161KV | Install 3 - stages of 22 MVAR each for total of 66 MVAR capacitor bank at Aurora Sub #124 bus# 547537 | [5 empty] | 12 | 12 | [30 empty] | 2013-06-01 | 2013-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V1222417SP |  |  | SUB 124 - AURORA H.T. 161KV | REL | EMDE |  | AURORA |  |  | 547468 | AUR124 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.93104 | 0.9039 | 0.92654 | 0.92 | 1.05 | CATEGORYB | SINGLE | FLINT CREEK - GRDA1 345KV CKT 1 | 0 | 512650 | GRDA1 7 345.00 | 506935 | FLINTCR7 345.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 124 - AURORA H.T. 161KV | Install 3 - stages of 22 MVAR each for total of 66 MVAR capacitor bank at Aurora Sub #124 bus# 547537 | [5 empty] | 12 | 12 | [30 empty] | 2013-06-01 | 2013-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V20422217SP |  |  | OZARKS 161KV | REL | EMDE |  | OZARK |  |  | 547621 | OZARKS 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.93377 | 0.90394 | 0.92896 | 0.92 | 1.05 | CATEGORYB | NONSINGLE | AI03 | 0 | 0 |  | 0 |  | 0 | [6 empty] | EMDE | SUB 124 - AURORA H.T. 161KV | Install 3 - stages of 22 MVAR each for total of 66 MVAR capacitor bank at Aurora Sub #124 bus# 547537 | [5 empty] | 12 | 12 | [30 empty] | 2013-06-01 | 2013-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V22242417SP |  |  | SUB 368 - DADEVILLE EAST 161KV | REL | EMDE |  | BOLIVAR |  |  | 547478 | DAD368 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.96 | 0.90585 | 0.94061 | 0.92 | 1.05 | CATEGORYB | GENOUT | GEN549893 2-SOUTHWEST 2 | 0 | 96101 | 5MORGAN 161.00 | 547478 | DAD368 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 124 - AURORA H.T. 161KV | Install 3 - stages of 22 MVAR each for total of 66 MVAR capacitor bank at Aurora Sub #124 bus# 547537 | [5 empty] | 12 | 12 | [30 empty] | 2013-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V21462417SP |  |  | SUB 368 - DADEVILLE EAST 161KV | REL | EMDE |  | BOLIVAR |  |  | 547478 | DAD368 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.94332 | 0.91135 | 0.94061 | 0.92 | 1.05 | CATEGORYB | NONSINGLE | SPP-SPRM-OP1 | 0 | 0 |  | 0 |  | 0 | [6 empty] | EMDE | SUB 124 - AURORA H.T. 161KV | Install 3 - stages of 22 MVAR each for total of 66 MVAR capacitor bank at Aurora Sub #124 bus# 547537 | [5 empty] | 12 | 12 | [30 empty] | 2013-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V20322417SP |  |  | SUB 431 - BOLIVAR SOUTH 161KV | REL | EMDE |  | BOLIVAR |  |  | 547493 | BOL431 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.94877 | 0.91197 | 0.95749 | 0.92 | 1.05 | CATEGORYB | SINGLE | MORGAN - SUB 368 - DADEVILLE EAST 161KV CKT 1 | 0 | 96101 | 5MORGAN 161.00 | 547478 | DAD368 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 124 - AURORA H.T. 161KV | Install 3 - stages of 22 MVAR each for total of 66 MVAR capacitor bank at Aurora Sub #124 bus# 547537 | [5 empty] | 12 | 12 | [30 empty] | 2013-06-01 | 2013-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V22302417SP |  |  | SUB 431 - BOLIVAR SOUTH 161KV | REL | EMDE |  | BOLIVAR |  |  | 547493 | BOL431 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.9792 | 0.91664 | 0.95749 | 0.92 | 1.05 | CATEGORYB | GENOUT | GEN549893 2-SOUTHWEST 2 | 0 | 96101 | 5MORGAN 161.00 | 547478 | DAD368 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 124 - AURORA H.T. 161KV | Install 3 - stages of 22 MVAR each for total of 66 MVAR capacitor bank at Aurora Sub #124 bus# 547537 | [5 empty] | 12 | 12 | [30 empty] | 2013-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V20292417SP |  |  | SUB 73 - BOLIVAR BURNS 161KV | REL | EMDE |  | BOLIVAR |  |  | 547464 | BOL 73 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.95685 | 0.91809 | 0.96665 | 0.92 | 1.05 | CATEGORYB | SINGLE | MORGAN - SUB 368 - DADEVILLE EAST 161KV CKT 1 | 0 | 96101 | 5MORGAN 161.00 | 547478 | DAD368 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 124 - AURORA H.T. 161KV | Install 3 - stages of 22 MVAR each for total of 66 MVAR capacitor bank at Aurora Sub #124 bus# 547537 | [5 empty] | 12 | 12 | [30 empty] | 2013-06-01 | 2013-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V20362417SP |  |  | SUB 390 - PURDY SOUTH 69KV | EXP | EMDE |  | AURORA |  |  | 547404 | PUR390 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.90353 | 0.86039 | 0.91539 | 0.9 | 1.05 | CATEGORYB | SINGLE | SUB 383 - MONETT (MONETT) 161/69/12.5KV TRANSFORMER CKT 1 | 1 | 547480 | MON383 5 161.00 | 547591 | MON383 2 69.000 | 547712 | MON383 1 12.500 | 1 |  |  |  |  | EMDE | SUB 383 - MONETT - SUB 376 - MONETT CITY SOUTH 161/69/12.5KV TRANSFORMER CKT 1 | Install new line from Sub #383 to new Sub MONETT 5. Install 3-wind transformer from 161 kV new bus to Monett city south 69kV | [12 empty] | 8000000 | 2016-06-01 | [23 empty] | 2015-06-01 | 2015-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V20352417SP |  |  | SUB 416 - MONETT CITY EAST 69KV | EXP | EMDE |  | AURORA |  |  | 547403 | MON416 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.93353 | 0.89446 | 0.94738 | 0.9 | 1.05 | CATEGORYB | SINGLE | SUB 383 - MONETT (MONETT) 161/69/12.5KV TRANSFORMER CKT 1 | 1 | 547480 | MON383 5 161.00 | 547591 | MON383 2 69.000 | 547712 | MON383 1 12.500 | 1 |  |  |  |  | EMDE | SUB 383 - MONETT - SUB 376 - MONETT CITY SOUTH 161/69/12.5KV TRANSFORMER CKT 1 | Install new line from Sub #383 to new Sub MONETT 5. Install 3-wind transformer from 161 kV new bus to Monett city south 69kV | [12 empty] | 8000000 | 2016-06-01 | [23 empty] | 2015-06-01 | 2015-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V20352417SP |  |  | SUB 416 - MONETT CITY EAST 69KV | EXP | EMDE |  | AURORA |  |  | 547403 | MON416 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.93353 | 0.89446 | 0.94738 | 0.9 | 1.05 | CATEGORYB | SINGLE | SUB 383 - MONETT (MONETT) 161/69/12.5KV TRANSFORMER CKT 1 | 1 | 547480 | MON383 5 161.00 | 547591 | MON383 2 69.000 | 547712 | MON383 1 12.500 | 1 |  |  |  |  | EMDE | SUB 383 - MONETT - SUB 376 - MONETT CITY SOUTH 161/69/12.5KV TRANSFORMER CKT 1 | Install new line from Sub #383 to new Sub MONETT 5. Install 3-wind transformer from 161 kV new bus to Monett city south 69kV | [12 empty] | 8000000 | 2016-06-01 | [23 empty] | 2015-06-01 | 2015-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V632212SP |  |  | SUB 413 - BRANSON SOUTHWEST 161KV | EXP | EMDE |  | BRANSON |  |  | 547489 | BRN413 5 161.00 | [5 empty] | 12SP | [6 empty] | 0.91631 | 0.8956 | 0.96024 | 0.92 | 1.05 | CATEGORYB | SINGLE | SUB 438 - RIVERSIDE - TABLE ROCK 161KV CKT 1 | 0 | 505472 | TABLE R5 161.00 | 547497 | RVS438 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V632212SP |  |  | SUB 413 - BRANSON SOUTHWEST 161KV | EXP | EMDE |  | BRANSON |  |  | 547489 | BRN413 5 161.00 | [5 empty] | 12SP | [6 empty] | 0.91631 | 0.8956 | 0.96024 | 0.92 | 1.05 | CATEGORYB | SINGLE | SUB 438 - RIVERSIDE - TABLE ROCK 161KV CKT 1 | 0 | 505472 | TABLE R5 161.00 | 547497 | RVS438 5 161.00 | 0 |  | 1 |  |  |  | Change settings on capacitor @ MONETT bus# 547591 - Adjust xfmr taps @ CPK 547478 (from .9 --> 1.00) | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V652212SP |  |  | SUB 433 - GRETNA 161KV | EXP | EMDE |  | BRANSON |  |  | 547495 | GRT433 5 161.00 | [5 empty] | 12SP | [6 empty] | 0.91672 | 0.89608 | 0.95809 | 0.92 | 1.05 | CATEGORYB | SINGLE | SUB 438 - RIVERSIDE - TABLE ROCK 161KV CKT 1 | 0 | 505472 | TABLE R5 161.00 | 547497 | RVS438 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V662212SP |  |  | SUB 438 - RIVERSIDE 161KV | EXP | EMDE |  | BRANSON |  |  | 547497 | RVS438 5 161.00 | [5 empty] | 12SP | [6 empty] | 0.91677 | 0.89609 | 0.96357 | 0.92 | 1.05 | CATEGORYB | SINGLE | SUB 438 - RIVERSIDE - TABLE ROCK 161KV CKT 1 | 0 | 505472 | TABLE R5 161.00 | 547497 | RVS438 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V662212SP |  |  | SUB 438 - RIVERSIDE 161KV | EXP | EMDE |  | BRANSON |  |  | 547497 | RVS438 5 161.00 | [5 empty] | 12SP | [6 empty] | 0.91677 | 0.89609 | 0.96357 | 0.92 | 1.05 | CATEGORYB | SINGLE | SUB 438 - RIVERSIDE - TABLE ROCK 161KV CKT 1 | 0 | 505472 | TABLE R5 161.00 | 547497 | RVS438 5 161.00 | 0 |  | 1 |  |  |  | Change settings on capacitor @ MONETT bus# 547591 - Adjust xfmr taps @ CPK 547478 (from .9 --> 1.00) | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V602212SP |  |  | SUB 331 - BRANSON NORTH 161KV | EXP | EMDE |  | BRANSON |  |  | 547475 | BRN331 5 161.00 | [5 empty] | 12SP | [6 empty] | 0.91756 | 0.89703 | 0.95638 | 0.92 | 1.05 | CATEGORYB | SINGLE | SUB 438 - RIVERSIDE - TABLE ROCK 161KV CKT 1 | 0 | 505472 | TABLE R5 161.00 | 547497 | RVS438 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V602212SP |  |  | SUB 331 - BRANSON NORTH 161KV | EXP | EMDE |  | BRANSON |  |  | 547475 | BRN331 5 161.00 | [5 empty] | 12SP | [6 empty] | 0.91756 | 0.89703 | 0.95638 | 0.92 | 1.05 | CATEGORYB | SINGLE | SUB 438 - RIVERSIDE - TABLE ROCK 161KV CKT 1 | 0 | 505472 | TABLE R5 161.00 | 547497 | RVS438 5 161.00 | 0 |  | 1 |  |  |  | Change settings on capacitor @ MONETT bus# 547591 - Adjust xfmr taps @ CPK 547478 (from .9 --> 1.00) | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V622212SP |  |  | SUB 412 - BRANSON NORTHWEST 161KV | EXP | EMDE |  | BRANSON |  |  | 547488 | BRN412 5 161.00 | [5 empty] | 12SP | [6 empty] | 0.91755 | 0.89704 | 0.95639 | 0.92 | 1.05 | CATEGORYB | SINGLE | SUB 438 - RIVERSIDE - TABLE ROCK 161KV CKT 1 | 0 | 505472 | TABLE R5 161.00 | 547497 | RVS438 5 161.00 | 0 |  | 1 |  |  |  | Change settings on capacitor @ MONETT bus# 547591 - Adjust xfmr taps @ CPK 547478 (from .9 --> 1.00) | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V622212SP |  |  | SUB 412 - BRANSON NORTHWEST 161KV | EXP | EMDE |  | BRANSON |  |  | 547488 | BRN412 5 161.00 | [5 empty] | 12SP | [6 empty] | 0.91755 | 0.89704 | 0.95639 | 0.92 | 1.05 | CATEGORYB | SINGLE | SUB 438 - RIVERSIDE - TABLE ROCK 161KV CKT 1 | 0 | 505472 | TABLE R5 161.00 | 547497 | RVS438 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V612212SP |  |  | SUB 387 - HOLLISTER EAST 161KV | EXP | EMDE |  | BRANSON |  |  | 547482 | HOL387 5 161.00 | [5 empty] | 12SP | [6 empty] | 0.9181 | 0.89754 | 0.961 | 0.92 | 1.05 | CATEGORYB | SINGLE | SUB 438 - RIVERSIDE - TABLE ROCK 161KV CKT 1 | 0 | 505472 | TABLE R5 161.00 | 547497 | RVS438 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V612212SP |  |  | SUB 387 - HOLLISTER EAST 161KV | EXP | EMDE |  | BRANSON |  |  | 547482 | HOL387 5 161.00 | [5 empty] | 12SP | [6 empty] | 0.9181 | 0.89754 | 0.961 | 0.92 | 1.05 | CATEGORYB | SINGLE | SUB 438 - RIVERSIDE - TABLE ROCK 161KV CKT 1 | 0 | 505472 | TABLE R5 161.00 | 547497 | RVS438 5 161.00 | 0 |  | 1 |  |  |  | Change settings on capacitor @ MONETT bus# 547591 - Adjust xfmr taps @ CPK 547478 (from .9 --> 1.00) | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V592212SP |  |  | SUB 312 - POWERSITE 161KV | EXP | EMDE |  | BRANSON |  |  | 547474 | OZD312 5 161.00 | [5 empty] | 12SP | [6 empty] | 0.92008 | 0.89975 | 0.95886 | 0.92 | 1.05 | CATEGORYB | SINGLE | SUB 438 - RIVERSIDE - TABLE ROCK 161KV CKT 1 | 0 | 505472 | TABLE R5 161.00 | 547497 | RVS438 5 161.00 | 0 |  | 1 |  |  |  | Change settings on capacitor @ MONETT bus# 547591 - Adjust xfmr taps @ CPK 547478 (from .9 --> 1.00) | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V592212SP |  |  | SUB 312 - POWERSITE 161KV | EXP | EMDE |  | BRANSON |  |  | 547474 | OZD312 5 161.00 | [5 empty] | 12SP | [6 empty] | 0.92008 | 0.89975 | 0.95886 | 0.92 | 1.05 | CATEGORYB | SINGLE | SUB 438 - RIVERSIDE - TABLE ROCK 161KV CKT 1 | 0 | 505472 | TABLE R5 161.00 | 547497 | RVS438 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81V925517SP |  |  | SUB 413 - BRANSON SOUTHWEST 161KV | EXP | EMDE |  | BRANSON |  |  | 547489 | BRN413 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.89101 | 0.8679 | 0.93296 | 0.92 | 1.05 | CATEGORYB | SINGLE | SUB 438 - RIVERSIDE - TABLE ROCK 161KV CKT 1 | 0 | 505472 | TABLE R5 161.00 | 547497 | RVS438 5 161.00 | 0 |  | 1 |  |  |  | Change settings on capacitor @ MONETT bus# 547591 - Adjust xfmr taps @ CPK 547478 (from .9 --> 1.00) | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81V925517SP |  |  | SUB 413 - BRANSON SOUTHWEST 161KV | EXP | EMDE |  | BRANSON |  |  | 547489 | BRN413 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.89101 | 0.8679 | 0.93296 | 0.92 | 1.05 | CATEGORYB | SINGLE | SUB 438 - RIVERSIDE - TABLE ROCK 161KV CKT 1 | 0 | 505472 | TABLE R5 161.00 | 547497 | RVS438 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81V945517SP |  |  | SUB 433 - GRETNA 161KV | EXP | EMDE |  | BRANSON |  |  | 547495 | GRT433 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.89136 | 0.86829 | 0.93058 | 0.92 | 1.05 | CATEGORYB | SINGLE | SUB 438 - RIVERSIDE - TABLE ROCK 161KV CKT 1 | 0 | 505472 | TABLE R5 161.00 | 547497 | RVS438 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81V955517SP |  |  | SUB 438 - RIVERSIDE 161KV | EXP | EMDE |  | BRANSON |  |  | 547497 | RVS438 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.89166 | 0.86862 | 0.93667 | 0.92 | 1.05 | CATEGORYB | SINGLE | SUB 438 - RIVERSIDE - TABLE ROCK 161KV CKT 1 | 0 | 505472 | TABLE R5 161.00 | 547497 | RVS438 5 161.00 | 0 |  | 1 |  |  |  | Change settings on capacitor @ MONETT bus# 547591 - Adjust xfmr taps @ CPK 547478 (from .9 --> 1.00) | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81V955517SP |  |  | SUB 438 - RIVERSIDE 161KV | EXP | EMDE |  | BRANSON |  |  | 547497 | RVS438 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.89166 | 0.86862 | 0.93667 | 0.92 | 1.05 | CATEGORYB | SINGLE | SUB 438 - RIVERSIDE - TABLE ROCK 161KV CKT 1 | 0 | 505472 | TABLE R5 161.00 | 547497 | RVS438 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81V915517SP |  |  | SUB 412 - BRANSON NORTHWEST 161KV | EXP | EMDE |  | BRANSON |  |  | 547488 | BRN412 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.8922 | 0.86923 | 0.92871 | 0.92 | 1.05 | CATEGORYB | SINGLE | SUB 438 - RIVERSIDE - TABLE ROCK 161KV CKT 1 | 0 | 505472 | TABLE R5 161.00 | 547497 | RVS438 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81V915517SP |  |  | SUB 412 - BRANSON NORTHWEST 161KV | EXP | EMDE |  | BRANSON |  |  | 547488 | BRN412 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.8922 | 0.86923 | 0.92871 | 0.92 | 1.05 | CATEGORYB | SINGLE | SUB 438 - RIVERSIDE - TABLE ROCK 161KV CKT 1 | 0 | 505472 | TABLE R5 161.00 | 547497 | RVS438 5 161.00 | 0 |  | 1 |  |  |  | Change settings on capacitor @ MONETT bus# 547591 - Adjust xfmr taps @ CPK 547478 (from .9 --> 1.00) | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81V895517SP |  |  | SUB 331 - BRANSON NORTH 161KV | EXP | EMDE |  | BRANSON |  |  | 547475 | BRN331 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.89235 | 0.8694 | 0.92884 | 0.92 | 1.05 | CATEGORYB | SINGLE | SUB 438 - RIVERSIDE - TABLE ROCK 161KV CKT 1 | 0 | 505472 | TABLE R5 161.00 | 547497 | RVS438 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81V895517SP |  |  | SUB 331 - BRANSON NORTH 161KV | EXP | EMDE |  | BRANSON |  |  | 547475 | BRN331 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.89235 | 0.8694 | 0.92884 | 0.92 | 1.05 | CATEGORYB | SINGLE | SUB 438 - RIVERSIDE - TABLE ROCK 161KV CKT 1 | 0 | 505472 | TABLE R5 161.00 | 547497 | RVS438 5 161.00 | 0 |  | 1 |  |  |  | Change settings on capacitor @ MONETT bus# 547591 - Adjust xfmr taps @ CPK 547478 (from .9 --> 1.00) | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81V905517SP |  |  | SUB 387 - HOLLISTER EAST 161KV | EXP | EMDE |  | BRANSON |  |  | 547482 | HOL387 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.89348 | 0.87066 | 0.93436 | 0.92 | 1.05 | CATEGORYB | SINGLE | SUB 438 - RIVERSIDE - TABLE ROCK 161KV CKT 1 | 0 | 505472 | TABLE R5 161.00 | 547497 | RVS438 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81V905517SP |  |  | SUB 387 - HOLLISTER EAST 161KV | EXP | EMDE |  | BRANSON |  |  | 547482 | HOL387 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.89348 | 0.87066 | 0.93436 | 0.92 | 1.05 | CATEGORYB | SINGLE | SUB 438 - RIVERSIDE - TABLE ROCK 161KV CKT 1 | 0 | 505472 | TABLE R5 161.00 | 547497 | RVS438 5 161.00 | 0 |  | 1 |  |  |  | Change settings on capacitor @ MONETT bus# 547591 - Adjust xfmr taps @ CPK 547478 (from .9 --> 1.00) | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81V935517SP |  |  | SUB 424 - AEC REEDS SPRING 161KV | EXP | EMDE |  | BRANSON |  |  | 547492 | RDS424 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.89516 | 0.87247 | 0.92162 | 0.92 | 1.05 | CATEGORYB | SINGLE | SUB 438 - RIVERSIDE - TABLE ROCK 161KV CKT 1 | 0 | 505472 | TABLE R5 161.00 | 547497 | RVS438 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81V935517SP |  |  | SUB 424 - AEC REEDS SPRING 161KV | EXP | EMDE |  | BRANSON |  |  | 547492 | RDS424 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.89516 | 0.87247 | 0.92162 | 0.92 | 1.05 | CATEGORYB | SINGLE | SUB 438 - RIVERSIDE - TABLE ROCK 161KV CKT 1 | 0 | 505472 | TABLE R5 161.00 | 547497 | RVS438 5 161.00 | 0 |  | 1 |  |  |  | Change settings on capacitor @ MONETT bus# 547591 - Adjust xfmr taps @ CPK 547478 (from .9 --> 1.00) | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81V885517SP |  |  | SUB 312 - POWERSITE 161KV | EXP | EMDE |  | BRANSON |  |  | 547474 | OZD312 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.89614 | 0.87365 | 0.93266 | 0.92 | 1.05 | CATEGORYB | SINGLE | SUB 438 - RIVERSIDE - TABLE ROCK 161KV CKT 1 | 0 | 505472 | TABLE R5 161.00 | 547497 | RVS438 5 161.00 | 0 |  | 1 |  |  |  | Change settings on capacitor @ MONETT bus# 547591 - Adjust xfmr taps @ CPK 547478 (from .9 --> 1.00) | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81V885517SP |  |  | SUB 312 - POWERSITE 161KV | EXP | EMDE |  | BRANSON |  |  | 547474 | OZD312 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.89614 | 0.87365 | 0.93266 | 0.92 | 1.05 | CATEGORYB | SINGLE | SUB 438 - RIVERSIDE - TABLE ROCK 161KV CKT 1 | 0 | 505472 | TABLE R5 161.00 | 547497 | RVS438 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81V875517SP |  |  | SUB 295 - REEDS SPRING 161KV | EXP | EMDE |  | BRANSON |  |  | 547473 | RDS295 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.89884 | 0.87675 | 0.9226 | 0.92 | 1.05 | CATEGORYB | SINGLE | SUB 438 - RIVERSIDE - TABLE ROCK 161KV CKT 1 | 0 | 505472 | TABLE R5 161.00 | 547497 | RVS438 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V16072417SP |  |  | SUB 424 - AEC REEDS SPRING 161KV | EXP | EMDE |  | BRANSON |  |  | 547492 | RDS424 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.91285 | 0.88095 | 0.91241 | 0.92 | 1.05 | CATEGORYB | SINGLE | SUB 412 - BRANSON NORTHWEST - SUB 424 - AEC REEDS SPRING 161KV CKT 1 | 0 | 547488 | BRN412 5 161.00 | 547492 | RDS424 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V16072417SP |  |  | SUB 424 - AEC REEDS SPRING 161KV | EXP | EMDE |  | BRANSON |  |  | 547492 | RDS424 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.91285 | 0.88095 | 0.91241 | 0.92 | 1.05 | CATEGORYB | SINGLE | SUB 412 - BRANSON NORTHWEST - SUB 424 - AEC REEDS SPRING 161KV CKT 1 | 0 | 547488 | BRN412 5 161.00 | 547492 | RDS424 5 161.00 | 0 |  | 1 |  |  |  | Change settings on capacitor @ MONETT bus# 547591 - Adjust xfmr taps @ CPK 547478 (from .9 --> 1.00) | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V16062417SP |  |  | SUB 295 - REEDS SPRING 161KV | EXP | EMDE |  | BRANSON |  |  | 547473 | RDS295 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.9155 | 0.88472 | 0.91387 | 0.92 | 1.05 | CATEGORYB | SINGLE | SUB 412 - BRANSON NORTHWEST - SUB 424 - AEC REEDS SPRING 161KV CKT 1 | 0 | 547488 | BRN412 5 161.00 | 547492 | RDS424 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V22212417SP |  |  | SUB 295 - REEDS SPRING 161KV | EXP | EMDE |  | BRANSON |  |  | 547473 | RDS295 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.93539 | 0.88521 | 0.91387 | 0.92 | 1.05 | CATEGORYB | GENOUT | GEN549893 2-SOUTHWEST 2 | 0 | 506935 | FLINTCR7 345.00 | 547481 | MON383 7 345.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V14712217SP |  |  | SUB 124 - AURORA H.T. 161KV | EXP | EMDE |  | AURORA |  |  | 547468 | AUR124 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.91339 | 0.88584 | 0.92839 | 0.92 | 1.05 | CATEGORYB | SINGLE | SUB 124 - AURORA H.T. - SUB 383 - MONETT 161KV CKT 1 | 0 | 547480 | MON383 5 161.00 | 547468 | AUR124 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V22232417SP |  |  | SUB 331 - BRANSON NORTH 161KV | EXP | EMDE |  | BRANSON |  |  | 547475 | BRN331 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.9402 | 0.88897 | 0.91893 | 0.92 | 1.05 | CATEGORYB | GENOUT | GEN549893 2-SOUTHWEST 2 | 0 | 506935 | FLINTCR7 345.00 | 547481 | MON383 7 345.00 | 0 |  | 1 |  |  |  | Change settings on capacitor @ MONETT bus# 547591 - Adjust xfmr taps @ CPK 547478 (from .9 --> 1.00) | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V22232417SP |  |  | SUB 331 - BRANSON NORTH 161KV | EXP | EMDE |  | BRANSON |  |  | 547475 | BRN331 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.9402 | 0.88897 | 0.91893 | 0.92 | 1.05 | CATEGORYB | GENOUT | GEN549893 2-SOUTHWEST 2 | 0 | 506935 | FLINTCR7 345.00 | 547481 | MON383 7 345.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V22272417SP |  |  | SUB 412 - BRANSON NORTHWEST 161KV | EXP | EMDE |  | BRANSON |  |  | 547488 | BRN412 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.94016 | 0.88903 | 0.9189 | 0.92 | 1.05 | CATEGORYB | GENOUT | GEN549893 2-SOUTHWEST 2 | 0 | 506935 | FLINTCR7 345.00 | 547481 | MON383 7 345.00 | 0 |  | 1 |  |  |  | Change settings on capacitor @ MONETT bus# 547591 - Adjust xfmr taps @ CPK 547478 (from .9 --> 1.00) | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V22272417SP |  |  | SUB 412 - BRANSON NORTHWEST 161KV | EXP | EMDE |  | BRANSON |  |  | 547488 | BRN412 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.94016 | 0.88903 | 0.9189 | 0.92 | 1.05 | CATEGORYB | GENOUT | GEN549893 2-SOUTHWEST 2 | 0 | 506935 | FLINTCR7 345.00 | 547481 | MON383 7 345.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V14762217SP |  |  | SUB 446 - CHESAPEAKE 161KV | EXP | EMDE |  | AURORA |  |  | 547499 | CPK446 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.92109 | 0.89353 | 0.92737 | 0.92 | 1.05 | CATEGORYB | SINGLE | SUB 124 - AURORA H.T. - SUB 383 - MONETT 161KV CKT 1 | 0 | 547480 | MON383 5 161.00 | 547468 | AUR124 5 161.00 | 0 |  | 1 |  |  |  | Change settings on capacitor @ MONETT bus# 547591 | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V22372417SP |  |  | NORTON 161KV | EXP | SPRM |  | SPRM |  |  | 549967 | NORTON 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.96482 | 0.89508 | 0.93972 | 0.9 | 1.1 | CATEGORYB | GENOUT | GEN549893 2-SOUTHWEST 2 | 0 | 549966 | SUMMIT 5 161.00 | 549967 | NORTON 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V22332417SP |  |  | SUB 446 - CHESAPEAKE 161KV | EXP | EMDE |  | AURORA |  |  | 547499 | CPK446 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.94474 | 0.89642 | 0.92547 | 0.92 | 1.05 | CATEGORYB | GENOUT | GEN549893 2-SOUTHWEST 2 | 0 | 96101 | 5MORGAN 161.00 | 547478 | DAD368 5 161.00 | 0 |  | 1 |  |  |  | Change settings on capacitor @ MONETT bus# 547591 | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V22972417SP |  |  | SUB 73 - BOLIVAR BURNS 161KV | EXP | EMDE |  | BOLIVAR |  |  | 547464 | BOL 73 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.92068 | 0.89735 | 0.96665 | 0.92 | 1.05 | CATEGORYB | SWSHUNT | SUB 73 - BOLIVAR BURNS 161KV SWITCHED SHUNT | 0 | 96101 | 5MORGAN 161.00 | 547478 | DAD368 5 161.00 | 0 |  | 1 |  |  |  | Change settings on capacitor @ MONETT bus# 547591 | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V20332417SP |  |  | SUB 446 - CHESAPEAKE 161KV | EXP | EMDE |  | AURORA |  |  | 547499 | CPK446 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.92571 | 0.89758 | 0.92547 | 0.92 | 1.05 | CATEGORYB | SINGLE | MORGAN - SUB 368 - DADEVILLE EAST 161KV CKT 1 | 0 | 96101 | 5MORGAN 161.00 | 547478 | DAD368 5 161.00 | 0 |  | 1 |  |  |  | Change settings on capacitor @ MONETT bus# 547591 | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V16142417SP |  |  | NORTON 161KV | EXP | SPRM |  | SPRM |  |  | 549967 | NORTON 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.93919 | 0.89939 | 0.93972 | 0.9 | 1.1 | CATEGORYB | SINGLE | NORTON - SUMMIT 161KV CKT 1 | 0 | 549966 | SUMMIT 5 161.00 | 549967 | NORTON 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V22202417SP |  |  | SUB 124 - AURORA H.T. 161KV | EXP | EMDE |  | AURORA |  |  | 547468 | AUR124 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.94518 | 0.89977 | 0.92654 | 0.92 | 1.05 | CATEGORYB | GENOUT | GEN549893 2-SOUTHWEST 2 | 0 | 547480 | MON383 5 161.00 | 547468 | AUR124 5 161.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V22992417SP |  |  | SUB 431 - BOLIVAR SOUTH 161KV | EXP | EMDE |  | BOLIVAR |  |  | 547493 | BOL431 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.92473 | 0.90162 | 0.95749 | 0.92 | 1.05 | CATEGORYB | SWSHUNT | SUB 73 - BOLIVAR BURNS 161KV SWITCHED SHUNT | 0 | 96101 | 5MORGAN 161.00 | 547478 | DAD368 5 161.00 | 0 |  | 1 |  |  |  | Change settings on capacitor @ MONETT bus# 547591 - Adjust xfmr taps @ CPK 547478 (from .9 --> 1.00) | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V1222417SP |  |  | SUB 124 - AURORA H.T. 161KV | EXP | EMDE |  | AURORA |  |  | 547468 | AUR124 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.93104 | 0.9039 | 0.92654 | 0.92 | 1.05 | CATEGORYB | SINGLE | FLINT CREEK - GRDA1 345KV CKT 1 | 0 | 512650 | GRDA1 7 345.00 | 506935 | FLINTCR7 345.00 | 0 |  | 1 |  |  |  |  | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V20422217SP |  |  | OZARKS 161KV | EXP | EMDE |  | OZARK |  |  | 547621 | OZARKS 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.93377 | 0.90394 | 0.92896 | 0.92 | 1.05 | CATEGORYB | NONSINGLE | AI03 | 0 | 0 |  | 0 |  | 0 | [6 empty] | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V20322417SP |  |  | SUB 431 - BOLIVAR SOUTH 161KV | EXP | EMDE |  | BOLIVAR |  |  | 547493 | BOL431 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.94877 | 0.91197 | 0.95749 | 0.92 | 1.05 | CATEGORYB | SINGLE | MORGAN - SUB 368 - DADEVILLE EAST 161KV CKT 1 | 0 | 96101 | 5MORGAN 161.00 | 547478 | DAD368 5 161.00 | 0 |  | 1 |  |  |  | Change settings on capacitor @ MONETT bus# 547591 - Adjust xfmr taps @ CPK 547478 (from .9 --> 1.00) | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V22252417SP |  |  | SUB 383 - MONETT 161KV | EXP | EMDE |  | AURORA |  |  | 547480 | MON383 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.96021 | 0.9164 | 0.94424 | 0.92 | 1.05 | CATEGORYB | GENOUT | GEN549893 2-SOUTHWEST 2 | 0 | 512650 | GRDA1 7 345.00 | 506935 | FLINTCR7 345.00 | 0 |  | 1 |  |  |  | Change settings on capacitor @ MONETT bus# 547591 - Turn on Binit at Aurora Sub# 124 bus# 547704 | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V22252417SP |  |  | SUB 383 - MONETT 161KV | EXP | EMDE |  | AURORA |  |  | 547480 | MON383 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.96021 | 0.9164 | 0.94424 | 0.92 | 1.05 | CATEGORYB | GENOUT | GEN549893 2-SOUTHWEST 2 | 0 | 512650 | GRDA1 7 345.00 | 506935 | FLINTCR7 345.00 | 0 |  | 1 |  |  |  | Change settings on capacitor @ MONETT bus# 547591 - Turn on Binit at Aurora Sub# 124 bus# 547704 | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V22302417SP |  |  | SUB 431 - BOLIVAR SOUTH 161KV | EXP | EMDE |  | BOLIVAR |  |  | 547493 | BOL431 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.9792 | 0.91664 | 0.95749 | 0.92 | 1.05 | CATEGORYB | GENOUT | GEN549893 2-SOUTHWEST 2 | 0 | 96101 | 5MORGAN 161.00 | 547478 | DAD368 5 161.00 | 0 |  | 1 |  |  |  | Change settings on capacitor @ MONETT bus# 547591 - Adjust xfmr taps @ CPK 547478 (from .9 --> 1.00) | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V16052417SP |  |  | SUB 383 - MONETT 161KV | EXP | EMDE |  | AURORA |  |  | 547480 | MON383 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.94385 | 0.91805 | 0.94424 | 0.92 | 1.05 | CATEGORYB | SINGLE | SUB 382 - LARUSSEL - SUB 383 - MONETT 161KV CKT 1 | 0 | 547479 | LAR382 5 161.00 | 547480 | MON383 5 161.00 | 0 |  | 1 |  |  |  | Change settings on capacitor @ MONETT bus# 547591 - Turn on Binit at Aurora Sub# 124 bus# 547704 | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V16052417SP |  |  | SUB 383 - MONETT 161KV | EXP | EMDE |  | AURORA |  |  | 547480 | MON383 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.94385 | 0.91805 | 0.94424 | 0.92 | 1.05 | CATEGORYB | SINGLE | SUB 382 - LARUSSEL - SUB 383 - MONETT 161KV CKT 1 | 0 | 547479 | LAR382 5 161.00 | 547480 | MON383 5 161.00 | 0 |  | 1 |  |  |  | Change settings on capacitor @ MONETT bus# 547591 - Turn on Binit at Aurora Sub# 124 bus# 547704 | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V20292417SP |  |  | SUB 73 - BOLIVAR BURNS 161KV | EXP | EMDE |  | BOLIVAR |  |  | 547464 | BOL 73 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.95685 | 0.91809 | 0.96665 | 0.92 | 1.05 | CATEGORYB | SINGLE | MORGAN - SUB 368 - DADEVILLE EAST 161KV CKT 1 | 0 | 96101 | 5MORGAN 161.00 | 547478 | DAD368 5 161.00 | 0 |  | 1 |  |  |  | Change settings on capacitor @ MONETT bus# 547591 | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V1272417SP |  |  | SUB 383 - MONETT 161KV | EXP | EMDE |  | AURORA |  |  | 547480 | MON383 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.94656 | 0.91935 | 0.94424 | 0.92 | 1.05 | CATEGORYB | SINGLE | FLINT CREEK - GRDA1 345KV CKT 1 | 0 | 512650 | GRDA1 7 345.00 | 506935 | FLINTCR7 345.00 | 0 |  | 1 |  |  |  | Change settings on capacitor @ MONETT bus# 547591 - Turn on Binit at Aurora Sub# 124 bus# 547704 | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V1272417SP |  |  | SUB 383 - MONETT 161KV | EXP | EMDE |  | AURORA |  |  | 547480 | MON383 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.94656 | 0.91935 | 0.94424 | 0.92 | 1.05 | CATEGORYB | SINGLE | FLINT CREEK - GRDA1 345KV CKT 1 | 0 | 512650 | GRDA1 7 345.00 | 506935 | FLINTCR7 345.00 | 0 |  | 1 |  |  |  | Change settings on capacitor @ MONETT bus# 547591 - Turn on Binit at Aurora Sub# 124 bus# 547704 | EMDE | SUB 438 - RIVERSIDE 161KV | Install 3 - stages of 22 MVAR each for a total of 66 MVAR capacitor bank at Riverside Sub #438 547497 | [5 empty] | 24 | 12 | [5 empty] | 2600000 | 2015-06-01 | [23 empty] | 2011-06-01 | 2011-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V22972417SP |  |  | SUB 73 - BOLIVAR BURNS 161KV | EXP | EMDE |  | BOLIVAR |  |  | 547464 | BOL 73 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.92068 | 0.89735 | 0.96665 | 0.92 | 1.05 | CATEGORYB | SWSHUNT | SUB 73 - BOLIVAR BURNS 161KV SWITCHED SHUNT | 0 | 96101 | 5MORGAN 161.00 | 547478 | DAD368 5 161.00 | 0 |  | 1 |  |  |  | Change settings on capacitor @ MONETT bus# 547591 | EMDE | SUB 73 - BOLIVAR BURNS 69KV | Add 14 MVAR cap bank at Bolivar Sub# 73 bus# 547528 | [12 empty] | 1500000 | 2007-01-01 | [23 empty] | 2015-06-01 | 2015-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V22992417SP |  |  | SUB 431 - BOLIVAR SOUTH 161KV | EXP | EMDE |  | BOLIVAR |  |  | 547493 | BOL431 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.92473 | 0.90162 | 0.95749 | 0.92 | 1.05 | CATEGORYB | SWSHUNT | SUB 73 - BOLIVAR BURNS 161KV SWITCHED SHUNT | 0 | 96101 | 5MORGAN 161.00 | 547478 | DAD368 5 161.00 | 0 |  | 1 |  |  |  | Change settings on capacitor @ MONETT bus# 547591 - Adjust xfmr taps @ CPK 547478 (from .9 --> 1.00) | EMDE | SUB 73 - BOLIVAR BURNS 69KV | Add 14 MVAR cap bank at Bolivar Sub# 73 bus# 547528 | [12 empty] | 1500000 | 2007-01-01 | [23 empty] | 2015-06-01 | 2015-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V20322417SP |  |  | SUB 431 - BOLIVAR SOUTH 161KV | EXP | EMDE |  | BOLIVAR |  |  | 547493 | BOL431 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.94877 | 0.91197 | 0.95749 | 0.92 | 1.05 | CATEGORYB | SINGLE | MORGAN - SUB 368 - DADEVILLE EAST 161KV CKT 1 | 0 | 96101 | 5MORGAN 161.00 | 547478 | DAD368 5 161.00 | 0 |  | 1 |  |  |  | Change settings on capacitor @ MONETT bus# 547591 - Adjust xfmr taps @ CPK 547478 (from .9 --> 1.00) | EMDE | SUB 73 - BOLIVAR BURNS 69KV | Add 14 MVAR cap bank at Bolivar Sub# 73 bus# 547528 | [12 empty] | 1500000 | 2007-01-01 | [23 empty] | 2015-06-01 | 2015-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V22302417SP |  |  | SUB 431 - BOLIVAR SOUTH 161KV | EXP | EMDE |  | BOLIVAR |  |  | 547493 | BOL431 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.9792 | 0.91664 | 0.95749 | 0.92 | 1.05 | CATEGORYB | GENOUT | GEN549893 2-SOUTHWEST 2 | 0 | 96101 | 5MORGAN 161.00 | 547478 | DAD368 5 161.00 | 0 |  | 1 |  |  |  | Change settings on capacitor @ MONETT bus# 547591 - Adjust xfmr taps @ CPK 547478 (from .9 --> 1.00) | EMDE | SUB 73 - BOLIVAR BURNS 69KV | Add 14 MVAR cap bank at Bolivar Sub# 73 bus# 547528 | [12 empty] | 1500000 | 2007-01-01 | [23 empty] | 2015-06-01 | 2015-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V20292417SP |  |  | SUB 73 - BOLIVAR BURNS 161KV | EXP | EMDE |  | BOLIVAR |  |  | 547464 | BOL 73 5 161.00 | [5 empty] | 17SP | [6 empty] | 0.95685 | 0.91809 | 0.96665 | 0.92 | 1.05 | CATEGORYB | SINGLE | MORGAN - SUB 368 - DADEVILLE EAST 161KV CKT 1 | 0 | 96101 | 5MORGAN 161.00 | 547478 | DAD368 5 161.00 | 0 |  | 1 |  |  |  | Change settings on capacitor @ MONETT bus# 547591 | EMDE | SUB 73 - BOLIVAR BURNS 69KV | Add 14 MVAR cap bank at Bolivar Sub# 73 bus# 547528 | [12 empty] | 1500000 | 2007-01-01 | [23 empty] | 2015-06-01 | 2015-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15032312SP |  |  | WATHENA 69KV | S | WERE |  | NEAST |  |  | 533485 | WATHENA2 69.000 | [5 empty] | 12SP | [6 empty] | 0.88434 | 0.8519 | 0.93789 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15032312SP |  |  | WATHENA 69KV | S | WERE |  | NEAST |  |  | 533485 | WATHENA2 69.000 | [5 empty] | 12SP | [6 empty] | 0.88434 | 0.8519 | 0.93789 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14922312SP |  |  | ATCHISON CASTINGS 69KV | S | WERE |  | NEAST |  |  | 533474 | ATCHCST2 69.000 | [5 empty] | 12SP | [6 empty] | 0.91812 | 0.88723 | 0.96955 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14952312SP |  |  | MIDWEST GRAIN 69KV | S | WERE |  | NEAST |  |  | 533477 | MW SOLV2 69.000 | [5 empty] | 12SP | [6 empty] | 0.92188 | 0.89112 | 0.97316 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14912312SP |  |  | ATCHISON JCT2 69KV | S | WERE |  | NEAST |  |  | 533473 | ATCH J22 69.000 | [5 empty] | 12SP | [6 empty] | 0.92258 | 0.89185 | 0.97382 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14902312SP |  |  | ATCHISON JCT1 69KV | S | WERE |  | NEAST |  |  | 533472 | ATCH J12 69.000 | [5 empty] | 12SP | [6 empty] | 0.92263 | 0.89189 | 0.97382 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14962312SP |  |  | MIDWEST GRAIN SOLVENTS JCT1 69KV | S | WERE |  | NEAST |  |  | 533478 | MWSOLJ12 69.000 | [5 empty] | 12SP | [6 empty] | 0.9227 | 0.89197 | 0.97389 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15022312SP |  |  | WALNUT STREET 69KV | S | WERE |  | NEAST |  |  | 533484 | WALNUT 2 69.000 | [5 empty] | 12SP | [6 empty] | 0.92429 | 0.89356 | 0.9754 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14942312SP |  |  | MAUR HILL 69KV | S | WERE |  | NEAST |  |  | 533476 | MAUR HL2 69.000 | [5 empty] | 12SP | [6 empty] | 0.92448 | 0.89385 | 0.97575 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14972312SP |  |  | MIDWEST GRAIN SOLVENTS JCT2 69KV | S | WERE |  | NEAST |  |  | 533479 | MWSOLJ22 69.000 | [5 empty] | 12SP | [6 empty] | 0.92519 | 0.89456 | 0.97609 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14932312SP |  |  | KEREFORD JUNCTION 69KV | S | WERE |  | NEAST |  |  | 533475 | KERFORD2 69.000 | [5 empty] | 12SP | [6 empty] | 0.92938 | 0.89897 | 0.98057 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14682312SP |  |  | WALNUT STREET 115KV | S | WERE |  | NEAST |  |  | 533220 | WALNUT 3 115.00 | [5 empty] | 12SP | [6 empty] | 0.92929 | 0.89956 | 0.97745 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14682312SP |  |  | WALNUT STREET 115KV | S | WERE |  | NEAST |  |  | 533220 | WALNUT 3 115.00 | [5 empty] | 12SP | [6 empty] | 0.92929 | 0.89956 | 0.97745 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14662312SP |  |  | PARALLEL 115KV | S | WERE |  | NEAST |  |  | 533218 | PARALEL3 115.00 | [5 empty] | 12SP | [6 empty] | 0.93108 | 0.90149 | 0.97901 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14892312SP |  |  | ARNOLD 69KV | S | WERE |  | NEAST |  |  | 533471 | ARNOLD 2 69.000 | [5 empty] | 12SP | [6 empty] | 0.93501 | 0.90478 | 0.98468 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14642312SP |  |  | ARNOLD 115KV | S | WERE |  | NEAST |  |  | 533211 | ARNOLD 3 115.00 | [5 empty] | 12SP | [6 empty] | 0.93571 | 0.9064 | 0.98329 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14652312SP |  |  | KEREFORD JUNCTION 115KV | S | WERE |  | NEAST |  |  | 533216 | KERFORD3 115.00 | [5 empty] | 12SP | [6 empty] | 0.93781 | 0.90868 | 0.98529 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14982312SP |  |  | MUSCOTAH 69KV | S | WERE |  | NEAST |  |  | 533480 | MUSCOTA2 69.000 | [5 empty] | 12SP | [6 empty] | 0.94761 | 0.91972 | 0.96454 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14982312SP |  |  | MUSCOTAH 69KV | S | WERE |  | NEAST |  |  | 533480 | MUSCOTA2 69.000 | [5 empty] | 12SP | [6 empty] | 0.94761 | 0.91972 | 0.96454 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14982312SP |  |  | MUSCOTAH 69KV | S | WERE |  | NEAST |  |  | 533480 | MUSCOTA2 69.000 | [5 empty] | 12SP | [6 empty] | 0.94761 | 0.91972 | 0.96454 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14982312SP |  |  | MUSCOTAH 69KV | S | WERE |  | NEAST |  |  | 533480 | MUSCOTA2 69.000 | [5 empty] | 12SP | [6 empty] | 0.94761 | 0.91972 | 0.96454 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14982312SP |  |  | MUSCOTAH 69KV | S | WERE |  | NEAST |  |  | 533480 | MUSCOTA2 69.000 | [5 empty] | 12SP | [6 empty] | 0.94761 | 0.91972 | 0.96454 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14822312SP |  |  | SPRUCE STREET 115KV | S | WERE |  | NEAST |  |  | 533266 | SPRUCE 3 115.00 | [5 empty] | 12SP | [6 empty] | 0.95018 | 0.9226 | 0.99588 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14852312SP |  |  | THORNTON STREET 115KV | S | WERE |  | NEAST |  |  | 533272 | THORNTN3 115.00 | [5 empty] | 12SP | [6 empty] | 0.9502 | 0.92269 | 0.99589 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14732312SP |  |  | HALLMARK 115KV | S | WERE |  | NEAST |  |  | 533242 | HALLMRK3 115.00 | [5 empty] | 12SP | [6 empty] | 0.9509 | 0.92353 | 0.99437 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14792312SP |  |  | NORTHWEST LEAVENWORTH 115KV | S | WERE |  | NEAST |  |  | 533259 | NW LEAV3 115.00 | [5 empty] | 12SP | [6 empty] | 0.9535 | 0.92568 | 0.9993 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14762312SP |  |  | LANSING3 115.00 115KV | S | WERE |  | NEAST |  |  | 533246 | LANSING3 115.00 | [5 empty] | 12SP | [6 empty] | 0.9552 | 0.92818 | 0.99696 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14992312SP |  |  | NORTONVILLE 69KV | S | WERE |  | NEAST |  |  | 533481 | NORTONV2 69.000 | [5 empty] | 12SP | [6 empty] | 0.95609 | 0.92849 | 0.97286 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14842312SP |  |  | STRANGER CREEK 115KV | S | WERE |  | NEAST |  |  | 533268 | STRANGR3 115.00 | [5 empty] | 12SP | [6 empty] | 0.95608 | 0.92894 | 1.003 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15012312SP |  |  | VALLEY FALLS 69KV | S | WERE |  | NEAST |  |  | 533483 | VALLEY22 69.000 | [5 empty] | 12SP | [6 empty] | 0.96124 | 0.93669 | 0.97769 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15012312SP |  |  | VALLEY FALLS 69KV | S | WERE |  | NEAST |  |  | 533483 | VALLEY22 69.000 | [5 empty] | 12SP | [6 empty] | 0.96124 | 0.93669 | 0.97769 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14772312SP |  |  | MOONLIGHT 115KV | S | WERE |  | NEAST |  |  | 533254 | MOONLIT3 115.00 | [5 empty] | 12SP | [6 empty] | 0.96432 | 0.93941 | 0.97251 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14882312SP |  |  | 95TH & WAVERLY 115KV | S | WERE |  | NEAST |  |  | 533278 | WAVERLY3 115.00 | [5 empty] | 12SP | [6 empty] | 0.96371 | 0.93974 | 0.97737 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12812312SP |  |  | NEW SPRING HILL 115KV | S | WERE |  | NEAST |  |  | 533267 | SPRINGH3 115.00 | [5 empty] | 12SP | [6 empty] | 0.96726 | 0.93985 | 0.97259 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14712312SP |  |  | EAST S.A.A.P. JCT 115KV | S | WERE |  | NEAST |  |  | 533239 | ESAAPJ 3 115.00 | [5 empty] | 12SP | [6 empty] | 0.96413 | 0.93994 | 0.9766 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14782312SP |  |  | MOONLIGHT JUNCTION SWITCHING STATION 115KV | S | WERE |  | NEAST |  |  | 533255 | MOONLTJ3 115.00 | [5 empty] | 12SP | [6 empty] | 0.96582 | 0.94095 | 0.974 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12792312SP |  |  | 160TH STREET 115KV | S | WERE |  | NEAST |  |  | 533262 | 160TH 3 115.00 | [5 empty] | 12SP | [6 empty] | 0.96832 | 0.94254 | 0.97259 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14752312SP |  |  | JARBALO JUNCTION SWITCHING STATION 115KV | S | WERE |  | NEAST |  |  | 533244 | JARBALO3 115.00 | [5 empty] | 12SP | [6 empty] | 0.96888 | 0.94286 | 1.00546 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14812312SP |  |  | SOUTHTOWN 115KV | S | WERE |  | NEAST |  |  | 533265 | SOUTHTN3 115.00 | [5 empty] | 12SP | [6 empty] | 0.96862 | 0.94344 | 0.97319 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14672312SP |  |  | TONGA TAP 115KV | S | WERE |  | NEAST |  |  | 533219 | TONGATP3 115.00 | [5 empty] | 12SP | [6 empty] | 0.96875 | 0.94382 | 1.00336 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V9402312SP |  |  | NEW SPRING HILL 115KV | S | WERE |  | NEAST |  |  | 533267 | SPRINGH3 115.00 | [5 empty] | 12SP | [6 empty] | 0.9711 | 0.94404 | 0.97259 | 0.95 | 1.05 | CATEGORYB | SINGLE | CRAIG - STRANGER CREEK 345KV CKT 1 | 0 | 532772 | STRANGR7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14692312SP |  |  | 166TH STREET 115KV | S | WERE |  | NEAST |  |  | 533233 | 166TH 3 115.00 | [5 empty] | 12SP | [6 empty] | 0.96984 | 0.94475 | 0.99465 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14862312SP |  |  | TIMBERLANE 115KV | S | WERE |  | NEAST |  |  | 533273 | TIMBRLN3 115.00 | [5 empty] | 12SP | [6 empty] | 0.96996 | 0.94501 | 0.9769 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12772312SP |  |  | MOONLIGHT 115KV | S | WERE |  | NEAST |  |  | 533254 | MOONLIT3 115.00 | [5 empty] | 12SP | [6 empty] | 0.96914 | 0.94523 | 0.97251 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14702312SP |  |  | CAPTAIN JUNCTION 115KV | S | WERE |  | NEAST |  |  | 533235 | CAPTAIN3 115.00 | [5 empty] | 12SP | [6 empty] | 0.96972 | 0.94673 | 0.98736 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12782312SP |  |  | MOONLIGHT JUNCTION SWITCHING STATION 115KV | S | WERE |  | NEAST |  |  | 533255 | MOONLTJ3 115.00 | [5 empty] | 12SP | [6 empty] | 0.97063 | 0.94676 | 0.974 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14722312SP |  |  | EUDORA TOWNSHIP 115KV | S | WERE |  | NEAST |  |  | 533240 | EUDORA 3 115.00 | [5 empty] | 12SP | [6 empty] | 0.96977 | 0.94707 | 0.98899 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14742312SP |  |  | JAGGARD JUNCTION 115KV | S | WERE |  | NEAST |  |  | 533243 | JAGGARD3 115.00 | [5 empty] | 12SP | [6 empty] | 0.97213 | 0.94777 | 0.9898 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V14872312SP |  |  | WAKARUSA JUNCTION SWITCHING STATION 115KV | S | WERE |  | NEAST |  |  | 533277 | WAKARUS3 115.00 | [5 empty] | 12SP | [6 empty] | 0.97129 | 0.94909 | 0.99267 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12822312SP |  |  | TIMBERLANE 115KV | S | WERE |  | NEAST |  |  | 533273 | TIMBRLN3 115.00 | [5 empty] | 12SP | [6 empty] | 0.97358 | 0.9495 | 0.9769 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V9372312SP |  |  | MOONLIGHT 115KV | S | WERE |  | NEAST |  |  | 533254 | MOONLIT3 115.00 | [5 empty] | 12SP | [6 empty] | 0.97338 | 0.94972 | 0.97251 | 0.95 | 1.05 | CATEGORYB | SINGLE | CRAIG - STRANGER CREEK 345KV CKT 1 | 0 | 532772 | STRANGR7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20352317SP |  |  | WATHENA 69KV | S | WERE |  | NEAST |  |  | 533485 | WATHENA2 69.000 | [5 empty] | 17SP | [6 empty] | 0.82937 | 0.76196 | 0.93811 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20352317SP |  |  | WATHENA 69KV | S | WERE |  | NEAST |  |  | 533485 | WATHENA2 69.000 | [5 empty] | 17SP | [6 empty] | 0.82937 | 0.76196 | 0.93811 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19782317SP |  |  | WALNUT STREET 115KV | S | WERE |  | NEAST |  |  | 533220 | WALNUT 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.84913 | 0.79126 | 0.94755 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19782317SP |  |  | WALNUT STREET 115KV | S | WERE |  | NEAST |  |  | 533220 | WALNUT 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.84913 | 0.79126 | 0.94755 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19762317SP |  |  | PARALLEL 115KV | S | WERE |  | NEAST |  |  | 533218 | PARALEL3 115.00 | [5 empty] | 17SP | [6 empty] | 0.85229 | 0.79471 | 0.9508 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19742317SP |  |  | ARNOLD 115KV | S | WERE |  | NEAST |  |  | 533211 | ARNOLD 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.8596 | 0.80265 | 0.95809 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19752317SP |  |  | KEREFORD JUNCTION 115KV | S | WERE |  | NEAST |  |  | 533216 | KERFORD3 115.00 | [5 empty] | 17SP | [6 empty] | 0.86208 | 0.80564 | 0.96045 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20242317SP |  |  | ATCHISON CASTINGS 69KV | S | WERE |  | NEAST |  |  | 533474 | ATCHCST2 69.000 | [5 empty] | 17SP | [6 empty] | 0.87015 | 0.80739 | 0.97491 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20272317SP |  |  | MIDWEST GRAIN 69KV | S | WERE |  | NEAST |  |  | 533477 | MW SOLV2 69.000 | [5 empty] | 17SP | [6 empty] | 0.87445 | 0.81196 | 0.97873 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20222317SP |  |  | ATCHISON JCT1 69KV | S | WERE |  | NEAST |  |  | 533472 | ATCH J12 69.000 | [5 empty] | 17SP | [6 empty] | 0.87491 | 0.81251 | 0.97915 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20282317SP |  |  | MIDWEST GRAIN SOLVENTS JCT1 69KV | S | WERE |  | NEAST |  |  | 533478 | MWSOLJ12 69.000 | [5 empty] | 17SP | [6 empty] | 0.875 | 0.81261 | 0.97924 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20232317SP |  |  | ATCHISON JCT2 69KV | S | WERE |  | NEAST |  |  | 533473 | ATCH J22 69.000 | [5 empty] | 17SP | [6 empty] | 0.87519 | 0.81276 | 0.97939 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20292317SP |  |  | MIDWEST GRAIN SOLVENTS JCT2 69KV | S | WERE |  | NEAST |  |  | 533479 | MWSOLJ22 69.000 | [5 empty] | 17SP | [6 empty] | 0.87717 | 0.81504 | 0.98109 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20342317SP |  |  | WALNUT STREET 69KV | S | WERE |  | NEAST |  |  | 533484 | WALNUT 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.87838 | 0.81579 | 0.98097 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20262317SP |  |  | MAUR HILL 69KV | S | WERE |  | NEAST |  |  | 533476 | MAUR HL2 69.000 | [5 empty] | 17SP | [6 empty] | 0.87802 | 0.81583 | 0.98258 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20252317SP |  |  | KEREFORD JUNCTION 69KV | S | WERE |  | NEAST |  |  | 533475 | KERFORD2 69.000 | [5 empty] | 17SP | [6 empty] | 0.88481 | 0.82317 | 0.98967 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20212317SP |  |  | ARNOLD 69KV | S | WERE |  | NEAST |  |  | 533471 | ARNOLD 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.88582 | 0.82474 | 0.98834 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20072317SP |  |  | SPRUCE STREET 115KV | S | WERE |  | NEAST |  |  | 533266 | SPRUCE 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.88194 | 0.82954 | 0.98008 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20132317SP |  |  | THORNTON STREET 115KV | S | WERE |  | NEAST |  |  | 533272 | THORNTN3 115.00 | [5 empty] | 17SP | [6 empty] | 0.8823 | 0.83007 | 0.98053 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20022317SP |  |  | NORTHWEST LEAVENWORTH 115KV | S | WERE |  | NEAST |  |  | 533259 | NW LEAV3 115.00 | [5 empty] | 17SP | [6 empty] | 0.88436 | 0.83137 | 0.98179 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19882317SP |  |  | HALLMARK 115KV | S | WERE |  | NEAST |  |  | 533242 | HALLMRK3 115.00 | [5 empty] | 17SP | [6 empty] | 0.88371 | 0.83186 | 0.97889 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19922317SP |  |  | LANSING3 115.00 115KV | S | WERE |  | NEAST |  |  | 533246 | LANSING3 115.00 | [5 empty] | 17SP | [6 empty] | 0.88996 | 0.839 | 0.98202 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20092317SP |  |  | STRANGER CREEK 115KV | S | WERE |  | NEAST |  |  | 533268 | STRANGR3 115.00 | [5 empty] | 17SP | [6 empty] | 0.89049 | 0.83918 | 0.99206 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20302317SP |  |  | MUSCOTAH 69KV | S | WERE |  | NEAST |  |  | 533480 | MUSCOTA2 69.000 | [5 empty] | 17SP | [6 empty] | 0.89898 | 0.84172 | 0.96362 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20302317SP |  |  | MUSCOTAH 69KV | S | WERE |  | NEAST |  |  | 533480 | MUSCOTA2 69.000 | [5 empty] | 17SP | [6 empty] | 0.89898 | 0.84172 | 0.96362 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20302317SP |  |  | MUSCOTAH 69KV | S | WERE |  | NEAST |  |  | 533480 | MUSCOTA2 69.000 | [5 empty] | 17SP | [6 empty] | 0.89898 | 0.84172 | 0.96362 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20302317SP |  |  | MUSCOTAH 69KV | S | WERE |  | NEAST |  |  | 533480 | MUSCOTA2 69.000 | [5 empty] | 17SP | [6 empty] | 0.89898 | 0.84172 | 0.96362 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20302317SP |  |  | MUSCOTAH 69KV | S | WERE |  | NEAST |  |  | 533480 | MUSCOTA2 69.000 | [5 empty] | 17SP | [6 empty] | 0.89898 | 0.84172 | 0.96362 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20312317SP |  |  | NORTONVILLE 69KV | S | WERE |  | NEAST |  |  | 533481 | NORTONV2 69.000 | [5 empty] | 17SP | [6 empty] | 0.90941 | 0.85293 | 0.9733 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19902317SP |  |  | JARBALO JUNCTION SWITCHING STATION 115KV | S | WERE |  | NEAST |  |  | 533244 | JARBALO3 115.00 | [5 empty] | 17SP | [6 empty] | 0.90942 | 0.86106 | 0.99222 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19772317SP |  |  | TONGA TAP 115KV | S | WERE |  | NEAST |  |  | 533219 | TONGATP3 115.00 | [5 empty] | 17SP | [6 empty] | 0.91322 | 0.86721 | 0.98979 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20332317SP |  |  | VALLEY FALLS 69KV | S | WERE |  | NEAST |  |  | 533483 | VALLEY22 69.000 | [5 empty] | 17SP | [6 empty] | 0.92127 | 0.87091 | 0.9784 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20332317SP |  |  | VALLEY FALLS 69KV | S | WERE |  | NEAST |  |  | 533483 | VALLEY22 69.000 | [5 empty] | 17SP | [6 empty] | 0.92127 | 0.87091 | 0.9784 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20332317SP |  |  | VALLEY FALLS 69KV | S | WERE |  | NEAST |  |  | 533483 | VALLEY22 69.000 | [5 empty] | 17SP | [6 empty] | 0.92127 | 0.87091 | 0.9784 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20332317SP |  |  | VALLEY FALLS 69KV | S | WERE |  | NEAST |  |  | 533483 | VALLEY22 69.000 | [5 empty] | 17SP | [6 empty] | 0.92127 | 0.87091 | 0.9784 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19802317SP |  |  | 166TH STREET 115KV | S | WERE |  | NEAST |  |  | 533233 | 166TH 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.91737 | 0.87214 | 0.9833 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20162317SP |  |  | 95TH & WAVERLY 115KV | S | WERE |  | NEAST |  |  | 533278 | WAVERLY3 115.00 | [5 empty] | 17SP | [6 empty] | 0.92146 | 0.8812 | 0.9649 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19892317SP |  |  | JAGGARD JUNCTION 115KV | S | WERE |  | NEAST |  |  | 533243 | JAGGARD3 115.00 | [5 empty] | 17SP | [6 empty] | 0.92496 | 0.88205 | 0.98018 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19852317SP |  |  | EAST S.A.A.P. JCT 115KV | S | WERE |  | NEAST |  |  | 533239 | ESAAPJ 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.92259 | 0.88235 | 0.96473 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19982317SP |  |  | MOONLIGHT 115KV | S | WERE |  | NEAST |  |  | 533254 | MOONLIT3 115.00 | [5 empty] | 17SP | [6 empty] | 0.92549 | 0.8854 | 0.96299 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19862317SP |  |  | EUDORA TOWNSHIP 115KV | S | WERE |  | NEAST |  |  | 533240 | EUDORA 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.92596 | 0.8862 | 0.97507 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19822317SP |  |  | CAPTAIN JUNCTION 115KV | S | WERE |  | NEAST |  |  | 533235 | CAPTAIN3 115.00 | [5 empty] | 17SP | [6 empty] | 0.92655 | 0.88679 | 0.97404 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19992317SP |  |  | MOONLIGHT JUNCTION SWITCHING STATION 115KV | S | WERE |  | NEAST |  |  | 533255 | MOONLTJ3 115.00 | [5 empty] | 17SP | [6 empty] | 0.92703 | 0.88701 | 0.96446 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20152317SP |  |  | WAKARUSA JUNCTION SWITCHING STATION 115KV | S | WERE |  | NEAST |  |  | 533277 | WAKARUS3 115.00 | [5 empty] | 17SP | [6 empty] | 0.92701 | 0.88747 | 0.97826 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19832317SP |  |  | FARMERS CONSUMER CO-OP 115KV | S | WERE |  | NEAST |  |  | 533236 | COOP 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.92839 | 0.88894 | 0.98071 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20002317SP |  |  | 19TH STREET 115KV | S | WERE |  | NEAST |  |  | 533256 | 19THST 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.92898 | 0.88985 | 0.98089 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19912317SP |  |  | KU CAMPUS 115KV | S | WERE |  | NEAST |  |  | 533245 | KU CAMP3 115.00 | [5 empty] | 17SP | [6 empty] | 0.92971 | 0.89067 | 0.9815 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20012317SP |  |  | 19TH STREET JUNCTION 115KV | S | WERE |  | NEAST |  |  | 533257 | 19THSTJ3 115.00 | [5 empty] | 17SP | [6 empty] | 0.93039 | 0.89144 | 0.98208 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20142317SP |  |  | TIMBERLANE 115KV | S | WERE |  | NEAST |  |  | 533273 | TIMBRLN3 115.00 | [5 empty] | 17SP | [6 empty] | 0.93207 | 0.89231 | 0.96803 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20122317SP |  |  | SOUTHWEST LAWRENCE 115KV | S | WERE |  | NEAST |  |  | 533271 | SWLWRNC3 115.00 | [5 empty] | 17SP | [6 empty] | 0.93261 | 0.89392 | 0.98397 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19812317SP |  |  | BISMARK JUNCTION SWITCHING STATION 115KV | S | WERE |  | NEAST |  |  | 533234 | BISMARK3 115.00 | [5 empty] | 17SP | [6 empty] | 0.93358 | 0.89408 | 0.9878 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20062317SP |  |  | SOUTHTOWN 115KV | S | WERE |  | NEAST |  |  | 533265 | SOUTHTN3 115.00 | [5 empty] | 17SP | [6 empty] | 0.93342 | 0.89464 | 0.96492 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19872317SP |  |  | FMC 115KV | S | WERE |  | NEAST |  |  | 533241 | FMC 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.93457 | 0.89508 | 0.98908 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20182317SP |  |  | MONTICELLO 115KV | S | WERE |  | NEAST |  |  | 533281 | MNTCLLO3 115.00 | [5 empty] | 17SP | [6 empty] | 0.93641 | 0.89658 | 0.97665 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20052317SP |  |  | 6TH STREET 115KV | S | WERE |  | NEAST |  |  | 533264 | 6TH ST 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.9368 | 0.89738 | 0.99157 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19972317SP |  |  | MOCKINGBIRD HILL SWITCHING STATION 115KV | S | WERE |  | NEAST |  |  | 533253 | MOCKBRD3 115.00 | [5 empty] | 17SP | [6 empty] | 0.93653 | 0.89867 | 0.98682 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19962317SP |  |  | MIDLAND JUNCTION 115KV | S | WERE |  | NEAST |  |  | 533252 | MIDLAND3 115.00 | [5 empty] | 17SP | [6 empty] | 0.93851 | 0.89884 | 0.99504 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20042317SP |  |  | 160TH STREET 115KV | S | WERE |  | NEAST |  |  | 533262 | 160TH 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.93733 | 0.89942 | 0.96514 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20032317SP |  |  | PENTAGON 115KV | S | WERE |  | NEAST |  |  | 533261 | PENTAGN3 115.00 | [5 empty] | 17SP | [6 empty] | 0.93935 | 0.89955 | 0.98142 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19792317SP |  |  | BALDWIN CREEK 115KV | S | WERE |  | NEAST |  |  | 533232 | BALDCRK3 115.00 | [5 empty] | 17SP | [6 empty] | 0.93886 | 0.89988 | 0.99234 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20172317SP |  |  | WREN 115KV | S | WERE |  | NEAST |  |  | 533280 | WREN 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.9412 | 0.90193 | 0.99639 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20202317SP |  |  | ROCK CREEK 69KV | S | WERE |  | NEAST |  |  | 533458 | ROCKCRK2 69.000 | [5 empty] | 17SP | [6 empty] | 0.94658 | 0.90464 | 0.99031 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20202317SP |  |  | ROCK CREEK 69KV | S | WERE |  | NEAST |  |  | 533458 | ROCKCRK2 69.000 | [5 empty] | 17SP | [6 empty] | 0.94658 | 0.90464 | 0.99031 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20202317SP |  |  | ROCK CREEK 69KV | S | WERE |  | NEAST |  |  | 533458 | ROCKCRK2 69.000 | [5 empty] | 17SP | [6 empty] | 0.94658 | 0.90464 | 0.99031 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19932317SP |  |  | LAWRENCE ENERGY CENTER UNIT 3 115KV | S | WERE |  | NEAST |  |  | 533248 | LEC U3 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.94395 | 0.90474 | 0.99918 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19952317SP |  |  | LAWRENCE HILL 115KV | S | WERE |  | NEAST |  |  | 533250 | LWRNCHL3 115.00 | [5 empty] | 17SP | [6 empty] | 0.94447 | 0.90536 | 0.99949 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19942317SP |  |  | LAWRENCE ENERGY CENTER UNIT 4 115KV | S | WERE |  | NEAST |  |  | 533249 | LEC U4 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.94492 | 0.90561 | 1.00077 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19722317SP |  |  | MIDLAND JUNCTION 230KV | S | WERE |  | NEAST |  |  | 532855 | MIDLAND6 230.00 | [5 empty] | 17SP | [6 empty] | 0.94759 | 0.9123 | 0.99553 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20082317SP |  |  | NEW SPRING HILL 115KV | S | WERE |  | NEAST |  |  | 533267 | SPRINGH3 115.00 | [5 empty] | 17SP | [6 empty] | 0.94913 | 0.91334 | 0.96738 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19702317SP |  |  | LAWRENCE HILL 230KV | S | WERE |  | NEAST |  |  | 532853 | LAWHILL6 230.00 | [5 empty] | 17SP | [6 empty] | 0.95061 | 0.916 | 0.99682 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19712317SP |  |  | LAWRENCE ENERGY CENTER UNIT 5 230KV | S | WERE |  | NEAST |  |  | 532854 | LEC U5 6 230.00 | [5 empty] | 17SP | [6 empty] | 0.95128 | 0.91668 | 0.99747 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20192317SP |  |  | MUND 115KV | S | WERE |  | NEAST |  |  | 533282 | MUND 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.95473 | 0.91692 | 0.98963 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20102317SP |  |  | STULL (KAW VALLEY R.E.C.) 115KV | S | WERE |  | NEAST |  |  | 533269 | STULL 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.95807 | 0.926 | 0.99486 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V20112317SP |  |  | STULL SWITCHING STATION 115KV | S | WERE |  | NEAST |  |  | 533270 | STULL T3 115.00 | [5 empty] | 17SP | [6 empty] | 0.95809 | 0.92601 | 0.99488 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16072317SP |  |  | MOONLIGHT 115KV | S | WERE |  | NEAST |  |  | 533254 | MOONLIT3 115.00 | [5 empty] | 17SP | [6 empty] | 0.96004 | 0.92758 | 0.96299 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16102317SP |  |  | 160TH STREET 115KV | S | WERE |  | NEAST |  |  | 533262 | 160TH 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.96196 | 0.92825 | 0.96514 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16112317SP |  |  | SOUTHTOWN 115KV | S | WERE |  | NEAST |  |  | 533265 | SOUTHTN3 115.00 | [5 empty] | 17SP | [6 empty] | 0.96186 | 0.92856 | 0.96492 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16082317SP |  |  | MOONLIGHT JUNCTION SWITCHING STATION 115KV | S | WERE |  | NEAST |  |  | 533255 | MOONLTJ3 115.00 | [5 empty] | 17SP | [6 empty] | 0.96152 | 0.92912 | 0.96446 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16122317SP |  |  | NEW SPRING HILL 115KV | S | WERE |  | NEAST |  |  | 533267 | SPRINGH3 115.00 | [5 empty] | 17SP | [6 empty] | 0.96381 | 0.92916 | 0.96738 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16042317SP |  |  | EAST S.A.A.P. JCT 115KV | S | WERE |  | NEAST |  |  | 533239 | ESAAPJ 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.9618 | 0.93079 | 0.96473 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16152317SP |  |  | 95TH & WAVERLY 115KV | S | WERE |  | NEAST |  |  | 533278 | WAVERLY3 115.00 | [5 empty] | 17SP | [6 empty] | 0.96198 | 0.93139 | 0.9649 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12132317SP |  |  | 95TH & WAVERLY 115KV | S | WERE |  | NEAST |  |  | 533278 | WAVERLY3 115.00 | [5 empty] | 17SP | [6 empty] | 0.96043 | 0.93429 | 0.9649 | 0.95 | 1.05 | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12012317SP |  |  | EAST S.A.A.P. JCT 115KV | S | WERE |  | NEAST |  |  | 533239 | ESAAPJ 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.96088 | 0.93463 | 0.96473 | 0.95 | 1.05 | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V19842317SP |  |  | EDWARDSVILLE 115KV | S | WERE |  | NEAST |  |  | 533238 | EDWARVL3 115.00 | [5 empty] | 17SP | [6 empty] | 0.97579 | 0.94044 | 1.00191 | 0.95 | 1.05 | CATEGORYB | SINGLE | STRANGER CREEK (STRNGR1X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532772 | STRANGR7 345.00 | 533268 | STRANGR3 115.00 | 532811 | STRAN1 1 14.400 | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V11992317SP |  |  | CAPTAIN JUNCTION 115KV | S | WERE |  | NEAST |  |  | 533235 | CAPTAIN3 115.00 | [5 empty] | 17SP | [6 empty] | 0.96765 | 0.9423 | 0.97404 | 0.95 | 1.05 | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12022317SP |  |  | EUDORA TOWNSHIP 115KV | S | WERE |  | NEAST |  |  | 533240 | EUDORA 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.96762 | 0.94243 | 0.97507 | 0.95 | 1.05 | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16032317SP |  |  | CAPTAIN JUNCTION 115KV | S | WERE |  | NEAST |  |  | 533235 | CAPTAIN3 115.00 | [5 empty] | 17SP | [6 empty] | 0.97122 | 0.94246 | 0.97404 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16162317SP |  |  | MONTICELLO 115KV | S | WERE |  | NEAST |  |  | 533281 | MNTCLLO3 115.00 | [5 empty] | 17SP | [6 empty] | 0.97393 | 0.94312 | 0.97665 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16052317SP |  |  | EUDORA TOWNSHIP 115KV | S | WERE |  | NEAST |  |  | 533240 | EUDORA 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.97225 | 0.94417 | 0.97507 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12122317SP |  |  | WAKARUSA JUNCTION SWITCHING STATION 115KV | S | WERE |  | NEAST |  |  | 533277 | WAKARUS3 115.00 | [5 empty] | 17SP | [6 empty] | 0.96948 | 0.94469 | 0.97826 | 0.95 | 1.05 | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12002317SP |  |  | FARMERS CONSUMER CO-OP 115KV | S | WERE |  | NEAST |  |  | 533236 | COOP 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.97176 | 0.94719 | 0.98071 | 0.95 | 1.05 | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12062317SP |  |  | 19TH STREET 115KV | S | WERE |  | NEAST |  |  | 533256 | 19THST 3 115.00 | [5 empty] | 17SP | [6 empty] | 0.97175 | 0.94734 | 0.98089 | 0.95 | 1.05 | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12032317SP |  |  | KU CAMPUS 115KV | S | WERE |  | NEAST |  |  | 533245 | KU CAMP3 115.00 | [5 empty] | 17SP | [6 empty] | 0.97232 | 0.94796 | 0.9815 | 0.95 | 1.05 | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16142317SP |  |  | WAKARUSA JUNCTION SWITCHING STATION 115KV | S | WERE |  | NEAST |  |  | 533277 | WAKARUS3 115.00 | [5 empty] | 17SP | [6 empty] | 0.97545 | 0.94847 | 0.97826 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12072317SP |  |  | 19TH STREET JUNCTION 115KV | S | WERE |  | NEAST |  |  | 533257 | 19THSTJ3 115.00 | [5 empty] | 17SP | [6 empty] | 0.97288 | 0.94856 | 0.98208 | 0.95 | 1.05 | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16092317SP |  |  | PENTAGON 115KV | S | WERE |  | NEAST |  |  | 533261 | PENTAGN3 115.00 | [5 empty] | 17SP | [6 empty] | 0.97888 | 0.9489 | 0.98142 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V16062317SP |  |  | JAGGARD JUNCTION 115KV | S | WERE |  | NEAST |  |  | 533243 | JAGGARD3 115.00 | [5 empty] | 17SP | [6 empty] | 0.97764 | 0.94938 | 0.98018 | 0.95 | 1.05 | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542981 | LACYGNE7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  |  | WERE | TECUMSEH ENERGY CENTER - MIDLAND 115KV CKT 1 Displacement | Convert 161 kV Line to 115 kV Operation | [5 empty] | 6 | 6 | [5 empty] | 2000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2009-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V3602108AP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08AP | [6 empty] | 1.0133 | 0.8986 | 0.94789 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V3622108AP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08AP | [6 empty] | 1.0133 | 0.9157 | 0.96407 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V3612108AP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08AP | [6 empty] | 1.0133 | 0.91888 | 0.96708 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V3531108AP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08AP | [6 empty] | 0.95794 | 0.92052 | 0.94425 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V4721108AP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08AP | [6 empty] | 0.95806 | 0.92058 | 0.94425 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 5 | 5 | 2008-12-01 | 2007AG1AFS81V1365508AP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08AP | [6 empty] | 0.94863 | 0.92418 | 0.94905 | 0.95 | 1.05 | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V3531208AP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08AP | [6 empty] | 0.99424 | 0.93133 | 0.95309 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V3561208AP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08AP | [6 empty] | 0.99421 | 0.93137 | 0.95309 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V3351208AP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 08AP | [6 empty] | 0.96678 | 0.94393 | 0.9833 | 0.95 | 1.05 | CATEGORYB | SINGLE | DEARING - MONTGOMERY 138KV CKT 1 | 0 | 533002 | DEARING4 138.00 | 533004 | MONTGOM4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V2862408AP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 08AP | [6 empty] | 0.97555 | 0.94533 | 0.97004 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V3361208AP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 08AP | [6 empty] | 0.96785 | 0.94533 | 0.98215 | 0.95 | 1.05 | CATEGORYB | SINGLE | DEARING - MONTGOMERY 138KV CKT 1 | 0 | 533002 | DEARING4 138.00 | 533004 | MONTGOM4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V3371208AP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 08AP | [6 empty] | 0.96788 | 0.94535 | 0.98217 | 0.95 | 1.05 | CATEGORYB | SINGLE | DEARING - MONTGOMERY 138KV CKT 1 | 0 | 533002 | DEARING4 138.00 | 533004 | MONTGOM4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V4052408AP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 08AP | [6 empty] | 0.97571 | 0.9456 | 0.97004 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V3541208AP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08AP | [6 empty] | 0.99421 | 0.9478 | 0.96918 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 2 | 2008-12-01 | 2007AG1AFS81V3571208AP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08AP | [6 empty] | 0.99418 | 0.94784 | 0.96918 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V6063308FA |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08FA | [6 empty] | 0.99922 | 0.87127 | 0.94183 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V6083308FA |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08FA | [6 empty] | 0.99919 | 0.88942 | 0.95853 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V6073308FA |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08FA | [6 empty] | 0.99942 | 0.89294 | 0.96177 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V3154408FA |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08FA | [6 empty] | 0.9635 | 0.92212 | 0.95452 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V3434108FA |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08FA | [6 empty] | 0.98653 | 0.92213 | 0.9442 | 0.95 | 1.05 | CATEGORYB | SINGLE | ARCO TAP - ENA 69KV CKT 1 | 0 | 533634 | ENA 2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V3164408FA |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08FA | [6 empty] | 0.96385 | 0.92253 | 0.95452 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V3001108FA |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08FA | [6 empty] | 0.97138 | 0.92255 | 0.95449 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 2 | 2008-12-01 | 2007AG1AFS81V6403208FA |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08FA | [6 empty] | 0.98865 | 0.92277 | 0.94289 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V3454108FA |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08FA | [6 empty] | 0.98651 | 0.93919 | 0.96086 | 0.95 | 1.05 | CATEGORYB | SINGLE | ARCO TAP - ENA 69KV CKT 1 | 0 | 533634 | ENA 2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V6172208FA |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08FA | [6 empty] | 0.98582 | 0.93987 | 0.96001 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V3144408FA |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 08FA | [6 empty] | 0.99563 | 0.94239 | 0.9779 | 0.95 | 1.05 | CATEGORYB | SINGLE | ATHENS SWITCHING STATION - OWL CREEK 69KV CKT 1 | 0 | 533623 | ATHENS 2 69.000 | 533642 | OWL CRK2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V3444108FA |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08FA | [6 empty] | 0.98673 | 0.9425 | 0.9641 | 0.95 | 1.05 | CATEGORYB | SINGLE | ARCO TAP - ENA 69KV CKT 1 | 0 | 533634 | ENA 2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V6162208FA |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08FA | [6 empty] | 0.98605 | 0.94318 | 0.96324 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V2744408FA |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 08FA | [6 empty] | 0.98469 | 0.94579 | 0.97556 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V4794408FA |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 08FA | [6 empty] | 0.98311 | 0.94602 | 0.97556 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V1541408G |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08G | [6 empty] | 0.99837 | 0.87792 | 0.9443 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V1561408G |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08G | [6 empty] | 0.99834 | 0.89541 | 0.96054 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V1551408G |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08G | [6 empty] | 0.99857 | 0.89881 | 0.9637 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V1351108G |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08G | [6 empty] | 0.95625 | 0.91484 | 0.94864 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V1981108G |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08G | [6 empty] | 0.9568 | 0.91537 | 0.94864 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V1591408G |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08G | [6 empty] | 0.95217 | 0.91965 | 0.94887 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V1791108G |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08G | [6 empty] | 0.98612 | 0.92338 | 0.94374 | 0.95 | 1.05 | CATEGORYB | SINGLE | ENA - TIOGA 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V1601408G |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08G | [6 empty] | 0.98548 | 0.92382 | 0.9443 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V1361108G |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 08G | [6 empty] | 0.97037 | 0.93744 | 0.97027 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V1851408G |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 08G | [6 empty] | 0.96997 | 0.93817 | 0.96979 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V1621408G |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08G | [6 empty] | 0.98545 | 0.94042 | 0.96054 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V2532308G |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08G | [6 empty] | 0.98671 | 0.94056 | 0.96233 | 0.95 | 1.05 | CATEGORYB | SINGLE | ARCO TAP - ENA 69KV CKT 1 | 0 | 533634 | ENA 2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V1781108G |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 08G | [6 empty] | 0.99364 | 0.94316 | 0.97873 | 0.95 | 1.05 | CATEGORYB | SINGLE | ATHENS SWITCHING STATION - OWL CREEK 69KV CKT 1 | 0 | 533623 | ATHENS 2 69.000 | 533642 | OWL CRK2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V1611408G |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08G | [6 empty] | 0.98568 | 0.94365 | 0.9637 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V2522308G |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08G | [6 empty] | 0.98694 | 0.94378 | 0.96549 | 0.95 | 1.05 | CATEGORYB | SINGLE | ARCO TAP - ENA 69KV CKT 1 | 0 | 533634 | ENA 2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 3 | 2008-12-01 | 2007AG1AFS81V3731308SH |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08SH | [6 empty] | 0.99621 | 0.86184 | 0.9398 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 3 | 2008-12-01 | 2007AG1AFS81V3761308SH |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08SH | [6 empty] | 0.99618 | 0.8804 | 0.95673 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 3 | 2008-12-01 | 2007AG1AFS81V3741308SH |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08SH | [6 empty] | 0.99647 | 0.88407 | 0.96008 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V2831108SH |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08SH | [6 empty] | 0.94857 | 0.91022 | 0.94459 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V4841108SH |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08SH | [6 empty] | 0.94875 | 0.91028 | 0.94459 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V4201108SH |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08SH | [6 empty] | 0.95384 | 0.91473 | 0.94459 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V4021408SH |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08SH | [6 empty] | 0.98421 | 0.91607 | 0.93991 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V4061408SH |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08SH | [6 empty] | 0.98506 | 0.91684 | 0.93991 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V2841108SH |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 08SH | [6 empty] | 0.96242 | 0.93044 | 0.9679 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V4851108SH |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 08SH | [6 empty] | 0.96279 | 0.9307 | 0.9679 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V3361408SH |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 08SH | [6 empty] | 0.9582 | 0.93193 | 0.97651 | 0.95 | 1.05 | CATEGORYB | SINGLE | DEARING - MONTGOMERY 138KV CKT 1 | 0 | 533002 | DEARING4 138.00 | 533004 | MONTGOM4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V3371408SH |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 08SH | [6 empty] | 0.95919 | 0.93312 | 0.97499 | 0.95 | 1.05 | CATEGORYB | SINGLE | DEARING - MONTGOMERY 138KV CKT 1 | 0 | 533002 | DEARING4 138.00 | 533004 | MONTGOM4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V3381408SH |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 08SH | [6 empty] | 0.95926 | 0.9332 | 0.97506 | 0.95 | 1.05 | CATEGORYB | SINGLE | DEARING - MONTGOMERY 138KV CKT 1 | 0 | 533002 | DEARING4 138.00 | 533004 | MONTGOM4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V4041408SH |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08SH | [6 empty] | 0.98418 | 0.93345 | 0.95684 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V4081408SH |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08SH | [6 empty] | 0.98503 | 0.9342 | 0.95684 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V4211108SH |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 08SH | [6 empty] | 0.96848 | 0.93597 | 0.9679 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V4031408SH |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08SH | [6 empty] | 0.98448 | 0.93689 | 0.96019 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V4071408SH |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08SH | [6 empty] | 0.98533 | 0.93763 | 0.96019 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V4432308SH |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 08SH | [6 empty] | 0.96573 | 0.94072 | 0.97111 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V4442308SH |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 08SH | [6 empty] | 0.9658 | 0.94079 | 0.97118 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V4412308SH |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 08SH | [6 empty] | 0.96534 | 0.94142 | 0.97197 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 3 | 2008-12-01 | 2007AG1AFS81V3751308SH |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 08SH | [6 empty] | 1.001 | 0.94363 | 0.97647 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V5632108SP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08SP | [6 empty] | 0.99181 | 0.80904 | 0.92862 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V5662108SP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08SP | [6 empty] | 0.99178 | 0.83233 | 0.94881 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V5642108SP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08SP | [6 empty] | 0.99213 | 0.83693 | 0.95281 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V6412408SP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08SP | [6 empty] | 0.98111 | 0.89687 | 0.92889 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V6492408SP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08SP | [6 empty] | 0.98184 | 0.8978 | 0.92889 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V6741108SP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.94537 | 0.90732 | 0.93288 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V5191408SP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.95007 | 0.90782 | 0.93661 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V8171408SP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.94595 | 0.90788 | 0.93661 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V5652108SP |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 08SP | [6 empty] | 0.99755 | 0.91193 | 0.97173 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V6452408SP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08SP | [6 empty] | 0.98108 | 0.91778 | 0.94907 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V6522408SP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08SP | [6 empty] | 0.98182 | 0.91869 | 0.94907 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V6422408SP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08SP | [6 empty] | 0.98143 | 0.92192 | 0.95306 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V6502408SP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08SP | [6 empty] | 0.98217 | 0.92282 | 0.95306 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V6751108SP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 08SP | [6 empty] | 0.95906 | 0.92502 | 0.95977 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V5201408SP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 08SP | [6 empty] | 0.96363 | 0.92682 | 0.96213 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V8181408SP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 08SP | [6 empty] | 0.96041 | 0.92697 | 0.96213 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V5622108SP |  |  | ATHENS SWITCHING STATION 69KV | S | WERE |  | SEAST |  |  | 533623 | ATHENS 2 69.000 | [5 empty] | 08SP | [6 empty] | 0.99907 | 0.93047 | 0.97668 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V7612308SP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.96101 | 0.93257 | 0.97246 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V7622308SP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 08SP | [6 empty] | 0.96109 | 0.93265 | 0.97254 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V7592308SP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 08SP | [6 empty] | 0.96115 | 0.93377 | 0.97397 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V6442408SP |  |  | UNITED NO. 8 HUMBOLDT 69KV | S | WERE |  | SEAST |  |  | 533650 | UN8HUMB2 69.000 | [5 empty] | 08SP | [6 empty] | 0.97317 | 0.93955 | 0.98621 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V7572308SP |  |  | DEARING 138KV | S | WERE |  | SEAST |  |  | 533002 | DEARING4 138.00 | [5 empty] | 08SP | [6 empty] | 0.96349 | 0.94071 | 0.98072 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V6512408SP |  |  | UNITED NO. 8 HUMBOLDT 69KV | S | WERE |  | SEAST |  |  | 533650 | UN8HUMB2 69.000 | [5 empty] | 08SP | [6 empty] | 0.97423 | 0.94079 | 0.98621 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V6432408SP |  |  | UNITED NO. 1 ELSMORE 69KV | S | WERE |  | SEAST |  |  | 533647 | UN1ELSM2 69.000 | [5 empty] | 08SP | [6 empty] | 0.97597 | 0.94244 | 1.00474 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V6462408SP |  |  | ZILA JUNCTION 69KV | S | WERE |  | SEAST |  |  | 533654 | ZILAJCT2 69.000 | [5 empty] | 08SP | [6 empty] | 0.97632 | 0.94281 | 0.98932 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V4901108SP |  |  | NORTHEAST PARSONS 138KV | S | WERE |  | SEAST |  |  | 533005 | NEPARSN4 138.00 | [5 empty] | 08SP | [6 empty] | 0.98296 | 0.94298 | 0.98661 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533021 | NEOSHO 4 138.00 | 533005 | NEPARSN4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V5402208SP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.97056 | 0.94335 | 0.97494 | 0.95 | 1.05 | CATEGORYB | SINGLE | DEARING - MONTGOMERY 138KV CKT 1 | 0 | 533002 | DEARING4 138.00 | 533004 | MONTGOM4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V5412208SP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 08SP | [6 empty] | 0.97064 | 0.94344 | 0.97502 | 0.95 | 1.05 | CATEGORYB | SINGLE | DEARING - MONTGOMERY 138KV CKT 1 | 0 | 533002 | DEARING4 138.00 | 533004 | MONTGOM4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V5392208SP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 08SP | [6 empty] | 0.97079 | 0.94361 | 0.97683 | 0.95 | 1.05 | CATEGORYB | SINGLE | DEARING - MONTGOMERY 138KV CKT 1 | 0 | 533002 | DEARING4 138.00 | 533004 | MONTGOM4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V6532408SP |  |  | ZILA JUNCTION 69KV | S | WERE |  | SEAST |  |  | 533654 | ZILAJCT2 69.000 | [5 empty] | 08SP | [6 empty] | 0.97738 | 0.94405 | 0.98932 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V8812208SP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 08SP | [6 empty] | 0.9718 | 0.94506 | 0.97494 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-20 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V8822208SP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 08SP | [6 empty] | 0.97188 | 0.94515 | 0.97502 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-20 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V6402408SP |  |  | ALLEN 69KV | S | WERE |  | SEAST |  |  | 533621 | ALLEN 2 69.000 | [5 empty] | 08SP | [6 empty] | 0.97867 | 0.94527 | 0.98256 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V6482408SP |  |  | ALLEN 69KV | S | WERE |  | SEAST |  |  | 533621 | ALLEN 2 69.000 | [5 empty] | 08SP | [6 empty] | 0.97959 | 0.94634 | 0.98256 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V6891108SP |  |  | UNITED NO. 8 HUMBOLDT 69KV | S | WERE |  | SEAST |  |  | 533650 | UN8HUMB2 69.000 | [5 empty] | 08SP | [6 empty] | 0.97446 | 0.94847 | 0.98523 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V1211408WP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08WP | [6 empty] | 1.0023 | 0.87229 | 0.94225 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V1231408WP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08WP | [6 empty] | 1.0023 | 0.89035 | 0.95894 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V1221408WP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08WP | [6 empty] | 1.0025 | 0.89388 | 0.9622 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 1 | 2008-12-01 | 2007AG1AFS81V1433108WP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08WP | [6 empty] | 0.98507 | 0.92126 | 0.94257 | 0.95 | 1.05 | CATEGORYB | SINGLE | ENA - TIOGA 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V1642108WP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 08WP | [6 empty] | 0.98626 | 0.92165 | 0.94214 | 0.95 | 1.05 | CATEGORYB | SINGLE | ARCO TAP - ENA 69KV CKT 1 | 0 | 533634 | ENA 2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V1384108WP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08WP | [6 empty] | 0.96856 | 0.92242 | 0.95455 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V1261408WP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08WP | [6 empty] | 0.96145 | 0.92283 | 0.95476 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V1271408WP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 08WP | [6 empty] | 0.9617 | 0.92312 | 0.95476 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 1 | 2008-12-01 | 2007AG1AFS81V1453108WP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08WP | [6 empty] | 0.98504 | 0.93834 | 0.95926 | 0.95 | 1.05 | CATEGORYB | SINGLE | ENA - TIOGA 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V1662108WP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 08WP | [6 empty] | 0.98624 | 0.93872 | 0.95884 | 0.95 | 1.05 | CATEGORYB | SINGLE | ARCO TAP - ENA 69KV CKT 1 | 0 | 533634 | ENA 2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 1 | 2008-12-01 | 2007AG1AFS81V1443108WP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08WP | [6 empty] | 0.98529 | 0.94167 | 0.96252 | 0.95 | 1.05 | CATEGORYB | SINGLE | ENA - TIOGA 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533634 | ENA 2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V1652108WP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 08WP | [6 empty] | 0.98649 | 0.94205 | 0.9621 | 0.95 | 1.05 | CATEGORYB | SINGLE | ARCO TAP - ENA 69KV CKT 1 | 0 | 533634 | ENA 2 69.000 | 533620 | ARCOTAP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 1 | 2008-12-01 | 2007AG1AFS81V1423108WP |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 08WP | [6 empty] | 0.99825 | 0.94323 | 0.97902 | 0.95 | 1.05 | CATEGORYB | SINGLE | ATHENS SWITCHING STATION - OWL CREEK 69KV CKT 1 | 0 | 533623 | ATHENS 2 69.000 | 533642 | OWL CRK2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V1394108WP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 08WP | [6 empty] | 0.98252 | 0.94609 | 0.9771 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V2304108WP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 08WP | [6 empty] | 0.98063 | 0.94821 | 0.9771 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V5831409SP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 09SP | [6 empty] | 0.99267 | 0.80256 | 0.92634 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V5871409SP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 09SP | [6 empty] | 0.99264 | 0.82642 | 0.94695 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V5841409SP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 09SP | [6 empty] | 0.99299 | 0.83114 | 0.95103 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5894409SP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 09SP | [6 empty] | 0.98089 | 0.89457 | 0.92826 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5974409SP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 09SP | [6 empty] | 0.98165 | 0.89554 | 0.92826 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V7134109SP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 09SP | [6 empty] | 0.93638 | 0.90346 | 0.92884 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V8342109SP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 09SP | [6 empty] | 0.93998 | 0.9043 | 0.93181 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V5452109SP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 09SP | [6 empty] | 0.93942 | 0.90466 | 0.93181 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V5851409SP |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 09SP | [6 empty] | 0.99796 | 0.90811 | 0.96948 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5934409SP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 09SP | [6 empty] | 0.98086 | 0.91593 | 0.94883 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V6004409SP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 09SP | [6 empty] | 0.98162 | 0.91687 | 0.94883 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V7144109SP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 09SP | [6 empty] | 0.95069 | 0.9187 | 0.95683 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5904409SP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 09SP | [6 empty] | 0.98121 | 0.92015 | 0.9529 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5984409SP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 09SP | [6 empty] | 0.98198 | 0.92109 | 0.9529 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V8352109SP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 09SP | [6 empty] | 0.9548 | 0.92237 | 0.95863 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V5462109SP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 09SP | [6 empty] | 0.95412 | 0.92294 | 0.95863 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8872309SP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 09SP | [6 empty] | 0.95426 | 0.92539 | 0.96836 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8882309SP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 09SP | [6 empty] | 0.95435 | 0.92548 | 0.96844 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8852309SP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 09SP | [6 empty] | 0.95427 | 0.92624 | 0.96964 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V5821409SP |  |  | ATHENS SWITCHING STATION 69KV | S | WERE |  | SEAST |  |  | 533623 | ATHENS 2 69.000 | [5 empty] | 09SP | [6 empty] | 0.99942 | 0.92714 | 0.97442 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V8832309SP |  |  | DEARING 138KV | S | WERE |  | SEAST |  |  | 533002 | DEARING4 138.00 | [5 empty] | 09SP | [6 empty] | 0.95631 | 0.93232 | 0.97588 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V5404109SP |  |  | NORTHEAST PARSONS 138KV | S | WERE |  | SEAST |  |  | 533005 | NEPARSN4 138.00 | [5 empty] | 09SP | [6 empty] | 0.97987 | 0.9377 | 0.98649 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533021 | NEOSHO 4 138.00 | 533005 | NEPARSN4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5924409SP |  |  | UNITED NO. 8 HUMBOLDT 69KV | S | WERE |  | SEAST |  |  | 533650 | UN8HUMB2 69.000 | [5 empty] | 09SP | [6 empty] | 0.97298 | 0.93836 | 0.98616 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5994409SP |  |  | UNITED NO. 8 HUMBOLDT 69KV | S | WERE |  | SEAST |  |  | 533650 | UN8HUMB2 69.000 | [5 empty] | 09SP | [6 empty] | 0.97408 | 0.93964 | 0.98616 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5384409SP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 09SP | [6 empty] | 0.97014 | 0.94085 | 0.97185 | 0.95 | 1.05 | CATEGORYB | SINGLE | DEARING - MONTGOMERY 138KV CKT 1 | 0 | 533002 | DEARING4 138.00 | 533004 | MONTGOM4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5394409SP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 09SP | [6 empty] | 0.97022 | 0.94094 | 0.97193 | 0.95 | 1.05 | CATEGORYB | SINGLE | DEARING - MONTGOMERY 138KV CKT 1 | 0 | 533002 | DEARING4 138.00 | 533004 | MONTGOM4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5374409SP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 09SP | [6 empty] | 0.97041 | 0.94114 | 0.97395 | 0.95 | 1.05 | CATEGORYB | SINGLE | DEARING - MONTGOMERY 138KV CKT 1 | 0 | 533002 | DEARING4 138.00 | 533004 | MONTGOM4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5914409SP |  |  | UNITED NO. 1 ELSMORE 69KV | S | WERE |  | SEAST |  |  | 533647 | UN1ELSM2 69.000 | [5 empty] | 09SP | [6 empty] | 0.97577 | 0.94125 | 1.00421 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5944409SP |  |  | ZILA JUNCTION 69KV | S | WERE |  | SEAST |  |  | 533654 | ZILAJCT2 69.000 | [5 empty] | 09SP | [6 empty] | 0.97613 | 0.94163 | 0.98927 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V6014409SP |  |  | ZILA JUNCTION 69KV | S | WERE |  | SEAST |  |  | 533654 | ZILAJCT2 69.000 | [5 empty] | 09SP | [6 empty] | 0.97723 | 0.9429 | 0.98927 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5884409SP |  |  | ALLEN 69KV | S | WERE |  | SEAST |  |  | 533621 | ALLEN 2 69.000 | [5 empty] | 09SP | [6 empty] | 0.97849 | 0.9441 | 0.98284 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V5964409SP |  |  | ALLEN 69KV | S | WERE |  | SEAST |  |  | 533621 | ALLEN 2 69.000 | [5 empty] | 09SP | [6 empty] | 0.97943 | 0.9452 | 0.98284 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V7902409SP |  |  | UNITED NO. 8 HUMBOLDT 69KV | S | WERE |  | SEAST |  |  | 533650 | UN8HUMB2 69.000 | [5 empty] | 09SP | [6 empty] | 0.97478 | 0.94705 | 0.98465 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V9942309SP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 09SP | [6 empty] | 0.96845 | 0.94773 | 0.96964 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 4 | 2008-12-01 | 2007AG1AFS81V5861409SP |  |  | ORCHARD 69KV | S | WERE |  | SEAST |  |  | 533643 | ORCHARD2 69.000 | [5 empty] | 09SP | [6 empty] | 1.0014 | 0.94866 | 0.98299 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1503309WP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 09WP | [6 empty] | 0.99737 | 0.87101 | 0.94188 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1523309WP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 09WP | [6 empty] | 0.99734 | 0.88906 | 0.95855 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1513309WP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 09WP | [6 empty] | 0.9976 | 0.8926 | 0.96182 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V1594109WP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 09WP | [6 empty] | 0.9636 | 0.91758 | 0.95107 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 4 | 2008-12-01 | 2007AG1AFS81V1063409WP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 09WP | [6 empty] | 0.96419 | 0.91899 | 0.95082 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V1162409WP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 09WP | [6 empty] | 0.95983 | 0.92166 | 0.95281 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V1172409WP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 09WP | [6 empty] | 0.98648 | 0.92199 | 0.94308 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V1212409WP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 09WP | [6 empty] | 0.98738 | 0.92242 | 0.94308 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V1192409WP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 09WP | [6 empty] | 0.98646 | 0.93903 | 0.95973 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V1232409WP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 09WP | [6 empty] | 0.98735 | 0.93945 | 0.95973 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 4 | 2008-12-01 | 2007AG1AFS81V1724409WP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 09WP | [6 empty] | 0.97866 | 0.94093 | 0.97431 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V1182409WP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 09WP | [6 empty] | 0.98672 | 0.94237 | 0.963 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 4 | 2008-12-01 | 2007AG1AFS81V1073409WP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 09WP | [6 empty] | 0.97799 | 0.94251 | 0.97352 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V1222409WP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 09WP | [6 empty] | 0.98762 | 0.94279 | 0.963 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V8961112SP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.56419 | 0.94109 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9031112SP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.58308 | 0.95815 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12491112SP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.58852 | 0.95815 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9171112SP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.60886 | 0.97512 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9081112SP |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.61007 | 0.99865 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9001112SP |  |  | ATHENS SWITCHING STATION 69KV | S | WERE |  | SEAST |  |  | 533623 | ATHENS 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.61276 | 1.00456 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9041112SP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.61412 | 0.97857 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12631112SP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.61425 | 0.97512 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12541112SP |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.61573 | 0.99865 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9091112SP |  |  | ORCHARD 69KV | S | WERE |  | SEAST |  |  | 533643 | ORCHARD2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.61729 | 1.00395 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12461112SP |  |  | ATHENS SWITCHING STATION 69KV | S | WERE |  | SEAST |  |  | 533623 | ATHENS 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.61848 | 1.00456 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12501112SP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.6195 | 0.97857 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9271112SP |  |  | CHANUTE PLANT3 69KV | S | WERE |  | SEAST |  |  | 533665 | CHANP3 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.62259 | 0.9955 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9251112SP |  |  | CHANUTE PLANT1 69KV | S | WERE |  | SEAST |  |  | 533663 | CHANP1 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.62293 | 0.99572 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9261112SP |  |  | CHANUTE PLANT2 69KV | S | WERE |  | SEAST |  |  | 533664 | CHANP2 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.62293 | 0.99572 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12551112SP |  |  | ORCHARD 69KV | S | WERE |  | SEAST |  |  | 533643 | ORCHARD2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.62303 | 1.00395 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9191112SP |  |  | ASH GROVE1 69KV | S | WERE |  | SEAST |  |  | 533657 | ASHGRV12 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.62622 | 0.99784 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9151112SP |  |  | UNITED NO. 7 ROSE 69KV | S | WERE |  | SEAST |  |  | 533649 | UN7ROSE2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.6268 | 1.00579 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9211112SP |  |  | ASH GROVE JCT1 69KV | S | WERE |  | SEAST |  |  | 533659 | ASHGRJ12 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.62699 | 0.99833 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9231112SP |  |  | CHANUTE GENERATION TAP 69KV | S | WERE |  | SEAST |  |  | 533661 | CGENTAP2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.62722 | 0.99848 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9201112SP |  |  | ASH GROVE2 69KV | S | WERE |  | SEAST |  |  | 533658 | ASHGRV22 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.62751 | 0.99949 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9221112SP |  |  | ASH GROVE JCT2 69KV | S | WERE |  | SEAST |  |  | 533660 | ASHGRJ22 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.62828 | 0.99998 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12731112SP |  |  | CHANUTE PLANT3 69KV | S | WERE |  | SEAST |  |  | 533665 | CHANP3 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.62832 | 0.9955 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12711112SP |  |  | CHANUTE PLANT1 69KV | S | WERE |  | SEAST |  |  | 533663 | CHANP1 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.62866 | 0.99572 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12721112SP |  |  | CHANUTE PLANT2 69KV | S | WERE |  | SEAST |  |  | 533664 | CHANP2 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.62866 | 0.99572 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9241112SP |  |  | CHANUTE GENERATION SUB 69KV | S | WERE |  | SEAST |  |  | 533662 | CGENSUB2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.62959 | 1.0 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9281112SP |  |  | CHANUTE TAP 69KV | S | WERE |  | SEAST |  |  | 533666 | CHANTAP2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.63161 | 1.00181 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12651112SP |  |  | ASH GROVE1 69KV | S | WERE |  | SEAST |  |  | 533657 | ASHGRV12 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.63193 | 0.99784 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12611112SP |  |  | UNITED NO. 7 ROSE 69KV | S | WERE |  | SEAST |  |  | 533649 | UN7ROSE2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.63254 | 1.00579 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12671112SP |  |  | ASH GROVE JCT1 69KV | S | WERE |  | SEAST |  |  | 533659 | ASHGRJ12 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.63269 | 0.99833 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12691112SP |  |  | CHANUTE GENERATION TAP 69KV | S | WERE |  | SEAST |  |  | 533661 | CGENTAP2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.63292 | 0.99848 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12661112SP |  |  | ASH GROVE2 69KV | S | WERE |  | SEAST |  |  | 533658 | ASHGRV22 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.63323 | 0.99949 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12681112SP |  |  | ASH GROVE JCT2 69KV | S | WERE |  | SEAST |  |  | 533660 | ASHGRJ22 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.63399 | 0.99998 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9121112SP |  |  | TIOGA 69KV | S | WERE |  | SEAST |  |  | 533646 | TIOGA 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.63506 | 1.0078 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12701112SP |  |  | CHANUTE GENERATION SUB 69KV | S | WERE |  | SEAST |  |  | 533662 | CGENSUB2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.63529 | 1.0 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12741112SP |  |  | CHANUTE TAP 69KV | S | WERE |  | SEAST |  |  | 533666 | CHANTAP2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.6373 | 1.00181 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12581112SP |  |  | TIOGA 69KV | S | WERE |  | SEAST |  |  | 533646 | TIOGA 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.64078 | 1.0078 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9141112SP |  |  | UNITED NO. 6 URBANA 69KV | S | WERE |  | SEAST |  |  | 533648 | UN6URBA2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.65044 | 1.01031 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V10972412SP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 12SP | [6 empty] | 0.97877 | 0.65045 | 0.94092 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9011112SP |  |  | ENA 69KV | S | WERE |  | SEAST |  |  | 533634 | ENA 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.65276 | 0.9995 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V8971112SP |  |  | ARCO 69KV | S | WERE |  | SEAST |  |  | 533619 | ARCO 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.65372 | 0.99907 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V8981112SP |  |  | ARCO TAP 69KV | S | WERE |  | SEAST |  |  | 533620 | ARCOTAP2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.65392 | 0.9992 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12601112SP |  |  | UNITED NO. 6 URBANA 69KV | S | WERE |  | SEAST |  |  | 533648 | UN6URBA2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.65597 | 1.01031 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9071112SP |  |  | MONARCH 69KV | S | WERE |  | SEAST |  |  | 533641 | MONARCH2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.65598 | 0.99879 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12471112SP |  |  | ENA 69KV | S | WERE |  | SEAST |  |  | 533634 | ENA 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.65809 | 0.9995 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12431112SP |  |  | ARCO 69KV | S | WERE |  | SEAST |  |  | 533619 | ARCO 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.65904 | 0.99907 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12441112SP |  |  | ARCO TAP 69KV | S | WERE |  | SEAST |  |  | 533620 | ARCOTAP2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.65924 | 0.9992 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12531112SP |  |  | MONARCH 69KV | S | WERE |  | SEAST |  |  | 533641 | MONARCH2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.66126 | 0.99879 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9291112SP |  |  | CITY OF ERIE 69KV | S | WERE |  | SEAST |  |  | 533760 | ERIE 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.67095 | 1.02 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V8991112SP |  |  | ALLEN 69KV | S | WERE |  | SEAST |  |  | 533621 | ALLEN 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.67363 | 1.00104 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12751112SP |  |  | CITY OF ERIE 69KV | S | WERE |  | SEAST |  |  | 533760 | ERIE 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.67632 | 1.02 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12451112SP |  |  | ALLEN 69KV | S | WERE |  | SEAST |  |  | 533621 | ALLEN 2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.67868 | 1.00104 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11072412SP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 12SP | [6 empty] | 0.97874 | 0.68133 | 0.96239 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V10982412SP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 12SP | [6 empty] | 0.97911 | 0.68744 | 0.96663 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11062412SP |  |  | UNITED NO. 8 HUMBOLDT 69KV | S | WERE |  | SEAST |  |  | 533650 | UN8HUMB2 69.000 | [5 empty] | 12SP | [6 empty] | 0.9709 | 0.71327 | 0.99719 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11032412SP |  |  | UNITED NO. 1 ELSMORE 69KV | S | WERE |  | SEAST |  |  | 533647 | UN1ELSM2 69.000 | [5 empty] | 12SP | [6 empty] | 0.97368 | 0.717 | 1.01321 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9161112SP |  |  | UNITED NO. 8 HUMBOLDT 69KV | S | WERE |  | SEAST |  |  | 533650 | UN8HUMB2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.71715 | 0.99944 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11082412SP |  |  | ZILA JUNCTION 69KV | S | WERE |  | SEAST |  |  | 533654 | ZILAJCT2 69.000 | [5 empty] | 12SP | [6 empty] | 0.97406 | 0.71761 | 1.00027 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V10942412SP |  |  | ALLEN 69KV | S | WERE |  | SEAST |  |  | 533621 | ALLEN 2 69.000 | [5 empty] | 12SP | [6 empty] | 0.97643 | 0.72105 | 0.9963 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9181112SP |  |  | ZILA JUNCTION 69KV | S | WERE |  | SEAST |  |  | 533654 | ZILAJCT2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.72146 | 1.00251 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12621112SP |  |  | UNITED NO. 8 HUMBOLDT 69KV | S | WERE |  | SEAST |  |  | 533650 | UN8HUMB2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.72148 | 0.99944 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12641112SP |  |  | ZILA JUNCTION 69KV | S | WERE |  | SEAST |  |  | 533654 | ZILAJCT2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.72576 | 1.00251 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V10992412SP |  |  | MONARCH 69KV | S | WERE |  | SEAST |  |  | 533641 | MONARCH2 69.000 | [5 empty] | 12SP | [6 empty] | 0.97891 | 0.72923 | 0.99397 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V10922412SP |  |  | ARCO 69KV | S | WERE |  | SEAST |  |  | 533619 | ARCO 2 69.000 | [5 empty] | 12SP | [6 empty] | 0.98021 | 0.73208 | 0.99424 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V10932412SP |  |  | ARCO TAP 69KV | S | WERE |  | SEAST |  |  | 533620 | ARCOTAP2 69.000 | [5 empty] | 12SP | [6 empty] | 0.98034 | 0.73226 | 0.99438 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11002412SP |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 12SP | [6 empty] | 0.98913 | 0.73409 | 0.98839 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V10962412SP |  |  | ENA 69KV | S | WERE |  | SEAST |  |  | 533634 | ENA 2 69.000 | [5 empty] | 12SP | [6 empty] | 0.98128 | 0.73421 | 0.99467 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V10952412SP |  |  | ATHENS SWITCHING STATION 69KV | S | WERE |  | SEAST |  |  | 533623 | ATHENS 2 69.000 | [5 empty] | 12SP | [6 empty] | 0.99162 | 0.74577 | 0.99487 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11012412SP |  |  | ORCHARD 69KV | S | WERE |  | SEAST |  |  | 533643 | ORCHARD2 69.000 | [5 empty] | 12SP | [6 empty] | 0.99464 | 0.75613 | 0.99581 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11172412SP |  |  | CHANUTE PLANT3 69KV | S | WERE |  | SEAST |  |  | 533665 | CHANP3 2 69.000 | [5 empty] | 12SP | [6 empty] | 1.0056 | 0.76372 | 0.98304 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11152412SP |  |  | CHANUTE PLANT1 69KV | S | WERE |  | SEAST |  |  | 533663 | CHANP1 2 69.000 | [5 empty] | 12SP | [6 empty] | 1.0056 | 0.76401 | 0.98327 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11162412SP |  |  | CHANUTE PLANT2 69KV | S | WERE |  | SEAST |  |  | 533664 | CHANP2 2 69.000 | [5 empty] | 12SP | [6 empty] | 1.0056 | 0.76402 | 0.98327 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11192412SP |  |  | CITY OF ERIE 69KV | S | WERE |  | SEAST |  |  | 533760 | ERIE 2 69.000 | [5 empty] | 12SP | [6 empty] | 1.0038 | 0.76455 | 0.98401 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11092412SP |  |  | ASH GROVE1 69KV | S | WERE |  | SEAST |  |  | 533657 | ASHGRV12 69.000 | [5 empty] | 12SP | [6 empty] | 1.0056 | 0.76685 | 0.98546 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11042412SP |  |  | UNITED NO. 6 URBANA 69KV | S | WERE |  | SEAST |  |  | 533648 | UN6URBA2 69.000 | [5 empty] | 12SP | [6 empty] | 1.0036 | 0.76688 | 0.98574 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11112412SP |  |  | ASH GROVE JCT1 69KV | S | WERE |  | SEAST |  |  | 533659 | ASHGRJ12 69.000 | [5 empty] | 12SP | [6 empty] | 1.0056 | 0.7675 | 0.98597 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11132412SP |  |  | CHANUTE GENERATION TAP 69KV | S | WERE |  | SEAST |  |  | 533661 | CGENTAP2 69.000 | [5 empty] | 12SP | [6 empty] | 1.0056 | 0.7677 | 0.98613 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11142412SP |  |  | CHANUTE GENERATION SUB 69KV | S | WERE |  | SEAST |  |  | 533662 | CGENSUB2 69.000 | [5 empty] | 12SP | [6 empty] | 1.0056 | 0.76974 | 0.9877 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11102412SP |  |  | ASH GROVE2 69KV | S | WERE |  | SEAST |  |  | 533658 | ASHGRV22 69.000 | [5 empty] | 12SP | [6 empty] | 1.0057 | 0.77051 | 0.98827 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11122412SP |  |  | ASH GROVE JCT2 69KV | S | WERE |  | SEAST |  |  | 533660 | ASHGRJ22 69.000 | [5 empty] | 12SP | [6 empty] | 1.0057 | 0.77117 | 0.98878 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11182412SP |  |  | CHANUTE TAP 69KV | S | WERE |  | SEAST |  |  | 533666 | CHANTAP2 69.000 | [5 empty] | 12SP | [6 empty] | 1.0056 | 0.77259 | 0.98991 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11052412SP |  |  | UNITED NO. 7 ROSE 69KV | S | WERE |  | SEAST |  |  | 533649 | UN7ROSE2 69.000 | [5 empty] | 12SP | [6 empty] | 1.0008 | 0.77383 | 0.99946 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V10872412SP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 12SP | [6 empty] | 0.95969 | 0.77845 | 0.9212 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V10752112SP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 12SP | [6 empty] | 0.96022 | 0.78132 | 0.91953 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V11022412SP |  |  | TIOGA 69KV | S | WERE |  | SEAST |  |  | 533646 | TIOGA 2 69.000 | [5 empty] | 12SP | [6 empty] | 1.0061 | 0.78951 | 1.00284 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9131112SP |  |  | UNITED NO. 1 ELSMORE 69KV | S | WERE |  | SEAST |  |  | 533647 | UN1ELSM2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.84414 | 1.01051 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12591112SP |  |  | UNITED NO. 1 ELSMORE 69KV | S | WERE |  | SEAST |  |  | 533647 | UN1ELSM2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.84687 | 1.01051 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V9051112SP |  |  | MARMATON 69KV | S | WERE |  | SEAST |  |  | 533639 | MARMATN2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.872 | 1.01246 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12511112SP |  |  | MARMATON 69KV | S | WERE |  | SEAST |  |  | 533639 | MARMATN2 69.000 | [5 empty] | 12SP | [6 empty] | 1 | 0.87442 | 1.01246 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V10762112SP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 12SP | [6 empty] | 0.97968 | 0.89271 | 0.95606 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V10882412SP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 12SP | [6 empty] | 0.97966 | 0.89336 | 0.95637 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V14572412SP |  |  | MARMATON 69KV | S | WERE |  | SEAST |  |  | 533639 | MARMATN2 69.000 | [5 empty] | 12SP | [6 empty] | 0.9757 | 0.89612 | 1.01623 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V13302112SP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 12SP | [6 empty] | 0.95963 | 0.89804 | 0.95606 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15102312SP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 12SP | [6 empty] | 0.9556 | 0.90129 | 0.96206 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15112312SP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 12SP | [6 empty] | 0.9557 | 0.90139 | 0.96215 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15082312SP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 12SP | [6 empty] | 0.95478 | 0.90206 | 0.96306 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V15062312SP |  |  | DEARING 138KV | S | WERE |  | SEAST |  |  | 533002 | DEARING4 138.00 | [5 empty] | 12SP | [6 empty] | 0.95342 | 0.90925 | 0.96833 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V8951112SP |  |  | MARMTNE5 161KV | S | WERE |  | SEAST |  |  | 532934 | MARMTNE5 161.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.91678 | 0.99744 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 1 | 1 | 2008-12-01 | 2007AG1AFS81V12421112SP |  |  | MARMTNE5 161KV | S | WERE |  | SEAST |  |  | 532934 | MARMTNE5 161.00 | [5 empty] | 12SP | [6 empty] | 1 | 0.91761 | 0.99744 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V11312312SP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 12SP | [6 empty] | 0.97943 | 0.92227 | 0.96206 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V11322312SP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 12SP | [6 empty] | 0.97952 | 0.92237 | 0.96215 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V10792112SP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 12SP | [6 empty] | 0.98045 | 0.92308 | 0.96441 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V10802112SP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 12SP | [6 empty] | 0.98054 | 0.92318 | 0.9645 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V9162112SP |  |  | NORTHEAST PARSONS 138KV | S | WERE |  | SEAST |  |  | 533005 | NEPARSN4 138.00 | [5 empty] | 12SP | [6 empty] | 1.0066 | 0.92618 | 0.98581 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533021 | NEOSHO 4 138.00 | 533005 | NEPARSN4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V11302312SP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 12SP | [6 empty] | 0.97934 | 0.92661 | 0.96306 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V10782112SP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 12SP | [6 empty] | 0.98065 | 0.92767 | 0.96573 | 0.95 | 1.05 | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V1162412SP |  |  | DEARING 138KV | S | WERE |  | SEAST |  |  | 533002 | DEARING4 138.00 | [5 empty] | 12SP | [6 empty] | 0.95484 | 0.93271 | 0.97492 | 0.95 | 1.05 | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V11292312SP |  |  | DEARING 138KV | S | WERE |  | SEAST |  |  | 533002 | DEARING4 138.00 | [5 empty] | 12SP | [6 empty] | 0.9807 | 0.94632 | 0.96833 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1823312WP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 12WP | [6 empty] | 0.8913 | 0.45704 | 0.95214 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2133312WP |  |  | CHANUTE PLANT3 69KV | S | WERE |  | SEAST |  |  | 533665 | CHANP3 2 69.000 | [5 empty] | 12WP | [6 empty] | 1.003 | 0.49095 | 1.00517 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2113312WP |  |  | CHANUTE PLANT1 69KV | S | WERE |  | SEAST |  |  | 533663 | CHANP1 2 69.000 | [5 empty] | 12WP | [6 empty] | 1.003 | 0.49122 | 1.00533 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2123312WP |  |  | CHANUTE PLANT2 69KV | S | WERE |  | SEAST |  |  | 533664 | CHANP2 2 69.000 | [5 empty] | 12WP | [6 empty] | 1.003 | 0.49122 | 1.00533 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3713312WP |  |  | CHANUTE PLANT3 69KV | S | WERE |  | SEAST |  |  | 533665 | CHANP3 2 69.000 | [5 empty] | 12WP | [6 empty] | 0.99925 | 0.49237 | 1.00517 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3693312WP |  |  | CHANUTE PLANT1 69KV | S | WERE |  | SEAST |  |  | 533663 | CHANP1 2 69.000 | [5 empty] | 12WP | [6 empty] | 0.99925 | 0.49264 | 1.00533 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3703312WP |  |  | CHANUTE PLANT2 69KV | S | WERE |  | SEAST |  |  | 533664 | CHANP2 2 69.000 | [5 empty] | 12WP | [6 empty] | 0.99925 | 0.49264 | 1.00533 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2053312WP |  |  | ASH GROVE1 69KV | S | WERE |  | SEAST |  |  | 533657 | ASHGRV12 69.000 | [5 empty] | 12WP | [6 empty] | 1.003 | 0.49385 | 1.00693 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2073312WP |  |  | ASH GROVE JCT1 69KV | S | WERE |  | SEAST |  |  | 533659 | ASHGRJ12 69.000 | [5 empty] | 12WP | [6 empty] | 1.003 | 0.49447 | 1.00731 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2093312WP |  |  | CHANUTE GENERATION TAP 69KV | S | WERE |  | SEAST |  |  | 533661 | CGENTAP2 69.000 | [5 empty] | 12WP | [6 empty] | 1.003 | 0.49466 | 1.00742 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3633312WP |  |  | ASH GROVE1 69KV | S | WERE |  | SEAST |  |  | 533657 | ASHGRV12 69.000 | [5 empty] | 12WP | [6 empty] | 0.99925 | 0.49528 | 1.00693 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3653312WP |  |  | ASH GROVE JCT1 69KV | S | WERE |  | SEAST |  |  | 533659 | ASHGRJ12 69.000 | [5 empty] | 12WP | [6 empty] | 0.99925 | 0.49589 | 1.00731 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3673312WP |  |  | CHANUTE GENERATION TAP 69KV | S | WERE |  | SEAST |  |  | 533661 | CGENTAP2 69.000 | [5 empty] | 12WP | [6 empty] | 0.99925 | 0.49608 | 1.00742 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2103312WP |  |  | CHANUTE GENERATION SUB 69KV | S | WERE |  | SEAST |  |  | 533662 | CGENSUB2 69.000 | [5 empty] | 12WP | [6 empty] | 1.003 | 0.49656 | 1.00857 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2003312WP |  |  | UNITED NO. 6 URBANA 69KV | S | WERE |  | SEAST |  |  | 533648 | UN6URBA2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0016 | 0.49668 | 1.0087 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2153312WP |  |  | CITY OF ERIE 69KV | S | WERE |  | SEAST |  |  | 533760 | ERIE 2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0018 | 0.49709 | 1.00873 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2063312WP |  |  | ASH GROVE2 69KV | S | WERE |  | SEAST |  |  | 533658 | ASHGRV22 69.000 | [5 empty] | 12WP | [6 empty] | 1.0031 | 0.49721 | 1.00894 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2083312WP |  |  | ASH GROVE JCT2 69KV | S | WERE |  | SEAST |  |  | 533660 | ASHGRJ22 69.000 | [5 empty] | 12WP | [6 empty] | 1.0031 | 0.49783 | 1.00932 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3683312WP |  |  | CHANUTE GENERATION SUB 69KV | S | WERE |  | SEAST |  |  | 533662 | CGENSUB2 69.000 | [5 empty] | 12WP | [6 empty] | 0.99925 | 0.49799 | 1.00857 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3583312WP |  |  | UNITED NO. 6 URBANA 69KV | S | WERE |  | SEAST |  |  | 533648 | UN6URBA2 69.000 | [5 empty] | 12WP | [6 empty] | 0.99784 | 0.4981 | 1.0087 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3733312WP |  |  | CITY OF ERIE 69KV | S | WERE |  | SEAST |  |  | 533760 | ERIE 2 69.000 | [5 empty] | 12WP | [6 empty] | 0.99802 | 0.4985 | 1.00873 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3643312WP |  |  | ASH GROVE2 69KV | S | WERE |  | SEAST |  |  | 533658 | ASHGRV22 69.000 | [5 empty] | 12WP | [6 empty] | 0.99927 | 0.49864 | 1.00894 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3663312WP |  |  | ASH GROVE JCT2 69KV | S | WERE |  | SEAST |  |  | 533660 | ASHGRJ22 69.000 | [5 empty] | 12WP | [6 empty] | 0.99927 | 0.49925 | 1.00932 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2143312WP |  |  | CHANUTE TAP 69KV | S | WERE |  | SEAST |  |  | 533666 | CHANTAP2 69.000 | [5 empty] | 12WP | [6 empty] | 1.003 | 0.49929 | 1.01023 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3723312WP |  |  | CHANUTE TAP 69KV | S | WERE |  | SEAST |  |  | 533666 | CHANTAP2 69.000 | [5 empty] | 12WP | [6 empty] | 0.99924 | 0.50072 | 1.01023 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1893312WP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 12WP | [6 empty] | 1.006 | 0.51044 | 0.97067 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3473312WP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0017 | 0.51157 | 0.97067 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1983312WP |  |  | TIOGA 69KV | S | WERE |  | SEAST |  |  | 533646 | TIOGA 2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0033 | 0.51454 | 1.01926 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3563312WP |  |  | TIOGA 69KV | S | WERE |  | SEAST |  |  | 533646 | TIOGA 2 69.000 | [5 empty] | 12WP | [6 empty] | 0.99955 | 0.51596 | 1.01926 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2013312WP |  |  | UNITED NO. 7 ROSE 69KV | S | WERE |  | SEAST |  |  | 533649 | UN7ROSE2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0066 | 0.51642 | 1.01829 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3593312WP |  |  | UNITED NO. 7 ROSE 69KV | S | WERE |  | SEAST |  |  | 533649 | UN7ROSE2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0027 | 0.5178 | 1.01829 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1953312WP |  |  | ORCHARD 69KV | S | WERE |  | SEAST |  |  | 533643 | ORCHARD2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0111 | 0.51997 | 1.01745 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3533312WP |  |  | ORCHARD 69KV | S | WERE |  | SEAST |  |  | 533643 | ORCHARD2 69.000 | [5 empty] | 12WP | [6 empty] | 1.007 | 0.52128 | 1.01745 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1863312WP |  |  | ATHENS SWITCHING STATION 69KV | S | WERE |  | SEAST |  |  | 533623 | ATHENS 2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0161 | 0.52546 | 1.01811 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3443312WP |  |  | ATHENS SWITCHING STATION 69KV | S | WERE |  | SEAST |  |  | 533623 | ATHENS 2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0119 | 0.52673 | 1.01811 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1943312WP |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0131 | 0.52726 | 1.01213 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3523312WP |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0089 | 0.52849 | 1.01213 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2033312WP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0059 | 0.53769 | 0.98773 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3613312WP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0016 | 0.53881 | 0.98773 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1903312WP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0062 | 0.54304 | 0.99107 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3483312WP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0019 | 0.54416 | 0.99107 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1873312WP |  |  | ENA 69KV | S | WERE |  | SEAST |  |  | 533634 | ENA 2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0004 | 0.57422 | 1.01069 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3453312WP |  |  | ENA 69KV | S | WERE |  | SEAST |  |  | 533634 | ENA 2 69.000 | [5 empty] | 12WP | [6 empty] | 0.9962 | 0.57536 | 1.01069 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1833312WP |  |  | ARCO 69KV | S | WERE |  | SEAST |  |  | 533619 | ARCO 2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0002 | 0.57673 | 1.01028 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1843312WP |  |  | ARCO TAP 69KV | S | WERE |  | SEAST |  |  | 533620 | ARCOTAP2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0003 | 0.57687 | 1.01036 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3413312WP |  |  | ARCO 69KV | S | WERE |  | SEAST |  |  | 533619 | ARCO 2 69.000 | [5 empty] | 12WP | [6 empty] | 0.99601 | 0.57785 | 1.01028 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3423312WP |  |  | ARCO TAP 69KV | S | WERE |  | SEAST |  |  | 533620 | ARCOTAP2 69.000 | [5 empty] | 12WP | [6 empty] | 0.99609 | 0.57799 | 1.01036 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1933312WP |  |  | MONARCH 69KV | S | WERE |  | SEAST |  |  | 533641 | MONARCH2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0002 | 0.58129 | 1.00988 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3513312WP |  |  | MONARCH 69KV | S | WERE |  | SEAST |  |  | 533641 | MONARCH2 69.000 | [5 empty] | 12WP | [6 empty] | 0.99598 | 0.5824 | 1.00988 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1853312WP |  |  | ALLEN 69KV | S | WERE |  | SEAST |  |  | 533621 | ALLEN 2 69.000 | [5 empty] | 12WP | [6 empty] | 1.004 | 0.61001 | 1.01178 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3433312WP |  |  | ALLEN 69KV | S | WERE |  | SEAST |  |  | 533621 | ALLEN 2 69.000 | [5 empty] | 12WP | [6 empty] | 0.9997 | 0.61103 | 1.01178 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2023312WP |  |  | UNITED NO. 8 HUMBOLDT 69KV | S | WERE |  | SEAST |  |  | 533650 | UN8HUMB2 69.000 | [5 empty] | 12WP | [6 empty] | 1.004 | 0.67852 | 1.00982 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3603312WP |  |  | UNITED NO. 8 HUMBOLDT 69KV | S | WERE |  | SEAST |  |  | 533650 | UN8HUMB2 69.000 | [5 empty] | 12WP | [6 empty] | 0.99942 | 0.67933 | 1.00982 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V2043312WP |  |  | ZILA JUNCTION 69KV | S | WERE |  | SEAST |  |  | 533654 | ZILAJCT2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0062 | 0.68187 | 1.01207 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3623312WP |  |  | ZILA JUNCTION 69KV | S | WERE |  | SEAST |  |  | 533654 | ZILAJCT2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0017 | 0.68268 | 1.01207 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1993312WP |  |  | UNITED NO. 1 ELSMORE 69KV | S | WERE |  | SEAST |  |  | 533647 | UN1ELSM2 69.000 | [5 empty] | 12WP | [6 empty] | 1.014 | 0.82823 | 1.01655 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3573312WP |  |  | UNITED NO. 1 ELSMORE 69KV | S | WERE |  | SEAST |  |  | 533647 | UN1ELSM2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0091 | 0.82872 | 1.01655 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V2014212WP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0033 | 0.85015 | 0.95731 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1913312WP |  |  | MARMATON 69KV | S | WERE |  | SEAST |  |  | 533639 | MARMATN2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0157 | 0.85884 | 1.01769 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3493312WP |  |  | MARMATON 69KV | S | WERE |  | SEAST |  |  | 533639 | MARMATN2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0108 | 0.85927 | 1.01769 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V2044212WP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0033 | 0.86966 | 0.97462 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V2024212WP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0035 | 0.87348 | 0.97801 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V3594112WP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 12WP | [6 empty] | 0.97193 | 0.89516 | 0.93711 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V1994112WP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 12WP | [6 empty] | 0.97312 | 0.89543 | 0.93711 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V1813312WP |  |  | MARMTNE5 161KV | S | WERE |  | SEAST |  |  | 532934 | MARMTNE5 161.00 | [5 empty] | 12WP | [6 empty] | 1.0044 | 0.91209 | 0.99823 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V3403312WP |  |  | MARMTNE5 161KV | S | WERE |  | SEAST |  |  | 532934 | MARMTNE5 161.00 | [5 empty] | 12WP | [6 empty] | 1.0049 | 0.91227 | 0.99823 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V3604112WP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 12WP | [6 empty] | 0.98023 | 0.92191 | 0.96479 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V2004112WP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 12WP | [6 empty] | 0.98137 | 0.92197 | 0.96479 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V2974112WP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 12WP | [6 empty] | 0.98347 | 0.93505 | 0.96479 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 2 | 2008-12-01 | 2007AG1AFS81V2034212WP |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 12WP | [6 empty] | 1.0076 | 0.93555 | 0.99734 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V614112WP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 12WP | [6 empty] | 0.96701 | 0.94498 | 0.97736 | 0.95 | 1.05 | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V624112WP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 12WP | [6 empty] | 0.96707 | 0.94504 | 0.97742 | 0.95 | 1.05 | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V522212WP |  |  | DEARING 138KV | S | WERE |  | SEAST |  |  | 533002 | DEARING4 138.00 | [5 empty] | 12WP | [6 empty] | 0.96698 | 0.94566 | 0.98584 | 0.95 | 1.05 | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V532212WP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 12WP | [6 empty] | 0.97048 | 0.94578 | 0.98117 | 0.95 | 1.05 | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V3002112WP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 12WP | [6 empty] | 0.98481 | 0.94764 | 0.97773 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V3012112WP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 12WP | [6 empty] | 0.98487 | 0.9477 | 0.97779 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V3614112WP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 12WP | [6 empty] | 0.98626 | 0.94853 | 0.97736 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-20 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 4 | 1 | 2008-12-01 | 2007AG1AFS81V3624112WP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 12WP | [6 empty] | 0.98632 | 0.94859 | 0.97742 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-20 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V2992112WP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 12WP | [6 empty] | 0.98494 | 0.94942 | 0.97947 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12752317SP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 17SP | [6 empty] | 0.8767 | 0.81369 | 0.94449 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V14982117SP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.98247 | 0.81534 | 0.93789 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V15022117SP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 17SP | [6 empty] | 0.98244 | 0.83702 | 0.95669 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V14992117SP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 17SP | [6 empty] | 0.98284 | 0.84142 | 0.96051 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12812317SP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97705 | 0.86198 | 0.93855 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21052317SP |  |  | CITY OF IOLA 69KV | S | WERE |  | SEAST |  |  | 533637 | IOLA 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97757 | 0.86724 | 0.93855 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12902317SP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97702 | 0.88246 | 0.95734 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12822317SP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97743 | 0.88662 | 0.96116 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21142317SP |  |  | UNITED NO. 9 CONGER 69KV | S | WERE |  | SEAST |  |  | 533651 | UN9CONG2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97754 | 0.8876 | 0.95734 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21062317SP |  |  | LEHIGH TAP 69KV | S | WERE |  | SEAST |  |  | 533638 | LEHIGTP2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97795 | 0.89173 | 0.96116 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V19902117SP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 17SP | [6 empty] | 0.95113 | 0.89265 | 0.94414 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12842317SP |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97733 | 0.89539 | 0.98575 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12792317SP |  |  | ATHENS SWITCHING STATION 69KV | S | WERE |  | SEAST |  |  | 533623 | ATHENS 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97793 | 0.90032 | 0.99287 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21082317SP |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 17SP | [6 empty] | 0.9779 | 0.90078 | 0.98575 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12852317SP |  |  | ORCHARD 69KV | S | WERE |  | SEAST |  |  | 533643 | ORCHARD2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97912 | 0.90355 | 0.99461 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21032317SP |  |  | ATHENS SWITCHING STATION 69KV | S | WERE |  | SEAST |  |  | 533623 | ATHENS 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97852 | 0.90579 | 0.99287 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 4 | 2008-12-01 | 2007AG1AFS81V19942417SP |  |  | TIOGA 138KV | S | WERE |  | SEAST |  |  | 532996 | TIOGA 4 138.00 | [5 empty] | 17SP | [6 empty] | 0.96338 | 0.907 | 0.94771 | 0.95 | 1.05 | CATEGORYB | SINGLE | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V18283317SP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 17SP | [6 empty] | 0.95278 | 0.90724 | 0.96581 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V13002317SP |  |  | CHANUTE PLANT3 69KV | S | WERE |  | SEAST |  |  | 533665 | CHANP3 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.99002 | 0.90728 | 0.99482 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V18303317SP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 17SP | [6 empty] | 0.95421 | 0.90748 | 0.96565 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12982317SP |  |  | CHANUTE PLANT1 69KV | S | WERE |  | SEAST |  |  | 533663 | CHANP1 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.99002 | 0.90755 | 0.99506 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12992317SP |  |  | CHANUTE PLANT2 69KV | S | WERE |  | SEAST |  |  | 533664 | CHANP2 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.99002 | 0.90755 | 0.99506 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V18313317SP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 17SP | [6 empty] | 0.95432 | 0.9076 | 0.96576 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21092317SP |  |  | ORCHARD 69KV | S | WERE |  | SEAST |  |  | 533643 | ORCHARD2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97973 | 0.9091 | 0.99461 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 1 | 2008-12-01 | 2007AG1AFS81V18823117SP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 17SP | [6 empty] | 0.95846 | 0.90946 | 0.96537 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12922317SP |  |  | ASH GROVE1 69KV | S | WERE |  | SEAST |  |  | 533657 | ASHGRV12 69.000 | [5 empty] | 17SP | [6 empty] | 0.99002 | 0.91009 | 0.99738 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12882317SP |  |  | UNITED NO. 7 ROSE 69KV | S | WERE |  | SEAST |  |  | 533649 | UN7ROSE2 69.000 | [5 empty] | 17SP | [6 empty] | 0.98326 | 0.91031 | 0.9997 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12942317SP |  |  | ASH GROVE JCT1 69KV | S | WERE |  | SEAST |  |  | 533659 | ASHGRJ12 69.000 | [5 empty] | 17SP | [6 empty] | 0.99002 | 0.91068 | 0.99792 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12962317SP |  |  | CHANUTE GENERATION TAP 69KV | S | WERE |  | SEAST |  |  | 533661 | CGENTAP2 69.000 | [5 empty] | 17SP | [6 empty] | 0.99002 | 0.91086 | 0.99808 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V18263317SP |  |  | DEARING 138KV | S | WERE |  | SEAST |  |  | 533002 | DEARING4 138.00 | [5 empty] | 17SP | [6 empty] | 0.9489 | 0.91118 | 0.96684 | 0.95 | 1.05 | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12932317SP |  |  | ASH GROVE2 69KV | S | WERE |  | SEAST |  |  | 533658 | ASHGRV22 69.000 | [5 empty] | 17SP | [6 empty] | 0.98966 | 0.91118 | 0.99866 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12952317SP |  |  | ASH GROVE JCT2 69KV | S | WERE |  | SEAST |  |  | 533660 | ASHGRJ22 69.000 | [5 empty] | 17SP | [6 empty] | 0.98966 | 0.91178 | 0.99921 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12972317SP |  |  | CHANUTE GENERATION SUB 69KV | S | WERE |  | SEAST |  |  | 533662 | CGENSUB2 69.000 | [5 empty] | 17SP | [6 empty] | 0.99002 | 0.9127 | 0.99975 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21242317SP |  |  | CHANUTE PLANT3 69KV | S | WERE |  | SEAST |  |  | 533665 | CHANP3 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.99062 | 0.913 | 0.99482 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21222317SP |  |  | CHANUTE PLANT1 69KV | S | WERE |  | SEAST |  |  | 533663 | CHANP1 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.99062 | 0.91327 | 0.99506 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21232317SP |  |  | CHANUTE PLANT2 69KV | S | WERE |  | SEAST |  |  | 533664 | CHANP2 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.99062 | 0.91327 | 0.99506 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V15002117SP |  |  | OWL CREEK 69KV | S | WERE |  | SEAST |  |  | 533642 | OWL CRK2 69.000 | [5 empty] | 17SP | [6 empty] | 0.98925 | 0.91331 | 0.9853 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V13012317SP |  |  | CHANUTE TAP 69KV | S | WERE |  | SEAST |  |  | 533666 | CHANTAP2 69.000 | [5 empty] | 17SP | [6 empty] | 0.99038 | 0.91441 | 1.001 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21162317SP |  |  | ASH GROVE1 69KV | S | WERE |  | SEAST |  |  | 533657 | ASHGRV12 69.000 | [5 empty] | 17SP | [6 empty] | 0.99062 | 0.9158 | 0.99738 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21122317SP |  |  | UNITED NO. 7 ROSE 69KV | S | WERE |  | SEAST |  |  | 533649 | UN7ROSE2 69.000 | [5 empty] | 17SP | [6 empty] | 0.98389 | 0.91592 | 0.9997 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12862317SP |  |  | TIOGA 69KV | S | WERE |  | SEAST |  |  | 533646 | TIOGA 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.98695 | 0.91602 | 1.00434 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21182317SP |  |  | ASH GROVE JCT1 69KV | S | WERE |  | SEAST |  |  | 533659 | ASHGRJ12 69.000 | [5 empty] | 17SP | [6 empty] | 0.99062 | 0.91639 | 0.99792 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21202317SP |  |  | CHANUTE GENERATION TAP 69KV | S | WERE |  | SEAST |  |  | 533661 | CGENTAP2 69.000 | [5 empty] | 17SP | [6 empty] | 0.99062 | 0.91656 | 0.99808 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12802317SP |  |  | ENA 69KV | S | WERE |  | SEAST |  |  | 533634 | ENA 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97937 | 0.91664 | 0.98667 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12762317SP |  |  | ARCO 69KV | S | WERE |  | SEAST |  |  | 533619 | ARCO 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97896 | 0.91669 | 0.98586 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12772317SP |  |  | ARCO TAP 69KV | S | WERE |  | SEAST |  |  | 533620 | ARCOTAP2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97911 | 0.91685 | 0.98601 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21172317SP |  |  | ASH GROVE2 69KV | S | WERE |  | SEAST |  |  | 533658 | ASHGRV22 69.000 | [5 empty] | 17SP | [6 empty] | 0.99026 | 0.91688 | 0.99866 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12832317SP |  |  | MONARCH 69KV | S | WERE |  | SEAST |  |  | 533641 | MONARCH2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97876 | 0.91731 | 0.98501 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21192317SP |  |  | ASH GROVE JCT2 69KV | S | WERE |  | SEAST |  |  | 533660 | ASHGRJ22 69.000 | [5 empty] | 17SP | [6 empty] | 0.99026 | 0.91747 | 0.99921 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21212317SP |  |  | CHANUTE GENERATION SUB 69KV | S | WERE |  | SEAST |  |  | 533662 | CGENSUB2 69.000 | [5 empty] | 17SP | [6 empty] | 0.99062 | 0.91839 | 0.99975 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21252317SP |  |  | CHANUTE TAP 69KV | S | WERE |  | SEAST |  |  | 533666 | CHANTAP2 69.000 | [5 empty] | 17SP | [6 empty] | 0.99096 | 0.92009 | 1.001 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21042317SP |  |  | ENA 69KV | S | WERE |  | SEAST |  |  | 533634 | ENA 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97991 | 0.92161 | 0.98667 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21002317SP |  |  | ARCO 69KV | S | WERE |  | SEAST |  |  | 533619 | ARCO 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97949 | 0.92164 | 0.98586 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21102317SP |  |  | TIOGA 69KV | S | WERE |  | SEAST |  |  | 533646 | TIOGA 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.9876 | 0.92168 | 1.00434 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21012317SP |  |  | ARCO TAP 69KV | S | WERE |  | SEAST |  |  | 533620 | ARCOTAP2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97964 | 0.9218 | 0.98601 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21072317SP |  |  | MONARCH 69KV | S | WERE |  | SEAST |  |  | 533641 | MONARCH2 69.000 | [5 empty] | 17SP | [6 empty] | 0.97929 | 0.9222 | 0.98501 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12782317SP |  |  | ALLEN 69KV | S | WERE |  | SEAST |  |  | 533621 | ALLEN 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.98144 | 0.92452 | 0.98459 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21022317SP |  |  | ALLEN 69KV | S | WERE |  | SEAST |  |  | 533621 | ALLEN 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.98193 | 0.92916 | 0.98459 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 1 | 2008-12-01 | 2007AG1AFS81V14972117SP |  |  | ATHENS SWITCHING STATION 69KV | S | WERE |  | SEAST |  |  | 533623 | ATHENS 2 69.000 | [5 empty] | 17SP | [6 empty] | 0.99112 | 0.93108 | 0.99245 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V2122217SP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 17SP | [6 empty] | 0.95535 | 0.93316 | 0.96942 | 0.95 | 1.05 | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 1 | 2008-12-01 | 2007AG1AFS81V13373117SP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 17SP | [6 empty] | 0.98867 | 0.9335 | 0.96537 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 4 | 2008-12-01 | 2007AG1AFS81V19823417SP |  |  | ALTOONA 138KV | S | WERE |  | SEAST |  |  | 533001 | ALTOONA4 138.00 | [5 empty] | 17SP | [6 empty] | 0.98545 | 0.93376 | 0.96537 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-14 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12872317SP |  |  | UNITED NO. 6 URBANA 69KV | S | WERE |  | SEAST |  |  | 533648 | UN6URBA2 69.000 | [5 empty] | 17SP | [6 empty] | 1.0044 | 0.9338 | 1.00954 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V2132217SP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 17SP | [6 empty] | 0.95682 | 0.9339 | 0.96907 | 0.95 | 1.05 | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  | FDNS |  | FDNS |  | 2 | 2 | 2008-12-01 | 2007AG1AFS81V2142217SP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 17SP | [6 empty] | 0.95693 | 0.93401 | 0.96918 | 0.95 | 1.05 | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12892317SP |  |  | UNITED NO. 8 HUMBOLDT 69KV | S | WERE |  | SEAST |  |  | 533650 | UN8HUMB2 69.000 | [5 empty] | 17SP | [6 empty] | 0.98413 | 0.93422 | 0.98603 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12912317SP |  |  | ZILA JUNCTION 69KV | S | WERE |  | SEAST |  |  | 533654 | ZILAJCT2 69.000 | [5 empty] | 17SP | [6 empty] | 0.98725 | 0.9375 | 0.98914 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21132317SP |  |  | UNITED NO. 8 HUMBOLDT 69KV | S | WERE |  | SEAST |  |  | 533650 | UN8HUMB2 69.000 | [5 empty] | 17SP | [6 empty] | 0.98455 | 0.93815 | 0.98603 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21112317SP |  |  | UNITED NO. 6 URBANA 69KV | S | WERE |  | SEAST |  |  | 533648 | UN6URBA2 69.000 | [5 empty] | 17SP | [6 empty] | 1.0047 | 0.93939 | 1.00954 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V21152317SP |  |  | ZILA JUNCTION 69KV | S | WERE |  | SEAST |  |  | 533654 | ZILAJCT2 69.000 | [5 empty] | 17SP | [6 empty] | 0.98766 | 0.94142 | 0.98914 | 0.95 | 1.05 | CATEGORYB | SINGLE | TIOGA (TIOGA 1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532996 | TIOGA 4 138.00 | 533646 | TIOGA 2 69.000 | 533084 | TIOGA 1 13.200 | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V20033317SP |  |  | MONTGOMERY 138KV | S | WERE |  | SEAST |  |  | 533004 | MONTGOM4 138.00 | [5 empty] | 17SP | [6 empty] | 0.97016 | 0.94495 | 0.96581 | 0.95 | 1.05 | CATEGORYB | NONSINGLE | SPP-WERE-19 | 0 | 0 |  | 0 |  | 0 | [6 empty] | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V11663317SP |  |  | TAYLOR 138KV | S | WERE |  | SEAST |  |  | 533006 | TAYLOR 4 138.00 | [5 empty] | 17SP | [6 empty] | 0.98445 | 0.94496 | 0.96565 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 3 | 3 | 2008-12-01 | 2007AG1AFS81V11673317SP |  |  | TAYLOR JUNCTION 138KV | S | WERE |  | SEAST |  |  | 533007 | TAYLORJ4 138.00 | [5 empty] | 17SP | [6 empty] | 0.98455 | 0.94508 | 0.96576 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - NORTHEAST PARSONS 138KV CKT 1 | 0 | 533005 | NEPARSN4 138.00 | 533001 | ALTOONA4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01
2007-AG1 | AFS11 |  |  |  | FDNS |  | 2 | 3 | 2008-12-01 | 2007AG1AFS81V12742317SP |  |  | MARMTNE5 161KV | S | WERE |  | SEAST |  |  | 532934 | MARMTNE5 161.00 | [5 empty] | 17SP | [6 empty] | 0.99345 | 0.94916 | 0.98255 | 0.95 | 1.05 | CATEGORYB | SINGLE | ALTOONA - TIOGA 138KV CKT 1 | 0 | 533001 | ALTOONA4 138.00 | 532996 | TIOGA 4 138.00 | 0 |  | 1 |  |  |  |  | WERE | TIOGA 69KV Capacitor | Tioga 69 kV 15 MVAR Capacitor Addition | [12 empty] | 607500 | 2008-01-01 | [23 empty] | 2008-06-01 | 2010-06-01