## tblAllFacilityLog
STUDYDES | STUDYDES2 | EVENTTYPE | AssessmentSOLUTIONTYPE | AssessmenFDNS-TERMINATION | SOLUTIONTYPE | FDNS-TERMINATION | GROUP | SCENARIO | FGNAME | DIRECTION | FacilityName | FacilityUpgradeCode | ModelArea1 | ModelArea2 | FZONENAME | TZONENAME | MONTFLAG | MONTFB | MONTFNAME | MONTTB1 | MONTTNAME1 | MONTTB2 | MONTTNAME2 | MONTCKT | Case | SISRateA | SISRateB | STEPLoading | Assessment Loading | BaseCaseLoading | TransferCaseLoading | STEPVoltage | Assessment Voltage | BaseCaseVoltage | TransferCaseVoltage | VINIT | VMIN | VMAX | CATEGORY | CONTTYPE | CONTNAME | CONTXFMRFLAG | CONTFB | CONTFNAME | CONTTB1 | CONTTNAME1 | CONTTB2 | CONTTNAME2 | CONTCKT | RequiredRateB | TransmissionOwnerComments | OwnerDesignation | UpgradeName | UpgradeComponentWithinFacility | NewSummerA | NewSummerB | NewOtherA | NewOtherB | DistToConstruct | TotalLead | ConstructionLeadOnly | NewOrConstructWhileEnergized | NewR | NewX | NewB | CommentsRegardingUpgradeRequirements | NewCost | EffDate | NetPlantDate | ReusableEx_GrossValue | ReusableEx_NetValue | Reusable_EndofDepr | SalvageValue | NewCostWhileExpediting | EffDateExpedited | StartDeprExpedited | EndDeprExpedited | NetPlantDateExpedited | ReusableEx_GrossExpedited | ReusableEx_NetExpedited | Reusable_EndofDeprExpedited | SalvageValueExpedited | Generation 1 Owner & Unit (Name) | Generation 1 Redispatch Cost ($) | Generation 1 Redispatch Date (M/D/Y) | Generation 2 Owner & Unit (Name) | Generation 2 Redispatch Cost ($) | Generation 2 Redispatch Date (M/D/Y) | Generation 3 Owner & Unit (Name) | Generation 3 Redispatch Cost ($) | Generation 3 Redispatch Date (M/D/Y) | COD | EOC | EarliestDate
2007-AG2 | AFS9 | 0618 - Auburn Road 230-115kV XFMR | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T8003310SP | TO->FROM | 27TH & CROCO - TECUMSEH HILL 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533182 | TECHILE3 115.00 | 533187 | 27CROCO3 115.00 | 0 |  | 1 | 10SP | 68 | 68 | 131.3 | 130.4 | 131.3589 | 133.8329 | [7 empty] | CATEGORYB | SINGLE | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 |  |  | WERE | 27TH & CROCO - TECUMSEH HILL 115KV CKT 1 | Tear down and rebuild 2.72 mile Tecumseh Hill-27th & Croco 115 kV line as a single circuit. | 223 | 240 | 223 | 240 | 2.72 | 12 | 5 | N | 0.0016601 | 0.014656 | 0.0021654 | 240 MVA is breaker and CT limit. | 1147500 | 2008-01-01 | [23 empty] | 2010-06-01 | 2010-12-01 | 2010-10-01
2007-AG2 | AFS9 | 0618 - Auburn Road 230-115kV XFMR | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T8013310SP | TO->FROM | 27TH & CROCO - TECUMSEH HILL 115KV CKT 2 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533182 | TECHILE3 115.00 | 533187 | 27CROCO3 115.00 | 0 |  | 2 | 10SP | 92 | 92 | 115.6 | 114.8 | 115.6839 | 117.8627 | [7 empty] | CATEGORYB | SINGLE | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 |  |  | WERE | 27TH & CROCO - TECUMSEH HILL 115KV CKT 1 | Tear down and rebuild 2.72 mile Tecumseh Hill-27th & Croco 115 kV line as a single circuit. | 223 | 240 | 223 | 240 | 2.72 | 12 | 5 | N | 0.0016601 | 0.014656 | 0.0021654 | 240 MVA is breaker and CT limit. | 1147500 | 2008-01-01 | [23 empty] | 2010-06-01 | 2010-12-01 | 2010-10-01
2007-AG2 | AFS9 | 0618 - Auburn Road 230-115kV XFMR | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T8013310SP | TO->FROM | 27TH & CROCO - TECUMSEH HILL 115KV CKT 2 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533182 | TECHILE3 115.00 | 533187 | 27CROCO3 115.00 | 0 |  | 2 | 10SP | 92 | 92 | 115.6 | 114.8 | 115.6839 | 117.8627 | [7 empty] | CATEGORYB | SINGLE | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 |  |  | WERE | 27TH & CROCO - TECUMSEH HILL 115KV CKT 1 | Tear down and rebuild 2.72 mile Tecumseh Hill-27th & Croco 115 kV line as a single circuit. | 223 | 240 | 223 | 240 | 2.72 | 12 | 5 | N | 0.0016601 | 0.014656 | 0.0021654 | 240 MVA is breaker and CT limit. | 1147500 | 2008-01-01 | [23 empty] | 2010-06-01 | 2010-12-01 | 2010-10-01
2007-AG2 | AFS9 | 0618 - Auburn Road 230-115kV XFMR | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T7983310SP | FROM->TO | 27TH & CROCO JUNCTION - 41ST & CALIFORNIA 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533188 | 27CROCJ3 115.00 | 533160 | 41CALIF3 115.00 | 0 |  | 1 | 10SP | 68 | 68 | 119.4 | 118.5 | 119.6578 | 121.8709 | [7 empty] | CATEGORYB | SINGLE | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 |  |  | WERE | 27TH & CROCO - TECUMSEH HILL 115KV CKT 1 | Tear down and rebuild 2.72 mile Tecumseh Hill-27th & Croco 115 kV line as a single circuit. | 223 | 240 | 223 | 240 | 2.72 | 12 | 5 | N | 0.0016601 | 0.014656 | 0.0021654 | 240 MVA is breaker and CT limit. | 1147500 | 2008-01-01 | [23 empty] | 2010-06-01 | 2010-12-01 | 2010-10-01
2007-AG2 | AFS9 | 0618 - Auburn Road 230-115kV XFMR | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T7983310SP | FROM->TO | 27TH & CROCO JUNCTION - 41ST & CALIFORNIA 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533188 | 27CROCJ3 115.00 | 533160 | 41CALIF3 115.00 | 0 |  | 1 | 10SP | 68 | 68 | 119.4 | 118.5 | 119.6578 | 121.8709 | [7 empty] | CATEGORYB | SINGLE | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 |  |  | WERE | 27TH & CROCO JUNCTION - 41ST & CALIFORNIA 115KV CKT 1 | Tear down and rebuild 3.43 mile 27th & Croco-41ST & CALIFORNIA 115 kV line as a single circuit. | 223 | 240 | 223 | 240 | 3.43 | 12 | 5 | N | 0.0021952 | 0.01715 | 0.0028812 | 240 MVA is breaker and CT limit. | 1445000 | 2008-01-01 | [23 empty] | 2010-06-01 | 2011-12-01 | 2010-10-01
2007-AG2 | AFS9 | 0618 - Auburn Road 230-115kV XFMR | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T7993310SP | FROM->TO | 27TH & CROCO JUNCTION - 41ST & CALIFORNIA 115KV CKT 2 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533188 | 27CROCJ3 115.00 | 533160 | 41CALIF3 115.00 | 0 |  | 2 | 10SP | 92 | 92 | 104.2 | 103.4 | 104.4123 | 106.3433 | [7 empty] | CATEGORYB | SINGLE | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 |  |  | WERE | 27TH & CROCO JUNCTION - 41ST & CALIFORNIA 115KV CKT 1 | Tear down and rebuild 3.43 mile 27th & Croco-41ST & CALIFORNIA 115 kV line as a single circuit. | 223 | 240 | 223 | 240 | 3.43 | 12 | 5 | N | 0.0021952 | 0.01715 | 0.0028812 | 240 MVA is breaker and CT limit. | 1445000 | 2008-01-01 | [23 empty] | 2010-06-01 | 2011-12-01 | 2010-10-01
2007-AG2 | AFS9 | 0618 - Auburn Road 230-115kV XFMR | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T7993310SP | FROM->TO | 27TH & CROCO JUNCTION - 41ST & CALIFORNIA 115KV CKT 2 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533188 | 27CROCJ3 115.00 | 533160 | 41CALIF3 115.00 | 0 |  | 2 | 10SP | 92 | 92 | 104.2 | 103.4 | 104.4123 | 106.3433 | [7 empty] | CATEGORYB | SINGLE | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 |  |  | WERE | 27TH & CROCO JUNCTION - 41ST & CALIFORNIA 115KV CKT 1 | Tear down and rebuild 3.43 mile 27th & Croco-41ST & CALIFORNIA 115 kV line as a single circuit. | 223 | 240 | 223 | 240 | 3.43 | 12 | 5 | N | 0.0021952 | 0.01715 | 0.0028812 | 240 MVA is breaker and CT limit. | 1445000 | 2008-01-01 | [23 empty] | 2010-06-01 | 2011-12-01 | 2010-10-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 2 | 2007AG2AFS81T5303218SP | TO->FROM | 3RDST - ARKOMA 161KV CKT 1 | REL | OKGE | OKGE | FT SMITH | FT SMITH | 0 | 515306 | ARKOMA 5 161.00 | 515308 | 3RDST 5 161.00 | 0 |  | 1 | 18SP | 313 | 335 |  | 103.4 | 103.526 | 103.5428 | [7 empty] | CATEGORYB | SINGLE | AES - TARBY 161KV CKT 1 | 0 | 515262 | AES 5 161.00 | 515264 | TARBY 5 161.00 | 0 |  | 1 |  |  | OKGE | 3RDST - ARKOMA 161KV CKT 1 | Replace 8-1200A switches & 2-wave traps. | 313 | 359 | 404 | 418 |  | 14 | 10 | Y |  |  |  |  | 1300000 | 2008-07-29 | [23 empty] | 2017-06-01 | 2017-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 2 | 2007AG2AFS81T5323218SP | TO->FROM | 3RDST - ARKOMA 161KV CKT 1 | REL | OKGE | OKGE | FT SMITH | FT SMITH | 0 | 515306 | ARKOMA 5 161.00 | 515308 | 3RDST 5 161.00 | 0 |  | 1 | 18SP | 313 | 335 |  | 102.9 | 103.0308 | 103.0618 | [7 empty] | CATEGORYB | SINGLE | FT SMITH - QUANEX TAP 161KV CKT 1 | 0 | 515300 | FTSMTHE5 161.00 | 515310 | QUANXTP5 161.00 | 0 |  | 1 |  |  | OKGE | 3RDST - ARKOMA 161KV CKT 1 | Replace 8-1200A switches & 2-wave traps. | 313 | 359 | 404 | 418 |  | 14 | 10 | Y |  |  |  |  | 1300000 | 2008-07-29 | [23 empty] | 2017-06-01 | 2017-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 2 | 2007AG2AFS81T5393218SP | TO->FROM | 3RDST - ARKOMA 161KV CKT 1 | REL | OKGE | OKGE | FT SMITH | FT SMITH | 0 | 515306 | ARKOMA 5 161.00 | 515308 | 3RDST 5 161.00 | 0 |  | 1 | 18SP | 313 | 335 |  | 101.8 | 102.0064 | 102.0498 | [7 empty] | CATEGORYB | SINGLE | MASSARD - WHITESIDE 161KV CKT 1 | 0 | 515341 | WHITESD5 161.00 | 515343 | MASSARD5 161.00 | 0 |  | 1 |  |  | OKGE | 3RDST - ARKOMA 161KV CKT 1 | Replace 8-1200A switches & 2-wave traps. | 313 | 359 | 404 | 418 |  | 14 | 10 | Y |  |  |  |  | 1300000 | 2008-07-29 | [23 empty] | 2017-06-01 | 2017-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2007AG2AFS81T24865518SP | TO->FROM | 4FISHERTP 138.00 - KEYSTONE DAM 138KV CKT 1 | S | SWPA | AECI | EMINTH | KAMO-OK | 0 | 505610 | KEYSTON4 138.00 | 300131 | 4FISHERTP 138.00 | 0 |  | 1 | 18SP | 174 | 174 | 108.9 | 108.2 | 107.7419 | 105.7646 | [7 empty] | CATEGORYB | SINGLE | SILVER CITY - WEKIWA 138KV CKT 1 | 0 | 509757 | WEKIWA-4 138.00 | 300140 | 4SILVCTY 138.00 | 0 |  | 1 |  | Limit is AECI/KAMO line. SWPA equipment good for 223 MVA | AECI | 4FISHERTP 138.00 - KEYSTONE DAM 138KV CKT 1 | Upgrade this line |  |  |  |  | 4.26 | [7 empty] | 1300000 | [24 empty] | 2018-06-01 | 2018-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 4 | 1 | 2007AG2AFS81T4134118SP | FROM->TO | 5 TRIBES - HANCOCK 161KV CKT 1 | EXP | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515228 | 5TRIBES5 161.00 | 515250 | HANCOK-5 161.00 | 0 |  | 1 | 18SP | 223 | 223 | 110.2 | 107.8 | 106.3605 | 108.5169 | [7 empty] | CATEGORYB | SINGLE | AGENCY - PECAN CREEK 161KV CKT 1 | 0 | 515230 | AGENCY 5 161.00 | 515234 | PECANCK5 161.00 | 0 |  | 1 |  |  | OKGE | 5 TRIBES - HANCOCK 161KV CKT 1 | Replace 800A Wave Trap, increase Relay CTR to 1200-5A. | 272 | 312 | 335 | 335 |  | 12 | 8 | Y |  |  |  |  | 150000 | 2008-07-29 | [23 empty] | 2017-06-01 | 2017-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 4 | 1 | 2007AG2AFS81T4144118SP | FROM->TO | 5 TRIBES - HANCOCK 161KV CKT 1 | EXP | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515228 | 5TRIBES5 161.00 | 515250 | HANCOK-5 161.00 | 0 |  | 1 | 18SP | 223 | 223 | 104.0 | 101.4 | 99.7706 | 102.1205 | [7 empty] | CATEGORYB | SINGLE | AGENCY - EUCLID 161KV CKT 1 | 0 | 515230 | AGENCY 5 161.00 | 515251 | EUCLID 5 161.00 | 0 |  | 1 |  |  | OKGE | 5 TRIBES - HANCOCK 161KV CKT 1 | Replace 800A Wave Trap, increase Relay CTR to 1200-5A. | 272 | 312 | 335 | 335 |  | 12 | 8 | Y |  |  |  |  | 150000 | 2008-07-29 | [23 empty] | 2017-06-01 | 2017-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 4 | 1 | 2007AG2AFS81T4124118SP | TO->FROM | 5 TRIBES - PECAN CREEK 161KV CKT 1 | EXP | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515234 | PECANCK5 161.00 | 515228 | 5TRIBES5 161.00 | 0 |  | 1 | 18SP | 272 | 312 | 105.1 | 103.4 | 102.2012 | 103.9054 | [7 empty] | CATEGORYB | SINGLE | AGENCY - PECAN CREEK 161KV CKT 1 | 0 | 515230 | AGENCY 5 161.00 | 515234 | PECANCK5 161.00 | 0 |  | 1 |  |  | OKGE | 5 TRIBES - PECAN CREEK 161KV CKT 1 | Reconductor 4.07 miles of line to 1590AS52 and replace 2-wave traps, 1-161kV breaker, 3-switches @ Five Tribes & 5-switches, relaying @ Pecan Creek. | 471 | 542 | 558 | 558 | 4.07 | 20 | 12 |  | 0.00106 | 0.01081 | 0.00657 |  | 3000000 | 2008-07-29 | [23 empty] | 2018-06-01 | 2018-06-01
2006-AG1 | 2006-AG1 | [7 empty] | 53245532501SPP-AEPW-293216SP |  | ALUMAX TAP - BANN 138KV CKT 1 | U | AEPW | AEPW |  |  | 0 | 508049 | ALUMXT 4 138 | 508054 | BANN 4 138 | 0 |  | 1 | 16SP |  | 261 | [12 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | AEPW | ALUMAX TAP - BANN 138KV CKT 1 | Replace six (6) 138 kV switches, five at Bann & one at Alumax Tap. Rebuild 0.67 miles of 1024 ACAR with 2156 ACSR. Replace wavetrap & jumpers @ Bann. Replace breaker 3300 @ Bann. | 430 | 449 | 430 | 449 | 0.67 | 15 | 6 |  | 0.00018 | 0.002397 | 0.00081 | New limits are CTs and relay settings @ Bann | 1000000 | [24 empty] | 2008-06-01 | 2008-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T4192213SP | FROM->TO | AQUARIUS - HUDSON JUNCTION 69KV CKT 1 | REL | WERE | WERE | SEAST | SEAST | 0 | 533756 | AQUARS 2 69.000 | 533764 | HUDSJCT2 69.000 | 0 |  | 1 | 13SP | 72 | 72 | 100.5 | 103.9 | 103.9545 | 103.5412 | [7 empty] | CATEGORYB | SINGLE | LITCHFIELD - ROUSE 69KV CKT 1 | 0 | 533765 | LITCH 2 69.000 | 533771 | ROUSE 2 69.000 | 0 |  | 1 |  |  | WERE | LITCHFIELD - AQUARIUS - HUDSON JUNCTION 69KV CKT 1 | Replace 69 kV disconnect switches at Aquarius. | 80 | 80 | 80 | 80 |  | 12 | 12 | [5 empty] | 30000 | 2007-01-01 | [23 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 2 | 2007AG2AFS81T7173218SP | FROM->TO | AQUARIUS - HUDSON JUNCTION 69KV CKT 1 | REL | WERE | WERE | SEAST | SEAST | 0 | 533756 | AQUARS 2 69.000 | 533764 | HUDSJCT2 69.000 | 0 |  | 1 | 18SP | 72 | 72 | 106.8 | 111.3 | 109.4152 | 111.2553 | [7 empty] | CATEGORYB | SINGLE | LITCHFIELD - ROUSE 69KV CKT 1 | 0 | 533765 | LITCH 2 69.000 | 533771 | ROUSE 2 69.000 | 0 |  | 1 |  |  | WERE | AQUARIUS - HUDSON JUNCTION 69KV CKT 1 | Rebuild 0.72 miles | [11 empty] | 450k per mile | 324000 | 2008-01-01 | [23 empty] | 2018-06-01 | 2018-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 2 | 2007AG2AFS81T7173218SP | FROM->TO | AQUARIUS - HUDSON JUNCTION 69KV CKT 1 | REL | WERE | WERE | SEAST | SEAST | 0 | 533756 | AQUARS 2 69.000 | 533764 | HUDSJCT2 69.000 | 0 |  | 1 | 18SP | 72 | 72 | 106.8 | 111.3 | 109.4152 | 111.2553 | [7 empty] | CATEGORYB | SINGLE | LITCHFIELD - ROUSE 69KV CKT 1 | 0 | 533765 | LITCH 2 69.000 | 533771 | ROUSE 2 69.000 | 0 |  | 1 |  |  | WERE | LITCHFIELD - AQUARIUS - HUDSON JUNCTION 69KV CKT 1 | Replace 69 kV disconnect switches at Aquarius. | 80 | 80 | 80 | 80 |  | 12 | 12 | [5 empty] | 30000 | 2007-01-01 | [23 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T4202213SP | TO->FROM | AQUARIUS - LITCHFIELD 69KV CKT 1 | REL | WERE | WERE | SEAST | SEAST | 0 | 533765 | LITCH 2 69.000 | 533756 | AQUARS 2 69.000 | 0 |  | 1 | 13SP | 72 | 72 | 101.5 | 105 | 104.9791 | 104.5658 | [7 empty] | CATEGORYB | SINGLE | LITCHFIELD - ROUSE 69KV CKT 1 | 0 | 533765 | LITCH 2 69.000 | 533771 | ROUSE 2 69.000 | 0 |  | 1 |  |  | WERE | LITCHFIELD - AQUARIUS - HUDSON JUNCTION 69KV CKT 1 | Replace 69 kV disconnect switches at Aquarius. | 80 | 80 | 80 | 80 |  | 12 | 12 | [5 empty] | 30000 | 2007-01-01 | [23 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 2 | 2007AG2AFS81T7183218SP | TO->FROM | AQUARIUS - LITCHFIELD 69KV CKT 1 | REL | WERE | WERE | SEAST | SEAST | 0 | 533765 | LITCH 2 69.000 | 533756 | AQUARS 2 69.000 | 0 |  | 1 | 18SP | 72 | 72 | 107.8 | 112.2 | 110.3916 | 112.2447 | [7 empty] | CATEGORYB | SINGLE | LITCHFIELD - ROUSE 69KV CKT 1 | 0 | 533765 | LITCH 2 69.000 | 533771 | ROUSE 2 69.000 | 0 |  | 1 |  |  | WERE | AQUARIUS - LITCHFIELD 69KV CKT 1 | Rebuild 5.54 miles | [11 empty] | 450k per mile | 2493000 | 2008-01-01 | [23 empty] | 2018-06-01 | 2018-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 2 | 2007AG2AFS81T7183218SP | TO->FROM | AQUARIUS - LITCHFIELD 69KV CKT 1 | REL | WERE | WERE | SEAST | SEAST | 0 | 533765 | LITCH 2 69.000 | 533756 | AQUARS 2 69.000 | 0 |  | 1 | 18SP | 72 | 72 | 107.8 | 112.2 | 110.3916 | 112.2447 | [7 empty] | CATEGORYB | SINGLE | LITCHFIELD - ROUSE 69KV CKT 1 | 0 | 533765 | LITCH 2 69.000 | 533771 | ROUSE 2 69.000 | 0 |  | 1 |  |  | WERE | LITCHFIELD - AQUARIUS - HUDSON JUNCTION 69KV CKT 1 | Replace 69 kV disconnect switches at Aquarius. | 80 | 80 | 80 | 80 |  | 12 | 12 | [5 empty] | 30000 | 2007-01-01 | [23 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2007AG2AFS81T4575518SP | FROM->TO | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 | EXP | OKGE |  |  |  | 2 | 514908 | ARCADIA7 345.00 | 514907 | ARCADIA4 138.00 | 515703 | ARCADI21 13.800 | 1 | 18SP | 493 | 493 | 101.4 | 104 | 103.4286 | 101.9489 | [7 empty] | CATEGORYB | SINGLE | ARCADIA - NORTHWEST 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 514908 | ARCADIA7 345.00 | 0 |  | 1 |  |  | OKGE | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 | Add 3rd 345/138KV Auto and convert the 345kV and 138kV to a breaker and a half configuration. | [12 empty] | 13500000 | 2008-07-29 | [23 empty] | 2017-06-01 | 2017-06-01
2007-AG2 | AFS9 | ISLAND-LOAD |  |  | FDNS |  | 1 | 4 | 2007AG2AFS81T23551418SP | FROM->TO | ARSENAL HILL (ARSHILL2) 138/69/14.5KV TRANSFORMER CKT 2 | S | AEPW |  | SHREVEPO |  | 2 | 507711 | ARSHILL4 138.00 | 507710 | ARSHILL2 69.000 | 507714 | ARSH2-1 14.500 | 2 | 18SP | 200 | 240 |  |  | 97.568 | 100.1072 | [7 empty] | CATEGORYB | SINGLE | ARSENAL HILL (ARSHILL1) 138/69/12.47KV TRANSFORMER CKT 1 | 1 | 507710 | ARSHILL2 69.000 | 507711 | ARSHILL4 138.00 | 507712 | ARSH1-1 12.470 | 1 |  |  | AEPW | ARSENAL HILL (ARSHILL2) 138/69/14.5KV TRANSFORMER CKT 2 | Indeterminate Outside End of Term of all 3% or greater impacting reservations | [37 empty] | 2018-06-01 | 2018-06-01
GEN-2006-010 | Turk | [7 empty] | 507428507402012SP | TO->FROM | ASHDOWN REC (MILLWOOD) - OKAY 138KV CKT 1 | U | AEPW | AEPW | SARK | SARKAECC | 0 | 507428 | OKAY 4 138.00 | 507402 | ASHDWNR4 138.00 | 0 |  | 1 |  | 368 | 512 |  |  | 116 | [9 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | AEPW | ASHDOWN REC (MILLWOOD) - OKAY 138KV CKT 1 | Recunductor and convert line to 138 kV and replace switches at Ashdown REC | [12 empty] | 11100000 | [24 empty] | 2012-07-01 | 2012-07-01
GEN-2006-010 | Turk | [7 empty] | 507402507431012SP | FROM->TO | ASHDOWN REC (MILLWOOD) - PATTERSON 138KV CKT 1 | U | AEPW | AEPW | SARKAECC | SARK | 0 | 507402 | ASHDWNR4 138.00 | 507431 | PATTERS4 138.00 | 0 |  | 1 |  | 368 | 512 |  |  | 108.5 | [9 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | AEPW | ASHDOWN REC (MILLWOOD) - PATTERSON 138KV CKT 1 | Reconductor Line & Convert Line to 138 kV and convert Patterson station to breaker-and-a half cofiguration | [12 empty] | 6670000 | [24 empty] | 2012-07-01 | 2012-07-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T1702213SP | FROM->TO | ASHDOWN WEST - CRAIG JUNCTION 138KV CKT 1 | REL | AEPW | AEPW | SARKAECC | EASTERN | 0 | 504124 | ASHDWN_W 4 138.00 | 510890 | CRAIGJT4 138.00 | 0 |  | 1 | 13SP | 202 | 235 |  | 105.7 | 105.7044 | 105.9943 | [7 empty] | CATEGORYB | SINGLE | LYDIA - VALLIANT 345KV CKT 1 | 0 | 508298 | LYDIA 7 345.00 | 510911 | VALIANT7 345.00 | 0 |  | 1 |  |  | AEPW | ASHDOWN WEST - CRAIG JUNCTION 138KV CKT 1 | Rebuild 2.45 miles of 795 ACSR with 1590 ACSR and reset relays | 287 | 287 | 287 | 287 | 2.45 | 18 | 6 |  | 0.01434 | 0.13352 | 0.04001 | New limits would be a breaker at Craig Juntion and switches at both Craig Junction and Ashdown West | 2500000 | 2008-11-07 | [23 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T23412213SP | FROM->TO | ASHDOWN WEST - CRAIG JUNCTION 138KV CKT 1 | REL | AEPW | AEPW | SARKAECC | EASTERN | 0 | 504124 | ASHDWN_W 4 138.00 | 510890 | CRAIGJT4 138.00 | 0 |  | 1 | 13SP | 202 | 235 |  | 101.7 | 101.7604 | 102.1484 | [7 empty] | CATEGORYB | NONSINGLE | SPP-AEPW-01 | 0 | 0 |  | 0 |  | 0 |  |  |  |  | AEPW | ASHDOWN WEST - CRAIG JUNCTION 138KV CKT 1 | Rebuild 2.45 miles of 795 ACSR with 1590 ACSR and reset relays | 287 | 287 | 287 | 287 | 2.45 | 18 | 6 |  | 0.01434 | 0.13352 | 0.04001 | New limits would be a breaker at Craig Juntion and switches at both Craig Junction and Ashdown West | 2500000 | 2008-11-07 | [23 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 2 | 2 | 2007AG2AFS81T4462210SP | TO->FROM | ASHERVILLE - IDALIA 161KV CKT 1 | REL | SWPA | AECI | EMINTH | M&A | 0 | 505434 | IDALIA 5 161.00 | 300056 | 5ASHRVL 161.00 | 0 |  | 1 | 10SP | 206 | 206 |  |  | 96.9382 | 102.7936 | [7 empty] | CATEGORYB | SINGLE | GREEN FOREST - ST FRANCIS 1 161KV CKT 1 | 0 | 300084 | 5GRNFRT 161.00 | 300115 | 5STFRAN 161.00 | 0 |  | 1 |  |  | SWPA | ASHERVILLE - IDALIA 161KV CKT 1 SWPA | Reconductor line |  | 335 |  |  |  | 24 | 24 | [30 empty] | 2010-06-01 | 2011-06-01 | 2010-10-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T5392213SPG | TO->FROM | ASHERVILLE - IDALIA 161KV CKT 1 | REL | SWPA | AECI | EMINTH | M&A | 0 | 505434 | IDALIA 5 161.00 | 300056 | 5ASHRVL 161.00 | 0 |  | 1 | 13SP | 206 | 206 | 110.4 | 111.8 | 111.825 | 116.9376 | [7 empty] | CATEGORYB | SINGLE | GREEN FOREST - ST FRANCIS 1 161KV CKT 1 | 0 | 300084 | 5GRNFRT 161.00 | 300115 | 5STFRAN 161.00 | 0 |  | 1 |  |  | SWPA | ASHERVILLE - IDALIA 161KV CKT 1 SWPA | Reconductor line |  | 335 |  |  |  | 24 | 24 | [30 empty] | 2010-06-01 | 2011-06-01 | 2010-10-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T5192213SP | TO->FROM | ASHERVILLE - IDALIA 161KV CKT 1 | REL | SWPA | AECI | EMINTH | M&A | 0 | 505434 | IDALIA 5 161.00 | 300056 | 5ASHRVL 161.00 | 0 |  | 1 | 13SP | 206 | 206 |  | 101.6 | 101.6168 | 105.6348 | [7 empty] | CATEGORYB | SINGLE | WHITEWATER EAST - WILHELMINA 345KV CKT 1 | 0 | 300051 | 7WILHLM 345.00 | 300054 | 7GOBKNOB 345.00 | 0 |  | 1 |  |  | SWPA | ASHERVILLE - IDALIA 161KV CKT 1 SWPA | Reconductor line |  | 335 |  |  |  | 24 | 24 | [30 empty] | 2010-06-01 | 2011-06-01 | 2010-10-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 2 | 2 | 2007AG2AFS81T24092213SP | TO->FROM | ASHERVILLE - IDALIA 161KV CKT 1 | REL | SWPA | AECI | EMINTH | M&A | 0 | 505434 | IDALIA 5 161.00 | 300056 | 5ASHRVL 161.00 | 0 |  | 1 | 13SP | 206 | 206 |  |  | 98.0553 | 102.2787 | [7 empty] | CATEGORYB | NONSINGLE | AI32 | 0 | 0 |  | 0 |  | 0 |  |  |  |  | SWPA | ASHERVILLE - IDALIA 161KV CKT 1 SWPA | Reconductor line |  | 335 |  |  |  | 24 | 24 | [30 empty] | 2010-06-01 | 2011-06-01 | 2010-10-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 2 | 2 | 2007AG2AFS81T232213SPG | TO->FROM | ASHERVILLE - IDALIA 161KV CKT 1 | REL | SWPA | AECI | EMINTH | M&A | 0 | 505434 | IDALIA 5 161.00 | 300056 | 5ASHRVL 161.00 | 0 |  | 1 | 13SP | 206 | 206 |  |  | 96.6167 | 100.9705 | [7 empty] | CATEGORYB | GENOUT | GEN300010 1-ST FRANCIS UNIT 1 | 0 | 0 |  | 0 |  | 0 |  |  |  |  | SWPA | ASHERVILLE - IDALIA 161KV CKT 1 SWPA | Reconductor line |  | 335 |  |  |  | 24 | 24 | [30 empty] | 2010-06-01 | 2011-06-01 | 2010-10-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 2 | 2007AG2AFS81T9343218SP | TO->FROM | ASHERVILLE - IDALIA 161KV CKT 1 | REL | SWPA | AECI | EMINTH | M&A | 0 | 505434 | IDALIA 5 161.00 | 300056 | 5ASHRVL 161.00 | 0 |  | 1 | 18SP | 206 | 206 | 115.3 | 118.2 | 118.2533 | 123.3173 | [7 empty] | CATEGORYB | SINGLE | GREEN FOREST - ST FRANCIS 1 161KV CKT 1 | 0 | 300084 | 5GRNFRT 161.00 | 300115 | 5STFRAN 161.00 | 0 |  | 1 |  |  | SWPA | ASHERVILLE - IDALIA 161KV CKT 1 SWPA | Reconductor line |  | 335 |  |  |  | 24 | 24 | [30 empty] | 2010-06-01 | 2011-06-01 | 2010-10-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 2 | 2007AG2AFS81T9063218SP | TO->FROM | ASHERVILLE - IDALIA 161KV CKT 1 | REL | SWPA | AECI | EMINTH | M&A | 0 | 505434 | IDALIA 5 161.00 | 300056 | 5ASHRVL 161.00 | 0 |  | 1 | 18SP | 206 | 206 | 104.2 | 108.1 | 108.2148 | 112.2568 | [7 empty] | CATEGORYB | SINGLE | WHITEWATER EAST - WILHELMINA 345KV CKT 1 | 0 | 300051 | 7WILHLM 345.00 | 300054 | 7GOBKNOB 345.00 | 0 |  | 1 |  |  | SWPA | ASHERVILLE - IDALIA 161KV CKT 1 SWPA | Reconductor line |  | 335 |  |  |  | 24 | 24 | [30 empty] | 2010-06-01 | 2011-06-01 | 2010-10-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 2 | 2007AG2AFS81T40833218SP | TO->FROM | ASHERVILLE - IDALIA 161KV CKT 1 | REL | SWPA | AECI | EMINTH | M&A | 0 | 505434 | IDALIA 5 161.00 | 300056 | 5ASHRVL 161.00 | 0 |  | 1 | 18SP | 206 | 206 | 100.8 | 104.4 | 104.5073 | 108.7884 | [7 empty] | CATEGORYB | NONSINGLE | AI32 | 0 | 0 |  | 0 |  | 0 |  |  |  |  | SWPA | ASHERVILLE - IDALIA 161KV CKT 1 SWPA | Reconductor line |  | 335 |  |  |  | 24 | 24 | [30 empty] | 2010-06-01 | 2011-06-01 | 2010-10-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 2 | 2007AG2AFS81T303218SPG | TO->FROM | ASHERVILLE - IDALIA 161KV CKT 1 | REL | SWPA | AECI | EMINTH | M&A | 0 | 505434 | IDALIA 5 161.00 | 300056 | 5ASHRVL 161.00 | 0 |  | 1 | 18SP | 206 | 206 | 101.3 | 103.3 | 103.37 | 107.503 | [7 empty] | CATEGORYB | GENOUT | GEN300010 1-ST FRANCIS UNIT 1 | 0 | 0 |  | 0 |  | 0 |  |  |  |  | SWPA | ASHERVILLE - IDALIA 161KV CKT 1 SWPA | Reconductor line |  | 335 |  |  |  | 24 | 24 | [30 empty] | 2010-06-01 | 2011-06-01 | 2010-10-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T5402213SP | FROM->TO | ASHERVILLE - POPLAR BLUFF 161KV CKT 1 | REL | AECI | SWPA | M&A | EMINTH | 0 | 300056 | 5ASHRVL 161.00 | 505438 | POP BLF5 161.00 | 0 |  | 1 | 13SP | 167 | 167 | 106.5 | 108.4 | 108.3785 | 115.2973 | [7 empty] | CATEGORYB | SINGLE | GREEN FOREST - ST FRANCIS 1 161KV CKT 1 | 0 | 300084 | 5GRNFRT 161.00 | 300115 | 5STFRAN 161.00 | 0 |  | 1 |  |  | SWPA | ASHERVILLE - POPLAR BLUFF 161KV CKT 1 SWPA | Replace disconnect switches, replace some structures and resag line | [37 empty] | 2011-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 2 | 2007AG2AFS81T9353218SP | FROM->TO | ASHERVILLE - POPLAR BLUFF 161KV CKT 1 | REL | AECI | SWPA | M&A | EMINTH | 0 | 300056 | 5ASHRVL 161.00 | 505438 | POP BLF5 161.00 | 0 |  | 1 | 18SP | 167 | 167 | 110.4 | 114.6 | 114.6922 | 121.6092 | [7 empty] | CATEGORYB | SINGLE | GREEN FOREST - ST FRANCIS 1 161KV CKT 1 | 0 | 300084 | 5GRNFRT 161.00 | 300115 | 5STFRAN 161.00 | 0 |  | 1 |  |  | SWPA | ASHERVILLE - POPLAR BLUFF 161KV CKT 1 SWPA | Replace disconnect switches, replace some structures and resag line | [37 empty] | 2011-06-01 | 2011-06-01
2007-AG2 | AFS9 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 4 | 1 | 2007AG2AFS81T2704113SP | FROM->TO | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 13SP | 280 | 308 | 115.5 | 116.7 | 116.094 | 116.7421 | [7 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  | WERE | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 2 | Add second Auburn 230-115 kV transformer. | 280 | 308 | 280 | 308 |  | 12 | 2 | Y |  |  |  | See transformer #1 for NewR, NewX, NewB | 2250000 | 2004-06-24 | [23 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | 0623 - Hoyt 345-115kV Xfmr | FDNS |  | FDNS |  | 4 | 1 | 2007AG2AFS81T11414113SP | FROM->TO | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 13SP | 280 | 308 | 107.1 | 107.5 | 107.0754 | 107.4999 | [7 empty] | CATEGORYB | SINGLE | HOYT (HOYT 44X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532765 | HOYT 7 345.00 | 533163 | HOYT 3 115.00 | 532804 | HOYT 1 14.400 | 1 |  |  | WERE | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 2 | Add second Auburn 230-115 kV transformer. | 280 | 308 | 280 | 308 |  | 12 | 2 | Y |  |  |  | See transformer #1 for NewR, NewX, NewB | 2250000 | 2004-06-24 | [23 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | CONT-0900 - JEC - East Manhattan 230kV | FDNS |  | FDNS |  | 4 | 1 | 2007AG2AFS81T2774113SP | FROM->TO | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 13SP | 280 | 308 | 102.3 | 102.4 | 102.0408 | 102.1861 | [7 empty] | CATEGORYB | SINGLE | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 0 | 532852 | JEC 6 230.00 | 532861 | EMANHAT6 230.00 | 0 |  | 1 |  | Build SW Manhattan 230-115 kV substation; Convert SW Manhattan-McDowell Creek line to 230 kV operation; Convert McDowell-E Manhattan line to 230 kV operation; Build new SW Manhattan-E Manhattan 115 kV ilne | WERE | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 2 | Add second Auburn 230-115 kV transformer. | 280 | 308 | 280 | 308 |  | 12 | 2 | Y |  |  |  | See transformer #1 for NewR, NewX, NewB | 2250000 | 2004-06-24 | [23 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 2 | 1 | 2007AG2AFS81T4832118SP | FROM->TO | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 18SP | 280 | 308 | 119.6 | 123.5 | 123.9764 | 123.7154 | [7 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  | Directive 400 / Build 50-mile JEC-Swissvale 345 kV line | WERE | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 2 | Add second Auburn 230-115 kV transformer. | 280 | 308 | 280 | 308 |  | 12 | 2 | Y |  |  |  | See transformer #1 for NewR, NewX, NewB | 2250000 | 2004-06-24 | [23 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | 0623 - Hoyt 345-115kV Xfmr | FDNS |  | FDNS |  | 4 | 1 | 2007AG2AFS81T23144118SP | FROM->TO | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 18SP | 280 | 308 | 112.7 | 113.7 | 113.8267 | 113.7752 | [7 empty] | CATEGORYB | SINGLE | HOYT (HOYT 44X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532765 | HOYT 7 345.00 | 533163 | HOYT 3 115.00 | 532804 | HOYT 1 14.400 | 1 |  |  | WERE | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 2 | Add second Auburn 230-115 kV transformer. | 280 | 308 | 280 | 308 |  | 12 | 2 | Y |  |  |  | See transformer #1 for NewR, NewX, NewB | 2250000 | 2004-06-24 | [23 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | CONT-0900 - JEC - East Manhattan 230kV | FDNS |  | FDNS |  | 4 | 1 | 2007AG2AFS81T5104118SP | FROM->TO | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 18SP | 280 | 308 | 108.0 | 108.6 | 108.6091 | 108.3411 | [7 empty] | CATEGORYB | SINGLE | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 0 | 532852 | JEC 6 230.00 | 532861 | EMANHAT6 230.00 | 0 |  | 1 |  | Directive 400 / Build 50-mile JEC-Swissvale 345 kV line | WERE | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 2 | Add second Auburn 230-115 kV transformer. | 280 | 308 | 280 | 308 |  | 12 | 2 | Y |  |  |  | See transformer #1 for NewR, NewX, NewB | 2250000 | 2004-06-24 | [23 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | CONT-0633 - East Manhattan 230-115kV XFMR | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81T27442418SP | FROM->TO | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 18SP | 280 | 308 | 101.4 | 104.5 | 104.5925 | 104.5118 | [7 empty] | CATEGORYB | SINGLE | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 |  |  | WERE | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 2 | Add second Auburn 230-115 kV transformer. | 280 | 308 | 280 | 308 |  | 12 | 2 | Y |  |  |  | See transformer #1 for NewR, NewX, NewB | 2250000 | 2004-06-24 | [23 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 2 | 4 | 2007AG2AFS81T5872418SP | FROM->TO | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 18SP | 280 | 308 |  |  | 100.2982 | 100 | [7 empty] | CATEGORYB | SINGLE | AUBURN ROAD - SWISSVALE 230KV CKT 1 | 0 | 532851 | AUBURN 6 230.00 | 532856 | SWISVAL6 230.00 | 0 |  | 1 |  |  | WERE | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 2 | Add second Auburn 230-115 kV transformer. | 280 | 308 | 280 | 308 |  | 12 | 2 | Y |  |  |  | See transformer #1 for NewR, NewX, NewB | 2250000 | 2004-06-24 | [23 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2007AG2AFS81T1885509SP | FROM->TO | BAILEYVILLE N.M. STATION (NEMAHA MARSHALL R - SMITTYVILLE N.M. COOP (NEMAHA MARSHALL R.E. 115KV CKT 1 | EXP | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533322 | BAILEYV3 115.00 | 533338 | SMITTYV3 115.00 | 0 |  | 1 | 09SP | 92 | 92 |  |  | 104.9414 | 104.9414 | [7 empty] | CATEGORYB | SINGLE | CONCORDIA - ELMCREK6 230.00 230KV CKT 1 | 0 | 539639 | ELMCREK6 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [23 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2007-AG2 | AFS9 | ISLAND-LOAD |  |  | FDNS |  | 5 | 5 | 2007AG2AFS81T6905509SP | FROM->TO | BAILEYVILLE N.M. STATION (NEMAHA MARSHALL R - SMITTYVILLE N.M. COOP (NEMAHA MARSHALL R.E. 115KV CKT 1 | EXP | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533322 | BAILEYV3 115.00 | 533338 | SMITTYV3 115.00 | 0 |  | 1 | 09SP | 92 | 92 |  |  | 104.9369 | 104.9373 | [7 empty] | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539657 | CONCORD3 115.00 | 539658 | CONCRD6 230.00 | 539904 | CONCOD-T 13.800 | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [23 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2007AG2AFS81T1405509SP | FROM->TO | BAILEYVILLE N.M. STATION (NEMAHA MARSHALL R - SMITTYVILLE N.M. COOP (NEMAHA MARSHALL R.E. 115KV CKT 1 | EXP | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533322 | BAILEYV3 115.00 | 533338 | SMITTYV3 115.00 | 0 |  | 1 | 09SP | 92 | 92 |  |  | 104.5999 | 104.579 | [7 empty] | CATEGORYB | SINGLE | EAST MANHATTAN - ELMCREK6 230.00 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 539639 | ELMCREK6 230.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [23 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2007AG2AFS81T1875509SP | TO->FROM | BAILEYVILLE N.M. STATION (NEMAHA MARSHALL R - SOUTH SENECA 115KV CKT 1 | EXP | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533337 | SENECA 3 115.00 | 533322 | BAILEYV3 115.00 | 0 |  | 1 | 09SP | 92 | 92 |  |  | 107.4636 | 107.4682 | [7 empty] | CATEGORYB | SINGLE | CONCORDIA - ELMCREK6 230.00 230KV CKT 1 | 0 | 539639 | ELMCREK6 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [23 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2007-AG2 | AFS9 | ISLAND-LOAD |  |  | FDNS |  | 5 | 5 | 2007AG2AFS81T6895509SP | TO->FROM | BAILEYVILLE N.M. STATION (NEMAHA MARSHALL R - SOUTH SENECA 115KV CKT 1 | EXP | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533337 | SENECA 3 115.00 | 533322 | BAILEYV3 115.00 | 0 |  | 1 | 09SP | 92 | 92 |  |  | 107.4588 | 107.464 | [7 empty] | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539657 | CONCORD3 115.00 | 539658 | CONCRD6 230.00 | 539904 | CONCOD-T 13.800 | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [23 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2007AG2AFS81T1395509SP | TO->FROM | BAILEYVILLE N.M. STATION (NEMAHA MARSHALL R - SOUTH SENECA 115KV CKT 1 | EXP | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533337 | SENECA 3 115.00 | 533322 | BAILEYV3 115.00 | 0 |  | 1 | 09SP | 92 | 92 |  |  | 107.1017 | 107.0874 | [7 empty] | CATEGORYB | SINGLE | EAST MANHATTAN - ELMCREK6 230.00 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 539639 | ELMCREK6 230.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [23 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
GEN-2006-010 | Turk | [7 empty] | 508054508075012SP | FROM->TO | BANN - RED SPRINGS REC 138KV CKT 1 | U | AEPW | AEPW | TEXARK | TXARNTEC | 0 | 508054 | BANN 4 138.00 | 508075 | REDSPRG4 138.00 | 0 |  | 1 |  | 224 | 261 |  |  | 72.8 | [9 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | AEPW | BANN - RED SPRINGS REC 138KV CKT 1 | Replace 138 kV breakers 3300 & 3310 | [12 empty] | 300000 | [24 empty] | 2012-07-01 | 2012-07-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T433309SH | FROM->TO | BARTLESVILLE SOUTHEAST - NORTH BARTLESVILLE 138KV CKT 1 | CP | AEPW | AEPW | NORTHERN | TS-KAMO | 0 | 510391 | BV-SE--4 138.00 | 510386 | NBVILLE4 138.00 | 0 |  | 1 | 09SH | 202 | 235 |  | 102.3 | 104.8198 | 105.3666 | [7 empty] | CATEGORYB | SINGLE | DELAWARE - NORTHEAST STATION 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 510406 | N.E.S.-7 345.00 | 0 |  | 1 |  |  | AEPW | BARTLESVILLE SOUTHEAST - NORTH BARTLESVILLE 138KV CKT 1 | Rebuild 8.37 miles of 795 ACSR with 1590 ACSR & reset relays @ BSE | 280 | 287 | 287 | 287 | 8.37 | 24 | 9 |  | 0.00286 | 0.030814 | 0.0097 | New limits will be wavetrap jumpers, breakers & switches | 8400000 | 2007-08-13 | [23 empty] | 2009-06-01 | 2011-06-01
2007-AG2 | AFS9 | CONT-1211 - Mockingbird Hill - SW Lawrence 115kV | FDNS |  | FDNS |  | 4 | 3 | 2007AG2AFS81T2024310SP | FROM->TO | BISMARK JUNCTION SWITCHING STATION - FARMERS CONSUMER CO-OP 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533234 | BISMARK3 115.00 | 533236 | COOP 3 115.00 | 0 |  | 1 | 10SP | 118 | 118 | 108.0 | 110.3 | 110.3008 | 110.4449 | [7 empty] | CATEGORYB | SINGLE | MOCKINGBIRD HILL SWITCHING STATION - SOUTHWEST LAWRENCE 115KV CKT 1 | 0 | 533253 | MOCKBRD3 115.00 | 533271 | SWLWRNC3 115.00 | 0 |  | 1 |  |  | WERE | BISMARK JUNCTION SWITCHING STATION - FARMERS CONSUMER CO-OP 115KV CKT 1 | Rebuild 2.9 mi 115 kV line Bismark to COOP | [5 empty] | 18 | [6 empty] | 2085000 | 2009-01-01 | [23 empty] | 2010-06-01 | 2011-06-01 | 2010-10-01
2007-AG2 | AFS9 | CONT-1211 - Mockingbird Hill - SW Lawrence 115kV | FDNS |  | FDNS |  | 4 | 3 | 2007AG2AFS81T2904313SP | FROM->TO | BISMARK JUNCTION SWITCHING STATION - FARMERS CONSUMER CO-OP 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533234 | BISMARK3 115.00 | 533236 | COOP 3 115.00 | 0 |  | 1 | 13SP | 118 | 118 | 107.8 | 109.7 | 109.8119 | 109.8399 | [7 empty] | CATEGORYB | SINGLE | MOCKINGBIRD HILL SWITCHING STATION - SOUTHWEST LAWRENCE 115KV CKT 1 | 0 | 533253 | MOCKBRD3 115.00 | 533271 | SWLWRNC3 115.00 | 0 |  | 1 |  |  | WERE | BISMARK JUNCTION SWITCHING STATION - FARMERS CONSUMER CO-OP 115KV CKT 1 | Rebuild 2.9 mi 115 kV line Bismark to COOP | [5 empty] | 18 | [6 empty] | 2085000 | 2009-01-01 | [23 empty] | 2010-06-01 | 2011-06-01 | 2010-10-01
2007-AG2 | AFS9 | CONT-1211 - Mockingbird Hill - SW Lawrence 115kV | FDNS |  | FDNS |  | 2 | 3 | 2007AG2AFS81T5372318SP | FROM->TO | BISMARK JUNCTION SWITCHING STATION - FARMERS CONSUMER CO-OP 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533234 | BISMARK3 115.00 | 533236 | COOP 3 115.00 | 0 |  | 1 | 18SP | 118 | 118 | 110.9 | 112.7 | 113.0058 | 112.9077 | [7 empty] | CATEGORYB | SINGLE | MOCKINGBIRD HILL SWITCHING STATION - SOUTHWEST LAWRENCE 115KV CKT 1 | 0 | 533253 | MOCKBRD3 115.00 | 533271 | SWLWRNC3 115.00 | 0 |  | 1 |  |  | WERE | BISMARK JUNCTION SWITCHING STATION - FARMERS CONSUMER CO-OP 115KV CKT 1 | Rebuild 2.9 mi 115 kV line Bismark to COOP | [5 empty] | 18 | [6 empty] | 2085000 | 2009-01-01 | [23 empty] | 2010-06-01 | 2011-06-01 | 2010-10-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81V4052410SP |  | BLANCHARD 69KV | EXP | WFEC |  | FLA |  |  | 520828 | BLANCHD2 69.000 | [5 empty] | 10SP | [6 empty] | 0.76994 | 0.77083 | 0.77088 | 0.77067 | 1.0175 | 0.9 | 1.05 | CATEGORYB | SINGLE | OU SW 4 138.00 (OW SW) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 521104 | OU SW 4 138.00 | 521018 | OU SW 2 69.000 | 521183 | OUSWTERT 13.800 | 1 |  |  | WFEC | Norman Area Voltage Conversion | Convert Canadian - OU - Cole - Criner to 138 KV and Canadian-Goldsby-OU-W Norman-Acme-Franklin | [5 empty] | 24 | 18 | [5 empty] | 4000000 | 2007-04-13 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 2 | 2007AG2AFS81V15293218SP |  | BLANCHARD 69KV | EXP | WFEC |  | FLA |  |  | 520828 | BLANCHD2 69.000 | [5 empty] | 18SP | [6 empty] | 0.63993 | 0.64213 | 0.63811 | 0.6381 | 0.98166 | 0.9 | 1.05 | CATEGORYB | SINGLE | OU SW 4 138.00 (OW SW) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 521104 | OU SW 4 138.00 | 521018 | OU SW 2 69.000 | 521183 | OUSWTERT 13.800 | 1 |  |  | WFEC | Norman Area Voltage Conversion | Convert Canadian - OU - Cole - Criner to 138 KV and Canadian-Goldsby-OU-W Norman-Acme-Franklin | [5 empty] | 24 | 18 | [5 empty] | 4000000 | 2007-04-13 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 3 | 2007AG2AFS81T914309FA | TO->FROM | BPU - CITY OF MCPHERSON JOHNS-MANVILLE - EAST MCPHERSON SWITCHING STATION 115KV CKT 1 | REL | WERE | WERE | WEST | WEST | 0 | 533417 | EMCPHER3 115.00 | 533426 | MANVILE3 115.00 | 0 |  | 1 | 09FA | 84 | 84 |  |  | 102.4044 | 103.7478 | [7 empty] | CATEGORYB | SINGLE | EAST MCPHERSON SWITCHING STATION - REFINRY3 115.00 115KV CKT 1 | 0 | 533417 | EMCPHER3 115.00 | 533427 | REFINRY3 115.00 | 0 |  | 1 |  |  | WERE | BPU - CITY OF MCPHERSON JOHNS-MANVILLE - EAST MCPHERSON SWITCHING STATION 115KV CKT 1 | Rebuild Line | 248 | 248 |  |  | 5.7 | 24 | 24 |  | 0.00392 | 0.03057 | 0.00456 | Line owned by City of McPherson Board of Public Utilities | [25 empty] | 2009-06-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 3 | 2007AG2AFS81T1454309SH | TO->FROM | BPU - CITY OF MCPHERSON JOHNS-MANVILLE - EAST MCPHERSON SWITCHING STATION 115KV CKT 1 | REL | WERE | WERE | WEST | WEST | 0 | 533417 | EMCPHER3 115.00 | 533426 | MANVILE3 115.00 | 0 |  | 1 | 09SH | 84 | 84 |  |  | 102.0423 | 103.1018 | [7 empty] | CATEGORYB | SINGLE | EAST MCPHERSON SWITCHING STATION - REFINRY3 115.00 115KV CKT 1 | 0 | 533417 | EMCPHER3 115.00 | 533427 | REFINRY3 115.00 | 0 |  | 1 |  |  | WERE | BPU - CITY OF MCPHERSON JOHNS-MANVILLE - EAST MCPHERSON SWITCHING STATION 115KV CKT 1 | Rebuild Line | 248 | 248 |  |  | 5.7 | 24 | 24 |  | 0.00392 | 0.03057 | 0.00456 | Line owned by City of McPherson Board of Public Utilities | [25 empty] | 2009-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 4 | 3 | 2007AG2AFS81T2034309SP | TO->FROM | BPU - CITY OF MCPHERSON JOHNS-MANVILLE - EAST MCPHERSON SWITCHING STATION 115KV CKT 1 | REL | WERE | WERE | WEST | WEST | 0 | 533417 | EMCPHER3 115.00 | 533426 | MANVILE3 115.00 | 0 |  | 1 | 09SP | 84 | 84 | 106.2 | 105.2 | 109.9321 | 110.918 | [7 empty] | CATEGORYB | SINGLE | EAST MCPHERSON SWITCHING STATION - REFINRY3 115.00 115KV CKT 1 | 0 | 533417 | EMCPHER3 115.00 | 533427 | REFINRY3 115.00 | 0 |  | 1 |  |  | WERE | BPU - CITY OF MCPHERSON JOHNS-MANVILLE - EAST MCPHERSON SWITCHING STATION 115KV CKT 1 | Rebuild Line | 248 | 248 |  |  | 5.7 | 24 | 24 |  | 0.00392 | 0.03057 | 0.00456 | Line owned by City of McPherson Board of Public Utilities | [25 empty] | 2009-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 2 | 2007AG2AFS81T3303210SP | TO->FROM | BPU - CITY OF MCPHERSON JOHNS-MANVILLE - EAST MCPHERSON SWITCHING STATION 115KV CKT 1 | REL | WERE | WERE | WEST | WEST | 0 | 533417 | EMCPHER3 115.00 | 533426 | MANVILE3 115.00 | 0 |  | 1 | 10SP | 84 | 84 | 103.3 | 111.9 | 112.2211 | 115.6411 | [7 empty] | CATEGORYB | SINGLE | EAST MCPHERSON SWITCHING STATION - REFINRY3 115.00 115KV CKT 1 | 0 | 533417 | EMCPHER3 115.00 | 533427 | REFINRY3 115.00 | 0 |  | 1 |  |  | WERE | BPU - CITY OF MCPHERSON JOHNS-MANVILLE - EAST MCPHERSON SWITCHING STATION 115KV CKT 1 | Rebuild Line | 248 | 248 |  |  | 5.7 | 24 | 24 |  | 0.00392 | 0.03057 | 0.00456 | Line owned by City of McPherson Board of Public Utilities | [25 empty] | 2009-06-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 3 | 2 | 2007AG2AFS81T3963213SP | TO->FROM | BPU - CITY OF MCPHERSON JOHNS-MANVILLE - EAST MCPHERSON SWITCHING STATION 115KV CKT 1 | REL | WERE | WERE | WEST | WEST | 0 | 533417 | EMCPHER3 115.00 | 533426 | MANVILE3 115.00 | 0 |  | 1 | 13SP | 84 | 84 |  |  | 114.0299 | 117.4916 | [7 empty] | CATEGORYB | SINGLE | EAST MCPHERSON SWITCHING STATION - REFINRY3 115.00 115KV CKT 1 | 0 | 533417 | EMCPHER3 115.00 | 533427 | REFINRY3 115.00 | 0 |  | 1 |  |  | WERE | BPU - CITY OF MCPHERSON JOHNS-MANVILLE - EAST MCPHERSON SWITCHING STATION 115KV CKT 1 | Rebuild Line | 248 | 248 |  |  | 5.7 | 24 | 24 |  | 0.00392 | 0.03057 | 0.00456 | Line owned by City of McPherson Board of Public Utilities | [25 empty] | 2009-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 4 | 1 | 2007AG2AFS81T6344118SP | FROM->TO | BROOKLINE - JUNCTION 161KV CKT 1 | REL | SPRM | SPRM | SPRM | SPRM | 0 | 549969 | BROOKLINE 5161.00 | 549955 | JUNCTION 5161.00 | 0 |  | 1 | 18SP | 340 | 358 | 101.7 | 101.2 | 98.9804 | 101.6351 | [7 empty] | CATEGORYB | SINGLE | BATTLEFIELD - MAIN 161KV CKT 1 | 0 | 549958 | MAIN STREET5161.00 | 549959 | BATTLEFIELD5161.00 | 0 |  | 1 |  |  | SPRM | BROOKLINE - JUNCTION 161KV CKT 1 | Reconductor 1192 AAC with 1158.4 ACSS/TW 3.4 miles | 450 | 475 |  |  | 3.4 | 24 | 24 | N | 0.0014 | 0.0094 | 0.0052 |  | 1000000 | 2008-01-01 | [23 empty] | 2017-06-01 | 2017-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 4 | 2007AG2AFS81T1263410SP | TO->FROM | BUFFALO - FT SUPPLY 69KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520919 | FTSUPLY2 69.000 | 520835 | BUFFALO2 69.000 | 0 |  | 1 | 10SP | 24 | 24 | 120.7 | 101.3 | 101.3106 | 101.8773 | [7 empty] | CATEGORYB | SINGLE | KNOBHILL - MOORELAND 138KV CKT 1 | 0 | 514795 | KNOBHIL4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 |  |  | WFEC | BUFFALO - FT SUPPLY 69KV CKT 1 | Upgrade CTs at Buffalo Southwest (Fort Supply Branch) | 29 | 35 | [9 empty] | Conductor will be the new limiting factor at 29/35 | 150000 | 2008-12-01 | [23 empty] | 2010-06-01 | 2011-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 4 | 2007AG2AFS81T7023410SP | TO->FROM | BUFFALO - FT SUPPLY 69KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520919 | FTSUPLY2 69.000 | 520835 | BUFFALO2 69.000 | 0 |  | 1 | 10SP | 24 | 24 | 120.6 | 101.2 | 101.2831 | 101.8497 | [7 empty] | CATEGORYB | SINGLE | KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 514794 | KNOBHIL2 69.000 | 514795 | KNOBHIL4 138.00 | 515732 | KNOBHIL1 13.200 | 1 |  |  | WFEC | BUFFALO - FT SUPPLY 69KV CKT 1 | Upgrade CTs at Buffalo Southwest (Fort Supply Branch) | 29 | 35 | [9 empty] | Conductor will be the new limiting factor at 29/35 | 150000 | 2008-12-01 | [23 empty] | 2010-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 4 | 2007AG2AFS81T1253410SP | TO->FROM | BUFFALO - FT SUPPLY 69KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520919 | FTSUPLY2 69.000 | 520835 | BUFFALO2 69.000 | 0 |  | 1 | 10SP | 24 | 24 | 115.2 | 100.8 | 100.8179 | 101.2344 | [7 empty] | CATEGORYB | SINGLE | ALVA - KNOBHILL 69KV CKT 1 | 0 | 514792 | ALVAOGE2 69.000 | 514794 | KNOBHIL2 69.000 | 0 |  | 1 |  |  | WFEC | BUFFALO - FT SUPPLY 69KV CKT 1 | Upgrade CTs at Buffalo Southwest (Fort Supply Branch) | 29 | 35 | [9 empty] | Conductor will be the new limiting factor at 29/35 | 150000 | 2008-12-01 | [23 empty] | 2010-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 4 | 2007AG2AFS81T4453418SP | TO->FROM | BUFFALO - FT SUPPLY 69KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520919 | FTSUPLY2 69.000 | 520835 | BUFFALO2 69.000 | 0 |  | 1 | 18SP | 24 | 24 | 121.2 | 110.4 | 110.3042 | 110.479 | [7 empty] | CATEGORYB | SINGLE | ALVA - KNOBHILL 69KV CKT 1 | 0 | 514792 | ALVAOGE2 69.000 | 514794 | KNOBHIL2 69.000 | 0 |  | 1 |  |  | WFEC | BUFFALO - FT SUPPLY 69KV CKT 1 | Upgrade CTs at Buffalo Southwest (Fort Supply Branch) | 29 | 35 | [9 empty] | Conductor will be the new limiting factor at 29/35 | 150000 | 2008-12-01 | [23 empty] | 2010-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 4 | 2007AG2AFS81T4463418SP | TO->FROM | BUFFALO - FT SUPPLY 69KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520919 | FTSUPLY2 69.000 | 520835 | BUFFALO2 69.000 | 0 |  | 1 | 18SP | 24 | 24 | 121.1 | 107.7 | 107.7449 | 108.01 | [7 empty] | CATEGORYB | SINGLE | KNOBHILL - MOORELAND 138KV CKT 1 | 0 | 514795 | KNOBHIL4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 |  |  | WFEC | BUFFALO - FT SUPPLY 69KV CKT 1 | Upgrade CTs at Buffalo Southwest (Fort Supply Branch) | 29 | 35 | [9 empty] | Conductor will be the new limiting factor at 29/35 | 150000 | 2008-12-01 | [23 empty] | 2010-06-01 | 2011-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 4 | 2007AG2AFS81T26603418SP | TO->FROM | BUFFALO - FT SUPPLY 69KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520919 | FTSUPLY2 69.000 | 520835 | BUFFALO2 69.000 | 0 |  | 1 | 18SP | 24 | 24 | 120.7 | 107.6 | 107.6825 | 107.9476 | [7 empty] | CATEGORYB | SINGLE | KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 514794 | KNOBHIL2 69.000 | 514795 | KNOBHIL4 138.00 | 515732 | KNOBHIL1 13.200 | 1 |  |  | WFEC | BUFFALO - FT SUPPLY 69KV CKT 1 | Upgrade CTs at Buffalo Southwest (Fort Supply Branch) | 29 | 35 | [9 empty] | Conductor will be the new limiting factor at 29/35 | 150000 | 2008-12-01 | [23 empty] | 2010-06-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 1 | 4 | 2007AG2AFS81T211409AP | FROM->TO | BUFFALO - WEST 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520835 | BUFFALO2 69.000 | 521093 | WEST 2 69.000 | 0 |  | 1 | 09AP | 24 | 24 |  |  | 111.0045 | 123.6277 | [7 empty] | CATEGORYB | SINGLE | FT SUPPLY - IODINE 138KV CKT 1 | 0 | 520920 | FTSUPLY4 138.00 | 520957 | IODINE 4 138.00 | 0 |  | 1 |  |  | WFEC | BUFFALO - WEST 69KV CKT 1 | Upgrade terminal equipment at Buffalo to 600A | 53 | 65 | [9 empty] | next limit is 3/0 conductor | 150000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 1 | 4 | 2007AG2AFS81T241409AP | FROM->TO | BUFFALO - WEST 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520835 | BUFFALO2 69.000 | 521093 | WEST 2 69.000 | 0 |  | 1 | 09AP | 24 | 24 |  |  | 109.5096 | 122.1303 | [7 empty] | CATEGORYB | SINGLE | IODINE - MOORELAND 138KV CKT 1 | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 |  |  | WFEC | BUFFALO - WEST 69KV CKT 1 | Upgrade terminal equipment at Buffalo to 600A | 53 | 65 | [9 empty] | next limit is 3/0 conductor | 150000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 1 | 1 | 2007AG2AFS81T471109FA | FROM->TO | BUFFALO - WEST 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520835 | BUFFALO2 69.000 | 521093 | WEST 2 69.000 | 0 |  | 1 | 09FA | 24 | 24 |  |  | 70.923 | 118.0325 | [7 empty] | CATEGORYB | SINGLE | FT SUPPLY - IODINE 138KV CKT 1 | 0 | 520920 | FTSUPLY4 138.00 | 520957 | IODINE 4 138.00 | 0 |  | 1 |  |  | WFEC | BUFFALO - WEST 69KV CKT 1 | Upgrade terminal equipment at Buffalo to 600A | 53 | 65 | [9 empty] | next limit is 3/0 conductor | 150000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 1 | 1 | 2007AG2AFS81T501109FA | FROM->TO | BUFFALO - WEST 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520835 | BUFFALO2 69.000 | 521093 | WEST 2 69.000 | 0 |  | 1 | 09FA | 24 | 24 |  |  | 68.0555 | 115.0502 | [7 empty] | CATEGORYB | SINGLE | IODINE - MOORELAND 138KV CKT 1 | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 |  |  | WFEC | BUFFALO - WEST 69KV CKT 1 | Upgrade terminal equipment at Buffalo to 600A | 53 | 65 | [9 empty] | next limit is 3/0 conductor | 150000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 1 | 2007AG2AFS81T834109G | FROM->TO | BUFFALO - WEST 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520835 | BUFFALO2 69.000 | 521093 | WEST 2 69.000 | 0 |  | 1 | 09G | 24 | 24 |  |  | 114.2359 | 126.7193 | [7 empty] | CATEGORYB | SINGLE | FT SUPPLY - IODINE 138KV CKT 1 | 0 | 520920 | FTSUPLY4 138.00 | 520957 | IODINE 4 138.00 | 0 |  | 1 |  |  | WFEC | BUFFALO - WEST 69KV CKT 1 | Upgrade terminal equipment at Buffalo to 600A | 53 | 65 | [9 empty] | next limit is 3/0 conductor | 150000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 1 | 2007AG2AFS81T904109G | FROM->TO | BUFFALO - WEST 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520835 | BUFFALO2 69.000 | 521093 | WEST 2 69.000 | 0 |  | 1 | 09G | 24 | 24 |  |  | 110.6452 | 123.1428 | [7 empty] | CATEGORYB | SINGLE | IODINE - MOORELAND 138KV CKT 1 | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 |  |  | WFEC | BUFFALO - WEST 69KV CKT 1 | Upgrade terminal equipment at Buffalo to 600A | 53 | 65 | [9 empty] | next limit is 3/0 conductor | 150000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 1 | 2007AG2AFS81T654109G | FROM->TO | BUFFALO - WEST 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520835 | BUFFALO2 69.000 | 521093 | WEST 2 69.000 | 0 |  | 1 | 09G | 24 | 24 |  |  | 112.8572 | 117.9244 | [7 empty] | CATEGORYB | SINGLE | KNOBHILL - MOORELAND 138KV CKT 1 | 0 | 514795 | KNOBHIL4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 |  |  | WFEC | BUFFALO - WEST 69KV CKT 1 | Upgrade terminal equipment at Buffalo to 600A | 53 | 65 | [9 empty] | next limit is 3/0 conductor | 150000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 4 | 2007AG2AFS81T1064409SH | FROM->TO | BUFFALO - WEST 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520835 | BUFFALO2 69.000 | 521093 | WEST 2 69.000 | 0 |  | 1 | 09SH | 24 | 24 |  |  | 110.4325 | 122.9423 | [7 empty] | CATEGORYB | SINGLE | FT SUPPLY - IODINE 138KV CKT 1 | 0 | 520920 | FTSUPLY4 138.00 | 520957 | IODINE 4 138.00 | 0 |  | 1 |  |  | WFEC | BUFFALO - WEST 69KV CKT 1 | Upgrade terminal equipment at Buffalo to 600A | 53 | 65 | [9 empty] | next limit is 3/0 conductor | 150000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 4 | 2007AG2AFS81T1114409SH | FROM->TO | BUFFALO - WEST 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520835 | BUFFALO2 69.000 | 521093 | WEST 2 69.000 | 0 |  | 1 | 09SH | 24 | 24 |  |  | 106.9429 | 119.3789 | [7 empty] | CATEGORYB | SINGLE | IODINE - MOORELAND 138KV CKT 1 | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 |  |  | WFEC | BUFFALO - WEST 69KV CKT 1 | Upgrade terminal equipment at Buffalo to 600A | 53 | 65 | [9 empty] | next limit is 3/0 conductor | 150000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 4 | 2007AG2AFS81T854409SH | FROM->TO | BUFFALO - WEST 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520835 | BUFFALO2 69.000 | 521093 | WEST 2 69.000 | 0 |  | 1 | 09SH | 24 | 24 |  |  | 105.6909 | 110.7721 | [7 empty] | CATEGORYB | SINGLE | KNOBHILL - MOORELAND 138KV CKT 1 | 0 | 514795 | KNOBHIL4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 |  |  | WFEC | BUFFALO - WEST 69KV CKT 1 | Upgrade terminal equipment at Buffalo to 600A | 53 | 65 | [9 empty] | next limit is 3/0 conductor | 150000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 4 | 2007AG2AFS81T1354409SP | FROM->TO | BUFFALO - WEST 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520835 | BUFFALO2 69.000 | 521093 | WEST 2 69.000 | 0 |  | 1 | 09SP | 24 | 24 |  |  | 107.2113 | 119.6084 | [7 empty] | CATEGORYB | SINGLE | FT SUPPLY - IODINE 138KV CKT 1 | 0 | 520920 | FTSUPLY4 138.00 | 520957 | IODINE 4 138.00 | 0 |  | 1 |  |  | WFEC | BUFFALO - WEST 69KV CKT 1 | Upgrade terminal equipment at Buffalo to 600A | 53 | 65 | [9 empty] | next limit is 3/0 conductor | 150000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 4 | 2007AG2AFS81T1114409SP | FROM->TO | BUFFALO - WEST 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520835 | BUFFALO2 69.000 | 521093 | WEST 2 69.000 | 0 |  | 1 | 09SP | 24 | 24 |  |  | 113.4524 | 118.6343 | [7 empty] | CATEGORYB | SINGLE | KNOBHILL - MOORELAND 138KV CKT 1 | 0 | 514795 | KNOBHIL4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 |  |  | WFEC | BUFFALO - WEST 69KV CKT 1 | Upgrade terminal equipment at Buffalo to 600A | 53 | 65 | [9 empty] | next limit is 3/0 conductor | 150000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 | ISLAND-LOAD |  |  | FDNS |  | 4 | 4 | 2007AG2AFS81T6124409SP | FROM->TO | BUFFALO - WEST 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520835 | BUFFALO2 69.000 | 521093 | WEST 2 69.000 | 0 |  | 1 | 09SP | 24 | 24 |  |  | 113.4087 | 118.587 | [7 empty] | CATEGORYB | SINGLE | KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 514794 | KNOBHIL2 69.000 | 514795 | KNOBHIL4 138.00 | 515732 | KNOBHIL1 13.200 | 1 |  |  | WFEC | BUFFALO - WEST 69KV CKT 1 | Upgrade terminal equipment at Buffalo to 600A | 53 | 65 | [9 empty] | next limit is 3/0 conductor | 150000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 1 | 4 | 2007AG2AFS81T901409WP | FROM->TO | BUFFALO - WEST 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520835 | BUFFALO2 69.000 | 521093 | WEST 2 69.000 | 0 |  | 1 | 09WP | 24 | 24 |  |  | 66.0285 | 111.6088 | [7 empty] | CATEGORYB | SINGLE | FT SUPPLY - IODINE 138KV CKT 1 | 0 | 520920 | FTSUPLY4 138.00 | 520957 | IODINE 4 138.00 | 0 |  | 1 |  |  | WFEC | BUFFALO - WEST 69KV CKT 1 | Upgrade terminal equipment at Buffalo to 600A | 53 | 65 | [9 empty] | next limit is 3/0 conductor | 150000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 1 | 4 | 2007AG2AFS81T921409WP | FROM->TO | BUFFALO - WEST 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520835 | BUFFALO2 69.000 | 521093 | WEST 2 69.000 | 0 |  | 1 | 09WP | 24 | 24 |  |  | 62.3922 | 107.8342 | [7 empty] | CATEGORYB | SINGLE | IODINE - MOORELAND 138KV CKT 1 | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 |  |  | WFEC | BUFFALO - WEST 69KV CKT 1 | Upgrade terminal equipment at Buffalo to 600A | 53 | 65 | [9 empty] | next limit is 3/0 conductor | 150000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 1 | 4 | 2007AG2AFS81T1371410SP | FROM->TO | BUFFALO - WEST 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520835 | BUFFALO2 69.000 | 521093 | WEST 2 69.000 | 0 |  | 1 | 10SP | 24 | 24 |  |  | 66.6817 | 112.2238 | [7 empty] | CATEGORYB | SINGLE | FT SUPPLY - IODINE 138KV CKT 1 | 0 | 520920 | FTSUPLY4 138.00 | 520957 | IODINE 4 138.00 | 0 |  | 1 |  |  | WFEC | BUFFALO - WEST 69KV CKT 1 | Upgrade terminal equipment at Buffalo to 600A | 53 | 65 | [9 empty] | next limit is 3/0 conductor | 150000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 1 | 4 | 2007AG2AFS81T1421410SP | FROM->TO | BUFFALO - WEST 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520835 | BUFFALO2 69.000 | 521093 | WEST 2 69.000 | 0 |  | 1 | 10SP | 24 | 24 |  |  | 62.3243 | 107.8062 | [7 empty] | CATEGORYB | SINGLE | IODINE - MOORELAND 138KV CKT 1 | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 |  |  | WFEC | BUFFALO - WEST 69KV CKT 1 | Upgrade terminal equipment at Buffalo to 600A | 53 | 65 | [9 empty] | next limit is 3/0 conductor | 150000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 1 | 4 | 2007AG2AFS81T1191410SP | FROM->TO | BUFFALO - WEST 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520835 | BUFFALO2 69.000 | 521093 | WEST 2 69.000 | 0 |  | 1 | 10SP | 24 | 24 |  |  | 76.3913 | 106.1566 | [7 empty] | CATEGORYB | SINGLE | KNOBHILL - MOORELAND 138KV CKT 1 | 0 | 514795 | KNOBHIL4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 |  |  | WFEC | BUFFALO - WEST 69KV CKT 1 | Upgrade terminal equipment at Buffalo to 600A | 53 | 65 | [9 empty] | next limit is 3/0 conductor | 150000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 1 | 4 | 2007AG2AFS81T611410WP | FROM->TO | BUFFALO - WEST 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520835 | BUFFALO2 69.000 | 521093 | WEST 2 69.000 | 0 |  | 1 | 10WP | 24 | 24 |  |  | 66.1496 | 111.8441 | [7 empty] | CATEGORYB | SINGLE | FT SUPPLY - IODINE 138KV CKT 1 | 0 | 520920 | FTSUPLY4 138.00 | 520957 | IODINE 4 138.00 | 0 |  | 1 |  |  | WFEC | BUFFALO - WEST 69KV CKT 1 | Upgrade terminal equipment at Buffalo to 600A | 53 | 65 | [9 empty] | next limit is 3/0 conductor | 150000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 1 | 4 | 2007AG2AFS81T621410WP | FROM->TO | BUFFALO - WEST 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520835 | BUFFALO2 69.000 | 521093 | WEST 2 69.000 | 0 |  | 1 | 10WP | 24 | 24 |  |  | 62.4597 | 108.0155 | [7 empty] | CATEGORYB | SINGLE | IODINE - MOORELAND 138KV CKT 1 | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 |  |  | WFEC | BUFFALO - WEST 69KV CKT 1 | Upgrade terminal equipment at Buffalo to 600A | 53 | 65 | [9 empty] | next limit is 3/0 conductor | 150000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 1 | 4 | 2007AG2AFS81T2171413SP | FROM->TO | BUFFALO - WEST 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520835 | BUFFALO2 69.000 | 521093 | WEST 2 69.000 | 0 |  | 1 | 13SP | 24 | 24 |  |  | 66.8463 | 114.081 | [7 empty] | CATEGORYB | SINGLE | FT SUPPLY - IODINE 138KV CKT 1 | 0 | 520920 | FTSUPLY4 138.00 | 520957 | IODINE 4 138.00 | 0 |  | 1 |  |  | WFEC | BUFFALO - WEST 69KV CKT 1 | Upgrade terminal equipment at Buffalo to 600A | 53 | 65 | [9 empty] | next limit is 3/0 conductor | 150000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 1 | 4 | 2007AG2AFS81T2201413SP | FROM->TO | BUFFALO - WEST 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520835 | BUFFALO2 69.000 | 521093 | WEST 2 69.000 | 0 |  | 1 | 13SP | 24 | 24 |  |  | 62.25 | 109.307 | [7 empty] | CATEGORYB | SINGLE | IODINE - MOORELAND 138KV CKT 1 | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 |  |  | WFEC | BUFFALO - WEST 69KV CKT 1 | Upgrade terminal equipment at Buffalo to 600A | 53 | 65 | [9 empty] | next limit is 3/0 conductor | 150000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 | ISLAND-LOAD |  |  | FDNS |  | 1 | 4 | 2007AG2AFS81T11901413SP | FROM->TO | BUFFALO - WEST 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520835 | BUFFALO2 69.000 | 521093 | WEST 2 69.000 | 0 |  | 1 | 13SP | 24 | 24 |  |  | 70.3363 | 100.5606 | [7 empty] | CATEGORYB | SINGLE | KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 514794 | KNOBHIL2 69.000 | 514795 | KNOBHIL4 138.00 | 515732 | KNOBHIL1 13.200 | 1 |  |  | WFEC | BUFFALO - WEST 69KV CKT 1 | Upgrade terminal equipment at Buffalo to 600A | 53 | 65 | [9 empty] | next limit is 3/0 conductor | 150000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 1 | 4 | 2007AG2AFS81T751413WP | FROM->TO | BUFFALO - WEST 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520835 | BUFFALO2 69.000 | 521093 | WEST 2 69.000 | 0 |  | 1 | 13WP | 24 | 24 |  |  | 64.3858 | 110.1566 | [7 empty] | CATEGORYB | SINGLE | FT SUPPLY - IODINE 138KV CKT 1 | 0 | 520920 | FTSUPLY4 138.00 | 520957 | IODINE 4 138.00 | 0 |  | 1 |  |  | WFEC | BUFFALO - WEST 69KV CKT 1 | Upgrade terminal equipment at Buffalo to 600A | 53 | 65 | [9 empty] | next limit is 3/0 conductor | 150000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 1 | 4 | 2007AG2AFS81T761413WP | FROM->TO | BUFFALO - WEST 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520835 | BUFFALO2 69.000 | 521093 | WEST 2 69.000 | 0 |  | 1 | 13WP | 24 | 24 |  |  | 60.5635 | 106.0981 | [7 empty] | CATEGORYB | SINGLE | IODINE - MOORELAND 138KV CKT 1 | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 |  |  | WFEC | BUFFALO - WEST 69KV CKT 1 | Upgrade terminal equipment at Buffalo to 600A | 53 | 65 | [9 empty] | next limit is 3/0 conductor | 150000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 1 | 4 | 2007AG2AFS81T4621418SP | FROM->TO | BUFFALO - WEST 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520835 | BUFFALO2 69.000 | 521093 | WEST 2 69.000 | 0 |  | 1 | 18SP | 24 | 24 |  |  | 67.7688 | 115.2069 | [7 empty] | CATEGORYB | SINGLE | FT SUPPLY - IODINE 138KV CKT 1 | 0 | 520920 | FTSUPLY4 138.00 | 520957 | IODINE 4 138.00 | 0 |  | 1 |  |  | WFEC | BUFFALO - WEST 69KV CKT 1 | Upgrade terminal equipment at Buffalo to 600A | 53 | 65 | [9 empty] | next limit is 3/0 conductor | 150000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 1 | 4 | 2007AG2AFS81T4691418SP | FROM->TO | BUFFALO - WEST 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520835 | BUFFALO2 69.000 | 521093 | WEST 2 69.000 | 0 |  | 1 | 18SP | 24 | 24 |  |  | 62.7001 | 109.9919 | [7 empty] | CATEGORYB | SINGLE | IODINE - MOORELAND 138KV CKT 1 | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 |  |  | WFEC | BUFFALO - WEST 69KV CKT 1 | Upgrade terminal equipment at Buffalo to 600A | 53 | 65 | [9 empty] | next limit is 3/0 conductor | 150000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 1 | 4 | 2007AG2AFS81T4201418SP | FROM->TO | BUFFALO - WEST 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520835 | BUFFALO2 69.000 | 521093 | WEST 2 69.000 | 0 |  | 1 | 18SP | 24 | 24 |  |  | 78.9742 | 109.7305 | [7 empty] | CATEGORYB | SINGLE | KNOBHILL - MOORELAND 138KV CKT 1 | 0 | 514795 | KNOBHIL4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 |  |  | WFEC | BUFFALO - WEST 69KV CKT 1 | Upgrade terminal equipment at Buffalo to 600A | 53 | 65 | [9 empty] | next limit is 3/0 conductor | 150000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 4 | 2007AG2AFS81V3524418SP |  | BUFFALO 69KV | EXP | WFEC |  | AEP-OP |  |  | 520835 | BUFFALO2 69.000 | [5 empty] | 18SP | [8 empty] | 0.93615 | 0.88464 | 0.96675 | 0.9 | 1.05 | CATEGORYB | SINGLE | BUFFALO - FT SUPPLY 69KV CKT 1 | 0 | 520919 | FTSUPLY2 69.000 | 520835 | BUFFALO2 69.000 | 0 |  | 1 |  |  | WFEC | Multi-Dover-Twin Lake_Cresent 138 kV | Convert 69 kV to 138 kV and install terminal equipment at Dover SW; Instal 7 miles of new 138 kV fro WFEC Twin Lakes to OGE Cresent substation | [37 empty] | 2014-06-01 | 2014-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T7152210SP | FROM->TO | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | EXP | SWPA | EES | EMINTH | EES_ARK | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 10SP | 167 | 167 | 109.1 | 118.6 | 118.6439 | 118.7372 | [7 empty] | CATEGORYB | SINGLE | HILLTOP - ST JOE 161KV CKT 1 | 0 | 338108 | 5ST_JOE 161.00 | 338110 | 5HILLTOP 161.00 | 0 |  | 1 |  |  | SWPA | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | Replace buswork in Bull Shoals switchyard | [37 empty] | 2010-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T7152210SP | FROM->TO | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | EXP | SWPA | EES | EMINTH | EES_ARK | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 10SP | 167 | 167 | 109.1 | 118.6 | 118.6439 | 118.7372 | [7 empty] | CATEGORYB | SINGLE | HILLTOP - ST JOE 161KV CKT 1 | 0 | 338108 | 5ST_JOE 161.00 | 338110 | 5HILLTOP 161.00 | 0 |  | 1 |  |  | SWPA | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | Replace buswork in Bull Shoals switchyard | [37 empty] | 2010-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T7132210SP | FROM->TO | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | EXP | SWPA | EES | EMINTH | EES_ARK | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 10SP | 167 | 167 | 108.6 | 117.9 | 118.0241 | 118.08 | [7 empty] | CATEGORYB | SINGLE | EVERTON - ST JOE 161KV CKT 1 | 0 | 338107 | 5EVRTON 161.00 | 338108 | 5ST_JOE 161.00 | 0 |  | 1 |  |  | SWPA | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | Replace buswork in Bull Shoals switchyard | [37 empty] | 2010-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T7132210SP | FROM->TO | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | EXP | SWPA | EES | EMINTH | EES_ARK | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 10SP | 167 | 167 | 108.6 | 117.9 | 118.0241 | 118.08 | [7 empty] | CATEGORYB | SINGLE | EVERTON - ST JOE 161KV CKT 1 | 0 | 338107 | 5EVRTON 161.00 | 338108 | 5ST_JOE 161.00 | 0 |  | 1 |  |  | SWPA | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | Replace buswork in Bull Shoals switchyard | [37 empty] | 2010-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T7062210SP | FROM->TO | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | EXP | SWPA | EES | EMINTH | EES_ARK | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 10SP | 167 | 167 | 106.7 | 116.1 | 116.1979 | 116.2891 | [7 empty] | CATEGORYB | SINGLE | EVERTON - HARRISON-EAST 161KV CKT 1 | 0 | 338104 | 5HARR-E 161.00 | 338107 | 5EVRTON 161.00 | 0 |  | 1 |  |  | SWPA | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | Replace buswork in Bull Shoals switchyard | [37 empty] | 2010-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T7062210SP | FROM->TO | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | EXP | SWPA | EES | EMINTH | EES_ARK | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 10SP | 167 | 167 | 106.7 | 116.1 | 116.1979 | 116.2891 | [7 empty] | CATEGORYB | SINGLE | EVERTON - HARRISON-EAST 161KV CKT 1 | 0 | 338104 | 5HARR-E 161.00 | 338107 | 5EVRTON 161.00 | 0 |  | 1 |  |  | SWPA | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | Replace buswork in Bull Shoals switchyard | [37 empty] | 2010-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T4112210WP | FROM->TO | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | EXP | SWPA | EES | EMINTH | EES_ARK | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 10WP | 167 | 167 |  | 106.7 | 106.8196 | 106.866 | [7 empty] | CATEGORYB | SINGLE | HILLTOP - ST JOE 161KV CKT 1 | 0 | 338108 | 5ST_JOE 161.00 | 338110 | 5HILLTOP 161.00 | 0 |  | 1 |  |  | SWPA | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | Replace buswork in Bull Shoals switchyard | [37 empty] | 2010-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T4112210WP | FROM->TO | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | EXP | SWPA | EES | EMINTH | EES_ARK | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 10WP | 167 | 167 |  | 106.7 | 106.8196 | 106.866 | [7 empty] | CATEGORYB | SINGLE | HILLTOP - ST JOE 161KV CKT 1 | 0 | 338108 | 5ST_JOE 161.00 | 338110 | 5HILLTOP 161.00 | 0 |  | 1 |  |  | SWPA | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | Replace buswork in Bull Shoals switchyard | [37 empty] | 2010-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T4092210WP | FROM->TO | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | EXP | SWPA | EES | EMINTH | EES_ARK | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 10WP | 167 | 167 |  | 106.2 | 106.311 | 106.3593 | [7 empty] | CATEGORYB | SINGLE | EVERTON - ST JOE 161KV CKT 1 | 0 | 338107 | 5EVRTON 161.00 | 338108 | 5ST_JOE 161.00 | 0 |  | 1 |  |  | SWPA | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | Replace buswork in Bull Shoals switchyard | [37 empty] | 2010-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T4092210WP | FROM->TO | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | EXP | SWPA | EES | EMINTH | EES_ARK | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 10WP | 167 | 167 |  | 106.2 | 106.311 | 106.3593 | [7 empty] | CATEGORYB | SINGLE | EVERTON - ST JOE 161KV CKT 1 | 0 | 338107 | 5EVRTON 161.00 | 338108 | 5ST_JOE 161.00 | 0 |  | 1 |  |  | SWPA | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | Replace buswork in Bull Shoals switchyard | [37 empty] | 2010-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T3992210WP | FROM->TO | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | EXP | SWPA | EES | EMINTH | EES_ARK | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 10WP | 167 | 167 |  | 104.9 | 104.9802 | 105.0137 | [7 empty] | CATEGORYB | SINGLE | EVERTON - HARRISON-EAST 161KV CKT 1 | 0 | 338104 | 5HARR-E 161.00 | 338107 | 5EVRTON 161.00 | 0 |  | 1 |  |  | SWPA | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | Replace buswork in Bull Shoals switchyard | [37 empty] | 2010-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T3992210WP | FROM->TO | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | EXP | SWPA | EES | EMINTH | EES_ARK | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 10WP | 167 | 167 |  | 104.9 | 104.9802 | 105.0137 | [7 empty] | CATEGORYB | SINGLE | EVERTON - HARRISON-EAST 161KV CKT 1 | 0 | 338104 | 5HARR-E 161.00 | 338107 | 5EVRTON 161.00 | 0 |  | 1 |  |  | SWPA | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | Replace buswork in Bull Shoals switchyard | [37 empty] | 2010-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T11142213SP | FROM->TO | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | EXP | SWPA | EES | EMINTH | EES_ARK | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 13SP | 167 | 167 | 120.1 | 130.4 | 130.4482 | 130.3627 | [7 empty] | CATEGORYB | SINGLE | HILLTOP - ST JOE 161KV CKT 1 | 0 | 338108 | 5ST_JOE 161.00 | 338110 | 5HILLTOP 161.00 | 0 |  | 1 |  |  | SWPA | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | Replace buswork in Bull Shoals switchyard | [37 empty] | 2010-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T11142213SP | FROM->TO | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | EXP | SWPA | EES | EMINTH | EES_ARK | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 13SP | 167 | 167 | 120.1 | 130.4 | 130.4482 | 130.3627 | [7 empty] | CATEGORYB | SINGLE | HILLTOP - ST JOE 161KV CKT 1 | 0 | 338108 | 5ST_JOE 161.00 | 338110 | 5HILLTOP 161.00 | 0 |  | 1 |  |  | SWPA | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | Replace buswork in Bull Shoals switchyard | [37 empty] | 2010-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T11122213SP | FROM->TO | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | EXP | SWPA | EES | EMINTH | EES_ARK | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 13SP | 167 | 167 | 119.4 | 129.7 | 129.7213 | 129.6354 | [7 empty] | CATEGORYB | SINGLE | EVERTON - ST JOE 161KV CKT 1 | 0 | 338107 | 5EVRTON 161.00 | 338108 | 5ST_JOE 161.00 | 0 |  | 1 |  |  | SWPA | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | Replace buswork in Bull Shoals switchyard | [37 empty] | 2010-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T11122213SP | FROM->TO | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | EXP | SWPA | EES | EMINTH | EES_ARK | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 13SP | 167 | 167 | 119.4 | 129.7 | 129.7213 | 129.6354 | [7 empty] | CATEGORYB | SINGLE | EVERTON - ST JOE 161KV CKT 1 | 0 | 338107 | 5EVRTON 161.00 | 338108 | 5ST_JOE 161.00 | 0 |  | 1 |  |  | SWPA | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | Replace buswork in Bull Shoals switchyard | [37 empty] | 2010-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T11032213SP | FROM->TO | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | EXP | SWPA | EES | EMINTH | EES_ARK | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 13SP | 167 | 167 | 117.3 | 127.7 | 127.6922 | 127.5998 | [7 empty] | CATEGORYB | SINGLE | EVERTON - HARRISON-EAST 161KV CKT 1 | 0 | 338104 | 5HARR-E 161.00 | 338107 | 5EVRTON 161.00 | 0 |  | 1 |  |  | SWPA | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | Replace buswork in Bull Shoals switchyard | [37 empty] | 2010-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T11032213SP | FROM->TO | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | EXP | SWPA | EES | EMINTH | EES_ARK | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 13SP | 167 | 167 | 117.3 | 127.7 | 127.6922 | 127.5998 | [7 empty] | CATEGORYB | SINGLE | EVERTON - HARRISON-EAST 161KV CKT 1 | 0 | 338104 | 5HARR-E 161.00 | 338107 | 5EVRTON 161.00 | 0 |  | 1 |  |  | SWPA | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | Replace buswork in Bull Shoals switchyard | [37 empty] | 2010-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T4292213WP | FROM->TO | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | EXP | SWPA | EES | EMINTH | EES_ARK | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 13WP | 167 | 167 | 104.4 | 113.1 | 113.0762 | 113.0457 | [7 empty] | CATEGORYB | SINGLE | HILLTOP - ST JOE 161KV CKT 1 | 0 | 338108 | 5ST_JOE 161.00 | 338110 | 5HILLTOP 161.00 | 0 |  | 1 |  |  | SWPA | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | Replace buswork in Bull Shoals switchyard | [37 empty] | 2010-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T4292213WP | FROM->TO | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | EXP | SWPA | EES | EMINTH | EES_ARK | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 13WP | 167 | 167 | 104.4 | 113.1 | 113.0762 | 113.0457 | [7 empty] | CATEGORYB | SINGLE | HILLTOP - ST JOE 161KV CKT 1 | 0 | 338108 | 5ST_JOE 161.00 | 338110 | 5HILLTOP 161.00 | 0 |  | 1 |  |  | SWPA | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | Replace buswork in Bull Shoals switchyard | [37 empty] | 2010-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T4272213WP | FROM->TO | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | EXP | SWPA | EES | EMINTH | EES_ARK | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 13WP | 167 | 167 | 103.8 | 112.5 | 112.5189 | 112.4884 | [7 empty] | CATEGORYB | SINGLE | EVERTON - ST JOE 161KV CKT 1 | 0 | 338107 | 5EVRTON 161.00 | 338108 | 5ST_JOE 161.00 | 0 |  | 1 |  |  | SWPA | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | Replace buswork in Bull Shoals switchyard | [37 empty] | 2010-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T4272213WP | FROM->TO | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | EXP | SWPA | EES | EMINTH | EES_ARK | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 13WP | 167 | 167 | 103.8 | 112.5 | 112.5189 | 112.4884 | [7 empty] | CATEGORYB | SINGLE | EVERTON - ST JOE 161KV CKT 1 | 0 | 338107 | 5EVRTON 161.00 | 338108 | 5ST_JOE 161.00 | 0 |  | 1 |  |  | SWPA | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | Replace buswork in Bull Shoals switchyard | [37 empty] | 2010-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T4192213WP | FROM->TO | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | EXP | SWPA | EES | EMINTH | EES_ARK | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 13WP | 167 | 167 | 102.3 | 111 | 110.991 | 110.9667 | [7 empty] | CATEGORYB | SINGLE | EVERTON - HARRISON-EAST 161KV CKT 1 | 0 | 338104 | 5HARR-E 161.00 | 338107 | 5EVRTON 161.00 | 0 |  | 1 |  |  | SWPA | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | Replace buswork in Bull Shoals switchyard | [37 empty] | 2010-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T4192213WP | FROM->TO | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | EXP | SWPA | EES | EMINTH | EES_ARK | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 13WP | 167 | 167 | 102.3 | 111 | 110.991 | 110.9667 | [7 empty] | CATEGORYB | SINGLE | EVERTON - HARRISON-EAST 161KV CKT 1 | 0 | 338104 | 5HARR-E 161.00 | 338107 | 5EVRTON 161.00 | 0 |  | 1 |  |  | SWPA | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | Replace buswork in Bull Shoals switchyard | [37 empty] | 2010-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 4 | 2 | 2007AG2AFS81T21354218SP | FROM->TO | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | EXP | SWPA | EES | EMINTH | EES_ARK | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 18SP | 167 | 167 |  | 114.2 | 115.324 | 114.035 | [7 empty] | CATEGORYB | SINGLE | HILLTOP - ST JOE 161KV CKT 1 | 0 | 338108 | 5ST_JOE 161.00 | 338110 | 5HILLTOP 161.00 | 0 |  | 1 |  |  | SWPA | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | Replace buswork in Bull Shoals switchyard | [37 empty] | 2010-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 4 | 2 | 2007AG2AFS81T21354218SP | FROM->TO | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | EXP | SWPA | EES | EMINTH | EES_ARK | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 18SP | 167 | 167 |  | 114.2 | 115.324 | 114.035 | [7 empty] | CATEGORYB | SINGLE | HILLTOP - ST JOE 161KV CKT 1 | 0 | 338108 | 5ST_JOE 161.00 | 338110 | 5HILLTOP 161.00 | 0 |  | 1 |  |  | SWPA | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | Replace buswork in Bull Shoals switchyard | [37 empty] | 2010-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 4 | 2 | 2007AG2AFS81T21344218SP | FROM->TO | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | EXP | SWPA | EES | EMINTH | EES_ARK | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 18SP | 167 | 167 |  | 113.5 | 114.5842 | 113.2319 | [7 empty] | CATEGORYB | SINGLE | EVERTON - ST JOE 161KV CKT 1 | 0 | 338107 | 5EVRTON 161.00 | 338108 | 5ST_JOE 161.00 | 0 |  | 1 |  |  | SWPA | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | Replace buswork in Bull Shoals switchyard | [37 empty] | 2010-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 4 | 2 | 2007AG2AFS81T21344218SP | FROM->TO | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | EXP | SWPA | EES | EMINTH | EES_ARK | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 18SP | 167 | 167 |  | 113.5 | 114.5842 | 113.2319 | [7 empty] | CATEGORYB | SINGLE | EVERTON - ST JOE 161KV CKT 1 | 0 | 338107 | 5EVRTON 161.00 | 338108 | 5ST_JOE 161.00 | 0 |  | 1 |  |  | SWPA | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | Replace buswork in Bull Shoals switchyard | [37 empty] | 2010-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 4 | 2 | 2007AG2AFS81T21294218SP | FROM->TO | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | EXP | SWPA | EES | EMINTH | EES_ARK | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 18SP | 167 | 167 |  | 111.2 | 112.3493 | 111.0054 | [7 empty] | CATEGORYB | SINGLE | EVERTON - HARRISON-EAST 161KV CKT 1 | 0 | 338104 | 5HARR-E 161.00 | 338107 | 5EVRTON 161.00 | 0 |  | 1 |  |  | SWPA | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | Replace buswork in Bull Shoals switchyard | [37 empty] | 2010-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 4 | 2 | 2007AG2AFS81T21294218SP | FROM->TO | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | EXP | SWPA | EES | EMINTH | EES_ARK | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 18SP | 167 | 167 |  | 111.2 | 112.3493 | 111.0054 | [7 empty] | CATEGORYB | SINGLE | EVERTON - HARRISON-EAST 161KV CKT 1 | 0 | 338104 | 5HARR-E 161.00 | 338107 | 5EVRTON 161.00 | 0 |  | 1 |  |  | SWPA | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | Replace buswork in Bull Shoals switchyard | [37 empty] | 2010-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T7072210WP | FROM->TO | CALICO ROCK - NORFORK 161KV CKT 1 | CP | EES | SWPA | EES_ARK | EMINTH | 0 | 338130 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 10WP | 148 | 148 | 115.2 | 125.3 | 125.3685 | 126.2698 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 | 186.8793 | AP&L (EES) owns the line (SWPAs facilities good for 167 MVA) | SWPA | CALICO ROCK - NORFORK 161KV CKT 1 | Replace buswork within bay and change metering CT ratio, replace wavetraps. Entergy must also reconductor their line to increase the rating. | 236 | 236 | 236 | 236 |  | 18 | 3 |  |  |  |  | New ratings are based on CT limits. They assume that Entergy also upgrades their line. | 100000 | 2007-04-20 | [23 empty] | 2010-12-01 | 2010-12-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T2392210WPG | FROM->TO | CALICO ROCK - NORFORK 161KV CKT 1 | CP | EES | SWPA | EES_ARK | EMINTH | 0 | 338130 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 10WP | 148 | 148 | 113.2 | 121.4 | 121.399 | 122.203 | [7 empty] | CATEGORYB | GENOUT | GEN532751 1-WOLF CREEK GENERATING STATION UNIT 1 | 0 | 0 |  | 0 |  | 0 |  |  | 180.8604 | AP&L (EES) owns the line (SWPAs facilities good for 167 MVA) | SWPA | CALICO ROCK - NORFORK 161KV CKT 1 | Replace buswork within bay and change metering CT ratio, replace wavetraps. Entergy must also reconductor their line to increase the rating. | 236 | 236 | 236 | 236 |  | 18 | 3 |  |  |  |  | New ratings are based on CT limits. They assume that Entergy also upgrades their line. | 100000 | 2007-04-20 | [23 empty] | 2010-12-01 | 2010-12-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T4502210WP | FROM->TO | CALICO ROCK - NORFORK 161KV CKT 1 | CP | EES | SWPA | EES_ARK | EMINTH | 0 | 338130 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 10WP | 148 | 148 | 113.0 | 121.5 | 121.5538 | 122.1155 | [7 empty] | CATEGORYB | SINGLE | DELL 500 - INDEPENDENCE 500KV CKT 1 | 0 | 338145 | 8ISES 5 500.00 | 338187 | 8DELL 5 500.00 | 0 |  | 1 | 180.7309 | AP&L (EES) owns the line (SWPAs facilities good for 167 MVA) | SWPA | CALICO ROCK - NORFORK 161KV CKT 1 | Replace buswork within bay and change metering CT ratio, replace wavetraps. Entergy must also reconductor their line to increase the rating. | 236 | 236 | 236 | 236 |  | 18 | 3 |  |  |  |  | New ratings are based on CT limits. They assume that Entergy also upgrades their line. | 100000 | 2007-04-20 | [23 empty] | 2010-12-01 | 2010-12-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T2282210WP | FROM->TO | CALICO ROCK - NORFORK 161KV CKT 1 | CP | EES | SWPA | EES_ARK | EMINTH | 0 | 338130 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 10WP | 148 | 148 | 110.5 | 119.1 | 119.1297 | 120.0125 | [7 empty] | CATEGORYB | SINGLE | WHITEWATER EAST - WILHELMINA 345KV CKT 1 | 0 | 300051 | 7WILHLM 345.00 | 300054 | 7GOBKNOB 345.00 | 0 |  | 1 | 177.6185 | AP&L (EES) owns the line (SWPAs facilities good for 167 MVA) | SWPA | CALICO ROCK - NORFORK 161KV CKT 1 | Replace buswork within bay and change metering CT ratio, replace wavetraps. Entergy must also reconductor their line to increase the rating. | 236 | 236 | 236 | 236 |  | 18 | 3 |  |  |  |  | New ratings are based on CT limits. They assume that Entergy also upgrades their line. | 100000 | 2007-04-20 | [23 empty] | 2010-12-01 | 2010-12-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T2552210WPG | FROM->TO | CALICO ROCK - NORFORK 161KV CKT 1 | CP | EES | SWPA | EES_ARK | EMINTH | 0 | 338130 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 10WP | 148 | 148 | 108.2 | 116.4 | 116.3839 | 117.176 | [7 empty] | CATEGORYB | GENOUT | GEN542962 2-IATAN UNIT #2 | 0 | 0 |  | 0 |  | 0 |  |  | 173.4205 | AP&L (EES) owns the line (SWPAs facilities good for 167 MVA) | SWPA | CALICO ROCK - NORFORK 161KV CKT 1 | Replace buswork within bay and change metering CT ratio, replace wavetraps. Entergy must also reconductor their line to increase the rating. | 236 | 236 | 236 | 236 |  | 18 | 3 |  |  |  |  | New ratings are based on CT limits. They assume that Entergy also upgrades their line. | 100000 | 2007-04-20 | [23 empty] | 2010-12-01 | 2010-12-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T1152210WPG | FROM->TO | CALICO ROCK - NORFORK 161KV CKT 1 | CP | EES | SWPA | EES_ARK | EMINTH | 0 | 338130 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 10WP | 148 | 148 | 107.7 | 115.8 | 115.8606 | 116.6539 | [7 empty] | CATEGORYB | GENOUT | GEN509394 1-FLINT CREEK | 0 | 0 |  | 0 |  | 0 |  |  | 172.6478 | AP&L (EES) owns the line (SWPAs facilities good for 167 MVA) | SWPA | CALICO ROCK - NORFORK 161KV CKT 1 | Replace buswork within bay and change metering CT ratio, replace wavetraps. Entergy must also reconductor their line to increase the rating. | 236 | 236 | 236 | 236 |  | 18 | 3 |  |  |  |  | New ratings are based on CT limits. They assume that Entergy also upgrades their line. | 100000 | 2007-04-20 | [23 empty] | 2010-12-01 | 2010-12-01
2007-AG2 | AFS9 | CONT-Hayti-Blytheville 161kV Line Overload | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T2112210WP | FROM->TO | CALICO ROCK - NORFORK 161KV CKT 1 | CP | EES | SWPA | EES_ARK | EMINTH | 0 | 338130 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 10WP | 148 | 148 | 106.0 | 115.1 | 115.1219 | 116.3172 | [7 empty] | CATEGORYB | SINGLE | DELL 500 - NEW MADRID 500KV CKT 1 | 0 | 300035 | 8NEWMAD 500.00 | 338187 | 8DELL 5 500.00 | 0 |  | 1 | 172.1495 | AP&L (EES) owns the line (SWPAs facilities good for 167 MVA) | SWPA | CALICO ROCK - NORFORK 161KV CKT 1 | Replace buswork within bay and change metering CT ratio, replace wavetraps. Entergy must also reconductor their line to increase the rating. | 236 | 236 | 236 | 236 |  | 18 | 3 |  |  |  |  | New ratings are based on CT limits. They assume that Entergy also upgrades their line. | 100000 | 2007-04-20 | [23 empty] | 2010-12-01 | 2010-12-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T18292213SP | FROM->TO | CALICO ROCK - NORFORK 161KV CKT 1 | CP | EES | SWPA | EES_ARK | EMINTH | 0 | 338130 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 13SP | 148 | 148 | 110.2 | 120.2 | 120.2765 | 121.5769 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 | 179.9338 | AP&L (EES) owns the line (SWPAs facilities good for 167 MVA) | SWPA | CALICO ROCK - NORFORK 161KV CKT 1 | Replace buswork within bay and change metering CT ratio, replace wavetraps. Entergy must also reconductor their line to increase the rating. | 236 | 236 | 236 | 236 |  | 18 | 3 |  |  |  |  | New ratings are based on CT limits. They assume that Entergy also upgrades their line. | 100000 | 2007-04-20 | [23 empty] | 2010-12-01 | 2010-12-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T5172213SPG | FROM->TO | CALICO ROCK - NORFORK 161KV CKT 1 | CP | EES | SWPA | EES_ARK | EMINTH | 0 | 338130 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 13SP | 148 | 148 | 106.4 | 113.7 | 113.955 | 115.0762 | [7 empty] | CATEGORYB | GENOUT | GEN532751 1-WOLF CREEK GENERATING STATION UNIT 1 | 0 | 0 |  | 0 |  | 0 |  |  | 170.3128 | AP&L (EES) owns the line (SWPAs facilities good for 167 MVA) | SWPA | CALICO ROCK - NORFORK 161KV CKT 1 | Replace buswork within bay and change metering CT ratio, replace wavetraps. Entergy must also reconductor their line to increase the rating. | 236 | 236 | 236 | 236 |  | 18 | 3 |  |  |  |  | New ratings are based on CT limits. They assume that Entergy also upgrades their line. | 100000 | 2007-04-20 | [23 empty] | 2010-12-01 | 2010-12-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T5202213SP | FROM->TO | CALICO ROCK - NORFORK 161KV CKT 1 | CP | EES | SWPA | EES_ARK | EMINTH | 0 | 338130 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 13SP | 148 | 148 | 103.3 | 111.6 | 111.6671 | 112.9053 | [7 empty] | CATEGORYB | SINGLE | WHITEWATER EAST - WILHELMINA 345KV CKT 1 | 0 | 300051 | 7WILHLM 345.00 | 300054 | 7GOBKNOB 345.00 | 0 |  | 1 | 167.0998 | AP&L (EES) owns the line (SWPAs facilities good for 167 MVA) | SWPA | CALICO ROCK - NORFORK 161KV CKT 1 | Replace buswork within bay and change metering CT ratio, replace wavetraps. Entergy must also reconductor their line to increase the rating. | 236 | 236 | 236 | 236 |  | 18 | 3 |  |  |  |  | New ratings are based on CT limits. They assume that Entergy also upgrades their line. | 100000 | 2007-04-20 | [23 empty] | 2010-12-01 | 2010-12-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T7652213WP | FROM->TO | CALICO ROCK - NORFORK 161KV CKT 1 | CP | EES | SWPA | EES_ARK | EMINTH | 0 | 338130 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 13WP | 148 | 148 | 103.2 | 114.8 | 114.8566 | 116.028 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 | 171.7214 | AP&L (EES) owns the line (SWPAs facilities good for 167 MVA) | SWPA | CALICO ROCK - NORFORK 161KV CKT 1 | Replace buswork within bay and change metering CT ratio, replace wavetraps. Entergy must also reconductor their line to increase the rating. | 236 | 236 | 236 | 236 |  | 18 | 3 |  |  |  |  | New ratings are based on CT limits. They assume that Entergy also upgrades their line. | 100000 | 2007-04-20 | [23 empty] | 2010-12-01 | 2010-12-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 2 | 2007AG2AFS81T32273218SP | FROM->TO | CALICO ROCK - NORFORK 161KV CKT 1 | CP | EES | SWPA | EES_ARK | EMINTH | 0 | 338130 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 18SP | 148 | 148 | 104.3 | 124.6 | 125.0885 | 125.8881 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 | 186.3144 | AP&L (EES) owns the line (SWPAs facilities good for 167 MVA) | SWPA | CALICO ROCK - NORFORK 161KV CKT 1 | Replace buswork within bay and change metering CT ratio, replace wavetraps. Entergy must also reconductor their line to increase the rating. | 236 | 236 | 236 | 236 |  | 18 | 3 |  |  |  |  | New ratings are based on CT limits. They assume that Entergy also upgrades their line. | 100000 | 2007-04-20 | [23 empty] | 2010-12-01 | 2010-12-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T8712218SPG | FROM->TO | CALICO ROCK - NORFORK 161KV CKT 1 | CP | EES | SWPA | EES_ARK | EMINTH | 0 | 338130 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 18SP | 148 | 148 |  | 115.6 | 115.8039 | 116.5171 | [7 empty] | CATEGORYB | GENOUT | GEN532751 1-WOLF CREEK GENERATING STATION UNIT 1 | 0 | 0 |  | 0 |  | 0 |  |  | 172.4453 | AP&L (EES) owns the line (SWPAs facilities good for 167 MVA) | SWPA | CALICO ROCK - NORFORK 161KV CKT 1 | Replace buswork within bay and change metering CT ratio, replace wavetraps. Entergy must also reconductor their line to increase the rating. | 236 | 236 | 236 | 236 |  | 18 | 3 |  |  |  |  | New ratings are based on CT limits. They assume that Entergy also upgrades their line. | 100000 | 2007-04-20 | [23 empty] | 2010-12-01 | 2010-12-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 2 | 2007AG2AFS81T22413218SP | FROM->TO | CALICO ROCK - NORFORK 161KV CKT 1 | CP | EES | SWPA | EES_ARK | EMINTH | 0 | 338130 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 18SP | 148 | 148 |  | 115 | 115.4077 | 115.9211 | [7 empty] | CATEGORYB | SINGLE | DELL 500 - INDEPENDENCE 500KV CKT 1 | 0 | 338145 | 8ISES 5 500.00 | 338187 | 8DELL 5 500.00 | 0 |  | 1 | 171.5632 | AP&L (EES) owns the line (SWPAs facilities good for 167 MVA) | SWPA | CALICO ROCK - NORFORK 161KV CKT 1 | Replace buswork within bay and change metering CT ratio, replace wavetraps. Entergy must also reconductor their line to increase the rating. | 236 | 236 | 236 | 236 |  | 18 | 3 |  |  |  |  | New ratings are based on CT limits. They assume that Entergy also upgrades their line. | 100000 | 2007-04-20 | [23 empty] | 2010-12-01 | 2010-12-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 2 | 2007AG2AFS81T9073218SP | FROM->TO | CALICO ROCK - NORFORK 161KV CKT 1 | CP | EES | SWPA | EES_ARK | EMINTH | 0 | 338130 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 18SP | 148 | 148 |  | 113.6 | 113.9781 | 114.9257 | [7 empty] | CATEGORYB | SINGLE | WHITEWATER EAST - WILHELMINA 345KV CKT 1 | 0 | 300051 | 7WILHLM 345.00 | 300054 | 7GOBKNOB 345.00 | 0 |  | 1 | 170.09 | AP&L (EES) owns the line (SWPAs facilities good for 167 MVA) | SWPA | CALICO ROCK - NORFORK 161KV CKT 1 | Replace buswork within bay and change metering CT ratio, replace wavetraps. Entergy must also reconductor their line to increase the rating. | 236 | 236 | 236 | 236 |  | 18 | 3 |  |  |  |  | New ratings are based on CT limits. They assume that Entergy also upgrades their line. | 100000 | 2007-04-20 | [23 empty] | 2010-12-01 | 2010-12-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2007AG2AFS81T5105518SP | TO->FROM | CARNEGIE - FORT COBB 138KV CKT 1 | REL | AEPW | AEPW | WESTERN | WESTERN | 0 | 511454 | FTCOBNG4 138.00 | 511445 | CARNEG-4 138.00 | 0 |  | 1 | 18SP | 131 | 151 | 118.5 | 100.3 | 97.9033 | 104.7775 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - HOLCOMB 345KV CKT 1 | 0 | 523853 | FINNEY7 345.00 | 531449 | HOLCOMB7 345.00 | 0 |  | 1 |  |  | AEPW | CARNEGIE - FORT COBB 138KV CKT 1 | Reconductor 11.03 miles with 795 ACSR Carnegie -Fort Cobb | [12 empty] | 7500000 | [24 empty] | 2018-06-01 | 2018-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 2 | 2007AG2AFS81T40444218SP | TO->FROM | CARNEGIE - FORT COBB 138KV CKT 1 | REL | AEPW | AEPW | WESTERN | WESTERN | 0 | 511454 | FTCOBNG4 138.00 | 511445 | CARNEG-4 138.00 | 0 |  | 1 | 18SP | 131 | 151 | 102.0 |  | 95.136 | 101.6857 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05B | 0 | 0 |  | 0 |  | 0 |  |  |  |  | AEPW | CARNEGIE - FORT COBB 138KV CKT 1 | Reconductor 11.03 miles with 795 ACSR Carnegie -Fort Cobb | [12 empty] | 7500000 | [24 empty] | 2018-06-01 | 2018-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 2 | 2007AG2AFS81T4124218SP | TO->FROM | CARNEGIE - FORT COBB 138KV CKT 1 | REL | AEPW | AEPW | WESTERN | WESTERN | 0 | 511454 | FTCOBNG4 138.00 | 511445 | CARNEG-4 138.00 | 0 |  | 1 | 18SP | 131 | 151 |  |  | 94.9659 | 100.8847 | [7 empty] | CATEGORYB | SINGLE | CACHE - SNYDER 138KV CKT 1 | 0 | 511435 | SNYDER-4 138.00 | 511500 | CACHE4 138.00 | 0 |  | 1 |  |  | AEPW | CARNEGIE - FORT COBB 138KV CKT 1 | Reconductor 11.03 miles with 795 ACSR Carnegie -Fort Cobb | [12 empty] | 7500000 | [24 empty] | 2018-06-01 | 2018-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2007AG2AFS81T5115518SP | FROM->TO | CARNEGIE - HOBART JUNCTION 138KV CKT 1 | REL | AEPW | AEPW | WESTERN | WESTERN | 0 | 511445 | CARNEG-4 138.00 | 511463 | HOB-JCT4 138.00 | 0 |  | 1 | 18SP | 131 | 143 | 118.8 |  | 97.3364 | 104.3589 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - HOLCOMB 345KV CKT 1 | 0 | 523853 | FINNEY7 345.00 | 531449 | HOLCOMB7 345.00 | 0 |  | 1 |  |  | AEPW | CARNEGIE - HOBART JUNCTION 138KV CKT 1 | Reconductor 26.15 miles with 795 ACSR from Carnegie-Hobart Junction | [12 empty] | 18300000 | [24 empty] | 2018-06-01 | 2018-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 2 | 2007AG2AFS81T40454218SP | FROM->TO | CARNEGIE - HOBART JUNCTION 138KV CKT 1 | REL | AEPW | AEPW | WESTERN | WESTERN | 0 | 511445 | CARNEG-4 138.00 | 511463 | HOB-JCT4 138.00 | 0 |  | 1 | 18SP | 131 | 143 | 101.7 |  | 94.5729 | 101.3532 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05B | 0 | 0 |  | 0 |  | 0 |  |  |  |  | AEPW | CARNEGIE - HOBART JUNCTION 138KV CKT 1 | Reconductor 26.15 miles with 795 ACSR from Carnegie-Hobart Junction | [12 empty] | 18300000 | [24 empty] | 2018-06-01 | 2018-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 2 | 2007AG2AFS81T4134218SP | FROM->TO | CARNEGIE - HOBART JUNCTION 138KV CKT 1 | REL | AEPW | AEPW | WESTERN | WESTERN | 0 | 511445 | CARNEG-4 138.00 | 511463 | HOB-JCT4 138.00 | 0 |  | 1 | 18SP | 131 | 143 |  |  | 94.3934 | 100.5075 | [7 empty] | CATEGORYB | SINGLE | CACHE - SNYDER 138KV CKT 1 | 0 | 511435 | SNYDER-4 138.00 | 511500 | CACHE4 138.00 | 0 |  | 1 |  |  | AEPW | CARNEGIE - HOBART JUNCTION 138KV CKT 1 | Reconductor 26.15 miles with 795 ACSR from Carnegie-Hobart Junction | [12 empty] | 18300000 | [24 empty] | 2018-06-01 | 2018-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T10853313SP | FROM->TO | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 | 13SP | 84 | 84 | 112.9 | 116.3 | 116.5763 | 126.8752 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 1 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T10853313SP | FROM->TO | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 | 13SP | 84 | 84 | 115.1 | 116.3 | 116.5763 | 126.8752 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 1 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T10853313SP | FROM->TO | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 | 13SP | 84 | 84 | 112.9 | 116.3 | 116.5763 | 126.8752 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 1 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T10853313SP | FROM->TO | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 | 13SP | 84 | 84 | 115.1 | 116.3 | 116.5763 | 126.8752 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 1 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T10853313SP | FROM->TO | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 | 13SP | 84 | 84 | 112.9 | 116.3 | 116.5763 | 126.8752 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 1 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T10853313SP | FROM->TO | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 | 13SP | 84 | 84 | 115.1 | 116.3 | 116.5763 | 126.8752 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 1 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T10853313SP | FROM->TO | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 | 13SP | 84 | 84 | 112.9 | 116.3 | 116.5763 | 126.8752 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 1 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T10853313SP | FROM->TO | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 | 13SP | 84 | 84 | 112.9 | 116.3 | 116.5763 | 126.8752 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 1 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T10853313SP | FROM->TO | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 | 13SP | 84 | 84 | 115.1 | 116.3 | 116.5763 | 126.8752 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 1 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T10853313SP | FROM->TO | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 | 13SP | 84 | 84 | 112.9 | 116.3 | 116.5763 | 126.8752 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 1 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T10853313SP | FROM->TO | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 | 13SP | 84 | 84 | 115.1 | 116.3 | 116.5763 | 126.8752 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 1 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T10853313SP | FROM->TO | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 | 13SP | 84 | 84 | 115.1 | 116.3 | 116.5763 | 126.8752 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 1 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T22533318SP | FROM->TO | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 | 18SP | 84 | 84 | 129.1 | 132.8 | 132.7843 | 142.9923 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 1 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T22533318SP | FROM->TO | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 | 18SP | 84 | 84 | 129.1 | 132.8 | 132.7843 | 142.9923 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 1 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T22533318SP | FROM->TO | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 | 18SP | 84 | 84 | 126.0 | 132.8 | 132.7843 | 142.9923 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 1 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T22533318SP | FROM->TO | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 | 18SP | 84 | 84 | 129.1 | 132.8 | 132.7843 | 142.9923 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 1 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T22533318SP | FROM->TO | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 | 18SP | 84 | 84 | 126.0 | 132.8 | 132.7843 | 142.9923 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 1 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T22533318SP | FROM->TO | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 | 18SP | 84 | 84 | 129.1 | 132.8 | 132.7843 | 142.9923 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 1 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T22533318SP | FROM->TO | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 | 18SP | 84 | 84 | 126.0 | 132.8 | 132.7843 | 142.9923 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 1 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T22533318SP | FROM->TO | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 | 18SP | 84 | 84 | 126.0 | 132.8 | 132.7843 | 142.9923 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 1 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T22533318SP | FROM->TO | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 | 18SP | 84 | 84 | 126.0 | 132.8 | 132.7843 | 142.9923 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 1 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T22533318SP | FROM->TO | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 | 18SP | 84 | 84 | 129.1 | 132.8 | 132.7843 | 142.9923 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 1 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T22533318SP | FROM->TO | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 | 18SP | 84 | 84 | 126.0 | 132.8 | 132.7843 | 142.9923 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 1 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T22533318SP | FROM->TO | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 | 18SP | 84 | 84 | 129.1 | 132.8 | 132.7843 | 142.9923 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 1 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T10833313SP | FROM->TO | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 | 13SP | 84 | 84 | 112.2 | 115.6 | 115.9345 | 126.1213 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 2 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T10833313SP | FROM->TO | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 | 13SP | 84 | 84 | 114.4 | 115.6 | 115.9345 | 126.1213 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 2 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T10833313SP | FROM->TO | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 | 13SP | 84 | 84 | 114.4 | 115.6 | 115.9345 | 126.1213 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 2 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T10833313SP | FROM->TO | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 | 13SP | 84 | 84 | 112.2 | 115.6 | 115.9345 | 126.1213 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 2 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T10833313SP | FROM->TO | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 | 13SP | 84 | 84 | 114.4 | 115.6 | 115.9345 | 126.1213 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 2 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T10833313SP | FROM->TO | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 | 13SP | 84 | 84 | 112.2 | 115.6 | 115.9345 | 126.1213 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 2 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T10833313SP | FROM->TO | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 | 13SP | 84 | 84 | 114.4 | 115.6 | 115.9345 | 126.1213 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 2 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T10833313SP | FROM->TO | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 | 13SP | 84 | 84 | 112.2 | 115.6 | 115.9345 | 126.1213 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 2 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T10833313SP | FROM->TO | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 | 13SP | 84 | 84 | 112.2 | 115.6 | 115.9345 | 126.1213 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 2 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T10833313SP | FROM->TO | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 | 13SP | 84 | 84 | 114.4 | 115.6 | 115.9345 | 126.1213 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 2 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T10833313SP | FROM->TO | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 | 13SP | 84 | 84 | 112.2 | 115.6 | 115.9345 | 126.1213 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 2 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T10833313SP | FROM->TO | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 | 13SP | 84 | 84 | 114.4 | 115.6 | 115.9345 | 126.1213 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 2 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T22513318SP | FROM->TO | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 | 18SP | 84 | 84 | 128.4 | 132.1 | 131.9796 | 142.1354 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 2 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T22513318SP | FROM->TO | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 | 18SP | 84 | 84 | 125.1 | 132.1 | 131.9796 | 142.1354 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 2 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T22513318SP | FROM->TO | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 | 18SP | 84 | 84 | 128.4 | 132.1 | 131.9796 | 142.1354 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 2 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T22513318SP | FROM->TO | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 | 18SP | 84 | 84 | 125.1 | 132.1 | 131.9796 | 142.1354 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 2 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T22513318SP | FROM->TO | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 | 18SP | 84 | 84 | 128.4 | 132.1 | 131.9796 | 142.1354 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 2 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T22513318SP | FROM->TO | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 | 18SP | 84 | 84 | 125.1 | 132.1 | 131.9796 | 142.1354 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 2 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T22513318SP | FROM->TO | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 | 18SP | 84 | 84 | 128.4 | 132.1 | 131.9796 | 142.1354 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 2 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T22513318SP | FROM->TO | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 | 18SP | 84 | 84 | 125.1 | 132.1 | 131.9796 | 142.1354 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 2 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T22513318SP | FROM->TO | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 | 18SP | 84 | 84 | 125.1 | 132.1 | 131.9796 | 142.1354 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 2 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T22513318SP | FROM->TO | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 | 18SP | 84 | 84 | 128.4 | 132.1 | 131.9796 | 142.1354 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 2 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T22513318SP | FROM->TO | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 | 18SP | 84 | 84 | 125.1 | 132.1 | 131.9796 | 142.1354 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 2 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T22513318SP | FROM->TO | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505489 | CRG X2 1 13.800 | 1 | 18SP | 84 | 84 | 128.4 | 132.1 | 131.9796 | 142.1354 | [7 empty] | CATEGORYB | SINGLE | CARTHAGE (CRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505488 | CARTHAG5 161.00 | 505490 | CARTHG 2 69.000 | 505487 | CRG X1 1 13.800 | 1 |  | 1) Increase generation at Carthage, or 2) open Carthage-Reeds 69kV line, or 3) shed load at Carthage | SWPA | CARTHAGE (CRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer 2 with larger unit -125 MVA | [37 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 4 | 4 | 2007AG2AFS81V10664418SP |  | CASHION 69KV | EXP | WFEC |  | AEP-IM |  |  | 520847 | CASHION2 69.000 | [5 empty] | 18SP | [6 empty] | 0.71273 | 0.72463 | 0.73698 | 0.72163 | 0.96282 | 0.9 | 1.05 | CATEGORYB | SINGLE | DOVER SW (DOVER) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 520882 | DOVERSW4 138.00 | 520881 | DOVERSW2 69.000 | 521166 | DVRTERT 13.800 | 1 |  |  | WFEC | Multi-Dover-Twin Lake_Cresent 138 kV | Convert 69 kV to 138 kV and install terminal equipment at Dover SW; Instal 7 miles of new 138 kV fro WFEC Twin Lakes to OGE Cresent substation | [37 empty] | 2014-06-01 | 2014-06-01
2007-AG2 | AFS9 | 1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 4 | 2 | 2007AG2AFS81T2634209SP | FROM->TO | CHISHOLM - RIPLEY 69KV CKT 1 | EXP | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533786 | CHISHLM2 69.000 | 533832 | RIPLEYM2 69.000 | 0 |  | 1 | 09SP | 116 | 128 | 105.0 | 105.5 | 105.5458 | 105.605 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  | WERE | CHISHOLM - RIPLEY 69KV CKT 1 | Tear down and rebuild 2.40 miles using single 1192.5 ACSR operated at 69 kV. | 134 | 137 |  |  |  | 18 | 18 | [5 empty] | 1000000 | 2008-01-01 | [23 empty] | 2009-06-01 | 2012-06-01 | 2011-10-01
2007-AG2 | AFS9 | CONT-0600 - 17th Street 138-69kV XFMR | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T9172209SP | FROM->TO | CHISHOLM - RIPLEY 69KV CKT 1 | EXP | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533786 | CHISHLM2 69.000 | 533832 | RIPLEYM2 69.000 | 0 |  | 1 | 09SP | 116 | 128 | 103.9 | 103.8 | 103.9071 | 103.9496 | [7 empty] | CATEGORYB | SINGLE | SEVENTEENTH (17TH 4X) 138/69/11.295KV TRANSFORMER CKT 1 | 1 | 533064 | 17TH 4 138.00 | 533840 | 17TH 2 69.000 | 533112 | 17TH 1 11.295 | 1 |  |  | WERE | CHISHOLM - RIPLEY 69KV CKT 1 | Tear down and rebuild 2.40 miles using single 1192.5 ACSR operated at 69 kV. | 134 | 137 |  |  |  | 18 | 18 | [5 empty] | 1000000 | 2008-01-01 | [23 empty] | 2009-06-01 | 2012-06-01 | 2011-10-01
2007-AG2 | AFS9 | 1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T3202210SP | FROM->TO | CHISHOLM - RIPLEY 69KV CKT 1 | EXP | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533786 | CHISHLM2 69.000 | 533832 | RIPLEYM2 69.000 | 0 |  | 1 | 10SP | 116 | 128 | 108.9 | 107.6 | 108.8166 | 108.9916 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  | WERE | CHISHOLM - RIPLEY 69KV CKT 1 | Tear down and rebuild 2.40 miles using single 1192.5 ACSR operated at 69 kV. | 134 | 137 |  |  |  | 18 | 18 | [5 empty] | 1000000 | 2008-01-01 | [23 empty] | 2009-06-01 | 2012-06-01 | 2011-10-01
2007-AG2 | AFS9 | CONT-0600 - 17th Street 138-69kV XFMR | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T12672210SP | FROM->TO | CHISHOLM - RIPLEY 69KV CKT 1 | EXP | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533786 | CHISHLM2 69.000 | 533832 | RIPLEYM2 69.000 | 0 |  | 1 | 10SP | 116 | 128 | 106.8 | 105.4 | 106.6377 | 106.7557 | [7 empty] | CATEGORYB | SINGLE | SEVENTEENTH (17TH 4X) 138/69/11.295KV TRANSFORMER CKT 1 | 1 | 533064 | 17TH 4 138.00 | 533840 | 17TH 2 69.000 | 533112 | 17TH 1 11.295 | 1 |  |  | WERE | CHISHOLM - RIPLEY 69KV CKT 1 | Tear down and rebuild 2.40 miles using single 1192.5 ACSR operated at 69 kV. | 134 | 137 |  |  |  | 18 | 18 | [5 empty] | 1000000 | 2008-01-01 | [23 empty] | 2009-06-01 | 2012-06-01 | 2011-10-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 4 | 4 | 2007AG2AFS81V10674418SP |  | CIMARRON 69KV | EXP | WFEC |  | AEP-IM |  |  | 520853 | KNGFSHSW2 69.000 | [5 empty] | 18SP | [6 empty] | 0.78703 | 0.79821 | 0.80529 | 0.79537 | 0.97399 | 0.9 | 1.05 | CATEGORYB | SINGLE | DOVER SW (DOVER) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 520882 | DOVERSW4 138.00 | 520881 | DOVERSW2 69.000 | 521166 | DVRTERT 13.800 | 1 |  |  | WFEC | Multi-Dover-Twin Lake_Cresent 138 kV | Convert 69 kV to 138 kV and install terminal equipment at Dover SW; Instal 7 miles of new 138 kV fro WFEC Twin Lakes to OGE Cresent substation | [37 empty] | 2014-06-01 | 2014-06-01
2007-AG2 | AFS9 | CONT-0626 - HEC 115-69kV XFMR | FDNS |  | FDNS |  | 4 | 1 | 2007AG2AFS81T6984110SP | TO->FROM | CIRCLE - HUTCHINSON GAS TURBINE STATION 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533421 | HEC GT 3 115.00 | 533413 | CIRCLE 3 115.00 | 0 |  | 1 | 10SP | 141 | 152 |  | 111.9 | 111.9593 | 111.9344 | [7 empty] | CATEGORYB | SINGLE | HUTCHINSON ENERGY CENTER (HEC 122X) 115/69/34.5KV TRANSFORMER CKT 1 | 1 | 533419 | HEC 3 115.00 | 533513 | HEC 2 69.000 | 533445 | HEC 1 34.500 | 1 |  |  | WERE | CIRCLE - HUTCHINSON GAS TURBINE STATION 115KV CKT 1 | Rebuild Circle - HEC GT 115 kV line. | 223 | 240 | 223 | 240 | 0.38 | 12 | 6 | No | 0.00023 | 0.00205 | 0.0003 | Rebuild HEC-Circle 115 kV line. ***Cost estimate is for all work on HEC-HEC GT-Circle loop.*** | 300000 | 2007-01-01 | [23 empty] | 2010-06-01 | 2009-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 4 | 1 | 2007AG2AFS81T44110SP | TO->FROM | CIRCLE - HUTCHINSON GAS TURBINE STATION 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533421 | HEC GT 3 115.00 | 533413 | CIRCLE 3 115.00 | 0 |  | 1 | 10SP | 141 | 152 |  | 103.8 | 103.8866 | 103.8512 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WERE | CIRCLE - HUTCHINSON GAS TURBINE STATION 115KV CKT 1 | Rebuild Circle - HEC GT 115 kV line. | 223 | 240 | 223 | 240 | 0.38 | 12 | 6 | No | 0.00023 | 0.00205 | 0.0003 | Rebuild HEC-Circle 115 kV line. ***Cost estimate is for all work on HEC-HEC GT-Circle loop.*** | 300000 | 2007-01-01 | [23 empty] | 2010-06-01 | 2009-06-01
2007-AG2 | AFS9 | CONT-0626 - HEC 115-69kV XFMR | FDNS |  | FDNS |  | 2 | 1 | 2007AG2AFS81T11942113SP | TO->FROM | CIRCLE - HUTCHINSON GAS TURBINE STATION 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533421 | HEC GT 3 115.00 | 533413 | CIRCLE 3 115.00 | 0 |  | 1 | 13SP | 141 | 152 | 111.5 | 120.6 | 120.5984 | 120.6083 | [7 empty] | CATEGORYB | SINGLE | HUTCHINSON ENERGY CENTER (HEC 122X) 115/69/34.5KV TRANSFORMER CKT 1 | 1 | 533419 | HEC 3 115.00 | 533513 | HEC 2 69.000 | 533445 | HEC 1 34.500 | 1 |  |  | WERE | CIRCLE - HUTCHINSON GAS TURBINE STATION 115KV CKT 1 | Rebuild Circle - HEC GT 115 kV line. | 223 | 240 | 223 | 240 | 0.38 | 12 | 6 | No | 0.00023 | 0.00205 | 0.0003 | Rebuild HEC-Circle 115 kV line. ***Cost estimate is for all work on HEC-HEC GT-Circle loop.*** | 300000 | 2007-01-01 | [23 empty] | 2010-06-01 | 2009-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 1 | 2007AG2AFS81T72113SP | TO->FROM | CIRCLE - HUTCHINSON GAS TURBINE STATION 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533421 | HEC GT 3 115.00 | 533413 | CIRCLE 3 115.00 | 0 |  | 1 | 13SP | 141 | 152 | 103.6 | 112.3 | 112.2863 | 112.2951 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WERE | CIRCLE - HUTCHINSON GAS TURBINE STATION 115KV CKT 1 | Rebuild Circle - HEC GT 115 kV line. | 223 | 240 | 223 | 240 | 0.38 | 12 | 6 | No | 0.00023 | 0.00205 | 0.0003 | Rebuild HEC-Circle 115 kV line. ***Cost estimate is for all work on HEC-HEC GT-Circle loop.*** | 300000 | 2007-01-01 | [23 empty] | 2010-06-01 | 2009-06-01
2007-AG2 | AFS9 | CONT-0626 - HEC 115-69kV XFMR | FDNS |  | FDNS |  | 3 | 1 | 2007AG2AFS81T24453118SP | TO->FROM | CIRCLE - HUTCHINSON GAS TURBINE STATION 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533421 | HEC GT 3 115.00 | 533413 | CIRCLE 3 115.00 | 0 |  | 1 | 18SP | 141 | 152 | 120.6 | 120.7 | 121.2567 | 120.6872 | [7 empty] | CATEGORYB | SINGLE | HUTCHINSON ENERGY CENTER (HEC 122X) 115/69/34.5KV TRANSFORMER CKT 1 | 1 | 533419 | HEC 3 115.00 | 533513 | HEC 2 69.000 | 533445 | HEC 1 34.500 | 1 |  |  | WERE | CIRCLE - HUTCHINSON GAS TURBINE STATION 115KV CKT 1 | Rebuild Circle - HEC GT 115 kV line. | 223 | 240 | 223 | 240 | 0.38 | 12 | 6 | No | 0.00023 | 0.00205 | 0.0003 | Rebuild HEC-Circle 115 kV line. ***Cost estimate is for all work on HEC-HEC GT-Circle loop.*** | 300000 | 2007-01-01 | [23 empty] | 2010-06-01 | 2009-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 1 | 2007AG2AFS81T123118SP | TO->FROM | CIRCLE - HUTCHINSON GAS TURBINE STATION 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533421 | HEC GT 3 115.00 | 533413 | CIRCLE 3 115.00 | 0 |  | 1 | 18SP | 141 | 152 | 112.1 | 112.2 | 112.3555 | 112.2 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WERE | CIRCLE - HUTCHINSON GAS TURBINE STATION 115KV CKT 1 | Rebuild Circle - HEC GT 115 kV line. | 223 | 240 | 223 | 240 | 0.38 | 12 | 6 | No | 0.00023 | 0.00205 | 0.0003 | Rebuild HEC-Circle 115 kV line. ***Cost estimate is for all work on HEC-HEC GT-Circle loop.*** | 300000 | 2007-01-01 | [23 empty] | 2010-06-01 | 2009-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T373309FA | FROM->TO | COFFEYVILLE TAP - DEARING 138KV CKT 1 | CP | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 09FA | 202 | 232 |  | 105.4 | 107.5123 | 108.3679 | [7 empty] | CATEGORYB | SINGLE | DELAWARE - NEOSHO 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 532793 | NEOSHO 7 345.00 | 0 |  | 1 |  | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | AEPW | COFFEYVILLE TAP - DEARING 138KV CKT 1 AEPW | Tie Line, Reconductor 1.09 miles of 795 ACSR with 1590 ACSR. | 368 | 512 | 434 | 555 | 1.09 | 15 | 6 |  | 0.00039 | 0.003837 | 0.00133 | AEP: The limiting factor is the AEP portion of 795 ACSR conductor. New ratings are for AEP only. The new limit is the 1590 ACSR conductor. | 950000 | 2007-04-13 | [23 empty] | 2009-06-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T373309FA | FROM->TO | COFFEYVILLE TAP - DEARING 138KV CKT 1 | CP | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 09FA | 202 | 232 |  | 105.4 | 107.5123 | 108.3679 | [7 empty] | CATEGORYB | SINGLE | DELAWARE - NEOSHO 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 532793 | NEOSHO 7 345.00 | 0 |  | 1 |  | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | WERE | COFFEYVILLE TAP - DEARING 138KV CKT 1 WERE | Tie Line, Rebuild 3.93 miles of 795 ACSR with 1590 ACSR. | 287 | 287 | 287 | 287 | 3.93 | 15 | 6 |  | 0.0014061 | 0.013834 | 0.0047953 |  | 3000000 | 2006-06-01 | [23 empty] | 2008-12-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T373309FA | FROM->TO | COFFEYVILLE TAP - DEARING 138KV CKT 1 | CP | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 09FA | 202 | 232 |  | 105.4 | 107.5123 | 108.3679 | [7 empty] | CATEGORYB | SINGLE | DELAWARE - NEOSHO 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 532793 | NEOSHO 7 345.00 | 0 |  | 1 |  | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | WERE | COFFEYVILLE TAP - DEARING 138KV CKT 1 WERE #2 | Replace Terminal Equipment. | 478 | 478 |  |  | 3.93 | [7 empty] | 1000000 | 2007-01-01 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T483309SH | FROM->TO | COFFEYVILLE TAP - DEARING 138KV CKT 1 | CP | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 09SH | 202 | 232 |  | 101.8 | 104.6243 | 105.5009 | [7 empty] | CATEGORYB | SINGLE | DELAWARE - NEOSHO 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 532793 | NEOSHO 7 345.00 | 0 |  | 1 |  | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | AEPW | COFFEYVILLE TAP - DEARING 138KV CKT 1 AEPW | Tie Line, Reconductor 1.09 miles of 795 ACSR with 1590 ACSR. | 368 | 512 | 434 | 555 | 1.09 | 15 | 6 |  | 0.00039 | 0.003837 | 0.00133 | AEP: The limiting factor is the AEP portion of 795 ACSR conductor. New ratings are for AEP only. The new limit is the 1590 ACSR conductor. | 950000 | 2007-04-13 | [23 empty] | 2009-06-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T483309SH | FROM->TO | COFFEYVILLE TAP - DEARING 138KV CKT 1 | CP | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 09SH | 202 | 232 |  | 101.8 | 104.6243 | 105.5009 | [7 empty] | CATEGORYB | SINGLE | DELAWARE - NEOSHO 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 532793 | NEOSHO 7 345.00 | 0 |  | 1 |  | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | WERE | COFFEYVILLE TAP - DEARING 138KV CKT 1 WERE | Tie Line, Rebuild 3.93 miles of 795 ACSR with 1590 ACSR. | 287 | 287 | 287 | 287 | 3.93 | 15 | 6 |  | 0.0014061 | 0.013834 | 0.0047953 |  | 3000000 | 2006-06-01 | [23 empty] | 2008-12-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T483309SH | FROM->TO | COFFEYVILLE TAP - DEARING 138KV CKT 1 | CP | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 09SH | 202 | 232 |  | 101.8 | 104.6243 | 105.5009 | [7 empty] | CATEGORYB | SINGLE | DELAWARE - NEOSHO 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 532793 | NEOSHO 7 345.00 | 0 |  | 1 |  | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | WERE | COFFEYVILLE TAP - DEARING 138KV CKT 1 WERE #2 | Replace Terminal Equipment. | 478 | 478 |  |  | 3.93 | [7 empty] | 1000000 | 2007-01-01 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 3 | 3 | 2007AG2AFS81T753309SP | FROM->TO | COFFEYVILLE TAP - DEARING 138KV CKT 1 | CP | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 09SP | 202 | 232 |  |  | 100.8386 | 101.613 | [7 empty] | CATEGORYB | SINGLE | DELAWARE - NEOSHO 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 532793 | NEOSHO 7 345.00 | 0 |  | 1 |  | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | AEPW | COFFEYVILLE TAP - DEARING 138KV CKT 1 AEPW | Tie Line, Reconductor 1.09 miles of 795 ACSR with 1590 ACSR. | 368 | 512 | 434 | 555 | 1.09 | 15 | 6 |  | 0.00039 | 0.003837 | 0.00133 | AEP: The limiting factor is the AEP portion of 795 ACSR conductor. New ratings are for AEP only. The new limit is the 1590 ACSR conductor. | 950000 | 2007-04-13 | [23 empty] | 2009-06-01 | 2010-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 3 | 3 | 2007AG2AFS81T753309SP | FROM->TO | COFFEYVILLE TAP - DEARING 138KV CKT 1 | CP | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 09SP | 202 | 232 |  |  | 100.8386 | 101.613 | [7 empty] | CATEGORYB | SINGLE | DELAWARE - NEOSHO 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 532793 | NEOSHO 7 345.00 | 0 |  | 1 |  | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | WERE | COFFEYVILLE TAP - DEARING 138KV CKT 1 WERE | Tie Line, Rebuild 3.93 miles of 795 ACSR with 1590 ACSR. | 287 | 287 | 287 | 287 | 3.93 | 15 | 6 |  | 0.0014061 | 0.013834 | 0.0047953 |  | 3000000 | 2006-06-01 | [23 empty] | 2008-12-01 | 2010-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 3 | 3 | 2007AG2AFS81T753309SP | FROM->TO | COFFEYVILLE TAP - DEARING 138KV CKT 1 | CP | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 09SP | 202 | 232 |  |  | 100.8386 | 101.613 | [7 empty] | CATEGORYB | SINGLE | DELAWARE - NEOSHO 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 532793 | NEOSHO 7 345.00 | 0 |  | 1 |  | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | WERE | COFFEYVILLE TAP - DEARING 138KV CKT 1 WERE #2 | Replace Terminal Equipment. | 478 | 478 |  |  | 3.93 | [7 empty] | 1000000 | 2007-01-01 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T443309SH | TO->FROM | COFFEYVILLE TAP - NORTH BARTLESVILLE 138KV CKT 1 | CP | AEPW | AEPW | TS-KAMO | NORTHERN | 0 | 510386 | NBVILLE4 138.00 | 510422 | COFFEYT4 138.00 | 0 |  | 1 | 09SH | 202 | 235 |  | 100.3 | 102.7766 | 103.3224 | [7 empty] | CATEGORYB | SINGLE | DELAWARE - NORTHEAST STATION 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 510406 | N.E.S.-7 345.00 | 0 |  | 1 |  |  | AEPW | COFFEYVILLE TAP - NORTH BARTLESVILLE 138KV CKT 1 | Rebuild 13.11 miles of 795 ACSR with 1590 ACSR. | 287 | 287 | 287 | 287 | 13.11 | 24 | 9 |  | 0.00468 | 0.04865 | 0.01512 | New Limits will be switches on both ends | 13100000 | 2007-09-18 | [23 empty] | 2009-06-01 | 2011-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81V4062410SP |  | COLE 69KV | EXP | WFEC |  | FLA |  |  | 520861 | COLE 2 69.000 | [5 empty] | 10SP | [6 empty] | 0.75049 | 0.75117 | 0.75122 | 0.751 | 1.0124 | 0.9 | 1.05 | CATEGORYB | SINGLE | OU SW 4 138.00 (OW SW) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 521104 | OU SW 4 138.00 | 521018 | OU SW 2 69.000 | 521183 | OUSWTERT 13.800 | 1 |  |  | WFEC | Norman Area Voltage Conversion | Convert Canadian - OU - Cole - Criner to 138 KV and Canadian-Goldsby-OU-W Norman-Acme-Franklin | [5 empty] | 24 | 18 | [5 empty] | 4000000 | 2007-04-13 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 2 | 2007AG2AFS81V15303218SP |  | COLE 69KV | EXP | WFEC |  | FLA |  |  | 520861 | COLE 2 69.000 | [5 empty] | 18SP | [6 empty] | 0.61021 | 0.61249 | 0.60837 | 0.60837 | 0.97346 | 0.9 | 1.05 | CATEGORYB | SINGLE | OU SW 4 138.00 (OW SW) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 521104 | OU SW 4 138.00 | 521018 | OU SW 2 69.000 | 521183 | OUSWTERT 13.800 | 1 |  |  | WFEC | Norman Area Voltage Conversion | Convert Canadian - OU - Cole - Criner to 138 KV and Canadian-Goldsby-OU-W Norman-Acme-Franklin | [5 empty] | 24 | 18 | [5 empty] | 4000000 | 2007-04-13 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81V4072410SP |  | CRINER 69KV | EXP | WFEC |  | FLA |  |  | 520868 | CRINER 2 69.000 | [5 empty] | 10SP | [6 empty] | 0.74234 | 0.74295 | 0.74299 | 0.74277 | 1.0065 | 0.9 | 1.05 | CATEGORYB | SINGLE | OU SW 4 138.00 (OW SW) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 521104 | OU SW 4 138.00 | 521018 | OU SW 2 69.000 | 521183 | OUSWTERT 13.800 | 1 |  |  | WFEC | Norman Area Voltage Conversion | Convert Canadian - OU - Cole - Criner to 138 KV and Canadian-Goldsby-OU-W Norman-Acme-Franklin | [5 empty] | 24 | 18 | [5 empty] | 4000000 | 2007-04-13 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 2 | 2007AG2AFS81V15313218SP |  | CRINER 69KV | EXP | WFEC |  | FLA |  |  | 520868 | CRINER 2 69.000 | [5 empty] | 18SP | [6 empty] | 0.59889 | 0.60119 | 0.59704 | 0.59704 | 0.96633 | 0.9 | 1.05 | CATEGORYB | SINGLE | OU SW 4 138.00 (OW SW) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 521104 | OU SW 4 138.00 | 521018 | OU SW 2 69.000 | 521183 | OUSWTERT 13.800 | 1 |  |  | WFEC | Norman Area Voltage Conversion | Convert Canadian - OU - Cole - Criner to 138 KV and Canadian-Goldsby-OU-W Norman-Acme-Franklin | [5 empty] | 24 | 18 | [5 empty] | 4000000 | 2007-04-13 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T11782210SP | TO->FROM | DARDANELLE - RUSSELLVILLE SOUTH 161KV CKT 1 | CP | EES | SWPA | EES_ARK | EMINTH | 0 | 337904 | 5RUSL-S 161.00 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 10SP | 335 | 335 | 102.9 | 120.1 | 120.1712 | 120.7243 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 |  |  | SWPA | DARDANELLE - RUSSELLVILLE SOUTH 161KV CKT 1 SWPA #2 | Replace the bus within the bay for the Russellville line. | 457 | 457 |  |  |  | 12 | 12 |  |  |  |  | The next limit (after other equipment in the bay is replaced) will be the main and transfer buses, which are 3" aluminum pipe and are good for 1670 amps. | 40000 | 2008-01-01 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T11782210SP | TO->FROM | DARDANELLE - RUSSELLVILLE SOUTH 161KV CKT 1 | REL | EES | SWPA | EES_ARK | EMINTH | 0 | 337904 | 5RUSL-S 161.00 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 10SP | 335 | 335 | 102.9 | 120.1 | 120.1712 | 120.7243 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 |  |  | SWPA | DARDANELLE - RUSSELLVILLE SOUTH 161KV CKT 1 SWPA #1 | Replace wave trap, disconnect switches, current transformers, and breaker. Bus will limit rating to 1340 amps. | 374 | 374 |  |  |  | 12 | 2 | [5 empty] | 2500000 | 2008-01-01 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T7092210WP | TO->FROM | DARDANELLE - RUSSELLVILLE SOUTH 161KV CKT 1 | CP | EES | SWPA | EES_ARK | EMINTH | 0 | 337904 | 5RUSL-S 161.00 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 10WP | 335 | 335 | 101.2 | 114.4 | 114.5051 | 114.9948 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 |  |  | SWPA | DARDANELLE - RUSSELLVILLE SOUTH 161KV CKT 1 SWPA #2 | Replace the bus within the bay for the Russellville line. | 457 | 457 |  |  |  | 12 | 12 |  |  |  |  | The next limit (after other equipment in the bay is replaced) will be the main and transfer buses, which are 3" aluminum pipe and are good for 1670 amps. | 40000 | 2008-01-01 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T7092210WP | TO->FROM | DARDANELLE - RUSSELLVILLE SOUTH 161KV CKT 1 | REL | EES | SWPA | EES_ARK | EMINTH | 0 | 337904 | 5RUSL-S 161.00 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 10WP | 335 | 335 | 101.2 | 114.4 | 114.5051 | 114.9948 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 |  |  | SWPA | DARDANELLE - RUSSELLVILLE SOUTH 161KV CKT 1 SWPA #1 | Replace wave trap, disconnect switches, current transformers, and breaker. Bus will limit rating to 1340 amps. | 374 | 374 |  |  |  | 12 | 2 | [5 empty] | 2500000 | 2008-01-01 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG2 | AFS9 | ISLAND-LOAD |  |  | FDNS |  | 4 | 2 | 2007AG2AFS81T3504209WP | FROM->TO | DIANA - LONE STAR SOUTH 138KV CKT 1 | EXP | AEPW | AEPW | NWLANTEC | MTPL | 0 | 508831 | DIANA 4 138.00 | 508297 | LSSOUTH4 138.00 | 0 |  | 1 | 09WP | 287 | 287 |  |  | 100.394 | 101.8521 | [7 empty] | CATEGORYB | SINGLE | WILKES (WILKES) 345/138/13.2KV TRANSFORMER CKT 1 | 1 | 508840 | WILKES 4 138.00 | 508841 | WILKES 7 345.00 | 508826 | WILKES-1 13.200 | 1 |  |  | AEPW | DIANA - LONE STAR SOUTH 138KV CKT 1 | Replace switches and reset CT | 287 | 287 | 287 | 316 |  | 12 | [6 empty] | 150000 | 2008-06-20 | [23 empty] | 2009-12-01 | 2010-06-01
2007-AG2 | AFS9 | ISLAND-LOAD |  |  | FDNS |  | 4 | 2 | 2007AG2AFS81T6134210WP | FROM->TO | DIANA - LONE STAR SOUTH 138KV CKT 1 | EXP | AEPW | AEPW | NWLANTEC | MTPL | 0 | 508831 | DIANA 4 138.00 | 508297 | LSSOUTH4 138.00 | 0 |  | 1 | 10WP | 287 | 287 |  |  | 102.0305 | 103.7195 | [7 empty] | CATEGORYB | SINGLE | WILKES (WILKES) 345/138/13.2KV TRANSFORMER CKT 1 | 1 | 508840 | WILKES 4 138.00 | 508841 | WILKES 7 345.00 | 508826 | WILKES-1 13.200 | 1 |  |  | AEPW | DIANA - LONE STAR SOUTH 138KV CKT 1 | Replace switches and reset CT | 287 | 287 | 287 | 316 |  | 12 | [6 empty] | 150000 | 2008-06-20 | [23 empty] | 2009-12-01 | 2010-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 4 | 4 | 2007AG2AFS81V10684418SP |  | DOVER 69KV | EXP | WFEC |  | AEP-IM |  |  | 520879 | DOVER 2 69.000 | [5 empty] | 18SP | [6 empty] | 0.74545 | 0.75654 | 0.76691 | 0.75384 | 0.97537 | 0.9 | 1.05 | CATEGORYB | SINGLE | DOVER SW (DOVER) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 520882 | DOVERSW4 138.00 | 520881 | DOVERSW2 69.000 | 521166 | DVRTERT 13.800 | 1 |  |  | WFEC | Multi-Dover-Twin Lake_Cresent 138 kV | Convert 69 kV to 138 kV and install terminal equipment at Dover SW; Instal 7 miles of new 138 kV fro WFEC Twin Lakes to OGE Cresent substation | [37 empty] | 2014-06-01 | 2014-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 4 | 4 | 2007AG2AFS81V10694418SP |  | DOVER SW 69KV | EXP | WFEC |  | AEP-IM |  |  | 520881 | DOVERSW2 69.000 | [5 empty] | 18SP | [6 empty] | 0.78149 | 0.7915 | 0.79959 | 0.78917 | 0.9877 | 0.9 | 1.05 | CATEGORYB | SINGLE | DOVER SW (DOVER) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 520882 | DOVERSW4 138.00 | 520881 | DOVERSW2 69.000 | 521166 | DVRTERT 13.800 | 1 |  |  | WFEC | Multi-Dover-Twin Lake_Cresent 138 kV | Convert 69 kV to 138 kV and install terminal equipment at Dover SW; Instal 7 miles of new 138 kV fro WFEC Twin Lakes to OGE Cresent substation | [37 empty] | 2014-06-01 | 2014-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 4 | 4 | 2007AG2AFS81V10634418SP |  | DOVER TAP 69KV | EXP | OKGE |  | ENID |  |  | 514772 | DOVERTP2 69.000 | [5 empty] | 18SP | [6 empty] | 0.78546 | 0.79523 | 0.80316 | 0.79299 | 0.98759 | 0.9 | 1.05 | CATEGORYB | SINGLE | DOVER SW (DOVER) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 520882 | DOVERSW4 138.00 | 520881 | DOVERSW2 69.000 | 521166 | DVRTERT 13.800 | 1 |  |  | WFEC | Multi-Dover-Twin Lake_Cresent 138 kV | Convert 69 kV to 138 kV and install terminal equipment at Dover SW; Instal 7 miles of new 138 kV fro WFEC Twin Lakes to OGE Cresent substation | [37 empty] | 2014-06-01 | 2014-06-01
GEN-2001-024 | Mattison | [7 empty] | 506957506927012SP | TO->FROM | DYESS - TONTITOWN 161KV CKT 1 | U | AEPW | AEPW | FAYETTEV | FAYETTEV | 0 | 506957 | TONTITN5 161.00 | 506927 | DYESS 5 161.00 | 0 |  | 1 |  | 451 | 592 |  |  | 238.5 | [9 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | AEPW | DYESS - TONTITOWN 161KV CKT 1 | Add one 161KV terminal for Tontitown | [12 empty] | 537700 | [24 empty] | 2008-06-01 | 2008-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 4 | 4 | 2007AG2AFS81V10704418SP |  | EAST KINGFISHER 69KV | EXP | WFEC |  | AEP-IM |  |  | 520891 | EKNGFSH2 69.000 | [5 empty] | 18SP | [6 empty] | 0.78115 | 0.79239 | 0.79961 | 0.78952 | 0.96931 | 0.9 | 1.05 | CATEGORYB | SINGLE | DOVER SW (DOVER) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 520882 | DOVERSW4 138.00 | 520881 | DOVERSW2 69.000 | 521166 | DVRTERT 13.800 | 1 |  |  | WFEC | Multi-Dover-Twin Lake_Cresent 138 kV | Convert 69 kV to 138 kV and install terminal equipment at Dover SW; Instal 7 miles of new 138 kV fro WFEC Twin Lakes to OGE Cresent substation | [37 empty] | 2014-06-01 | 2014-06-01
2007-AG2 | AFS9 | CONT-0617 - Summit 345-230kV XFMR |  |  | FDNS |  | 3 | 2 | 2007AG2AFS81T9103209SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | EXP | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 09SP | 280 | 308 |  |  | 103.724 | 103.7995 | [7 empty] | CATEGORYB | SINGLE | SUMMIT (SUMMIT1X) 345/230/14.4KV TRANSFORMER CKT 1 | 1 | 532773 | SUMMIT 7 345.00 | 532873 | SUMMIT 6 230.00 | 532813 | SUMMIT 1 14.400 | 1 |  |  | WERE | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | Uprate JEC- E.Manhattan 230 kV line to 100 deg C operation by raising structures | 446 | 490 |  |  |  | 24 | 24 | [5 empty] | 17085937.5 | 2008-01-01 | [23 empty] | 2009-06-01 | 2012-06-01 | 2011-10-01
2007-AG2 | AFS9 | CONT-0617 - Summit 345-230kV XFMR |  |  | FDNS |  | 3 | 2 | 2007AG2AFS81T9103209SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | EXP | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 09SP | 280 | 308 |  |  | 103.724 | 103.7995 | [7 empty] | CATEGORYB | SINGLE | SUMMIT (SUMMIT1X) 345/230/14.4KV TRANSFORMER CKT 1 | 1 | 532773 | SUMMIT 7 345.00 | 532873 | SUMMIT 6 230.00 | 532813 | SUMMIT 1 14.400 | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 |  | 1000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2011-06-01 | 2010-10-01
2007-AG2 | AFS9 | CONT-0402 - JEC - Summit 345kV |  |  | FDNS |  | 3 | 2 | 2007AG2AFS81T2653209SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | EXP | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 09SP | 280 | 308 |  |  | 103.4073 | 103.4835 | [7 empty] | CATEGORYB | SINGLE | JEFFERY ENERGY CENTER - SUMMIT 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532773 | SUMMIT 7 345.00 | 0 |  | 1 |  |  | WERE | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | Uprate JEC- E.Manhattan 230 kV line to 100 deg C operation by raising structures | 446 | 490 |  |  |  | 24 | 24 | [5 empty] | 17085937.5 | 2008-01-01 | [23 empty] | 2009-06-01 | 2012-06-01 | 2011-10-01
2007-AG2 | AFS9 | CONT-0402 - JEC - Summit 345kV |  |  | FDNS |  | 3 | 2 | 2007AG2AFS81T2653209SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | EXP | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 09SP | 280 | 308 |  |  | 103.4073 | 103.4835 | [7 empty] | CATEGORYB | SINGLE | JEFFERY ENERGY CENTER - SUMMIT 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532773 | SUMMIT 7 345.00 | 0 |  | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 |  | 1000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2011-06-01 | 2010-10-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 2 | 2007AG2AFS81T2843210SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | EXP | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 10SP | 280 | 308 |  | 104.8 | 104.0292 | 105.17 | [7 empty] | CATEGORYB | SINGLE | MCDOWELL CREEK - MORRIS COUNTY 230KV CKT 1 | 0 | 532862 | MCDOWEL6 230.00 | 532863 | MORRIS 6 230.00 | 0 |  | 1 |  |  | WERE | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | Uprate JEC- E.Manhattan 230 kV line to 100 deg C operation by raising structures | 446 | 490 |  |  |  | 24 | 24 | [5 empty] | 17085937.5 | 2008-01-01 | [23 empty] | 2009-06-01 | 2012-06-01 | 2011-10-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 2 | 2007AG2AFS81T2843210SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | EXP | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 10SP | 280 | 308 |  | 104.8 | 104.0292 | 105.17 | [7 empty] | CATEGORYB | SINGLE | MCDOWELL CREEK - MORRIS COUNTY 230KV CKT 1 | 0 | 532862 | MCDOWEL6 230.00 | 532863 | MORRIS 6 230.00 | 0 |  | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 |  | 1000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2011-06-01 | 2010-10-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 2 | 2007AG2AFS81T12063210SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | EXP | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 10SP | 280 | 308 |  | 104.8 | 104.0054 | 105.1473 | [7 empty] | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 |  |  | WERE | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | Uprate JEC- E.Manhattan 230 kV line to 100 deg C operation by raising structures | 446 | 490 |  |  |  | 24 | 24 | [5 empty] | 17085937.5 | 2008-01-01 | [23 empty] | 2009-06-01 | 2012-06-01 | 2011-10-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 2 | 2007AG2AFS81T12063210SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | EXP | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 10SP | 280 | 308 |  | 104.8 | 104.0054 | 105.1473 | [7 empty] | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 |  |  | WERE | EAST MANHATTAN - NW MANHATTAN 230/115KV | Tap the Concordia - East Manhattan 230kV line and add a new substation"NW Manhattan"; Add a 230kV/115kV transformer and tap the KSU - Wildcat 115kV line into NW Manhattan | [12 empty] | 17437500 | 2008-01-01 | [23 empty] | 2009-06-01 | 2012-06-01 | 2011-10-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 2 | 2007AG2AFS81T12063210SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | EXP | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 10SP | 280 | 308 |  | 104.8 | 104.0054 | 105.1473 | [7 empty] | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 |  | 1000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2011-06-01 | 2010-10-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 2 | 2007AG2AFS81T2783210SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | EXP | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 10SP | 280 | 308 |  | 103.4 | 102.9156 | 103.8788 | [7 empty] | CATEGORYB | SINGLE | AUBURN ROAD - JEFFREY ENERGY CENTER 230KV CKT 1 | 0 | 532851 | AUBURN 6 230.00 | 532852 | JEC 6 230.00 | 0 |  | 1 |  |  | WERE | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | Uprate JEC- E.Manhattan 230 kV line to 100 deg C operation by raising structures | 446 | 490 |  |  |  | 24 | 24 | [5 empty] | 17085937.5 | 2008-01-01 | [23 empty] | 2009-06-01 | 2012-06-01 | 2011-10-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 2 | 2007AG2AFS81T2783210SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | EXP | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 10SP | 280 | 308 |  | 103.4 | 102.9156 | 103.8788 | [7 empty] | CATEGORYB | SINGLE | AUBURN ROAD - JEFFREY ENERGY CENTER 230KV CKT 1 | 0 | 532851 | AUBURN 6 230.00 | 532852 | JEC 6 230.00 | 0 |  | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 |  | 1000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2011-06-01 | 2010-10-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 3 | 2 | 2007AG2AFS81T3733213SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | EXP | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 13SP | 280 | 308 |  |  | 99.2196 | 100.3978 | [7 empty] | CATEGORYB | SINGLE | MCDOWELL CREEK - MORRIS COUNTY 230KV CKT 1 | 0 | 532862 | MCDOWEL6 230.00 | 532863 | MORRIS 6 230.00 | 0 |  | 1 |  |  | WERE | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | Uprate JEC- E.Manhattan 230 kV line to 100 deg C operation by raising structures | 446 | 490 |  |  |  | 24 | 24 | [5 empty] | 17085937.5 | 2008-01-01 | [23 empty] | 2009-06-01 | 2012-06-01 | 2011-10-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 3 | 2 | 2007AG2AFS81T3733213SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | EXP | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 13SP | 280 | 308 |  |  | 99.2196 | 100.3978 | [7 empty] | CATEGORYB | SINGLE | MCDOWELL CREEK - MORRIS COUNTY 230KV CKT 1 | 0 | 532862 | MCDOWEL6 230.00 | 532863 | MORRIS 6 230.00 | 0 |  | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 |  | 1000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2011-06-01 | 2010-10-01
2007-AG2 | AFS9 | ISLAND-LOAD |  |  | FDNS |  | 3 | 2 | 2007AG2AFS81T18483213SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | EXP | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 13SP | 280 | 308 |  |  | 99.1914 | 100.3453 | [7 empty] | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 |  |  | WERE | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | Uprate JEC- E.Manhattan 230 kV line to 100 deg C operation by raising structures | 446 | 490 |  |  |  | 24 | 24 | [5 empty] | 17085937.5 | 2008-01-01 | [23 empty] | 2009-06-01 | 2012-06-01 | 2011-10-01
2007-AG2 | AFS9 | ISLAND-LOAD |  |  | FDNS |  | 3 | 2 | 2007AG2AFS81T18483213SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | EXP | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 13SP | 280 | 308 |  |  | 99.1914 | 100.3453 | [7 empty] | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 |  |  | WERE | EAST MANHATTAN - NW MANHATTAN 230/115KV | Tap the Concordia - East Manhattan 230kV line and add a new substation"NW Manhattan"; Add a 230kV/115kV transformer and tap the KSU - Wildcat 115kV line into NW Manhattan | [12 empty] | 17437500 | 2008-01-01 | [23 empty] | 2009-06-01 | 2012-06-01 | 2011-10-01
2007-AG2 | AFS9 | ISLAND-LOAD |  |  | FDNS |  | 3 | 2 | 2007AG2AFS81T18483213SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | EXP | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 13SP | 280 | 308 |  |  | 99.1914 | 100.3453 | [7 empty] | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 |  | 1000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2011-06-01 | 2010-10-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 3 | 2 | 2007AG2AFS81T3673213SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | EXP | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 13SP | 280 | 308 |  |  | 99.095 | 100 | [7 empty] | CATEGORYB | SINGLE | AUBURN ROAD - JEFFREY ENERGY CENTER 230KV CKT 1 | 0 | 532851 | AUBURN 6 230.00 | 532852 | JEC 6 230.00 | 0 |  | 1 |  |  | WERE | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | Uprate JEC- E.Manhattan 230 kV line to 100 deg C operation by raising structures | 446 | 490 |  |  |  | 24 | 24 | [5 empty] | 17085937.5 | 2008-01-01 | [23 empty] | 2009-06-01 | 2012-06-01 | 2011-10-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 3 | 2 | 2007AG2AFS81T3673213SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | EXP | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 13SP | 280 | 308 |  |  | 99.095 | 100 | [7 empty] | CATEGORYB | SINGLE | AUBURN ROAD - JEFFREY ENERGY CENTER 230KV CKT 1 | 0 | 532851 | AUBURN 6 230.00 | 532852 | JEC 6 230.00 | 0 |  | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 |  | 1000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2011-06-01 | 2010-10-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 2 | 2007AG2AFS81T6583218SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | EXP | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 18SP | 280 | 308 |  | 100.8 | 100.2332 | 101.3838 | [7 empty] | CATEGORYB | SINGLE | MCDOWELL CREEK - MORRIS COUNTY 230KV CKT 1 | 0 | 532862 | MCDOWEL6 230.00 | 532863 | MORRIS 6 230.00 | 0 |  | 1 |  |  | WERE | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | Uprate JEC- E.Manhattan 230 kV line to 100 deg C operation by raising structures | 446 | 490 |  |  |  | 24 | 24 | [5 empty] | 17085937.5 | 2008-01-01 | [23 empty] | 2009-06-01 | 2012-06-01 | 2011-10-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 2 | 2007AG2AFS81T6583218SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | EXP | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 18SP | 280 | 308 |  | 100.8 | 100.2332 | 101.3838 | [7 empty] | CATEGORYB | SINGLE | MCDOWELL CREEK - MORRIS COUNTY 230KV CKT 1 | 0 | 532862 | MCDOWEL6 230.00 | 532863 | MORRIS 6 230.00 | 0 |  | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 |  | 1000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2011-06-01 | 2010-10-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 2 | 2007AG2AFS81T33033218SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | EXP | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 18SP | 280 | 308 |  | 100.8 | 100.2049 | 101.3658 | [7 empty] | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 |  |  | WERE | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | Uprate JEC- E.Manhattan 230 kV line to 100 deg C operation by raising structures | 446 | 490 |  |  |  | 24 | 24 | [5 empty] | 17085937.5 | 2008-01-01 | [23 empty] | 2009-06-01 | 2012-06-01 | 2011-10-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 2 | 2007AG2AFS81T33033218SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | EXP | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 18SP | 280 | 308 |  | 100.8 | 100.2049 | 101.3658 | [7 empty] | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 |  |  | WERE | EAST MANHATTAN - NW MANHATTAN 230/115KV | Tap the Concordia - East Manhattan 230kV line and add a new substation"NW Manhattan"; Add a 230kV/115kV transformer and tap the KSU - Wildcat 115kV line into NW Manhattan | [12 empty] | 17437500 | 2008-01-01 | [23 empty] | 2009-06-01 | 2012-06-01 | 2011-10-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 2 | 2007AG2AFS81T33033218SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | EXP | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 18SP | 280 | 308 |  | 100.8 | 100.2049 | 101.3658 | [7 empty] | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 |  | 1000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2011-06-01 | 2010-10-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81T5862418SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | EXP | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 18SP | 280 | 308 |  | 100.2 | 100.5994 | 100.2039 | [7 empty] | CATEGORYB | SINGLE | AUBURN ROAD - JEFFREY ENERGY CENTER 230KV CKT 1 | 0 | 532851 | AUBURN 6 230.00 | 532852 | JEC 6 230.00 | 0 |  | 1 |  |  | WERE | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | Uprate JEC- E.Manhattan 230 kV line to 100 deg C operation by raising structures | 446 | 490 |  |  |  | 24 | 24 | [5 empty] | 17085937.5 | 2008-01-01 | [23 empty] | 2009-06-01 | 2012-06-01 | 2011-10-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81T5862418SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | EXP | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 18SP | 280 | 308 |  | 100.2 | 100.5994 | 100.2039 | [7 empty] | CATEGORYB | SINGLE | AUBURN ROAD - JEFFREY ENERGY CENTER 230KV CKT 1 | 0 | 532851 | AUBURN 6 230.00 | 532852 | JEC 6 230.00 | 0 |  | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 |  | 1000000 | 2007-01-01 | [23 empty] | 2009-06-01 | 2011-06-01 | 2010-10-01
GEN-2001-024 | Mattison | [7 empty] | 506957504010012SP | TO->FROM | ELMSPRGS 5 161.00 - TONTITOWN 161KV CKT 1 | U | AEPW | AEPW | FAYETTEV | FAYTAECC | 0 | 506957 | TONTITN5 161.00 | 504010 | ELMSPRGS 5 161.00 | 0 |  | 1 |  | 451 | 592 |  |  | 362.25 | [9 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | AEPW | ELMSPRGS 5 161.00 - TONTITOWN 161KV CKT 1 | Add one 161KV terminal for Tontitown | [12 empty] | 537700 | [24 empty] | 2008-06-01 | 2008-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T3092210SP | FROM->TO | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | CP | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 | 10SP | 382 | 382 | 101.8 | 100.5 | 101.8793 | 102.2037 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 |  |  | WERE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 Displacement | Replace Disconnect Switches, Wavetrap, Breaker, Jumpers | 382 | 414 | 382 | 414 |  | 12 | 12 | [5 empty] | 1575000 | 2008-01-01 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 1 | 4 | 2007AG2AFS81T3021413SP | FROM->TO | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | CP | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 | 13SP | 382 | 382 | 101.4 | 101.1 | 100.5559 | 102.4448 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 |  |  | WERE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 Displacement | Replace Disconnect Switches, Wavetrap, Breaker, Jumpers | 382 | 414 | 382 | 414 |  | 12 | 12 | [5 empty] | 1575000 | 2008-01-01 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 4 | 2 | 2007AG2AFS81T6694218SP | FROM->TO | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | CP | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 | 18SP | 382 | 382 | 103.2 | 103.9 | 103.6832 | 104.0783 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 |  |  | WERE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 Displacement | Replace Disconnect Switches, Wavetrap, Breaker, Jumpers | 382 | 414 | 382 | 414 |  | 12 | 12 | [5 empty] | 1575000 | 2008-01-01 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 1 | 4 | 2007AG2AFS81T1471409SH | FROM->TO | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533368 | EXIDE J3 115.00 | 533372 | PHILIPS3 115.00 | 0 |  | 1 | 09SH | 181 | 196 | 100.8 | 102 | 102.8401 | 103.2497 | [7 empty] | CATEGORYB | SINGLE | NORTHVIEW - SUMMIT 115KV CKT 1 | 0 | 533371 | NORTHVW3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2009-06-01 | 2009-12-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 4 | 2 | 2007AG2AFS81T2734209SP | FROM->TO | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533368 | EXIDE J3 115.00 | 533372 | PHILIPS3 115.00 | 0 |  | 1 | 09SP | 181 | 196 | 117.4 | 118 | 117.6362 | 118.2709 | [7 empty] | CATEGORYB | SINGLE | NORTHVIEW - SUMMIT 115KV CKT 1 | 0 | 533371 | NORTHVW3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2009-06-01 | 2009-12-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 2 | 2007AG2AFS81T2434209SP | FROM->TO | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533368 | EXIDE J3 115.00 | 533372 | PHILIPS3 115.00 | 0 |  | 1 | 09SP | 181 | 196 |  |  | 99.3938 | 101.1977 | [7 empty] | CATEGORYB | SINGLE | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 0 | 532872 | EMCPHER6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2009-06-01 | 2009-12-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 4 | 3 | 2007AG2AFS81T894309FA | TO->FROM | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533368 | EXIDE J3 115.00 | 0 |  | 1 | 09FA | 181 | 196 | 100.3 | 102.8 | 103.009 | 103.9516 | [7 empty] | CATEGORYB | SINGLE | NORTHVIEW - SUMMIT 115KV CKT 1 | 0 | 533371 | NORTHVW3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2009-06-01 | 2009-12-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 1 | 4 | 2007AG2AFS81T1481409SH | TO->FROM | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533368 | EXIDE J3 115.00 | 0 |  | 1 | 09SH | 181 | 196 | 106.4 | 107.6 | 108.3942 | 108.7849 | [7 empty] | CATEGORYB | SINGLE | NORTHVIEW - SUMMIT 115KV CKT 1 | 0 | 533371 | NORTHVW3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2009-06-01 | 2009-12-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 4 | 2 | 2007AG2AFS81T2744209SP | TO->FROM | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533368 | EXIDE J3 115.00 | 0 |  | 1 | 09SP | 181 | 196 | 123.0 | 123.7 | 123.3378 | 123.9562 | [7 empty] | CATEGORYB | SINGLE | NORTHVIEW - SUMMIT 115KV CKT 1 | 0 | 533371 | NORTHVW3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2009-06-01 | 2009-12-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 4 | 2 | 2007AG2AFS81T2444209SP | TO->FROM | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533368 | EXIDE J3 115.00 | 0 |  | 1 | 09SP | 181 | 196 | 103.0 | 103.8 | 104.8361 | 106.6435 | [7 empty] | CATEGORYB | SINGLE | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 0 | 532872 | EMCPHER6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2009-06-01 | 2009-12-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 4 | 2 | 2007AG2AFS81T8724209SP | TO->FROM | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533368 | EXIDE J3 115.00 | 0 |  | 1 | 09SP | 181 | 196 |  | 100.5 | 100.5397 | 101.3456 | [7 empty] | CATEGORYB | SINGLE | EAST MCPHERSON (EMCPHR1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532872 | EMCPHER6 230.00 | 533417 | EMCPHER3 115.00 | 532894 | EMCPHER1 13.800 | 1 |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2009-06-01 | 2009-12-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 1 | 2007AG2AFS81T244109AP | TO->FROM | FARGOJCT2 69.000 - FT SUPPLY 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520919 | FTSUPLY2 69.000 | 521196 | FARGOJCT2 69.000 | 0 |  | 1 | 09AP | 53 | 65 |  |  | 111.8403 | 129.6074 | [7 empty] | CATEGORYB | SINGLE | FT SUPPLY - IODINE 138KV CKT 1 | 0 | 520920 | FTSUPLY4 138.00 | 520957 | IODINE 4 138.00 | 0 |  | 1 |  |  | WFEC | FARGOJCT2 69.000 - FT SUPPLY 69KV CKT 1 | upgrade line between Ft supply Switchyard and Woodward Switchyard (through Fargo Jct) to 795ACSR | 91 | 95 |  |  | 17.7 | [6 empty] | limited by 800A CTs at FT Supply | 5350000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 1 | 2007AG2AFS81T274109AP | TO->FROM | FARGOJCT2 69.000 - FT SUPPLY 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520919 | FTSUPLY2 69.000 | 521196 | FARGOJCT2 69.000 | 0 |  | 1 | 09AP | 53 | 65 |  |  | 109.4713 | 127.2341 | [7 empty] | CATEGORYB | SINGLE | IODINE - MOORELAND 138KV CKT 1 | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 |  |  | WFEC | FARGOJCT2 69.000 - FT SUPPLY 69KV CKT 1 | upgrade line between Ft supply Switchyard and Woodward Switchyard (through Fargo Jct) to 795ACSR | 91 | 95 |  |  | 17.7 | [6 empty] | limited by 800A CTs at FT Supply | 5350000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 4 | 2007AG2AFS81T414409FA | TO->FROM | FARGOJCT2 69.000 - FT SUPPLY 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520919 | FTSUPLY2 69.000 | 521196 | FARGOJCT2 69.000 | 0 |  | 1 | 09FA | 53 | 65 |  |  | 80.9298 | 116.8677 | [7 empty] | CATEGORYB | SINGLE | FT SUPPLY - IODINE 138KV CKT 1 | 0 | 520920 | FTSUPLY4 138.00 | 520957 | IODINE 4 138.00 | 0 |  | 1 |  |  | WFEC | FARGOJCT2 69.000 - FT SUPPLY 69KV CKT 1 | upgrade line between Ft supply Switchyard and Woodward Switchyard (through Fargo Jct) to 795ACSR | 91 | 95 |  |  | 17.7 | [6 empty] | limited by 800A CTs at FT Supply | 5350000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 4 | 2007AG2AFS81T444409FA | TO->FROM | FARGOJCT2 69.000 - FT SUPPLY 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520919 | FTSUPLY2 69.000 | 521196 | FARGOJCT2 69.000 | 0 |  | 1 | 09FA | 53 | 65 |  |  | 76.2493 | 112.0623 | [7 empty] | CATEGORYB | SINGLE | IODINE - MOORELAND 138KV CKT 1 | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 |  |  | WFEC | FARGOJCT2 69.000 - FT SUPPLY 69KV CKT 1 | upgrade line between Ft supply Switchyard and Woodward Switchyard (through Fargo Jct) to 795ACSR | 91 | 95 |  |  | 17.7 | [6 empty] | limited by 800A CTs at FT Supply | 5350000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 1 | 4 | 2007AG2AFS81T1231409G | TO->FROM | FARGOJCT2 69.000 - FT SUPPLY 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520919 | FTSUPLY2 69.000 | 521196 | FARGOJCT2 69.000 | 0 |  | 1 | 09G | 53 | 65 |  |  | 92.4724 | 110.4472 | [7 empty] | CATEGORYB | SINGLE | FT SUPPLY - IODINE 138KV CKT 1 | 0 | 520920 | FTSUPLY4 138.00 | 520957 | IODINE 4 138.00 | 0 |  | 1 |  |  | WFEC | FARGOJCT2 69.000 - FT SUPPLY 69KV CKT 1 | upgrade line between Ft supply Switchyard and Woodward Switchyard (through Fargo Jct) to 795ACSR | 91 | 95 |  |  | 17.7 | [6 empty] | limited by 800A CTs at FT Supply | 5350000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 1 | 4 | 2007AG2AFS81T1291409G | TO->FROM | FARGOJCT2 69.000 - FT SUPPLY 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520919 | FTSUPLY2 69.000 | 521196 | FARGOJCT2 69.000 | 0 |  | 1 | 09G | 53 | 65 |  |  | 86.6834 | 104.6669 | [7 empty] | CATEGORYB | SINGLE | IODINE - MOORELAND 138KV CKT 1 | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 |  |  | WFEC | FARGOJCT2 69.000 - FT SUPPLY 69KV CKT 1 | upgrade line between Ft supply Switchyard and Woodward Switchyard (through Fargo Jct) to 795ACSR | 91 | 95 |  |  | 17.7 | [6 empty] | limited by 800A CTs at FT Supply | 5350000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 1 | 1 | 2007AG2AFS81T751109SH | TO->FROM | FARGOJCT2 69.000 - FT SUPPLY 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520919 | FTSUPLY2 69.000 | 521196 | FARGOJCT2 69.000 | 0 |  | 1 | 09SH | 53 | 65 |  |  | 96.8536 | 114.6609 | [7 empty] | CATEGORYB | SINGLE | FT SUPPLY - IODINE 138KV CKT 1 | 0 | 520920 | FTSUPLY4 138.00 | 520957 | IODINE 4 138.00 | 0 |  | 1 |  |  | WFEC | FARGOJCT2 69.000 - FT SUPPLY 69KV CKT 1 | upgrade line between Ft supply Switchyard and Woodward Switchyard (through Fargo Jct) to 795ACSR | 91 | 95 |  |  | 17.7 | [6 empty] | limited by 800A CTs at FT Supply | 5350000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 1 | 1 | 2007AG2AFS81T801109SH | TO->FROM | FARGOJCT2 69.000 - FT SUPPLY 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520919 | FTSUPLY2 69.000 | 521196 | FARGOJCT2 69.000 | 0 |  | 1 | 09SH | 53 | 65 |  |  | 91.2485 | 109.0586 | [7 empty] | CATEGORYB | SINGLE | IODINE - MOORELAND 138KV CKT 1 | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 |  |  | WFEC | FARGOJCT2 69.000 - FT SUPPLY 69KV CKT 1 | upgrade line between Ft supply Switchyard and Woodward Switchyard (through Fargo Jct) to 795ACSR | 91 | 95 |  |  | 17.7 | [6 empty] | limited by 800A CTs at FT Supply | 5350000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 1 | 1 | 2007AG2AFS81T1051109SP | TO->FROM | FARGOJCT2 69.000 - FT SUPPLY 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520919 | FTSUPLY2 69.000 | 521196 | FARGOJCT2 69.000 | 0 |  | 1 | 09SP | 53 | 65 |  |  | 90.4805 | 108.2177 | [7 empty] | CATEGORYB | SINGLE | FT SUPPLY - IODINE 138KV CKT 1 | 0 | 520920 | FTSUPLY4 138.00 | 520957 | IODINE 4 138.00 | 0 |  | 1 |  |  | WFEC | FARGOJCT2 69.000 - FT SUPPLY 69KV CKT 1 | upgrade line between Ft supply Switchyard and Woodward Switchyard (through Fargo Jct) to 795ACSR | 91 | 95 |  |  | 17.7 | [6 empty] | limited by 800A CTs at FT Supply | 5350000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 1 | 1 | 2007AG2AFS81T1081109SP | TO->FROM | FARGOJCT2 69.000 - FT SUPPLY 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520919 | FTSUPLY2 69.000 | 521196 | FARGOJCT2 69.000 | 0 |  | 1 | 09SP | 53 | 65 |  |  | 83.6304 | 101.3616 | [7 empty] | CATEGORYB | SINGLE | IODINE - MOORELAND 138KV CKT 1 | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 |  |  | WFEC | FARGOJCT2 69.000 - FT SUPPLY 69KV CKT 1 | upgrade line between Ft supply Switchyard and Woodward Switchyard (through Fargo Jct) to 795ACSR | 91 | 95 |  |  | 17.7 | [6 empty] | limited by 800A CTs at FT Supply | 5350000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 1 | 1 | 2007AG2AFS81T741109WP | TO->FROM | FARGOJCT2 69.000 - FT SUPPLY 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520919 | FTSUPLY2 69.000 | 521196 | FARGOJCT2 69.000 | 0 |  | 1 | 09WP | 69 | 78 |  |  | 69.9247 | 100 | [7 empty] | CATEGORYB | SINGLE | FT SUPPLY - IODINE 138KV CKT 1 | 0 | 520920 | FTSUPLY4 138.00 | 520957 | IODINE 4 138.00 | 0 |  | 1 |  |  | WFEC | FARGOJCT2 69.000 - FT SUPPLY 69KV CKT 1 | upgrade line between Ft supply Switchyard and Woodward Switchyard (through Fargo Jct) to 795ACSR | 91 | 95 |  |  | 17.7 | [6 empty] | limited by 800A CTs at FT Supply | 5350000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 4 | 2007AG2AFS81T1434410SP | TO->FROM | FARGOJCT2 69.000 - FT SUPPLY 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520919 | FTSUPLY2 69.000 | 521196 | FARGOJCT2 69.000 | 0 |  | 1 | 10SP | 53 | 65 |  |  | 76.4221 | 112.7046 | [7 empty] | CATEGORYB | SINGLE | FT SUPPLY - IODINE 138KV CKT 1 | 0 | 520920 | FTSUPLY4 138.00 | 520957 | IODINE 4 138.00 | 0 |  | 1 |  |  | WFEC | FARGOJCT2 69.000 - FT SUPPLY 69KV CKT 1 | upgrade line between Ft supply Switchyard and Woodward Switchyard (through Fargo Jct) to 795ACSR | 91 | 95 |  |  | 17.7 | [6 empty] | limited by 800A CTs at FT Supply | 5350000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 4 | 2007AG2AFS81T1484410SP | TO->FROM | FARGOJCT2 69.000 - FT SUPPLY 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520919 | FTSUPLY2 69.000 | 521196 | FARGOJCT2 69.000 | 0 |  | 1 | 10SP | 53 | 65 |  |  | 69.244 | 105.5568 | [7 empty] | CATEGORYB | SINGLE | IODINE - MOORELAND 138KV CKT 1 | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 |  |  | WFEC | FARGOJCT2 69.000 - FT SUPPLY 69KV CKT 1 | upgrade line between Ft supply Switchyard and Woodward Switchyard (through Fargo Jct) to 795ACSR | 91 | 95 |  |  | 17.7 | [6 empty] | limited by 800A CTs at FT Supply | 5350000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 4 | 2007AG2AFS81T2234413SP | TO->FROM | FARGOJCT2 69.000 - FT SUPPLY 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520919 | FTSUPLY2 69.000 | 521196 | FARGOJCT2 69.000 | 0 |  | 1 | 13SP | 53 | 65 |  |  | 76.063 | 113.5953 | [7 empty] | CATEGORYB | SINGLE | FT SUPPLY - IODINE 138KV CKT 1 | 0 | 520920 | FTSUPLY4 138.00 | 520957 | IODINE 4 138.00 | 0 |  | 1 |  |  | WFEC | FARGOJCT2 69.000 - FT SUPPLY 69KV CKT 1 | upgrade line between Ft supply Switchyard and Woodward Switchyard (through Fargo Jct) to 795ACSR | 91 | 95 |  |  | 17.7 | [6 empty] | limited by 800A CTs at FT Supply | 5350000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 4 | 2007AG2AFS81T2264413SP | TO->FROM | FARGOJCT2 69.000 - FT SUPPLY 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520919 | FTSUPLY2 69.000 | 521196 | FARGOJCT2 69.000 | 0 |  | 1 | 13SP | 53 | 65 |  |  | 68.5176 | 105.9021 | [7 empty] | CATEGORYB | SINGLE | IODINE - MOORELAND 138KV CKT 1 | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 |  |  | WFEC | FARGOJCT2 69.000 - FT SUPPLY 69KV CKT 1 | upgrade line between Ft supply Switchyard and Woodward Switchyard (through Fargo Jct) to 795ACSR | 91 | 95 |  |  | 17.7 | [6 empty] | limited by 800A CTs at FT Supply | 5350000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 1 | 2007AG2AFS81T4274118SP | TO->FROM | FARGOJCT2 69.000 - FT SUPPLY 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520919 | FTSUPLY2 69.000 | 521196 | FARGOJCT2 69.000 | 0 |  | 1 | 18SP | 53 | 65 |  |  | 72.7024 | 110.3506 | [7 empty] | CATEGORYB | SINGLE | FT SUPPLY - IODINE 138KV CKT 1 | 0 | 520920 | FTSUPLY4 138.00 | 520957 | IODINE 4 138.00 | 0 |  | 1 |  |  | WFEC | FARGOJCT2 69.000 - FT SUPPLY 69KV CKT 1 | upgrade line between Ft supply Switchyard and Woodward Switchyard (through Fargo Jct) to 795ACSR | 91 | 95 |  |  | 17.7 | [6 empty] | limited by 800A CTs at FT Supply | 5350000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 1 | 2007AG2AFS81T4304118SP | TO->FROM | FARGOJCT2 69.000 - FT SUPPLY 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520919 | FTSUPLY2 69.000 | 521196 | FARGOJCT2 69.000 | 0 |  | 1 | 18SP | 53 | 65 |  |  | 64.4034 | 101.7863 | [7 empty] | CATEGORYB | SINGLE | IODINE - MOORELAND 138KV CKT 1 | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 |  |  | WFEC | FARGOJCT2 69.000 - FT SUPPLY 69KV CKT 1 | upgrade line between Ft supply Switchyard and Woodward Switchyard (through Fargo Jct) to 795ACSR | 91 | 95 |  |  | 17.7 | [6 empty] | limited by 800A CTs at FT Supply | 5350000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 1 | 2007AG2AFS81T254109AP | FROM->TO | FARGOJCT2 69.000 - WOODWARD 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521196 | FARGOJCT2 69.000 | 521096 | WOODWRD2 69.000 | 0 |  | 1 | 09AP | 53 | 65 |  |  | 108.2822 | 126.0451 | [7 empty] | CATEGORYB | SINGLE | FT SUPPLY - IODINE 138KV CKT 1 | 0 | 520920 | FTSUPLY4 138.00 | 520957 | IODINE 4 138.00 | 0 |  | 1 |  |  | WFEC | FARGOJCT2 69.000 - WOODWARD 69KV CKT 1 | upgrade the terminal equipment at Woodward to 1200A | 91 | 114 | [10 empty] | 100000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 1 | 2007AG2AFS81T284109AP | FROM->TO | FARGOJCT2 69.000 - WOODWARD 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521196 | FARGOJCT2 69.000 | 521096 | WOODWRD2 69.000 | 0 |  | 1 | 09AP | 53 | 65 |  |  | 105.9128 | 123.6719 | [7 empty] | CATEGORYB | SINGLE | IODINE - MOORELAND 138KV CKT 1 | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 |  |  | WFEC | FARGOJCT2 69.000 - WOODWARD 69KV CKT 1 | upgrade the terminal equipment at Woodward to 1200A | 91 | 114 | [10 empty] | 100000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 4 | 2007AG2AFS81T424409FA | FROM->TO | FARGOJCT2 69.000 - WOODWARD 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521196 | FARGOJCT2 69.000 | 521096 | WOODWRD2 69.000 | 0 |  | 1 | 09FA | 53 | 65 |  |  | 74.49 | 110.2987 | [7 empty] | CATEGORYB | SINGLE | FT SUPPLY - IODINE 138KV CKT 1 | 0 | 520920 | FTSUPLY4 138.00 | 520957 | IODINE 4 138.00 | 0 |  | 1 |  |  | WFEC | FARGOJCT2 69.000 - WOODWARD 69KV CKT 1 | upgrade the terminal equipment at Woodward to 1200A | 91 | 114 | [10 empty] | 100000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 4 | 2007AG2AFS81T454409FA | FROM->TO | FARGOJCT2 69.000 - WOODWARD 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521196 | FARGOJCT2 69.000 | 521096 | WOODWRD2 69.000 | 0 |  | 1 | 09FA | 53 | 65 |  |  | 69.8162 | 105.503 | [7 empty] | CATEGORYB | SINGLE | IODINE - MOORELAND 138KV CKT 1 | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 |  |  | WFEC | FARGOJCT2 69.000 - WOODWARD 69KV CKT 1 | upgrade the terminal equipment at Woodward to 1200A | 91 | 114 | [10 empty] | 100000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 1 | 4 | 2007AG2AFS81T1251409G | FROM->TO | FARGOJCT2 69.000 - WOODWARD 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521196 | FARGOJCT2 69.000 | 521096 | WOODWRD2 69.000 | 0 |  | 1 | 09G | 53 | 65 |  |  | 84.6968 | 102.6413 | [7 empty] | CATEGORYB | SINGLE | FT SUPPLY - IODINE 138KV CKT 1 | 0 | 520920 | FTSUPLY4 138.00 | 520957 | IODINE 4 138.00 | 0 |  | 1 |  |  | WFEC | FARGOJCT2 69.000 - WOODWARD 69KV CKT 1 | upgrade the terminal equipment at Woodward to 1200A | 91 | 114 | [10 empty] | 100000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 1 | 1 | 2007AG2AFS81T761109SH | FROM->TO | FARGOJCT2 69.000 - WOODWARD 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521196 | FARGOJCT2 69.000 | 521096 | WOODWRD2 69.000 | 0 |  | 1 | 09SH | 53 | 65 |  |  | 89.3884 | 107.1609 | [7 empty] | CATEGORYB | SINGLE | FT SUPPLY - IODINE 138KV CKT 1 | 0 | 520920 | FTSUPLY4 138.00 | 520957 | IODINE 4 138.00 | 0 |  | 1 |  |  | WFEC | FARGOJCT2 69.000 - WOODWARD 69KV CKT 1 | upgrade the terminal equipment at Woodward to 1200A | 91 | 114 | [10 empty] | 100000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 1 | 1 | 2007AG2AFS81T811109SH | FROM->TO | FARGOJCT2 69.000 - WOODWARD 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521196 | FARGOJCT2 69.000 | 521096 | WOODWRD2 69.000 | 0 |  | 1 | 09SH | 53 | 65 |  |  | 83.7933 | 101.5684 | [7 empty] | CATEGORYB | SINGLE | IODINE - MOORELAND 138KV CKT 1 | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 |  |  | WFEC | FARGOJCT2 69.000 - WOODWARD 69KV CKT 1 | upgrade the terminal equipment at Woodward to 1200A | 91 | 114 | [10 empty] | 100000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 1 | 1 | 2007AG2AFS81T1061109SP | FROM->TO | FARGOJCT2 69.000 - WOODWARD 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521196 | FARGOJCT2 69.000 | 521096 | WOODWRD2 69.000 | 0 |  | 1 | 09SP | 53 | 65 |  |  | 83.9177 | 101.5966 | [7 empty] | CATEGORYB | SINGLE | FT SUPPLY - IODINE 138KV CKT 1 | 0 | 520920 | FTSUPLY4 138.00 | 520957 | IODINE 4 138.00 | 0 |  | 1 |  |  | WFEC | FARGOJCT2 69.000 - WOODWARD 69KV CKT 1 | upgrade the terminal equipment at Woodward to 1200A | 91 | 114 | [10 empty] | 100000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 4 | 2007AG2AFS81T1454410SP | FROM->TO | FARGOJCT2 69.000 - WOODWARD 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521196 | FARGOJCT2 69.000 | 521096 | WOODWRD2 69.000 | 0 |  | 1 | 10SP | 53 | 65 |  |  | 69.6076 | 105.7424 | [7 empty] | CATEGORYB | SINGLE | FT SUPPLY - IODINE 138KV CKT 1 | 0 | 520920 | FTSUPLY4 138.00 | 520957 | IODINE 4 138.00 | 0 |  | 1 |  |  | WFEC | FARGOJCT2 69.000 - WOODWARD 69KV CKT 1 | upgrade the terminal equipment at Woodward to 1200A | 91 | 114 | [10 empty] | 100000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 4 | 2007AG2AFS81T2244413SP | FROM->TO | FARGOJCT2 69.000 - WOODWARD 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521196 | FARGOJCT2 69.000 | 521096 | WOODWRD2 69.000 | 0 |  | 1 | 13SP | 53 | 65 |  |  | 68.5157 | 106.0064 | [7 empty] | CATEGORYB | SINGLE | FT SUPPLY - IODINE 138KV CKT 1 | 0 | 520920 | FTSUPLY4 138.00 | 520957 | IODINE 4 138.00 | 0 |  | 1 |  |  | WFEC | FARGOJCT2 69.000 - WOODWARD 69KV CKT 1 | upgrade the terminal equipment at Woodward to 1200A | 91 | 114 | [10 empty] | 100000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 1 | 2007AG2AFS81T4284118SP | FROM->TO | FARGOJCT2 69.000 - WOODWARD 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521196 | FARGOJCT2 69.000 | 521096 | WOODWRD2 69.000 | 0 |  | 1 | 18SP | 53 | 65 |  |  | 64.5091 | 102.1173 | [7 empty] | CATEGORYB | SINGLE | FT SUPPLY - IODINE 138KV CKT 1 | 0 | 520920 | FTSUPLY4 138.00 | 520957 | IODINE 4 138.00 | 0 |  | 1 |  |  | WFEC | FARGOJCT2 69.000 - WOODWARD 69KV CKT 1 | upgrade the terminal equipment at Woodward to 1200A | 91 | 114 | [10 empty] | 100000 | 2008-12-01 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 1 | 1 | 2007AG2AFS81T31118SP | TO->FROM | FIXICO TAP - MAUD 138KV CKT 1 | EXP | OKGE | AEPW | SHAWNEE | EASTERN | 0 | 515055 | MAUD 4 138.00 | 510877 | FIXCT4 138.00 | 0 |  | 1 | 18SP | 88 | 107 |  |  | 95.6122 | 100.6941 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | OKGE | MAUD - FIXICO - WELEETKA 138KV CKT 1 | Build another 1.43 mile line from Fixico to the location of Fixico Tap and install dead end structures in the area of Fixico Tap. Install another breaker in Fixico and remove Fixico Tap. This will loop the 138kV line through Fixico and eliminate the tap. | [12 empty] | 2530000 | [24 empty] | 2018-06-01 | 2018-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2007AG2AFS81T5125518SP | TO->FROM | FORT COBB - SOUTHWESTERN STATION 138KV CKT 1 | REL | AEPW | AEPW | WESTERN | WESTERN | 0 | 511477 | S.W.S.-4 138.00 | 511454 | FTCOBNG4 138.00 | 0 |  | 1 | 18SP | 131 | 151 | 118.5 | 100.3 | 97.888 | 104.7606 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - HOLCOMB 345KV CKT 1 | 0 | 523853 | FINNEY7 345.00 | 531449 | HOLCOMB7 345.00 | 0 |  | 1 |  |  | AEPW | FORT COBB - SOUTHWESTERN STATION 138KV CKT 1 | Reconductor 3.34 miles with 795 ACSR South West Station - Fort Cobb | [12 empty] | 2300000 | [24 empty] | 2018-06-01 | 2018-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 2 | 2007AG2AFS81T40464218SP | TO->FROM | FORT COBB - SOUTHWESTERN STATION 138KV CKT 1 | REL | AEPW | AEPW | WESTERN | WESTERN | 0 | 511477 | S.W.S.-4 138.00 | 511454 | FTCOBNG4 138.00 | 0 |  | 1 | 18SP | 131 | 151 | 102.0 |  | 95.1338 | 101.681 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05B | 0 | 0 |  | 0 |  | 0 |  |  |  |  | AEPW | FORT COBB - SOUTHWESTERN STATION 138KV CKT 1 | Reconductor 3.34 miles with 795 ACSR South West Station - Fort Cobb | [12 empty] | 2300000 | [24 empty] | 2018-06-01 | 2018-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 2 | 2007AG2AFS81T4144218SP | TO->FROM | FORT COBB - SOUTHWESTERN STATION 138KV CKT 1 | REL | AEPW | AEPW | WESTERN | WESTERN | 0 | 511477 | S.W.S.-4 138.00 | 511454 | FTCOBNG4 138.00 | 0 |  | 1 | 18SP | 131 | 151 |  |  | 94.9661 | 100.8818 | [7 empty] | CATEGORYB | SINGLE | CACHE - SNYDER 138KV CKT 1 | 0 | 511435 | SNYDER-4 138.00 | 511500 | CACHE4 138.00 | 0 |  | 1 |  |  | AEPW | FORT COBB - SOUTHWESTERN STATION 138KV CKT 1 | Reconductor 3.34 miles with 795 ACSR South West Station - Fort Cobb | [12 empty] | 2300000 | [24 empty] | 2018-06-01 | 2018-06-01
2006-AG1 | 2006-AG1 | [7 empty] | 55919559201559575599913316SP |  | FT SUPPLY 138/69KV TRANSFORMER CKT 1 | U | WFEC | WFEC |  |  | 1 | 520920 | FTSUPLY4 138 | 520919 | FTSUPLY269.0 | 521182 |  | 2 | 16SP |  | 70 | [12 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | FT SUPPLY 138/69KV TRANSFORMER CKT 1 | Install 2nd 70 MVA auto at Ft Supply | 70 | 70 |  |  |  | 12 | 18 |  |  |  |  | Use RS from Ft Supply Auto | 2000000 | [24 empty] | 2006-12-01 | 2008-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 4 | 2007AG2AFS81V3534418SP |  | G06-24 69.000 69KV | EXP | WFEC |  |  |  |  | 560156 | G06-24 69.000 | [5 empty] | 18SP | [8 empty] | 0.93615 | 0.87812 | 0.96132 | 0.9 | 1.05 | CATEGORYB | SINGLE | BUFFALO - FT SUPPLY 69KV CKT 1 | 0 | 520919 | FTSUPLY2 69.000 | 520835 | BUFFALO2 69.000 | 0 |  | 1 |  |  | WFEC | Multi-Dover-Twin Lake_Cresent 138 kV | Convert 69 kV to 138 kV and install terminal equipment at Dover SW; Instal 7 miles of new 138 kV fro WFEC Twin Lakes to OGE Cresent substation | [37 empty] | 2014-06-01 | 2014-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2007AG2AFS81T125509G | FROM->TO | GENTLMREDWIL | S |  |  |  |  | GENTLMREDWIL | 0 |  | 0 |  | 0 |  |  | 09G | 380 | 380 |  |  | 101.04 | 100.9887 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | NPPD | SPEARVILLE - KNOLL - AXTELL 345KV CKT 1 | Build a new 345kV line from Spearville - Knoll - Axtell | [5 empty] | 48 | 48 | [5 empty] | 240000000 | 2008-01-01 | [23 empty] | 2009-04-01 | 2013-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2007AG2AFS81T115509SH | FROM->TO | GENTLMREDWIL | S |  |  |  |  | GENTLMREDWIL | 0 |  | 0 |  | 0 |  |  | 09SH | 380 | 380 |  |  | 100.2719 | 100.2132 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | NPPD | SPEARVILLE - KNOLL - AXTELL 345KV CKT 1 | Build a new 345kV line from Spearville - Knoll - Axtell | [5 empty] | 48 | 48 | [5 empty] | 240000000 | 2008-01-01 | [23 empty] | 2009-04-01 | 2013-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 3 | 2 | 2007AG2AFS81T193209SP | FROM->TO | GENTLMREDWIL | S |  |  |  |  | GENTLMREDWIL | 0 |  | 0 |  | 0 |  |  | 09SP | 380 | 380 | 100.2 |  | 103.5352 | 103.7917 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | NPPD | SPEARVILLE - KNOLL - AXTELL 345KV CKT 1 | Build a new 345kV line from Spearville - Knoll - Axtell | [5 empty] | 48 | 48 | [5 empty] | 240000000 | 2008-01-01 | [23 empty] | 2009-04-01 | 2013-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T182210SP | FROM->TO | GENTLMREDWIL | S |  |  |  |  | GENTLMREDWIL | 0 |  | 0 |  | 0 |  |  | 10SP | 380 | 380 | 105.7 | 104.9 | 103.1051 | 104.9041 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | NPPD | SPEARVILLE - KNOLL - AXTELL 345KV CKT 1 | Build a new 345kV line from Spearville - Knoll - Axtell | [5 empty] | 48 | 48 | [5 empty] | 240000000 | 2008-01-01 | [23 empty] | 2009-04-01 | 2013-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T272213SP | FROM->TO | GENTLMREDWIL | S |  |  |  |  | GENTLMREDWIL | 0 |  | 0 |  | 0 |  |  | 13SP | 380 | 380 | 109.9 | 108.5 | 106.8378 | 108.4486 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | NPPD | SPEARVILLE - KNOLL - AXTELL 345KV CKT 1 | Build a new 345kV line from Spearville - Knoll - Axtell | [5 empty] | 48 | 48 | [5 empty] | 240000000 | 2008-01-01 | [23 empty] | 2009-04-01 | 2013-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2007AG2AFS81T515518SP | FROM->TO | GENTLMREDWIL | S |  |  |  |  | GENTLMREDWIL | 0 |  | 0 |  | 0 |  |  | 18SP | 380 | 380 | 120.4 | 119.9 | 117.3142 | 110.7474 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | NPPD | SPEARVILLE - KNOLL - AXTELL 345KV CKT 1 | Build a new 345kV line from Spearville - Knoll - Axtell | [5 empty] | 48 | 48 | [5 empty] | 240000000 | 2008-01-01 | [23 empty] | 2009-04-01 | 2013-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 1 | 2007AG2AFS81T5632118SP | FROM->TO | GILL ENERGY CENTER EAST - MACARTHUR 69KV CKT 1 | REL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533795 | GILL E 2 69.000 | 533813 | MACARTH2 69.000 | 0 |  | 1 | 18SP | 80 | 80 |  | 101 | 101.3434 | 100.9616 | [7 empty] | CATEGORYB | SINGLE | GILL ENERGY CENTER EAST - GILLJCT2 69.000 69KV CKT 1 | 0 | 533795 | GILL E 2 69.000 | 533798 | GILLJCT2 69.000 | 0 |  | 1 |  |  | WERE | GILL ENERGY CENTER EAST - MACARTHUR 69KV CKT 1 | Rebuild 5.56-mile line, 954 ACSR | 107 | 116 |  |  | 3.8 | 12 | 5 |  | 0.0127 | 0.0798 | 0.01697 |  | 2200000 | 2006-07-25 | [23 empty] | 2015-06-01 | 2015-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T1933310SP | FROM->TO | GILL ENERGY CENTER WEST - WACO 138KV CKT 1 | REL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533045 | GILL W 4 138.00 | 533072 | WACO 4 138.00 | 0 |  | 1 | 10SP | 232 | 232 | 100.3 | 100.5 | 98.6598 | 100.8513 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 |  |  | WERE | GILL ENERGY CENTER WEST - WACO 138KV CKT 1 | Tear down and rebuild Gill - Waco with bundled 1192.5 ACSR conductor |  |  |  |  | 1.87 | 24 | 24 | [5 empty] | 1000000 | 2007-01-01 | [23 empty] | 2010-06-01 | 2012-06-01 | 2011-10-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 1 | 4 | 2007AG2AFS81T3031413SP | FROM->TO | GILL ENERGY CENTER WEST - WACO 138KV CKT 1 | REL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533045 | GILL W 4 138.00 | 533072 | WACO 4 138.00 | 0 |  | 1 | 13SP | 232 | 232 | 123.9 | 124.3 | 121.7938 | 124.3572 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 |  |  | WERE | GILL ENERGY CENTER WEST - WACO 138KV CKT 1 | Tear down and rebuild Gill - Waco with bundled 1192.5 ACSR conductor |  |  |  |  | 1.87 | 24 | 24 | [5 empty] | 1000000 | 2007-01-01 | [23 empty] | 2010-06-01 | 2012-06-01 | 2011-10-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 2 | 2007AG2AFS81T6673218SP | FROM->TO | GILL ENERGY CENTER WEST - WACO 138KV CKT 1 | REL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533045 | GILL W 4 138.00 | 533072 | WACO 4 138.00 | 0 |  | 1 | 18SP | 232 | 232 | 127.3 | 127.9 | 125.3035 | 127.8811 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 |  |  | WERE | GILL ENERGY CENTER WEST - WACO 138KV CKT 1 | Tear down and rebuild Gill - Waco with bundled 1192.5 ACSR conductor |  |  |  |  | 1.87 | 24 | 24 | [5 empty] | 1000000 | 2007-01-01 | [23 empty] | 2010-06-01 | 2012-06-01 | 2011-10-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 4 | 4 | 2007AG2AFS81V10714418SP |  | HENESSEY 69KV | EXP | WFEC |  | AEP-IM |  |  | 520940 | HENESEY2 69.000 | [5 empty] | 18SP | [6 empty] | 0.78036 | 0.79038 | 0.7985 | 0.78804 | 0.98681 | 0.9 | 1.05 | CATEGORYB | SINGLE | DOVER SW (DOVER) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 520882 | DOVERSW4 138.00 | 520881 | DOVERSW2 69.000 | 521166 | DVRTERT 13.800 | 1 |  |  | WFEC | Multi-Dover-Twin Lake_Cresent 138 kV | Convert 69 kV to 138 kV and install terminal equipment at Dover SW; Instal 7 miles of new 138 kV fro WFEC Twin Lakes to OGE Cresent substation | [37 empty] | 2014-06-01 | 2014-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T12272213SP | TO->FROM | HERGETT - JONESBORO 161KV CKT 1 | S | EES | SWPA | EES_ARK | EMINTH | 0 | 338170 | 5JONES 161.00 | 505420 | HERGETT5 161.00 | 0 |  | 1 | 13SP | 148 | 148 | 162.7 | 164.4 | 164.3705 | 167.2198 | [7 empty] | CATEGORYB | SINGLE | HARISBURG TAP - MARKED TREE 161KV CKT 1 | 0 | 338165 | 5MTREE 161.00 | 338167 | 5HRSBRG* 161.00 | 0 |  | 1 |  | This is based on 1200/5MR CTs connected at 600/5 in the bushings of a 1600 amp breaker. According to Criteria 12, the CT should be rated for 980 amps. The next limits are 1200 amp for a wave trap and disconnect switches, 1600 amps for the breaker, and 1890 amps for the bus. | SWPA | HERGETT - JONESBORO 161KV CKT 1 SWPA | Increase the CT ratio to 1200/5. This would involve changing taps on the CT, adjusting the scaling on a panel meter, and changing relay settings. | [11 empty] | 505420-338170 | [25 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T12292213SP | TO->FROM | HERGETT - JONESBORO 161KV CKT 1 | S | EES | SWPA | EES_ARK | EMINTH | 0 | 338170 | 5JONES 161.00 | 505420 | HERGETT5 161.00 | 0 |  | 1 | 13SP | 148 | 148 | 156.9 | 158.5 | 158.4799 | 161.2795 | [7 empty] | CATEGORYB | SINGLE | HARISBURG TAP - TRUMANN 161KV CKT 1 | 0 | 338167 | 5HRSBRG* 161.00 | 338169 | 5TRUMAN 161.00 | 0 |  | 1 |  | This is based on 1200/5MR CTs connected at 600/5 in the bushings of a 1600 amp breaker. According to Criteria 12, the CT should be rated for 980 amps. The next limits are 1200 amp for a wave trap and disconnect switches, 1600 amps for the breaker, and 1890 amps for the bus. | SWPA | HERGETT - JONESBORO 161KV CKT 1 SWPA | Increase the CT ratio to 1200/5. This would involve changing taps on the CT, adjusting the scaling on a panel meter, and changing relay settings. | [11 empty] | 505420-338170 | [25 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T12312213SP | TO->FROM | HERGETT - JONESBORO 161KV CKT 1 | S | EES | SWPA | EES_ARK | EMINTH | 0 | 338170 | 5JONES 161.00 | 505420 | HERGETT5 161.00 | 0 |  | 1 | 13SP | 148 | 148 | 149.9 | 151.6 | 151.6272 | 154.3054 | [7 empty] | CATEGORYB | SINGLE | TRUMANN - TRUMANN WEST AECC 161KV CKT 1 | 0 | 338169 | 5TRUMAN 161.00 | 338707 | 5TRUM-W# 161.00 | 0 |  | 1 |  | This is based on 1200/5MR CTs connected at 600/5 in the bushings of a 1600 amp breaker. According to Criteria 12, the CT should be rated for 980 amps. The next limits are 1200 amp for a wave trap and disconnect switches, 1600 amps for the breaker, and 1890 amps for the bus. | SWPA | HERGETT - JONESBORO 161KV CKT 1 SWPA | Increase the CT ratio to 1200/5. This would involve changing taps on the CT, adjusting the scaling on a panel meter, and changing relay settings. | [11 empty] | 505420-338170 | [25 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T4852213WP | TO->FROM | HERGETT - JONESBORO 161KV CKT 1 | S | EES | SWPA | EES_ARK | EMINTH | 0 | 338170 | 5JONES 161.00 | 505420 | HERGETT5 161.00 | 0 |  | 1 | 13WP | 148 | 148 | 119.1 | 121 | 121.0038 | 123.2726 | [7 empty] | CATEGORYB | SINGLE | HARISBURG TAP - MARKED TREE 161KV CKT 1 | 0 | 338165 | 5MTREE 161.00 | 338167 | 5HRSBRG* 161.00 | 0 |  | 1 |  | This is based on 1200/5MR CTs connected at 600/5 in the bushings of a 1600 amp breaker. According to Criteria 12, the CT should be rated for 980 amps. The next limits are 1200 amp for a wave trap and disconnect switches, 1600 amps for the breaker, and 1890 amps for the bus. | SWPA | HERGETT - JONESBORO 161KV CKT 1 SWPA | Increase the CT ratio to 1200/5. This would involve changing taps on the CT, adjusting the scaling on a panel meter, and changing relay settings. | [11 empty] | 505420-338170 | [25 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T4862213WP | TO->FROM | HERGETT - JONESBORO 161KV CKT 1 | S | EES | SWPA | EES_ARK | EMINTH | 0 | 338170 | 5JONES 161.00 | 505420 | HERGETT5 161.00 | 0 |  | 1 | 13WP | 148 | 148 | 114.8 | 116.7 | 116.723 | 118.9761 | [7 empty] | CATEGORYB | SINGLE | HARISBURG TAP - TRUMANN 161KV CKT 1 | 0 | 338167 | 5HRSBRG* 161.00 | 338169 | 5TRUMAN 161.00 | 0 |  | 1 |  | This is based on 1200/5MR CTs connected at 600/5 in the bushings of a 1600 amp breaker. According to Criteria 12, the CT should be rated for 980 amps. The next limits are 1200 amp for a wave trap and disconnect switches, 1600 amps for the breaker, and 1890 amps for the bus. | SWPA | HERGETT - JONESBORO 161KV CKT 1 SWPA | Increase the CT ratio to 1200/5. This would involve changing taps on the CT, adjusting the scaling on a panel meter, and changing relay settings. | [11 empty] | 505420-338170 | [25 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T4872213WP | TO->FROM | HERGETT - JONESBORO 161KV CKT 1 | S | EES | SWPA | EES_ARK | EMINTH | 0 | 338170 | 5JONES 161.00 | 505420 | HERGETT5 161.00 | 0 |  | 1 | 13WP | 148 | 148 | 109.6 | 111.5 | 111.4614 | 113.6771 | [7 empty] | CATEGORYB | SINGLE | TRUMANN - TRUMANN WEST AECC 161KV CKT 1 | 0 | 338169 | 5TRUMAN 161.00 | 338707 | 5TRUM-W# 161.00 | 0 |  | 1 |  | This is based on 1200/5MR CTs connected at 600/5 in the bushings of a 1600 amp breaker. According to Criteria 12, the CT should be rated for 980 amps. The next limits are 1200 amp for a wave trap and disconnect switches, 1600 amps for the breaker, and 1890 amps for the bus. | SWPA | HERGETT - JONESBORO 161KV CKT 1 SWPA | Increase the CT ratio to 1200/5. This would involve changing taps on the CT, adjusting the scaling on a panel meter, and changing relay settings. | [11 empty] | 505420-338170 | [25 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 2 | 2007AG2AFS81T23093218SP | TO->FROM | HERGETT - JONESBORO 161KV CKT 1 | S | EES | SWPA | EES_ARK | EMINTH | 0 | 338170 | 5JONES 161.00 | 505420 | HERGETT5 161.00 | 0 |  | 1 | 18SP | 148 | 148 | 186.6 | 190.8 | 190.8768 | 194.2293 | [7 empty] | CATEGORYB | SINGLE | HARISBURG TAP - MARKED TREE 161KV CKT 1 | 0 | 338165 | 5MTREE 161.00 | 338167 | 5HRSBRG* 161.00 | 0 |  | 1 |  | This is based on 1200/5MR CTs connected at 600/5 in the bushings of a 1600 amp breaker. According to Criteria 12, the CT should be rated for 980 amps. The next limits are 1200 amp for a wave trap and disconnect switches, 1600 amps for the breaker, and 1890 amps for the bus. | SWPA | HERGETT - JONESBORO 161KV CKT 1 SWPA | Increase the CT ratio to 1200/5. This would involve changing taps on the CT, adjusting the scaling on a panel meter, and changing relay settings. | [11 empty] | 505420-338170 | [25 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 2 | 2007AG2AFS81T23123218SP | TO->FROM | HERGETT - JONESBORO 161KV CKT 1 | S | EES | SWPA | EES_ARK | EMINTH | 0 | 338170 | 5JONES 161.00 | 505420 | HERGETT5 161.00 | 0 |  | 1 | 18SP | 148 | 148 | 180.0 | 184.2 | 184.2264 | 187.4949 | [7 empty] | CATEGORYB | SINGLE | HARISBURG TAP - TRUMANN 161KV CKT 1 | 0 | 338167 | 5HRSBRG* 161.00 | 338169 | 5TRUMAN 161.00 | 0 |  | 1 |  | This is based on 1200/5MR CTs connected at 600/5 in the bushings of a 1600 amp breaker. According to Criteria 12, the CT should be rated for 980 amps. The next limits are 1200 amp for a wave trap and disconnect switches, 1600 amps for the breaker, and 1890 amps for the bus. | SWPA | HERGETT - JONESBORO 161KV CKT 1 SWPA | Increase the CT ratio to 1200/5. This would involve changing taps on the CT, adjusting the scaling on a panel meter, and changing relay settings. | [11 empty] | 505420-338170 | [25 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 2 | 2007AG2AFS81T23153218SP | TO->FROM | HERGETT - JONESBORO 161KV CKT 1 | S | EES | SWPA | EES_ARK | EMINTH | 0 | 338170 | 5JONES 161.00 | 505420 | HERGETT5 161.00 | 0 |  | 1 | 18SP | 148 | 148 | 171.9 | 175.9 | 176.0306 | 179.1092 | [7 empty] | CATEGORYB | SINGLE | TRUMANN - TRUMANN WEST AECC 161KV CKT 1 | 0 | 338169 | 5TRUMAN 161.00 | 338707 | 5TRUM-W# 161.00 | 0 |  | 1 |  | This is based on 1200/5MR CTs connected at 600/5 in the bushings of a 1600 amp breaker. According to Criteria 12, the CT should be rated for 980 amps. The next limits are 1200 amp for a wave trap and disconnect switches, 1600 amps for the breaker, and 1890 amps for the bus. | SWPA | HERGETT - JONESBORO 161KV CKT 1 SWPA | Increase the CT ratio to 1200/5. This would involve changing taps on the CT, adjusting the scaling on a panel meter, and changing relay settings. | [11 empty] | 505420-338170 | [25 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 4 | 4 | 2007AG2AFS81T27634418SP | FROM->TO | HUBEN 345/161KV TRANSFORMER CKT 1 | S | AECI | AECI | AECI | SHO-ME | 0 | 300042 | 7HUBEN 345.00 | 300088 | 5HUBEN 161.00 | 0 |  | 1 | 18SP | 392 | 392 | 100.6 | 102.2 | 102.4262 | 103.676 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE - MORGAN 345KV CKT 1 | 0 | 549984 | BROOKLINE 7345.00 | 300045 | 7MORGAN 345.00 | 0 |  | 1 |  |  | AECI | HUBEN 345/161KV TRANSFORMER CKT 1 | Install a second Huben 345/161kV transformer | [12 empty] | 6500000 | 2008-01-01 | [23 empty] | 2017-06-01 | 2017-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 2 | 2007AG2AFS81T7193218SP | FROM->TO | HUDSON JUNCTION - PITTSBURG 69KV CKT 1 | REL | WERE | WERE | SEAST | SEAST | 0 | 533764 | HUDSJCT2 69.000 | 533770 | PITTSBG2 69.000 | 0 |  | 1 | 18SP | 80 | 80 |  | 100.2 | 98.4718 | 100.1287 | [7 empty] | CATEGORYB | SINGLE | LITCHFIELD - ROUSE 69KV CKT 1 | 0 | 533765 | LITCH 2 69.000 | 533771 | ROUSE 2 69.000 | 0 |  | 1 |  |  | WERE | HUDSON JUNCTION - PITTSBURG 69KV CKT 1 | Rebuild 1.41 miles | [11 empty] | 450k per mile | 634500 | 2008-01-01 | [23 empty] | 2018-06-01 | 2018-06-01
2005-AG2 | 2005-AG2 | [7 empty] | 55948540441559485607913310SP |  | HUGO POWER PLANT - VALLIANT 138KV CKT 1 | U | WFEC | AEPW |  |  | 0 | 55948 | HUGO PP4 138 | 54044 | VALIANT4 138 | 0 |  | 1 | 10SP |  | 315 | [12 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | AEPW | HUGO POWER PLANT - VALLIANT 345 KV AEPW | Vallient 345 KV line terminal | [5 empty] | 24 |  | Y |  |  |  |  | 2500000 | [24 empty] | 2012-07-01 | 2012-07-01
2005-AG2 | 2005-AG2 | [7 empty] | 55948540441559485607913310SP |  | HUGO POWER PLANT - VALLIANT 138KV CKT 1 | U | WFEC | AEPW |  |  | 0 | 55948 | HUGO PP4 138 | 54044 | VALIANT4 138 | 0 |  | 1 | 10SP |  | 315 | [12 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | HUGO POWER PLANT - VALLIANT 345 KV WFEC | New 19 miles 345 KV | 500 | 500 |  |  | 19 | 24 |  | Y |  |  |  | The 345kv line would go: From Hugo Power Station (55948) to a new 500 MVA 138/345kv autotransformer at the Hugo plant site to PSO Valiant (54037) USE data from GEN-2004-018 | 16000000 | [24 empty] | 2012-07-01 | 2012-07-01
2005-AG2 | 2005-AG2 | [7 empty] | 55948540441559485607913310SP |  | HUGO POWER PLANT 345/138KV TRANSFORMER CKT 1 | U | WFEC | AEPW |  |  | 0 | 55948 | HUGO PP4 138 | 54044 | VALIANT4 138 | 0 |  | 1 | 10SP |  | 315 | [12 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | HUGO POWER PLANT 345/138KV TRANSFORMER CKT 1 | New 345/138 kv Auto | 500 | 500 |  |  | 19 | 24 |  | Y |  |  |  | The 345kv line would go: From Hugo Power Station (55948) to a new 500 MVA 138/345kv autotransformer at the Hugo plant site to PSO Valiant (54037) USE data from GEN-2004-018 | 16000000 | [24 empty] | 2012-07-01 | 2012-07-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2007AG2AFS81T6175518SP | TO->FROM | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | EXP | WERE | MIDW | WEST | REG E-IL | 0 | 533419 | HEC 3 115.00 | 530618 | HUNTSVL3 115.00 | 0 |  | 1 | 18SP | 92 | 92 |  | 108.5 | 100.9386 | 102.9209 | [7 empty] | CATEGORYB | SINGLE | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 533045 | GILL W 4 138.00 | 0 |  | 1 |  |  | MIDW | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 MIDW | Tear down and rebuild 73.4% Ownership 28.79 mile HEC-Huntsville 115 kV line and replace CT, wavetrap and relays. | 223 | 240 | 223 | 240 | 21.13 | 9 | 9 |  |  |  |  | 562.5k per mile | 11885625 | 2008-01-01 | [23 empty] | 2018-06-01 | 2018-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2007AG2AFS81T6175518SP | TO->FROM | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | EXP | WERE | MIDW | WEST | REG E-IL | 0 | 533419 | HEC 3 115.00 | 530618 | HUNTSVL3 115.00 | 0 |  | 1 | 18SP | 92 | 92 |  | 108.5 | 100.9386 | 102.9209 | [7 empty] | CATEGORYB | SINGLE | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 533045 | GILL W 4 138.00 | 0 |  | 1 |  |  | MIDW | HUNTSVILLE - ST_JOHN 115KV CKT 1 | Rebuild 26.5 miles Huntsville - St. John 115 kV line and replace CT, wavetrap, breakers, and relays. | 223 | 240 | 223 | 240 | 26.5 | 9 | 9 | [5 empty] | 7965000 | 2008-01-01 | [23 empty] | 2018-06-01 | 2018-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2007AG2AFS81T6175518SP | TO->FROM | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | EXP | WERE | MIDW | WEST | REG E-IL | 0 | 533419 | HEC 3 115.00 | 530618 | HUNTSVL3 115.00 | 0 |  | 1 | 18SP | 92 | 92 |  | 108.5 | 100.9386 | 102.9209 | [7 empty] | CATEGORYB | SINGLE | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 533045 | GILL W 4 138.00 | 0 |  | 1 |  |  | WERE | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 WERE | Tear down and rebuild 26.6% Ownership 28.79 mile HEC-Huntsville 115 kV line and replace CT, wavetrap and relays. | 223 | 240 | 223 | 240 | 7.66 | 36 | 36 |  |  |  |  | 562.5k per mile | 4308750 | 2008-01-01 | [23 empty] | 2018-06-01 | 2018-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2007AG2AFS81T6125518SP | TO->FROM | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | EXP | WERE | MIDW | WEST | REG E-IL | 0 | 533419 | HEC 3 115.00 | 530618 | HUNTSVL3 115.00 | 0 |  | 1 | 18SP | 92 | 92 | 112.6 | 108.8 | 101.4679 | 101.7134 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - MULLERGREN 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 |  |  | MIDW | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 MIDW | Tear down and rebuild 73.4% Ownership 28.79 mile HEC-Huntsville 115 kV line and replace CT, wavetrap and relays. | 223 | 240 | 223 | 240 | 21.13 | 9 | 9 |  |  |  |  | 562.5k per mile | 11885625 | 2008-01-01 | [23 empty] | 2018-06-01 | 2018-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2007AG2AFS81T6125518SP | TO->FROM | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | EXP | WERE | MIDW | WEST | REG E-IL | 0 | 533419 | HEC 3 115.00 | 530618 | HUNTSVL3 115.00 | 0 |  | 1 | 18SP | 92 | 92 | 112.6 | 108.8 | 101.4679 | 101.7134 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - MULLERGREN 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 |  |  | MIDW | HUNTSVILLE - ST_JOHN 115KV CKT 1 | Rebuild 26.5 miles Huntsville - St. John 115 kV line and replace CT, wavetrap, breakers, and relays. | 223 | 240 | 223 | 240 | 26.5 | 9 | 9 | [5 empty] | 7965000 | 2008-01-01 | [23 empty] | 2018-06-01 | 2018-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2007AG2AFS81T6125518SP | TO->FROM | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | EXP | WERE | MIDW | WEST | REG E-IL | 0 | 533419 | HEC 3 115.00 | 530618 | HUNTSVL3 115.00 | 0 |  | 1 | 18SP | 92 | 92 | 112.6 | 108.8 | 101.4679 | 101.7134 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - MULLERGREN 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 |  |  | WERE | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 WERE | Tear down and rebuild 26.6% Ownership 28.79 mile HEC-Huntsville 115 kV line and replace CT, wavetrap and relays. | 223 | 240 | 223 | 240 | 7.66 | 36 | 36 |  |  |  |  | 562.5k per mile | 4308750 | 2008-01-01 | [23 empty] | 2018-06-01 | 2018-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2007AG2AFS81T6165518SP | FROM->TO | HUNTSVILLE - ST_JOHN 115KV CKT 1 | EXP | MIDW | MIDW | REG E-IL | REG E-IL | 0 | 530618 | HUNTSVL3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 18SP | 80 | 88 |  | 106.7 | 98.8595 | 100.8385 | [7 empty] | CATEGORYB | SINGLE | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 533045 | GILL W 4 138.00 | 0 |  | 1 |  |  | MIDW | HUNTSVILLE - ST_JOHN 115KV CKT 1 | Rebuild 26.5 miles Huntsville - St. John 115 kV line and replace CT, wavetrap, breakers, and relays. | 223 | 240 | 223 | 240 | 26.5 | 9 | 9 | [5 empty] | 7965000 | 2008-01-01 | [23 empty] | 2018-06-01 | 2018-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 1 | 4 | 2007AG2AFS81T161409AP | FROM->TO | IODINE - MOORELAND 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 09AP | 72 | 72 | 103.4 | 103.3 | 115.6884 | 131.3028 | [7 empty] | CATEGORYB | SINGLE | FPL SWITCH - MOORELAND 138KV CKT 1 | 0 | 515785 | WINDFRM4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 |  |  | WFEC | IODINE - MOORELAND 138KV CKT 1 | Upgrade CTs at Mooreland (Iodine Branch) to 1200A. | 183 | 228 | [35 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 1 | 2007AG2AFS81T224109AP | FROM->TO | IODINE - MOORELAND 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 09AP | 72 | 72 |  |  | 110.4443 | 128.6944 | [7 empty] | CATEGORYB | SINGLE | FARGOJCT2 69.000 - FT SUPPLY 69KV CKT 1 | 0 | 520919 | FTSUPLY2 69.000 | 521196 | FARGOJCT2 69.000 | 0 |  | 1 |  |  | WFEC | IODINE - MOORELAND 138KV CKT 1 | Upgrade CTs at Mooreland (Iodine Branch) to 1200A. | 183 | 228 | [35 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 1 | 2007AG2AFS81T304109AP | FROM->TO | IODINE - MOORELAND 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 09AP | 72 | 72 |  |  | 107.9137 | 126.1705 | [7 empty] | CATEGORYB | SINGLE | FARGOJCT2 69.000 - WOODWARD 69KV CKT 1 | 0 | 521096 | WOODWRD2 69.000 | 521196 | FARGOJCT2 69.000 | 0 |  | 1 |  |  | WFEC | IODINE - MOORELAND 138KV CKT 1 | Upgrade CTs at Mooreland (Iodine Branch) to 1200A. | 183 | 228 | [35 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 1 | 4 | 2007AG2AFS81T11409AP | FROM->TO | IODINE - MOORELAND 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 09AP | 72 | 72 |  |  | 87.139 | 102.6196 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | IODINE - MOORELAND 138KV CKT 1 | Upgrade CTs at Mooreland (Iodine Branch) to 1200A. | 183 | 228 | [35 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 4 | 2007AG2AFS81T364409FA | FROM->TO | IODINE - MOORELAND 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 09FA | 72 | 72 |  |  | 86.0795 | 114.2462 | [7 empty] | CATEGORYB | SINGLE | FPL SWITCH - MOORELAND 138KV CKT 1 | 0 | 515785 | WINDFRM4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 |  |  | WFEC | IODINE - MOORELAND 138KV CKT 1 | Upgrade CTs at Mooreland (Iodine Branch) to 1200A. | 183 | 228 | [35 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 1 | 2007AG2AFS81T454109FA | FROM->TO | IODINE - MOORELAND 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 09FA | 72 | 72 |  |  | 76.1656 | 111.7693 | [7 empty] | CATEGORYB | SINGLE | FARGOJCT2 69.000 - FT SUPPLY 69KV CKT 1 | 0 | 520919 | FTSUPLY2 69.000 | 521196 | FARGOJCT2 69.000 | 0 |  | 1 |  |  | WFEC | IODINE - MOORELAND 138KV CKT 1 | Upgrade CTs at Mooreland (Iodine Branch) to 1200A. | 183 | 228 | [35 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 1 | 2007AG2AFS81T544109FA | FROM->TO | IODINE - MOORELAND 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 09FA | 72 | 72 |  |  | 71.142 | 106.6235 | [7 empty] | CATEGORYB | SINGLE | FARGOJCT2 69.000 - WOODWARD 69KV CKT 1 | 0 | 521096 | WOODWRD2 69.000 | 521196 | FARGOJCT2 69.000 | 0 |  | 1 |  |  | WFEC | IODINE - MOORELAND 138KV CKT 1 | Upgrade CTs at Mooreland (Iodine Branch) to 1200A. | 183 | 228 | [35 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 1 | 4 | 2007AG2AFS81T1191409G | FROM->TO | IODINE - MOORELAND 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 09G | 72 | 72 |  |  | 84.7126 | 103.3326 | [7 empty] | CATEGORYB | SINGLE | FARGOJCT2 69.000 - FT SUPPLY 69KV CKT 1 | 0 | 520919 | FTSUPLY2 69.000 | 521196 | FARGOJCT2 69.000 | 0 |  | 1 |  |  | WFEC | IODINE - MOORELAND 138KV CKT 1 | Upgrade CTs at Mooreland (Iodine Branch) to 1200A. | 183 | 228 | [35 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 1 | 4 | 2007AG2AFS81T961409G | FROM->TO | IODINE - MOORELAND 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 09G | 72 | 72 |  |  | 85.146 | 100.5115 | [7 empty] | CATEGORYB | SINGLE | FPL SWITCH - MOORELAND 138KV CKT 1 | 0 | 515785 | WINDFRM4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 |  |  | WFEC | IODINE - MOORELAND 138KV CKT 1 | Upgrade CTs at Mooreland (Iodine Branch) to 1200A. | 183 | 228 | [35 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 1 | 1 | 2007AG2AFS81T721109SH | FROM->TO | IODINE - MOORELAND 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 09SH | 72 | 72 |  |  | 87.7143 | 106.3087 | [7 empty] | CATEGORYB | SINGLE | FARGOJCT2 69.000 - FT SUPPLY 69KV CKT 1 | 0 | 520919 | FTSUPLY2 69.000 | 521196 | FARGOJCT2 69.000 | 0 |  | 1 |  |  | WFEC | IODINE - MOORELAND 138KV CKT 1 | Upgrade CTs at Mooreland (Iodine Branch) to 1200A. | 183 | 228 | [35 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 1 | 4 | 2007AG2AFS81T911409SH | FROM->TO | IODINE - MOORELAND 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 09SH | 72 | 72 |  |  | 85.2314 | 100.7366 | [7 empty] | CATEGORYB | SINGLE | FPL SWITCH - MOORELAND 138KV CKT 1 | 0 | 515785 | WINDFRM4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 |  |  | WFEC | IODINE - MOORELAND 138KV CKT 1 | Upgrade CTs at Mooreland (Iodine Branch) to 1200A. | 183 | 228 | [35 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 1 | 1 | 2007AG2AFS81T831109SH | FROM->TO | IODINE - MOORELAND 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 09SH | 72 | 72 |  |  | 81.6932 | 100.2935 | [7 empty] | CATEGORYB | SINGLE | FARGOJCT2 69.000 - WOODWARD 69KV CKT 1 | 0 | 521096 | WOODWRD2 69.000 | 521196 | FARGOJCT2 69.000 | 0 |  | 1 |  |  | WFEC | IODINE - MOORELAND 138KV CKT 1 | Upgrade CTs at Mooreland (Iodine Branch) to 1200A. | 183 | 228 | [35 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 1 | 2007AG2AFS81T714109WP | FROM->TO | IODINE - MOORELAND 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 09WP | 72 | 72 |  |  | 72.9674 | 108.686 | [7 empty] | CATEGORYB | SINGLE | FARGOJCT2 69.000 - FT SUPPLY 69KV CKT 1 | 0 | 520919 | FTSUPLY2 69.000 | 521196 | FARGOJCT2 69.000 | 0 |  | 1 |  |  | WFEC | IODINE - MOORELAND 138KV CKT 1 | Upgrade CTs at Mooreland (Iodine Branch) to 1200A. | 183 | 228 | [35 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 1 | 2007AG2AFS81T794109WP | FROM->TO | IODINE - MOORELAND 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 09WP | 72 | 72 |  |  | 66.6388 | 102.3133 | [7 empty] | CATEGORYB | SINGLE | FARGOJCT2 69.000 - WOODWARD 69KV CKT 1 | 0 | 521096 | WOODWRD2 69.000 | 521196 | FARGOJCT2 69.000 | 0 |  | 1 |  |  | WFEC | IODINE - MOORELAND 138KV CKT 1 | Upgrade CTs at Mooreland (Iodine Branch) to 1200A. | 183 | 228 | [35 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 4 | 2007AG2AFS81T1404410SP | FROM->TO | IODINE - MOORELAND 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 10SP | 72 | 72 |  |  | 64.3172 | 100.2771 | [7 empty] | CATEGORYB | SINGLE | FARGOJCT2 69.000 - FT SUPPLY 69KV CKT 1 | 0 | 520919 | FTSUPLY2 69.000 | 521196 | FARGOJCT2 69.000 | 0 |  | 1 |  |  | WFEC | IODINE - MOORELAND 138KV CKT 1 | Upgrade CTs at Mooreland (Iodine Branch) to 1200A. | 183 | 228 | [35 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 1 | 2007AG2AFS81T404110WP | FROM->TO | IODINE - MOORELAND 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 10WP | 72 | 72 |  |  | 72.1867 | 107.932 | [7 empty] | CATEGORYB | SINGLE | FARGOJCT2 69.000 - FT SUPPLY 69KV CKT 1 | 0 | 520919 | FTSUPLY2 69.000 | 521196 | FARGOJCT2 69.000 | 0 |  | 1 |  |  | WFEC | IODINE - MOORELAND 138KV CKT 1 | Upgrade CTs at Mooreland (Iodine Branch) to 1200A. | 183 | 228 | [35 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 1 | 2007AG2AFS81T454110WP | FROM->TO | IODINE - MOORELAND 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 10WP | 72 | 72 |  |  | 65.753 | 101.454 | [7 empty] | CATEGORYB | SINGLE | FARGOJCT2 69.000 - WOODWARD 69KV CKT 1 | 0 | 521096 | WOODWRD2 69.000 | 521196 | FARGOJCT2 69.000 | 0 |  | 1 |  |  | WFEC | IODINE - MOORELAND 138KV CKT 1 | Upgrade CTs at Mooreland (Iodine Branch) to 1200A. | 183 | 228 | [35 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 1 | 4 | 2007AG2AFS81T2151413SP | FROM->TO | IODINE - MOORELAND 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 13SP | 72 | 72 |  |  | 64.2661 | 100.2528 | [7 empty] | CATEGORYB | SINGLE | FARGOJCT2 69.000 - FT SUPPLY 69KV CKT 1 | 0 | 520919 | FTSUPLY2 69.000 | 521196 | FARGOJCT2 69.000 | 0 |  | 1 |  |  | WFEC | IODINE - MOORELAND 138KV CKT 1 | Upgrade CTs at Mooreland (Iodine Branch) to 1200A. | 183 | 228 | [35 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 1 | 2007AG2AFS81T814113WP | FROM->TO | IODINE - MOORELAND 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 13WP | 72 | 72 |  |  | 73.1247 | 108.9744 | [7 empty] | CATEGORYB | SINGLE | FARGOJCT2 69.000 - FT SUPPLY 69KV CKT 1 | 0 | 520919 | FTSUPLY2 69.000 | 521196 | FARGOJCT2 69.000 | 0 |  | 1 |  |  | WFEC | IODINE - MOORELAND 138KV CKT 1 | Upgrade CTs at Mooreland (Iodine Branch) to 1200A. | 183 | 228 | [35 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 1 | 2007AG2AFS81T864113WP | FROM->TO | IODINE - MOORELAND 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 13WP | 72 | 72 |  |  | 66.4156 | 102.1644 | [7 empty] | CATEGORYB | SINGLE | FARGOJCT2 69.000 - WOODWARD 69KV CKT 1 | 0 | 521096 | WOODWRD2 69.000 | 521196 | FARGOJCT2 69.000 | 0 |  | 1 |  |  | WFEC | IODINE - MOORELAND 138KV CKT 1 | Upgrade CTs at Mooreland (Iodine Branch) to 1200A. | 183 | 228 | [35 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 2 | 2007AG2AFS81T3233210SP | TO->FROM | JARBALO JUNCTION SWITCHING STATION - STRANGER CREEK 115KV CKT 1 | REL | WERE | WERE | NEAST | NEAST | 0 | 533268 | STRANGR3 115.00 | 533244 | JARBALO3 115.00 | 0 |  | 1 | 10SP | 223 | 240 |  | 100 | 98.3925 | 100.7043 | [7 empty] | CATEGORYB | SINGLE | STRANGER CREEK - THORNTON STREET 115KV CKT 1 | 0 | 533268 | STRANGR3 115.00 | 533272 | THORNTN3 115.00 | 0 |  | 1 |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 18 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2010-06-01 | 2011-06-01 | 2010-10-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 2 | 2007AG2AFS81T3913213SP | TO->FROM | JARBALO JUNCTION SWITCHING STATION - STRANGER CREEK 115KV CKT 1 | REL | WERE | WERE | NEAST | NEAST | 0 | 533268 | STRANGR3 115.00 | 533244 | JARBALO3 115.00 | 0 |  | 1 | 13SP | 223 | 240 | 101.1 | 100.6 | 99.5031 | 101.806 | [7 empty] | CATEGORYB | SINGLE | STRANGER CREEK - THORNTON STREET 115KV CKT 1 | 0 | 533268 | STRANGR3 115.00 | 533272 | THORNTN3 115.00 | 0 |  | 1 |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 18 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2010-06-01 | 2011-06-01 | 2010-10-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 2 | 2007AG2AFS81T6823218SP | TO->FROM | JARBALO JUNCTION SWITCHING STATION - STRANGER CREEK 115KV CKT 1 | REL | WERE | WERE | NEAST | NEAST | 0 | 533268 | STRANGR3 115.00 | 533244 | JARBALO3 115.00 | 0 |  | 1 | 18SP | 223 | 240 | 105.0 | 103.8 | 104.1644 | 106.4123 | [7 empty] | CATEGORYB | SINGLE | STRANGER CREEK - THORNTON STREET 115KV CKT 1 | 0 | 533268 | STRANGR3 115.00 | 533272 | THORNTN3 115.00 | 0 |  | 1 |  |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 18 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 8050000 | 2006-07-25 | [23 empty] | 2010-06-01 | 2011-06-01 | 2010-10-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 3 | 2 | 2007AG2AFS81T3313209SP | FROM->TO | JEWELL 3 - SMITH CENTER 115KV CKT 1 | S | MKEC | MKEC |  |  | 0 | 539669 | JEWELL 3 115.00 | 539693 | SMITH-C3 115.00 | 0 |  | 1 | 09SP | 79.7 | 79.7 |  |  | 99.505 | 100.8629 | [7 empty] | CATEGORYB | SINGLE | BELOIT - CONCORDIA 115KV CKT 1 | 0 | 539650 | BELOIT 3 115.00 | 539657 | CONCORD3 115.00 | 0 |  | 1 |  |  | MKEC | JEWELL 3 - SMITH CENTER 115KV CKT 1 | Interim Redispatch from 6/1/09-10/1/09 | [37 empty] | 2009-06-01 | 2009-10-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2007AG2AFS81T575509SH | FROM->TO | KELLY - SOUTH SENECA 115KV CKT 1 | EXP | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 09SH | 92 | 92 | 113.9 | 114.4 | 116.7108 | 117.167 | [7 empty] | CATEGORYB | SINGLE | EAST MANHATTAN - ELMCREK6 230.00 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 539639 | ELMCREK6 230.00 | 0 |  | 1 |  |  | WERE | KELLY - SOUTH SENECA 115KV CKT 1 | Rebuild 10.28 mile line with 1192.5 kcmil ACSR and replace CTs. | 160 | 160 | 160 | 160 | 10.28 | 24 | 24 |  | 0.0062742 | 0.055391 | 0.0081838 | Breaker limit is 160 MVA. | 4100000 | 2008-01-01 | [23 empty] | 2009-06-01 | 2010-12-01 | 2009-10-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2007AG2AFS81T825509SH | FROM->TO | KELLY - SOUTH SENECA 115KV CKT 1 | EXP | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 09SH | 92 | 92 | 113.8 | 114.3 | 116.6148 | 117.1366 | [7 empty] | CATEGORYB | SINGLE | CONCORDIA - ELMCREK6 230.00 230KV CKT 1 | 0 | 539639 | ELMCREK6 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  | WERE | KELLY - SOUTH SENECA 115KV CKT 1 | Rebuild 10.28 mile line with 1192.5 kcmil ACSR and replace CTs. | 160 | 160 | 160 | 160 | 10.28 | 24 | 24 |  | 0.0062742 | 0.055391 | 0.0081838 | Breaker limit is 160 MVA. | 4100000 | 2008-01-01 | [23 empty] | 2009-06-01 | 2010-12-01 | 2009-10-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 5 | 5 | 2007AG2AFS81T3515509SH | FROM->TO | KELLY - SOUTH SENECA 115KV CKT 1 | EXP | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 09SH | 92 | 92 | 113.8 | 114.3 | 116.6134 | 117.1318 | [7 empty] | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539657 | CONCORD3 115.00 | 539658 | CONCRD6 230.00 | 539904 | CONCOD-T 13.800 | 1 |  |  | WERE | KELLY - SOUTH SENECA 115KV CKT 1 | Rebuild 10.28 mile line with 1192.5 kcmil ACSR and replace CTs. | 160 | 160 | 160 | 160 | 10.28 | 24 | 24 |  | 0.0062742 | 0.055391 | 0.0081838 | Breaker limit is 160 MVA. | 4100000 | 2008-01-01 | [23 empty] | 2009-06-01 | 2010-12-01 | 2009-10-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2007AG2AFS81T1865509SP | FROM->TO | KELLY - SOUTH SENECA 115KV CKT 1 | EXP | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 09SP | 92 | 92 | 111.1 | 110.5 | 135.2013 | 135.2348 | [7 empty] | CATEGORYB | SINGLE | CONCORDIA - ELMCREK6 230.00 230KV CKT 1 | 0 | 539639 | ELMCREK6 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  | WERE | KELLY - SOUTH SENECA 115KV CKT 1 | Rebuild 10.28 mile line with 1192.5 kcmil ACSR and replace CTs. | 160 | 160 | 160 | 160 | 10.28 | 24 | 24 |  | 0.0062742 | 0.055391 | 0.0081838 | Breaker limit is 160 MVA. | 4100000 | 2008-01-01 | [23 empty] | 2009-06-01 | 2010-12-01 | 2009-10-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 5 | 5 | 2007AG2AFS81T6885509SP | FROM->TO | KELLY - SOUTH SENECA 115KV CKT 1 | EXP | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 09SP | 92 | 92 | 111.1 | 110.5 | 135.1949 | 135.2289 | [7 empty] | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539657 | CONCORD3 115.00 | 539658 | CONCRD6 230.00 | 539904 | CONCOD-T 13.800 | 1 |  |  | WERE | KELLY - SOUTH SENECA 115KV CKT 1 | Rebuild 10.28 mile line with 1192.5 kcmil ACSR and replace CTs. | 160 | 160 | 160 | 160 | 10.28 | 24 | 24 |  | 0.0062742 | 0.055391 | 0.0081838 | Breaker limit is 160 MVA. | 4100000 | 2008-01-01 | [23 empty] | 2009-06-01 | 2010-12-01 | 2009-10-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2007AG2AFS81T1385509SP | FROM->TO | KELLY - SOUTH SENECA 115KV CKT 1 | EXP | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 09SP | 92 | 92 | 111.2 | 110.6 | 134.7637 | 134.7834 | [7 empty] | CATEGORYB | SINGLE | EAST MANHATTAN - ELMCREK6 230.00 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 539639 | ELMCREK6 230.00 | 0 |  | 1 |  |  | WERE | KELLY - SOUTH SENECA 115KV CKT 1 | Rebuild 10.28 mile line with 1192.5 kcmil ACSR and replace CTs. | 160 | 160 | 160 | 160 | 10.28 | 24 | 24 |  | 0.0062742 | 0.055391 | 0.0081838 | Breaker limit is 160 MVA. | 4100000 | 2008-01-01 | [23 empty] | 2009-06-01 | 2010-12-01 | 2009-10-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2007AG2AFS81V7545518SP |  | KINSLEY 115KV | REL | MIDW |  | REG E-IL |  |  | 530619 | KINSLEY3 115.00 | [5 empty] | 18SP | [6 empty] | 0.86472 | 0.89657 | 0.92878 | 0.89912 | 0.9423 | 0.9 | 1.05 | CATEGORYB | SINGLE | SEWARD - ST JOHN 115KV CKT 1 | 0 | 539692 | SEWARD 3 115.00 | 539696 | ST-JOHN3 115.00 | 0 |  | 1 |  |  | MIDW | KINSLEY 115KV Capacitor | Install 10MVAR capacitors at Kinsley 115 kV | [5 empty] | 12 | 12 | [30 empty] | 2011-06-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2007AG2AFS81T1895509SP | TO->FROM | KNOB HILL - SMITTYVILLE N.M. COOP (NEMAHA MARSHALL R.E. 115KV CKT 1 | EXP | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533338 | SMITTYV3 115.00 | 533332 | KNOB HL3 115.00 | 0 |  | 1 | 09SP | 92 | 92 |  |  | 103.2854 | 103.2818 | [7 empty] | CATEGORYB | SINGLE | CONCORDIA - ELMCREK6 230.00 230KV CKT 1 | 0 | 539639 | ELMCREK6 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [23 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2007-AG2 | AFS9 | ISLAND-LOAD |  |  | FDNS |  | 5 | 5 | 2007AG2AFS81T6915509SP | TO->FROM | KNOB HILL - SMITTYVILLE N.M. COOP (NEMAHA MARSHALL R.E. 115KV CKT 1 | EXP | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533338 | SMITTYV3 115.00 | 533332 | KNOB HL3 115.00 | 0 |  | 1 | 09SP | 92 | 92 |  |  | 103.281 | 103.2778 | [7 empty] | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539657 | CONCORD3 115.00 | 539658 | CONCRD6 230.00 | 539904 | CONCOD-T 13.800 | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [23 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2007AG2AFS81T1415509SP | TO->FROM | KNOB HILL - SMITTYVILLE N.M. COOP (NEMAHA MARSHALL R.E. 115KV CKT 1 | EXP | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533338 | SMITTYV3 115.00 | 533332 | KNOB HL3 115.00 | 0 |  | 1 | 09SP | 92 | 92 |  |  | 102.9507 | 102.9271 | [7 empty] | CATEGORYB | SINGLE | EAST MANHATTAN - ELMCREK6 230.00 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 539639 | ELMCREK6 230.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [23 empty] | 2009-06-01 | 2010-06-01 | 2009-10-01
2006-AG1 | 2006-AG1 | [7 empty] | KNOOBHIL41421OKGEMTL-51316SP |  | KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1 | U | OKGE |  |  |  | 1 | 514795 | KNOBHIL4 138 | 514794 | KNOBHIL269.0 | 515732 | KNOBHIL113.2 | 1 | 16SP |  | 67 | [12 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | OKGE | KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1 | Replace bus tie with 100MVA transformer | 123 | 134 | 123 | 134 |  | 15 | 12 | [5 empty] | 1750000 | [24 empty] | 2006-06-01 | 2008-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 4 | 4 | 2007AG2AFS81V10734418SP |  | LACEY 69KV | EXP | WFEC |  | AEP-IM |  |  | 520967 | LACEY 2 69.000 | [5 empty] | 18SP | [6 empty] | 0.77181 | 0.78192 | 0.79024 | 0.77955 | 0.98015 | 0.9 | 1.05 | CATEGORYB | SINGLE | DOVER SW (DOVER) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 520882 | DOVERSW4 138.00 | 520881 | DOVERSW2 69.000 | 521166 | DVRTERT 13.800 | 1 |  |  | WFEC | Multi-Dover-Twin Lake_Cresent 138 kV | Convert 69 kV to 138 kV and install terminal equipment at Dover SW; Instal 7 miles of new 138 kV fro WFEC Twin Lakes to OGE Cresent substation | [37 empty] | 2014-06-01 | 2014-06-01
NA | [8 empty] | NAKACP5429815429651 |  | LACYGNE - WEST GARDNER 345KV CKT 1 | U | KACP | KACP |  |  | 0 | 542981 | LACYGNE7 | 542965 | W.GRDNR7 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | KACP | LACYGNE - WEST GARDNER 345KV CKT 1 | KCPL Sponsored Project to Reconductor Line to be In-Service by 6/1/2006 | [37 empty] | 2006-06-01 | 2006-06-01
2007-AG2 | AFS9 | CONT-1210 - Bismark - COOP 115kV | FDNS |  | FDNS |  | 4 | 3 | 2007AG2AFS81T1914309SP | FROM->TO | LAWRENCE HILL - MOCKINGBIRD HILL SWITCHING STATION 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533250 | LWRNCHL3 115.00 | 533253 | MOCKBRD3 115.00 | 0 |  | 1 | 09SP | 92 | 92 | 100.1 | 100.9 | 100.6188 | 100.4145 | [7 empty] | CATEGORYB | SINGLE | BISMARK JUNCTION SWITCHING STATION - FARMERS CONSUMER CO-OP 115KV CKT 1 | 0 | 533234 | BISMARK3 115.00 | 533236 | COOP 3 115.00 | 0 |  | 1 |  |  | WERE | LAWRENCE HILL - MOCKINGBIRD HILL SWITCHING STATION 115KV CKT 1 | Rebuild 5.49 miles | [5 empty] | 18 | 18 | [30 empty] | 2009-06-01 | 2012-06-01 | 2011-10-01
2007-AG2 | AFS9 | CONT-1210 - Bismark - COOP 115kV |  |  | FDNS |  | 3 | 3 | 2007AG2AFS81T2103310SP | FROM->TO | LAWRENCE HILL - MOCKINGBIRD HILL SWITCHING STATION 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533250 | LWRNCHL3 115.00 | 533253 | MOCKBRD3 115.00 | 0 |  | 1 | 10SP | 92 | 92 | 100.2 |  | 100.3634 | 101.3696 | [7 empty] | CATEGORYB | SINGLE | BISMARK JUNCTION SWITCHING STATION - FARMERS CONSUMER CO-OP 115KV CKT 1 | 0 | 533234 | BISMARK3 115.00 | 533236 | COOP 3 115.00 | 0 |  | 1 |  |  | WERE | LAWRENCE HILL - MOCKINGBIRD HILL SWITCHING STATION 115KV CKT 1 | Rebuild 5.49 miles | [5 empty] | 18 | 18 | [30 empty] | 2009-06-01 | 2012-06-01 | 2011-10-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 3 | 3 | 2007AG2AFS81T11203310SP | FROM->TO | LAWRENCE HILL - MOCKINGBIRD HILL SWITCHING STATION 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533250 | LWRNCHL3 115.00 | 533253 | MOCKBRD3 115.00 | 0 |  | 1 | 10SP | 92 | 92 |  |  | 99.5229 | 100.4914 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-58 | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WERE | LAWRENCE HILL - MOCKINGBIRD HILL SWITCHING STATION 115KV CKT 1 | Rebuild 5.49 miles | [5 empty] | 18 | 18 | [30 empty] | 2009-06-01 | 2012-06-01 | 2011-10-01
2007-AG2 | AFS9 | CONT-1210 - Bismark - COOP 115kV | FDNS |  | FDNS |  | 5 | 5 | 2007AG2AFS81T2975513SP | FROM->TO | LAWRENCE HILL - MOCKINGBIRD HILL SWITCHING STATION 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533250 | LWRNCHL3 115.00 | 533253 | MOCKBRD3 115.00 | 0 |  | 1 | 13SP | 92 | 92 | 103.7 | 104 | 102.5329 | 104.2405 | [7 empty] | CATEGORYB | SINGLE | BISMARK JUNCTION SWITCHING STATION - FARMERS CONSUMER CO-OP 115KV CKT 1 | 0 | 533234 | BISMARK3 115.00 | 533236 | COOP 3 115.00 | 0 |  | 1 |  |  | WERE | LAWRENCE HILL - MOCKINGBIRD HILL SWITCHING STATION 115KV CKT 1 | Rebuild 5.49 miles | [5 empty] | 18 | 18 | [30 empty] | 2009-06-01 | 2012-06-01 | 2011-10-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2007AG2AFS81T16285513SP | FROM->TO | LAWRENCE HILL - MOCKINGBIRD HILL SWITCHING STATION 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533250 | LWRNCHL3 115.00 | 533253 | MOCKBRD3 115.00 | 0 |  | 1 | 13SP | 92 | 92 | 102.8 | 103.2 | 101.7013 | 103.3733 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-58 | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WERE | LAWRENCE HILL - MOCKINGBIRD HILL SWITCHING STATION 115KV CKT 1 | Rebuild 5.49 miles | [5 empty] | 18 | 18 | [30 empty] | 2009-06-01 | 2012-06-01 | 2011-10-01
2007-AG2 | AFS9 | CONT-1210 - Bismark - COOP 115kV | FDNS |  | FDNS |  | 4 | 3 | 2007AG2AFS81T5274318SP | FROM->TO | LAWRENCE HILL - MOCKINGBIRD HILL SWITCHING STATION 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533250 | LWRNCHL3 115.00 | 533253 | MOCKBRD3 115.00 | 0 |  | 1 | 18SP | 92 | 92 | 107.0 | 107.3 | 107.3123 | 107.4754 | [7 empty] | CATEGORYB | SINGLE | BISMARK JUNCTION SWITCHING STATION - FARMERS CONSUMER CO-OP 115KV CKT 1 | 0 | 533234 | BISMARK3 115.00 | 533236 | COOP 3 115.00 | 0 |  | 1 |  |  | WERE | LAWRENCE HILL - MOCKINGBIRD HILL SWITCHING STATION 115KV CKT 1 | Rebuild 5.49 miles | [5 empty] | 18 | 18 | [30 empty] | 2009-06-01 | 2012-06-01 | 2011-10-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 4 | 3 | 2007AG2AFS81T30204318SP | FROM->TO | LAWRENCE HILL - MOCKINGBIRD HILL SWITCHING STATION 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533250 | LWRNCHL3 115.00 | 533253 | MOCKBRD3 115.00 | 0 |  | 1 | 18SP | 92 | 92 | 106.2 | 106.6 | 106.5426 | 106.7033 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-58 | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WERE | LAWRENCE HILL - MOCKINGBIRD HILL SWITCHING STATION 115KV CKT 1 | Rebuild 5.49 miles | [5 empty] | 18 | 18 | [30 empty] | 2009-06-01 | 2012-06-01 | 2011-10-01
GEN-2001-024 | Mattison | [7 empty] | 506957506938012SP | TO->FROM | LOWELL 5 - TONTITOWN 161KV CKT 1 | U | AEPW | AEPW | FAYETTEV | FAYETTEV | 0 | 506957 | TONTITN5 161.00 | 506938 | LOWELL 5 161.00 | 0 |  | 1 |  | 373 | 443 |  |  | 167.5 | [9 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | AEPW | LOWELL 5 - TONTITOWN 161KV CKT 1 | Add one 161KV terminal for Tontitown | [12 empty] | 537700 | [24 empty] | 2008-06-01 | 2008-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T862210SP | TO->FROM | LYDIA - WELSH 345KV CKT 1 | S | AEPW | AEPW | MTPL | MTPL | 0 | 508359 | WELSH 7 345.00 | 508298 | LYDIA 7 345.00 | 0 |  | 1 | 10SP | 905 | 1059 |  | 102.4 | 102.3651 | 102.6278 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST TEXARKANA - WELSH 345KV CKT 1 | 0 | 508072 | NWTXARK7 345.00 | 508359 | WELSH 7 345.00 | 0 |  | 1 |  |  | AEPW | LYDIA - WELSH 345KV CKT 1 | Interim Redispatch from 6/1/10-10/1/2010 and 6/1/2011-10/1/2011 | [37 empty] | 2010-06-01 | 2011-10-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T16282210SP | TO->FROM | LYDIA - WELSH 345KV CKT 1 | S | AEPW | AEPW | MTPL | MTPL | 0 | 508359 | WELSH 7 345.00 | 508298 | LYDIA 7 345.00 | 0 |  | 1 | 10SP | 905 | 1059 |  | 100.3 | 100.3354 | 100.6708 | [7 empty] | CATEGORYB | NONSINGLE | SPP-AEPW-04 | 0 | 0 |  | 0 |  | 0 |  |  |  |  | AEPW | LYDIA - WELSH 345KV CKT 1 | Interim Redispatch from 6/1/10-10/1/2010 and 6/1/2011-10/1/2011 | [37 empty] | 2010-06-01 | 2011-10-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2007AG2AFS81T5765518SP | TO->FROM | LYONS - WHEATLAND 115KV CKT 1 | REL | WERE | MIDW | WEST | REG E-IL | 0 | 533439 | WHEATLD3 115.00 | 530620 | LYONS 3 115.00 | 0 |  | 1 | 18SP | 70 | 70 |  | 101.3 | 87.438 | 101.1807 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICE_CO 115KV CKT 1 | 0 | 530623 | RICE 3 115.00 | 533413 | CIRCLE 3 115.00 | 0 |  | 1 |  |  | MIDW | LYONS - WHEATLAND 115KV CKT 1 MIDW | Rebuild 98.5% ownership of 19.4 miles | 223 | 240 | 223 | 240 | 19.109 | [6 empty] | 562.5k per mile | 10748812 | 2008-01-01 | [23 empty] | 2018-06-01 | 2018-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2007AG2AFS81T5765518SP | TO->FROM | LYONS - WHEATLAND 115KV CKT 1 | REL | WERE | MIDW | WEST | REG E-IL | 0 | 533439 | WHEATLD3 115.00 | 530620 | LYONS 3 115.00 | 0 |  | 1 | 18SP | 70 | 70 |  | 101.3 | 87.438 | 101.1807 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICE_CO 115KV CKT 1 | 0 | 530623 | RICE 3 115.00 | 533413 | CIRCLE 3 115.00 | 0 |  | 1 |  |  | WERE | LYONS - WHEATLAND 115KV CKT 1 WERE | Rebuild 1.5% ownership of 19.4 miles | [11 empty] | 562.5k per mile | 163688 | 2008-01-01 | [23 empty] | 2018-06-01 | 2018-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T1012213SP | TO->FROM | MALDEN - NEW MADRID 69KV CKT 1 | REL | SWPA | SWPA | EMINTH | EMINTH | 0 | 505402 | N MADRD2 69.000 | 505404 | MALDEN 2 69.000 | 0 |  | 1 | 13SP | 59 | 59 | 100.9 | 100.8 | 100.7978 | 118.7362 | [7 empty] | CATEGORYB | SINGLE | KENNETT - NEW MADRID 161KV CKT 1 | 0 | 505400 | N MADRD5 161.00 | 505410 | KENNETT5 161.00 | 0 |  | 1 |  |  | SWPA | MALDEN - NEW MADRID 69KV CKT 1 | Reconductor line, replace disconnect switches | 143 | 143 | 143 | 143 | 22.6 | 24 | 12 | [5 empty] | 2000000 | 2008-08-11 | [23 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 2 | 2007AG2AFS81T2333218SP | TO->FROM | MALDEN - NEW MADRID 69KV CKT 1 | REL | SWPA | SWPA | EMINTH | EMINTH | 0 | 505402 | N MADRD2 69.000 | 505404 | MALDEN 2 69.000 | 0 |  | 1 | 18SP | 59 | 59 | 106.9 | 108.9 | 108.8968 | 127.6719 | [7 empty] | CATEGORYB | SINGLE | KENNETT - NEW MADRID 161KV CKT 1 | 0 | 505400 | N MADRD5 161.00 | 505410 | KENNETT5 161.00 | 0 |  | 1 |  |  | SWPA | MALDEN - NEW MADRID 69KV CKT 1 | Reconductor line, replace disconnect switches | 143 | 143 | 143 | 143 | 22.6 | 24 | 12 | [5 empty] | 2000000 | 2008-08-11 | [23 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 3 | 2 | 2007AG2AFS81T2343218SP | FROM->TO | MALDEN - PIGGOTT 69KV CKT 1 | S | SWPA | SWPA | EMINTH | EMINTH | 0 | 505404 | MALDEN 2 69.000 | 505406 | PIGGOTT2 69.000 | 0 |  | 1 | 18SP | 59 | 59 |  |  | 99.9766 | 107.3165 | [7 empty] | CATEGORYB | SINGLE | KENNETT - NEW MADRID 161KV CKT 1 | 0 | 505400 | N MADRD5 161.00 | 505410 | KENNETT5 161.00 | 0 |  | 1 |  |  | SWPA | MALDEN - PIGGOTT 69KV CKT 1 | Reconductor line, replace disconnect switches | 143 | 143 | 143 | 143 | 21 | 24 | 12 | [5 empty] | 2000000 | 2008-08-11 | [23 empty] | 2016-06-01 | 2014-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 1 | 3 | 2007AG2AFS81T2581309SP | TO->FROM | MARTIN CITY - REDEL 161KV CKT 1 | EXP | KACP | KACP | JOCO | METRO | 0 | 543053 | REDEL 5 161.00 | 543002 | MARTCIT5 161.00 | 0 |  | 1 | 09SP | 293 | 335 |  | 102.8 | 100.9367 | 102.3486 | [7 empty] | CATEGORYB | SINGLE | PECULIAR - STILWELL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  | MIPU | South Harper 161 kV cut-in to Stilwell-Archie JCT 161 kV line | To tap Stilwell-Archie JCT 161 kV line into South Harper 161 kV sub and make it two new 161 kV sections: Stilwell-South Harper and Archie JCT- South Harper . | 293 | 335 |  |  |  | 30 | 30 | [5 empty] | 2259673 | 2009-02-06 | [23 empty] | 2009-06-01 | 2010-11-01 | 2010-10-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 3 | 2007AG2AFS81T2292310SP | TO->FROM | MARTIN CITY - REDEL 161KV CKT 1 | EXP | KACP | KACP | JOCO | METRO | 0 | 543053 | REDEL 5 161.00 | 543002 | MARTCIT5 161.00 | 0 |  | 1 | 10SP | 293 | 335 |  | 105.7 | 105.4304 | 105.5545 | [7 empty] | CATEGORYB | SINGLE | PECULIAR - STILWELL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  | MIPU | South Harper 161 kV cut-in to Stilwell-Archie JCT 161 kV line | To tap Stilwell-Archie JCT 161 kV line into South Harper 161 kV sub and make it two new 161 kV sections: Stilwell-South Harper and Archie JCT- South Harper . | 293 | 335 |  |  |  | 30 | 30 | [5 empty] | 2259673 | 2009-02-06 | [23 empty] | 2009-06-01 | 2010-11-01 | 2010-10-01
GEN-2006-010 | Turk | [7 empty] | 504122507456012SP | FROM->TO | MCNAB REC - TURK 115KV CKT 1 | U | AEPW | AEPW | SARK | SARKAECC | 0 | 504122 | MCNAB 3 115.00 | 507456 | HEMPSTD3 115.00 | 0 |  | 1 |  | 150 | 174 |  |  | 47.9 | [9 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | AEPW | MCNAB REC - TURK 115KV CKT 1 | Build a new two mile, 138 kV, 1590 ACSR line section (operated at 115 kV) from Turk Substation to the existing Okay- Hope 115 kV line to form a Turk - Hope 115 kV line. | [12 empty] | 1520000 | [24 empty] | 2012-07-01 | 2012-07-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 2 | 1 | 2007AG2AFS81T252109FAG | FROM->TO | MEDICINE LODGE (MED-LDG4) 138/115/2.72KV TRANSFORMER CKT 1 | S | MKEC |  |  |  | 1 | 539674 | MED-LDG4 138.00 | 539673 | MED-LDG3 115.00 | 539917 | MEDLGT-T 2.7200 | 1 | 09FA | 56 | 56 |  |  | 111.7165 | 119.2392 | [7 empty] | CATEGORYB | GENOUT | GEN531447 1-HOLCOMB GENERATOR | 0 | 0 |  | 0 |  | 0 |  |  |  |  | MKEC | MEDICINE LODGE (MED-LDG4) 138/115/2.72KV TRANSFORMER CKT 1 | Interim Redispatch | [37 empty] | 2009-06-01 | 2009-12-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 2 | 1 | 2007AG2AFS81T292109FAG | FROM->TO | MEDICINE LODGE (MED-LDG4) 138/115/2.72KV TRANSFORMER CKT 1 | S | MKEC |  |  |  | 1 | 539674 | MED-LDG4 138.00 | 539673 | MED-LDG3 115.00 | 539917 | MEDLGT-T 2.7200 | 1 | 09FA | 56 | 56 |  |  | 99.6401 | 107.3542 | [7 empty] | CATEGORYB | GENOUT | GEN539670 4-JUDSON LARGE GENERATOR | 0 | 0 |  | 0 |  | 0 |  |  |  |  | MKEC | MEDICINE LODGE (MED-LDG4) 138/115/2.72KV TRANSFORMER CKT 1 | Interim Redispatch | [37 empty] | 2009-06-01 | 2009-12-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 2 | 1 | 2007AG2AFS81T312109FAG | FROM->TO | MEDICINE LODGE (MED-LDG4) 138/115/2.72KV TRANSFORMER CKT 1 | S | MKEC |  |  |  | 1 | 539674 | MED-LDG4 138.00 | 539673 | MED-LDG3 115.00 | 539917 | MEDLGT-T 2.7200 | 1 | 09FA | 56 | 56 |  |  | 99.2111 | 106.9832 | [7 empty] | CATEGORYB | GENOUT | GEN539767 1-GRAY COUNTY WIND FARM | 0 | 0 |  | 0 |  | 0 |  |  |  |  | MKEC | MEDICINE LODGE (MED-LDG4) 138/115/2.72KV TRANSFORMER CKT 1 | Interim Redispatch | [37 empty] | 2009-06-01 | 2009-12-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 2 | 1 | 2007AG2AFS81T582109SHG | FROM->TO | MEDICINE LODGE (MED-LDG4) 138/115/2.72KV TRANSFORMER CKT 1 | S | MKEC |  |  |  | 1 | 539674 | MED-LDG4 138.00 | 539673 | MED-LDG3 115.00 | 539917 | MEDLGT-T 2.7200 | 1 | 09SH | 56 | 56 |  |  | 130.1219 | 135.227 | [7 empty] | CATEGORYB | GENOUT | GEN531447 1-HOLCOMB GENERATOR | 0 | 0 |  | 0 |  | 0 |  |  |  |  | MKEC | MEDICINE LODGE (MED-LDG4) 138/115/2.72KV TRANSFORMER CKT 1 | Interim Redispatch | [37 empty] | 2009-06-01 | 2009-12-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 2 | 1 | 2007AG2AFS81T692109SHG | FROM->TO | MEDICINE LODGE (MED-LDG4) 138/115/2.72KV TRANSFORMER CKT 1 | S | MKEC |  |  |  | 1 | 539674 | MED-LDG4 138.00 | 539673 | MED-LDG3 115.00 | 539917 | MEDLGT-T 2.7200 | 1 | 09SH | 56 | 56 |  |  | 129.3328 | 134.4341 | [7 empty] | CATEGORYB | GENOUT | GEN539670 4-JUDSON LARGE GENERATOR | 0 | 0 |  | 0 |  | 0 |  |  |  |  | MKEC | MEDICINE LODGE (MED-LDG4) 138/115/2.72KV TRANSFORMER CKT 1 | Interim Redispatch | [37 empty] | 2009-06-01 | 2009-12-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 2 | 1 | 2007AG2AFS81T712109SHG | FROM->TO | MEDICINE LODGE (MED-LDG4) 138/115/2.72KV TRANSFORMER CKT 1 | S | MKEC |  |  |  | 1 | 539674 | MED-LDG4 138.00 | 539673 | MED-LDG3 115.00 | 539917 | MEDLGT-T 2.7200 | 1 | 09SH | 56 | 56 |  |  | 118.1667 | 122.9196 | [7 empty] | CATEGORYB | GENOUT | GEN539767 1-GRAY COUNTY WIND FARM | 0 | 0 |  | 0 |  | 0 |  |  |  |  | MKEC | MEDICINE LODGE (MED-LDG4) 138/115/2.72KV TRANSFORMER CKT 1 | Interim Redispatch | [37 empty] | 2009-06-01 | 2009-12-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 3 | 1 | 2007AG2AFS81T523109SPG | FROM->TO | MEDICINE LODGE (MED-LDG4) 138/115/2.72KV TRANSFORMER CKT 1 | S | MKEC |  |  |  | 1 | 539674 | MED-LDG4 138.00 | 539673 | MED-LDG3 115.00 | 539917 | MEDLGT-T 2.7200 | 1 | 09SP | 56 | 56 |  |  | 131.1216 | 135.1877 | [7 empty] | CATEGORYB | GENOUT | GEN531447 1-HOLCOMB GENERATOR | 0 | 0 |  | 0 |  | 0 |  |  |  |  | MKEC | MEDICINE LODGE (MED-LDG4) 138/115/2.72KV TRANSFORMER CKT 1 | Interim Redispatch | [37 empty] | 2009-06-01 | 2009-12-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 3 | 1 | 2007AG2AFS81T623109SPG | FROM->TO | MEDICINE LODGE (MED-LDG4) 138/115/2.72KV TRANSFORMER CKT 1 | S | MKEC |  |  |  | 1 | 539674 | MED-LDG4 138.00 | 539673 | MED-LDG3 115.00 | 539917 | MEDLGT-T 2.7200 | 1 | 09SP | 56 | 56 |  |  | 130.6969 | 130.6771 | [7 empty] | CATEGORYB | GENOUT | GEN539670 4-JUDSON LARGE GENERATOR | 0 | 0 |  | 0 |  | 0 |  |  |  |  | MKEC | MEDICINE LODGE (MED-LDG4) 138/115/2.72KV TRANSFORMER CKT 1 | Interim Redispatch | [37 empty] | 2009-06-01 | 2009-12-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 3 | 1 | 2007AG2AFS81T663109SPG | FROM->TO | MEDICINE LODGE (MED-LDG4) 138/115/2.72KV TRANSFORMER CKT 1 | S | MKEC |  |  |  | 1 | 539674 | MED-LDG4 138.00 | 539673 | MED-LDG3 115.00 | 539917 | MEDLGT-T 2.7200 | 1 | 09SP | 56 | 56 |  |  | 119.1065 | 123.3611 | [7 empty] | CATEGORYB | GENOUT | GEN539767 1-GRAY COUNTY WIND FARM | 0 | 0 |  | 0 |  | 0 |  |  |  |  | MKEC | MEDICINE LODGE (MED-LDG4) 138/115/2.72KV TRANSFORMER CKT 1 | Interim Redispatch | [37 empty] | 2009-06-01 | 2009-12-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81T172409APG | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09AP | 96 | 96 | 100.4 | 100 | 110.8219 | 111.2575 | [7 empty] | CATEGORYB | GENOUT | GEN525562 1-TOLK GEN #2 24 KV | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 2 | 4 | 2007AG2AFS81T152409APG | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09AP | 96 | 96 |  |  | 109.0847 | 109.4923 | [7 empty] | CATEGORYB | GENOUT | GEN525561 1-TOLK GEN #1 24 KV | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 3 | 4 | 2007AG2AFS81T1883409AP | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09AP | 96 | 96 |  |  | 108.2694 | 108.9515 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05A | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 2 | 4 | 2007AG2AFS81T1832409AP | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09AP | 96 | 96 |  |  | 107.3862 | 107.5119 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-04 | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 2 | 4 | 2007AG2AFS81T142409APG | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09AP | 96 | 96 |  |  | 100.7936 | 101.1798 | [7 empty] | CATEGORYB | GENOUT | GEN523972 1-HARRINGTON GEN #2 24 KV | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 4 | 4 | 2007AG2AFS81T394409FAG | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09FA | 96 | 96 | 108.7 | 108.1 | 106.6351 | 110.1114 | [7 empty] | CATEGORYB | GENOUT | GEN525562 1-TOLK GEN #2 24 KV | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 4 | 4 | 2007AG2AFS81T4114409FA | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09FA | 96 | 96 | 105.6 | 105.7 | 104.3776 | 107.2457 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05A | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 4 | 4 | 2007AG2AFS81T374409FAG | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09FA | 96 | 96 | 105.1 | 104.6 | 103.2999 | 106.7531 | [7 empty] | CATEGORYB | GENOUT | GEN525561 1-TOLK GEN #1 24 KV | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 4 | 4 | 2007AG2AFS81T4094409FA | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09FA | 96 | 96 | 104.3 | 104.4 | 103.0727 | 105.9355 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-04 | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 4 | 4 | 2007AG2AFS81T354409FAG | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09FA | 96 | 96 | 100.7 | 100.1 | 98.6587 | 102.1314 | [7 empty] | CATEGORYB | GENOUT | GEN523973 1-HARRINGTON GEN #3 24 KV | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 1 | 4 | 2007AG2AFS81T731409GG | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09G | 96 | 96 | 151.9 | 152.4 | 164.1223 | 163.3621 | [7 empty] | CATEGORYB | GENOUT | GEN525562 1-TOLK GEN #2 24 KV | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 1 | 4 | 2007AG2AFS81T5961409G | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09G | 96 | 96 | 147.6 | 149.1 | 162.4649 | 161.5177 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05A | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 1 | 4 | 2007AG2AFS81T681409GG | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09G | 96 | 96 | 148.9 | 149.6 | 161.3793 | 160.6249 | [7 empty] | CATEGORYB | GENOUT | GEN525561 1-TOLK GEN #1 24 KV | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 1 | 4 | 2007AG2AFS81T5951409G | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09G | 96 | 96 | 146.3 | 147.8 | 161.1099 | 160.1611 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-04 | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 1 | 4 | 2007AG2AFS81T621409GG | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09G | 96 | 96 | 143.5 | 144.2 | 155.5709 | 154.9149 | [7 empty] | CATEGORYB | GENOUT | GEN523972 1-HARRINGTON GEN #2 24 KV | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 1 | 4 | 2007AG2AFS81T851409G | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09G | 96 | 96 | 142.0 | 143.1 | 153.3115 | 153.8467 | [7 empty] | CATEGORYB | SINGLE | DEWEY - SOUTHARD 138KV CKT 1 | 0 | 514787 | DEWEY 4 138.00 | 514822 | SOUTHRD4 138.00 | 0 |  | 1 |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 1 | 4 | 2007AG2AFS81T31409G | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09G | 96 | 96 | 120.5 | 121.2 | 131.9485 | 131.3224 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 | CONT-0802 - Wichita - OG&E (Woodring) 345kV | FDNS |  | FDNS |  | 1 | 4 | 2007AG2AFS81T761409G | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09G | 96 | 96 | 116.9 | 116.2 | 126.6954 | 126.1227 | [7 empty] | CATEGORYB | SINGLE | WICHITA - WOODRING 345KV CKT 1 | 0 | 514715 | WOODRNG7 345.00 | 532796 | WICHITA7 345.00 | 0 |  | 1 |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81T622409SHG | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09SH | 96 | 96 | 141.6 | 141.1 | 147.817 | 148.2414 | [7 empty] | CATEGORYB | GENOUT | GEN525562 1-TOLK GEN #2 24 KV | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81T592409SHG | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09SH | 96 | 96 | 138.3 | 137.8 | 144.8453 | 145.2455 | [7 empty] | CATEGORYB | GENOUT | GEN525561 1-TOLK GEN #1 24 KV | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81T6492409SH | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09SH | 96 | 96 | 134.7 | 134.6 | 142.8289 | 142.9773 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05A | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81T6482409SH | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09SH | 96 | 96 | 133.3 | 133.2 | 141.7477 | 141.8929 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-04 | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81T542409SHG | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09SH | 96 | 96 | 132.4 | 131.7 | 138.2633 | 138.6752 | [7 empty] | CATEGORYB | GENOUT | GEN523972 1-HARRINGTON GEN #2 24 KV | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 1 | 4 | 2007AG2AFS81T811409SH | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09SH | 96 | 96 | 128.9 | 128.2 | 134.1126 | 134.7403 | [7 empty] | CATEGORYB | SINGLE | DEWEY - SOUTHARD 138KV CKT 1 | 0 | 514787 | DEWEY 4 138.00 | 514822 | SOUTHRD4 138.00 | 0 |  | 1 |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81T22409SH | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09SH | 96 | 96 | 110.2 | 109.3 | 115.2655 | 115.6965 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 | CONT-0802 - Wichita - OG&E (Woodring) 345kV | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81T822409SH | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09SH | 96 | 96 | 107.4 | 105.8 | 111.2038 | 111.5677 | [7 empty] | CATEGORYB | SINGLE | WICHITA - WOODRING 345KV CKT 1 | 0 | 514715 | WOODRNG7 345.00 | 532796 | WICHITA7 345.00 | 0 |  | 1 |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 4 | 2007AG2AFS81T543409SPG | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09SP | 96 | 96 | 160.1 | 159.3 | 169.223 | 169.9346 | [7 empty] | CATEGORYB | GENOUT | GEN525562 1-TOLK GEN #2 24 KV | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 4 | 2007AG2AFS81T9763409SP | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09SP | 96 | 96 | 154.9 | 155 | 165.9704 | 166.6578 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05A | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 4 | 2007AG2AFS81T533409SPG | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09SP | 96 | 96 | 156.8 | 156.1 | 166.0283 | 166.0833 | [7 empty] | CATEGORYB | GENOUT | GEN525561 1-TOLK GEN #1 24 KV | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 4 | 2007AG2AFS81T9743409SP | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09SP | 96 | 96 | 153.6 | 153.7 | 164.6754 | 165.3332 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-04 | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 4 | 2007AG2AFS81T473409SPG | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09SP | 96 | 96 | 152.3 | 151.7 | 161.2493 | 161.8737 | [7 empty] | CATEGORYB | GENOUT | GEN523972 1-HARRINGTON GEN #2 24 KV | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 4 | 2007AG2AFS81T1063409SP | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09SP | 96 | 96 | 150.0 | 149.5 | 158.3516 | 158.9461 | [7 empty] | CATEGORYB | SINGLE | DEWEY - SOUTHARD 138KV CKT 1 | 0 | 514787 | DEWEY 4 138.00 | 514822 | SOUTHRD4 138.00 | 0 |  | 1 |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 4 | 2007AG2AFS81T13409SP | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09SP | 96 | 96 | 129.7 | 129.1 | 137.9971 | 138.6093 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 | CONT-0802 - Wichita - OG&E (Woodring) 345kV | FDNS |  | FDNS |  | 3 | 4 | 2007AG2AFS81T1003409SP | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09SP | 96 | 96 | 126.7 | 125.6 | 134.5953 | 135.1888 | [7 empty] | CATEGORYB | SINGLE | WICHITA - WOODRING 345KV CKT 1 | 0 | 514715 | WOODRNG7 345.00 | 532796 | WICHITA7 345.00 | 0 |  | 1 |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81T722409WPG | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09WP | 96 | 96 | 159.7 | 134 | 133.7268 | 134.2948 | [7 empty] | CATEGORYB | GENOUT | GEN525562 1-TOLK GEN #2 24 KV | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 4 | 4 | 2007AG2AFS81T834409WP | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09WP | 96 | 96 |  | 130.7 | 128.5583 | 132.0761 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - WOODWRD7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515375 | WOODWRD7 345.00 | 0 |  | 1 |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 4 | 4 | 2007AG2AFS81T3584409WP | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09WP | 96 | 96 |  | 130.7 | 128.4882 | 132.0038 | [7 empty] | CATEGORYB | SINGLE | WOODWRD7 345.00 (WWDEHV-T) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WOODWRD7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WOODWR31 13.800 | 1 |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81T682409WPG | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09WP | 96 | 96 | 157.4 | 131.5 | 131.31 | 131.874 | [7 empty] | CATEGORYB | GENOUT | GEN525561 1-TOLK GEN #1 24 KV | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81T5952409WP | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09WP | 96 | 96 | 156.0 | 130.4 | 130.324 | 130.5313 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05A | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81T652409WPG | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09WP | 96 | 96 | 150.6 | 123.9 | 123.6401 | 124.147 | [7 empty] | CATEGORYB | GENOUT | GEN523972 1-HARRINGTON GEN #2 24 KV | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81T10762410SP | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 10SP | 96 | 96 | 166.5 | 145.8 | 145.5715 | 146.6312 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05B | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81T1542410SP | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 10SP | 96 | 96 | 165.1 | 144.1 | 143.8607 | 144.9143 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7 345.00 | 523853 | FINNEY7 345.00 | 0 |  | 1 |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81T412410SPG | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 10SP | 96 | 96 | 164.1 | 141.7 | 141.124 | 142.555 | [7 empty] | CATEGORYB | GENOUT | GEN525562 1-TOLK GEN #2 24 KV | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81T402410SPG | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 10SP | 96 | 96 | 160.1 | 137.4 | 137.0116 | 138.5334 | [7 empty] | CATEGORYB | GENOUT | GEN525561 1-TOLK GEN #1 24 KV | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81T1342410SP | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 10SP | 96 | 96 |  | 134.2 | 133.7109 | 135.4911 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - WOODWRD7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515375 | WOODWRD7 345.00 | 0 |  | 1 |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81T332410SPG | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 10SP | 96 | 96 | 156.0 | 132.6 | 132.0638 | 133.4939 | [7 empty] | CATEGORYB | GENOUT | GEN523972 1-HARRINGTON GEN #2 24 KV | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81T32410SP | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 10SP | 96 | 96 | 134.9 | 108.7 | 108.0993 | 109.5157 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 | CONT-0802 - Wichita - OG&E (Woodring) 345kV | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81T1182410SP | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 10SP | 96 | 96 | 131.1 | 104 | 103.5109 | 104.8683 | [7 empty] | CATEGORYB | SINGLE | WICHITA - WOODRING 345KV CKT 1 | 0 | 514715 | WOODRNG7 345.00 | 532796 | WICHITA7 345.00 | 0 |  | 1 |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81T5702410WP | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 10WP | 96 | 96 | 163.1 | 138.5 | 138.2622 | 138.5518 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05B | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81T792410WP | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 10WP | 96 | 96 | 161.7 | 136.9 | 136.586 | 136.883 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7 345.00 | 523853 | FINNEY7 345.00 | 0 |  | 1 |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 4 | 4 | 2007AG2AFS81T704410WP | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 10WP | 96 | 96 |  | 129.2 | 128.5751 | 132.199 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - WOODWRD7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515375 | WOODWRD7 345.00 | 0 |  | 1 |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81T562410WPG | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 10WP | 96 | 96 | 156.2 | 130.2 | 129.5472 | 130.3356 | [7 empty] | CATEGORYB | GENOUT | GEN525562 1-TOLK GEN #2 24 KV | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81T532410WPG | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 10WP | 96 | 96 | 153.2 | 126.8 | 126.3644 | 127.1077 | [7 empty] | CATEGORYB | GENOUT | GEN525561 1-TOLK GEN #1 24 KV | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81T522410WPG | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 10WP | 96 | 96 | 148.6 | 121.7 | 121.0224 | 121.8052 | [7 empty] | CATEGORYB | GENOUT | GEN523973 1-HARRINGTON GEN #3 24 KV | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 4 | 2007AG2AFS81T16903413SP | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 13SP | 96 | 96 | 150.5 | 135 | 136.1297 | 136.0383 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05B | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 4 | 2007AG2AFS81T2323413SP | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 13SP | 96 | 96 | 149.1 | 133.4 | 134.5648 | 134.479 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7 345.00 | 523853 | FINNEY7 345.00 | 0 |  | 1 |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81T2012413SPG | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 13SP | 96 | 96 | 147.0 | 130.8 | 130.0721 | 130.9142 | [7 empty] | CATEGORYB | GENOUT | GEN525562 1-TOLK GEN #2 24 KV | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81T1992413SPG | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 13SP | 96 | 96 | 142.9 | 126.5 | 125.9604 | 127.0514 | [7 empty] | CATEGORYB | GENOUT | GEN525561 1-TOLK GEN #1 24 KV | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81T1862413SPG | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 13SP | 96 | 96 | 138.5 | 121.9 | 121.171 | 122.0252 | [7 empty] | CATEGORYB | GENOUT | GEN523972 1-HARRINGTON GEN #2 24 KV | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 4 | 4 | 2007AG2AFS81T2084413SP | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 13SP | 96 | 96 |  | 114.7 | 110.8225 | 115.9375 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - WOODWRD7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515375 | WOODWRD7 345.00 | 0 |  | 1 |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81T5762413WP | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 13WP | 96 | 96 | 124.7 | 108.6 | 108.3108 | 108.6702 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05B | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81T752413WP | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 13WP | 96 | 96 | 123.3 | 107.1 | 106.7317 | 107.1009 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7 345.00 | 523853 | FINNEY7 345.00 | 0 |  | 1 |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81T932413WPG | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 13WP | 96 | 96 | 119.2 | 102.7 | 101.8402 | 102.8285 | [7 empty] | CATEGORYB | GENOUT | GEN525562 1-TOLK GEN #2 24 KV | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81T912413WPG | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 13WP | 96 | 96 | 116.9 | 100.2 | 99.4565 | 100.3804 | [7 empty] | CATEGORYB | GENOUT | GEN525561 1-TOLK GEN #1 24 KV | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2007AG2AFS81T5135518SP | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 18SP | 96 | 96 | 155.9 | 176.1 | 174.0334 | 174.5764 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - HOLCOMB 345KV CKT 1 | 0 | 523853 | FINNEY7 345.00 | 531449 | HOLCOMB7 345.00 | 0 |  | 1 |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81T33672418SP | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 18SP | 96 | 96 | 165.4 | 161.5 | 161.8401 | 162.0838 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05B | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81T4952418SP | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 18SP | 96 | 96 | 163.8 | 159.8 | 160.0823 | 160.3478 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7 345.00 | 523853 | FINNEY7 345.00 | 0 |  | 1 |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81T5092418SPG | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 18SP | 96 | 96 | 162.3 | 157.6 | 157.2322 | 158.1277 | [7 empty] | CATEGORYB | GENOUT | GEN525562 1-TOLK GEN #2 24 KV | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81T5022418SPG | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 18SP | 96 | 96 | 158.3 | 153.2 | 152.7947 | 153.5322 | [7 empty] | CATEGORYB | GENOUT | GEN525561 1-TOLK GEN #1 24 KV | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81T4792418SPG | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 18SP | 96 | 96 | 152.0 | 146.1 | 145.6745 | 146.439 | [7 empty] | CATEGORYB | GENOUT | GEN523972 1-HARRINGTON GEN #2 24 KV | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81T52418SP | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | EXP | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 18SP | 96 | 96 | 130.2 | 121.9 | 121.4916 | 122.2154 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | MOORELAND - MOREWOOD SW 138KV CKT 1 |  | 144 | 179 | 188 | 214 | [33 empty] | 2009-04-01 | 2010-06-01
GEN-2004-014 | Spearville2 | [7 empty] | 539695539679012SP | TO->FROM | MULLERGREN - SPEARVILLE 230KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539695 | SPEARVL6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 |  | 330.3 | 355.3 |  |  | 116.6 | [9 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | MKEC | MULLERGREN - SPEARVILLE 230KV CKT 1 | 230kv line terminal at Spearville | [12 empty] | 650000 | [24 empty] | 2009-12-31 | 2009-12-31
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T963310SP | FROM->TO | NEOSHO - NORTHEAST PARSONS 138KV CKT 1 | CP | WERE | WERE | SEAST | SEAST | 0 | 533021 | NEOSHO 4 138.00 | 533005 | NEPARSN4 138.00 | 0 |  | 1 | 10SP | 159 | 159 |  | 103.6 | 102.5271 | 102.803 | [7 empty] | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  | WERE | NEOSHO - NORTHEAST PARSONS 138KV CKT 1 | Replace bus and Jumpers at NE Parsons 138 kV substation | 203 | 203 | 203 | 203 |  | 6 | 1 |  |  |  |  | 203 MVA is CT limit | 250000 | 2006-03-21 | [23 empty] | 2010-06-01 | 2011-06-01 | 2010-10-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T1553313SP | FROM->TO | NEOSHO - NORTHEAST PARSONS 138KV CKT 1 | CP | WERE | WERE | SEAST | SEAST | 0 | 533021 | NEOSHO 4 138.00 | 533005 | NEPARSN4 138.00 | 0 |  | 1 | 13SP | 159 | 159 |  | 102.2 | 101.0973 | 100.49 | [7 empty] | CATEGORYB | SINGLE | COFFEYVILLE TAP - DEARING 138KV CKT 1 | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 |  |  | WERE | NEOSHO - NORTHEAST PARSONS 138KV CKT 1 | Replace bus and Jumpers at NE Parsons 138 kV substation | 203 | 203 | 203 | 203 |  | 6 | 1 |  |  |  |  | 203 MVA is CT limit | 250000 | 2006-03-21 | [23 empty] | 2010-06-01 | 2011-06-01 | 2010-10-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 3 | 2 | 2007AG2AFS81T2463218SP | FROM->TO | NEW MADRID - NEW MADRID 161KV CKT 1 | S | AECI | SWPA | AECI | EMINTH | 0 | 300103 | 5NEWMAD 161.00 | 505400 | N MADRD5 161.00 | 0 |  | 1 | 18SP | 261 | 261 |  |  | 95.3719 | 102.4671 | [7 empty] | CATEGORYB | SINGLE | NEW MADRID - SIKESTON 161KV CKT 1 | 0 | 505400 | N MADRD5 161.00 | 505428 | SIKESTN5 161.00 | 0 |  | 1 |  |  | AECI | NEW MADRID - NEW MADRID 161KV CKT 1 | 5.4 mile line designed for 75-C. If this can be uprated to 100-C | [12 empty] | 600000 | [24 empty] | 2017-06-01 | 2017-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 3 | 2 | 2007AG2AFS81T40573218SP | FROM->TO | NEW MADRID - NEW MADRID 161KV CKT 1 | S | AECI | SWPA | AECI | EMINTH | 0 | 300103 | 5NEWMAD 161.00 | 505400 | N MADRD5 161.00 | 0 |  | 1 | 18SP | 261 | 261 |  |  | 95.0146 | 101.977 | [7 empty] | CATEGORYB | NONSINGLE | ESEX-IDAL | 0 | 0 |  | 0 |  | 0 |  |  |  |  | AECI | NEW MADRID - NEW MADRID 161KV CKT 1 | 5.4 mile line designed for 75-C. If this can be uprated to 100-C | [12 empty] | 600000 | [24 empty] | 2017-06-01 | 2017-06-01
2007-AG2 | AFS9 | ISLAND-LOAD |  |  | FDNS |  | 3 | 2 | 2007AG2AFS81T27853218SP | FROM->TO | NEW MADRID (NMA X1) 161/69/13.8KV TRANSFORMER CKT 1 | S | SWPA |  | EMINTH |  | 2 | 505400 | N MADRD5 161.00 | 505402 | N MADRD2 69.000 | 505401 | NMA X1 1 13.800 | 1 | 18SP | 67.2 | 67.2 |  |  | 93.2203 | 100.6601 | [7 empty] | CATEGORYB | SINGLE | NEW MADRID (NMA X2) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505400 | N MADRD5 161.00 | 505402 | N MADRD2 69.000 | 505403 | NMA X2 1 13.800 | 1 |  |  | SWPA | NEW MADRID (NMA X1) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer | 100 | 100 | 100 | 100 |  | 18 | 12 |  |  |  |  | AECI Line. SWPA equipment good for 1200 amps (335 MVA). | 1500000 | 1500000 | [23 empty] | 2018-06-01 | 2014-06-01
2007-AG2 | AFS9 | ISLAND-LOAD |  |  | FDNS |  | 3 | 2 | 2007AG2AFS81T27833218SP | FROM->TO | NEW MADRID (NMA X2) 161/69/13.8KV TRANSFORMER CKT 1 | S | SWPA |  | EMINTH |  | 2 | 505400 | N MADRD5 161.00 | 505402 | N MADRD2 69.000 | 505403 | NMA X2 1 13.800 | 1 | 18SP | 67.2 | 67.2 |  |  | 94.1252 | 101.6341 | [7 empty] | CATEGORYB | SINGLE | NEW MADRID (NMA X1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505400 | N MADRD5 161.00 | 505402 | N MADRD2 69.000 | 505401 | NMA X1 1 13.800 | 1 |  |  | SWPA | NEW MADRID (NMA X2) 161/69/13.8KV TRANSFORMER CKT 1 | Replace transformer | 100 | 100 | 100 | 100 |  | 18 | 12 |  |  |  |  | AECI Line. SWPA equipment good for 1200 amps (335 MVA). | 1500000 | 1500000 | [23 empty] | 2017-06-01 | 2014-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 4 | 3 | 2007AG2AFS81T884309FA | TO->FROM | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 09FA | 181 | 181 |  | 100.1 | 100.1201 | 100.8955 | [7 empty] | CATEGORYB | SINGLE | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | 0 | 533368 | EXIDE J3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2009-06-01 | 2009-12-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 4 | 3 | 2007AG2AFS81T1414309SH | TO->FROM | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 09SH | 181 | 181 | 102.1 | 104.2 | 105.5644 | 105.9667 | [7 empty] | CATEGORYB | SINGLE | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | 0 | 533368 | EXIDE J3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2009-06-01 | 2009-12-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 4 | 3 | 2007AG2AFS81T7024309SH | TO->FROM | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 09SH | 181 | 181 |  | 101.2 | 102.5815 | 102.9953 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-73 | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2009-06-01 | 2009-12-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 3 | 2007AG2AFS81T1404309SH | TO->FROM | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 09SH | 181 | 181 |  |  | 101.3681 | 101.7843 | [7 empty] | CATEGORYB | SINGLE | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | 0 | 533368 | EXIDE J3 115.00 | 533372 | PHILIPS3 115.00 | 0 |  | 1 |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2009-06-01 | 2009-12-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 4 | 3 | 2007AG2AFS81T1944309SP | TO->FROM | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 09SP | 181 | 181 | 118.7 | 119.8 | 120.7236 | 121.7542 | [7 empty] | CATEGORYB | SINGLE | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | 0 | 533368 | EXIDE J3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2009-06-01 | 2009-12-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 4 | 3 | 2007AG2AFS81T11034309SP | TO->FROM | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 09SP | 181 | 181 | 115.6 | 116.6 | 117.5164 | 118.5999 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-73 | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2009-06-01 | 2009-12-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 4 | 3 | 2007AG2AFS81T1934309SP | TO->FROM | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 09SP | 181 | 181 | 114.4 | 115.4 | 116.3589 | 117.4027 | [7 empty] | CATEGORYB | SINGLE | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | 0 | 533368 | EXIDE J3 115.00 | 533372 | PHILIPS3 115.00 | 0 |  | 1 |  |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [37 empty] | 2009-06-01 | 2009-12-01
NA | [10 empty] | NORTHWEST - WOODWARD 345KV CKT 1 | U | OKGE | OKGE | ENID | ENID | 0 | 514880 |  | 515375 |  |  |  | 1 |  | 2021 | 2325 | [12 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 kV | [12 empty] | 221000000 | [24 empty] | 2010-01-01 | 2010-01-01
GEN-2006-010 | Turk | [7 empty] | 507454507428012SP | TO->FROM | OKAY - TURK 138KV CKT 1 | U | AEPW | AEPW | SARK | SARK | 0 | 507454 | HEMPSTD4 138.00 | 507428 | OKAY 4 138.00 | 0 |  | 1 |  | 368 | 512 |  |  | 175.2 | [9 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | AEPW | OKAY - TURK 138KV CKT 1 | Build two mile, 138 kV, 1590ACSR line section from Turk Sub to existing Okay-Hope 115 kV line and rebuild twelve miles of 115 kV line to Okay Sub to 138 kV, 1590 ACSR , to form a Turk-Okay 138 kV line | [12 empty] | 9190000 | [24 empty] | 2012-07-01 | 2012-07-01
GEN-2006-010 | Turk | [7 empty] | 50742850742750744212SP | FROM->TO | OKAY 138/69KV TRANSFORMER CKT 1 | U | AEPW | AEPW | SARK | SARK | 1 | 507428 | OKAY 4 138.00 | 507427 | OKAY 2 69.000 | 507442 |  | 1 |  | 150 | 174 |  |  | 57.8 | [9 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | AEPW | OKAY 138/69KV TRANSFORMER CKT 1 | Replace three single-phase 115-69 kV autotransformers with one 90 MVA, three-phase 138-69 kV autotransformer and convert high side of station to 138 kV | [12 empty] | 3400000 | [24 empty] | 2012-07-01 | 2012-07-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 2 | 4 | 2007AG2AFS81V4082410SP |  | OKLAHOMA UNIVERSITY SW 69KV | EXP | WFEC |  | AEP-IM-I |  |  | 521018 | OU SW 2 69.000 | [5 empty] | 10SP | [6 empty] | 0.76536 | 0.76618 | 0.76623 | 0.76601 | 1.0233 | 0.9 | 1.05 | CATEGORYB | SINGLE | OU SW 4 138.00 (OW SW) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 521104 | OU SW 4 138.00 | 521018 | OU SW 2 69.000 | 521183 | OUSWTERT 13.800 | 1 |  |  | WFEC | Norman Area Voltage Conversion | Convert Canadian - OU - Cole - Criner to 138 KV and Canadian-Goldsby-OU-W Norman-Acme-Franklin | [5 empty] | 24 | 18 | [5 empty] | 4000000 | 2007-04-13 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 2 | 2007AG2AFS81V15323218SP |  | OKLAHOMA UNIVERSITY SW 69KV | EXP | WFEC |  | AEP-IM-I |  |  | 521018 | OU SW 2 69.000 | [5 empty] | 18SP | [6 empty] | 0.63081 | 0.63305 | 0.62897 | 0.62897 | 0.98657 | 0.9 | 1.05 | CATEGORYB | SINGLE | OU SW 4 138.00 (OW SW) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 521104 | OU SW 4 138.00 | 521018 | OU SW 2 69.000 | 521183 | OUSWTERT 13.800 | 1 |  |  | WFEC | Norman Area Voltage Conversion | Convert Canadian - OU - Cole - Criner to 138 KV and Canadian-Goldsby-OU-W Norman-Acme-Franklin | [5 empty] | 24 | 18 | [5 empty] | 4000000 | 2007-04-13 | [23 empty] | 2010-06-01 | 2010-06-01
2007-AG2 | AFS9 | [9 empty] | PAWNEE 115/34.5KV TRANSFORMER | S | MIDW |  |  |  |  | 530621 | PAWNEE 3 115.00 | 530622 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [10 empty] | MIDW | Pawnee to City of Larned 115 kV | Build 2 mile 115 kV line from MIDW Pawnee 115 kV to City of Larned | [11 empty] | 250k per mile | 500000 | 2009-01-01 | [23 empty] | 2009-06-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2007AG2AFS81V7555518SP |  | PAWNEE 115KV | REL | MIDW |  | REG E-IL |  |  | 530621 | PAWNEE 3 115.00 | [5 empty] | 18SP | [6 empty] | 0.86261 | 0.89454 | 0.92895 | 0.89709 | 0.94036 | 0.9 | 1.05 | CATEGORYB | SINGLE | SEWARD - ST JOHN 115KV CKT 1 | 0 | 539692 | SEWARD 3 115.00 | 539696 | ST-JOHN3 115.00 | 0 |  | 1 |  |  | MIDW | KINSLEY 115KV Capacitor | Install 10MVAR capacitors at Kinsley 115 kV | [5 empty] | 12 | 12 | [30 empty] | 2011-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2007AG2AFS81V6865518SP |  | PAWNEE 115KV | REL | MIDW |  | REG E-IL |  |  | 530621 | PAWNEE 3 115.00 | [5 empty] | 18SP | [7 empty] | 0.89433 | 0.92222 | 0.89952 | 0.94036 | 0.9 | 1.05 | CATEGORYB | SINGLE | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | 0 | 533045 | GILL W 4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 |  |  | MIDW | KINSLEY 115KV Capacitor | Install 10MVAR capacitors at Kinsley 115 kV | [5 empty] | 12 | 12 | [30 empty] | 2011-06-01 | 2011-06-01
2007-AG2 | AFS9 | CONT-1202 - Jarbalo - Stranger Creek 115kV | FDNS |  | FDNS |  | 4 | 1 | 2007AG2AFS81T744110WP | FROM->TO | PLATTE CITY - SMITHVILLE 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541221 | PLTCTY 5 161.00 | 541204 | SMTHVL 5 161.00 | 0 |  | 1 | 10WP | 223 | 245 | 102 | 102.5 | 101.297 | 102.7136 | [7 empty] | CATEGORYB | SINGLE | IATAN - ST JOE 345KV CKT 1 | 0 | 541199 | ST JOE 3 345.00 | 542982 | IATAN 7 345.00 | 0 |  | 1 |  |  | MIPU | PLATTE CITY - SMITHVILLE 161KV CKT 1 | Replace wavetrap between Platte City and Smithville. | 233 | 265 |  |  |  | 6 | 6 | [5 empty] | 50000 | 2009-02-06 | [23 empty] | 2010-12-01 | 2010-12-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2007AG2AFS81T835509SH | TO->FROM | REDEL - STILWELL 161KV CKT 1 | CP | KACP | KACP | JOCO | JOCO | 0 | 542969 | STILWEL5 161.00 | 543053 | REDEL 5 161.00 | 0 |  | 1 | 09SH | 293 | 335 | 100.1 | 111.4 | 106.6875 | 106.2168 | [7 empty] | CATEGORYB | SINGLE | PECULIAR - STILWELL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  | reconductor with 1192 acss / 584 | KACP | REDEL - STILWELL 161KV CKT 1 | Reconductor line with 1192 ACSS and upgrade terminal equipment for 2000 amps | 558 | 558 |  |  |  | 24 | 4 | [5 empty] | 2200000 | 2008-02-21 | [23 empty] | 2009-06-01 | 2011-06-01 | 2010-10-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2007AG2AFS81T835509SH | TO->FROM | REDEL - STILWELL 161KV CKT 1 | EXP | KACP | KACP | JOCO | JOCO | 0 | 542969 | STILWEL5 161.00 | 543053 | REDEL 5 161.00 | 0 |  | 1 | 09SH | 293 | 335 | 100.1 | 111.4 | 106.6875 | 106.2168 | [7 empty] | CATEGORYB | SINGLE | PECULIAR - STILWELL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  | MIPU | South Harper 161 kV cut-in to Stilwell-Archie JCT 161 kV line | To tap Stilwell-Archie JCT 161 kV line into South Harper 161 kV sub and make it two new 161 kV sections: Stilwell-South Harper and Archie JCT- South Harper . | 293 | 335 |  |  |  | 30 | 30 | [5 empty] | 2259673 | 2009-02-06 | [23 empty] | 2009-06-01 | 2010-11-01 | 2010-10-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 1 | 3 | 2007AG2AFS81T2571309SP | TO->FROM | REDEL - STILWELL 161KV CKT 1 | CP | KACP | KACP | JOCO | JOCO | 0 | 542969 | STILWEL5 161.00 | 543053 | REDEL 5 161.00 | 0 |  | 1 | 09SP | 293 | 335 |  | 112.4 | 110.5301 | 111.9407 | [7 empty] | CATEGORYB | SINGLE | PECULIAR - STILWELL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  | reconductor with 1192 acss / 584 | KACP | REDEL - STILWELL 161KV CKT 1 | Reconductor line with 1192 ACSS and upgrade terminal equipment for 2000 amps | 558 | 558 |  |  |  | 24 | 4 | [5 empty] | 2200000 | 2008-02-21 | [23 empty] | 2009-06-01 | 2011-06-01 | 2010-10-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 1 | 3 | 2007AG2AFS81T2571309SP | TO->FROM | REDEL - STILWELL 161KV CKT 1 | EXP | KACP | KACP | JOCO | JOCO | 0 | 542969 | STILWEL5 161.00 | 543053 | REDEL 5 161.00 | 0 |  | 1 | 09SP | 293 | 335 |  | 112.4 | 110.5301 | 111.9407 | [7 empty] | CATEGORYB | SINGLE | PECULIAR - STILWELL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  | MIPU | South Harper 161 kV cut-in to Stilwell-Archie JCT 161 kV line | To tap Stilwell-Archie JCT 161 kV line into South Harper 161 kV sub and make it two new 161 kV sections: Stilwell-South Harper and Archie JCT- South Harper . | 293 | 335 |  |  |  | 30 | 30 | [5 empty] | 2259673 | 2009-02-06 | [23 empty] | 2009-06-01 | 2010-11-01 | 2010-10-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 3 | 2007AG2AFS81T2282310SP | TO->FROM | REDEL - STILWELL 161KV CKT 1 | CP | KACP | KACP | JOCO | JOCO | 0 | 542969 | STILWEL5 161.00 | 543053 | REDEL 5 161.00 | 0 |  | 1 | 10SP | 293 | 335 |  | 115.4 | 115.1747 | 115.2899 | [7 empty] | CATEGORYB | SINGLE | PECULIAR - STILWELL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  | reconductor with 1192 acss / 584 | KACP | REDEL - STILWELL 161KV CKT 1 | Reconductor line with 1192 ACSS and upgrade terminal equipment for 2000 amps | 558 | 558 |  |  |  | 24 | 4 | [5 empty] | 2200000 | 2008-02-21 | [23 empty] | 2009-06-01 | 2011-06-01 | 2010-10-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 3 | 2007AG2AFS81T2282310SP | TO->FROM | REDEL - STILWELL 161KV CKT 1 | EXP | KACP | KACP | JOCO | JOCO | 0 | 542969 | STILWEL5 161.00 | 543053 | REDEL 5 161.00 | 0 |  | 1 | 10SP | 293 | 335 |  | 115.4 | 115.1747 | 115.2899 | [7 empty] | CATEGORYB | SINGLE | PECULIAR - STILWELL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  | MIPU | South Harper 161 kV cut-in to Stilwell-Archie JCT 161 kV line | To tap Stilwell-Archie JCT 161 kV line into South Harper 161 kV sub and make it two new 161 kV sections: Stilwell-South Harper and Archie JCT- South Harper . | 293 | 335 |  |  |  | 30 | 30 | [5 empty] | 2259673 | 2009-02-06 | [23 empty] | 2009-06-01 | 2010-11-01 | 2010-10-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 4 | 4 | 2007AG2AFS81V10744418SP |  | REEDING 69KV | EXP | WFEC |  | AEP-IM |  |  | 521037 | REEDING2 69.000 | [5 empty] | 18SP | [6 empty] | 0.75676 | 0.76825 | 0.77604 | 0.7653 | 0.94995 | 0.9 | 1.05 | CATEGORYB | SINGLE | DOVER SW (DOVER) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 520882 | DOVERSW4 138.00 | 520881 | DOVERSW2 69.000 | 521166 | DVRTERT 13.800 | 1 |  |  | WFEC | Multi-Dover-Twin Lake_Cresent 138 kV | Convert 69 kV to 138 kV and install terminal equipment at Dover SW; Instal 7 miles of new 138 kV fro WFEC Twin Lakes to OGE Cresent substation | [37 empty] | 2014-06-01 | 2014-06-01
NA | [8 empty] | NAWERERENNO 1X731 |  | RENO 345/115KV CKT 1 | U | WERE | WERE |  |  | 1 | 532771 | RENO 7 345.00 | 533416 | RENO 3 115.00 | 532807 |  | 1 | [15 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WERE | RENO 345/115KV CKT 1 | New stepdown transformer at a new substation in Reno County east northeast of Hutchinson | [37 empty] | 2009-06-01 | 2009-06-01
NA | [8 empty] | NAWERERENNO 2X731 |  | RENO 345/115KV CKT 2 | U | WERE | WERE |  |  | 1 | 532771 | RENO 7 345.00 | 533416 | RENO 3 115.00 | 532810 |  | 1 | [15 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WERE | RENO 345/115KV CKT 2 | Install 2nd stepdown transformer at Reno County substation east northeast of Hutchinson | [37 empty] | 2010-06-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 2 | 1 | 2007AG2AFS81T712110SP | FROM->TO | RIVERSIDE STATION - TULSA POWER STATION 138KV CKT 1 | REL | AEPW | AEPW | TULSA | TULSA | 0 | 509783 | R.S.S.-4 138.00 | 509788 | T.P.S.-4 138.00 | 0 |  | 1 | 10SP | 161 | 187 |  | 101 | 101.0789 | 100.5459 | [7 empty] | CATEGORYB | SINGLE | OAKS EAST TAP - RIVERSIDE STATION 138KV CKT 1 | 0 | 509783 | R.S.S.-4 138.00 | 509850 | OAKSETP4 138.00 | 0 |  | 1 |  |  | AEPW | RIVERSIDE STATION - TULSA POWER STATION 138KV CKT 1 | Rebuild 5.82 miles with 1272 ACSR. Replace TPS wavetrap & jumpers. Reset TPS CTs | 280 | 331 | 332 | 374 | 5.82 | 20 | 5 |  | 0.0046 | 0.03366 | 0.01001 | Limiting factor will be Riverside Jumpers | 6200000 | 2008-07-30 | [23 empty] | 2010-06-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 1 | 2007AG2AFS81T1384113SP | FROM->TO | RIVERSIDE STATION - TULSA POWER STATION 138KV CKT 1 | REL | AEPW | AEPW | TULSA | TULSA | 0 | 509783 | R.S.S.-4 138.00 | 509788 | T.P.S.-4 138.00 | 0 |  | 1 | 13SP | 161 | 187 |  |  | 103.2116 | 104.5422 | [7 empty] | CATEGORYB | SINGLE | OAKS EAST TAP - RIVERSIDE STATION 138KV CKT 1 | 0 | 509783 | R.S.S.-4 138.00 | 509850 | OAKSETP4 138.00 | 0 |  | 1 |  |  | AEPW | RIVERSIDE STATION - TULSA POWER STATION 138KV CKT 1 | Rebuild 5.82 miles with 1272 ACSR. Replace TPS wavetrap & jumpers. Reset TPS CTs | 280 | 331 | 332 | 374 | 5.82 | 20 | 5 |  | 0.0046 | 0.03366 | 0.01001 | Limiting factor will be Riverside Jumpers | 6200000 | 2008-07-30 | [23 empty] | 2010-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2007AG2AFS81T1355513SP | FROM->TO | RIVERSIDE STATION - TULSA POWER STATION 138KV CKT 1 | REL | AEPW | AEPW | TULSA | TULSA | 0 | 509783 | R.S.S.-4 138.00 | 509788 | T.P.S.-4 138.00 | 0 |  | 1 | 13SP | 161 | 187 |  | 101.9 | 99.9789 | 102.0829 | [7 empty] | CATEGORYB | SINGLE | RIVERSIDE STATION - SAPULPA ROAD 345KV CKT 1 | 0 | 509782 | R.S.S.-7 345.00 | 509870 | SAPLPRD7 345.00 | 0 |  | 1 |  |  | AEPW | RIVERSIDE STATION - TULSA POWER STATION 138KV CKT 1 | Rebuild 5.82 miles with 1272 ACSR. Replace TPS wavetrap & jumpers. Reset TPS CTs | 280 | 331 | 332 | 374 | 5.82 | 20 | 5 |  | 0.0046 | 0.03366 | 0.01001 | Limiting factor will be Riverside Jumpers | 6200000 | 2008-07-30 | [23 empty] | 2010-06-01 | 2011-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 1 | 2007AG2AFS81T1394113SP | FROM->TO | RIVERSIDE STATION - TULSA POWER STATION 138KV CKT 1 | REL | AEPW | AEPW | TULSA | TULSA | 0 | 509783 | R.S.S.-4 138.00 | 509788 | T.P.S.-4 138.00 | 0 |  | 1 | 13SP | 161 | 187 |  |  | 99.5416 | 100.7887 | [7 empty] | CATEGORYB | SINGLE | OAKS EAST TAP - TULSA POWER STATION 138KV CKT 1 | 0 | 509788 | T.P.S.-4 138.00 | 509850 | OAKSETP4 138.00 | 0 |  | 1 |  |  | AEPW | RIVERSIDE STATION - TULSA POWER STATION 138KV CKT 1 | Rebuild 5.82 miles with 1272 ACSR. Replace TPS wavetrap & jumpers. Reset TPS CTs | 280 | 331 | 332 | 374 | 5.82 | 20 | 5 |  | 0.0046 | 0.03366 | 0.01001 | Limiting factor will be Riverside Jumpers | 6200000 | 2008-07-30 | [23 empty] | 2010-06-01 | 2011-06-01
2007-AG2 | AFS9 | ISLAND-LOAD |  |  | FDNS |  | 2 | 3 | 2007AG2AFS81T3142309FA | FROM->TO | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 1 | CP | WERE |  | SCENTRAL |  | 2 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532826 | ROSEH1 1 13.800 | 1 | 09FA | 400 | 440 |  |  | 100.2229 | 101.2982 | [7 empty] | CATEGORYB | SINGLE | ROSE HILL (ROSEHL3X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532827 | ROSEH3 1 13.800 | 1 |  |  | WERE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 Displacement | Add third 345-138 kV transformer at Rose Hill | 400 | 440 | 400 | 440 | 0 | 15 | 2 | Y | 0 | 0 | 0 | Like existing Rose Hill 345-138 units | 5000000 | 1134650 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 | ISLAND-LOAD |  |  | FDNS |  | 3 | 2 | 2007AG2AFS81T4543209G | FROM->TO | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 1 | CP | WERE |  | SCENTRAL |  | 2 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532826 | ROSEH1 1 13.800 | 1 | 09G | 400 | 440 |  |  | 100.8143 | 100.8719 | [7 empty] | CATEGORYB | SINGLE | ROSE HILL (ROSEHL3X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532827 | ROSEH3 1 13.800 | 1 |  |  | WERE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 Displacement | Add third 345-138 kV transformer at Rose Hill | 400 | 440 | 400 | 440 | 0 | 15 | 2 | Y | 0 | 0 | 0 | Like existing Rose Hill 345-138 units | 5000000 | 1134650 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 2 | 2007AG2AFS81T11973210SP | FROM->TO | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 1 | CP | WERE |  | SCENTRAL |  | 2 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532826 | ROSEH1 1 13.800 | 1 | 10SP | 400 | 440 | 102.2 | 100.5 | 100.0601 | 102.4293 | [7 empty] | CATEGORYB | SINGLE | ROSE HILL (ROSEHL3X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532827 | ROSEH3 1 13.800 | 1 |  |  | WERE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 Displacement | Add third 345-138 kV transformer at Rose Hill | 400 | 440 | 400 | 440 | 0 | 15 | 2 | Y | 0 | 0 | 0 | Like existing Rose Hill 345-138 units | 5000000 | 1134650 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 | ISLAND-LOAD |  |  | FDNS |  | 2 | 3 | 2007AG2AFS81T3132309FA | FROM->TO | ROSE HILL (ROSEHL3X) 345/138/13.8KV TRANSFORMER CKT 1 | CP | WERE |  | SCENTRAL |  | 2 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532827 | ROSEH3 1 13.800 | 1 | 09FA | 400 | 440 |  |  | 100.2536 | 101.3269 | [7 empty] | CATEGORYB | SINGLE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532826 | ROSEH1 1 13.800 | 1 |  |  | WERE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 Displacement | Add third 345-138 kV transformer at Rose Hill | 400 | 440 | 400 | 440 | 0 | 15 | 2 | Y | 0 | 0 | 0 | Like existing Rose Hill 345-138 units | 5000000 | 1134650 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 | ISLAND-LOAD |  |  | FDNS |  | 3 | 2 | 2007AG2AFS81T4533209G | FROM->TO | ROSE HILL (ROSEHL3X) 345/138/13.8KV TRANSFORMER CKT 1 | CP | WERE |  | SCENTRAL |  | 2 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532827 | ROSEH3 1 13.800 | 1 | 09G | 400 | 440 |  |  | 100.8459 | 100.9036 | [7 empty] | CATEGORYB | SINGLE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532826 | ROSEH1 1 13.800 | 1 |  |  | WERE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 Displacement | Add third 345-138 kV transformer at Rose Hill | 400 | 440 | 400 | 440 | 0 | 15 | 2 | Y | 0 | 0 | 0 | Like existing Rose Hill 345-138 units | 5000000 | 1134650 | [23 empty] | 2009-04-01 | 2011-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 2 | 2007AG2AFS81T11963210SP | FROM->TO | ROSE HILL (ROSEHL3X) 345/138/13.8KV TRANSFORMER CKT 1 | CP | WERE |  | SCENTRAL |  | 2 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532827 | ROSEH3 1 13.800 | 1 | 10SP | 400 | 440 | 102.3 | 100.6 | 100.111 | 102.4847 | [7 empty] | CATEGORYB | SINGLE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532826 | ROSEH1 1 13.800 | 1 |  |  | WERE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 Displacement | Add third 345-138 kV transformer at Rose Hill | 400 | 440 | 400 | 440 | 0 | 15 | 2 | Y | 0 | 0 | 0 | Like existing Rose Hill 345-138 units | 5000000 | 1134650 | [23 empty] | 2009-04-01 | 2011-06-01
GEN-2006-010 | Turk | [7 empty] | 507454508078012SP | TO->FROM | SE TEXARKANA - TURK 138KV CKT 1 | U | AEPW | AEPW | SARK | TEXARK | 0 | 507454 | HEMPSTD4 138.00 | 508078 | SETEXAR4 138.00 | 0 |  | 1 |  | 368 | 512 |  |  | 125.3 | [9 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | AEPW | SE TEXARKANA - TURK 138KV CKT 1 | Build new Turk-SE Texarkana 138 kV line and add SE Texarkana 138 kV terminal. | [12 empty] | 26850000 | [24 empty] | 2012-07-01 | 2012-07-01
2007-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T2812209SP | FROM->TO | SEVENTEENTH (17TH 4X) 138/69/11.295KV TRANSFORMER CKT 1 | REL | WERE |  | SCENTRAL |  | 1 | 533064 | 17TH 4 138.00 | 533840 | 17TH 2 69.000 | 533112 | 17TH 1 11.295 | 1 | 09SP | 150 | 165 | 101.9 | 102 | 102.0081 | 102.0774 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  | WERE | SEVENTEENTH () 138/69/11.295KV TRANSFORMER CKT 2 | Install second 17th St. 138-69 kV transformer | 150 | 165 | 150 | 165 |  | 12 | 6 |  | 0.002 | 0.0653 |  | 165 MVA is transformer limit | 2400000 | 2006-03-21 | [23 empty] | 2009-06-01 | 2012-06-01 | 2010-10-01
2007-AG2 | AFS9 | CONT-0602 - Chisholm #1 138-69kV XFMR | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T9052209SP | FROM->TO | SEVENTEENTH (17TH 4X) 138/69/11.295KV TRANSFORMER CKT 1 | REL | WERE |  | SCENTRAL |  | 1 | 533064 | 17TH 4 138.00 | 533840 | 17TH 2 69.000 | 533112 | 17TH 1 11.295 | 1 | 09SP | 150 | 165 | 101.0 | 100.8 | 100.9029 | 100.9653 | [7 empty] | CATEGORYB | SINGLE | CHISHOLM (CHISLM1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 533035 | CHISHLM4 138.00 | 533786 | CHISHLM2 69.000 | 533103 | CHISOLM1 13.200 | 1 |  |  | WERE | SEVENTEENTH () 138/69/11.295KV TRANSFORMER CKT 2 | Install second 17th St. 138-69 kV transformer | 150 | 165 | 150 | 165 |  | 12 | 6 |  | 0.002 | 0.0653 |  | 165 MVA is transformer limit | 2400000 | 2006-03-21 | [23 empty] | 2009-06-01 | 2012-06-01 | 2010-10-01
2007-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T3212210SP | FROM->TO | SEVENTEENTH (17TH 4X) 138/69/11.295KV TRANSFORMER CKT 1 | REL | WERE |  | SCENTRAL |  | 1 | 533064 | 17TH 4 138.00 | 533840 | 17TH 2 69.000 | 533112 | 17TH 1 11.295 | 1 | 10SP | 150 | 165 | 105.3 | 103.6 | 104.9974 | 105.1622 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  | WERE | SEVENTEENTH () 138/69/11.295KV TRANSFORMER CKT 2 | Install second 17th St. 138-69 kV transformer | 150 | 165 | 150 | 165 |  | 12 | 6 |  | 0.002 | 0.0653 |  | 165 MVA is transformer limit | 2400000 | 2006-03-21 | [23 empty] | 2009-06-01 | 2012-06-01 | 2010-10-01
2007-AG2 | AFS9 | CONT-0602 - Chisholm #1 138-69kV XFMR | FDNS |  | FDNS |  | 2 | 2 | 2007AG2AFS81T12552210SP | FROM->TO | SEVENTEENTH (17TH 4X) 138/69/11.295KV TRANSFORMER CKT 1 | REL | WERE |  | SCENTRAL |  | 1 | 533064 | 17TH 4 138.00 | 533840 | 17TH 2 69.000 | 533112 | 17TH 1 11.295 | 1 | 10SP | 150 | 165 | 102.5 | 102 | 103.2752 | 103.3831 | [7 empty] | CATEGORYB | SINGLE | CHISHOLM (CHISLM1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 533035 | CHISHLM4 138.00 | 533786 | CHISHLM2 69.000 | 533103 | CHISOLM1 13.200 | 1 |  |  | WERE | SEVENTEENTH () 138/69/11.295KV TRANSFORMER CKT 2 | Install second 17th St. 138-69 kV transformer | 150 | 165 | 150 | 165 |  | 12 | 6 |  | 0.002 | 0.0653 |  | 165 MVA is transformer limit | 2400000 | 2006-03-21 | [23 empty] | 2009-06-01 | 2012-06-01 | 2010-10-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 1 | 3 | 2007AG2AFS81T351309SH | FROM->TO | SILOAM CITY - SILOAM SPRINGS 161KV CKT 1 | REL | GRDA | AEPW | GRDA-MUN | FAYETTEV | 0 | 512643 | SILMCTY5 161.00 | 506948 | SILOAM 5 161.00 | 0 |  | 1 | 09SH | 288 | 335 |  |  | 98.3538 | 100.6646 | [7 empty] | CATEGORYB | SINGLE | CHAMBER SPRINGS - CLARKSVILLE 345KV CKT 1 | 0 | 506945 | CHAMSPR7 345.00 | 509745 | CLARKSV7 345.00 | 0 |  | 1 |  |  | AEPW | SILOAM CITY - SILOAM SPRINGS 161KV CKT 1 | Rebuild 2.06 miles of 2-397 ACSR with 2156 ACSR. Replace breaker, wavetrap, switches, & jumpers @ AEP Siloam Springs. | 531 | 638 | 633 | 721 | 2.06 | 20 | 6 |  | 0.0004 | 0.005282 | 0.00344 | New AEP limits will be Siloam Springs bus | 2500000 | 2008-08-04 | [23 empty] | 2009-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 1 | 3 | 2007AG2AFS81T531309SP | FROM->TO | SILOAM CITY - SILOAM SPRINGS 161KV CKT 1 | REL | GRDA | AEPW | GRDA-MUN | FAYETTEV | 0 | 512643 | SILMCTY5 161.00 | 506948 | SILOAM 5 161.00 | 0 |  | 1 | 09SP | 288 | 335 |  | 101.1 | 99.2296 | 101.6199 | [7 empty] | CATEGORYB | SINGLE | CHAMBER SPRINGS - CLARKSVILLE 345KV CKT 1 | 0 | 506945 | CHAMSPR7 345.00 | 509745 | CLARKSV7 345.00 | 0 |  | 1 |  |  | AEPW | SILOAM CITY - SILOAM SPRINGS 161KV CKT 1 | Rebuild 2.06 miles of 2-397 ACSR with 2156 ACSR. Replace breaker, wavetrap, switches, & jumpers @ AEP Siloam Springs. | 531 | 638 | 633 | 721 | 2.06 | 20 | 6 |  | 0.0004 | 0.005282 | 0.00344 | New AEP limits will be Siloam Springs bus | 2500000 | 2008-08-04 | [23 empty] | 2009-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T613310SP | FROM->TO | SILOAM CITY - SILOAM SPRINGS 161KV CKT 1 | REL | GRDA | AEPW | GRDA-MUN | FAYETTEV | 0 | 512643 | SILMCTY5 161.00 | 506948 | SILOAM 5 161.00 | 0 |  | 1 | 10SP | 288 | 335 |  | 103.4 | 102.6118 | 103.787 | [7 empty] | CATEGORYB | SINGLE | CHAMBER SPRINGS - CLARKSVILLE 345KV CKT 1 | 0 | 506945 | CHAMSPR7 345.00 | 509745 | CLARKSV7 345.00 | 0 |  | 1 |  |  | AEPW | SILOAM CITY - SILOAM SPRINGS 161KV CKT 1 | Rebuild 2.06 miles of 2-397 ACSR with 2156 ACSR. Replace breaker, wavetrap, switches, & jumpers @ AEP Siloam Springs. | 531 | 638 | 633 | 721 | 2.06 | 20 | 6 |  | 0.0004 | 0.005282 | 0.00344 | New AEP limits will be Siloam Springs bus | 2500000 | 2008-08-04 | [23 empty] | 2009-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T1083313SP | FROM->TO | SILOAM CITY - SILOAM SPRINGS 161KV CKT 1 | REL | GRDA | AEPW | GRDA-MUN | FAYETTEV | 0 | 512643 | SILMCTY5 161.00 | 506948 | SILOAM 5 161.00 | 0 |  | 1 | 13SP | 288 | 335 |  | 102.6 | 102.1051 | 103.2058 | [7 empty] | CATEGORYB | SINGLE | CHAMBER SPRINGS - CLARKSVILLE 345KV CKT 1 | 0 | 506945 | CHAMSPR7 345.00 | 509745 | CLARKSV7 345.00 | 0 |  | 1 |  |  | AEPW | SILOAM CITY - SILOAM SPRINGS 161KV CKT 1 | Rebuild 2.06 miles of 2-397 ACSR with 2156 ACSR. Replace breaker, wavetrap, switches, & jumpers @ AEP Siloam Springs. | 531 | 638 | 633 | 721 | 2.06 | 20 | 6 |  | 0.0004 | 0.005282 | 0.00344 | New AEP limits will be Siloam Springs bus | 2500000 | 2008-08-04 | [23 empty] | 2009-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 4 | 1 | 2007AG2AFS81T2324118SP | FROM->TO | SILOAM CITY - SILOAM SPRINGS 161KV CKT 1 | REL | GRDA | AEPW | GRDA-MUN | FAYETTEV | 0 | 512643 | SILMCTY5 161.00 | 506948 | SILOAM 5 161.00 | 0 |  | 1 | 18SP | 288 | 335 |  | 102.5 | 100.8426 | 102.7649 | [7 empty] | CATEGORYB | SINGLE | CHAMBER SPRINGS - CLARKSVILLE 345KV CKT 1 | 0 | 506945 | CHAMSPR7 345.00 | 509745 | CLARKSV7 345.00 | 0 |  | 1 |  |  | AEPW | SILOAM CITY - SILOAM SPRINGS 161KV CKT 1 | Rebuild 2.06 miles of 2-397 ACSR with 2156 ACSR. Replace breaker, wavetrap, switches, & jumpers @ AEP Siloam Springs. | 531 | 638 | 633 | 721 | 2.06 | 20 | 6 |  | 0.0004 | 0.005282 | 0.00344 | New AEP limits will be Siloam Springs bus | 2500000 | 2008-08-04 | [23 empty] | 2009-06-01 | 2011-06-01
GEN-2004-014 | Spearville2 | [7 empty] | 53969453969553993512SP | FROM->TO | SPEARVILLE (SPEARVL6) 230/115/13.8KV TRANSFORMER CKT 1 | U | MKEC |  |  |  | 1 | 539694 | SPEARVL3 115.00 | 539695 | SPEARVL6 230.00 | 539935 | SPERVLTT 13.800 | 1 |  | 205 | 205 |  |  | 38.8 | [9 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | MKEC | SPEARVILLE (SPEARVL6) 230/115/13.8KV TRANSFORMER CKT 1 | 230kv line terminal at Spearville | [12 empty] | 650000 | [24 empty] | 2009-12-31 | 2009-12-31
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 1 | 3 | 2007AG2AFS81T6161318SP | FROM->TO | SPRINGFIELD (SPF X1) 161/69/13.8KV TRANSFORMER CKT 1 | EXP | SWPA |  | EMINTH |  | 2 | 505492 | SPRGFLD5 161.00 | 505494 | SPRGFLD2 69.000 | 505491 | SPF X1 1 13.800 | 1 | 18SP | 80 | 80 | 113.3 | 113.2 | 111.2764 | 113.7909 | [7 empty] | CATEGORYB | SINGLE | JAMES RIVER - PLAINVIEW 69KV CKT 1 | 0 | 549904 | JAMES RIVER269.000 | 549905 | PLAINVIEW 269.000 | 0 |  | 1 |  |  | SWPA | SPRINGFIELD (SPF X1) 161/69/13.8KV TRANSFORMER CKT 1 | Replace Springfield xfmr #1 three winding transformer with 70 MVA auto transformer. | [5 empty] | 24 | [6 empty] | 1500000 | 2008-05-29 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 1 | 3 | 2007AG2AFS81T6161318SP | FROM->TO | SPRINGFIELD (SPF X1) 161/69/13.8KV TRANSFORMER CKT 1 | EXP | SWPA |  | EMINTH |  | 2 | 505492 | SPRGFLD5 161.00 | 505494 | SPRGFLD2 69.000 | 505491 | SPF X1 1 13.800 | 1 | 18SP | 80 | 80 | 103.4 | 113.2 | 111.2764 | 113.7909 | [7 empty] | CATEGORYB | SINGLE | JAMES RIVER - PLAINVIEW 69KV CKT 1 | 0 | 549904 | JAMES RIVER269.000 | 549905 | PLAINVIEW 269.000 | 0 |  | 1 |  |  | SWPA | SPRINGFIELD (SPF X1) 161/69/13.8KV TRANSFORMER CKT 1 | Replace Springfield xfmr #1 three winding transformer with 70 MVA auto transformer. | [5 empty] | 24 | [6 empty] | 1500000 | 2008-05-29 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 1 | 3 | 2007AG2AFS81T6161318SP | FROM->TO | SPRINGFIELD (SPF X1) 161/69/13.8KV TRANSFORMER CKT 1 | EXP | SWPA |  | EMINTH |  | 2 | 505492 | SPRGFLD5 161.00 | 505494 | SPRGFLD2 69.000 | 505491 | SPF X1 1 13.800 | 1 | 18SP | 80 | 80 | 113.3 | 113.2 | 111.2764 | 113.7909 | [7 empty] | CATEGORYB | SINGLE | JAMES RIVER - PLAINVIEW 69KV CKT 1 | 0 | 549904 | JAMES RIVER269.000 | 549905 | PLAINVIEW 269.000 | 0 |  | 1 |  |  | SWPA | SPRINGFIELD (SPF X1) 161/69/13.8KV TRANSFORMER CKT 1 | Replace Springfield xfmr #1 three winding transformer with 70 MVA auto transformer. | [5 empty] | 24 | [6 empty] | 1500000 | 2008-05-29 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 1 | 3 | 2007AG2AFS81T6161318SP | FROM->TO | SPRINGFIELD (SPF X1) 161/69/13.8KV TRANSFORMER CKT 1 | EXP | SWPA |  | EMINTH |  | 2 | 505492 | SPRGFLD5 161.00 | 505494 | SPRGFLD2 69.000 | 505491 | SPF X1 1 13.800 | 1 | 18SP | 80 | 80 | 103.4 | 113.2 | 111.2764 | 113.7909 | [7 empty] | CATEGORYB | SINGLE | JAMES RIVER - PLAINVIEW 69KV CKT 1 | 0 | 549904 | JAMES RIVER269.000 | 549905 | PLAINVIEW 269.000 | 0 |  | 1 |  |  | SWPA | SPRINGFIELD (SPF X1) 161/69/13.8KV TRANSFORMER CKT 1 | Replace Springfield xfmr #1 three winding transformer with 70 MVA auto transformer. | [5 empty] | 24 | [6 empty] | 1500000 | 2008-05-29 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 1 | 2 | 2007AG2AFS81T7681218SP | FROM->TO | SPRINGFIELD (SPF X1) 161/69/13.8KV TRANSFORMER CKT 1 | EXP | SWPA |  | EMINTH |  | 2 | 505492 | SPRGFLD5 161.00 | 505494 | SPRGFLD2 69.000 | 505491 | SPF X1 1 13.800 | 1 | 18SP | 80 | 80 | 102.2 | 101.5 | 100.4737 | 107.061 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE - JUNCTION 161KV CKT 1 | 0 | 549955 | JUNCTION 5161.00 | 549969 | BROOKLINE 5161.00 | 0 |  | 1 |  |  | SWPA | SPRINGFIELD (SPF X1) 161/69/13.8KV TRANSFORMER CKT 1 | Replace Springfield xfmr #1 three winding transformer with 70 MVA auto transformer. | [5 empty] | 24 | [6 empty] | 1500000 | 2008-05-29 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 1 | 2 | 2007AG2AFS81T7681218SP | FROM->TO | SPRINGFIELD (SPF X1) 161/69/13.8KV TRANSFORMER CKT 1 | EXP | SWPA |  | EMINTH |  | 2 | 505492 | SPRGFLD5 161.00 | 505494 | SPRGFLD2 69.000 | 505491 | SPF X1 1 13.800 | 1 | 18SP | 80 | 80 | 102.2 | 101.5 | 100.4737 | 107.061 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE - JUNCTION 161KV CKT 1 | 0 | 549955 | JUNCTION 5161.00 | 549969 | BROOKLINE 5161.00 | 0 |  | 1 |  |  | SWPA | SPRINGFIELD (SPF X1) 161/69/13.8KV TRANSFORMER CKT 1 | Replace Springfield xfmr #1 three winding transformer with 70 MVA auto transformer. | [5 empty] | 24 | [6 empty] | 1500000 | 2008-05-29 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2007AG2AFS81T5625518SPG | FROM->TO | SPRINGFIELD (SPF X1) 161/69/13.8KV TRANSFORMER CKT 1 | EXP | SWPA |  | EMINTH |  | 2 | 505492 | SPRGFLD5 161.00 | 505494 | SPRGFLD2 69.000 | 505491 | SPF X1 1 13.800 | 1 | 18SP | 80 | 80 | 100.4 | 100.7 | 99.6202 | 106.7739 | [7 empty] | CATEGORYB | GENOUT | GEN549898 4-JAMES RIVER 4 | 0 | 0 |  | 0 |  | 0 |  |  |  |  | SWPA | SPRINGFIELD (SPF X1) 161/69/13.8KV TRANSFORMER CKT 1 | Replace Springfield xfmr #1 three winding transformer with 70 MVA auto transformer. | [5 empty] | 24 | [6 empty] | 1500000 | 2008-05-29 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2007AG2AFS81T5625518SPG | FROM->TO | SPRINGFIELD (SPF X1) 161/69/13.8KV TRANSFORMER CKT 1 | EXP | SWPA |  | EMINTH |  | 2 | 505492 | SPRGFLD5 161.00 | 505494 | SPRGFLD2 69.000 | 505491 | SPF X1 1 13.800 | 1 | 18SP | 80 | 80 | 100.4 | 100.7 | 99.6202 | 106.7739 | [7 empty] | CATEGORYB | GENOUT | GEN549898 4-JAMES RIVER 4 | 0 | 0 |  | 0 |  | 0 |  |  |  |  | SWPA | SPRINGFIELD (SPF X1) 161/69/13.8KV TRANSFORMER CKT 1 | Replace Springfield xfmr #1 three winding transformer with 70 MVA auto transformer. | [5 empty] | 24 | [6 empty] | 1500000 | 2008-05-29 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T4703318SPG | FROM->TO | SPRINGFIELD (SPF X1) 161/69/13.8KV TRANSFORMER CKT 1 | EXP | SWPA |  | EMINTH |  | 2 | 505492 | SPRGFLD5 161.00 | 505494 | SPRGFLD2 69.000 | 505491 | SPF X1 1 13.800 | 1 | 18SP | 80 | 80 | 106.1 | 105.9 | 106.023 | 105.8951 | [7 empty] | CATEGORYB | GENOUT | GEN549899 5-JAMES RIVER 5 | 0 | 0 |  | 0 |  | 0 |  |  |  |  | SWPA | SPRINGFIELD (SPF X1) 161/69/13.8KV TRANSFORMER CKT 1 | Replace Springfield xfmr #1 three winding transformer with 70 MVA auto transformer. | [5 empty] | 24 | [6 empty] | 1500000 | 2008-05-29 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T4703318SPG | FROM->TO | SPRINGFIELD (SPF X1) 161/69/13.8KV TRANSFORMER CKT 1 | EXP | SWPA |  | EMINTH |  | 2 | 505492 | SPRGFLD5 161.00 | 505494 | SPRGFLD2 69.000 | 505491 | SPF X1 1 13.800 | 1 | 18SP | 80 | 80 | 106.1 | 105.9 | 106.023 | 105.8951 | [7 empty] | CATEGORYB | GENOUT | GEN549899 5-JAMES RIVER 5 | 0 | 0 |  | 0 |  | 0 |  |  |  |  | SWPA | SPRINGFIELD (SPF X1) 161/69/13.8KV TRANSFORMER CKT 1 | Replace Springfield xfmr #1 three winding transformer with 70 MVA auto transformer. | [5 empty] | 24 | [6 empty] | 1500000 | 2008-05-29 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 2 | 2007AG2AFS81T9514218SPG | FROM->TO | SPRINGFIELD (SPF X1) 161/69/13.8KV TRANSFORMER CKT 1 | EXP | SWPA |  | EMINTH |  | 2 | 505492 | SPRGFLD5 161.00 | 505494 | SPRGFLD2 69.000 | 505491 | SPF X1 1 13.800 | 1 | 18SP | 80 | 80 |  |  | 95.2071 | 100.5806 | [7 empty] | CATEGORYB | GENOUT | GEN549897 3-JAMES RIVER 3 | 0 | 0 |  | 0 |  | 0 |  |  |  |  | SWPA | SPRINGFIELD (SPF X1) 161/69/13.8KV TRANSFORMER CKT 1 | Replace Springfield xfmr #1 three winding transformer with 70 MVA auto transformer. | [5 empty] | 24 | [6 empty] | 1500000 | 2008-05-29 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG2 | AFS9 |  |  |  | FDNS |  | 4 | 2 | 2007AG2AFS81T9514218SPG | FROM->TO | SPRINGFIELD (SPF X1) 161/69/13.8KV TRANSFORMER CKT 1 | EXP | SWPA |  | EMINTH |  | 2 | 505492 | SPRGFLD5 161.00 | 505494 | SPRGFLD2 69.000 | 505491 | SPF X1 1 13.800 | 1 | 18SP | 80 | 80 |  |  | 95.2071 | 100.5806 | [7 empty] | CATEGORYB | GENOUT | GEN549897 3-JAMES RIVER 3 | 0 | 0 |  | 0 |  | 0 |  |  |  |  | SWPA | SPRINGFIELD (SPF X1) 161/69/13.8KV TRANSFORMER CKT 1 | Replace Springfield xfmr #1 three winding transformer with 70 MVA auto transformer. | [5 empty] | 24 | [6 empty] | 1500000 | 2008-05-29 | [23 empty] | 2016-06-01 | 2016-06-01
2005-AG2 | 2005-AG2 | [7 empty] | 59467594691594705949813315SP |  | SUB 110 - ORONOGO JCT. - SUB 167 - RIVERTON 161KV CKT 1 | U | EMDE | EMDE |  |  | 0 | 547469 | RIV167 5 161 | 547467 | ORO110 5 161 | 0 |  | 1 | 15SP |  | 214 | [12 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | EMDE | SUB 110 - ORONOGO JCT. - SUB 167 - RIVERTON 161KV CKT 1 | Reconductor Oronogo 59467 to Riverton 59469 with Bundled 556 ACSR | 299 | 335 | 299 | 335 | 11.84 | 24 | 12 |  | 0.00379 | 0.02451 | 0.02427 |  | 5400000 | [24 empty] | 2011-06-01 | 2011-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T5913318SP | TO->FROM | SUB 145 - JOPLIN WEST 7TH - SUB 439 - STATELINE 161KV CKT 1 | REL | EMDE | EMDE | JOPLIN | JOPLIN | 0 | 547498 | STL439 5 161.00 | 547470 | JOP145 5 161.00 | 0 |  | 1 | 18SP | 218 | 268 | 102.4 | 103.3 | 103.4002 | 104.0705 | [7 empty] | CATEGORYB | SINGLE | SUB 110 - ORONOGO JCT. - SUB 452 - RIVERTON 161KV CKT 1 | 0 | 547467 | ORO110 5 161.00 | 547469 | RIV4525 161.00 | 0 |  | 1 |  |  | EMDE | Multi - Stateline - Joplin - Reinmiller conversion | Tear down the Riverton to Joplin 59 69 kV line, rebuilding the line to 161 kV from Stateline to outside Joplin 59 sub. Tear down and rebuild Joplin 59 to Gateway to Pillsbury to Reinmiller, converting those 69 kV lines to 161 kV. Tap the 161 kV line between Joplin 59 and Gateway at Joplin 422. | [5 empty] | 48 | 48 | [5 empty] | 25000000 | 2008-06-01 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2007AG2AFS81T7185518SP | FROM->TO | SUB 389 - JOPLIN SOUTHWEST (JOPLINSW) 161/69/12.5KV TRANSFORMER CKT 1 | REL | EMDE |  | JOPLIN |  | 2 | 547483 | JOP389 5 161.00 | 547592 | JOP389 2 69.000 | 547713 | JOP389 1 12.500 | 1 | 18SP | 75 | 75 | 100.5 | 100.9 | 100.853 | 101.4252 | [7 empty] | CATEGORYB | SINGLE | SUB 292 - TIPTON FORD - SUB 389 - JOPLIN SOUTHWEST 161KV CKT 1 | 0 | 547472 | TIP292 5 161.00 | 547483 | JOP389 5 161.00 | 0 |  | 1 |  |  | EMDE | Multi - Stateline - Joplin - Reinmiller conversion | Tear down the Riverton to Joplin 59 69 kV line, rebuilding the line to 161 kV from Stateline to outside Joplin 59 sub. Tear down and rebuild Joplin 59 to Gateway to Pillsbury to Reinmiller, converting those 69 kV lines to 161 kV. Tap the 161 kV line between Joplin 59 and Gateway at Joplin 422. | [5 empty] | 48 | 48 | [5 empty] | 25000000 | 2008-06-01 | [23 empty] | 2016-06-01 | 2016-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 3 | 3 | 2007AG2AFS81T5983318SP | FROM->TO | SUB 389 - JOPLIN SOUTHWEST (JOPLINSW) 161/69/12.5KV TRANSFORMER CKT 1 | REL | EMDE |  | JOPLIN |  | 1 | 547483 | JOP389 5 161.00 | 547592 | JOP389 2 69.000 | 547713 | JOP389 1 12.500 | 1 | 18SP | 75 | 75 |  | 100.1 | 100.139 | 100.7027 | [7 empty] | CATEGORYB | SINGLE | SUB 145 - JOPLIN WEST 7TH - SUB 439 - STATELINE 161KV CKT 1 | 0 | 547470 | JOP145 5 161.00 | 547498 | STL439 5 161.00 | 0 |  | 1 |  |  | EMDE | Multi - Stateline - Joplin - Reinmiller conversion | Tear down the Riverton to Joplin 59 69 kV line, rebuilding the line to 161 kV from Stateline to outside Joplin 59 sub. Tear down and rebuild Joplin 59 to Gateway to Pillsbury to Reinmiller, converting those 69 kV lines to 161 kV. Tap the 161 kV line between Joplin 59 and Gateway at Joplin 422. | [5 empty] | 48 | 48 | [5 empty] | 25000000 | 2008-06-01 | [23 empty] | 2016-06-01 | 2016-06-01
GEN-2006-010 | Turk | [7 empty] | 507454508080012SP | TO->FROM | SUGAR HILL - TURK 138KV CKT 1 | U | AEPW | AEPW | SARK | TEXARK | 0 | 507454 | HEMPSTD4 138.00 | 508080 | SUGARHL4 138.00 | 0 |  | 1 |  | 368 | 512 |  |  | 159.6 | [9 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | AEPW | SUGAR HILL - TURK 138KV CKT 1 | Build new Turk-Sugar Hill 138 kV line and add Sugar Hill 138 kV terminal. | [12 empty] | 19700000 | [24 empty] | 2012-07-01 | 2012-07-01
NA | [8 empty] | NAWERE5327735327711 |  | SUMMIT - RENO 345KV | U | WERE | WERE |  |  | 0 | 532773 | SUMMIT 7 345.0 | 532771 | RENO 7 345.00 |  |  | 1 | [15 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WERE | SUMMIT - RENO 345KV | Install new 50.55-mile 345 kV line from Reno county to Summit; 31 miles of 115 kV line between Circle and S Philips would be rebuilt as double circuit with the 345 kV line to minimize ROW impacts; Substation work required at Summit for new 345 kV terminal and completion of ring bus. | [37 empty] | 2010-06-01 | 2010-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 4 | 4 | 2007AG2AFS81T2974413SP | FROM->TO | TECUMSEH ENERGY CENTER - TECUMSEH HILL 115KV CKT 1 | REL | WERE | WERE | NEAST | NEAST | 0 | 533180 | TEC E 3 115.00 | 533182 | TECHILE3 115.00 | 0 |  | 1 | 13SP | 236 | 236 |  | 102.3 | 101.8749 | 102.2718 | [7 empty] | CATEGORYB | SINGLE | SWISSVALE - TECUMSEH HILL 230KV CKT 1 | 0 | 532856 | SWISVAL6 230.00 | 532857 | TECHILL6 230.00 | 0 |  | 1 |  |  | WERE | TECUMSEH ENERGY CENTER - TECUMSEH HILL 115KV CKT 1 | Uprate 0.24 mile TEC-Tecumseh Hill 115 kV line to 100 degree operation. | 236 | 250 | 236 | 250 | 0.24 | 10 | 2 | [5 empty] | 80000 | 2006-07-25 | [23 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 4 | 4 | 2007AG2AFS81T12634413SP | FROM->TO | TECUMSEH ENERGY CENTER - TECUMSEH HILL 115KV CKT 1 | REL | WERE | WERE | NEAST | NEAST | 0 | 533180 | TEC E 3 115.00 | 533182 | TECHILE3 115.00 | 0 |  | 1 | 13SP | 236 | 236 |  | 102.2 | 101.7783 | 102.1754 | [7 empty] | CATEGORYB | SINGLE | TECUMSEH HILL (TECH194X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532857 | TECHILL6 230.00 | 533182 | TECHILE3 115.00 | 532886 | TECHILL1 13.800 | 1 |  |  | WERE | TECUMSEH ENERGY CENTER - TECUMSEH HILL 115KV CKT 1 | Uprate 0.24 mile TEC-Tecumseh Hill 115 kV line to 100 degree operation. | 236 | 250 | 236 | 250 | 0.24 | 10 | 2 | [5 empty] | 80000 | 2006-07-25 | [23 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2007AG2AFS81T6105518SP | FROM->TO | TECUMSEH ENERGY CENTER - TECUMSEH HILL 115KV CKT 1 | REL | WERE | WERE | NEAST | NEAST | 0 | 533180 | TEC E 3 115.00 | 533182 | TECHILE3 115.00 | 0 |  | 1 | 18SP | 236 | 236 | 104.8 | 104.3 | 103.5263 | 104.4513 | [7 empty] | CATEGORYB | SINGLE | SWISSVALE - TECUMSEH HILL 230KV CKT 1 | 0 | 532856 | SWISVAL6 230.00 | 532857 | TECHILL6 230.00 | 0 |  | 1 |  |  | WERE | TECUMSEH ENERGY CENTER - TECUMSEH HILL 115KV CKT 1 | Uprate 0.24 mile TEC-Tecumseh Hill 115 kV line to 100 degree operation. | 236 | 250 | 236 | 250 | 0.24 | 10 | 2 | [5 empty] | 80000 | 2006-07-25 | [23 empty] | 2013-06-01 | 2013-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 5 | 5 | 2007AG2AFS81T26645518SP | FROM->TO | TECUMSEH ENERGY CENTER - TECUMSEH HILL 115KV CKT 1 | REL | WERE | WERE | NEAST | NEAST | 0 | 533180 | TEC E 3 115.00 | 533182 | TECHILE3 115.00 | 0 |  | 1 | 18SP | 236 | 236 | 104.7 | 104.2 | 103.4215 | 104.3315 | [7 empty] | CATEGORYB | SINGLE | TECUMSEH HILL (TECH194X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532857 | TECHILL6 230.00 | 533182 | TECHILE3 115.00 | 532886 | TECHILL1 13.800 | 1 |  |  | WERE | TECUMSEH ENERGY CENTER - TECUMSEH HILL 115KV CKT 1 | Uprate 0.24 mile TEC-Tecumseh Hill 115 kV line to 100 degree operation. | 236 | 250 | 236 | 250 | 0.24 | 10 | 2 | [5 empty] | 80000 | 2006-07-25 | [23 empty] | 2013-06-01 | 2013-06-01
GEN-2006-010 | Turk | [7 empty] | 50745450745650745812SP | FROM->TO | TURK (HEMP 1) 138/115/13.8KV TRANSFORMER CKT 1 | U | AEPW |  | SARK |  | 1 | 507454 | HEMPSTD4 138.00 | 507456 | HEMPSTD3 115.00 | 507458 | HEMP1 1 13.800 | 1 |  | 175 | 234 |  |  | 109.4 | [9 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | AEPW | TURK (HEMP 1) 138/115/13.8KV TRANSFORMER CKT 1 | Build Turk 138-115 kV station and relocate autotransformer (and spare) from Patterson to this new Turk station | [12 empty] | 9110000 | [24 empty] | 2012-07-01 | 2012-07-01
GEN-2006-010 | Turk | [7 empty] | 50745650745450745912SP | FROM->TO | TURK (HEMP 2) 138/115/13.8KV TRANSFORMER CKT 2 | U | AEPW |  | SARK |  | 1 | 507456 | HEMPSTD3 115.00 | 507454 | HEMPSTD4 138.00 | 507459 | HEMP2 1 13.800 | 2 |  | 147 | 170 |  |  | 0 | [9 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | AEPW | TURK (HEMP 2) 138/115/13.8KV TRANSFORMER CKT 2 | Relocate autotransformer from Patterson to this new Turk substation | [37 empty] | 2012-07-01 | 2012-07-01
GEN-2006-010 | Turk | [7 empty] | 509416507454012SP | FROM->TO | TURK 138/24.0KV TRANSFORMER CKT 1 | U | AEPW | AEPW | SARK | SARK | 0 | 509416 | TURKCOAL 24.000 | 507454 | HEMPSTD4 138.00 | 0 |  | 1 |  | 750 | 750 |  |  | 618 | [9 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | AEPW | TURK 138/24.0KV TRANSFORMER CKT 1 | Install a GSU transformer at Turk | [37 empty] | 2012-07-01 | 2012-07-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 4 | 4 | 2007AG2AFS81V10624418SP |  | TURKEY CREEK 69KV | EXP | OKGE |  | ENID |  |  | 514735 | TURCRK 2 69.000 | [5 empty] | 18SP | [6 empty] | 0.78716 | 0.79685 | 0.80471 | 0.79463 | 0.98738 | 0.9 | 1.05 | CATEGORYB | SINGLE | DOVER SW (DOVER) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 520882 | DOVERSW4 138.00 | 520881 | DOVERSW2 69.000 | 521166 | DVRTERT 13.800 | 1 |  |  | WFEC | Multi-Dover-Twin Lake_Cresent 138 kV | Convert 69 kV to 138 kV and install terminal equipment at Dover SW; Instal 7 miles of new 138 kV fro WFEC Twin Lakes to OGE Cresent substation | [37 empty] | 2014-06-01 | 2014-06-01
2007-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 4 | 4 | 2007AG2AFS81V10754418SP |  | TWIN LAKES 69KV | EXP | WFEC |  | AEP-IM |  |  | 521073 | TWNLAKE2 69.000 | [5 empty] | 18SP | [6 empty] | 0.72944 | 0.74119 | 0.753 | 0.73826 | 0.97506 | 0.9 | 1.05 | CATEGORYB | SINGLE | DOVER SW (DOVER) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 520882 | DOVERSW4 138.00 | 520881 | DOVERSW2 69.000 | 521166 | DVRTERT 13.800 | 1 |  |  | WFEC | Multi-Dover-Twin Lake_Cresent 138 kV | Convert 69 kV to 138 kV and install terminal equipment at Dover SW; Instal 7 miles of new 138 kV fro WFEC Twin Lakes to OGE Cresent substation | [37 empty] | 2014-06-01 | 2014-06-01
NA | [8 empty] | NAWERE5327965327711 |  | WICHITA - RENO 345KV | U | WERE | WERE |  |  | 0 | 532796 | WICHITA7 345.0 | 532771 | RENO 7 345.00 |  |  | 1 | [15 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WERE | WICHITA - RENO 345KV | 40 mile 345 kV transmission line from existing Wichita 345 kV substation to a new 345-115 kV substation in Reno County east northeast of Hutchinson (Wichita to Reno) | [37 empty] | 2009-06-01 | 2009-06-01
NA | [10 empty] | WOODWARD - IODINE 138KV CKT 1 | U | OKGE | OKGE | ENID | ENID | 0 | 515376 |  | 514796 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | OKGE | WOODWARD - IODINE 138KV CKT 1 | Tap Iodine to Woodward 138 kV line | [12 empty] | 221000000 | [24 empty] | 2010-01-01 | 2010-01-01
NA | [10 empty] | WOODWARD - WOODWARD EHV 138KV CKT 1 | U | OKGE | OKGE | ENID | ENID | 0 | 515376 |  | 514785 |  |  |  | 1 |  | 537 | 616 | [12 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | OKGE | WOODWARD - WOODWARD EHV 138KV CKT 1 | Build .5 miles of 138 kV and install terminal equipment | [12 empty] | 221000000 | [24 empty] | 2010-01-01 | 2010-01-01
NA | [10 empty] | WOODWARD - WOODWARD EHV 138KV CKT 2 | U | OKGE | OKGE | ENID | ENID | 0 | 515376 |  | 514785 |  |  |  | 2 |  | 537 | 616 | [12 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | OKGE | WOODWARD - WOODWARD EHV 138KV CKT 2 | Build .5 miles of 138 kV and install terminal equipment | [12 empty] | 221000000 | [24 empty] | 2010-01-01 | 2010-01-01
NA | [10 empty] | WOODWARD 345/138KV TRANSFORMER CKT 1 | U | OKGE | OKGE | ENID | ENID | 1 | 515375 |  | 515376 |  | 515795 |  | 1 |  | 0 | 0 | [12 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | OKGE | WOODWARD 345/138KV TRANSFORMER CKT 1 | Install 345/138 kV XF | [12 empty] | 221000000 | [24 empty] | 2010-01-01 | 2010-01-01