## tblAllFacilityLog
STUDYDES | STUDYDES2 | EVENTTYPE | AssessmentSOLUTIONTYPE | AssessmenFDNS-TERMINATION | SOLUTIONTYPE | FDNS-TERMINATION | GROUP | SCENARIO | FGNAME | DIRECTION | FacilityName | FacilityUpgradeCode | ModelArea1 | ModelArea2 | FZONENAME | TZONENAME | MONTFLAG | MONTFB | MONTFNAME | MONTTB1 | MONTTNAME1 | MONTTB2 | MONTTNAME2 | MONTCKT | Case | SISRateA | SISRateB | STEPLoading | Assessment Loading | BaseCaseLoading | TransferCaseLoading | STEPVoltage | Assessment Voltage | BaseCaseVoltage | TransferCaseVoltage | VINIT | VMIN | VMAX | CATEGORY | CONTTYPE | CONTNAME | CONTXFMRFLAG | CONTFB | CONTFNAME | CONTTB1 | CONTTNAME1 | CONTTB2 | CONTTNAME2 | CONTCKT | RequiredRateB | TransmissionOwnerComments | OwnerDesignation | UpgradeName | UpgradeComponentWithinFacility | NewSummerA | NewSummerB | NewOtherA | NewOtherB | DistToConstruct | TotalLead | ConstructionLeadOnly | NewOrConstructWhileEnergized | NewR | NewX | NewB | CommentsRegardingUpgradeRequirements | NewCost | EffDate | NetPlantDate | ReusableEx_GrossValue | ReusableEx_NetValue | Reusable_EndofDepr | SalvageValue | NewCostWhileExpediting | EffDateExpedited | StartDeprExpedited | EndDeprExpedited | NetPlantDateExpedited | ReusableEx_GrossExpedited | ReusableEx_NetExpedited | Reusable_EndofDeprExpedited | SalvageValueExpedited | Generation 1 Owner & Unit (Name) | Generation 1 Redispatch Cost ($) | Generation 1 Redispatch Date (M/D/Y) | Generation 2 Owner & Unit (Name) | Generation 2 Redispatch Cost ($) | Generation 2 Redispatch Date (M/D/Y) | Generation 3 Owner & Unit (Name) | Generation 3 Redispatch Cost ($) | Generation 3 Redispatch Date (M/D/Y) | ActualCompletion | ActualNewCost | ActualNetPlantDate | ActualReusableEx_GrossValue | ActualReusableEx_NetValue | ActualReusable_EndofDepr | ActualSalvageValue | Actual_NewCostWhileExpediting | Actual_StartDeprExp | Actual_EndDeprExp | Actual_NetPlantDateExpedited | ActualReusableEx_GrossExpedited | ActualReusableEx_NetExpedited | ActualReusable_EndofDeprExpedited | Actual_SalvageValueExpedited | COD | EOC | EarliestDate
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31V8072209AP |  | WOODWARD NITROGEN 69KV | S | OKGE |  | ENID |  |  | 514779 | WDNITRO2 69.000 | [5 empty] | 09AP | [8 empty] | 1.0348 | 1.0591 | 1.0333 | 0.9 | 1.05 | CATEGORYB | GENOUT | GEN515364 1-CENT 11 0.6000 | 0 | 337909 | 8ANO 50 500.00 | 515305 | FTSMITH8 500.00 | 0 |  | 1 |  |  | OKGE | WOODWARD 138KV REACTOR | Install a reactor bank in the Woodward Area. | [12 empty] | 700000 | 2008-07-29 | [38 empty] | 2009-04-01 | 2011-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V1535509AP |  | WOODWARD 69KV | S | OKGE |  | ENID |  |  | 514782 | WODWRD 2 69.000 | [5 empty] | 09AP | [8 empty] | 1.0298 | 1.0502 | 1.0502 | 0.95 | 1.05 | CATEGORYA | BASECASE | BASE CASE | 1 | 514785 | WOODWRD4 138.00 | 514782 | WODWRD 2 69.000 | 515771 | WOODWR21 13.200 | 1 |  |  | OKGE | WOODWARD 138KV REACTOR | Install a reactor bank in the Woodward Area. | [12 empty] | 700000 | 2008-07-29 | [38 empty] | 2009-04-01 | 2011-06-01
NA | [8 empty] | NAOKGE5153755153765157951 |  | WOODWARD 345/138KV TRANSFORMER CKT 1 | U | OKGE | OKGE | ENID | ENID | 1 | 515375 |  | 515376 |  | 515795 |  | 1 |  | 0 | 0 | [12 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | OKGE | WOODWARD 345/138KV TRANSFORMER CKT 1 | Install 345/138 kV XF | [12 empty] | 221000000 | [39 empty] | 2010-01-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T472409AP | FROM->TO | WOODWARD (WOODWRD2) 138/69/13.2KV TRANSFORMER CKT 1 | PL | OKGE |  | ENID |  | 1 | 514785 | WOODWRD4 138.00 | 514782 | WODWRD 2 69.000 | 515771 | WOODWR21 13.200 | 1 | 09AP | 123 | 134 |  |  | 69.603 | 111.2275 | [7 empty] | CATEGORYB | SINGLE | FPL SWITCH - MOORELAND 138KV CKT 1 | 0 | 515785 | WINDFRM4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 149.0449 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T754409FA | FROM->TO | WOODWARD (WOODWRD2) 138/69/13.2KV TRANSFORMER CKT 1 | PL | OKGE |  | ENID |  | 1 | 514785 | WOODWRD4 138.00 | 514782 | WODWRD 2 69.000 | 515771 | WOODWR21 13.200 | 1 | 09FA | 123 | 134 |  |  | 77.2277 | 116.8011 | [7 empty] | CATEGORYB | SINGLE | FPL SWITCH - MOORELAND 138KV CKT 1 | 0 | 515785 | WINDFRM4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 156.5135 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T1112409G | FROM->TO | WOODWARD (WOODWRD2) 138/69/13.2KV TRANSFORMER CKT 1 | PL | OKGE |  | ENID |  | 1 | 514785 | WOODWRD4 138.00 | 514782 | WODWRD 2 69.000 | 515771 | WOODWR21 13.200 | 1 | 09G | 123 | 134 |  |  | 71.1363 | 111.1747 | [7 empty] | CATEGORYB | SINGLE | FPL SWITCH - MOORELAND 138KV CKT 1 | 0 | 515785 | WINDFRM4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 148.9741 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T892409SH | FROM->TO | WOODWARD (WOODWRD2) 138/69/13.2KV TRANSFORMER CKT 1 | PL | OKGE |  | ENID |  | 1 | 514785 | WOODWRD4 138.00 | 514782 | WODWRD 2 69.000 | 515771 | WOODWR21 13.200 | 1 | 09SH | 123 | 134 |  |  | 77.3534 | 117.1592 | [7 empty] | CATEGORYB | SINGLE | FPL SWITCH - MOORELAND 138KV CKT 1 | 0 | 515785 | WINDFRM4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 156.9933 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T1212409SP | FROM->TO | WOODWARD (WOODWRD2) 138/69/13.2KV TRANSFORMER CKT 1 | PL | OKGE |  | ENID |  | 1 | 514785 | WOODWRD4 138.00 | 514782 | WODWRD 2 69.000 | 515771 | WOODWR21 13.200 | 1 | 09SP | 123 | 134 |  |  | 79.2835 | 119.0602 | [7 empty] | CATEGORYB | SINGLE | FPL SWITCH - MOORELAND 138KV CKT 1 | 0 | 515785 | WINDFRM4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 159.5407 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T1154409WP | FROM->TO | WOODWARD (WOODWRD2) 138/69/13.2KV TRANSFORMER CKT 1 | PL | OKGE |  | ENID |  | 1 | 514785 | WOODWRD4 138.00 | 514782 | WODWRD 2 69.000 | 515771 | WOODWR21 13.200 | 1 | 09WP | 123 | 134 |  |  | 71.8198 | 112.0687 | [7 empty] | CATEGORYB | SINGLE | FPL SWITCH - MOORELAND 138KV CKT 1 | 0 | 515785 | WINDFRM4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 150.1721 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
NA | [8 empty] | NAOKGE5153765147852 |  | WOODWARD - WOODWARD EHV 138KV CKT 2 | U | OKGE | OKGE | ENID | ENID | 0 | 515376 |  | 514785 |  |  |  | 2 |  | 537 | 616 | [12 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | OKGE | WOODWARD - WOODWARD EHV 138KV CKT 2 | Build .5 miles of 138 kV and install terminal equipment | [12 empty] | 221000000 | [39 empty] | 2010-01-01 | 2010-01-01
NA | [8 empty] | NAOKGE5153765147851 |  | WOODWARD - WOODWARD EHV 138KV CKT 1 | U | OKGE | OKGE | ENID | ENID | 0 | 515376 |  | 514785 |  |  |  | 1 |  | 537 | 616 | [12 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | OKGE | WOODWARD - WOODWARD EHV 138KV CKT 1 | Build .5 miles of 138 kV and install terminal equipment | [12 empty] | 221000000 | [39 empty] | 2010-01-01 | 2010-01-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T442409AP | TO->FROM | WOODWARD - WOODWARD 69KV CKT 1 | PL | OKGE | WFEC | ENID | AEP-OP | 0 | 514782 | WODWRD 2 69.000 | 521096 | WOODWRD2 69.000 | 0 |  | 1 | 09AP | 53 | 65 | 124.9 | 122.4 | 120.489 | 205.7319 | [7 empty] | CATEGORYB | SINGLE | FPL SWITCH - MOORELAND 138KV CKT 1 | 0 | 515785 | WINDFRM4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 133.7257 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T182209AP | TO->FROM | WOODWARD - WOODWARD 69KV CKT 1 | PL | OKGE | WFEC | ENID | AEP-OP | 0 | 514782 | WODWRD 2 69.000 | 521096 | WOODWRD2 69.000 | 0 |  | 1 | 09AP | 53 | 65 |  |  | 68.6375 | 145.2943 | [7 empty] | CATEGORYB | SINGLE | FPL SWITCH - WOODWARD 138KV CKT 1 | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 94.4413 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T734409FA | TO->FROM | WOODWARD - WOODWARD 69KV CKT 1 | PL | OKGE | WFEC | ENID | AEP-OP | 0 | 514782 | WODWRD 2 69.000 | 521096 | WOODWRD2 69.000 | 0 |  | 1 | 09FA | 91 | 110 |  |  | 63.6313 | 112.3889 | [7 empty] | CATEGORYB | SINGLE | FPL SWITCH - MOORELAND 138KV CKT 1 | 0 | 515785 | WINDFRM4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 123.6278 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T1082409G | TO->FROM | WOODWARD - WOODWARD 69KV CKT 1 | PL | OKGE | WFEC | ENID | AEP-OP | 0 | 514782 | WODWRD 2 69.000 | 521096 | WOODWRD2 69.000 | 0 |  | 1 | 09G | 53 | 65 | 103.7 | 101.1 | 99.9361 | 182.8118 | [7 empty] | CATEGORYB | SINGLE | FPL SWITCH - MOORELAND 138KV CKT 1 | 0 | 515785 | WINDFRM4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 118.8277 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T405509G | TO->FROM | WOODWARD - WOODWARD 69KV CKT 1 | PL | OKGE | WFEC | ENID | AEP-OP | 0 | 514782 | WODWRD 2 69.000 | 521096 | WOODWRD2 69.000 | 0 |  | 1 | 09G | 53 | 65 |  |  | 58.6341 | 133.0243 | [7 empty] | CATEGORYB | SINGLE | FPL SWITCH - WOODWARD 138KV CKT 1 | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 86.4658 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T862409SH | TO->FROM | WOODWARD - WOODWARD 69KV CKT 1 | PL | OKGE | WFEC | ENID | AEP-OP | 0 | 514782 | WODWRD 2 69.000 | 521096 | WOODWRD2 69.000 | 0 |  | 1 | 09SH | 91 | 110 |  |  | 51.717 | 100.8452 | [7 empty] | CATEGORYB | SINGLE | FPL SWITCH - MOORELAND 138KV CKT 1 | 0 | 515785 | WINDFRM4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 110.9297 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T1124409WP | TO->FROM | WOODWARD - WOODWARD 69KV CKT 1 | PL | OKGE | WFEC | ENID | AEP-OP | 0 | 514782 | WODWRD 2 69.000 | 521096 | WOODWRD2 69.000 | 0 |  | 1 | 09WP | 91 | 110 |  |  | 54.1925 | 104.7021 | [7 empty] | CATEGORYB | SINGLE | FPL SWITCH - MOORELAND 138KV CKT 1 | 0 | 515785 | WINDFRM4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 115.1723 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
NA | [8 empty] | NAOKGE5153765147961 |  | WOODWARD - IODINE 138KV CKT 1 | U | OKGE | OKGE | ENID | ENID | 0 | 515376 |  | 514796 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | OKGE | WOODWARD - IODINE 138KV CKT 1 | Tap Iodine to Woodward 138 kV line | [12 empty] | 221000000 | [39 empty] | 2010-01-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 1 | 2008AGP1AFS31T2553113SP | FROM->TO | WOLFFORTH INTERCHANGE - YUMA INTERCHANGE 115KV CKT 1 | S | SPS | SPS | SPS-CNPL | SPS-CNPL | 0 | 526524 | WOLFRTH3 115.00 | 526475 | YUMA_INTG 3 115.00 | 0 |  | 1 | 13SP | 139 | 160 |  |  | 95.8571 | 101.2933 | [7 empty] | CATEGORYB | SINGLE | TOLK STATION EAST - TUCO INTERCHANGE 230KV CKT 1 | 0 | 525524 | TOLK_EAST 6 230.00 | 525830 | TUCO_INT 6 230.00 | 0 |  | 1 | 162.0693 |  | SPS | SOUTH PLAINS REC-YUMA - WOLFFORTH INTERCHANGE 115KV CKT 1 | Replace Terminal Equipment | 179 | 197 | [9 empty] | 225k per Wavetrap | 225000 | 2008-01-01 | [38 empty] | 2012-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 1 | 2008AGP1AFS31T2583113SP | FROM->TO | WOLFFORTH INTERCHANGE - YUMA INTERCHANGE 115KV CKT 1 | S | SPS | SPS | SPS-CNPL | SPS-CNPL | 0 | 526524 | WOLFRTH3 115.00 | 526475 | YUMA_INTG 3 115.00 | 0 |  | 1 | 13SP | 139 | 160 |  |  | 94.4933 | 100.5961 | [7 empty] | CATEGORYB | SINGLE | LUBBOCK SOUTH INTERCHANGE - WOLFFORTH INTERCHANGE 230KV CKT 1 | 0 | 526269 | LUBBCK_STH6 230.00 | 526525 | WOLFRTH6 230.00 | 0 |  | 1 | 160.9538 |  | SPS | SOUTH PLAINS REC-YUMA - WOLFFORTH INTERCHANGE 115KV CKT 1 | Replace Terminal Equipment | 179 | 197 | [9 empty] | 225k per Wavetrap | 225000 | 2008-01-01 | [38 empty] | 2012-06-01 | 2012-06-01
2008-AGP1 | AFS3 | CONT-0633 - East Manhattan 230-115kV XFMR | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17583318SP |  | WILDCAT CREEK 115KV | REL | WERE |  | NCENTRAL |  |  | 533345 | WILDCAT3 115.00 | [5 empty] | 18SP | [6 empty] | 0.91542 | 0.90566 | 0.90146 | 0.85038 | 0.99406 | 0.93 | 1.05 | CATEGORYB | SINGLE | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
NA | [8 empty] | NAWERE5327965327711 |  | WICHITA - RENO 345KV | U | WERE | WERE |  |  | 0 | 532796 | WICHITA7 345.0 | 532771 | RENO 7 345.00 |  |  | 1 | [15 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WERE | WICHITA - RENO 345KV | 40 mile 345 kV transmission line from existing Wichita 345 kV substation to a new 345-115 kV substation in Reno County east northeast of Hutchinson (Wichita to Reno) | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 2 | 2008AGP1AFS31V9173213SP |  | WEST JUNCTION CITY JUNCTION (WEST) 115KV | REL | WERE |  | NCENTRAL |  |  | 533344 | WJCCTYW3 115.00 | [5 empty] | 13SP | [8 empty] | 0.94322 | 0.92292 | 0.96467 | 0.93 | 1.05 | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 | CONT-0633 - East Manhattan 230-115kV XFMR | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17573318SP |  | WEST JUNCTION CITY JUNCTION (WEST) 115KV | REL | WERE |  | NCENTRAL |  |  | 533344 | WJCCTYW3 115.00 | [5 empty] | 18SP | [6 empty] | 0.92684 | 0.91575 | 0.89878 | 0.84993 | 0.95425 | 0.93 | 1.05 | CATEGORYB | SINGLE | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17713318SP |  | WEST JUNCTION CITY JUNCTION (WEST) 115KV | REL | WERE |  | NCENTRAL |  |  | 533344 | WJCCTYW3 115.00 | [5 empty] | 18SP | [8 empty] | 0.94165 | 0.9006 | 0.95425 | 0.93 | 1.05 | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 2 | 2008AGP1AFS31V9163213SP |  | WEST JUNCTION CITY JUNCTION (EAST) 115KV | REL | WERE |  | NCENTRAL |  |  | 533343 | WJCCTYE3 115.00 | [5 empty] | 13SP | [8 empty] | 0.9434 | 0.92313 | 0.96508 | 0.93 | 1.05 | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 | CONT-0633 - East Manhattan 230-115kV XFMR | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17563318SP |  | WEST JUNCTION CITY JUNCTION (EAST) 115KV | REL | WERE |  | NCENTRAL |  |  | 533343 | WJCCTYE3 115.00 | [5 empty] | 18SP | [6 empty] | 0.92652 | 0.91547 | 0.89884 | 0.85 | 0.95464 | 0.93 | 1.05 | CATEGORYB | SINGLE | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17703318SP |  | WEST JUNCTION CITY JUNCTION (EAST) 115KV | REL | WERE |  | NCENTRAL |  |  | 533343 | WJCCTYE3 115.00 | [5 empty] | 18SP | [8 empty] | 0.94181 | 0.90077 | 0.95464 | 0.93 | 1.05 | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 2 | 2008AGP1AFS31V9153213SP |  | WEST JUNCTION CITY 115KV | REL | WERE |  | NCENTRAL |  |  | 533342 | WJCCTY 3 115.00 | [5 empty] | 13SP | [8 empty] | 0.94325 | 0.92296 | 0.96486 | 0.93 | 1.05 | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 | CONT-0633 - East Manhattan 230-115kV XFMR | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17553318SP |  | WEST JUNCTION CITY 115KV | REL | WERE |  | NCENTRAL |  |  | 533342 | WJCCTY 3 115.00 | [5 empty] | 18SP | [6 empty] | 0.92648 | 0.91542 | 0.8987 | 0.84983 | 0.95441 | 0.93 | 1.05 | CATEGORYB | SINGLE | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17693318SP |  | WEST JUNCTION CITY 115KV | REL | WERE |  | NCENTRAL |  |  | 533342 | WJCCTY 3 115.00 | [5 empty] | 18SP | [8 empty] | 0.94165 | 0.90059 | 0.95441 | 0.93 | 1.05 | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T3752210SP | TO->FROM | WEST JUNCTION CITY - WEST JUNCTION CITY JUNCTION (EAST) 115KV CKT 1 | EXP | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533343 | WJCCTYE3 115.00 | 533342 | WJCCTY 3 115.00 | 0 |  | 1 | 10SP | 179 | 194 |  |  | 96.8173 | 101.0604 | [7 empty] | CATEGORYB | SINGLE | FORT JUNCTION SWITCHING STATION - JUNCTION CITY 115KV CKT 1 | 0 | 533328 | FT JCT 3 115.00 | 533330 | JCTCTY 3 115.00 | 0 |  | 1 | 196.0572 |  | WERE | FORT JUNCTION SWITCHING STATION - WEST JUNCTION CITY JUNCTION 115KV CKT 1 | Build new Ft Jct. - W. Jct City line that follows the path of the JEC - Summit 345kV. Remove old double circuit and WJCTYE - WJCTCTY 115 kV | [52 empty] | 2010-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T4672213SP | TO->FROM | WEST JUNCTION CITY - WEST JUNCTION CITY JUNCTION (EAST) 115KV CKT 1 | EXP | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533343 | WJCCTYE3 115.00 | 533342 | WJCCTY 3 115.00 | 0 |  | 1 | 13SP | 179 | 194 |  |  | 99.3143 | 103.7726 | [7 empty] | CATEGORYB | SINGLE | FORT JUNCTION SWITCHING STATION - JUNCTION CITY 115KV CKT 1 | 0 | 533328 | FT JCT 3 115.00 | 533330 | JCTCTY 3 115.00 | 0 |  | 1 | 201.3188 |  | WERE | FORT JUNCTION SWITCHING STATION - WEST JUNCTION CITY JUNCTION 115KV CKT 1 | Build new Ft Jct. - W. Jct City line that follows the path of the JEC - Summit 345kV. Remove old double circuit and WJCTYE - WJCTCTY 115 kV | [52 empty] | 2010-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T1892209AP | FROM->TO | WELLS 500/230KV TRANSFORMER CKT 1 | S | EES | CELE | EES_GSU-LA | CLE_CENTRAL | 0 | 335368 | 8WELLS 500.00 | 500950 | WELSRCT6 230.00 | 0 |  | 1 | 09AP | 560 | 560 |  |  | 96.587 | 100.6151 | [7 empty] | CATEGORYB | NONSINGLE | SERCW-21 | 0 | 0 |  | 0 |  | 0 |  |  | 563.4445 |  | EES | WELLS 500/230KV TRANSFORMER CKT 1 | Replace transformer | [12 empty] | 9000000 | [39 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T5252209FA | FROM->TO | WELLS 500/230KV TRANSFORMER CKT 1 | S | EES | CELE | EES_GSU-LA | CLE_CENTRAL | 0 | 335368 | 8WELLS 500.00 | 500950 | WELSRCT6 230.00 | 0 |  | 1 | 09FA | 560 | 560 | 113.8 | 110.5 | 120.9251 | 126.4883 | [7 empty] | CATEGORYB | NONSINGLE | SERCW-21 | 0 | 0 |  | 0 |  | 0 |  |  | 708.3345 |  | EES | WELLS 500/230KV TRANSFORMER CKT 1 | Replace transformer | [12 empty] | 9000000 | [39 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 2 | 2008AGP1AFS31T7863209SH | FROM->TO | WELLS 500/230KV TRANSFORMER CKT 1 | S | EES | CELE | EES_GSU-LA | CLE_CENTRAL | 0 | 335368 | 8WELLS 500.00 | 500950 | WELSRCT6 230.00 | 0 |  | 1 | 09SH | 560 | 560 |  |  | 101.2563 | 105.5196 | [7 empty] | CATEGORYB | NONSINGLE | SERCW-21 | 0 | 0 |  | 0 |  | 0 |  |  | 590.9098 |  | EES | WELLS 500/230KV TRANSFORMER CKT 1 | Replace transformer | [12 empty] | 9000000 | [39 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FNSL | FDNS-Iteration limit exceeded | FDNS |  | 2 | 2 | 2008AGP1AFS31T12692209SP | FROM->TO | WELLS 500/230KV TRANSFORMER CKT 1 | S | EES | CELE | EES_GSU-LA | CLE_CENTRAL | 0 | 335368 | 8WELLS 500.00 | 500950 | WELSRCT6 230.00 | 0 |  | 1 | 09SP | 560 | 560 | 142.7 | 139.9 | 150.8645 | 157.6743 | [7 empty] | CATEGORYB | NONSINGLE | SERCW-21 | 0 | 0 |  | 0 |  | 0 |  |  | 882.9761 |  | EES | WELLS 500/230KV TRANSFORMER CKT 1 | Replace transformer | [12 empty] | 9000000 | [39 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T6793309WP | FROM->TO | WELLS 500/230KV TRANSFORMER CKT 1 | S | EES | CELE | EES_GSU-LA | CLE_CENTRAL | 0 | 335368 | 8WELLS 500.00 | 500950 | WELSRCT6 230.00 | 0 |  | 1 | 09WP | 560 | 560 | 101.3 |  | 93.904 | 100.2645 | [7 empty] | CATEGORYB | NONSINGLE | SERCW-21 | 0 | 0 |  | 0 |  | 0 |  |  | 561.4812 |  | EES | WELLS 500/230KV TRANSFORMER CKT 1 | Replace transformer | [12 empty] | 9000000 | [39 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 2 | 2008AGP1AFS31T13221210SP | FROM->TO | WELLS 500/230KV TRANSFORMER CKT 1 | S | EES | CELE | EES_GSU-LA | CLE_CENTRAL | 0 | 335368 | 8WELLS 500.00 | 500950 | WELSRCT6 230.00 | 0 |  | 1 | 10SP | 560 | 560 | 142.1 | 135.3 | 144.4678 | 159.3208 | [7 empty] | CATEGORYB | NONSINGLE | SERCW-21 | 0 | 0 |  | 0 |  | 0 |  |  | 892.1965 |  | EES | WELLS 500/230KV TRANSFORMER CKT 1 | Replace transformer | [12 empty] | 9000000 | [39 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 2 | 2008AGP1AFS31T19401213SP | FROM->TO | WELLS 500/230KV TRANSFORMER CKT 1 | S | EES | CELE | EES_GSU-LA | CLE_CENTRAL | 0 | 335368 | 8WELLS 500.00 | 500950 | WELSRCT6 230.00 | 0 |  | 1 | 13SP | 560 | 560 | 164.9 | 157.6 | 168.1167 | 181.9443 | [7 empty] | CATEGORYB | NONSINGLE | SERCW-21 | 0 | 0 |  | 0 |  | 0 |  |  | 1018.8881 |  | EES | WELLS 500/230KV TRANSFORMER CKT 1 | Replace transformer | [12 empty] | 9000000 | [39 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 2 | 2008AGP1AFS31T8951213WP | FROM->TO | WELLS 500/230KV TRANSFORMER CKT 1 | S | EES | CELE | EES_GSU-LA | CLE_CENTRAL | 0 | 335368 | 8WELLS 500.00 | 500950 | WELSRCT6 230.00 | 0 |  | 1 | 13WP | 560 | 560 | 108.1 |  | 107.3323 | 118.8349 | [7 empty] | CATEGORYB | NONSINGLE | SERCW-21 | 0 | 0 |  | 0 |  | 0 |  |  | 665.4754 |  | EES | WELLS 500/230KV TRANSFORMER CKT 1 | Replace transformer | [12 empty] | 9000000 | [39 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 2 | 2008AGP1AFS31T36701218SP | FROM->TO | WELLS 500/230KV TRANSFORMER CKT 1 | S | EES | CELE | EES_GSU-LA | CLE_CENTRAL | 0 | 335368 | 8WELLS 500.00 | 500950 | WELSRCT6 230.00 | 0 |  | 1 | 18SP | 560 | 560 | 178.6 | 159.5 | 168.9695 | 179.6396 | [7 empty] | CATEGORYB | NONSINGLE | SERCW-21 | 0 | 0 |  | 0 |  | 0 |  |  | 1005.9818 |  | EES | WELLS 500/230KV TRANSFORMER CKT 1 | Replace transformer | [12 empty] | 9000000 | [39 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 2 | 2008AGP1AFS31T19311213SP | FROM->TO | WELLS - WELLS 230KV CKT 1 | S | CELE | CELE | CLE_CENTRAL | CLE_CENTRAL | 0 | 500950 | WELSRCT6 230.00 | 500940 | WELLS 6 230.00 | 0 |  | 1 | 13SP | 1000 | 1000 |  |  | 95.573 | 103.9652 | [7 empty] | CATEGORYB | NONSINGLE | SERCW-21 | 0 | 0 |  | 0 |  | 0 |  |  | 1039.652 |  | CELE | WELLS - WELLS 230KV CKT 1 | Indeterminate | [52 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 2 | 2008AGP1AFS31T36571218SP | FROM->TO | WELLS - WELLS 230KV CKT 1 | S | CELE | CELE | CLE_CENTRAL | CLE_CENTRAL | 0 | 500950 | WELSRCT6 230.00 | 500940 | WELLS 6 230.00 | 0 |  | 1 | 18SP | 1000 | 1000 | 101.5 |  | 95.8455 | 102.2575 | [7 empty] | CATEGORYB | NONSINGLE | SERCW-21 | 0 | 0 |  | 0 |  | 0 |  |  | 1022.575 |  | CELE | WELLS - WELLS 230KV CKT 1 | Indeterminate | [52 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V3315509SP |  | WARE 69KV | EXP | WERE |  | SEAST |  |  | 533652 | WARE 2 69.000 | [5 empty] | 09SP | [6 empty] | 0.86414 | 0.86316 | 0.89647 | 0.85384 | 0.99266 | 0.93 | 1.05 | CATEGORYB | SINGLE | LITCHFIELD - PITNAC 69KV CKT 1 | 0 | 533765 | LITCH 2 69.000 | 533769 | PITNAC 2 69.000 | 0 |  | 1 |  |  | WERE | Fort Scott 161/69kV Transformer CKT 1 | New 161/69 kV transformer at Ft Scott. | 100 | 110 |  |  |  | 18 | 18 | [5 empty] | 1400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V3515509SP |  | WALDO 115KV | EXP | MKEC |  |  |  |  | 539698 | WALDO 3 115.00 | [5 empty] | 09SP | [8 empty] | 0.90823 | 0.8767 | 0.96257 | 0.9 | 1.05 | CATEGORYB | SINGLE | CONCORDIA - ELMCREK6 230.00 230KV CKT 1 | 0 | 539639 | ELMCREK6 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V7355509SP |  | WALDO 115KV | EXP | MKEC |  |  |  |  | 539698 | WALDO 3 115.00 | [5 empty] | 09SP | [8 empty] | 0.90826 | 0.87674 | 0.96257 | 0.9 | 1.05 | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539658 | CONCRD6 230.00 | 539657 | CONCORD3 115.00 | 539904 | CONCOD-T 13.800 | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FNSL | FDNS-Iteration limit exceeded | 3 | 2 | 2008AGP1AFS32V113213SP |  | WALDO 115KV | EXP | MKEC |  |  |  |  | 539698 | WALDO 3 115.00 | [5 empty] | 13SP | [8 empty] | 0.97727 | 0.88597 | 0.9769 | 0.9 | 1.05 | CATEGORYB | SINGLE | EAST MANHATTAN - ELMCREK6 230.00 230KV CKT 1 | 0 | 539639 | ELMCREK6 230.00 | 532861 | EMANHAT6 230.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
GEN-2006-010 | Turk | [7 empty] | 509416507454012SP | FROM->TO | TURK 138/24.0KV TRANSFORMER CKT 1 | U | AEPW | AEPW | SARK | SARK | 0 | 509416 | TURKCOAL 24.000 | 507454 | HEMPSTD4 138.00 | 0 |  | 1 |  | 750 | 750 |  |  | 618 | [9 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | AEPW | TURK 138/24.0KV TRANSFORMER CKT 1 | Install a GSU transformer at Turk | [11 empty] | 0 | 0 | [39 empty] | 2012-07-01 | 2012-07-01
GEN-2006-010 | Turk | [7 empty] | 50745650745450745912SP | FROM->TO | TURK (HEMP 2) 138/115/13.8KV TRANSFORMER CKT 2 | U | AEPW |  | SARK |  | 1 | 507456 | HEMPSTD3 115.00 | 507454 | HEMPSTD4 138.00 | 507459 | HEMP2 1 13.800 | 2 |  | 147 | 170 |  |  | 0 | [9 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | AEPW | TURK (HEMP 2) 138/115/13.8KV TRANSFORMER CKT 2 | Relocate autotransformer from Patterson to this new Turk substation | [11 empty] | 0 | 0 | [39 empty] | 2012-07-01 | 2012-07-01
GEN-2006-010 | Turk | [7 empty] | 50745450745650745812SP | FROM->TO | TURK (HEMP 1) 138/115/13.8KV TRANSFORMER CKT 1 | U | AEPW |  | SARK |  | 1 | 507454 | HEMPSTD4 138.00 | 507456 | HEMPSTD3 115.00 | 507458 | HEMP1 1 13.800 | 1 |  | 175 | 234 |  |  | 109.4 | [9 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | AEPW | TURK (HEMP 1) 138/115/13.8KV TRANSFORMER CKT 1 | Build Turk 138-115 kV station and relocate autotransformer (and spare) from Patterson to this new Turk station | [11 empty] | 9110000 | 9110000 | [39 empty] | 2012-07-01 | 2012-07-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V1555509SH |  | TRANSCA3 115.00 115KV | EXP | WERE |  | NCENTRAL |  |  | 533348 | TRANSCA3 115.00 | [5 empty] | 09SH | [6 empty] | 0.79988 | 0.77079 | 0.80065 | 0.68931 | 0.9986 | 0.93 | 1.05 | CATEGORYB | SINGLE | KELLY - SOUTH SENECA 115KV CKT 1 | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 |  |  |  | 2009-04-01 | 2009-04-01 | 2009-04-01 | 41640 | 41640 | 1 | 1 | 2014 | 41897 | 42156 | 40179 | 41640 | 2014-01-01 | 2010-06-01 | [13 empty] | Ph1: 10.8 Mvar cap bank at Seneca 115 kV 09S. Ph2: Knob Hill -S. Beatrice 115 kV 10S | [7 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 3 | 2008AGP1AFS31V2871309SP |  | TRANSCA3 115.00 115KV | EXP | WERE |  | NCENTRAL |  |  | 533348 | TRANSCA3 115.00 | [5 empty] | 09SP | [6 empty] | 0.8129 | 0.63079 | 0.8198 | 0.41536 | 0.99776 | 0.93 | 1.05 | CATEGORYB | SINGLE | KELLY - SOUTH SENECA 115KV CKT 1 | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 |  |  |  | 2009-04-01 | 2009-04-01 | 2009-04-01 | 41640 | 41640 | 1 | 1 | 2014 | 41897 | 42156 | 40179 | 41640 | 2014-01-01 | 2010-06-01 | [13 empty] | Ph1: 10.8 Mvar cap bank at Seneca 115 kV 09S. Ph2: Knob Hill -S. Beatrice 115 kV 10S | [7 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 2 | 2008AGP1AFS31V3631209SP |  | TRANSCA3 115.00 115KV | EXP | WERE |  | NCENTRAL |  |  | 533348 | TRANSCA3 115.00 | [5 empty] | 09SP | [8 empty] | 0.99973 | 0.92313 | 1.0036 | 0.93 | 1.05 | CATEGORYB | SINGLE | CONCORDIA - ELMCREK6 230.00 230KV CKT 1 | 0 | 539639 | ELMCREK6 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 1 | 2 | 2008AGP1AFS31V7681209SP |  | TRANSCA3 115.00 115KV | EXP | WERE |  | NCENTRAL |  |  | 533348 | TRANSCA3 115.00 | [5 empty] | 09SP | [8 empty] | 0.99984 | 0.9233 | 1.0036 | 0.93 | 1.05 | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539658 | CONCRD6 230.00 | 539657 | CONCORD3 115.00 | 539904 | CONCOD-T 13.800 | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 1 | 2008AGP1AFS31T481109SP | TO->FROM | TEXAS EASTMAN - WHITNEY 138KV CKT 1 | REL | AEPW | AEPW | LONG-MAR | LONG-MAR | 0 | 508575 | WHITNEY4 138.00 | 508582 | EASTEX 4 138.00 | 0 |  | 1 | 09SP | 235 | 272 |  | 101.5 | 101.3143 | 101.9876 | [7 empty] | CATEGORYB | SINGLE | EASTON REC - PIRKEY 138KV CKT 1 | 0 | 508562 | PIRKEY 4 138.00 | 509092 | EASTON 4 138.00 | 0 |  | 1 | 277.4063 |  | AEPW | TEXAS EASTMAN - WHITNEY 138KV CKT 1 | Rebuild 2.49 miles with 1590 ACSR. Replace wavetrap & jumpers @ Whitney. Replace metering CT @ Texas Eastman | 320 | 380 | 379 | 429 | 2.49 | 18 | 6 |  | 0.00117 | 0.01147 | 0.00404 | New limits will be jumpers | 2800000 | 2008-07-30 | [38 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 1 | 2008AGP1AFS31T471109SP | TO->FROM | TEXAS EASTMAN - WHITNEY 138KV CKT 1 | REL | AEPW | AEPW | LONG-MAR | LONG-MAR | 0 | 508575 | WHITNEY4 138.00 | 508582 | EASTEX 4 138.00 | 0 |  | 1 | 09SP | 235 | 272 |  |  | 99.6949 | 100.3504 | [7 empty] | CATEGORYB | SINGLE | EASTON REC - KNOX LEE 138KV CKT 1 | 0 | 508548 | KNOXLEE4 138.00 | 509092 | EASTON 4 138.00 | 0 |  | 1 | 272.9531 |  | AEPW | TEXAS EASTMAN - WHITNEY 138KV CKT 1 | Rebuild 2.49 miles with 1590 ACSR. Replace wavetrap & jumpers @ Whitney. Replace metering CT @ Texas Eastman | 320 | 380 | 379 | 429 | 2.49 | 18 | 6 |  | 0.00117 | 0.01147 | 0.00404 | New limits will be jumpers | 2800000 | 2008-07-30 | [38 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 1 | 2008AGP1AFS31T1021113SP | TO->FROM | TEXAS EASTMAN - WHITNEY 138KV CKT 1 | REL | AEPW | AEPW | LONG-MAR | LONG-MAR | 0 | 508575 | WHITNEY4 138.00 | 508582 | EASTEX 4 138.00 | 0 |  | 1 | 13SP | 235 | 272 |  |  | 70.7562 | 106.9258 | [7 empty] | CATEGORYB | SINGLE | EASTON REC - PIRKEY 138KV CKT 1 | 0 | 508562 | PIRKEY 4 138.00 | 509092 | EASTON 4 138.00 | 0 |  | 1 | 290.8382 |  | AEPW | TEXAS EASTMAN - WHITNEY 138KV CKT 1 | Rebuild 2.49 miles with 1590 ACSR. Replace wavetrap & jumpers @ Whitney. Replace metering CT @ Texas Eastman | 320 | 380 | 379 | 429 | 2.49 | 18 | 6 |  | 0.00117 | 0.01147 | 0.00404 | New limits will be jumpers | 2800000 | 2008-07-30 | [38 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 1 | 2008AGP1AFS31T1011113SP | TO->FROM | TEXAS EASTMAN - WHITNEY 138KV CKT 1 | REL | AEPW | AEPW | LONG-MAR | LONG-MAR | 0 | 508575 | WHITNEY4 138.00 | 508582 | EASTEX 4 138.00 | 0 |  | 1 | 13SP | 235 | 272 |  |  | 68.945 | 105.089 | [7 empty] | CATEGORYB | SINGLE | EASTON REC - KNOX LEE 138KV CKT 1 | 0 | 508548 | KNOXLEE4 138.00 | 509092 | EASTON 4 138.00 | 0 |  | 1 | 285.8421 |  | AEPW | TEXAS EASTMAN - WHITNEY 138KV CKT 1 | Rebuild 2.49 miles with 1590 ACSR. Replace wavetrap & jumpers @ Whitney. Replace metering CT @ Texas Eastman | 320 | 380 | 379 | 429 | 2.49 | 18 | 6 |  | 0.00117 | 0.01147 | 0.00404 | New limits will be jumpers | 2800000 | 2008-07-30 | [38 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T2714413SP | FROM->TO | TECUMSEH ENERGY CENTER - TECUMSEH HILL 115KV CKT 1 | REL | WERE | WERE | NEAST | NEAST | 0 | 533180 | TEC E 3 115.00 | 533182 | TECHILE3 115.00 | 0 |  | 1 | 13SP | 236 | 236 |  | 102.6 | 102.2689 | 102.7626 | [7 empty] | CATEGORYB | SINGLE | SWISSVALE - TECUMSEH HILL 230KV CKT 1 | 0 | 532856 | SWISVAL6 230.00 | 532857 | TECHILL6 230.00 | 0 |  | 1 | 242.5197 |  | WERE | TECUMSEH ENERGY CENTER - TECUMSEH HILL 115KV CKT 1 | Uprate 0.24 mile TEC-Tecumseh Hill 115 kV line to 100 degree operation. | 236 | 250 | 236 | 250 | 0.24 | 10 | 2 | [5 empty] | 80000 | 2006-07-25 | [38 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T11694413SP | FROM->TO | TECUMSEH ENERGY CENTER - TECUMSEH HILL 115KV CKT 1 | REL | WERE | WERE | NEAST | NEAST | 0 | 533180 | TEC E 3 115.00 | 533182 | TECHILE3 115.00 | 0 |  | 1 | 13SP | 236 | 236 |  | 102.5 | 102.1725 | 102.6662 | [7 empty] | CATEGORYB | SINGLE | TECUMSEH HILL (TECH194X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532857 | TECHILL6 230.00 | 533182 | TECHILE3 115.00 | 532886 | TECHILL1 13.800 | 1 | 242.2922 |  | WERE | TECUMSEH ENERGY CENTER - TECUMSEH HILL 115KV CKT 1 | Uprate 0.24 mile TEC-Tecumseh Hill 115 kV line to 100 degree operation. | 236 | 250 | 236 | 250 | 0.24 | 10 | 2 | [5 empty] | 80000 | 2006-07-25 | [38 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T5715518SP | FROM->TO | TECUMSEH ENERGY CENTER - TECUMSEH HILL 115KV CKT 1 | REL | WERE | WERE | NEAST | NEAST | 0 | 533180 | TEC E 3 115.00 | 533182 | TECHILE3 115.00 | 0 |  | 1 | 18SP | 236 | 236 | 104.8 | 105.9 | 101.2228 | 105.3884 | [7 empty] | CATEGORYB | SINGLE | SWISSVALE - TECUMSEH HILL 230KV CKT 1 | 0 | 532856 | SWISVAL6 230.00 | 532857 | TECHILL6 230.00 | 0 |  | 1 | 248.7166 |  | WERE | TECUMSEH ENERGY CENTER - TECUMSEH HILL 115KV CKT 1 | Uprate 0.24 mile TEC-Tecumseh Hill 115 kV line to 100 degree operation. | 236 | 250 | 236 | 250 | 0.24 | 10 | 2 | [5 empty] | 80000 | 2006-07-25 | [38 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T23685518SP | FROM->TO | TECUMSEH ENERGY CENTER - TECUMSEH HILL 115KV CKT 1 | REL | WERE | WERE | NEAST | NEAST | 0 | 533180 | TEC E 3 115.00 | 533182 | TECHILE3 115.00 | 0 |  | 1 | 18SP | 236 | 236 | 104.7 | 105.8 | 101.1138 | 105.2769 | [7 empty] | CATEGORYB | SINGLE | TECUMSEH HILL (TECH194X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532857 | TECHILL6 230.00 | 533182 | TECHILE3 115.00 | 532886 | TECHILL1 13.800 | 1 | 248.4535 |  | WERE | TECUMSEH ENERGY CENTER - TECUMSEH HILL 115KV CKT 1 | Uprate 0.24 mile TEC-Tecumseh Hill 115 kV line to 100 degree operation. | 236 | 250 | 236 | 250 | 0.24 | 10 | 2 | [5 empty] | 80000 | 2006-07-25 | [38 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31V8032209AP |  | TANGIER 69KV | S | OKGE |  | ENID |  |  | 514771 | TANGIER2 69.000 | [5 empty] | 09AP | [8 empty] | 1.0349 | 1.0592 | 1.0335 | 0.9 | 1.05 | CATEGORYB | GENOUT | GEN515364 1-CENT 11 0.6000 | 0 | 337909 | 8ANO 50 500.00 | 515305 | FTSMITH8 500.00 | 0 |  | 1 |  |  | OKGE | WOODWARD 138KV REACTOR | Install a reactor bank in the Woodward Area. | [12 empty] | 700000 | 2008-07-29 | [38 empty] | 2009-04-01 | 2011-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T934409G | FROM->TO | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | PL | WFEC |  | AEP-OP |  | 1 | 521065 | TALOGA 4 138.00 | 521064 | TALOGA 2 69.000 | 521178 | TLGTERT 13.800 | 1 | 09G | 56 | 56 |  |  | 86.9195 | 107.2368 | [7 empty] | CATEGORYB | SINGLE | DEWEY - SOUTHARD 138KV CKT 1 | 0 | 514787 | DEWEY 4 138.00 | 514822 | SOUTHRD4 138.00 | 0 |  | 1 | 60.0526 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T1054409G | FROM->TO | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | PL | WFEC |  | AEP-OP |  | 1 | 521065 | TALOGA 4 138.00 | 521064 | TALOGA 2 69.000 | 521178 | TLGTERT 13.800 | 1 | 09G | 56 | 56 |  |  | 81.7036 | 101.8837 | [7 empty] | CATEGORYB | SINGLE | ROMAN NOSE - SOUTHARD 138KV CKT 1 | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 57.0549 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T1034409SP | FROM->TO | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | PL | WFEC |  | AEP-OP |  | 1 | 521065 | TALOGA 4 138.00 | 521064 | TALOGA 2 69.000 | 521178 | TLGTERT 13.800 | 1 | 09SP | 56 | 56 |  |  | 85.4171 | 105.8372 | [7 empty] | CATEGORYB | SINGLE | DEWEY - SOUTHARD 138KV CKT 1 | 0 | 514787 | DEWEY 4 138.00 | 514822 | SOUTHRD4 138.00 | 0 |  | 1 | 59.2688 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T922409WP | FROM->TO | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | PL | WFEC |  | AEP-OP |  | 1 | 521065 | TALOGA 4 138.00 | 521064 | TALOGA 2 69.000 | 521178 | TLGTERT 13.800 | 1 | 09WP | 56 | 56 |  |  | 95.8485 | 114.219 | [7 empty] | CATEGORYB | SINGLE | DEWEY - SOUTHARD 138KV CKT 1 | 0 | 514787 | DEWEY 4 138.00 | 514822 | SOUTHRD4 138.00 | 0 |  | 1 | 63.9626 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T1092409WP | FROM->TO | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | PL | WFEC |  | AEP-OP |  | 1 | 521065 | TALOGA 4 138.00 | 521064 | TALOGA 2 69.000 | 521178 | TLGTERT 13.800 | 1 | 09WP | 56 | 56 |  |  | 90.9942 | 108.4918 | [7 empty] | CATEGORYB | SINGLE | ROMAN NOSE - SOUTHARD 138KV CKT 1 | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 60.7554 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T1052409WP | FROM->TO | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | PL | WFEC |  | AEP-OP |  | 1 | 521065 | TALOGA 4 138.00 | 521064 | TALOGA 2 69.000 | 521178 | TLGTERT 13.800 | 1 | 09WP | 56 | 56 |  |  | 89.1218 | 106.1673 | [7 empty] | CATEGORYB | SINGLE | EL RENO - ROMAN NOSE 138KV CKT 1 | 0 | 514819 | EL-RENO4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 59.4537 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
NA | [8 empty] | NAWERE5327735327711 |  | SUMMIT - RENO 345KV | U | WERE | WERE |  |  | 0 | 532773 | SUMMIT 7 345.0 | 532771 | RENO 7 345.00 |  |  | 1 | [15 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WERE | SUMMIT - RENO 345KV | Install new 50.55-mile 345 kV line from Reno county to Summit; 31 miles of 115 kV line between Circle and S Philips would be rebuilt as double circuit with the 345 kV line to minimize ROW impacts; Substation work required at Summit for new 345 kV terminal | [52 empty] | 2010-06-01 | 2010-06-01
GEN-2006-010 | Turk | [7 empty] | 507454508080012SP | TO->FROM | SUGAR HILL - TURK 138KV CKT 1 | U | AEPW | AEPW | SARK | TEXARK | 0 | 507454 | HEMPSTD4 138.00 | 508080 | SUGARHL4 138.00 | 0 |  | 1 |  | 368 | 512 |  |  | 159.6 | [9 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | AEPW | SUGAR HILL - TURK 138KV CKT 1 | Build new Turk-Sugar Hill 138 kV line and add Sugar Hill 138 kV terminal. | [11 empty] | 19700000 | 19700000 | [39 empty] | 2012-07-01 | 2012-07-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 4 | 2008AGP1AFS31T2181409SP | FROM->TO | SUBSTATION M 161/69KV TRANSFORMER CKT 1 | REL | INDN | INDN | INDN | INDN | 0 | 548814 | SUB M-161 161.00 | 548815 | SUB M 69.000 | 0 |  | 1 | 09SP | 100 | 100 | 156.7 |  | 91.0333 | 101.2747 | [7 empty] | CATEGORYB | SINGLE | BLUE MILLS - ECKLES 161KV CKT 1 | 0 | 543004 | BLUMILS5 161.00 | 548808 | ECKLES-161 161.00 | 0 |  | 1 | 101.2747 |  | INDN | SUBSTATION M 161/69KV TRANSFORMER CKT 2 | Add second 100 MVA xfr at Subsation M | 100 | 100 |  |  |  | 18 | 18 | [5 empty] | 6600000 | [39 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T2534410SP | FROM->TO | SUBSTATION M 161/69KV TRANSFORMER CKT 1 | REL | INDN | INDN | INDN | INDN | 0 | 548814 | SUB M-161 161.00 | 548815 | SUB M 69.000 | 0 |  | 1 | 10SP | 100 | 100 | 153.8 | 109.5 | 109.5126 | 110.4907 | [7 empty] | CATEGORYB | SINGLE | BLUE MILLS - ECKLES 161KV CKT 1 | 0 | 543004 | BLUMILS5 161.00 | 548808 | ECKLES-161 161.00 | 0 |  | 1 | 110.4907 |  | INDN | SUBSTATION M 161/69KV TRANSFORMER CKT 2 | Add second 100 MVA xfr at Subsation M | 100 | 100 |  |  |  | 18 | 18 | [5 empty] | 6600000 | [39 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T2524410SP | FROM->TO | SUBSTATION M 161/69KV TRANSFORMER CKT 1 | REL | INDN | INDN | INDN | INDN | 0 | 548814 | SUB M-161 161.00 | 548815 | SUB M 69.000 | 0 |  | 1 | 10SP | 100 | 100 | 150.1 | 105.7 | 105.6324 | 106.6162 | [7 empty] | CATEGORYB | SINGLE | BLUE MILLS - BLUE VALLEY 161KV CKT 1 | 0 | 543004 | BLUMILS5 161.00 | 548807 | BLUVLY-161 161.00 | 0 |  | 1 | 106.6162 |  | INDN | SUBSTATION M 161/69KV TRANSFORMER CKT 2 | Add second 100 MVA xfr at Subsation M | 100 | 100 |  |  |  | 18 | 18 | [5 empty] | 6600000 | [39 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T815510WP | FROM->TO | SUBSTATION M 161/69KV TRANSFORMER CKT 1 | REL | INDN | INDN | INDN | INDN | 0 | 548814 | SUB M-161 161.00 | 548815 | SUB M 69.000 | 0 |  | 1 | 10WP | 100 | 100 | 135.5 |  | 91.2968 | 101.9128 | [7 empty] | CATEGORYB | SINGLE | BLUE MILLS - ECKLES 161KV CKT 1 | 0 | 543004 | BLUMILS5 161.00 | 548808 | ECKLES-161 161.00 | 0 |  | 1 | 101.9128 |  | INDN | SUBSTATION M 161/69KV TRANSFORMER CKT 2 | Add second 100 MVA xfr at Subsation M | 100 | 100 |  |  |  | 18 | 18 | [5 empty] | 6600000 | [39 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T3145513SP | FROM->TO | SUBSTATION M 161/69KV TRANSFORMER CKT 1 | REL | INDN | INDN | INDN | INDN | 0 | 548814 | SUB M-161 161.00 | 548815 | SUB M 69.000 | 0 |  | 1 | 13SP | 100 | 100 | 144.3 | 104.8 | 102.7013 | 108.7447 | [7 empty] | CATEGORYB | SINGLE | BLUE MILLS - ECKLES 161KV CKT 1 | 0 | 543004 | BLUMILS5 161.00 | 548808 | ECKLES-161 161.00 | 0 |  | 1 | 108.7447 |  | INDN | SUBSTATION M 161/69KV TRANSFORMER CKT 2 | Add second 100 MVA xfr at Subsation M | 100 | 100 |  |  |  | 18 | 18 | [5 empty] | 6600000 | [39 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T3135513SP | FROM->TO | SUBSTATION M 161/69KV TRANSFORMER CKT 1 | REL | INDN | INDN | INDN | INDN | 0 | 548814 | SUB M-161 161.00 | 548815 | SUB M 69.000 | 0 |  | 1 | 13SP | 100 | 100 | 140.6 | 101.2 | 99.8183 | 105.8444 | [7 empty] | CATEGORYB | SINGLE | BLUE MILLS - BLUE VALLEY 161KV CKT 1 | 0 | 543004 | BLUMILS5 161.00 | 548807 | BLUVLY-161 161.00 | 0 |  | 1 | 105.8444 |  | INDN | SUBSTATION M 161/69KV TRANSFORMER CKT 2 | Add second 100 MVA xfr at Subsation M | 100 | 100 |  |  |  | 18 | 18 | [5 empty] | 6600000 | [39 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T1215513WP | FROM->TO | SUBSTATION M 161/69KV TRANSFORMER CKT 1 | REL | INDN | INDN | INDN | INDN | 0 | 548814 | SUB M-161 161.00 | 548815 | SUB M 69.000 | 0 |  | 1 | 13WP | 100 | 100 | 127.3 |  | 93.0431 | 107.0325 | [7 empty] | CATEGORYB | SINGLE | BLUE MILLS - ECKLES 161KV CKT 1 | 0 | 543004 | BLUMILS5 161.00 | 548808 | ECKLES-161 161.00 | 0 |  | 1 | 107.0325 |  | INDN | SUBSTATION M 161/69KV TRANSFORMER CKT 2 | Add second 100 MVA xfr at Subsation M | 100 | 100 |  |  |  | 18 | 18 | [5 empty] | 6600000 | [39 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T1205513WP | FROM->TO | SUBSTATION M 161/69KV TRANSFORMER CKT 1 | REL | INDN | INDN | INDN | INDN | 0 | 548814 | SUB M-161 161.00 | 548815 | SUB M 69.000 | 0 |  | 1 | 13WP | 100 | 100 | 121.9 |  | 89.3906 | 103.0307 | [7 empty] | CATEGORYB | SINGLE | BLUE MILLS - BLUE VALLEY 161KV CKT 1 | 0 | 543004 | BLUMILS5 161.00 | 548807 | BLUVLY-161 161.00 | 0 |  | 1 | 103.0307 |  | INDN | SUBSTATION M 161/69KV TRANSFORMER CKT 2 | Add second 100 MVA xfr at Subsation M | 100 | 100 |  |  |  | 18 | 18 | [5 empty] | 6600000 | [39 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 4 | 2008AGP1AFS31T6563418SP | FROM->TO | SUBSTATION M 161/69KV TRANSFORMER CKT 1 | REL | INDN | INDN | INDN | INDN | 0 | 548814 | SUB M-161 161.00 | 548815 | SUB M 69.000 | 0 |  | 1 | 18SP | 100 | 100 | 148.6 | 104.2 | 103.5912 | 112.745 | [7 empty] | CATEGORYB | SINGLE | BLUE MILLS - ECKLES 161KV CKT 1 | 0 | 543004 | BLUMILS5 161.00 | 548808 | ECKLES-161 161.00 | 0 |  | 1 | 112.745 |  | INDN | SUBSTATION M 161/69KV TRANSFORMER CKT 2 | Add second 100 MVA xfr at Subsation M | 100 | 100 |  |  |  | 18 | 18 | [5 empty] | 6600000 | [39 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 4 | 2008AGP1AFS31T6553418SP | FROM->TO | SUBSTATION M 161/69KV TRANSFORMER CKT 1 | REL | INDN | INDN | INDN | INDN | 0 | 548814 | SUB M-161 161.00 | 548815 | SUB M 69.000 | 0 |  | 1 | 18SP | 100 | 100 | 145.0 | 100.4 | 100.4846 | 109.5123 | [7 empty] | CATEGORYB | SINGLE | BLUE MILLS - BLUE VALLEY 161KV CKT 1 | 0 | 543004 | BLUMILS5 161.00 | 548807 | BLUVLY-161 161.00 | 0 |  | 1 | 109.5123 |  | INDN | SUBSTATION M 161/69KV TRANSFORMER CKT 2 | Add second 100 MVA xfr at Subsation M | 100 | 100 |  |  |  | 18 | 18 | [5 empty] | 6600000 | [39 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T5971318SP | TO->FROM | SUB 145 - JOPLIN WEST 7TH - SUB 439 - STATELINE 161KV CKT 1 | REL | EMDE | EMDE | JOPLIN | JOPLIN | 0 | 547498 | STL439 5 161.00 | 547470 | JOP145 5 161.00 | 0 |  | 1 | 18SP | 218 | 268 | 102.4 | 103.7 | 104.5308 | 104.0721 | [7 empty] | CATEGORYB | SINGLE | SUB 110 - ORONOGO JCT. - SUB 452 - RIVERTON 161KV CKT 1 | 0 | 547467 | ORO110 5 161.00 | 547469 | RIV4525 161.00 | 0 |  | 1 | 278.9132 |  | EMDE | Multi - Stateline - Joplin - Reinmiller conversion | Tear down the Riverton to Joplin 59 69 kV line, rebuilding the line to 161 kV from Stateline to outside Joplin 59 sub. Tear down and rebuild Joplin 59 to Gateway to Pillsbury to Reinmiller, converting those 69 kV lines to 161 kV. Tap the 161 kV line betwe | [5 empty] | 48 | 48 | [45 empty] | 2016-06-01 | 2016-06-01
2005-AG2 | 2005-AG2 | [7 empty] | 59467594691594705949813315SP |  | SUB 110 - ORONOGO JCT. - SUB 167 - RIVERTON 161KV CKT 1 | U | EMDE | EMDE |  |  | 0 | 547469 | RIV167 5 161 | 547467 | ORO110 5 161 | 0 |  | 1 | 15SP |  | 214 | [12 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | EMDE | SUB 110 - ORONOGO JCT. - SUB 167 - RIVERTON 161KV CKT 1 | Reconductor Oronogo 59467 to Riverton 59469 with Bundled 556 ACSR | 299 | 335 | 299 | 335 | 11.84 | 24 | 12 |  | 0.00379 | 0.02451 | 0.02427 |  | 5400000 | [39 empty] | 2011-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 4 | 2008AGP1AFS31V1264413SP |  | STILLWATER NORTHTAP 69KV | EXP | GRDA |  | GRDA-COW |  |  | 512732 | NORTHTP2 69.000 | [5 empty] | 13SP | [8 empty] | 0.91084 | 0.89014 | 0.9567 | 0.9 | 1.05 | CATEGORYB | SINGLE | KINZE - STILLWATER KINZIE 138KV CKT 1 | 0 | 515008 | KINZE 4 138.00 | 512710 | KINZEGR4 138.00 | 0 |  | 1 |  |  | GRDA | SALLISAW 69KV CAP BANK | Add 20 Mvar cap at Sallisaw 69 kV. | [52 empty] | 2009-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 4 | 2008AGP1AFS31V1274413SP |  | STILLWATER INDUSTRIAL 69KV | EXP | GRDA |  | GRDA-COW |  |  | 512733 | INDUSTL2 69.000 | [5 empty] | 13SP | [8 empty] | 0.90733 | 0.88596 | 0.95282 | 0.9 | 1.05 | CATEGORYB | SINGLE | KINZE - STILLWATER KINZIE 138KV CKT 1 | 0 | 515008 | KINZE 4 138.00 | 512710 | KINZEGR4 138.00 | 0 |  | 1 |  |  | GRDA | SALLISAW 69KV CAP BANK | Add 20 Mvar cap at Sallisaw 69 kV. | [52 empty] | 2009-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 4 | 2008AGP1AFS31V3764418SP |  | STILLWATER HOSPITAL 69KV | EXP | GRDA |  | GRDA-COW |  |  | 512659 | HOSPITL2 69.000 | [5 empty] | 18SP | [8 empty] | 0.92714 | 0.89975 | 0.9772 | 0.9 | 1.05 | CATEGORYB | SINGLE | KINZE - STILLWATER KINZIE 138KV CKT 1 | 0 | 515008 | KINZE 4 138.00 | 512710 | KINZEGR4 138.00 | 0 |  | 1 |  |  | GRDA | SALLISAW 69KV CAP BANK | Add 20 Mvar cap at Sallisaw 69 kV. | [52 empty] | 2009-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 4 | 2008AGP1AFS31T1341413SP | FROM->TO | STILLWATER CENTRAL - STILLWATER PERKINS TAP 69KV CKT 1 | S | GRDA | GRDA | GRDA-COW | GRDA | 0 | 512653 | CENTRL 2 69.000 | 512662 | STILWTP2 69.000 | 0 |  | 1 | 13SP | 57 | 65 |  |  | 86.0495 | 103.25 | [7 empty] | CATEGORYB | SINGLE | STILLWATER ADMIRAL - STILLWATER KINZIE 69KV CKT 1 | 0 | 512660 | ADMIRAL2 69.000 | 512713 | KINZEGR2 69.000 | 0 |  | 1 | 67.1125 |  | GRDA | STILLWATER CENTRAL - STILLWATER PERKINS TAP 69KV CKT 1 | Indeterminate | [52 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T14834413SP | FROM->TO | STILLWATER CENTRAL - STILLWATER PERKINS TAP 69KV CKT 1 | S | GRDA | GRDA | GRDA-COW | GRDA | 0 | 512653 | CENTRL 2 69.000 | 512662 | STILWTP2 69.000 | 0 |  | 1 | 13SP | 57 | 65 |  |  | 85.455 | 101.0637 | [7 empty] | CATEGORYB | NONSINGLE | SPP-GRDA-02 | 0 | 0 |  | 0 |  | 0 |  |  | 65.6914 |  | GRDA | STILLWATER CENTRAL - STILLWATER PERKINS TAP 69KV CKT 1 | Indeterminate | [52 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T3414418SP | FROM->TO | STILLWATER CENTRAL - STILLWATER PERKINS TAP 69KV CKT 1 | S | GRDA | GRDA | GRDA-COW | GRDA | 0 | 512653 | CENTRL 2 69.000 | 512662 | STILWTP2 69.000 | 0 |  | 1 | 18SP | 57 | 65 |  |  | 85.9572 | 101.9369 | [7 empty] | CATEGORYB | SINGLE | STILLWATER ADMIRAL - STILLWATER KINZIE 69KV CKT 1 | 0 | 512660 | ADMIRAL2 69.000 | 512713 | KINZEGR2 69.000 | 0 |  | 1 | 66.259 |  | GRDA | STILLWATER CENTRAL - STILLWATER PERKINS TAP 69KV CKT 1 | Indeterminate | [52 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 4 | 2008AGP1AFS31T3121413SP | FROM->TO | STILLWATER 138/69KV TRANSFORMER CKT 2 | S | AECI | AECI | KAMO-OK | KAMO-OK | 0 | 300141 | 4STILWTR 138.00 | 300845 | 2STILWTR 69.000 | 0 |  | 2 | 13SP | 75 | 75 | 114.0 | 111.9 | 114.8055 | 126.625 | [7 empty] | CATEGORYB | SINGLE | STILLWATER 138/69KV TRANSFORMER CKT 1 | 0 | 300141 | 4STILWTR 138.00 | 300845 | 2STILWTR 69.000 | 0 |  | 1 | 94.9688 |  | AECI | STILLWATER 138/69KV TRANSFORMER CKT 2 | Upgrade to 112 MVA transformer | [12 empty] | 2500000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T6594418SP | FROM->TO | STILLWATER 138/69KV TRANSFORMER CKT 2 | S | AECI | AECI | KAMO-OK | KAMO-OK | 0 | 300141 | 4STILWTR 138.00 | 300845 | 2STILWTR 69.000 | 0 |  | 2 | 18SP | 75 | 75 | 114.6 | 114.1 | 117.5766 | 128.4565 | [7 empty] | CATEGORYB | SINGLE | STILLWATER 138/69KV TRANSFORMER CKT 1 | 0 | 300141 | 4STILWTR 138.00 | 300845 | 2STILWTR 69.000 | 0 |  | 1 | 96.3424 |  | AECI | STILLWATER 138/69KV TRANSFORMER CKT 2 | Upgrade to 112 MVA transformer | [12 empty] | 2500000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 4 | 2008AGP1AFS31T3131413SP | FROM->TO | STILLWATER 138/69KV TRANSFORMER CKT 1 | S | AECI | AECI | KAMO-OK | KAMO-OK | 0 | 300141 | 4STILWTR 138.00 | 300845 | 2STILWTR 69.000 | 0 |  | 1 | 13SP | 75 | 75 | 114.0 | 111.9 | 114.8055 | 126.625 | [7 empty] | CATEGORYB | SINGLE | STILLWATER 138/69KV TRANSFORMER CKT 2 | 0 | 300141 | 4STILWTR 138.00 | 300845 | 2STILWTR 69.000 | 0 |  | 2 | 94.9688 |  | AECI | STILLWATER 138/69KV TRANSFORMER CKT 1 | Upgrade to 112 MVA transformer | [12 empty] | 2500000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T6604418SP | FROM->TO | STILLWATER 138/69KV TRANSFORMER CKT 1 | S | AECI | AECI | KAMO-OK | KAMO-OK | 0 | 300141 | 4STILWTR 138.00 | 300845 | 2STILWTR 69.000 | 0 |  | 1 | 18SP | 75 | 75 | 114.6 | 114.1 | 117.5766 | 128.4565 | [7 empty] | CATEGORYB | SINGLE | STILLWATER 138/69KV TRANSFORMER CKT 2 | 0 | 300141 | 4STILWTR 138.00 | 300845 | 2STILWTR 69.000 | 0 |  | 2 | 96.3424 |  | AECI | STILLWATER 138/69KV TRANSFORMER CKT 1 | Upgrade to 112 MVA transformer | [12 empty] | 2500000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 1 | 2008AGP1AFS31T493109SH | FROM->TO | STILLWATER - STILLWATER CENTRAL 69KV CKT 1 | S | AECI | GRDA | KAMO-OK | GRDA-COW | 0 | 300845 | 2STILWTR 69.000 | 512653 | CENTRL 2 69.000 | 0 |  | 1 | 09SH | 75 | 93 |  |  | 124.4778 | 124.5688 | [7 empty] | CATEGORYB | SINGLE | STILLWATER ADMIRAL - STILLWATER KINZIE 69KV CKT 1 | 0 | 512660 | ADMIRAL2 69.000 | 512713 | KINZEGR2 69.000 | 0 |  | 1 | 115.849 |  | GRDA | STILLWATER - STILLWATER CENTRAL 69KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T3842409SH | FROM->TO | STILLWATER - STILLWATER CENTRAL 69KV CKT 1 | S | AECI | GRDA | KAMO-OK | GRDA-COW | 0 | 300845 | 2STILWTR 69.000 | 512653 | CENTRL 2 69.000 | 0 |  | 1 | 09SH | 75 | 93 |  |  | 122.3051 | 122.5153 | [7 empty] | CATEGORYB | SINGLE | STILLWATER KINZIE (KINAUTO1) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 512710 | KINZEGR4 138.00 | 512713 | KINZEGR2 69.000 | 512811 | KINZIE 13.800 | 1 | 113.9392 |  | GRDA | STILLWATER - STILLWATER CENTRAL 69KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T922409SP | FROM->TO | STILLWATER - STILLWATER CENTRAL 69KV CKT 1 | S | AECI | GRDA | KAMO-OK | GRDA-COW | 0 | 300845 | 2STILWTR 69.000 | 512653 | CENTRL 2 69.000 | 0 |  | 1 | 09SP | 75 | 93 |  |  | 126.9912 | 127.1534 | [7 empty] | CATEGORYB | SINGLE | STILLWATER ADMIRAL - STILLWATER KINZIE 69KV CKT 1 | 0 | 512660 | ADMIRAL2 69.000 | 512713 | KINZEGR2 69.000 | 0 |  | 1 | 118.2527 |  | GRDA | STILLWATER - STILLWATER CENTRAL 69KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T6322409SP | FROM->TO | STILLWATER - STILLWATER CENTRAL 69KV CKT 1 | S | AECI | GRDA | KAMO-OK | GRDA-COW | 0 | 300845 | 2STILWTR 69.000 | 512653 | CENTRL 2 69.000 | 0 |  | 1 | 09SP | 75 | 93 |  |  | 124.7946 | 124.9382 | [7 empty] | CATEGORYB | SINGLE | STILLWATER KINZIE (KINAUTO1) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 512710 | KINZEGR4 138.00 | 512713 | KINZEGR2 69.000 | 512811 | KINZIE 13.800 | 1 | 116.1925 |  | GRDA | STILLWATER - STILLWATER CENTRAL 69KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T1202410SP | FROM->TO | STILLWATER - STILLWATER CENTRAL 69KV CKT 1 | S | AECI | GRDA | KAMO-OK | GRDA-COW | 0 | 300845 | 2STILWTR 69.000 | 512653 | CENTRL 2 69.000 | 0 |  | 1 | 10SP | 75 | 93 |  | 124.5 | 124.1628 | 124.6295 | [7 empty] | CATEGORYB | SINGLE | STILLWATER ADMIRAL - STILLWATER KINZIE 69KV CKT 1 | 0 | 512660 | ADMIRAL2 69.000 | 512713 | KINZEGR2 69.000 | 0 |  | 1 | 115.9054 |  | GRDA | STILLWATER - STILLWATER CENTRAL 69KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T7155510SP | FROM->TO | STILLWATER - STILLWATER CENTRAL 69KV CKT 1 | S | AECI | GRDA | KAMO-OK | GRDA-COW | 0 | 300845 | 2STILWTR 69.000 | 512653 | CENTRL 2 69.000 | 0 |  | 1 | 10SP | 75 | 93 |  |  | 102.5559 | 122.47 | [7 empty] | CATEGORYB | SINGLE | STILLWATER KINZIE (KINAUTO1) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 512710 | KINZEGR4 138.00 | 512713 | KINZEGR2 69.000 | 512811 | KINZIE 13.800 | 1 | 113.8971 |  | GRDA | STILLWATER - STILLWATER CENTRAL 69KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 4 | 2008AGP1AFS31T1371413SP | FROM->TO | STILLWATER - STILLWATER CENTRAL 69KV CKT 1 | S | AECI | GRDA | KAMO-OK | GRDA-COW | 0 | 300845 | 2STILWTR 69.000 | 512653 | CENTRL 2 69.000 | 0 |  | 1 | 13SP | 75 | 93 | 109.9 | 109.9 | 119.5168 | 143.2428 | [7 empty] | CATEGORYB | SINGLE | STILLWATER ADMIRAL - STILLWATER KINZIE 69KV CKT 1 | 0 | 512660 | ADMIRAL2 69.000 | 512713 | KINZEGR2 69.000 | 0 |  | 1 | 133.2158 |  | GRDA | STILLWATER - STILLWATER CENTRAL 69KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T10854413SP | FROM->TO | STILLWATER - STILLWATER CENTRAL 69KV CKT 1 | S | AECI | GRDA | KAMO-OK | GRDA-COW | 0 | 300845 | 2STILWTR 69.000 | 512653 | CENTRL 2 69.000 | 0 |  | 1 | 13SP | 75 | 93 | 107.9 | 107.9 | 117.2109 | 140.0387 | [7 empty] | CATEGORYB | SINGLE | STILLWATER KINZIE (KINAUTO1) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 512710 | KINZEGR4 138.00 | 512713 | KINZEGR2 69.000 | 512811 | KINZIE 13.800 | 1 | 130.236 |  | GRDA | STILLWATER - STILLWATER CENTRAL 69KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 1 | 2008AGP1AFS31T104113SP | FROM->TO | STILLWATER - STILLWATER CENTRAL 69KV CKT 1 | S | AECI | GRDA | KAMO-OK | GRDA-COW | 0 | 300845 | 2STILWTR 69.000 | 512653 | CENTRL 2 69.000 | 0 |  | 1 | 13SP | 75 | 93 |  |  | 90.192 | 107.0607 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | 99.5665 |  | GRDA | STILLWATER - STILLWATER CENTRAL 69KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T1604413SP | FROM->TO | STILLWATER - STILLWATER CENTRAL 69KV CKT 1 | S | AECI | GRDA | KAMO-OK | GRDA-COW | 0 | 300845 | 2STILWTR 69.000 | 512653 | CENTRL 2 69.000 | 0 |  | 1 | 13SP | 75 | 93 |  |  | 88.4165 | 105.266 | [7 empty] | CATEGORYB | SINGLE | KINZE - STILLWATER KINZIE 138KV CKT 1 | 0 | 512710 | KINZEGR4 138.00 | 515008 | KINZE 4 138.00 | 0 |  | 1 | 97.8974 |  | GRDA | STILLWATER - STILLWATER CENTRAL 69KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 4 | 2008AGP1AFS31T791413WP | FROM->TO | STILLWATER - STILLWATER CENTRAL 69KV CKT 1 | S | AECI | GRDA | KAMO-OK | GRDA-COW | 0 | 300845 | 2STILWTR 69.000 | 512653 | CENTRL 2 69.000 | 0 |  | 1 | 13WP | 75 | 93 |  |  | 77.2414 | 100.1311 | [7 empty] | CATEGORYB | SINGLE | STILLWATER ADMIRAL - STILLWATER KINZIE 69KV CKT 1 | 0 | 512660 | ADMIRAL2 69.000 | 512713 | KINZEGR2 69.000 | 0 |  | 1 | 93.1219 |  | GRDA | STILLWATER - STILLWATER CENTRAL 69KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T3444418SP | FROM->TO | STILLWATER - STILLWATER CENTRAL 69KV CKT 1 | S | AECI | GRDA | KAMO-OK | GRDA-COW | 0 | 300845 | 2STILWTR 69.000 | 512653 | CENTRL 2 69.000 | 0 |  | 1 | 18SP | 75 | 93 | 107.5 | 107.6 | 119.4169 | 141.5437 | [7 empty] | CATEGORYB | SINGLE | STILLWATER ADMIRAL - STILLWATER KINZIE 69KV CKT 1 | 0 | 512660 | ADMIRAL2 69.000 | 512713 | KINZEGR2 69.000 | 0 |  | 1 | 131.6356 |  | GRDA | STILLWATER - STILLWATER CENTRAL 69KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T22634418SP | FROM->TO | STILLWATER - STILLWATER CENTRAL 69KV CKT 1 | S | AECI | GRDA | KAMO-OK | GRDA-COW | 0 | 300845 | 2STILWTR 69.000 | 512653 | CENTRL 2 69.000 | 0 |  | 1 | 18SP | 75 | 93 | 105.4 | 105.5 | 116.5275 | 138.2758 | [7 empty] | CATEGORYB | SINGLE | STILLWATER KINZIE (KINAUTO1) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 512710 | KINZEGR4 138.00 | 512713 | KINZEGR2 69.000 | 512811 | KINZIE 13.800 | 1 | 128.5965 |  | GRDA | STILLWATER - STILLWATER CENTRAL 69KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T294418SP | FROM->TO | STILLWATER - STILLWATER CENTRAL 69KV CKT 1 | S | AECI | GRDA | KAMO-OK | GRDA-COW | 0 | 300845 | 2STILWTR 69.000 | 512653 | CENTRL 2 69.000 | 0 |  | 1 | 18SP | 75 | 93 |  |  | 88.4196 | 104.7284 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | 97.3974 |  | GRDA | STILLWATER - STILLWATER CENTRAL 69KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T3514418SP | FROM->TO | STILLWATER - STILLWATER CENTRAL 69KV CKT 1 | S | AECI | GRDA | KAMO-OK | GRDA-COW | 0 | 300845 | 2STILWTR 69.000 | 512653 | CENTRL 2 69.000 | 0 |  | 1 | 18SP | 75 | 93 |  |  | 88.2596 | 103.8636 | [7 empty] | CATEGORYB | SINGLE | KINZE - STILLWATER KINZIE 138KV CKT 1 | 0 | 512710 | KINZEGR4 138.00 | 515008 | KINZE 4 138.00 | 0 |  | 1 | 96.5931 |  | GRDA | STILLWATER - STILLWATER CENTRAL 69KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 3 | 2008AGP1AFS31V4642309FA |  | STIGLER 161KV | S | SWPA |  | EMINTH |  |  | 505588 | STIGLER5 161.00 | [5 empty] | 09FA | [8 empty] | 1.0341 | 0.8993 | 1.0134 | 0.9 | 1.05 | CATEGORYB | NONSINGLE | SPP-SWPA-04 | 0 | 0 |  | 0 |  | 0 |  |  |  |  | SWPA | STIGLER 161KV | [53 empty] | 2009-04-01 | 2010-06-01
2008-AGP1 | AFS3 | CONT-0633 - East Manhattan 230-115kV XFMR | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17543318SP |  | STAGG HILL 115KV | REL | WERE |  | NCENTRAL |  |  | 533341 | STAGGHL3 115.00 | [5 empty] | 18SP | [6 empty] | 0.91803 | 0.90838 | 0.90376 | 0.85373 | 0.99185 | 0.93 | 1.05 | CATEGORYB | SINGLE | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V9483313SP |  | ST.FRANCIS TAP 115KV | REL | SUNC |  | SEPC |  |  | 531471 | STFRANT3 115.00 | [5 empty] | 13SP | [8 empty] | 0.92927 | 0.89933 | 1.0022 | 0.9 | 1.05 | CATEGORYB | SINGLE | MINGO (MINGO) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 531451 | MINGO 7 345.00 | 531429 | MINGO 3 115.00 | 531452 | MINGTER1 13.800 | 1 |  |  | SUNC | RULETON 115KV Capacitor | Install Second 12 Mvar cap bank at Ruleton 115kV | [12 empty] | 486000 | 2008-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17333318SP |  | ST.FRANCIS TAP 115KV | REL | SUNC |  | SEPC |  |  | 531471 | STFRANT3 115.00 | [5 empty] | 18SP | [8 empty] | 0.91672 | 0.88444 | 0.99083 | 0.9 | 1.05 | CATEGORYB | SINGLE | MINGO (MINGO) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 531451 | MINGO 7 345.00 | 531429 | MINGO 3 115.00 | 531452 | MINGTER1 13.800 | 1 |  |  | SUNC | RULETON 115KV Capacitor | Install Second 12 Mvar cap bank at Ruleton 115kV | [12 empty] | 486000 | 2008-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V9453313SP |  | ST.FRANCIS 115KV | REL | SUNC |  | NORTON-D |  |  | 531370 | STFRAN 3 115.00 | [5 empty] | 13SP | [8 empty] | 0.92905 | 0.89917 | 1.0012 | 0.9 | 1.05 | CATEGORYB | SINGLE | MINGO (MINGO) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 531451 | MINGO 7 345.00 | 531429 | MINGO 3 115.00 | 531452 | MINGTER1 13.800 | 1 |  |  | SUNC | RULETON 115KV Capacitor | Install Second 12 Mvar cap bank at Ruleton 115kV | [12 empty] | 486000 | 2008-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17283318SP |  | ST.FRANCIS 115KV | REL | SUNC |  | NORTON-D |  |  | 531370 | STFRAN 3 115.00 | [5 empty] | 18SP | [8 empty] | 0.91641 | 0.88426 | 0.99053 | 0.9 | 1.05 | CATEGORYB | SINGLE | MINGO (MINGO) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 531451 | MINGO 7 345.00 | 531429 | MINGO 3 115.00 | 531452 | MINGTER1 13.800 | 1 |  |  | SUNC | RULETON 115KV Capacitor | Install Second 12 Mvar cap bank at Ruleton 115kV | [12 empty] | 486000 | 2008-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T184410SP | FROM->TO | SPSSPPTIESC | S |  |  |  |  | SPSSPPTIESC | 0 |  | 0 |  | 0 |  |  | 10SP | 438 | 438 |  |  | -89.345 | 113.5 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | 497.13 |  | SPS | SPSSPPTIESC | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T222210WP | FROM->TO | SPSSPPTIESC | S |  |  |  |  | SPSSPPTIESC | 0 |  | 0 |  | 0 |  |  | 10WP | 438 | 438 |  |  | -88.8568 | 113.5 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | 497.13 |  | SPS | SPSSPPTIESC | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T262413SP | FROM->TO | SPSSPPTIESC | S |  |  |  |  | SPSSPPTIESC | 0 |  | 0 |  | 0 |  |  | 13SP | 438 | 438 |  |  | -89.3649 | 113.5 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | 497.13 |  | SPS | SPSSPPTIESC | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T192413WP | FROM->TO | SPSSPPTIESC | S |  |  |  |  | SPSSPPTIESC | 0 |  | 0 |  | 0 |  |  | 13WP | 438 | 438 |  |  | -89.086 | 113.2 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | 495.816 |  | SPS | SPSSPPTIESC | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T604218SP | FROM->TO | SPSSPPTIESC | S |  |  |  |  | SPSSPPTIESC | 0 |  | 0 |  | 0 |  |  | 18SP | 438 | 438 | 129.9 | 127.8 | -127.5487 | 129.1 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | 565.458 |  | SPS | SPSSPPTIESC | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T282210SP | FROM->TO | SPSSPPTIESB | S |  |  |  |  | SPSSPPTIESB | 0 |  | 0 |  | 0 |  |  | 10SP | 438 | 438 |  |  | -93.0266 | 112.6 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | 493.188 |  | SPS | SPSSPPTIESB | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T212210WP | FROM->TO | SPSSPPTIESB | S |  |  |  |  | SPSSPPTIESB | 0 |  | 0 |  | 0 |  |  | 10WP | 438 | 438 |  |  | -94.6756 | 114.6 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | 501.948 |  | SPS | SPSSPPTIESB | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T382213SP | FROM->TO | SPSSPPTIESB | S |  |  |  |  | SPSSPPTIESB | 0 |  | 0 |  | 0 |  |  | 13SP | 438 | 438 |  |  | -95.5016 | 115.1 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | 504.138 |  | SPS | SPSSPPTIESB | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T212213WP | FROM->TO | SPSSPPTIESB | S |  |  |  |  | SPSSPPTIESB | 0 |  | 0 |  | 0 |  |  | 13WP | 438 | 438 | 100.5 | 101.3 | -100.0891 | 119.7 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | 524.286 |  | SPS | SPSSPPTIESB | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T594218SP | FROM->TO | SPSSPPTIESB | S |  |  |  |  | SPSSPPTIESB | 0 |  | 0 |  | 0 |  |  | 18SP | 438 | 438 | 126.7 | 125.2 | -124.3183 | 125.7 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | 550.566 |  | SPS | SPSSPPTIESB | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T92209FA | FROM->TO | SPSSPPTIESA | S |  |  |  |  | SPSSPPTIESA | 0 |  | 0 |  | 0 |  |  | 09FA | 438 | 438 |  |  | -88.9105 | 102.8 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | 450.264 |  | SPS | SPSSPPTIESA | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T112409SH | FROM->TO | SPSSPPTIESA | S |  |  |  |  | SPSSPPTIESA | 0 |  | 0 |  | 0 |  |  | 09SH | 438 | 438 |  |  | -89.2697 | 102.5 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | 448.95 |  | SPS | SPSSPPTIESA | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T142409SP | FROM->TO | SPSSPPTIESA | S |  |  |  |  | SPSSPPTIESA | 0 |  | 0 |  | 0 |  |  | 09SP | 438 | 438 |  |  | -88.7083 | 102 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | 446.76 |  | SPS | SPSSPPTIESA | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T132409WP | FROM->TO | SPSSPPTIESA | S |  |  |  |  | SPSSPPTIESA | 0 |  | 0 |  | 0 |  |  | 09WP | 438 | 438 |  |  | -88.8137 | 113.4 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | 496.692 |  | SPS | SPSSPPTIESA | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T234210SP | FROM->TO | SPPSPSTIESC | S |  |  |  |  | SPPSPSTIESC | 0 |  | 0 |  | 0 |  |  | 10SP | 487 | 487 |  |  | 81.7022 | 102.4774 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | 499.0649 |  | SPS | SPPSPSTIESC | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T174210WP | FROM->TO | SPPSPSTIESC | S |  |  |  |  | SPPSPSTIESC | 0 |  | 0 |  | 0 |  |  | 10WP | 487 | 487 |  |  | 81.6576 | 102.3154 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | 498.276 |  | SPS | SPPSPSTIESC | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T334213SP | FROM->TO | SPPSPSTIESC | S |  |  |  |  | SPPSPSTIESC | 0 |  | 0 |  | 0 |  |  | 13SP | 487 | 487 |  |  | 81.7728 | 102.5579 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | 499.457 |  | SPS | SPPSPSTIESC | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T184213WP | FROM->TO | SPPSPSTIESC | S |  |  |  |  | SPPSPSTIESC | 0 |  | 0 |  | 0 |  |  | 13WP | 487 | 487 |  |  | 81.6113 | 102.3348 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | 498.3705 |  | SPS | SPPSPSTIESC | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T262210SP | FROM->TO | SPPSPSTIESB | S |  |  |  |  | SPPSPSTIESB | 0 |  | 0 |  | 0 |  |  | 10SP | 487 | 487 |  |  | 85.087 | 101.6803 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | 495.1831 |  | SPS | SPPSPSTIESB | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T192210WP | FROM->TO | SPPSPSTIESB | S |  |  |  |  | SPPSPSTIESB | 0 |  | 0 |  | 0 |  |  | 10WP | 487 | 487 |  |  | 86.8456 | 103.3521 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | 503.3247 |  | SPS | SPPSPSTIESB | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T362213SP | FROM->TO | SPPSPSTIESB | S |  |  |  |  | SPPSPSTIESB | 0 |  | 0 |  | 0 |  |  | 13SP | 487 | 487 |  |  | 87.3629 | 104.0541 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | 506.7435 |  | SPS | SPPSPSTIESB | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T192213WP | FROM->TO | SPPSPSTIESB | S |  |  |  |  | SPPSPSTIESB | 0 |  | 0 |  | 0 |  |  | 13WP | 487 | 487 |  |  | 91.6588 | 108.1967 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | 526.9179 |  | SPS | SPPSPSTIESB | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T574218SP | FROM->TO | SPPSPSTIESB | S |  |  |  |  | SPPSPSTIESB | 0 |  | 0 |  | 0 |  |  | 18SP | 487 | 487 | 113.9 | 112.6 | 113.9659 | 113.9722 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | 555.0446 |  | SPS | SPPSPSTIESB | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T134209WP | FROM->TO | SPPSPSTIESA | S |  |  |  |  | SPPSPSTIESA | 0 |  | 0 |  | 0 |  |  | 09WP | 487 | 487 |  |  | 81.9167 | 102.6863 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | 500.0823 |  | SPS | SPPSPSTIESA | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
GEN-2004-014 | Spearville2 | [7 empty] | 53969453969553993512SP | FROM->TO | SPEARVILLE (SPEARVL6) 230/115/13.8KV TRANSFORMER CKT 1 | U | MKEC |  |  |  | 1 | 539694 | SPEARVL3 115.00 | 539695 | SPEARVL6 230.00 | 539935 | SPERVLTT 13.800 | 1 |  | 205 | 205 |  |  | 38.8 | [9 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | MKEC | SPEARVILLE (SPEARVL6) 230/115/13.8KV TRANSFORMER CKT 1 | 230kv line terminal at Spearville | [12 empty] | 650000 | [39 empty] | 2009-12-31 | 2009-12-31
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V1535509SH |  | SOUTH SENECA 115KV | EXP | WERE |  | NCENTRAL |  |  | 533337 | SENECA 3 115.00 | [5 empty] | 09SH | [6 empty] | 0.80117 | 0.77213 | 0.80195 | 0.69082 | 0.99963 | 0.93 | 1.05 | CATEGORYB | SINGLE | KELLY - SOUTH SENECA 115KV CKT 1 | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 |  |  |  | 2009-04-01 | 2009-04-01 | 2009-04-01 | 41640 | 41640 | 1 | 1 | 2014 | 41897 | 42156 | 40179 | 41640 | 2014-01-01 | 2010-06-01 | [13 empty] | Ph1: 10.8 Mvar cap bank at Seneca 115 kV 09S. Ph2: Knob Hill -S. Beatrice 115 kV 10S | [7 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 3 | 2008AGP1AFS31V2851309SP |  | SOUTH SENECA 115KV | EXP | WERE |  | NCENTRAL |  |  | 533337 | SENECA 3 115.00 | [5 empty] | 09SP | [6 empty] | 0.81417 | 0.6324 | 0.82106 | 0.41703 | 0.99878 | 0.93 | 1.05 | CATEGORYB | SINGLE | KELLY - SOUTH SENECA 115KV CKT 1 | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 |  |  |  | 2009-04-01 | 2009-04-01 | 2009-04-01 | 41640 | 41640 | 1 | 1 | 2014 | 41897 | 42156 | 40179 | 41640 | 2014-01-01 | 2010-06-01 | [13 empty] | Ph1: 10.8 Mvar cap bank at Seneca 115 kV 09S. Ph2: Knob Hill -S. Beatrice 115 kV 10S | [7 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 2 | 2008AGP1AFS31V3611209SP |  | SOUTH SENECA 115KV | EXP | WERE |  | NCENTRAL |  |  | 533337 | SENECA 3 115.00 | [5 empty] | 09SP | [8 empty] | 1.0008 | 0.92424 | 1.0047 | 0.93 | 1.05 | CATEGORYB | SINGLE | CONCORDIA - ELMCREK6 230.00 230KV CKT 1 | 0 | 539639 | ELMCREK6 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 1 | 2 | 2008AGP1AFS31V7661209SP |  | SOUTH SENECA 115KV | EXP | WERE |  | NCENTRAL |  |  | 533337 | SENECA 3 115.00 | [5 empty] | 09SP | [8 empty] | 1.0009 | 0.92441 | 1.0047 | 0.93 | 1.05 | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539658 | CONCRD6 230.00 | 539657 | CONCORD3 115.00 | 539904 | CONCOD-T 13.800 | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | CONT-0633 - East Manhattan 230-115kV XFMR |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17533318SP |  | SOUTH MANHATTAN 115KV | REL | WERE |  | NCENTRAL |  |  | 533340 | SMANHAT3 115.00 | [5 empty] | 18SP | [8 empty] | 0.92745 | 0.8854 | 0.98745 | 0.93 | 1.05 | CATEGORYB | SINGLE | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 | CONT-0633 - East Manhattan 230-115kV XFMR |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17523318SP |  | SOUTH ALMA 115KV | REL | WERE |  | NCENTRAL |  |  | 533339 | S ALMA 3 115.00 | [5 empty] | 18SP | [8 empty] | 0.94205 | 0.90496 | 0.98267 | 0.93 | 1.05 | CATEGORYB | SINGLE | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V1545509SH |  | SMITTYVILLE N.M. COOP (NEMAHA MARSHALL R.E. 115KV | EXP | WERE |  | NCENTRAL |  |  | 533338 | SMITTYV3 115.00 | [5 empty] | 09SH | [6 empty] | 0.81362 | 0.78622 | 0.81378 | 0.70842 | 0.99619 | 0.93 | 1.05 | CATEGORYB | SINGLE | KELLY - SOUTH SENECA 115KV CKT 1 | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 |  |  |  | 2009-04-01 | 2009-04-01 | 2009-04-01 | 41640 | 41640 | 1 | 1 | 2014 | 41897 | 42156 | 40179 | 41640 | 2014-01-01 | 2010-06-01 | [13 empty] | Ph1: 10.8 Mvar cap bank at Seneca 115 kV 09S. Ph2: Knob Hill -S. Beatrice 115 kV 10S | [7 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 3 | 2008AGP1AFS31V2861309SP |  | SMITTYVILLE N.M. COOP (NEMAHA MARSHALL R.E. 115KV | EXP | WERE |  | NCENTRAL |  |  | 533338 | SMITTYV3 115.00 | [5 empty] | 09SP | [6 empty] | 0.82814 | 0.65563 | 0.83597 | 0.44093 | 0.99137 | 0.93 | 1.05 | CATEGORYB | SINGLE | KELLY - SOUTH SENECA 115KV CKT 1 | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 |  |  |  | 2009-04-01 | 2009-04-01 | 2009-04-01 | 41640 | 41640 | 1 | 1 | 2014 | 41897 | 42156 | 40179 | 41640 | 2014-01-01 | 2010-06-01 | [13 empty] | Ph1: 10.8 Mvar cap bank at Seneca 115 kV 09S. Ph2: Knob Hill -S. Beatrice 115 kV 10S | [7 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V3175509SP |  | SMITTYVILLE N.M. COOP (NEMAHA MARSHALL R.E. 115KV | EXP | WERE |  | NCENTRAL |  |  | 533338 | SMITTYV3 115.00 | [5 empty] | 09SP | [8 empty] | 0.88156 | 0.86089 | 0.98953 | 0.93 | 1.05 | CATEGORYB | SINGLE | BAILEYVILLE N.M. STATION (NEMAHA MARSHALL R - SOUTH SENECA 115KV CKT 1 | 0 | 533337 | SENECA 3 115.00 | 533322 | BAILEYV3 115.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V7265509SP |  | SMITTYVILLE N.M. COOP (NEMAHA MARSHALL R.E. 115KV | EXP | WERE |  | NCENTRAL |  |  | 533338 | SMITTYV3 115.00 | [5 empty] | 09SP | [8 empty] | 0.89922 | 0.87767 | 0.98953 | 0.93 | 1.05 | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539658 | CONCRD6 230.00 | 539657 | CONCORD3 115.00 | 539904 | CONCOD-T 13.800 | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V3505509SP |  | SMITH CENTER 115KV | EXP | MKEC |  |  |  |  | 539693 | SMITH-C3 115.00 | [5 empty] | 09SP | [8 empty] | 0.87926 | 0.84395 | 0.973 | 0.9 | 1.05 | CATEGORYB | SINGLE | CONCORDIA - ELMCREK6 230.00 230KV CKT 1 | 0 | 539639 | ELMCREK6 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V7345509SP |  | SMITH CENTER 115KV | EXP | MKEC |  |  |  |  | 539693 | SMITH-C3 115.00 | [5 empty] | 09SP | [8 empty] | 0.8793 | 0.844 | 0.973 | 0.9 | 1.05 | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539658 | CONCRD6 230.00 | 539657 | CONCORD3 115.00 | 539904 | CONCOD-T 13.800 | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V2535509SP |  | SMITH CENTER 115KV | EXP | MKEC |  |  |  |  | 539693 | SMITH-C3 115.00 | [5 empty] | 09SP | [8 empty] | 0.88721 | 0.85349 | 0.973 | 0.9 | 1.05 | CATEGORYB | SINGLE | EAST MANHATTAN - ELMCREK6 230.00 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 539639 | ELMCREK6 230.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FNSL | FDNS-Iteration limit exceeded | 3 | 2 | 2008AGP1AFS32V103213SP |  | SMITH CENTER 115KV | EXP | MKEC |  |  |  |  | 539693 | SMITH-C3 115.00 | [5 empty] | 13SP | [8 empty] | 0.98536 | 0.82224 | 0.9918 | 0.9 | 1.05 | CATEGORYB | SINGLE | EAST MANHATTAN - ELMCREK6 230.00 230KV CKT 1 | 0 | 539639 | ELMCREK6 230.00 | 532861 | EMANHAT6 230.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 1 | 2008AGP1AFS31T1173113SP | FROM->TO | SILOAM CITY - SILOAM SPRINGS 161KV CKT 1 | S | GRDA | AEPW | GRDA-MUN | FAYETTEV | 0 | 512643 | SILMCTY5 161.00 | 506948 | SILOAM 5 161.00 | 0 |  | 1 | 13SP | 288 | 335 |  |  | 99.7497 | 105.0034 | [7 empty] | CATEGORYB | SINGLE | CHAMBER SPRINGS - CLARKSVILLE 345KV CKT 1 | 0 | 506945 | CHAMSPR7 345.00 | 509745 | CLARKSV7 345.00 | 0 |  | 1 | 351.7614 |  | AEPW | SILOAM CITY - SILOAM SPRINGS 161KV CKT 1 | Rebuild 2.06 miles of 2-397 ACSR with 2156 ACSR. Replace breaker, wavetrap, switches, & jumpers @ AEP Siloam Springs. | 531 | 638 | 633 | 721 | 2.06 | 20 | 6 |  | 0.0004 | 0.005282 | 0.00344 | New AEP limits will be Siloam Springs bus | 2500000 | 2008-08-04 | [38 empty] | 2012-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 1 | 2008AGP1AFS31T1173113SP | FROM->TO | SILOAM CITY - SILOAM SPRINGS 161KV CKT 1 | S | GRDA | AEPW | GRDA-MUN | FAYETTEV | 0 | 512643 | SILMCTY5 161.00 | 506948 | SILOAM 5 161.00 | 0 |  | 1 | 13SP | 288 | 335 |  |  | 99.7497 | 105.0034 | [7 empty] | CATEGORYB | SINGLE | CHAMBER SPRINGS - CLARKSVILLE 345KV CKT 1 | 0 | 506945 | CHAMSPR7 345.00 | 509745 | CLARKSV7 345.00 | 0 |  | 1 | 351.7614 |  | GRDA | SILOAM CITY - SILOAM SPRINGS 161KV CKT 1 GRDA | Indeterminate | [52 empty] | 2012-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T663313WP | FROM->TO | SILOAM CITY - SILOAM SPRINGS 161KV CKT 1 | S | GRDA | AEPW | GRDA-MUN | FAYETTEV | 0 | 512643 | SILMCTY5 161.00 | 506948 | SILOAM 5 161.00 | 0 |  | 1 | 13WP | 335 | 335 |  |  | 96.7895 | 100.4616 | [7 empty] | CATEGORYB | SINGLE | CHAMBER SPRINGS - CLARKSVILLE 345KV CKT 1 | 0 | 506945 | CHAMSPR7 345.00 | 509745 | CLARKSV7 345.00 | 0 |  | 1 | 336.5464 |  | AEPW | SILOAM CITY - SILOAM SPRINGS 161KV CKT 1 | Rebuild 2.06 miles of 2-397 ACSR with 2156 ACSR. Replace breaker, wavetrap, switches, & jumpers @ AEP Siloam Springs. | 531 | 638 | 633 | 721 | 2.06 | 20 | 6 |  | 0.0004 | 0.005282 | 0.00344 | New AEP limits will be Siloam Springs bus | 2500000 | 2008-08-04 | [38 empty] | 2012-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T663313WP | FROM->TO | SILOAM CITY - SILOAM SPRINGS 161KV CKT 1 | S | GRDA | AEPW | GRDA-MUN | FAYETTEV | 0 | 512643 | SILMCTY5 161.00 | 506948 | SILOAM 5 161.00 | 0 |  | 1 | 13WP | 335 | 335 |  |  | 96.7895 | 100.4616 | [7 empty] | CATEGORYB | SINGLE | CHAMBER SPRINGS - CLARKSVILLE 345KV CKT 1 | 0 | 506945 | CHAMSPR7 345.00 | 509745 | CLARKSV7 345.00 | 0 |  | 1 | 336.5464 |  | GRDA | SILOAM CITY - SILOAM SPRINGS 161KV CKT 1 GRDA | Indeterminate | [52 empty] | 2012-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 1 | 2008AGP1AFS31T2323118SP | FROM->TO | SILOAM CITY - SILOAM SPRINGS 161KV CKT 1 | S | GRDA | AEPW | GRDA-MUN | FAYETTEV | 0 | 512643 | SILMCTY5 161.00 | 506948 | SILOAM 5 161.00 | 0 |  | 1 | 18SP | 288 | 335 |  |  | 101.2493 | 103.7055 | [7 empty] | CATEGORYB | SINGLE | CHAMBER SPRINGS - CLARKSVILLE 345KV CKT 1 | 0 | 506945 | CHAMSPR7 345.00 | 509745 | CLARKSV7 345.00 | 0 |  | 1 | 347.4134 |  | AEPW | SILOAM CITY - SILOAM SPRINGS 161KV CKT 1 | Rebuild 2.06 miles of 2-397 ACSR with 2156 ACSR. Replace breaker, wavetrap, switches, & jumpers @ AEP Siloam Springs. | 531 | 638 | 633 | 721 | 2.06 | 20 | 6 |  | 0.0004 | 0.005282 | 0.00344 | New AEP limits will be Siloam Springs bus | 2500000 | 2008-08-04 | [38 empty] | 2012-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 1 | 2008AGP1AFS31T2323118SP | FROM->TO | SILOAM CITY - SILOAM SPRINGS 161KV CKT 1 | S | GRDA | AEPW | GRDA-MUN | FAYETTEV | 0 | 512643 | SILMCTY5 161.00 | 506948 | SILOAM 5 161.00 | 0 |  | 1 | 18SP | 288 | 335 |  |  | 101.2493 | 103.7055 | [7 empty] | CATEGORYB | SINGLE | CHAMBER SPRINGS - CLARKSVILLE 345KV CKT 1 | 0 | 506945 | CHAMSPR7 345.00 | 509745 | CLARKSV7 345.00 | 0 |  | 1 | 347.4134 |  | GRDA | SILOAM CITY - SILOAM SPRINGS 161KV CKT 1 GRDA | Indeterminate | [52 empty] | 2012-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V3355509SP |  | SHEFFIELD 69KV | EXP | WERE |  | SEAST |  |  | 533774 | SHEFFLD2 69.000 | [5 empty] | 09SP | [6 empty] | 0.86027 | 0.85928 | 0.89542 | 0.84918 | 0.99574 | 0.93 | 1.05 | CATEGORYB | SINGLE | LITCHFIELD - PITNAC 69KV CKT 1 | 0 | 533765 | LITCH 2 69.000 | 533769 | PITNAC 2 69.000 | 0 |  | 1 |  |  | WERE | Fort Scott 161/69kV Transformer CKT 1 | New 161/69 kV transformer at Ft Scott. | 100 | 110 |  |  |  | 18 | 18 | [5 empty] | 1400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 2 | 2008AGP1AFS31T711209FA | FROM->TO | SEWARD - ST JOHN 115KV CKT 1 | S | MKEC | MKEC |  |  | 0 | 539692 | SEWARD 3 115.00 | 539696 | ST-JOHN3 115.00 | 0 |  | 1 | 09FA | 79.7 | 79.7 |  |  | 80.3732 | 101.6591 | [7 empty] | CATEGORYB | SINGLE | GREENSBURG - JUDSON LARGE 115KV CKT 1 | 0 | 539664 | GRNBURG3 115.00 | 539671 | JUD-LRG3 115.00 | 0 |  | 1 | 81.0223 |  | MKEC | SEWARD - ST JOHN 115KV CKT 1 | Replace Terminal Equipment | [11 empty] | 225k per Wavetrap | 225000 | 2008-01-01 | [38 empty] | 2009-10-01 | 2011-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 2 | 2008AGP1AFS31T1391209WP | FROM->TO | SEWARD - ST JOHN 115KV CKT 1 | S | MKEC | MKEC |  |  | 0 | 539692 | SEWARD 3 115.00 | 539696 | ST-JOHN3 115.00 | 0 |  | 1 | 09WP | 79.7 | 79.7 |  |  | 72.8324 | 100.9058 | [7 empty] | CATEGORYB | SINGLE | GREENSBURG - JUDSON LARGE 115KV CKT 1 | 0 | 539664 | GRNBURG3 115.00 | 539671 | JUD-LRG3 115.00 | 0 |  | 1 | 80.4219 |  | MKEC | SEWARD - ST JOHN 115KV CKT 1 | Replace Terminal Equipment | [11 empty] | 225k per Wavetrap | 225000 | 2008-01-01 | [38 empty] | 2009-10-01 | 2011-06-01
2008-AGP1 | AFS3 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T2902209SP | FROM->TO | SEVENTEENTH (17TH 4X) 138/69/11.295KV TRANSFORMER CKT 1 | REL | WERE |  | SCENTRAL |  | 1 | 533064 | 17TH 4 138.00 | 533840 | 17TH 2 69.000 | 533112 | 17TH 1 11.295 | 1 | 09SP | 150 | 165 | 101.9 | 101.8 | 101.8407 | 101.9701 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 | 168.2507 |  | WERE | SEVENTEENTH () 138/69/11.295KV TRANSFORMER CKT 2 | Install second 17th St. 138-69 kV transformer | 150 | 165 | 150 | 165 |  | 12 | 6 |  | 0.002 | 0.0653 |  | 165 MVA is transformer limit | 2400000 | 2006-03-21 | [38 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T2894210SP | FROM->TO | SEVENTEENTH (17TH 4X) 138/69/11.295KV TRANSFORMER CKT 1 | REL | WERE |  | SCENTRAL |  | 1 | 533064 | 17TH 4 138.00 | 533840 | 17TH 2 69.000 | 533112 | 17TH 1 11.295 | 1 | 10SP | 150 | 165 | 104.0 | 105.2 | 104.9651 | 105.3801 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 | 173.8772 |  | WERE | SEVENTEENTH () 138/69/11.295KV TRANSFORMER CKT 2 | Install second 17th St. 138-69 kV transformer | 150 | 165 | 150 | 165 |  | 12 | 6 |  | 0.002 | 0.0653 |  | 165 MVA is transformer limit | 2400000 | 2006-03-21 | [38 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T4542213SP | FROM->TO | SEVENTEENTH (17TH 4X) 138/69/11.295KV TRANSFORMER CKT 1 | REL | WERE |  | SCENTRAL |  | 1 | 533064 | 17TH 4 138.00 | 533840 | 17TH 2 69.000 | 533112 | 17TH 1 11.295 | 1 | 13SP | 150 | 165 | 101.4 | 101.4 | 100.4376 | 104.007 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 | 171.6116 |  | WERE | SEVENTEENTH () 138/69/11.295KV TRANSFORMER CKT 2 | Install second 17th St. 138-69 kV transformer | 150 | 165 | 150 | 165 |  | 12 | 6 |  | 0.002 | 0.0653 |  | 165 MVA is transformer limit | 2400000 | 2006-03-21 | [38 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T6304218SP | FROM->TO | SEVENTEENTH (17TH 4X) 138/69/11.295KV TRANSFORMER CKT 1 | REL | WERE |  | SCENTRAL |  | 1 | 533064 | 17TH 4 138.00 | 533840 | 17TH 2 69.000 | 533112 | 17TH 1 11.295 | 1 | 18SP | 150 | 165 | 101.9 | 103.1 | 102.7965 | 103.1626 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 | 170.2183 |  | WERE | SEVENTEENTH () 138/69/11.295KV TRANSFORMER CKT 2 | Install second 17th St. 138-69 kV transformer | 150 | 165 | 150 | 165 |  | 12 | 6 |  | 0.002 | 0.0653 |  | 165 MVA is transformer limit | 2400000 | 2006-03-21 | [38 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V8505513SP |  | SERVICE PL EL RENO 69KV | REL | OKGE |  |  |  |  | 514817 | SVCELRN2 69.000 | [5 empty] | 13SP | [8 empty] | 0.90493 | 0.86875 | 0.98751 | 0.9 | 1.05 | CATEGORYB | SINGLE | EL RENO (ELRENO5) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 514819 | EL-RENO4 138.00 | 514818 | ELRENO 2 69.000 | 515722 | EL RENO1 13.200 | 1 |  |  | OKGE | EL RENO 69KV CAP BANK | Install 12 Mvar Capacitor at El Reno 69 kV bus | [52 empty] | 2011-06-01 | 2011-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 4 | 1 | 2008AGP1AFS31V10904118SP |  | SERVICE PL EL RENO 69KV | REL | OKGE |  |  |  |  | 514817 | SVCELRN2 69.000 | [5 empty] | 18SP | [6 empty] | 0.88604 | 0.89006 | 0.86009 | 0.83817 | 0.98085 | 0.9 | 1.05 | CATEGORYB | SINGLE | EL RENO (ELRENO5) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 514819 | EL-RENO4 138.00 | 514818 | ELRENO 2 69.000 | 515722 | EL RENO1 13.200 | 1 |  |  | OKGE | EL RENO 69KV CAP BANK | Install 12 Mvar Capacitor at El Reno 69 kV bus | [52 empty] | 2011-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V3345509SP |  | SEKAN NO. 8 CLEMONS 69KV | EXP | WERE |  | SEAST |  |  | 533773 | SE8CLEM2 69.000 | [5 empty] | 09SP | [6 empty] | 0.86053 | 0.85954 | 0.89549 | 0.8495 | 0.99552 | 0.93 | 1.05 | CATEGORYB | SINGLE | LITCHFIELD - PITNAC 69KV CKT 1 | 0 | 533765 | LITCH 2 69.000 | 533769 | PITNAC 2 69.000 | 0 |  | 1 |  |  | WERE | Fort Scott 161/69kV Transformer CKT 1 | New 161/69 kV transformer at Ft Scott. | 100 | 110 |  |  |  | 18 | 18 | [5 empty] | 1400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
GEN-2006-010 | Turk | [7 empty] | 507454508078012SP | TO->FROM | SE TEXARKANA - TURK 138KV CKT 1 | U | AEPW | AEPW | SARK | TEXARK | 0 | 507454 | HEMPSTD4 138.00 | 508078 | SETEXAR4 138.00 | 0 |  | 1 |  | 368 | 512 |  |  | 125.3 | [9 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | AEPW | SE TEXARKANA - TURK 138KV CKT 1 | Build new Turk-SE Texarkana 138 kV line and add SE Texarkana 138 kV terminal. | [11 empty] | 26850000 | 26850000 | [39 empty] | 2012-07-01 | 2012-07-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V16485518SP |  | SALLISAW CITY #3 69KV | EXP | GRDA |  | GRDA-MUN |  |  | 512658 | SALICY32 69.000 | [5 empty] | 18SP | [6 empty] | 0.85552 | 0.85229 | 0.87381 | 0.85313 | 0.9683 | 0.9 | 1.05 | CATEGORYB | NONSINGLE | SPP-SWPA-03 | 0 | 0 |  | 0 |  | 0 |  |  |  |  | GRDA | SALLISAW 69KV CAP BANK | Add 20 Mvar cap at Sallisaw 69 kV. | [52 empty] | 2009-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V16475518SP |  | SALLISAW CITY #2 69KV | EXP | GRDA |  | GRDA-MUN |  |  | 512657 | SALICY22 69.000 | [5 empty] | 18SP | [6 empty] | 0.8551 | 0.85186 | 0.87341 | 0.85271 | 0.96793 | 0.9 | 1.05 | CATEGORYB | NONSINGLE | SPP-SWPA-03 | 0 | 0 |  | 0 |  | 0 |  |  |  |  | GRDA | SALLISAW 69KV CAP BANK | Add 20 Mvar cap at Sallisaw 69 kV. | [52 empty] | 2009-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 2 | 2008AGP1AFS31T2851209SH | TO->FROM | S963 8 69.000 - W BROCK8 69.000 69KV CKT 1 | S | OPPD | OPPD | BROOKFLD | BROOKFLD | 0 | 647111 | W BROCK8 69.000 | 647963 | S963 8 69.000 | 0 |  | 1 | 09SH | 57 | 57 | 103.8 | 120.5 | 119.0146 | 119.7551 | [7 empty] | CATEGORYB | SINGLE | HUMBOLT5 161.00 - S1280 5 161.00 161KV CKT 1 | 0 | 640234 | HUMBOLT5 161.00 | 646280 | S1280 5 161.00 | 0 |  | 1 | 68.2604 |  | OPPD | S963 8 69.000 - W BROCK8 69.000 69KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 2 | 2008AGP1AFS31T5281209SP | TO->FROM | S963 8 69.000 - W BROCK8 69.000 69KV CKT 1 | S | OPPD | OPPD | BROOKFLD | BROOKFLD | 0 | 647111 | W BROCK8 69.000 | 647963 | S963 8 69.000 | 0 |  | 1 | 09SP | 57 | 57 | 103.9 | 121.2 | 119.5675 | 123.8184 | [7 empty] | CATEGORYB | SINGLE | HUMBOLT5 161.00 - S1280 5 161.00 161KV CKT 1 | 0 | 640234 | HUMBOLT5 161.00 | 646280 | S1280 5 161.00 | 0 |  | 1 | 70.5765 |  | OPPD | S963 8 69.000 - W BROCK8 69.000 69KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 2 | 2008AGP1AFS31T6131210SP | TO->FROM | S963 8 69.000 - W BROCK8 69.000 69KV CKT 1 | S | OPPD | OPPD | BROOKFLD | BROOKFLD | 0 | 647111 | W BROCK8 69.000 | 647963 | S963 8 69.000 | 0 |  | 1 | 10SP | 57 | 57 | 109.5 | 124.3 | 123.5741 | 124.6239 | [7 empty] | CATEGORYB | SINGLE | HUMBOLT5 161.00 - S1280 5 161.00 161KV CKT 1 | 0 | 640234 | HUMBOLT5 161.00 | 646280 | S1280 5 161.00 | 0 |  | 1 | 71.0356 |  | OPPD | S963 8 69.000 - W BROCK8 69.000 69KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T5552210WP | TO->FROM | S963 8 69.000 - W BROCK8 69.000 69KV CKT 1 | S | OPPD | OPPD | BROOKFLD | BROOKFLD | 0 | 647111 | W BROCK8 69.000 | 647963 | S963 8 69.000 | 0 |  | 1 | 10WP | 57 | 57 | 111.5 | 105.3 | 104.4217 | 104.6979 | [7 empty] | CATEGORYB | SINGLE | HUMBOLT5 161.00 - S1280 5 161.00 161KV CKT 1 | 0 | 640234 | HUMBOLT5 161.00 | 646280 | S1280 5 161.00 | 0 |  | 1 | 59.6778 |  | OPPD | S963 8 69.000 - W BROCK8 69.000 69KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 2 | 2008AGP1AFS31T11793213SP | TO->FROM | S963 8 69.000 - W BROCK8 69.000 69KV CKT 1 | S | OPPD | OPPD | BROOKFLD | BROOKFLD | 0 | 647111 | W BROCK8 69.000 | 647963 | S963 8 69.000 | 0 |  | 1 | 13SP | 57 | 57 | 125.2 | 134 | 133.096 | 136.0763 | [7 empty] | CATEGORYB | SINGLE | HUMBOLT5 161.00 - S1280 5 161.00 161KV CKT 1 | 0 | 640234 | HUMBOLT5 161.00 | 646280 | S1280 5 161.00 | 0 |  | 1 | 77.5635 |  | OPPD | S963 8 69.000 - W BROCK8 69.000 69KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 2 | 2008AGP1AFS31T4703213WP | TO->FROM | S963 8 69.000 - W BROCK8 69.000 69KV CKT 1 | S | OPPD | OPPD | BROOKFLD | BROOKFLD | 0 | 647111 | W BROCK8 69.000 | 647963 | S963 8 69.000 | 0 |  | 1 | 13WP | 57 | 57 | 115.0 | 108.7 | 108.5284 | 109.4947 | [7 empty] | CATEGORYB | SINGLE | HUMBOLT5 161.00 - S1280 5 161.00 161KV CKT 1 | 0 | 640234 | HUMBOLT5 161.00 | 646280 | S1280 5 161.00 | 0 |  | 1 | 62.412 |  | OPPD | S963 8 69.000 - W BROCK8 69.000 69KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 2 | 2008AGP1AFS31T23293218SP | TO->FROM | S963 8 69.000 - W BROCK8 69.000 69KV CKT 1 | S | OPPD | OPPD | BROOKFLD | BROOKFLD | 0 | 647111 | W BROCK8 69.000 | 647963 | S963 8 69.000 | 0 |  | 1 | 18SP | 57 | 57 | 126.7 | 141.1 | 139.8446 | 144.382 | [7 empty] | CATEGORYB | SINGLE | HUMBOLT5 161.00 - S1280 5 161.00 161KV CKT 1 | 0 | 640234 | HUMBOLT5 161.00 | 646280 | S1280 5 161.00 | 0 |  | 1 | 82.2977 |  | OPPD | S963 8 69.000 - W BROCK8 69.000 69KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T22834218SP | FROM->TO | S3456T4T 345.00 345/161KV TRANSFORMER CKT 1 | S | OPPD | OPPD | BROOKFLD | BROOKFLD | 0 | 648056 | S3456T4T 345.00 | 646206 | S1206 5 161.00 | 0 |  | 1 | 18SP | 500 | 500 |  | 103.6 | 103.4721 | 103.329 | [7 empty] | CATEGORYB | SINGLE | S3455 3 345.00 - S3456 3 345.00 345KV CKT 1 | 0 | 645455 | S3455 3 345.00 | 645456 | S3456 3 345.00 | 0 |  | 1 | 516.645 |  | OPPD | S3456T4T 345.00 345/161KV TRANSFORMER CKT 1 | Indeterminate | [52 empty] | 2016-06-01 | 2016-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T22824218SP | FROM->TO | S3456 3 345.00 - S3456T4T 345.00 345KV CKT 1 | S | OPPD | OPPD | BROOKFLD | BROOKFLD | 0 | 645456 | S3456 3 345.00 | 648056 | S3456T4T 345.00 | 0 |  | 1 | 18SP | 500 | 500 |  | 103.6 | 103.4789 | 103.3358 | [7 empty] | CATEGORYB | SINGLE | S3455 3 345.00 - S3456 3 345.00 345KV CKT 1 | 0 | 645455 | S3455 3 345.00 | 645456 | S3456 3 345.00 | 0 |  | 1 | 516.679 |  | OPPD | S3456 3 345.00 - S3456T4T 345.00 345KV CKT 1 | Indeterminate | [52 empty] | 2016-06-01 | 2016-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T3044209FA | FROM->TO | RUSSELLVILLE EAST - RUSSELLVILLE SOUTH 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 337905 | 5RUSL-E 161.00 | 337904 | 5RUSL-S 161.00 | 0 |  | 1 | 09FA | 335 | 335 |  | 115.6 | 110.4714 | 106.9429 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 | 358.2587 |  | EES | RUSSELLVILLE EAST - RUSSELLVILLE SOUTH 161KV CKT 1 | Rebuild Transmission Line 4.10 miles | [52 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FNSL | FDNS-Iteration limit exceeded | FNSL | FDNS-Iteration limit exceeded | 2 | 2 | 2008AGP1AFS32T32209SP | FROM->TO | RUSSELLVILLE EAST - RUSSELLVILLE SOUTH 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 337905 | 5RUSL-E 161.00 | 337904 | 5RUSL-S 161.00 | 0 |  | 1 | 09SP | 335 | 335 |  | 129.4 | 126.2307 | 121.5083 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 | 407.0528 |  | EES | RUSSELLVILLE EAST - RUSSELLVILLE SOUTH 161KV CKT 1 | Rebuild Transmission Line 4.10 miles | [52 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T4822209WP | FROM->TO | RUSSELLVILLE EAST - RUSSELLVILLE SOUTH 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 337905 | 5RUSL-E 161.00 | 337904 | 5RUSL-S 161.00 | 0 |  | 1 | 09WP | 335 | 335 |  | 102.5 | 96.3352 | 102.0943 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 | 342.0159 |  | EES | RUSSELLVILLE EAST - RUSSELLVILLE SOUTH 161KV CKT 1 | Rebuild Transmission Line 4.10 miles | [52 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T11852210SP | FROM->TO | RUSSELLVILLE EAST - RUSSELLVILLE SOUTH 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 337905 | 5RUSL-E 161.00 | 337904 | 5RUSL-S 161.00 | 0 |  | 1 | 10SP | 335 | 335 |  | 144.8 | 136.6309 | 141.1692 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 | 472.9168 |  | EES | RUSSELLVILLE EAST - RUSSELLVILLE SOUTH 161KV CKT 1 | Rebuild Transmission Line 4.10 miles | [52 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T7602210WP | FROM->TO | RUSSELLVILLE EAST - RUSSELLVILLE SOUTH 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 337905 | 5RUSL-E 161.00 | 337904 | 5RUSL-S 161.00 | 0 |  | 1 | 10WP | 335 | 335 |  | 137.4 | 131.0353 | 133.6693 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 | 447.7921 |  | EES | RUSSELLVILLE EAST - RUSSELLVILLE SOUTH 161KV CKT 1 | Rebuild Transmission Line 4.10 miles | [52 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T18322213SP | FROM->TO | RUSSELLVILLE EAST - RUSSELLVILLE SOUTH 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 337905 | 5RUSL-E 161.00 | 337904 | 5RUSL-S 161.00 | 0 |  | 1 | 13SP | 335 | 335 |  | 155 | 146.1402 | 148.884 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 | 498.7614 |  | EES | RUSSELLVILLE EAST - RUSSELLVILLE SOUTH 161KV CKT 1 | Rebuild Transmission Line 4.10 miles | [52 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T7022213WP | FROM->TO | RUSSELLVILLE EAST - RUSSELLVILLE SOUTH 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 337905 | 5RUSL-E 161.00 | 337904 | 5RUSL-S 161.00 | 0 |  | 1 | 13WP | 335 | 335 |  | 128.6 | 121.3721 | 125.5939 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 | 420.7396 |  | EES | RUSSELLVILLE EAST - RUSSELLVILLE SOUTH 161KV CKT 1 | Rebuild Transmission Line 4.10 miles | [52 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T30022218SP | FROM->TO | RUSSELLVILLE EAST - RUSSELLVILLE SOUTH 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 337905 | 5RUSL-E 161.00 | 337904 | 5RUSL-S 161.00 | 0 |  | 1 | 18SP | 335 | 335 |  | 154.5 | 146.4173 | 147.8508 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 | 495.3002 |  | EES | RUSSELLVILLE EAST - RUSSELLVILLE SOUTH 161KV CKT 1 | Rebuild Transmission Line 4.10 miles | [52 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FNSL | FDNS-Iteration limit exceeded | FNSL | FDNS-Iteration limit exceeded | 2 | 2 | 2008AGP1AFS32T42209SP | TO->FROM | RUSSELLVILLE EAST - RUSSELLVILLE NORTH 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 337906 | 5RUSL-N 161.00 | 337905 | 5RUSL-E 161.00 | 0 |  | 1 | 09SP | 396 | 396 |  | 111.4 | 109.5845 | 106.9281 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 | 423.4353 |  | EES | RUSSELLVILLE EAST - RUSSELLVILLE NORTH 161KV CKT 1 | Rebuild Transmission Line 3.19 miles | [12 empty] | 4910000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T11862210SP | TO->FROM | RUSSELLVILLE EAST - RUSSELLVILLE NORTH 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 337906 | 5RUSL-N 161.00 | 337905 | 5RUSL-E 161.00 | 0 |  | 1 | 10SP | 396 | 396 |  | 120.9 | 116.4067 | 118.9015 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 | 470.8499 |  | EES | RUSSELLVILLE EAST - RUSSELLVILLE NORTH 161KV CKT 1 | Rebuild Transmission Line 3.19 miles | [12 empty] | 4910000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T7612210WP | TO->FROM | RUSSELLVILLE EAST - RUSSELLVILLE NORTH 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 337906 | 5RUSL-N 161.00 | 337905 | 5RUSL-E 161.00 | 0 |  | 1 | 10WP | 396 | 396 |  | 110.6 | 107.1314 | 108.5045 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 | 429.6778 |  | EES | RUSSELLVILLE EAST - RUSSELLVILLE NORTH 161KV CKT 1 | Rebuild Transmission Line 3.19 miles | [12 empty] | 4910000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T18332213SP | TO->FROM | RUSSELLVILLE EAST - RUSSELLVILLE NORTH 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 337906 | 5RUSL-N 161.00 | 337905 | 5RUSL-E 161.00 | 0 |  | 1 | 13SP | 396 | 396 |  | 130 | 125.0033 | 126.521 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 | 501.0232 |  | EES | RUSSELLVILLE EAST - RUSSELLVILLE NORTH 161KV CKT 1 | Rebuild Transmission Line 3.19 miles | [12 empty] | 4910000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T7032213WP | TO->FROM | RUSSELLVILLE EAST - RUSSELLVILLE NORTH 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 337906 | 5RUSL-N 161.00 | 337905 | 5RUSL-E 161.00 | 0 |  | 1 | 13WP | 396 | 396 |  | 108 | 104.0672 | 106.3414 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 | 421.1119 |  | EES | RUSSELLVILLE EAST - RUSSELLVILLE NORTH 161KV CKT 1 | Rebuild Transmission Line 3.19 miles | [12 empty] | 4910000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T30032218SP | TO->FROM | RUSSELLVILLE EAST - RUSSELLVILLE NORTH 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 337906 | 5RUSL-N 161.00 | 337905 | 5RUSL-E 161.00 | 0 |  | 1 | 18SP | 396 | 396 |  | 135 | 130.2742 | 131.0538 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 | 518.9731 |  | EES | RUSSELLVILLE EAST - RUSSELLVILLE NORTH 161KV CKT 1 | Rebuild Transmission Line 3.19 miles | [12 empty] | 4910000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V3525509SP |  | RUSSELL 115KV | EXP | MKEC |  |  |  |  | 539701 | RUSSELL3 115.00 | [5 empty] | 09SP | [8 empty] | 0.92431 | 0.89463 | 0.96331 | 0.9 | 1.05 | CATEGORYB | SINGLE | CONCORDIA - ELMCREK6 230.00 230KV CKT 1 | 0 | 539639 | ELMCREK6 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V7365509SP |  | RUSSELL 115KV | EXP | MKEC |  |  |  |  | 539701 | RUSSELL3 115.00 | [5 empty] | 09SP | [8 empty] | 0.92434 | 0.89466 | 0.96331 | 0.9 | 1.05 | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539658 | CONCRD6 230.00 | 539657 | CONCORD3 115.00 | 539904 | CONCOD-T 13.800 | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17203318SP |  | RULTON 3 115KV | REL | MIDW |  | REG E-IL |  |  | 530615 | RULTON 3 115.00 | [5 empty] | 18SP | [8 empty] | 0.92573 | 0.8931 | 0.99854 | 0.9 | 1.05 | CATEGORYB | SINGLE | MINGO (MINGO) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 531451 | MINGO 7 345.00 | 531429 | MINGO 3 115.00 | 531452 | MINGTER1 13.800 | 1 |  |  | SUNC | RULETON 115KV Capacitor | Install Second 12 Mvar cap bank at Ruleton 115kV | [12 empty] | 486000 | 2008-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17253318SP |  | RULETON 115KV | REL | SUNC |  | GREAT PL |  |  | 531357 | RULETON3 115.00 | [5 empty] | 18SP | [8 empty] | 0.92573 | 0.8931 | 0.99854 | 0.9 | 1.05 | CATEGORYB | SINGLE | MINGO (MINGO) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 531451 | MINGO 7 345.00 | 531429 | MINGO 3 115.00 | 531452 | MINGTER1 13.800 | 1 |  |  | SUNC | RULETON 115KV Capacitor | Install Second 12 Mvar cap bank at Ruleton 115kV | [12 empty] | 486000 | 2008-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T3224209FA | FROM->TO | ROSE HILL (ROSEHL3X) 345/138/13.8KV TRANSFORMER CKT 1 | CP | WERE |  | SCENTRAL |  | 2 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532827 | ROSEH3 1 13.800 | 1 | 09FA | 400 | 440 |  |  | 100.5825 | 101.1066 | [7 empty] | CATEGORYB | SINGLE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532826 | ROSEH1 1 13.800 | 1 | 444.869 |  | WERE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 Displacement | Add third 345-138 kV transformer at Rose Hill | 400 | 440 | 400 | 440 | 0 | 15 | 2 | Y | 0 | 0 | 0 | Like existing Rose Hill 345-138 units | [40 empty] | 2009-04-01 | 2011-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T4904209G | FROM->TO | ROSE HILL (ROSEHL3X) 345/138/13.8KV TRANSFORMER CKT 1 | CP | WERE |  | SCENTRAL |  | 2 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532827 | ROSEH3 1 13.800 | 1 | 09G | 400 | 440 |  |  | 101.4644 | 101.064 | [7 empty] | CATEGORYB | SINGLE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532826 | ROSEH1 1 13.800 | 1 | 444.6816 |  | WERE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 Displacement | Add third 345-138 kV transformer at Rose Hill | 400 | 440 | 400 | 440 | 0 | 15 | 2 | Y | 0 | 0 | 0 | Like existing Rose Hill 345-138 units | [40 empty] | 2009-04-01 | 2011-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T12492210SP | FROM->TO | ROSE HILL (ROSEHL3X) 345/138/13.8KV TRANSFORMER CKT 1 | CP | WERE |  | SCENTRAL |  | 2 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532827 | ROSEH3 1 13.800 | 1 | 10SP | 400 | 440 | 102.3 | 102.7 | 98.7634 | 103.0352 | [7 empty] | CATEGORYB | SINGLE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532826 | ROSEH1 1 13.800 | 1 | 453.3549 |  | WERE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 Displacement | Add third 345-138 kV transformer at Rose Hill | 400 | 440 | 400 | 440 | 0 | 15 | 2 | Y | 0 | 0 | 0 | Like existing Rose Hill 345-138 units | [40 empty] | 2009-04-01 | 2011-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T3234209FA | FROM->TO | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 1 | CP | WERE |  | SCENTRAL |  | 2 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532826 | ROSEH1 1 13.800 | 1 | 09FA | 400 | 440 |  |  | 100.5495 | 101.0591 | [7 empty] | CATEGORYB | SINGLE | ROSE HILL (ROSEHL3X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532827 | ROSEH3 1 13.800 | 1 | 444.66 |  | WERE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 Displacement | Add third 345-138 kV transformer at Rose Hill | 400 | 440 | 400 | 440 | 0 | 15 | 2 | Y | 0 | 0 | 0 | Like existing Rose Hill 345-138 units | [40 empty] | 2009-04-01 | 2011-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T4914209G | FROM->TO | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 1 | CP | WERE |  | SCENTRAL |  | 2 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532826 | ROSEH1 1 13.800 | 1 | 09G | 400 | 440 |  |  | 101.4335 | 101.0343 | [7 empty] | CATEGORYB | SINGLE | ROSE HILL (ROSEHL3X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532827 | ROSEH3 1 13.800 | 1 | 444.5509 |  | WERE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 Displacement | Add third 345-138 kV transformer at Rose Hill | 400 | 440 | 400 | 440 | 0 | 15 | 2 | Y | 0 | 0 | 0 | Like existing Rose Hill 345-138 units | [40 empty] | 2009-04-01 | 2011-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T12502210SP | FROM->TO | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 1 | CP | WERE |  | SCENTRAL |  | 2 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532826 | ROSEH1 1 13.800 | 1 | 10SP | 400 | 440 | 102.2 | 102.7 | 98.7148 | 102.9828 | [7 empty] | CATEGORYB | SINGLE | ROSE HILL (ROSEHL3X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532827 | ROSEH3 1 13.800 | 1 | 453.1243 |  | WERE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 Displacement | Add third 345-138 kV transformer at Rose Hill | 400 | 440 | 400 | 440 | 0 | 15 | 2 | Y | 0 | 0 | 0 | Like existing Rose Hill 345-138 units | [40 empty] | 2009-04-01 | 2011-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T681310SP | FROM->TO | RIVERSIDE STATION - TULSA POWER STATION 138KV CKT 1 | S | AEPW | AEPW | TULSA | TULSA | 0 | 509783 | R.S.S.-4 138.00 | 509788 | T.P.S.-4 138.00 | 0 |  | 1 | 10SP | 161 | 187 |  |  | 86.3889 | 100.1583 | [7 empty] | CATEGORYB | SINGLE | RIVERSIDE STATION - SAPULPA ROAD 345KV CKT 1 | 0 | 509782 | R.S.S.-7 345.00 | 509870 | SAPLPRD7 345.00 | 0 |  | 1 | 187.296 |  | AEPW | RIVERSIDE STATION - TULSA POWER STATION 138KV CKT 1 | Rebuild 5.82 miles with 1272 ACSR. Replace TPS wavetrap & jumpers. Reset TPS CTs | 280 | 331 | 332 | 374 | 5.82 | 20 | 5 |  | 0.0046 | 0.03366 | 0.01001 | Limiting factor will be Riverside Jumpers | 6200000 | 2008-07-30 | [38 empty] | 2010-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T1231313SP | FROM->TO | RIVERSIDE STATION - TULSA POWER STATION 138KV CKT 1 | S | AEPW | AEPW | TULSA | TULSA | 0 | 509783 | R.S.S.-4 138.00 | 509788 | T.P.S.-4 138.00 | 0 |  | 1 | 13SP | 161 | 187 |  |  | 86.6267 | 107.5142 | [7 empty] | CATEGORYB | SINGLE | RIVERSIDE STATION - SAPULPA ROAD 345KV CKT 1 | 0 | 509782 | R.S.S.-7 345.00 | 509870 | SAPLPRD7 345.00 | 0 |  | 1 | 201.0516 |  | AEPW | RIVERSIDE STATION - TULSA POWER STATION 138KV CKT 1 | Rebuild 5.82 miles with 1272 ACSR. Replace TPS wavetrap & jumpers. Reset TPS CTs | 280 | 331 | 332 | 374 | 5.82 | 20 | 5 |  | 0.0046 | 0.03366 | 0.01001 | Limiting factor will be Riverside Jumpers | 6200000 | 2008-07-30 | [38 empty] | 2010-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T1271313SP | FROM->TO | RIVERSIDE STATION - TULSA POWER STATION 138KV CKT 1 | S | AEPW | AEPW | TULSA | TULSA | 0 | 509783 | R.S.S.-4 138.00 | 509788 | T.P.S.-4 138.00 | 0 |  | 1 | 13SP | 161 | 187 |  |  | 85.5154 | 106.6802 | [7 empty] | CATEGORYB | SINGLE | OAKS EAST TAP - RIVERSIDE STATION 138KV CKT 1 | 0 | 509783 | R.S.S.-4 138.00 | 509850 | OAKSETP4 138.00 | 0 |  | 1 | 199.492 |  | AEPW | RIVERSIDE STATION - TULSA POWER STATION 138KV CKT 1 | Rebuild 5.82 miles with 1272 ACSR. Replace TPS wavetrap & jumpers. Reset TPS CTs | 280 | 331 | 332 | 374 | 5.82 | 20 | 5 |  | 0.0046 | 0.03366 | 0.01001 | Limiting factor will be Riverside Jumpers | 6200000 | 2008-07-30 | [38 empty] | 2010-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T1301313SP | FROM->TO | RIVERSIDE STATION - TULSA POWER STATION 138KV CKT 1 | S | AEPW | AEPW | TULSA | TULSA | 0 | 509783 | R.S.S.-4 138.00 | 509788 | T.P.S.-4 138.00 | 0 |  | 1 | 13SP | 161 | 187 |  |  | 81.7186 | 102.9213 | [7 empty] | CATEGORYB | SINGLE | OAKS EAST TAP - TULSA POWER STATION 138KV CKT 1 | 0 | 509788 | T.P.S.-4 138.00 | 509850 | OAKSETP4 138.00 | 0 |  | 1 | 192.4628 |  | AEPW | RIVERSIDE STATION - TULSA POWER STATION 138KV CKT 1 | Rebuild 5.82 miles with 1272 ACSR. Replace TPS wavetrap & jumpers. Reset TPS CTs | 280 | 331 | 332 | 374 | 5.82 | 20 | 5 |  | 0.0046 | 0.03366 | 0.01001 | Limiting factor will be Riverside Jumpers | 6200000 | 2008-07-30 | [38 empty] | 2010-06-01 | 2012-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 2 | 2008AGP1AFS31V9093213SP |  | RILEY 3 115.00 115KV | REL | WERE |  | NCENTRAL |  |  | 533319 | RILEY 3 115.00 | [5 empty] | 13SP | [7 empty] | 0.92574 | 0.89813 | 0.87649 | 0.91506 | 0.93 | 1.05 | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17633318SP |  | RILEY 3 115.00 115KV | REL | WERE |  | NCENTRAL |  |  | 533319 | RILEY 3 115.00 | [5 empty] | 18SP | [7 empty] | 0.92598 | 0.89789 | 0.85486 | 0.90526 | 0.93 | 1.05 | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
NA | [8 empty] | NAWERERENNO 2X731 |  | RENO 345/115KV CKT 2 | U | WERE | WERE |  |  | 1 | 532771 | RENO 7 345.00 | 533416 | RENO 3 115.00 | 532810 |  | 1 | [15 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WERE | RENO 345/115KV CKT 2 | Install 2nd stepdown transformer at Reno County substation east northeast of Hutchinson | [52 empty] | 2010-06-01 | 2010-06-01
NA | [8 empty] | NAWERERENNO 1X731 |  | RENO 345/115KV CKT 1 | U | WERE | WERE |  |  | 1 | 532771 | RENO 7 345.00 | 533416 | RENO 3 115.00 | 532807 |  | 1 | [15 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WERE | RENO 345/115KV CKT 1 | New stepdown transformer at a new substation in Reno County east northeast of Hutchinson | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 | 5219 - STIREDSTIPEC | FDNS |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T1671309SH | TO->FROM | REDEL - STILWELL 161KV CKT 1 | EXP | KACP | KACP | JOCO | JOCO | 0 | 542969 | STILWEL5 161.00 | 543053 | REDEL 5 161.00 | 0 |  | 1 | 09SH | 293 | 335 |  | 101.5 | 100.3094 | 102.6059 | [7 empty] | CATEGORYB | SINGLE | PECULIAR - STILWELL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 | 343.7298 |  | MIPU | South Harper 161 kV cut-in to Stilwell-Archie JCT 161 kV line | To tap Stilwell-Archie JCT 161 kV line into South Harper 161 kV sub and make it two new 161 kV sections: Stilwell-South Harper and Archie JCT- South Harper . | [5 empty] | 18 | 18 | [5 empty] | 2259673 | 2009-03-19 | [38 empty] | 2009-04-01 | 2010-10-01
2008-AGP1 | AFS3 | 5219 - STIREDSTIPEC | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T2743310SP | TO->FROM | REDEL - STILWELL 161KV CKT 1 | CP | KACP | KACP | JOCO | JOCO | 0 | 542969 | STILWEL5 161.00 | 543053 | REDEL 5 161.00 | 0 |  | 1 | 10SP | 293 | 335 |  | 105.8 | 103.2089 | 109.509 | [7 empty] | CATEGORYB | SINGLE | PECULIAR - STILWELL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 | 366.8552 | reconductor with 1192 acss / 584 | KACP | REDEL - STILWELL 161KV CKT 1 | Reconductor line with 1192 ACSS and upgrade terminal equipment for 2000 amps | 558 | 558 |  |  |  | 24 | 4 | [5 empty] | 2200000 | 2008-02-21 | [38 empty] | 2009-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T2511318SP | FROM->TO | PRYOR JUNCTION (PRY-JCT1) 115/69/13.8KV TRANSFORMER CKT 1 | REL | AEPW |  | NORTHERN |  | 2 | 510407 | PRY-JCT3 115.00 | 510400 | PRY-JCT2 69.000 | 510371 | PRYJT1-1 13.800 | 1 | 18SP | 75 | 83 | 105.0 | 106.4 | 102.43 | 106.6717 | [7 empty] | CATEGORYB | SINGLE | CATOOSA - INOLA TAP 138KV CKT 1 | 0 | 509752 | INOLATP4 138.00 | 509790 | CATOOSA4 138.00 | 0 |  | 1 | 88.5375 |  | AEPW | PRYOR JUNCTION (PRY-JCT1) 115/69/13.8KV TRANSFORMER CKT 1 | Replace transformer | [52 empty] | 2015-06-01 | 2015-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T2531318SP | FROM->TO | PRYOR JUNCTION (PRY-JCT1) 115/69/13.8KV TRANSFORMER CKT 1 | REL | AEPW |  | NORTHERN |  | 2 | 510407 | PRY-JCT3 115.00 | 510400 | PRY-JCT2 69.000 | 510371 | PRYJT1-1 13.800 | 1 | 18SP | 75 | 83 |  |  | 96.1529 | 100.2693 | [7 empty] | CATEGORYB | SINGLE | CHOUTEAU - INOLA TAP 138KV CKT 1 | 0 | 509752 | INOLATP4 138.00 | 510373 | CHOUTEA4 138.00 | 0 |  | 1 | 83.2235 |  | AEPW | PRYOR JUNCTION (PRY-JCT1) 115/69/13.8KV TRANSFORMER CKT 1 | Replace transformer | [52 empty] | 2015-06-01 | 2015-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 3 | 2008AGP1AFS31T10382309SP | TO->FROM | PONT DES MOUTON - WELLS 230KV CKT 1 | S | CELE | LAFA | CLE_CENTRAL | LAFA | 0 | 500940 | WELLS 6 230.00 | 502410 | PMOUTON6 230.00 | 0 |  | 1 | 09SP | 696 | 797 | 101.6 |  | 99.0665 | 101.1505 | [7 empty] | CATEGORYB | NONSINGLE | SERCW-21 | 0 | 0 |  | 0 |  | 0 |  |  | 806.1695 |  | CELE | PONT DES MOUTON - WELLS 230KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T16451313SP | TO->FROM | PONT DES MOUTON - WELLS 230KV CKT 1 | S | CELE | LAFA | CLE_CENTRAL | LAFA | 0 | 500940 | WELLS 6 230.00 | 502410 | PMOUTON6 230.00 | 0 |  | 1 | 13SP | 696 | 797 | 113.6 | 109.5 | 109.6433 | 113.8557 | [7 empty] | CATEGORYB | NONSINGLE | SERCW-21 | 0 | 0 |  | 0 |  | 0 |  |  | 907.4299 |  | CELE | PONT DES MOUTON - WELLS 230KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 | CONT-1202 - Jarbalo - Stranger Creek 115kV |  |  | FDNS |  | 3 | 1 | 2008AGP1AFS31T2153110SP | FROM->TO | PLATTE CITY - SMITHVILLE 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541221 | PLTCTY 5 161.00 | 541204 | SMTHVL 5 161.00 | 0 |  | 1 | 10SP | 223 | 245 |  |  | 95.0973 | 100.4148 | [7 empty] | CATEGORYB | SINGLE | IATAN - ST JOE 345KV CKT 1 | 0 | 541199 | ST JOE 3 345.00 | 542982 | IATAN 7 345.00 | 0 |  | 1 | 246.0163 | Replace wavetrap | MIPU | PLATTE CITY - SMITHVILLE 161KV CKT 1 #1 | Increase the normal/emergency ratings to 233/265 MVA by replacing wave trapes | 233 | 265 |  |  |  | 6 | 6 | [5 empty] | 50000 | 2009-03-19 | [38 empty] | 2010-06-01 | 2010-12-01
2008-AGP1 | AFS3 | CONT-1202 - Jarbalo - Stranger Creek 115kV | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T745510WP | FROM->TO | PLATTE CITY - SMITHVILLE 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541221 | PLTCTY 5 161.00 | 541204 | SMTHVL 5 161.00 | 0 |  | 1 | 10WP | 223 | 245 |  | 103.7 | 103.8415 | 108.4806 | [7 empty] | CATEGORYB | SINGLE | IATAN - ST JOE 345KV CKT 1 | 0 | 541199 | ST JOE 3 345.00 | 542982 | IATAN 7 345.00 | 0 |  | 1 | 265.7775 | Replace wavetrap | MIPU | PLATTE CITY - SMITHVILLE 161KV CKT 1 #1 | Increase the normal/emergency ratings to 233/265 MVA by replacing wave trapes | 233 | 265 |  |  |  | 6 | 6 | [5 empty] | 50000 | 2009-03-19 | [38 empty] | 2010-06-01 | 2010-12-01
2008-AGP1 | AFS3 | CONT-1202 - Jarbalo - Stranger Creek 115kV |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T1155513WP | FROM->TO | PLATTE CITY - SMITHVILLE 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541221 | PLTCTY 5 161.00 | 541204 | SMTHVL 5 161.00 | 0 |  | 1 | 13WP | 223 | 245 |  |  | 97.0932 | 102.7599 | [7 empty] | CATEGORYB | SINGLE | IATAN - ST JOE 345KV CKT 1 | 0 | 541199 | ST JOE 3 345.00 | 542982 | IATAN 7 345.00 | 0 |  | 1 | 251.7618 | Replace wavetrap | MIPU | PLATTE CITY - SMITHVILLE 161KV CKT 1 #1 | Increase the normal/emergency ratings to 233/265 MVA by replacing wave trapes | 233 | 265 |  |  |  | 6 | 6 | [5 empty] | 50000 | 2009-03-19 | [38 empty] | 2010-06-01 | 2010-12-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V3335509SP |  | PITNAC 69KV | EXP | WERE |  | SEAST |  |  | 533769 | PITNAC 2 69.000 | [5 empty] | 09SP | [6 empty] | 0.85378 | 0.85277 | 0.89205 | 0.84188 | 1.0033 | 0.93 | 1.05 | CATEGORYB | SINGLE | LITCHFIELD - PITNAC 69KV CKT 1 | 0 | 533765 | LITCH 2 69.000 | 533769 | PITNAC 2 69.000 | 0 |  | 1 |  |  | WERE | Fort Scott 161/69kV Transformer CKT 1 | New 161/69 kV transformer at Ft Scott. | 100 | 110 |  |  |  | 18 | 18 | [5 empty] | 1400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T9495509SP | TO->FROM | PIONEER TAP - PLYMELL 115KV CKT 1 | EXP | SUNC | SUNC | PIONEER | PIONEER | 0 | 531393 | PLYMELL3 115.00 | 531392 | PIONTAP3 115.00 | 0 |  | 1 | 09SP | 120 | 143 |  |  | 90.3117 | 108.4414 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SUNC-05 | 0 | 0 |  | 0 |  | 0 |  |  | 155.0712 |  | SUNC | PIONEER TAP - PLYMELL 115KV CKT 1 | Rebuild Plymell to Pioneer Tap | 185 | 222 |  |  | 14 | 24 | 24 |  | 0.01044 | 0.07657 | 0.01098 |  | 2441600 | 2006-06-01 | [38 empty] | 2009-06-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T1155509SP | TO->FROM | PIONEER TAP - PLYMELL 115KV CKT 1 | EXP | SUNC | SUNC | PIONEER | PIONEER | 0 | 531393 | PLYMELL3 115.00 | 531392 | PIONTAP3 115.00 | 0 |  | 1 | 09SP | 120 | 143 |  |  | 90.1996 | 107.8432 | [7 empty] | CATEGORYB | SINGLE | FLETCHER - HOLCOMB 115KV CKT 1 | 0 | 531420 | FLETCHR3 115.00 | 531448 | HOLCOMB3 115.00 | 0 |  | 1 | 154.2158 |  | SUNC | PIONEER TAP - PLYMELL 115KV CKT 1 | Rebuild Plymell to Pioneer Tap | 185 | 222 |  |  | 14 | 24 | 24 |  | 0.01044 | 0.07657 | 0.01098 |  | 2441600 | 2006-06-01 | [38 empty] | 2009-06-01 | 2010-01-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T6285509SP | TO->FROM | PIONEER TAP - PLYMELL 115KV CKT 1 | EXP | SUNC | SUNC | PIONEER | PIONEER | 0 | 531393 | PLYMELL3 115.00 | 531392 | PIONTAP3 115.00 | 0 |  | 1 | 09SP | 120 | 143 |  |  | 79.994 | 103.6513 | [7 empty] | CATEGORYB | SINGLE | HOLCOMB (HOLCOMB) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 531448 | HOLCOMB3 115.00 | 531449 | HOLCOMB7 345.00 | 531450 | HOLCTER1 13.800 | 1 | 148.2214 |  | SUNC | PIONEER TAP - PLYMELL 115KV CKT 1 | Rebuild Plymell to Pioneer Tap | 185 | 222 |  |  | 14 | 24 | 24 |  | 0.01044 | 0.07657 | 0.01098 |  | 2441600 | 2006-06-01 | [38 empty] | 2009-06-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 2 | 2008AGP1AFS31T1551210SP | TO->FROM | PIONEER TAP - PLYMELL 115KV CKT 1 | EXP | SUNC | SUNC | PIONEER | PIONEER | 0 | 531393 | PLYMELL3 115.00 | 531392 | PIONTAP3 115.00 | 0 |  | 1 | 10SP | 120 | 143 |  |  | 93.2286 | 101.8715 | [7 empty] | CATEGORYB | SINGLE | FLETCHER - HOLCOMB 115KV CKT 1 | 0 | 531420 | FLETCHR3 115.00 | 531448 | HOLCOMB3 115.00 | 0 |  | 1 | 145.6762 |  | SUNC | PIONEER TAP - PLYMELL 115KV CKT 1 | Rebuild Plymell to Pioneer Tap | 185 | 222 |  |  | 14 | 24 | 24 |  | 0.01044 | 0.07657 | 0.01098 |  | 2441600 | 2006-06-01 | [38 empty] | 2009-06-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 2 | 2008AGP1AFS31T14133210SP | TO->FROM | PIONEER TAP - PLYMELL 115KV CKT 1 | EXP | SUNC | SUNC | PIONEER | PIONEER | 0 | 531393 | PLYMELL3 115.00 | 531392 | PIONTAP3 115.00 | 0 |  | 1 | 10SP | 120 | 143 |  |  | 93.532 | 100.2906 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SUNC-05 | 0 | 0 |  | 0 |  | 0 |  |  | 143.4156 |  | SUNC | PIONEER TAP - PLYMELL 115KV CKT 1 | Rebuild Plymell to Pioneer Tap | 185 | 222 |  |  | 14 | 24 | 24 |  | 0.01044 | 0.07657 | 0.01098 |  | 2441600 | 2006-06-01 | [38 empty] | 2009-06-01 | 2010-01-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31V2652218SP |  | PIGGOTT CAP BANK 1 69KV | REL | SWPA |  | EMINTH |  |  | 505631 | PIG CAP2 69.000 | [5 empty] | 18SP | [7 empty] | 0.88939 | 0.89417 | 0.84701 | 1.0013 | 0.9 | 1.05 | CATEGORYB | SINGLE | KENNETT - NEW MADRID 161KV CKT 1 | 0 | 505400 | N MADRD5 161.00 | 505410 | KENNETT5 161.00 | 0 |  | 1 |  |  | SWPA | KENNETT CAP BANK 1 161KV CAP BANK | Install Additional Cap Bank at Kennett | [52 empty] | 2014-06-01 | 2014-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31V2532218SP |  | PIGGOTT 69KV | REL | SWPA |  | EMINTH |  |  | 505406 | PIGGOTT2 69.000 | [5 empty] | 18SP | [7 empty] | 0.88937 | 0.89416 | 0.847 | 1.0013 | 0.9 | 1.05 | CATEGORYB | SINGLE | KENNETT - NEW MADRID 161KV CKT 1 | 0 | 505400 | N MADRD5 161.00 | 505410 | KENNETT5 161.00 | 0 |  | 1 |  |  | SWPA | KENNETT CAP BANK 1 161KV CAP BANK | Install Additional Cap Bank at Kennett | [52 empty] | 2014-06-01 | 2014-06-01
2008-AGP1 | AFS3 |  |  |  | FNSL | FDNS-Iteration limit exceeded | 3 | 2 | 2008AGP1AFS32V93213SP |  | PHILLIPSBURG 115KV | REL | MKEC |  |  |  |  | 539685 | PHLBURG3 115.00 | [5 empty] | 13SP | [8 empty] | 0.97701 | 0.88925 | 0.98486 | 0.9 | 1.05 | CATEGORYB | SINGLE | EAST MANHATTAN - ELMCREK6 230.00 230KV CKT 1 | 0 | 539639 | ELMCREK6 230.00 | 532861 | EMANHAT6 230.00 | 0 |  | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17163318SP |  | PHEASANT RUN 115KV | REL | MIDW |  | REG E-IL |  |  | 530559 | PH RUN 3 115.00 | [5 empty] | 18SP | [8 empty] | 0.92631 | 0.89663 | 1.0228 | 0.9 | 1.05 | CATEGORYB | SINGLE | MINGO (MINGO) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 531451 | MINGO 7 345.00 | 531429 | MINGO 3 115.00 | 531452 | MINGTER1 13.800 | 1 |  |  | SUNC | RULETON 115KV Capacitor | Install Second 12 Mvar cap bank at Ruleton 115kV | [12 empty] | 486000 | 2008-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31V2692218SP |  | PARAGOULD CAP BANK 1 69KV | REL | SWPA |  | EMINTH |  |  | 505635 | PRG CAP2 69.000 | [5 empty] | 18SP | [8 empty] | 0.91964 | 0.88665 | 1.0145 | 0.9 | 1.05 | CATEGORYB | SINGLE | KENNETT - NEW MADRID 161KV CKT 1 | 0 | 505400 | N MADRD5 161.00 | 505410 | KENNETT5 161.00 | 0 |  | 1 |  |  | SWPA | KENNETT CAP BANK 1 161KV CAP BANK | Install Additional Cap Bank at Kennett | [52 empty] | 2014-06-01 | 2014-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31V2682218SP |  | PARAGOULD CAP BANK 1 161KV | REL | SWPA |  | EMINTH |  |  | 505634 | PRG CAP5 161.00 | [5 empty] | 18SP | [7 empty] | 0.84769 | 0.85184 | 0.82355 | 0.98277 | 0.9 | 1.05 | CATEGORYB | SINGLE | KENNETT - NEW MADRID 161KV CKT 1 | 0 | 505400 | N MADRD5 161.00 | 505410 | KENNETT5 161.00 | 0 |  | 1 |  |  | SWPA | KENNETT CAP BANK 1 161KV CAP BANK | Install Additional Cap Bank at Kennett | [52 empty] | 2014-06-01 | 2014-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31V2572218SP |  | PARAGOULD 69KV | REL | SWPA |  | EMINTH |  |  | 505414 | PARAGLD2 69.000 | [5 empty] | 18SP | [8 empty] | 0.91962 | 0.88663 | 1.0145 | 0.9 | 1.05 | CATEGORYB | SINGLE | KENNETT - NEW MADRID 161KV CKT 1 | 0 | 505400 | N MADRD5 161.00 | 505410 | KENNETT5 161.00 | 0 |  | 1 |  |  | SWPA | KENNETT CAP BANK 1 161KV CAP BANK | Install Additional Cap Bank at Kennett | [52 empty] | 2014-06-01 | 2014-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31V2562218SP |  | PARAGOULD 161KV | REL | SWPA |  | EMINTH |  |  | 505412 | PARAGLD5 161.00 | [5 empty] | 18SP | [7 empty] | 0.8476 | 0.85176 | 0.82347 | 0.98267 | 0.9 | 1.05 | CATEGORYB | SINGLE | KENNETT - NEW MADRID 161KV CKT 1 | 0 | 505400 | N MADRD5 161.00 | 505410 | KENNETT5 161.00 | 0 |  | 1 |  |  | SWPA | KENNETT CAP BANK 1 161KV CAP BANK | Install Additional Cap Bank at Kennett | [52 empty] | 2014-06-01 | 2014-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T11822210SP | FROM->TO | OZARK - VAN BUREN 161KV CKT 1 | REL | SWPA | SWPA | EMINTH | EMINTH | 0 | 505516 | OZARK H5 161.00 | 505522 | VAN BUR5 161.00 | 0 |  | 1 | 10SP | 167 | 167 |  | 105.7 | 103.6881 | 103.6943 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 | 173.1695 |  | SWPA | OZARK - VAN BUREN 161KV CKT 1 | Indeterminate | [52 empty] | 2010-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T1364409G | FROM->TO | OKEENE - WATONGA SW 69KV CKT 1 | PL | WFEC | WFEC | AEP-IM | AEP-IM | 0 | 521015 | OKEENE 2 69.000 | 521090 | WATNGSW2 69.000 | 0 |  | 1 | 09G | 48 | 48 |  |  | 79.9677 | 103.2965 | [7 empty] | CATEGORYB | SINGLE | DOVER SW - OKEENE 138KV CKT 1 | 0 | 520882 | DOVERSW4 138.00 | 521016 | OKEENE 4 138.00 | 0 |  | 1 | 49.5823 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T4002409G | FROM->TO | OKEENE - WATONGA SW 69KV CKT 1 | PL | WFEC | WFEC | AEP-IM | AEP-IM | 0 | 521015 | OKEENE 2 69.000 | 521090 | WATNGSW2 69.000 | 0 |  | 1 | 09G | 48 | 48 |  |  | 86.5864 | 100.6656 | [7 empty] | CATEGORYB | SINGLE | DOVER SW (DOVER) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 520881 | DOVERSW2 69.000 | 520882 | DOVERSW4 138.00 | 521166 | DVRTERT 13.800 | 1 | 48.3195 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T1332409WP | FROM->TO | OKEENE - WATONGA SW 69KV CKT 1 | PL | WFEC | WFEC | AEP-IM | AEP-IM | 0 | 521015 | OKEENE 2 69.000 | 521090 | WATNGSW2 69.000 | 0 |  | 1 | 09WP | 48 | 48 |  |  | 96.1107 | 116.735 | [7 empty] | CATEGORYB | SINGLE | DOVER SW - OKEENE 138KV CKT 1 | 0 | 520882 | DOVERSW4 138.00 | 521016 | OKEENE 4 138.00 | 0 |  | 1 | 56.0328 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T3972409WP | FROM->TO | OKEENE - WATONGA SW 69KV CKT 1 | PL | WFEC | WFEC | AEP-IM | AEP-IM | 0 | 521015 | OKEENE 2 69.000 | 521090 | WATNGSW2 69.000 | 0 |  | 1 | 09WP | 48 | 48 |  |  | 97.6695 | 110.1714 | [7 empty] | CATEGORYB | SINGLE | DOVER SW (DOVER) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 520881 | DOVERSW2 69.000 | 520882 | DOVERSW4 138.00 | 521166 | DVRTERT 13.800 | 1 | 52.8823 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
GEN-2006-010 | Turk | [7 empty] | 50742850742750744212SP | FROM->TO | OKAY 138/69KV TRANSFORMER CKT 1 | U | AEPW | AEPW | SARK | SARK | 1 | 507428 | OKAY 4 138.00 | 507427 | OKAY 2 69.000 | 507442 |  | 1 |  | 150 | 174 |  |  | 57.8 | [9 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | AEPW | OKAY 138/69KV TRANSFORMER CKT 1 | Replace three single-phase 115-69 kV autotransformers with one 90 MVA, three-phase 138-69 kV autotransformer and convert high side of station to 138 kV | [11 empty] | 3400000 | 3400000 | [39 empty] | 2012-07-01 | 2012-07-01
GEN-2006-010 | Turk | [7 empty] | 507454507428012SP | TO->FROM | OKAY - TURK 138KV CKT 1 | U | AEPW | AEPW | SARK | SARK | 0 | 507454 | HEMPSTD4 138.00 | 507428 | OKAY 4 138.00 | 0 |  | 1 |  | 368 | 512 |  |  | 175.2 | [9 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | AEPW | OKAY - TURK 138KV CKT 1 | Build two mile, 138 kV, 1590ACSR line section from Turk Sub to existing Okay-Hope 115 kV line and rebuild twelve miles of 115 kV line to Okay Sub to 138 kV, 1590 ACSR , to form a Turk-Okay 138 kV line | [11 empty] | 9190000 | 9190000 | [39 empty] | 2012-07-01 | 2012-07-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17233318SP |  | NSI 115KV | REL | SUNC |  | GREAT PL |  |  | 531355 | NSI 115.00 | [5 empty] | 18SP | [8 empty] | 0.92738 | 0.89512 | 0.9969 | 0.9 | 1.05 | CATEGORYB | SINGLE | MINGO (MINGO) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 531451 | MINGO 7 345.00 | 531429 | MINGO 3 115.00 | 531452 | MINGTER1 13.800 | 1 |  |  | SUNC | RULETON 115KV Capacitor | Install Second 12 Mvar cap bank at Ruleton 115kV | [12 empty] | 486000 | 2008-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17193318SP |  | NSI 3 115KV | REL | MIDW |  | REG E-IL |  |  | 530614 | NSI 3 115.00 | [5 empty] | 18SP | [8 empty] | 0.92738 | 0.89511 | 0.9969 | 0.9 | 1.05 | CATEGORYB | SINGLE | MINGO (MINGO) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 531451 | MINGO 7 345.00 | 531429 | MINGO 3 115.00 | 531452 | MINGTER1 13.800 | 1 |  |  | SUNC | RULETON 115KV Capacitor | Install Second 12 Mvar cap bank at Ruleton 115kV | [12 empty] | 486000 | 2008-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2008-AGP1 | AFS3 | 5042 - NWTPATLYDVAL | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T1062210SP | FROM->TO | NORTHWEST TEXARKANA - PATTERSON 138KV CKT 1 | S | AEPW | AEPW | TEXARK | SARK | 0 | 508071 | NWTXARK4 138.00 | 507431 | PATTERS4 138.00 | 0 |  | 1 | 10SP | 224 | 261 |  | 103.2 | 114.6764 | 106.173 | [7 empty] | CATEGORYB | SINGLE | LYDIA - VALLIANT 345KV CKT 1 | 0 | 508298 | LYDIA 7 345.00 | 510911 | VALIANT7 345.00 | 0 |  | 1 | 277.1115 |  | AEPW | NORTHWEST TEXARKANA - PATTERSON 138KV CKT 1 | Interim redispatch | [52 empty] | 2010-06-01 | 2012-06-01
NA | [8 empty] | NAOKGE5148805153751 |  | NORTHWEST - WOODWARD 345KV CKT 1 | U | OKGE | OKGE | ENID | ENID | 0 | 514880 |  | 515375 |  |  |  | 1 |  | 2021 | 2325 | [12 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 kV | [52 empty] | 2010-01-01 | 2010-01-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 3 | 2008AGP1AFS31T684309FA | TO->FROM | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 09FA | 181 | 181 |  | 101.2 | 103.1874 | 105.5444 | [7 empty] | CATEGORYB | SINGLE | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | 0 | 533368 | EXIDE J3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 | 191.0354 |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [52 empty] | 2009-04-01 | 2009-12-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 3 | 2008AGP1AFS31T4894309FA | TO->FROM | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 09FA | 181 | 181 |  |  | 99.684 | 102.0037 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-73 | 0 | 0 |  | 0 |  | 0 |  |  | 184.6267 |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [52 empty] | 2009-04-01 | 2009-12-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 3 | 2008AGP1AFS31T674309FA | TO->FROM | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 09FA | 181 | 181 |  |  | 98.4859 | 100.8092 | [7 empty] | CATEGORYB | SINGLE | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | 0 | 533368 | EXIDE J3 115.00 | 533372 | PHILIPS3 115.00 | 0 |  | 1 | 182.4646 |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [52 empty] | 2009-04-01 | 2009-12-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 3 | 2008AGP1AFS31T874309G | TO->FROM | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 09G | 181 | 181 |  |  | 97.7376 | 100.1581 | [7 empty] | CATEGORYB | SINGLE | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | 0 | 533368 | EXIDE J3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 | 181.2862 |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [52 empty] | 2009-04-01 | 2009-12-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 3 | 2008AGP1AFS31T1244309SH | TO->FROM | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 09SH | 181 | 181 | 102.1 | 105 | 107.5828 | 109.9868 | [7 empty] | CATEGORYB | SINGLE | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | 0 | 533368 | EXIDE J3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 | 199.0761 |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [52 empty] | 2009-04-01 | 2009-12-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 3 | 2008AGP1AFS31T6954309SH | TO->FROM | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 09SH | 181 | 181 |  | 102.1 | 104.6636 | 107.0671 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-73 | 0 | 0 |  | 0 |  | 0 |  |  | 193.7915 |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [52 empty] | 2009-04-01 | 2009-12-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 3 | 2008AGP1AFS31T1234309SH | TO->FROM | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 09SH | 181 | 181 |  | 100.9 | 103.4528 | 105.8603 | [7 empty] | CATEGORYB | SINGLE | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | 0 | 533368 | EXIDE J3 115.00 | 533372 | PHILIPS3 115.00 | 0 |  | 1 | 191.6071 |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [52 empty] | 2009-04-01 | 2009-12-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T1763309SP | TO->FROM | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 09SP | 181 | 181 | 118.7 | 122.1 | 123.3163 | 125.7627 | [7 empty] | CATEGORYB | SINGLE | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | 0 | 533368 | EXIDE J3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 | 227.6305 |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [52 empty] | 2009-04-01 | 2009-12-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T10233309SP | TO->FROM | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 09SP | 181 | 181 | 115.6 | 119 | 120.2104 | 122.62 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-73 | 0 | 0 |  | 0 |  | 0 |  |  | 221.9422 |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [52 empty] | 2009-04-01 | 2009-12-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T1753309SP | TO->FROM | NORTHVIEW - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | 09SP | 181 | 181 | 114.4 | 117.8 | 119.0103 | 121.4241 | [7 empty] | CATEGORYB | SINGLE | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | 0 | 533368 | EXIDE J3 115.00 | 533372 | PHILIPS3 115.00 | 0 |  | 1 | 219.7776 |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [52 empty] | 2009-04-01 | 2009-12-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 2 | 2008AGP1AFS31V9133213SP |  | NORTH CENTRAL FOUNDRY 115KV | REL | WERE |  | NCENTRAL |  |  | 533329 | NCFOUND3 115.00 | [5 empty] | 13SP | [8 empty] | 0.94325 | 0.92296 | 0.96486 | 0.93 | 1.05 | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 | CONT-0633 - East Manhattan 230-115kV XFMR | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17473318SP |  | NORTH CENTRAL FOUNDRY 115KV | REL | WERE |  | NCENTRAL |  |  | 533329 | NCFOUND3 115.00 | [5 empty] | 18SP | [6 empty] | 0.92649 | 0.91542 | 0.8987 | 0.84983 | 0.95441 | 0.93 | 1.05 | CATEGORYB | SINGLE | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17673318SP |  | NORTH CENTRAL FOUNDRY 115KV | REL | WERE |  | NCENTRAL |  |  | 533329 | NCFOUND3 115.00 | [5 empty] | 18SP | [8 empty] | 0.94166 | 0.90059 | 0.95441 | 0.93 | 1.05 | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 | 5204 - SPHWMCSUMEMC |  |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T1654209G | FROM->TO | NORTH AMERICAN PHILIPS JUNCTION (SOUTH) - WEST MCPHERSON 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533374 | SPHILPJ3 115.00 | 533438 | WMCPHER3 115.00 | 0 |  | 1 | 09G | 68 | 68 |  |  | 97.417 | 104.1138 | [7 empty] | CATEGORYB | SINGLE | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 0 | 532872 | EMCPHER6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 70.7974 |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [52 empty] | 2009-04-01 | 2009-12-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31V8062209AP |  | NEWMAN GRACE TAP 69KV | S | OKGE |  | ENID |  |  | 514776 | NEWGRTP2 69.000 | [5 empty] | 09AP | [8 empty] | 1.0375 | 1.0619 | 1.0362 | 0.9 | 1.05 | CATEGORYB | GENOUT | GEN515364 1-CENT 11 0.6000 | 0 | 337909 | 8ANO 50 500.00 | 515305 | FTSMITH8 500.00 | 0 |  | 1 |  |  | OKGE | WOODWARD 138KV REACTOR | Install a reactor bank in the Woodward Area. | [12 empty] | 700000 | 2008-07-29 | [38 empty] | 2009-04-01 | 2011-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31V8042209AP |  | NEWMAN 69KV | S | OKGE |  | ENID |  |  | 514773 | NEWMAN 2 69.000 | [5 empty] | 09AP | [8 empty] | 1.0371 | 1.0615 | 1.0357 | 0.9 | 1.05 | CATEGORYB | GENOUT | GEN515364 1-CENT 11 0.6000 | 0 | 337909 | 8ANO 50 500.00 | 515305 | FTSMITH8 500.00 | 0 |  | 1 |  |  | OKGE | WOODWARD 138KV REACTOR | Install a reactor bank in the Woodward Area. | [12 empty] | 700000 | 2008-07-29 | [38 empty] | 2009-04-01 | 2011-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T2332218SP | FROM->TO | NEW MADRID - NEW MADRID 161KV CKT 1 | S | AECI | SWPA | AECI | EMINTH | 0 | 300103 | 5NEWMAD 161.00 | 505400 | N MADRD5 161.00 | 0 |  | 1 | 18SP | 261 | 261 |  | 102.3 | 101.9147 | 104.0528 | [7 empty] | CATEGORYB | SINGLE | NEW MADRID - SIKESTON 161KV CKT 1 | 0 | 505400 | N MADRD5 161.00 | 505428 | SIKESTN5 161.00 | 0 |  | 1 | 271.5778 |  | AECI | 5NEWMAD 161.00 - NEW MADRID 161KV CKT 1 | 5.4 mile line designed for 75-C. If this can be uprated to 100-C | [12 empty] | 600000 | [39 empty] | 2015-06-01 | 2015-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T37792218SP | FROM->TO | NEW MADRID - NEW MADRID 161KV CKT 1 | S | AECI | SWPA | AECI | EMINTH | 0 | 300103 | 5NEWMAD 161.00 | 505400 | N MADRD5 161.00 | 0 |  | 1 | 18SP | 261 | 261 |  | 101.7 | 101.417 | 103.0501 | [7 empty] | CATEGORYB | NONSINGLE | ESEX-IDAL | 0 | 0 |  | 0 |  | 0 |  |  | 268.9608 |  | AECI | 5NEWMAD 161.00 - NEW MADRID 161KV CKT 1 | 5.4 mile line designed for 75-C. If this can be uprated to 100-C | [12 empty] | 600000 | [39 empty] | 2015-06-01 | 2015-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T26372218SP | FROM->TO | NEW MADRID - NEW MADRID 161KV CKT 1 | S | AECI | SWPA | AECI | EMINTH | 0 | 300103 | 5NEWMAD 161.00 | 505400 | N MADRD5 161.00 | 0 |  | 1 | 18SP | 261 | 261 |  |  | 98.9912 | 100.6656 | [7 empty] | CATEGORYB | SINGLE | ESSEX - IDALIA 161KV CKT 1 | 0 | 505434 | IDALIA 5 161.00 | 300075 | 5ESSEX 161.00 | 0 |  | 1 | 262.7372 |  | AECI | 5NEWMAD 161.00 - NEW MADRID 161KV CKT 1 | 5.4 mile line designed for 75-C. If this can be uprated to 100-C | [12 empty] | 600000 | [39 empty] | 2015-06-01 | 2015-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17243318SP |  | NATIONAL SUNFLOWER INDUSTRY TAP 115KV | REL | SUNC |  | GREAT PL |  |  | 531356 | NSI TAP3 115.00 | [5 empty] | 18SP | [8 empty] | 0.92803 | 0.89595 | 0.99763 | 0.9 | 1.05 | CATEGORYB | SINGLE | MINGO (MINGO) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 531451 | MINGO 7 345.00 | 531429 | MINGO 3 115.00 | 531452 | MINGTER1 13.800 | 1 |  |  | SUNC | RULETON 115KV Capacitor | Install Second 12 Mvar cap bank at Ruleton 115kV | [12 empty] | 486000 | 2008-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2008-AGP1 | AFS3 | CONT-1202 - Jarbalo - Stranger Creek 115kV |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T735510WP | TO->FROM | NASHUA - SMITHVILLE 161KV CKT 1 | S | MIPU | MIPU |  |  | 0 | 541204 | SMTHVL 5 161.00 | 541203 | NASHUA 5 161.00 | 0 |  | 1 | 10WP | 223 | 245 |  |  | 97.6589 | 102.2359 | [7 empty] | CATEGORYB | SINGLE | IATAN - ST JOE 345KV CKT 1 | 0 | 541199 | ST JOE 3 345.00 | 542982 | IATAN 7 345.00 | 0 |  | 1 | 250.478 | Replace wavetrap | MIPU | NASHUA - SMITHVILLE 161KV CKT 1 | Increase the normal/emergency ratings to 233/265 MVA by replacing the 800A wavetrap at Nashua side to a 1200A wavetrap | 233 | 265 |  |  |  | 12 | 12 | [5 empty] | 50000 | 2009-03-19 | [38 empty] | 2010-12-01 | 2011-01-01
GEN-2004-014 | Spearville2 | [7 empty] | 539695539679012SP | TO->FROM | MULLERGREN - SPEARVILLE 230KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539695 | SPEARVL6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 |  | 330.3 | 355.3 |  |  | 116.6 | [9 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | MKEC | MULLERGREN - SPEARVILLE 230KV CKT 1 | 230kv line terminal at Spearville | [12 empty] | 650000 | [39 empty] | 2009-12-31 | 2009-12-31
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V3325509SP |  | MULBERRY 69KV | EXP | WERE |  | SEAST |  |  | 533767 | MULBERY2 69.000 | [5 empty] | 09SP | [6 empty] | 0.85885 | 0.85785 | 0.89689 | 0.84703 | 1.0025 | 0.93 | 1.05 | CATEGORYB | SINGLE | LITCHFIELD - PITNAC 69KV CKT 1 | 0 | 533765 | LITCH 2 69.000 | 533769 | PITNAC 2 69.000 | 0 |  | 1 |  |  | WERE | Fort Scott 161/69kV Transformer CKT 1 | New 161/69 kV transformer at Ft Scott. | 100 | 110 |  |  |  | 18 | 18 | [5 empty] | 1400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V6355509AP |  | MOORELAND 69KV | S | WFEC |  | AEP-OP |  |  | 520995 | MOORLND2 69.000 | [5 empty] | 09AP | [8 empty] | 1.0377 | 1.058 | 1.037 | 0.9 | 1.05 | CATEGORYB | SINGLE | MOORELAND (MOORELND) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 520995 | MOORLND2 69.000 | 520999 | MOORLND4 138.00 | 521180 | MLNDTERT 13.800 | 1 |  |  | OKGE | WOODWARD 138KV REACTOR | Install a reactor bank in the Woodward Area. | [12 empty] | 700000 | 2008-07-29 | [38 empty] | 2009-04-01 | 2011-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T502409AP | FROM->TO | MOORELAND (MOORELND) 138/69/13.8KV TRANSFORMER CKT 1 | PL | WFEC |  | AEP-OP |  | 1 | 520995 | MOORLND2 69.000 | 520999 | MOORLND4 138.00 | 521180 | MLNDTERT 13.800 | 1 | 09AP | 65 | 65 |  |  | 64.5044 | 104.4166 | [7 empty] | CATEGORYB | SINGLE | FPL SWITCH - MOORELAND 138KV CKT 1 | 0 | 515785 | WINDFRM4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 67.8708 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T6902409G | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | PL | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09G | 96 | 96 | 151.9 | 154.6 | 163.853 | 193.3827 | [7 empty] | CATEGORYB | GENOUT | GEN525562 1-TOLK GEN #2 24 KV | 0 | 0 |  | 0 |  | 0 |  |  | 185.6474 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T912409G | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | PL | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09G | 96 | 96 | 142.0 | 146.5 | 154.8984 | 191.7466 | [7 empty] | CATEGORYB | SINGLE | DEWEY - SOUTHARD 138KV CKT 1 | 0 | 514787 | DEWEY 4 138.00 | 514822 | SOUTHRD4 138.00 | 0 |  | 1 | 184.0767 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T6152409G | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | PL | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09G | 96 | 96 | 147.6 | 151.7 | 161.9898 | 191.6148 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05A | 0 | 0 |  | 0 |  | 0 |  |  | 183.9502 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T6862409G | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | PL | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09G | 96 | 96 | 148.9 | 151.8 | 160.4374 | 189.8476 | [7 empty] | CATEGORYB | GENOUT | GEN525561 1-TOLK GEN #1 24 KV | 0 | 0 |  | 0 |  | 0 |  |  | 182.2537 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T9954409SP | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | PL | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09SP | 96 | 96 | 160.1 | 157.7 | 164.042 | 193.2633 | [7 empty] | CATEGORYB | GENOUT | GEN525562 1-TOLK GEN #2 24 KV | 0 | 0 |  | 0 |  | 0 |  |  | 185.5328 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T9304409SP | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | PL | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09SP | 96 | 96 | 154.9 | 152.7 | 160.4116 | 190.5826 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05A | 0 | 0 |  | 0 |  | 0 |  |  | 182.9593 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T1014409SP | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | PL | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09SP | 96 | 96 | 150.0 | 149.1 | 153.5564 | 190.4317 | [7 empty] | CATEGORYB | SINGLE | DEWEY - SOUTHARD 138KV CKT 1 | 0 | 514787 | DEWEY 4 138.00 | 514822 | SOUTHRD4 138.00 | 0 |  | 1 | 182.8144 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T9944409SP | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | PL | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09SP | 96 | 96 | 156.8 | 154.4 | 160.3869 | 189.9831 | [7 empty] | CATEGORYB | GENOUT | GEN525561 1-TOLK GEN #1 24 KV | 0 | 0 |  | 0 |  | 0 |  |  | 182.3838 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T892409WP | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | PL | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09WP | 96 | 96 | 152.6 | 158.6 | 163.9993 | 199.5107 | [7 empty] | CATEGORYB | SINGLE | DEWEY - SOUTHARD 138KV CKT 1 | 0 | 514787 | DEWEY 4 138.00 | 514822 | SOUTHRD4 138.00 | 0 |  | 1 | 191.5303 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T6922409WP | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | PL | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09WP | 96 | 96 | 159.7 | 163.1 | 167.3066 | 197.0445 | [7 empty] | CATEGORYB | GENOUT | GEN525562 1-TOLK GEN #2 24 KV | 0 | 0 |  | 0 |  | 0 |  |  | 189.1627 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T1072409WP | FROM->TO | MOORELAND - MOREWOOD SW 138KV CKT 1 | PL | WFEC | WFEC | AEP-OP | AEP-CS | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 09WP | 96 | 96 | 149.0 | 154.9 | 160.8167 | 195.7413 | [7 empty] | CATEGORYB | SINGLE | ROMAN NOSE - SOUTHARD 138KV CKT 1 | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 187.9117 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17293318SP |  | MINGO 115KV | REL | SUNC |  | WHEATLAN |  |  | 531429 | MINGO 3 115.00 | [5 empty] | 18SP | [8 empty] | 0.9202 | 0.89095 | 1.0339 | 0.9 | 1.05 | CATEGORYB | SINGLE | MINGO (MINGO) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 531451 | MINGO 7 345.00 | 531429 | MINGO 3 115.00 | 531452 | MINGTER1 13.800 | 1 |  |  | SUNC | RULETON 115KV Capacitor | Install Second 12 Mvar cap bank at Ruleton 115kV | [12 empty] | 486000 | 2008-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T201309AP | FROM->TO | MEDICINE LODGE - PRATT 115KV CKT 1 | CP | MKEC | MKEC |  |  | 0 | 539673 | MED-LDG3 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 | 09AP | 79.7 | 79.7 |  |  | 114.8551 | 115.5297 | [7 empty] | CATEGORYB | SINGLE | FLATRDG3 138.00 - HARPER 138KV CKT 1 | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 92.0772 |  | MKEC | MEDICINE LODGE - PRATT 115KV CKT 1 | Rebuild 26 mile line | [5 empty] | 18 | 18 |  |  |  |  | $249,916.24 per mile | [40 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T241309AP | FROM->TO | MEDICINE LODGE - PRATT 115KV CKT 1 | CP | MKEC | MKEC |  |  | 0 | 539673 | MED-LDG3 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 | 09AP | 79.7 | 79.7 |  |  | 105.4005 | 106.0047 | [7 empty] | CATEGORYB | SINGLE | HARPER - MILAN TAP 138KV CKT 1 | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 84.4857 |  | MKEC | MEDICINE LODGE - PRATT 115KV CKT 1 | Rebuild 26 mile line | [5 empty] | 18 | 18 |  |  |  |  | $249,916.24 per mile | [40 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 3 | 2008AGP1AFS31T934309G | FROM->TO | MEDICINE LODGE - PRATT 115KV CKT 1 | CP | MKEC | MKEC |  |  | 0 | 539673 | MED-LDG3 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 | 09G | 79.7 | 79.7 |  |  | 118.9888 | 121.4202 | [7 empty] | CATEGORYB | SINGLE | FLATRDG3 138.00 - HARPER 138KV CKT 1 | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 96.7719 |  | MKEC | MEDICINE LODGE - PRATT 115KV CKT 1 | Rebuild 26 mile line | [5 empty] | 18 | 18 |  |  |  |  | $249,916.24 per mile | [40 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 3 | 2008AGP1AFS31T974309G | FROM->TO | MEDICINE LODGE - PRATT 115KV CKT 1 | CP | MKEC | MKEC |  |  | 0 | 539673 | MED-LDG3 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 | 09G | 79.7 | 79.7 |  |  | 103.5085 | 105.6697 | [7 empty] | CATEGORYB | SINGLE | HARPER - MILAN TAP 138KV CKT 1 | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 84.2188 |  | MKEC | MEDICINE LODGE - PRATT 115KV CKT 1 | Rebuild 26 mile line | [5 empty] | 18 | 18 |  |  |  |  | $249,916.24 per mile | [40 empty] | 2009-04-01 | 2012-06-01
GEN-2006-010 | Turk | [7 empty] | 504122507456012SP | FROM->TO | MCNAB REC - TURK 115KV CKT 1 | U | AEPW | AEPW | SARK | SARKAECC | 0 | 504122 | MCNAB 3 115.00 | 507456 | HEMPSTD3 115.00 | 0 |  | 1 |  | 150 | 174 |  |  | 47.9 | [9 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | AEPW | MCNAB REC - TURK 115KV CKT 1 | Build a new two mile, 138 kV, 1590 ACSR line section (operated at 115 kV) from Turk Substation to the existing Okay- Hope 115 kV line to form a Turk - Hope 115 kV line. | [11 empty] | 1520000 | 1520000 | [39 empty] | 2012-07-01 | 2012-07-01
2008-AGP1 | AFS3 | 5245 - STIMCRSPRNOR | FDNS |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T1432410SP | TO->FROM | MCELROY - STILLWATER 138KV CKT 1 | REL | OKGE | OKGE | SHAWNEE | SHAWNEE | 0 | 515011 | STILWTR4 138.00 | 515009 | MCELROY4 138.00 | 0 |  | 1 | 10SP | 194 | 222 | 101.1 | 108.2 | 107.8842 | 103.6451 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - SPRING CREEK 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 514881 | SPRNGCK7 345.00 | 0 |  | 1 | 230.0921 |  | OKGE | MCELROY - STILLWATER 138KV CKT 1 | Reconductor 1.91 of 477AS33 to 795AS33 | 478 | 478 |  |  | 1.91 | [7 empty] | 800000 | [39 empty] | 2010-06-01 | 2010-06-01
2008-AGP1 | AFS3 | 5245 - STIMCRSPRNOR | FDNS |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T1794413SP | TO->FROM | MCELROY - STILLWATER 138KV CKT 1 | REL | OKGE | OKGE | SHAWNEE | SHAWNEE | 0 | 515011 | STILWTR4 138.00 | 515009 | MCELROY4 138.00 | 0 |  | 1 | 13SP | 194 | 222 |  | 104.1 | 101.0219 | 102.0991 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - SPRING CREEK 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 514881 | SPRNGCK7 345.00 | 0 |  | 1 | 226.66 |  | OKGE | MCELROY - STILLWATER 138KV CKT 1 | Reconductor 1.91 of 477AS33 to 795AS33 | 478 | 478 |  |  | 1.91 | [7 empty] | 800000 | [39 empty] | 2010-06-01 | 2010-06-01
2008-AGP1 | AFS3 | CONT-0633 - East Manhattan 230-115kV XFMR | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17513318SP |  | MCDOWELL CREEK SWITCHING STATION 115KV | REL | WERE |  | NCENTRAL |  |  | 533335 | MCDOWEL3 115.00 | [5 empty] | 18SP | [7 empty] | 0.92911 | 0.92201 | 0.87804 | 0.98945 | 0.93 | 1.05 | CATEGORYB | SINGLE | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 | CONT-0633 - East Manhattan 230-115kV XFMR | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17623318SP |  | MCDOWELL CREEK 230KV | REL | WERE |  | NCENTRAL |  |  | 532862 | MCDOWEL6 230.00 | [5 empty] | 18SP | [6 empty] | 0.94211 | 0.93489 | 0.9304 | 0.89701 | 0.97843 | 0.95 | 1.05 | CATEGORYB | SINGLE | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V7513318SP |  | MCDOWELL CREEK 230KV | REL | WERE |  | NCENTRAL |  |  | 532862 | MCDOWEL6 230.00 | [5 empty] | 18SP | [8 empty] | 0.94258 | 0.90613 | 0.97843 | 0.95 | 1.05 | CATEGORYB | SINGLE | MCDOWELL CREEK - MORRIS COUNTY 230KV CKT 1 | 0 | 532863 | MORRIS 6 230.00 | 532862 | MCDOWEL6 230.00 | 0 |  | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V3523310SP |  | MATTERS CORNER 115KV | REL | WERE |  | NCENTRAL |  |  | 533334 | MATTERS3 115.00 | [5 empty] | 10SP | [8 empty] | 0.9415 | 0.91741 | 1.0049 | 0.93 | 1.05 | CATEGORYB | SINGLE | EAST MANHATTAN - MATTERS CORNER 115KV CKT 1 | 0 | 533326 | EMANHAT3 115.00 | 533334 | MATTERS3 115.00 | 0 |  | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 | CONT-0633 - East Manhattan 230-115kV XFMR | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17503318SP |  | MATTERS CORNER 115KV | REL | WERE |  | NCENTRAL |  |  | 533334 | MATTERS3 115.00 | [5 empty] | 18SP | [6 empty] | 0.90911 | 0.89927 | 0.89555 | 0.84346 | 0.9974 | 0.93 | 1.05 | CATEGORYB | SINGLE | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 1 | 2008AGP1AFS31T991109SH | TO->FROM | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541259 | TURNER 5 161.00 | 541210 | MARTCTY5 161.00 | 0 |  | 1 | 09SH | 233 | 265 |  | 101.6 | 100.6908 | 102.1433 | [7 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 | 270.6798 |  | MIPU | South Harper 161 kV cut-in to Stilwell-Archie JCT 161 kV line | To tap Stilwell-Archie JCT 161 kV line into South Harper 161 kV sub and make it two new 161 kV sections: Stilwell-South Harper and Archie JCT- South Harper . | [5 empty] | 18 | 18 | [5 empty] | 2259673 | 2009-03-19 | [38 empty] | 2009-04-01 | 2010-10-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 1 | 2008AGP1AFS31T1691109SP | TO->FROM | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541259 | TURNER 5 161.00 | 541210 | MARTCTY5 161.00 | 0 |  | 1 | 09SP | 233 | 265 |  | 105.9 | 105.9735 | 107.225 | [7 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 | 284.1462 |  | MIPU | South Harper 161 kV cut-in to Stilwell-Archie JCT 161 kV line | To tap Stilwell-Archie JCT 161 kV line into South Harper 161 kV sub and make it two new 161 kV sections: Stilwell-South Harper and Archie JCT- South Harper . | [5 empty] | 18 | 18 | [5 empty] | 2259673 | 2009-03-19 | [38 empty] | 2009-04-01 | 2010-10-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 1 | 2008AGP1AFS31T941109WP | TO->FROM | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541259 | TURNER 5 161.00 | 541210 | MARTCTY5 161.00 | 0 |  | 1 | 09WP | 233 | 265 |  | 102.5 | 100.9715 | 104.6738 | [7 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 | 277.3856 |  | MIPU | South Harper 161 kV cut-in to Stilwell-Archie JCT 161 kV line | To tap Stilwell-Archie JCT 161 kV line into South Harper 161 kV sub and make it two new 161 kV sections: Stilwell-South Harper and Archie JCT- South Harper . | [5 empty] | 18 | 18 | [5 empty] | 2259673 | 2009-03-19 | [38 empty] | 2009-04-01 | 2010-10-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 1 | 2008AGP1AFS31T2133110SP | TO->FROM | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541259 | TURNER 5 161.00 | 541210 | MARTCTY5 161.00 | 0 |  | 1 | 10SP | 233 | 265 | 105.9 | 105.8 | 104.0758 | 109.023 | [7 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 | 288.911 |  | MIPU | South Harper 161 kV cut-in to Stilwell-Archie JCT 161 kV line | To tap Stilwell-Archie JCT 161 kV line into South Harper 161 kV sub and make it two new 161 kV sections: Stilwell-South Harper and Archie JCT- South Harper . | [5 empty] | 18 | 18 | [5 empty] | 2259673 | 2009-03-19 | [38 empty] | 2009-04-01 | 2010-10-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T3441313SP | TO->FROM | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541259 | TURNER 5 161.00 | 541210 | MARTCTY5 161.00 | 0 |  | 1 | 13SP | 233 | 265 |  | 101.4 | 100.0716 | 104.6588 | [7 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 | 277.3458 |  | MIPU | South Harper 161 kV cut-in to Stilwell-Archie JCT 161 kV line | To tap Stilwell-Archie JCT 161 kV line into South Harper 161 kV sub and make it two new 161 kV sections: Stilwell-South Harper and Archie JCT- South Harper . | [5 empty] | 18 | 18 | [5 empty] | 2259673 | 2009-03-19 | [38 empty] | 2009-04-01 | 2010-10-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 1 | 2008AGP1AFS31T1273113WP | TO->FROM | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541259 | TURNER 5 161.00 | 541210 | MARTCTY5 161.00 | 0 |  | 1 | 13WP | 233 | 265 |  |  | 94.8632 | 100.4138 | [7 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 | 266.0966 |  | MIPU | South Harper 161 kV cut-in to Stilwell-Archie JCT 161 kV line | To tap Stilwell-Archie JCT 161 kV line into South Harper 161 kV sub and make it two new 161 kV sections: Stilwell-South Harper and Archie JCT- South Harper . | [5 empty] | 18 | 18 | [5 empty] | 2259673 | 2009-03-19 | [38 empty] | 2009-04-01 | 2010-10-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T5631318SP | TO->FROM | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541259 | TURNER 5 161.00 | 541210 | MARTCTY5 161.00 | 0 |  | 1 | 18SP | 233 | 265 |  | 103.1 | 104.2972 | 105.8956 | [7 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 | 280.6233 |  | MIPU | South Harper 161 kV cut-in to Stilwell-Archie JCT 161 kV line | To tap Stilwell-Archie JCT 161 kV line into South Harper 161 kV sub and make it two new 161 kV sections: Stilwell-South Harper and Archie JCT- South Harper . | [5 empty] | 18 | 18 | [5 empty] | 2259673 | 2009-03-19 | [38 empty] | 2009-04-01 | 2010-10-01
2008-AGP1 | AFS3 | 5275 - TURMARSTIRED |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T6473318SP | TO->FROM | MARTIN CITY - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541259 | TURNER 5 161.00 | 541210 | MARTCTY5 161.00 | 0 |  | 1 | 18SP | 233 | 265 |  |  | 97.229 | 101.8617 | [7 empty] | CATEGORYB | SINGLE | REDEL - STILWELL 161KV CKT 1 | 0 | 542969 | STILWEL5 161.00 | 543053 | REDEL 5 161.00 | 0 |  | 1 | 269.9335 |  | MIPU | South Harper 161 kV cut-in to Stilwell-Archie JCT 161 kV line | To tap Stilwell-Archie JCT 161 kV line into South Harper 161 kV sub and make it two new 161 kV sections: Stilwell-South Harper and Archie JCT- South Harper . | [5 empty] | 18 | 18 | [5 empty] | 2259673 | 2009-03-19 | [38 empty] | 2009-04-01 | 2010-10-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 2 | 2008AGP1AFS31T2371209SP | FROM->TO | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | EXP | WERE |  | SEAST |  | 2 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1 | 09SP | 100 | 110 |  | 100.4 | 97.9319 | 100.3774 | [7 empty] | CATEGORYB | SINGLE | LITCHFIELD - PITNAC 69KV CKT 1 | 0 | 533765 | LITCH 2 69.000 | 533769 | PITNAC 2 69.000 | 0 |  | 1 | 110.4151 |  | WERE | Fort Scott 161/69kV Transformer CKT 1 | New 161/69 kV transformer at Ft Scott. | 100 | 110 |  |  |  | 18 | 18 | [5 empty] | 1400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 4 | 2008AGP1AFS31T4983418SP | FROM->TO | MANHATTAN TAP - OSAGE SWITCHING STATION 115KV CKT 1 | S | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524354 | MANHATN_TP 3115.00 | 524345 | OSAGE_ 3 115.00 | 0 |  | 1 | 18SP | 139 | 160 | 101.2 | 101.1 | 101.4045 | 103.0992 | [7 empty] | CATEGORYB | SINGLE | EAST PLANT INTERCHANGE - PIERCE STREET TAP 115KV CKT 1 | 0 | 524162 | EAST_PLANT3 115.00 | 524185 | PIERCT3 115.00 | 0 |  | 1 | 164.9587 |  | SPS | MANHATTAN TAP - OSAGE SWITCHING STATION 115KV CKT 1 Displacement | Replace Terminal Equipment | [12 empty] | 225000 | 2008-01-01 | [38 empty] | 2016-06-01 | 2014-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31V2642218SP |  | MALDEN CAP BANK 1 69KV | REL | SWPA |  | EMINTH |  |  | 505630 | MAL CAP2 69.000 | [5 empty] | 18SP | [8 empty] | 0.92176 | 0.89398 | 1.0091 | 0.9 | 1.05 | CATEGORYB | SINGLE | KENNETT - NEW MADRID 161KV CKT 1 | 0 | 505400 | N MADRD5 161.00 | 505410 | KENNETT5 161.00 | 0 |  | 1 |  |  | SWPA | KENNETT CAP BANK 1 161KV CAP BANK | Install Additional Cap Bank at Kennett | [52 empty] | 2014-06-01 | 2014-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31V2522218SP |  | MALDEN 69KV | REL | SWPA |  | EMINTH |  |  | 505404 | MALDEN 2 69.000 | [5 empty] | 18SP | [8 empty] | 0.92175 | 0.89397 | 1.0091 | 0.9 | 1.05 | CATEGORYB | SINGLE | KENNETT - NEW MADRID 161KV CKT 1 | 0 | 505400 | N MADRD5 161.00 | 505410 | KENNETT5 161.00 | 0 |  | 1 |  |  | SWPA | KENNETT CAP BANK 1 161KV CAP BANK | Install Additional Cap Bank at Kennett | [52 empty] | 2014-06-01 | 2014-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T2212218SP | FROM->TO | MALDEN - PIGGOTT 69KV CKT 1 | S | SWPA | SWPA | EMINTH | EMINTH | 0 | 505404 | MALDEN 2 69.000 | 505406 | PIGGOTT2 69.000 | 0 |  | 1 | 18SP | 59 | 59 |  | 107.1 | 106.3506 | 114.8634 | [7 empty] | CATEGORYB | SINGLE | KENNETT - NEW MADRID 161KV CKT 1 | 0 | 505400 | N MADRD5 161.00 | 505410 | KENNETT5 161.00 | 0 |  | 1 | 67.7694 |  | SWPA | MALDEN - PIGGOTT 69KV CKT 1 | Reconductor line, replace disconnect switches | 143 | 143 | 143 | 143 | 21 | 24 | 12 | [5 empty] | 2000000 | 2008-08-11 | [38 empty] | 2014-06-01 | 2014-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T1102213SP | TO->FROM | MALDEN - NEW MADRID 69KV CKT 1 | REL | SWPA | SWPA | EMINTH | EMINTH | 0 | 505402 | N MADRD2 69.000 | 505404 | MALDEN 2 69.000 | 0 |  | 1 | 13SP | 59 | 59 | 100.9 | 118.4 | 117.9112 | 123.3769 | [7 empty] | CATEGORYB | SINGLE | KENNETT - NEW MADRID 161KV CKT 1 | 0 | 505400 | N MADRD5 161.00 | 505410 | KENNETT5 161.00 | 0 |  | 1 | 72.7924 |  | SWPA | MALDEN - NEW MADRID 69KV CKT 1 | Reconductor line, replace disconnect switches | 143 | 143 | 143 | 143 | 22.6 | 24 | 12 | [5 empty] | 2000000 | 2008-08-11 | [38 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T2202218SP | TO->FROM | MALDEN - NEW MADRID 69KV CKT 1 | REL | SWPA | SWPA | EMINTH | EMINTH | 0 | 505402 | N MADRD2 69.000 | 505404 | MALDEN 2 69.000 | 0 |  | 1 | 18SP | 59 | 59 | 106.9 | 127.4 | 126.6793 | 135.0382 | [7 empty] | CATEGORYB | SINGLE | KENNETT - NEW MADRID 161KV CKT 1 | 0 | 505400 | N MADRD5 161.00 | 505410 | KENNETT5 161.00 | 0 |  | 1 | 79.6725 |  | SWPA | MALDEN - NEW MADRID 69KV CKT 1 | Reconductor line, replace disconnect switches | 143 | 143 | 143 | 143 | 22.6 | 24 | 12 | [5 empty] | 2000000 | 2008-08-11 | [38 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T29282218SP | FROM->TO | MAID (MAIAUTO2) 161/69/13.8KV TRANSFORMER CKT 2 | REL | GRDA |  | GRDA |  | 2 | 512648 | MAID 5 161.00 | 512626 | MAID 2 69.000 | 512837 | MAITER2 13.800 | 2 | 18SP | 84 | 105 | 101.7 | 102.6 | 102.8379 | 102.4797 | [7 empty] | CATEGORYB | SINGLE | MAID (MAIAUTO1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 512626 | MAID 2 69.000 | 512648 | MAID 5 161.00 | 512836 | MAITER1 13.800 | 1 | 107.6037 |  | GRDA | MAID (MAIAUTO2) 161/69/13.8KV TRANSFORMER CKT 2 | Indeterminate | [52 empty] | 2018-06-01 | 2018-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T29292218SP | FROM->TO | MAID (MAIAUTO1) 161/69/13.8KV TRANSFORMER CKT 1 | REL | GRDA |  | GRDA |  | 2 | 512648 | MAID 5 161.00 | 512626 | MAID 2 69.000 | 512836 | MAITER1 13.800 | 1 | 18SP | 84 | 105 | 101.8 | 102.7 | 102.9322 | 102.5736 | [7 empty] | CATEGORYB | SINGLE | MAID (MAIAUTO2) 161/69/13.8KV TRANSFORMER CKT 2 | 1 | 512626 | MAID 2 69.000 | 512648 | MAID 5 161.00 | 512837 | MAITER2 13.800 | 2 | 107.7023 |  | GRDA | MAID (MAIAUTO1) 161/69/13.8KV TRANSFORMER CKT 1 | Indeterminate | [52 empty] | 2018-06-01 | 2018-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T4262218SP | FROM->TO | MAID - REDDEN 69KV CKT 1 | REL | GRDA | GRDA | GRDA | GR-LIN | 0 | 512626 | MAID 2 69.000 | 512698 | REDDEN 2 69.000 | 0 |  | 1 | 18SP | 72 | 72 | 138.4 | 138.3 | 138.4964 | 138.2088 | [7 empty] | CATEGORYB | SINGLE | MAID - PRYOR FOUNDRY SOUTH 69KV CKT 1 | 0 | 512626 | MAID 2 69.000 | 512681 | FNDRY#S2 69.000 | 0 |  | 1 | 99.5103 |  | GRDA | MAID - REDDEN 69KV CKT 1 | Upgrade conductor size 795 ACSR | 130 | 150 |  |  | 1.2 | 18 | 7 | Outage | 0.00239 | 0.01984 | 0.0004 | Upgrade conductor size | 750000 | 2008-01-10 | [38 empty] | 2014-06-01 | 2014-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T4712218SP | FROM->TO | MAID - REDDEN 69KV CKT 1 | REL | GRDA | GRDA | GRDA | GR-LIN | 0 | 512626 | MAID 2 69.000 | 512698 | REDDEN 2 69.000 | 0 |  | 1 | 18SP | 72 | 72 | 121.0 | 121.7 | 121.9201 | 121.6315 | [7 empty] | CATEGORYB | SINGLE | CPP TRANSF #2 - PRYOR FOUNDRY SOUTH 69KV CKT 1 | 0 | 512661 | CPPXF#22 69.000 | 512681 | FNDRY#S2 69.000 | 0 |  | 1 | 87.5747 |  | GRDA | MAID - REDDEN 69KV CKT 1 | Upgrade conductor size 795 ACSR | 130 | 150 |  |  | 1.2 | 18 | 7 | Outage | 0.00239 | 0.01984 | 0.0004 | Upgrade conductor size | 750000 | 2008-01-10 | [38 empty] | 2014-06-01 | 2014-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T4272218SP | FROM->TO | MAID - PRYOR FOUNDRY SOUTH 69KV CKT 1 | REL | GRDA | GRDA | GRDA | GR-LIN | 0 | 512626 | MAID 2 69.000 | 512681 | FNDRY#S2 69.000 | 0 |  | 1 | 18SP | 72 | 72 | 139.0 | 139.7 | 139.8915 | 139.592 | [7 empty] | CATEGORYB | SINGLE | MAID - REDDEN 69KV CKT 1 | 0 | 512626 | MAID 2 69.000 | 512698 | REDDEN 2 69.000 | 0 |  | 1 | 100.5062 |  | GRDA | MAID - PRYOR FOUNDRY SOUTH 69KV CKT 1 | Upgrade conductor size 795 ACSR | 130 | 150 |  |  | 1.3 | 18 | 7 | Outage | 0.000222 | 0.0177 | 0.00041 | Upgrade conductor size | 750000 | 2008-01-10 | [38 empty] | 2014-06-01 | 2014-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T4742218SP | FROM->TO | MAID - PRYOR FOUNDRY SOUTH 69KV CKT 1 | REL | GRDA | GRDA | GRDA | GR-LIN | 0 | 512626 | MAID 2 69.000 | 512681 | FNDRY#S2 69.000 | 0 |  | 1 | 18SP | 72 | 72 | 105.2 | 105.1 | 105.3583 | 105.0568 | [7 empty] | CATEGORYB | SINGLE | PRYOR FOUNDRY TAP - REDDEN 69KV CKT 1 | 0 | 512685 | FNDRYTP2 69.000 | 512698 | REDDEN 2 69.000 | 0 |  | 1 | 75.6409 |  | GRDA | MAID - PRYOR FOUNDRY SOUTH 69KV CKT 1 | Upgrade conductor size 795 ACSR | 130 | 150 |  |  | 1.3 | 18 | 7 | Outage | 0.000222 | 0.0177 | 0.00041 | Upgrade conductor size | 750000 | 2008-01-10 | [38 empty] | 2014-06-01 | 2014-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T5223318SP | TO->FROM | LYONS - WHEATLAND 115KV CKT 1 | S | WERE | MIDW | WEST | REG E-IL | 0 | 533439 | WHEATLD3 115.00 | 530620 | LYONS 3 115.00 | 0 |  | 1 | 18SP | 70 | 70 |  | 101.3 | 89.4423 | 104.0957 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICE_CO 115KV CKT 1 | 0 | 530623 | RICE 3 115.00 | 533413 | CIRCLE 3 115.00 | 0 |  | 1 | 72.867 |  | MIDW | LYONS - WHEATLAND 115KV CKT 1 MIDW Displacement | Rebuild 19.1 miles |  | 240 | [9 empty] | 562.5k per mile | 10743750 | 2008-01-01 | [38 empty] | 2015-06-01 | 2015-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T5223318SP | TO->FROM | LYONS - WHEATLAND 115KV CKT 1 | S | WERE | MIDW | WEST | REG E-IL | 0 | 533439 | WHEATLD3 115.00 | 530620 | LYONS 3 115.00 | 0 |  | 1 | 18SP | 70 | 70 |  | 101.3 | 89.4423 | 104.0957 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICE_CO 115KV CKT 1 | 0 | 530623 | RICE 3 115.00 | 533413 | CIRCLE 3 115.00 | 0 |  | 1 | 72.867 |  | WERE | LYONS - WHEATLAND 115KV CKT 1 WERE Displacement | Rebuild 0.3 miles |  | 240 | [9 empty] | 562.5k per mile | 168750 | 2008-01-01 | [38 empty] | 2015-06-01 | 2015-06-01
GEN-2001-024 | Mattison | [7 empty] | 506957506938012SP | TO->FROM | LOWELL 5 - TONTITOWN 161KV CKT 1 | U | AEPW | AEPW | FAYETTEV | FAYETTEV | 0 | 506957 | TONTITN5 161.00 | 506938 | LOWELL 5 161.00 | 0 |  | 1 |  | 373 | 443 |  |  | 167.5 | [9 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | AEPW | LOWELL 5 - TONTITOWN 161KV CKT 1 | Add one 161KV terminal for Tontitown | [12 empty] | 537700 | [39 empty] | 2008-06-01 | 2008-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 1 | 2008AGP1AFS31T5783118SP | FROM->TO | LONGVIEW - WESTERN ELECTRIC 161KV CKT 1 | REL | MIPU | MIPU |  |  | 0 | 541224 | LNGVW 5 161.00 | 541222 | WSTELEC5 161.00 | 0 |  | 1 | 18SP | 223 | 245 | 100.8 | 100.5 | 101.3988 | 102.651 | [7 empty] | CATEGORYB | SINGLE | GREENWOOD ENERGY CENTER - LEES SUMMIT EAST 161KV CKT 1 | 0 | 541218 | GRNWD 5 161.00 | 541233 | LEESUM 5 161.00 | 0 |  | 1 | 251.495 |  | MIPU | LONGVIEW - WESTERN ELECTRIC 161KV CKT 1 | Replace wavetraps at Longview and Western Electric | 229 | 260 |  |  |  | 12 | 12 | [5 empty] | 50000 | [39 empty] | 2018-06-01 | 2018-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T8035510SP | TO->FROM | LONGVIEW - SAMPSON 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541345 | SAMPSON5 161.00 | 541224 | LNGVW 5 161.00 | 0 |  | 1 | 10SP | 223 | 245 | 102.0 |  | 101.5975 | 103.1855 | [7 empty] | CATEGORYB | SINGLE | PLEASANT HILL (P HILL) 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 541200 | PHILL 7 345.00 | 541225 | PHILL 5 161.00 | 541361 | PHILL T 13.800 | 1 | 252.8045 |  | MIPU | Grandview East - Sampson - Longview 161kV Ckt 1 | Replace wavetraps at Grandview East and Longview. | 233 | 265 |  |  |  | 6 | 6 | [5 empty] | 50000 | 2009-03-19 | [38 empty] | 2010-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T903310SP | FROM->TO | LOCUST GROVE - LONE STAR 115KV CKT 1 | EXP | AEPW | AEPW | NORTHERN | NORTHERN | 0 | 510423 | L GROVE3 115.00 | 510399 | LSTAR--3 115.00 | 0 |  | 1 | 10SP | 84 | 98 |  |  | 98.8424 | 101.2581 | [7 empty] | CATEGORYB | SINGLE | CATOOSA - INOLA TAP 138KV CKT 1 | 0 | 509752 | INOLATP4 138.00 | 509790 | CATOOSA4 138.00 | 0 |  | 1 | 99.2329 |  | AEPW | LOCUST GROVE - LONE STAR 115KV CKT 1 Displacement | Rebuild 2.15 miles of 266 ACSR with 795 ACSR | 120 | 120 | 120 | 120 | 2.15 | 20 | 6 |  | 0.0021 | 0.01145 | 0.00172 | New limits will be switch | 1935000 | 2007-06-04 | [38 empty] | 2010-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T2491318SP | FROM->TO | LOCUST GROVE - LONE STAR 115KV CKT 1 | EXP | AEPW | AEPW | NORTHERN | NORTHERN | 0 | 510423 | L GROVE3 115.00 | 510399 | LSTAR--3 115.00 | 0 |  | 1 | 18SP | 84 | 98 | 107.8 | 108.1 | 104.132 | 108.4126 | [7 empty] | CATEGORYB | SINGLE | CATOOSA - INOLA TAP 138KV CKT 1 | 0 | 509752 | INOLATP4 138.00 | 509790 | CATOOSA4 138.00 | 0 |  | 1 | 106.2443 |  | AEPW | LOCUST GROVE - LONE STAR 115KV CKT 1 Displacement | Rebuild 2.15 miles of 266 ACSR with 795 ACSR | 120 | 120 | 120 | 120 | 2.15 | 20 | 6 |  | 0.0021 | 0.01145 | 0.00172 | New limits will be switch | 1935000 | 2007-06-04 | [38 empty] | 2010-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T2521318SP | FROM->TO | LOCUST GROVE - LONE STAR 115KV CKT 1 | EXP | AEPW | AEPW | NORTHERN | NORTHERN | 0 | 510423 | L GROVE3 115.00 | 510399 | LSTAR--3 115.00 | 0 |  | 1 | 18SP | 84 | 98 | 102.0 | 102.1 | 98.3105 | 102.4119 | [7 empty] | CATEGORYB | SINGLE | CHOUTEAU - INOLA TAP 138KV CKT 1 | 0 | 509752 | INOLATP4 138.00 | 510373 | CHOUTEA4 138.00 | 0 |  | 1 | 100.3637 |  | AEPW | LOCUST GROVE - LONE STAR 115KV CKT 1 Displacement | Rebuild 2.15 miles of 266 ACSR with 795 ACSR | 120 | 120 | 120 | 120 | 2.15 | 20 | 6 |  | 0.0021 | 0.01145 | 0.00172 | New limits will be switch | 1935000 | 2007-06-04 | [38 empty] | 2010-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T22218SP | FROM->TO | LOCUST GROVE - LONE STAR 115KV CKT 1 | EXP | AEPW | AEPW | NORTHERN | NORTHERN | 0 | 510423 | L GROVE3 115.00 | 510399 | LSTAR--3 115.00 | 0 |  | 1 | 18SP | 84 | 98 |  | 100.9 | 101.3944 | 100.6706 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | 98.6572 |  | AEPW | LOCUST GROVE - LONE STAR 115KV CKT 1 Displacement | Rebuild 2.15 miles of 266 ACSR with 795 ACSR | 120 | 120 | 120 | 120 | 2.15 | 20 | 6 |  | 0.0021 | 0.01145 | 0.00172 | New limits will be switch | 1935000 | 2007-06-04 | [38 empty] | 2010-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T2721318SP | FROM->TO | LOCUST GROVE - LONE STAR 115KV CKT 1 | EXP | AEPW | AEPW | NORTHERN | NORTHERN | 0 | 510423 | L GROVE3 115.00 | 510399 | LSTAR--3 115.00 | 0 |  | 1 | 18SP | 84 | 98 |  |  | 95.9979 | 100 | [7 empty] | CATEGORYB | SINGLE | CHOUTEAU - EXPLORER CLAREMORE TAP 138KV CKT 1 | 0 | 510373 | CHOUTEA4 138.00 | 510401 | EXCLART4 138.00 | 0 |  | 1 | 98 |  | AEPW | LOCUST GROVE - LONE STAR 115KV CKT 1 Displacement | Rebuild 2.15 miles of 266 ACSR with 795 ACSR | 120 | 120 | 120 | 120 | 2.15 | 20 | 6 |  | 0.0021 | 0.01145 | 0.00172 | New limits will be switch | 1935000 | 2007-06-04 | [38 empty] | 2010-06-01 | 2012-06-01
2008-AGP1 | AFS3 | 1347 - WILLIVWEBRIC | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T3924209SP | TO->FROM | LIVONIA BULK - WILBERT 138KV CKT 1 | S | EES | EES | EES_GSU-LA | EES_GSU-LA | 0 | 335507 | 4WILBT 138.00 | 335505 | 4LIVON 138.00 | 0 |  | 1 | 09SP | 289 | 289 | 107.6 | 105.7 | 114.3591 | 119.4342 | [7 empty] | CATEGORYB | SINGLE | WEBRE - WELLS 500KV CKT 1 | 0 | 335368 | 8WELLS 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | 345.1648 |  | EES | LIVONIA BULK - WILBERT 138KV CKT 1 | Replace switches, breakers, & CTs @ Wilbert & Livonia. 19.29 miles transmission line | [12 empty] | 41123000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T7121309SP | FROM->TO | LITCHFIELD (LITCH 2X) 161/69/13.2KV TRANSFORMER CKT 1 | EXP | WERE |  | SEAST |  | 2 | 532932 | LITCH 5 161.00 | 533765 | LITCH 2 69.000 | 532953 | LITCH2 1 13.200 | 1 | 09SP | 100 | 110 | 102.3 | 107.2 | 104.8146 | 107.9634 | [7 empty] | CATEGORYB | SINGLE | LITCHFIELD (LITCH 1X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532932 | LITCH 5 161.00 | 533765 | LITCH 2 69.000 | 532952 | LITCH1 1 13.200 | 1 | 118.7597 |  | WERE | Fort Scott 161/69kV Transformer CKT 1 | New 161/69 kV transformer at Ft Scott. | 100 | 110 |  |  |  | 18 | 18 | [5 empty] | 1400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T7141309SP | FROM->TO | LITCHFIELD (LITCH 1X) 161/69/13.2KV TRANSFORMER CKT 1 | EXP | WERE |  | SEAST |  | 2 | 532932 | LITCH 5 161.00 | 533765 | LITCH 2 69.000 | 532952 | LITCH1 1 13.200 | 1 | 09SP | 100 | 110 | 102.7 | 108 | 105.2181 | 108.307 | [7 empty] | CATEGORYB | SINGLE | LITCHFIELD (LITCH 2X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532932 | LITCH 5 161.00 | 533765 | LITCH 2 69.000 | 532953 | LITCH2 1 13.200 | 1 | 119.1377 |  | WERE | Fort Scott 161/69kV Transformer CKT 1 | New 161/69 kV transformer at Ft Scott. | 100 | 110 |  |  |  | 18 | 18 | [5 empty] | 1400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 2 | 2008AGP1AFS31T12341209SP | FROM->TO | LEHIGH TAP - UNITED NO. 9 CONGER 69KV CKT 1 | CP | WERE | WERE | SEAST | SEAST | 0 | 533638 | LEHIGTP2 69.000 | 533651 | UN9CONG2 69.000 | 0 |  | 1 | 09SP | 32 | 32 |  | 112.7 | 111.0722 | 100.5446 | [7 empty] | CATEGORYB | GENOUT | GEN533637 2-CITY OF IOLA | 0 | 0 |  | 0 |  | 0 |  |  | 32.1743 |  | WERE | LEHIGH TAP - UNITED NO. 9 CONGER 69KV CKT 1 | Tear down / Rebuild 0.91-mile 69 kV line; 954 kcmiol ACSR | 72 | 72 | 72 | 72 | 0.91 | 12 | 6 |  | 0.002 | 0.014 | 0.00031 | 72 MVA limit is switches | 236391 | 2008-03-14 | [38 empty] | 2009-06-01 | 2013-10-31
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T1521309SH | TO->FROM | LEHIGH TAP - OWL CREEK 69KV CKT 1 | CP | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 09SH | 32 | 32 |  | 103.2 | 101.1 | 103.3332 | [7 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 33.0666 |  | WERE | LEHIGH TAP - OWL CREEK 69KV CKT 1 | Tear down / Rebuild 8.47-mile 69 kV line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 8.47 | 18 | 6 |  | 0.01787 | 0.12163 | 0.00259 | Terminal equipment limit | 3494292 | 2008-03-14 | [38 empty] | 2009-06-01 | 2012-12-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17273318SP |  | LAWN RIDGE 115KV | REL | SUNC |  | NORTON-D |  |  | 531368 | LAWNRID3 115.00 | [5 empty] | 18SP | [8 empty] | 0.91959 | 0.88681 | 0.99341 | 0.9 | 1.05 | CATEGORYB | SINGLE | MINGO (MINGO) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 531451 | MINGO 7 345.00 | 531429 | MINGO 3 115.00 | 531452 | MINGTER1 13.800 | 1 |  |  | SUNC | RULETON 115KV Capacitor | Install Second 12 Mvar cap bank at Ruleton 115kV | [12 empty] | 486000 | 2008-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
NA | [8 empty] | NAKACP5429815429651 |  | LACYGNE - WEST GARDNER 345KV CKT 1 | U | KACP | KACP |  |  | 0 | 542981 | LACYGNE7 | 542965 | W.GRDNR7 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | KACP | LACYGNE - WEST GARDNER 345KV CKT 1 | KCPL Sponsored Project to Reconductor Line to be In-Service by 6/1/2006 | [52 empty] | 2006-06-01 | 2006-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T16501313SP | TO->FROM | LABBE - PONT DES MOUTON 230KV CKT 1 | S | LAFA | LAFA | LAFA | LAFA | 0 | 502410 | PMOUTON6 230.00 | 502421 | LABBE 230.00 | 0 |  | 1 | 13SP | 655 | 785 | 111.3 | 107.1 | 107.282 | 111.5094 | [7 empty] | CATEGORYB | NONSINGLE | SERCW-21 | 0 | 0 |  | 0 |  | 0 |  |  | 875.3488 |  | LAFA | LABBE - PONT DES MOUTON 230KV CKT 1 | Indeterminate | [52 empty] | 2010-06-01 | 2010-06-01
2008-AGP1 | AFS3 | CONT-0633 - East Manhattan 230-115kV XFMR | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17493318SP |  | KSU CAMPUS 115KV | REL | WERE |  | NCENTRAL |  |  | 533333 | KSU 3 115.00 | [5 empty] | 18SP | [6 empty] | 0.91018 | 0.90033 | 0.8966 | 0.84447 | 0.99708 | 0.93 | 1.05 | CATEGORYB | SINGLE | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31V17082218SP |  | KOLACHE 69KV | REL | OKGE |  | SHAWNEE |  |  | 515079 | KOLACHE2 69.000 | [5 empty] | 18SP | [7 empty] | 0.89378 | 0.91605 | 0.89389 | 0.96591 | 0.9 | 1.05 | CATEGORYB | NONSINGLE | OGE3TERM36 | 0 | 0 |  | 0 |  | 0 |  |  |  |  | OKGE | EL RENO 69KV CAP BANK | Install 12 Mvar Capacitor at El Reno 69 kV bus | [52 empty] | 2011-06-01 | 2011-06-01
2006-AG1 | 2006-AG1 | [7 empty] | KNOOBHIL41421OKGEMTL-51316SP |  | KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1 | U | OKGE |  |  |  | 1 | 514795 | KNOBHIL4 138 | 514794 | KNOBHIL269.0 | 515732 | KNOBHIL113.2 | 1 | 16SP |  | 67 | [12 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | OKGE | KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1 | Replace bus tie with 100MVA transformer | 123 | 134 | 123 | 134 |  | 15 | 12 | [5 empty] | 1750000 | [39 empty] | 2006-06-01 | 2008-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V1525509SH |  | KNOB HILL 115KV | EXP | WERE |  | NCENTRAL |  |  | 533332 | KNOB HL3 115.00 | [5 empty] | 09SH | [6 empty] | 0.82962 | 0.80438 | 0.82906 | 0.7312 | 0.99362 | 0.93 | 1.05 | CATEGORYB | SINGLE | KELLY - SOUTH SENECA 115KV CKT 1 | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 |  |  |  | 2009-04-01 | 2009-04-01 | 2009-04-01 | 41640 | 41640 | 1 | 1 | 2014 | 41897 | 42156 | 40179 | 41640 | 2014-01-01 | 2010-06-01 | [13 empty] | Ph1: 10.8 Mvar cap bank at Seneca 115 kV 09S. Ph2: Knob Hill -S. Beatrice 115 kV 10S | [7 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 3 | 2008AGP1AFS31V2841309SP |  | KNOB HILL 115KV | EXP | WERE |  | NCENTRAL |  |  | 533332 | KNOB HL3 115.00 | [5 empty] | 09SP | [6 empty] | 0.84632 | 0.68621 | 0.85539 | 0.47259 | 0.98388 | 0.93 | 1.05 | CATEGORYB | SINGLE | KELLY - SOUTH SENECA 115KV CKT 1 | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 |  |  |  | 2009-04-01 | 2009-04-01 | 2009-04-01 | 41640 | 41640 | 1 | 1 | 2014 | 41897 | 42156 | 40179 | 41640 | 2014-01-01 | 2010-06-01 | [13 empty] | Ph1: 10.8 Mvar cap bank at Seneca 115 kV 09S. Ph2: Knob Hill -S. Beatrice 115 kV 10S | [7 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V3405509SP |  | KNOB HILL 115KV | EXP | WERE |  | NCENTRAL |  |  | 533332 | KNOB HL3 115.00 | [5 empty] | 09SP | [8 empty] | 0.86401 | 0.83448 | 0.9799 | 0.93 | 1.05 | CATEGORYB | SINGLE | CONCORDIA - ELMCREK6 230.00 230KV CKT 1 | 0 | 539639 | ELMCREK6 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V7245509SP |  | KNOB HILL 115KV | EXP | WERE |  | NCENTRAL |  |  | 533332 | KNOB HL3 115.00 | [5 empty] | 09SP | [8 empty] | 0.86407 | 0.83456 | 0.9799 | 0.93 | 1.05 | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539658 | CONCRD6 230.00 | 539657 | CONCORD3 115.00 | 539904 | CONCOD-T 13.800 | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FNSL | FDNS-Iteration limit exceeded | 3 | 2 | 2008AGP1AFS32V23213SP |  | KNOB HILL 115KV | EXP | WERE |  | NCENTRAL |  |  | 533332 | KNOB HL3 115.00 | [5 empty] | 13SP | [8 empty] | 0.99909 | 0.9265 | 1.0229 | 0.93 | 1.05 | CATEGORYB | SINGLE | EAST MANHATTAN - ELMCREK6 230.00 230KV CKT 1 | 0 | 539639 | ELMCREK6 230.00 | 532861 | EMANHAT6 230.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 |  |  |  | 2009-04-01 | 2009-04-01 | 2009-04-01 | 41640 | 41640 | 1 | 1 | 2014 | 41897 | 42156 | 40179 | 41640 | 2014-01-01 | 2010-06-01 | [13 empty] | Ph1: 10.8 Mvar cap bank at Seneca 115 kV 09S. Ph2: Knob Hill -S. Beatrice 115 kV 10S | [7 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T1735509SP | TO->FROM | KNOB HILL - SMITTYVILLE N.M. COOP (NEMAHA MARSHALL R.E. 115KV CKT 1 | EXP | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533338 | SMITTYV3 115.00 | 533332 | KNOB HL3 115.00 | 0 |  | 1 | 09SP | 92 | 92 |  |  | 105.3588 | 110.7964 | [7 empty] | CATEGORYB | SINGLE | CONCORDIA - ELMCREK6 230.00 230KV CKT 1 | 0 | 539639 | ELMCREK6 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 | 101.9327 |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T6795509SP | TO->FROM | KNOB HILL - SMITTYVILLE N.M. COOP (NEMAHA MARSHALL R.E. 115KV CKT 1 | EXP | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533338 | SMITTYV3 115.00 | 533332 | KNOB HL3 115.00 | 0 |  | 1 | 09SP | 92 | 92 |  |  | 105.3542 | 110.7903 | [7 empty] | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539657 | CONCORD3 115.00 | 539658 | CONCRD6 230.00 | 539904 | CONCOD-T 13.800 | 1 | 101.9271 |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T1335509SP | TO->FROM | KNOB HILL - SMITTYVILLE N.M. COOP (NEMAHA MARSHALL R.E. 115KV CKT 1 | EXP | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533338 | SMITTYV3 115.00 | 533332 | KNOB HL3 115.00 | 0 |  | 1 | 09SP | 92 | 92 |  |  | 105.0881 | 110.1524 | [7 empty] | CATEGORYB | SINGLE | EAST MANHATTAN - ELMCREK6 230.00 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 539639 | ELMCREK6 230.00 | 0 |  | 1 | 101.3402 |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 |  |  |  | 2009-04-01 | 2009-04-01 | 2009-04-01 | 41640 | 41640 | 1 | 1 | 2014 | 41897 | 42156 | 40179 | 41640 | 2014-01-01 | 2010-06-01 | [13 empty] | Ph1: 10.8 Mvar cap bank at Seneca 115 kV 09S. Ph2: Knob Hill -S. Beatrice 115 kV 10S | [7 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31V2662218SP |  | KENNETT CAP BANK 1 69KV | REL | SWPA |  | EMINTH |  |  | 505632 | KEN CAP2 69.000 | [5 empty] | 18SP | [8 empty] | 0.90784 | 0.8681 | 1.0129 | 0.9 | 1.05 | CATEGORYB | SINGLE | KENNETT - NEW MADRID 161KV CKT 1 | 0 | 505400 | N MADRD5 161.00 | 505410 | KENNETT5 161.00 | 0 |  | 1 |  |  | SWPA | KENNETT CAP BANK 1 161KV CAP BANK | Install Additional Cap Bank at Kennett | [52 empty] | 2014-06-01 | 2014-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31V2672218SP |  | KENNETT CAP BANK 1 161KV | REL | SWPA |  | EMINTH |  |  | 505633 | KEN CAP5 161.00 | [5 empty] | 18SP | [7 empty] | 0.84396 | 0.84837 | 0.81517 | 0.99478 | 0.9 | 1.05 | CATEGORYB | SINGLE | KENNETT - NEW MADRID 161KV CKT 1 | 0 | 505400 | N MADRD5 161.00 | 505410 | KENNETT5 161.00 | 0 |  | 1 |  |  | SWPA | KENNETT CAP BANK 1 161KV CAP BANK | Install Additional Cap Bank at Kennett | [52 empty] | 2014-06-01 | 2014-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31V2542218SP |  | KENNETT 69KV | REL | SWPA |  | EMINTH |  |  | 505408 | KENNETT2 69.000 | [5 empty] | 18SP | [8 empty] | 0.90782 | 0.86808 | 1.0129 | 0.9 | 1.05 | CATEGORYB | SINGLE | KENNETT - NEW MADRID 161KV CKT 1 | 0 | 505400 | N MADRD5 161.00 | 505410 | KENNETT5 161.00 | 0 |  | 1 |  |  | SWPA | KENNETT CAP BANK 1 161KV CAP BANK | Install Additional Cap Bank at Kennett | [52 empty] | 2014-06-01 | 2014-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31V2552218SP |  | KENNETT 161KV | REL | SWPA |  | EMINTH |  |  | 505410 | KENNETT5 161.00 | [5 empty] | 18SP | [7 empty] | 0.84391 | 0.84832 | 0.81513 | 0.99472 | 0.9 | 1.05 | CATEGORYB | SINGLE | KENNETT - NEW MADRID 161KV CKT 1 | 0 | 505400 | N MADRD5 161.00 | 505410 | KENNETT5 161.00 | 0 |  | 1 |  |  | SWPA | KENNETT CAP BANK 1 161KV CAP BANK | Install Additional Cap Bank at Kennett | [52 empty] | 2014-06-01 | 2014-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T545509SH | FROM->TO | KELLY - SOUTH SENECA 115KV CKT 1 | EXP | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 09SH | 92 | 92 | 113.9 | 115.8 | 117.8454 | 118.9526 | [7 empty] | CATEGORYB | SINGLE | EAST MANHATTAN - ELMCREK6 230.00 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 539639 | ELMCREK6 230.00 | 0 |  | 1 | 109.4364 |  | WERE | KELLY - SOUTH SENECA 115KV CKT 1 | Rebuild 10.28 mile line with 1192.5 kcmil ACSR and replace CTs. | 160 | 160 | 160 | 160 | 10.28 | 12 | 5 |  | 0.0062742 | 0.055391 | 0.0081838 | Breaker limit is 160 MVA. | [40 empty] | 2009-06-01 | 2010-12-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T785509SH | FROM->TO | KELLY - SOUTH SENECA 115KV CKT 1 | EXP | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 09SH | 92 | 92 | 113.8 | 115.7 | 117.6148 | 118.7663 | [7 empty] | CATEGORYB | SINGLE | CONCORDIA - ELMCREK6 230.00 230KV CKT 1 | 0 | 539639 | ELMCREK6 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 | 109.265 |  | WERE | KELLY - SOUTH SENECA 115KV CKT 1 | Rebuild 10.28 mile line with 1192.5 kcmil ACSR and replace CTs. | 160 | 160 | 160 | 160 | 10.28 | 12 | 5 |  | 0.0062742 | 0.055391 | 0.0081838 | Breaker limit is 160 MVA. | [40 empty] | 2009-06-01 | 2010-12-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T3535509SH | FROM->TO | KELLY - SOUTH SENECA 115KV CKT 1 | EXP | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 09SH | 92 | 92 | 113.8 | 115.7 | 117.6094 | 118.761 | [7 empty] | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539657 | CONCORD3 115.00 | 539658 | CONCRD6 230.00 | 539904 | CONCOD-T 13.800 | 1 | 109.2601 |  | WERE | KELLY - SOUTH SENECA 115KV CKT 1 | Rebuild 10.28 mile line with 1192.5 kcmil ACSR and replace CTs. | 160 | 160 | 160 | 160 | 10.28 | 12 | 5 |  | 0.0062742 | 0.055391 | 0.0081838 | Breaker limit is 160 MVA. | [40 empty] | 2009-06-01 | 2010-12-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 2 | 2008AGP1AFS31T2633209SP | FROM->TO | KELLY - SOUTH SENECA 115KV CKT 1 | EXP | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 09SP | 92 | 92 |  |  | 100.9739 | 140.9237 | [7 empty] | CATEGORYB | SINGLE | CONCORDIA - ELMCREK6 230.00 230KV CKT 1 | 0 | 539639 | ELMCREK6 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 | 129.6498 |  | WERE | KELLY - SOUTH SENECA 115KV CKT 1 | Rebuild 10.28 mile line with 1192.5 kcmil ACSR and replace CTs. | 160 | 160 | 160 | 160 | 10.28 | 12 | 5 |  | 0.0062742 | 0.055391 | 0.0081838 | Breaker limit is 160 MVA. | [40 empty] | 2009-06-01 | 2010-12-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 2 | 2008AGP1AFS31T8343209SP | FROM->TO | KELLY - SOUTH SENECA 115KV CKT 1 | EXP | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 09SP | 92 | 92 |  |  | 100.9646 | 140.9034 | [7 empty] | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539657 | CONCORD3 115.00 | 539658 | CONCRD6 230.00 | 539904 | CONCOD-T 13.800 | 1 | 129.6311 |  | WERE | KELLY - SOUTH SENECA 115KV CKT 1 | Rebuild 10.28 mile line with 1192.5 kcmil ACSR and replace CTs. | 160 | 160 | 160 | 160 | 10.28 | 12 | 5 |  | 0.0062742 | 0.055391 | 0.0081838 | Breaker limit is 160 MVA. | [40 empty] | 2009-06-01 | 2010-12-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T1305509SP | FROM->TO | KELLY - SOUTH SENECA 115KV CKT 1 | EXP | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 09SP | 92 | 92 | 111.2 | 112.1 | 135.3435 | 137.4265 | [7 empty] | CATEGORYB | SINGLE | EAST MANHATTAN - ELMCREK6 230.00 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 539639 | ELMCREK6 230.00 | 0 |  | 1 | 126.4324 |  | WERE | KELLY - SOUTH SENECA 115KV CKT 1 | Rebuild 10.28 mile line with 1192.5 kcmil ACSR and replace CTs. | 160 | 160 | 160 | 160 | 10.28 | 12 | 5 |  | 0.0062742 | 0.055391 | 0.0081838 | Breaker limit is 160 MVA. | [40 empty] | 2009-06-01 | 2010-12-01
2008-AGP1 | AFS3 | CONT-0900 - JEC - East Manhattan 230kV |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T1275509SP | FROM->TO | KELLY - SOUTH SENECA 115KV CKT 1 | EXP | WERE | WERE | NEAST | NCENTRAL | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 09SP | 92 | 92 |  |  | 107.5621 | 106.5249 | [7 empty] | CATEGORYB | SINGLE | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 0 | 532852 | JEC 6 230.00 | 532861 | EMANHAT6 230.00 | 0 |  | 1 | 98.0029 |  | WERE | KELLY - SOUTH SENECA 115KV CKT 1 | Rebuild 10.28 mile line with 1192.5 kcmil ACSR and replace CTs. | 160 | 160 | 160 | 160 | 10.28 | 12 | 5 |  | 0.0062742 | 0.055391 | 0.0081838 | Breaker limit is 160 MVA. | [40 empty] | 2009-06-01 | 2010-12-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 2 | 2008AGP1AFS31V9143213SP |  | JUNCTION CITY 115KV | REL | WERE |  | NCENTRAL |  |  | 533330 | JCTCTY 3 115.00 | [5 empty] | 13SP | [8 empty] | 0.9441 | 0.92385 | 0.96652 | 0.93 | 1.05 | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 | CONT-0633 - East Manhattan 230-115kV XFMR | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17483318SP |  | JUNCTION CITY 115KV | REL | WERE |  | NCENTRAL |  |  | 533330 | JCTCTY 3 115.00 | [5 empty] | 18SP | [6 empty] | 0.92511 | 0.91421 | 0.89872 | 0.8498 | 0.95578 | 0.93 | 1.05 | CATEGORYB | SINGLE | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17683318SP |  | JUNCTION CITY 115KV | REL | WERE |  | NCENTRAL |  |  | 533330 | JCTCTY 3 115.00 | [5 empty] | 18SP | [8 empty] | 0.94217 | 0.90107 | 0.95578 | 0.93 | 1.05 | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 3 | 2008AGP1AFS31V3072318SP |  | JONESBORO 161KV | REL | SWPA |  | EMINTH |  |  | 505418 | JONESBO5 161.00 | [5 empty] | 18SP | [7 empty] | 0.87876 | 0.8795 | 0.8594 | 0.97376 | 0.9 | 1.05 | CATEGORYB | SINGLE | KENNETT - NEW MADRID 161KV CKT 1 | 0 | 505400 | N MADRD5 161.00 | 505410 | KENNETT5 161.00 | 0 |  | 1 |  |  | SWPA | KENNETT CAP BANK 1 161KV CAP BANK | Install Additional Cap Bank at Kennett | [52 empty] | 2014-06-01 | 2014-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V3495509SP |  | JEWELL 3 115KV | EXP | MKEC |  |  |  |  | 539669 | JEWELL 3 115.00 | [5 empty] | 09SP | [8 empty] | 0.84929 | 0.80828 | 0.97591 | 0.9 | 1.05 | CATEGORYB | SINGLE | CONCORDIA - ELMCREK6 230.00 230KV CKT 1 | 0 | 539639 | ELMCREK6 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V7335509SP |  | JEWELL 3 115KV | EXP | MKEC |  |  |  |  | 539669 | JEWELL 3 115.00 | [5 empty] | 09SP | [8 empty] | 0.84934 | 0.80835 | 0.97591 | 0.9 | 1.05 | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539658 | CONCRD6 230.00 | 539657 | CONCORD3 115.00 | 539904 | CONCOD-T 13.800 | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V2525509SP |  | JEWELL 3 115KV | EXP | MKEC |  |  |  |  | 539669 | JEWELL 3 115.00 | [5 empty] | 09SP | [8 empty] | 0.86055 | 0.82148 | 0.97591 | 0.9 | 1.05 | CATEGORYB | SINGLE | EAST MANHATTAN - ELMCREK6 230.00 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 539639 | ELMCREK6 230.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FNSL | FDNS-Iteration limit exceeded | 3 | 2 | 2008AGP1AFS32V83213SP |  | JEWELL 3 115KV | EXP | MKEC |  |  |  |  | 539669 | JEWELL 3 115.00 | [5 empty] | 13SP | [8 empty] | 0.99998 | 0.77245 | 1.0049 | 0.9 | 1.05 | CATEGORYB | SINGLE | EAST MANHATTAN - ELMCREK6 230.00 230KV CKT 1 | 0 | 539639 | ELMCREK6 230.00 | 532861 | EMANHAT6 230.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T3992210SP | FROM->TO | JEWELL 3 - SMITH CENTER 115KV CKT 1 | EXP | MKEC | MKEC |  |  | 0 | 539669 | JEWELL 3 115.00 | 539693 | SMITH-C3 115.00 | 0 |  | 1 | 10SP | 79.7 | 79.7 |  |  | 97.1447 | 103.1495 | [7 empty] | CATEGORYB | SINGLE | BELOIT - CONCORDIA 115KV CKT 1 | 0 | 539650 | BELOIT 3 115.00 | 539657 | CONCORD3 115.00 | 0 |  | 1 | 82.2101 |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T4942213SP | FROM->TO | JEWELL 3 - SMITH CENTER 115KV CKT 1 | EXP | MKEC | MKEC |  |  | 0 | 539669 | JEWELL 3 115.00 | 539693 | SMITH-C3 115.00 | 0 |  | 1 | 13SP | 79.7 | 79.7 |  |  | 97.2523 | 103.8528 | [7 empty] | CATEGORYB | SINGLE | BELOIT - CONCORDIA 115KV CKT 1 | 0 | 539650 | BELOIT 3 115.00 | 539657 | CONCORD3 115.00 | 0 |  | 1 | 82.7707 |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T7332218SP | FROM->TO | JEWELL 3 - SMITH CENTER 115KV CKT 1 | EXP | MKEC | MKEC |  |  | 0 | 539669 | JEWELL 3 115.00 | 539693 | SMITH-C3 115.00 | 0 |  | 1 | 18SP | 79.7 | 79.7 |  |  | 102.0833 | 105.7826 | [7 empty] | CATEGORYB | SINGLE | BELOIT - CONCORDIA 115KV CKT 1 | 0 | 539650 | BELOIT 3 115.00 | 539657 | CONCORD3 115.00 | 0 |  | 1 | 84.3087 |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T3712210SP | TO->FROM | JARBALO JUNCTION SWITCHING STATION - STRANGER CREEK 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533268 | STRANGR3 115.00 | 533244 | JARBALO3 115.00 | 0 |  | 1 | 10SP | 223 | 240 |  |  | 98.0597 | 101.5033 | [7 empty] | CATEGORYB | SINGLE | STRANGER CREEK - THORNTON STREET 115KV CKT 1 | 0 | 533268 | STRANGR3 115.00 | 533272 | THORNTN3 115.00 | 0 |  | 1 | 243.6079 |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 4000000 | 2006-07-25 | [38 empty] | 2010-06-01 | 2011-06-01
2008-AGP1 | AFS3 | CONT-0800 - Stranger Creek - Craig 345kV |  |  | FDNS |  | 3 | 2 | 2008AGP1AFS31T2433210SP | TO->FROM | JARBALO JUNCTION SWITCHING STATION - STRANGER CREEK 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533268 | STRANGR3 115.00 | 533244 | JARBALO3 115.00 | 0 |  | 1 | 10SP | 223 | 240 |  |  | 96.6802 | 100.973 | [7 empty] | CATEGORYB | SINGLE | CRAIG - STRANGER CREEK 345KV CKT 1 | 0 | 532772 | STRANGR7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 | 242.3352 |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 4000000 | 2006-07-25 | [38 empty] | 2010-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 2 | 2008AGP1AFS31T3693213SP | TO->FROM | JARBALO JUNCTION SWITCHING STATION - STRANGER CREEK 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533268 | STRANGR3 115.00 | 533244 | JARBALO3 115.00 | 0 |  | 1 | 13SP | 223 | 240 | 101.1 | 100.4 | 98.3022 | 102.3815 | [7 empty] | CATEGORYB | SINGLE | STRANGER CREEK - THORNTON STREET 115KV CKT 1 | 0 | 533268 | STRANGR3 115.00 | 533272 | THORNTN3 115.00 | 0 |  | 1 | 245.7156 |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 4000000 | 2006-07-25 | [38 empty] | 2010-06-01 | 2011-06-01
2008-AGP1 | AFS3 | CONT-0800 - Stranger Creek - Craig 345kV |  |  | FDNS |  | 3 | 2 | 2008AGP1AFS31T3363213SP | TO->FROM | JARBALO JUNCTION SWITCHING STATION - STRANGER CREEK 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533268 | STRANGR3 115.00 | 533244 | JARBALO3 115.00 | 0 |  | 1 | 13SP | 223 | 240 |  |  | 95.5183 | 100.6701 | [7 empty] | CATEGORYB | SINGLE | CRAIG - STRANGER CREEK 345KV CKT 1 | 0 | 532772 | STRANGR7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 | 241.6082 |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 4000000 | 2006-07-25 | [38 empty] | 2010-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 2 | 2008AGP1AFS31T6553218SP | TO->FROM | JARBALO JUNCTION SWITCHING STATION - STRANGER CREEK 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533268 | STRANGR3 115.00 | 533244 | JARBALO3 115.00 | 0 |  | 1 | 18SP | 223 | 240 | 105.0 | 104.5 | 98.2198 | 106.9759 | [7 empty] | CATEGORYB | SINGLE | STRANGER CREEK - THORNTON STREET 115KV CKT 1 | 0 | 533268 | STRANGR3 115.00 | 533272 | THORNTN3 115.00 | 0 |  | 1 | 256.7422 |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 4000000 | 2006-07-25 | [38 empty] | 2010-06-01 | 2011-06-01
2008-AGP1 | AFS3 | CONT-0800 - Stranger Creek - Craig 345kV |  |  | FDNS |  | 3 | 2 | 2008AGP1AFS31T6163218SP | TO->FROM | JARBALO JUNCTION SWITCHING STATION - STRANGER CREEK 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533268 | STRANGR3 115.00 | 533244 | JARBALO3 115.00 | 0 |  | 1 | 18SP | 223 | 240 |  |  | 95.1258 | 102.7778 | [7 empty] | CATEGORYB | SINGLE | CRAIG - STRANGER CREEK 345KV CKT 1 | 0 | 532772 | STRANGR7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 | 246.6667 |  | WERE | STRANGER CREEK - NW LEAVENWORTH 115KV | Rebuild 11.62-mile Jarbalo-NW Leavenworth 115 kV line and tap in & out of Stranger 115 kV | 223 | 240 | 223 | 240 | 11.62 | 15 | 6 |  | 0.00386 | 0.03405 | 0.00503 |  | 4000000 | 2006-07-25 | [38 empty] | 2010-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T452409AP | FROM->TO | IODINE - MOORELAND 138KV CKT 1 | PL | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 09AP | 72 | 72 | 103.4 | 118.8 | 131.5842 | 149.1882 | [7 empty] | CATEGORYB | SINGLE | FPL SWITCH - MOORELAND 138KV CKT 1 | 0 | 515785 | WINDFRM4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 107.4155 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T312409AP | FROM->TO | IODINE - MOORELAND 138KV CKT 1 | PL | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 09AP | 72 | 72 |  | 100.3 | 112.6607 | 129.9193 | [7 empty] | CATEGORYB | SINGLE | FPL SWITCH - WOODWARD 138KV CKT 1 | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 93.5419 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T744409FA | FROM->TO | IODINE - MOORELAND 138KV CKT 1 | PL | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 09FA | 72 | 72 |  | 114.4 | 115.0263 | 136.5126 | [7 empty] | CATEGORYB | SINGLE | FPL SWITCH - MOORELAND 138KV CKT 1 | 0 | 515785 | WINDFRM4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 98.2891 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 1 | 2008AGP1AFS31T364109FA | FROM->TO | IODINE - MOORELAND 138KV CKT 1 | PL | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 09FA | 72 | 72 |  |  | 96.8056 | 114.7266 | [7 empty] | CATEGORYB | SINGLE | FPL SWITCH - WOODWARD 138KV CKT 1 | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 82.6032 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T1092409G | FROM->TO | IODINE - MOORELAND 138KV CKT 1 | PL | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 09G | 72 | 72 |  |  | 100.5818 | 121.9976 | [7 empty] | CATEGORYB | SINGLE | FPL SWITCH - MOORELAND 138KV CKT 1 | 0 | 515785 | WINDFRM4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 87.8383 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 1 | 2008AGP1AFS31T522109G | FROM->TO | IODINE - MOORELAND 138KV CKT 1 | PL | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 09G | 72 | 72 |  |  | 87.9205 | 106.0965 | [7 empty] | CATEGORYB | SINGLE | FPL SWITCH - WOODWARD 138KV CKT 1 | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 76.3895 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T872409SH | FROM->TO | IODINE - MOORELAND 138KV CKT 1 | PL | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 09SH | 72 | 72 |  |  | 100.8204 | 121.0426 | [7 empty] | CATEGORYB | SINGLE | FPL SWITCH - MOORELAND 138KV CKT 1 | 0 | 515785 | WINDFRM4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 87.1507 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T1192409SP | FROM->TO | IODINE - MOORELAND 138KV CKT 1 | PL | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 09SP | 72 | 72 |  |  | 88.3461 | 108.8898 | [7 empty] | CATEGORYB | SINGLE | FPL SWITCH - MOORELAND 138KV CKT 1 | 0 | 515785 | WINDFRM4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 78.4007 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T1134409WP | FROM->TO | IODINE - MOORELAND 138KV CKT 1 | PL | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520957 | IODINE 4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 09WP | 72 | 72 |  | 100.1 | 101.0656 | 120.7304 | [7 empty] | CATEGORYB | SINGLE | FPL SWITCH - MOORELAND 138KV CKT 1 | 0 | 515785 | WINDFRM4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 86.9259 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T5785518SP | FROM->TO | HUNTSVILLE - ST_JOHN 115KV CKT 1 | EXP | MIDW | MIDW | REG E-IL | REG E-IL | 0 | 530618 | HUNTSVL3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 18SP | 80 | 88 |  | 109.6 | 106.1267 | 105.2783 | [7 empty] | CATEGORYB | SINGLE | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 533045 | GILL W 4 138.00 | 0 |  | 1 | 92.6449 |  | MIDW | HUNTSVILLE - ST_JOHN 115KV CKT 1 | Rebuild 26.5 miles Huntsville - St. John 115 kV line and replace CT, wavetrap, breakers, and relays. | 223 | 240 | 223 | 240 | 26.5 | 9 | 9 | [5 empty] | 7965000 | 2008-01-01 | [38 empty] | 2015-06-01 | 2015-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T5735518SP | FROM->TO | HUNTSVILLE - ST_JOHN 115KV CKT 1 | EXP | MIDW | MIDW | REG E-IL | REG E-IL | 0 | 530618 | HUNTSVL3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 18SP | 80 | 88 | 111.1 | 111.5 | 108.2322 | 105.2727 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - MULLERGREN 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | 92.64 |  | MIDW | HUNTSVILLE - ST_JOHN 115KV CKT 1 | Rebuild 26.5 miles Huntsville - St. John 115 kV line and replace CT, wavetrap, breakers, and relays. | 223 | 240 | 223 | 240 | 26.5 | 9 | 9 | [5 empty] | 7965000 | 2008-01-01 | [38 empty] | 2015-06-01 | 2015-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T5825518SP | FROM->TO | HUNTSVILLE - ST_JOHN 115KV CKT 1 | EXP | MIDW | MIDW | REG E-IL | REG E-IL | 0 | 530618 | HUNTSVL3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 18SP | 80 | 88 | 103.4 | 105.7 | 102.3941 | 101.2981 | [7 empty] | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 89.1423 |  | MIDW | HUNTSVILLE - ST_JOHN 115KV CKT 1 | Rebuild 26.5 miles Huntsville - St. John 115 kV line and replace CT, wavetrap, breakers, and relays. | 223 | 240 | 223 | 240 | 26.5 | 9 | 9 | [5 empty] | 7965000 | 2008-01-01 | [38 empty] | 2015-06-01 | 2015-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T5795518SP | TO->FROM | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | EXP | WERE | MIDW | WEST | REG E-IL | 0 | 533419 | HEC 3 115.00 | 530618 | HUNTSVL3 115.00 | 0 |  | 1 | 18SP | 92 | 92 |  | 111.3 | 107.9519 | 107.1746 | [7 empty] | CATEGORYB | SINGLE | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 533045 | GILL W 4 138.00 | 0 |  | 1 | 98.6006 |  | WERE | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 WERE | Tear down and rebuild 26.6% Ownership 28.79 mile HEC-Huntsville 115 kV line and replace CT, wavetrap and relays. | 223 | 240 | 223 | 240 | 7.66 | 36 | 36 |  |  |  |  | 562.5k per mile | 4308750 | 2008-01-01 | [38 empty] | 2015-06-01 | 2015-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T5795518SP | TO->FROM | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | EXP | WERE | MIDW | WEST | REG E-IL | 0 | 533419 | HEC 3 115.00 | 530618 | HUNTSVL3 115.00 | 0 |  | 1 | 18SP | 92 | 92 |  | 111.3 | 107.9519 | 107.1746 | [7 empty] | CATEGORYB | SINGLE | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 533045 | GILL W 4 138.00 | 0 |  | 1 | 98.6006 |  | MIDW | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 MIDW | Tear down and rebuild 73.4% Ownership 28.79 mile HEC-Huntsville 115 kV line and replace CT, wavetrap and relays. | 223 | 240 | 223 | 240 | 21.13 | 9 | 9 |  |  |  |  | 562.5k per mile | 11885625 | 2008-01-01 | [38 empty] | 2015-06-01 | 2015-06-01
2008-AGP1 | AFS3 | 5270 - HECHUNCIRMUL | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T5745518SP | TO->FROM | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | EXP | WERE | MIDW | WEST | REG E-IL | 0 | 533419 | HEC 3 115.00 | 530618 | HUNTSVL3 115.00 | 0 |  | 1 | 18SP | 92 | 92 | 112.6 | 113 | 109.8406 | 107.0676 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - MULLERGREN 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | 98.5022 |  | WERE | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 WERE | Tear down and rebuild 26.6% Ownership 28.79 mile HEC-Huntsville 115 kV line and replace CT, wavetrap and relays. | 223 | 240 | 223 | 240 | 7.66 | 36 | 36 |  |  |  |  | 562.5k per mile | 4308750 | 2008-01-01 | [38 empty] | 2015-06-01 | 2015-06-01
2008-AGP1 | AFS3 | 5270 - HECHUNCIRMUL | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T5745518SP | TO->FROM | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | EXP | WERE | MIDW | WEST | REG E-IL | 0 | 533419 | HEC 3 115.00 | 530618 | HUNTSVL3 115.00 | 0 |  | 1 | 18SP | 92 | 92 | 112.6 | 113 | 109.8406 | 107.0676 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - MULLERGREN 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | 98.5022 |  | MIDW | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 MIDW | Tear down and rebuild 73.4% Ownership 28.79 mile HEC-Huntsville 115 kV line and replace CT, wavetrap and relays. | 223 | 240 | 223 | 240 | 21.13 | 9 | 9 |  |  |  |  | 562.5k per mile | 11885625 | 2008-01-01 | [38 empty] | 2015-06-01 | 2015-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T5835518SP | TO->FROM | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | EXP | WERE | MIDW | WEST | REG E-IL | 0 | 533419 | HEC 3 115.00 | 530618 | HUNTSVL3 115.00 | 0 |  | 1 | 18SP | 92 | 92 | 105.4 | 107.6 | 104.3594 | 103.3689 | [7 empty] | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 95.0994 |  | WERE | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 WERE | Tear down and rebuild 26.6% Ownership 28.79 mile HEC-Huntsville 115 kV line and replace CT, wavetrap and relays. | 223 | 240 | 223 | 240 | 7.66 | 36 | 36 |  |  |  |  | 562.5k per mile | 4308750 | 2008-01-01 | [38 empty] | 2015-06-01 | 2015-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T5835518SP | TO->FROM | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | EXP | WERE | MIDW | WEST | REG E-IL | 0 | 533419 | HEC 3 115.00 | 530618 | HUNTSVL3 115.00 | 0 |  | 1 | 18SP | 92 | 92 | 105.4 | 107.6 | 104.3594 | 103.3689 | [7 empty] | CATEGORYB | SINGLE | CLEARWATER - MILAN TAP 138KV CKT 1 | 0 | 533036 | CLEARWT4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 95.0994 |  | MIDW | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 MIDW | Tear down and rebuild 73.4% Ownership 28.79 mile HEC-Huntsville 115 kV line and replace CT, wavetrap and relays. | 223 | 240 | 223 | 240 | 21.13 | 9 | 9 |  |  |  |  | 562.5k per mile | 11885625 | 2008-01-01 | [38 empty] | 2015-06-01 | 2015-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T23465518SP | TO->FROM | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | EXP | WERE | MIDW | WEST | REG E-IL | 0 | 533419 | HEC 3 115.00 | 530618 | HUNTSVL3 115.00 | 0 |  | 1 | 18SP | 92 | 92 | 110.1 | 108.6 | 104.2529 | 101.0224 | [7 empty] | CATEGORYB | SINGLE | MINGO - REDWILO3 345.00 345KV CKT 1 | 0 | 531451 | MINGO 7 345.00 | 640325 | REDWILO3 345.00 | 0 |  | 1 | 92.9406 |  | WERE | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 WERE | Tear down and rebuild 26.6% Ownership 28.79 mile HEC-Huntsville 115 kV line and replace CT, wavetrap and relays. | 223 | 240 | 223 | 240 | 7.66 | 36 | 36 |  |  |  |  | 562.5k per mile | 4308750 | 2008-01-01 | [38 empty] | 2015-06-01 | 2015-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T23465518SP | TO->FROM | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | EXP | WERE | MIDW | WEST | REG E-IL | 0 | 533419 | HEC 3 115.00 | 530618 | HUNTSVL3 115.00 | 0 |  | 1 | 18SP | 92 | 92 | 110.1 | 108.6 | 104.2529 | 101.0224 | [7 empty] | CATEGORYB | SINGLE | MINGO - REDWILO3 345.00 345KV CKT 1 | 0 | 531451 | MINGO 7 345.00 | 640325 | REDWILO3 345.00 | 0 |  | 1 | 92.9406 |  | MIDW | HUNTSVILLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 MIDW | Tear down and rebuild 73.4% Ownership 28.79 mile HEC-Huntsville 115 kV line and replace CT, wavetrap and relays. | 223 | 240 | 223 | 240 | 21.13 | 9 | 9 |  |  |  |  | 562.5k per mile | 11885625 | 2008-01-01 | [38 empty] | 2015-06-01 | 2015-06-01
2005-AG2 | 2005-AG2 | [7 empty] | 55948540441559485607913310SP |  | HUGO POWER PLANT 345/138KV TRANSFORMER CKT 1 | U | WFEC | AEPW |  |  | 1 | 521157 | HUGO PP7 345 | 520948 | HUGO PP4 138 | 521189 | HUGO TERTA | 1 | 10SP |  | 315 | [12 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | HUGO POWER PLANT 345/138KV TRANSFORMER CKT 1 | New 345/138 kv Auto | 500 | 500 |  |  | 19 | 24 |  | Y |  |  |  | The 345kv line would go: From Hugo Power Station (55948) to a new 500 MVA 138/345kv autotransformer at the Hugo plant site to PSO Valiant (54037) USE data from GEN-2004-018 | 16000000 | [39 empty] | 2012-07-01 | 2012-07-01
2005-AG2 | 2005-AG2 | [7 empty] | 55948540441559485607913310SP |  | HUGO POWER PLANT - VALLIANT 138KV CKT 1 | U | WFEC | AEPW |  |  | 0 | 55948 | HUGO PP4 138 | 54044 | VALIANT4 138 | 0 |  | 1 | 10SP |  | 315 | [12 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | AEPW | HUGO POWER PLANT - VALLIANT 345 KV AEPW | Vallient 345 KV line terminal | [5 empty] | 24 |  | Y |  |  |  |  | 2500000 | [39 empty] | 2012-07-01 | 2012-07-01
2005-AG2 | 2005-AG2 | [7 empty] | 55948540441559485607913310SP |  | HUGO POWER PLANT - VALLIANT 138KV CKT 1 | U | WFEC | AEPW |  |  | 0 | 55948 | HUGO PP4 138 | 54044 | VALIANT4 138 | 0 |  | 1 | 10SP |  | 315 | [12 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | HUGO POWER PLANT - VALLIANT 345 KV WFEC | New 19 miles 345 KV | 500 | 500 |  |  | 19 | 24 |  | Y |  |  |  | The 345kv line would go: From Hugo Power Station (55948) to a new 500 MVA 138/345kv autotransformer at the Hugo plant site to PSO Valiant (54037) USE data from GEN-2004-018 | 16000000 | [39 empty] | 2012-07-01 | 2012-07-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17153318SP |  | HOXIE 115KV | REL | MIDW |  | REG E-IL |  |  | 530556 | HOXIE 3 115.00 | [5 empty] | 18SP | [8 empty] | 0.91977 | 0.89567 | 0.98271 | 0.9 | 1.05 | CATEGORYB | SINGLE | MINGO (MINGO) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 531451 | MINGO 7 345.00 | 531429 | MINGO 3 115.00 | 531452 | MINGTER1 13.800 | 1 |  |  | SUNC | RULETON 115KV Capacitor | Install Second 12 Mvar cap bank at Ruleton 115kV | [12 empty] | 486000 | 2008-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T495509SH | FROM->TO | HOLCOMB - PLYMELL 115KV CKT 1 | EXP | SUNC | SUNC | SEPC | PIONEER | 0 | 531448 | HOLCOMB3 115.00 | 531393 | PLYMELL3 115.00 | 0 |  | 1 | 09SH | 120 | 143 |  |  | 89.1745 | 102.5171 | [7 empty] | CATEGORYB | SINGLE | FLETCHER - HOLCOMB 115KV CKT 1 | 0 | 531420 | FLETCHR3 115.00 | 531448 | HOLCOMB3 115.00 | 0 |  | 1 | 146.5994 |  | SUNC | HOLCOMB - PLYMELL 115KV CKT 1 | Rebuild Holcomb to Plymell | 185 | 222 |  |  | 11 | 24 | 24 |  | 0.00821 | 0.06016 | 0.00862 |  | 1918400 | 2006-06-01 | [38 empty] | 2009-06-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T5785509SH | FROM->TO | HOLCOMB - PLYMELL 115KV CKT 1 | EXP | SUNC | SUNC | SEPC | PIONEER | 0 | 531448 | HOLCOMB3 115.00 | 531393 | PLYMELL3 115.00 | 0 |  | 1 | 09SH | 120 | 143 |  |  | 87.8998 | 102.4794 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SUNC-05 | 0 | 0 |  | 0 |  | 0 |  |  | 146.5455 |  | SUNC | HOLCOMB - PLYMELL 115KV CKT 1 | Rebuild Holcomb to Plymell | 185 | 222 |  |  | 11 | 24 | 24 |  | 0.00821 | 0.06016 | 0.00862 |  | 1918400 | 2006-06-01 | [38 empty] | 2009-06-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T9505509SP | FROM->TO | HOLCOMB - PLYMELL 115KV CKT 1 | EXP | SUNC | SUNC | SEPC | PIONEER | 0 | 531448 | HOLCOMB3 115.00 | 531393 | PLYMELL3 115.00 | 0 |  | 1 | 09SP | 120 | 143 |  |  | 93.7603 | 111.9416 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SUNC-05 | 0 | 0 |  | 0 |  | 0 |  |  | 160.0765 |  | SUNC | HOLCOMB - PLYMELL 115KV CKT 1 | Rebuild Holcomb to Plymell | 185 | 222 |  |  | 11 | 24 | 24 |  | 0.00821 | 0.06016 | 0.00862 |  | 1918400 | 2006-06-01 | [38 empty] | 2009-06-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T1165509SP | FROM->TO | HOLCOMB - PLYMELL 115KV CKT 1 | EXP | SUNC | SUNC | SEPC | PIONEER | 0 | 531448 | HOLCOMB3 115.00 | 531393 | PLYMELL3 115.00 | 0 |  | 1 | 09SP | 120 | 143 |  |  | 93.6852 | 111.3506 | [7 empty] | CATEGORYB | SINGLE | FLETCHER - HOLCOMB 115KV CKT 1 | 0 | 531420 | FLETCHR3 115.00 | 531448 | HOLCOMB3 115.00 | 0 |  | 1 | 159.2314 |  | SUNC | HOLCOMB - PLYMELL 115KV CKT 1 | Rebuild Holcomb to Plymell | 185 | 222 |  |  | 11 | 24 | 24 |  | 0.00821 | 0.06016 | 0.00862 |  | 1918400 | 2006-06-01 | [38 empty] | 2009-06-01 | 2010-01-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T6295509SP | FROM->TO | HOLCOMB - PLYMELL 115KV CKT 1 | EXP | SUNC | SUNC | SEPC | PIONEER | 0 | 531448 | HOLCOMB3 115.00 | 531393 | PLYMELL3 115.00 | 0 |  | 1 | 09SP | 120 | 143 |  |  | 83.4387 | 107.1634 | [7 empty] | CATEGORYB | SINGLE | HOLCOMB (HOLCOMB) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 531448 | HOLCOMB3 115.00 | 531449 | HOLCOMB7 345.00 | 531450 | HOLCTER1 13.800 | 1 | 153.2437 |  | SUNC | HOLCOMB - PLYMELL 115KV CKT 1 | Rebuild Holcomb to Plymell | 185 | 222 |  |  | 11 | 24 | 24 |  | 0.00821 | 0.06016 | 0.00862 |  | 1918400 | 2006-06-01 | [38 empty] | 2009-06-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 2 | 2008AGP1AFS31T1561210SP | FROM->TO | HOLCOMB - PLYMELL 115KV CKT 1 | EXP | SUNC | SUNC | SEPC | PIONEER | 0 | 531448 | HOLCOMB3 115.00 | 531393 | PLYMELL3 115.00 | 0 |  | 1 | 10SP | 120 | 143 |  |  | 96.7055 | 105.3578 | [7 empty] | CATEGORYB | SINGLE | FLETCHER - HOLCOMB 115KV CKT 1 | 0 | 531420 | FLETCHR3 115.00 | 531448 | HOLCOMB3 115.00 | 0 |  | 1 | 150.6617 |  | SUNC | HOLCOMB - PLYMELL 115KV CKT 1 | Rebuild Holcomb to Plymell | 185 | 222 |  |  | 11 | 24 | 24 |  | 0.00821 | 0.06016 | 0.00862 |  | 1918400 | 2006-06-01 | [38 empty] | 2009-06-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 2 | 2008AGP1AFS31T14143210SP | FROM->TO | HOLCOMB - PLYMELL 115KV CKT 1 | EXP | SUNC | SUNC | SEPC | PIONEER | 0 | 531448 | HOLCOMB3 115.00 | 531393 | PLYMELL3 115.00 | 0 |  | 1 | 10SP | 120 | 143 |  |  | 96.992 | 103.7633 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SUNC-05 | 0 | 0 |  | 0 |  | 0 |  |  | 148.3815 |  | SUNC | HOLCOMB - PLYMELL 115KV CKT 1 | Rebuild Holcomb to Plymell | 185 | 222 |  |  | 11 | 24 | 24 |  | 0.00821 | 0.06016 | 0.00862 |  | 1918400 | 2006-06-01 | [38 empty] | 2009-06-01 | 2010-01-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T7495510SP | FROM->TO | HOLCOMB - PLYMELL 115KV CKT 1 | EXP | SUNC | SUNC | SEPC | PIONEER | 0 | 531448 | HOLCOMB3 115.00 | 531393 | PLYMELL3 115.00 | 0 |  | 1 | 10SP | 120 | 143 |  |  | 83.6461 | 100.3231 | [7 empty] | CATEGORYB | SINGLE | HOLCOMB (HOLCOMB) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 531448 | HOLCOMB3 115.00 | 531449 | HOLCOMB7 345.00 | 531450 | HOLCTER1 13.800 | 1 | 143.462 |  | SUNC | HOLCOMB - PLYMELL 115KV CKT 1 | Rebuild Holcomb to Plymell | 185 | 222 |  |  | 11 | 24 | 24 |  | 0.00821 | 0.06016 | 0.00862 |  | 1918400 | 2006-06-01 | [38 empty] | 2009-06-01 | 2010-01-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T3984209SH | FROM->TO | HILLTOP - ST JOE 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 338110 | 5HILLTOP 161.00 | 338108 | 5ST_JOE 161.00 | 0 |  | 1 | 09SH | 167 | 167 |  | 108.2 | 107.0022 | 103.5409 | [7 empty] | CATEGORYB | SINGLE | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 172.9133 |  | EES | HILLTOP - ST JOE 161KV CKT 1 | Rebuild Transmission Line 4.4 miles | [12 empty] | 3170000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T3174209SH | FROM->TO | HILLTOP - ST JOE 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 338110 | 5HILLTOP 161.00 | 338108 | 5ST_JOE 161.00 | 0 |  | 1 | 09SH | 167 | 167 |  | 107 | 105.8148 | 102.3243 | [7 empty] | CATEGORYB | SINGLE | BULL SHOALS HES - FLIPPIN 161KV CKT 1 | 0 | 338122 | 5FLIPN 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 170.8816 |  | EES | HILLTOP - ST JOE 161KV CKT 1 | Rebuild Transmission Line 4.4 miles | [12 empty] | 3170000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T6634209SP | FROM->TO | HILLTOP - ST JOE 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 338110 | 5HILLTOP 161.00 | 338108 | 5ST_JOE 161.00 | 0 |  | 1 | 09SP | 167 | 167 | 105.0 | 112.3 | 110.2056 | 106.5133 | [7 empty] | CATEGORYB | SINGLE | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 177.8772 |  | EES | HILLTOP - ST JOE 161KV CKT 1 | Rebuild Transmission Line 4.4 miles | [12 empty] | 3170000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T5264209SP | FROM->TO | HILLTOP - ST JOE 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 338110 | 5HILLTOP 161.00 | 338108 | 5ST_JOE 161.00 | 0 |  | 1 | 09SP | 167 | 167 | 103.5 | 110.9 | 108.7571 | 105.0717 | [7 empty] | CATEGORYB | SINGLE | BULL SHOALS HES - FLIPPIN 161KV CKT 1 | 0 | 338122 | 5FLIPN 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 175.4697 |  | EES | HILLTOP - ST JOE 161KV CKT 1 | Rebuild Transmission Line 4.4 miles | [12 empty] | 3170000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T5244209SP | FROM->TO | HILLTOP - ST JOE 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 338110 | 5HILLTOP 161.00 | 338108 | 5ST_JOE 161.00 | 0 |  | 1 | 09SP | 167 | 167 | 100.1 | 107.6 | 105.3524 | 101.6946 | [7 empty] | CATEGORYB | SINGLE | FLIPPIN - SUMMIT 161KV CKT 1 | 0 | 338121 | 5SUMMIT 161.00 | 338122 | 5FLIPN 161.00 | 0 |  | 1 | 169.83 |  | EES | HILLTOP - ST JOE 161KV CKT 1 | Rebuild Transmission Line 4.4 miles | [12 empty] | 3170000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T3814209WP | FROM->TO | HILLTOP - ST JOE 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 338110 | 5HILLTOP 161.00 | 338108 | 5ST_JOE 161.00 | 0 |  | 1 | 09WP | 167 | 167 |  | 107.6 | 106.5481 | 107.1091 | [7 empty] | CATEGORYB | SINGLE | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 178.8722 |  | EES | HILLTOP - ST JOE 161KV CKT 1 | Rebuild Transmission Line 4.4 miles | [12 empty] | 3170000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T3094209WP | FROM->TO | HILLTOP - ST JOE 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 338110 | 5HILLTOP 161.00 | 338108 | 5ST_JOE 161.00 | 0 |  | 1 | 09WP | 167 | 167 |  | 106.5 | 105.4435 | 106.0031 | [7 empty] | CATEGORYB | SINGLE | BULL SHOALS HES - FLIPPIN 161KV CKT 1 | 0 | 338122 | 5FLIPN 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 177.0252 |  | EES | HILLTOP - ST JOE 161KV CKT 1 | Rebuild Transmission Line 4.4 miles | [12 empty] | 3170000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T3074209WP | FROM->TO | HILLTOP - ST JOE 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 338110 | 5HILLTOP 161.00 | 338108 | 5ST_JOE 161.00 | 0 |  | 1 | 09WP | 167 | 167 |  | 103.9 | 102.9003 | 103.4582 | [7 empty] | CATEGORYB | SINGLE | FLIPPIN - SUMMIT 161KV CKT 1 | 0 | 338121 | 5SUMMIT 161.00 | 338122 | 5FLIPN 161.00 | 0 |  | 1 | 172.7752 |  | EES | HILLTOP - ST JOE 161KV CKT 1 | Rebuild Transmission Line 4.4 miles | [12 empty] | 3170000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T9872210SP | FROM->TO | HILLTOP - ST JOE 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 338110 | 5HILLTOP 161.00 | 338108 | 5ST_JOE 161.00 | 0 |  | 1 | 10SP | 167 | 167 | 110.8 | 123.7 | 124.2095 | 121.5093 | [7 empty] | CATEGORYB | SINGLE | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 202.9205 |  | EES | HILLTOP - ST JOE 161KV CKT 1 | Rebuild Transmission Line 4.4 miles | [12 empty] | 3170000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T7482210SP | FROM->TO | HILLTOP - ST JOE 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 338110 | 5HILLTOP 161.00 | 338108 | 5ST_JOE 161.00 | 0 |  | 1 | 10SP | 167 | 167 | 109.3 | 122.3 | 122.7321 | 120.0303 | [7 empty] | CATEGORYB | SINGLE | BULL SHOALS HES - FLIPPIN 161KV CKT 1 | 0 | 338122 | 5FLIPN 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 200.4506 |  | EES | HILLTOP - ST JOE 161KV CKT 1 | Rebuild Transmission Line 4.4 miles | [12 empty] | 3170000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T7462210SP | FROM->TO | HILLTOP - ST JOE 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 338110 | 5HILLTOP 161.00 | 338108 | 5ST_JOE 161.00 | 0 |  | 1 | 10SP | 167 | 167 | 105.8 | 118.8 | 119.2848 | 116.6086 | [7 empty] | CATEGORYB | SINGLE | FLIPPIN - SUMMIT 161KV CKT 1 | 0 | 338121 | 5SUMMIT 161.00 | 338122 | 5FLIPN 161.00 | 0 |  | 1 | 194.7364 |  | EES | HILLTOP - ST JOE 161KV CKT 1 | Rebuild Transmission Line 4.4 miles | [12 empty] | 3170000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T6084210WP | FROM->TO | HILLTOP - ST JOE 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 338110 | 5HILLTOP 161.00 | 338108 | 5ST_JOE 161.00 | 0 |  | 1 | 10WP | 167 | 167 | 109.4 | 121.9 | 120.8515 | 117.7101 | [7 empty] | CATEGORYB | SINGLE | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 196.5759 |  | EES | HILLTOP - ST JOE 161KV CKT 1 | Rebuild Transmission Line 4.4 miles | [12 empty] | 3170000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T4624210WP | FROM->TO | HILLTOP - ST JOE 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 338110 | 5HILLTOP 161.00 | 338108 | 5ST_JOE 161.00 | 0 |  | 1 | 10WP | 167 | 167 | 108.3 | 120.8 | 119.7418 | 116.5991 | [7 empty] | CATEGORYB | SINGLE | BULL SHOALS HES - FLIPPIN 161KV CKT 1 | 0 | 338122 | 5FLIPN 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 194.7205 |  | EES | HILLTOP - ST JOE 161KV CKT 1 | Rebuild Transmission Line 4.4 miles | [12 empty] | 3170000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T4574210WP | FROM->TO | HILLTOP - ST JOE 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 338110 | 5HILLTOP 161.00 | 338108 | 5ST_JOE 161.00 | 0 |  | 1 | 10WP | 167 | 167 | 105.6 | 118.2 | 117.163 | 114.0165 | [7 empty] | CATEGORYB | SINGLE | FLIPPIN - SUMMIT 161KV CKT 1 | 0 | 338121 | 5SUMMIT 161.00 | 338122 | 5FLIPN 161.00 | 0 |  | 1 | 190.4076 |  | EES | HILLTOP - ST JOE 161KV CKT 1 | Rebuild Transmission Line 4.4 miles | [12 empty] | 3170000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T15862213SP | FROM->TO | HILLTOP - ST JOE 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 338110 | 5HILLTOP 161.00 | 338108 | 5ST_JOE 161.00 | 0 |  | 1 | 13SP | 167 | 167 | 117.1 | 129.9 | 130.1451 | 126.3471 | [7 empty] | CATEGORYB | SINGLE | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 210.9997 |  | EES | HILLTOP - ST JOE 161KV CKT 1 | Rebuild Transmission Line 4.4 miles | [12 empty] | 3170000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T11692213SP | FROM->TO | HILLTOP - ST JOE 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 338110 | 5HILLTOP 161.00 | 338108 | 5ST_JOE 161.00 | 0 |  | 1 | 13SP | 167 | 167 | 115.5 | 128.3 | 128.5859 | 124.7717 | [7 empty] | CATEGORYB | SINGLE | BULL SHOALS HES - FLIPPIN 161KV CKT 1 | 0 | 338122 | 5FLIPN 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 208.3687 |  | EES | HILLTOP - ST JOE 161KV CKT 1 | Rebuild Transmission Line 4.4 miles | [12 empty] | 3170000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T11662213SP | FROM->TO | HILLTOP - ST JOE 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 338110 | 5HILLTOP 161.00 | 338108 | 5ST_JOE 161.00 | 0 |  | 1 | 13SP | 167 | 167 | 111.6 | 124.4 | 124.6733 | 120.8448 | [7 empty] | CATEGORYB | SINGLE | FLIPPIN - SUMMIT 161KV CKT 1 | 0 | 338121 | 5SUMMIT 161.00 | 338122 | 5FLIPN 161.00 | 0 |  | 1 | 201.8108 |  | EES | HILLTOP - ST JOE 161KV CKT 1 | Rebuild Transmission Line 4.4 miles | [12 empty] | 3170000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T5644213WP | FROM->TO | HILLTOP - ST JOE 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 338110 | 5HILLTOP 161.00 | 338108 | 5ST_JOE 161.00 | 0 |  | 1 | 13WP | 167 | 167 | 107.1 | 118.8 | 117.6175 | 116.0096 | [7 empty] | CATEGORYB | SINGLE | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 193.736 |  | EES | HILLTOP - ST JOE 161KV CKT 1 | Rebuild Transmission Line 4.4 miles | [12 empty] | 3170000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T3924213WP | FROM->TO | HILLTOP - ST JOE 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 338110 | 5HILLTOP 161.00 | 338108 | 5ST_JOE 161.00 | 0 |  | 1 | 13WP | 167 | 167 | 106.0 | 117.6 | 116.4632 | 114.8416 | [7 empty] | CATEGORYB | SINGLE | BULL SHOALS HES - FLIPPIN 161KV CKT 1 | 0 | 338122 | 5FLIPN 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 191.7855 |  | EES | HILLTOP - ST JOE 161KV CKT 1 | Rebuild Transmission Line 4.4 miles | [12 empty] | 3170000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T3894213WP | FROM->TO | HILLTOP - ST JOE 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 338110 | 5HILLTOP 161.00 | 338108 | 5ST_JOE 161.00 | 0 |  | 1 | 13WP | 167 | 167 | 102.9 | 114.7 | 113.5465 | 111.9074 | [7 empty] | CATEGORYB | SINGLE | FLIPPIN - SUMMIT 161KV CKT 1 | 0 | 338121 | 5SUMMIT 161.00 | 338122 | 5FLIPN 161.00 | 0 |  | 1 | 186.8854 |  | EES | HILLTOP - ST JOE 161KV CKT 1 | Rebuild Transmission Line 4.4 miles | [12 empty] | 3170000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T26762218SP | FROM->TO | HILLTOP - ST JOE 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 338110 | 5HILLTOP 161.00 | 338108 | 5ST_JOE 161.00 | 0 |  | 1 | 18SP | 167 | 167 |  | 111.1 | 111.6431 | 106.6205 | [7 empty] | CATEGORYB | SINGLE | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 178.0562 |  | EES | HILLTOP - ST JOE 161KV CKT 1 | Rebuild Transmission Line 4.4 miles | [12 empty] | 3170000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T20602218SP | FROM->TO | HILLTOP - ST JOE 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 338110 | 5HILLTOP 161.00 | 338108 | 5ST_JOE 161.00 | 0 |  | 1 | 18SP | 167 | 167 |  | 109.7 | 110.1419 | 105.1228 | [7 empty] | CATEGORYB | SINGLE | BULL SHOALS HES - FLIPPIN 161KV CKT 1 | 0 | 338122 | 5FLIPN 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 175.5551 |  | EES | HILLTOP - ST JOE 161KV CKT 1 | Rebuild Transmission Line 4.4 miles | [12 empty] | 3170000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T20582218SP | FROM->TO | HILLTOP - ST JOE 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 338110 | 5HILLTOP 161.00 | 338108 | 5ST_JOE 161.00 | 0 |  | 1 | 18SP | 167 | 167 |  | 105.6 | 106.1467 | 101.143 | [7 empty] | CATEGORYB | SINGLE | FLIPPIN - SUMMIT 161KV CKT 1 | 0 | 338121 | 5SUMMIT 161.00 | 338122 | 5FLIPN 161.00 | 0 |  | 1 | 168.9088 |  | EES | HILLTOP - ST JOE 161KV CKT 1 | Rebuild Transmission Line 4.4 miles | [12 empty] | 3170000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T12692213SP | TO->FROM | HERGETT - JONESBORO 161KV CKT 1 | S | EES | SWPA | EES_ARK | EMINTH | 0 | 338170 | 5JONES 161.00 | 505420 | HERGETT5 161.00 | 0 |  | 1 | 13SP | 148 | 148 | 162.7 | 168.5 | 168.1113 | 168.4818 | [7 empty] | CATEGORYB | SINGLE | HARISBURG TAP - MARKED TREE 161KV CKT 1 | 0 | 338165 | 5MTREE 161.00 | 338167 | 5HRSBRG* 161.00 | 0 |  | 1 | 249.3531 |  | SWPA | HERGETT - JONESBORO 161KV CKT 1 SWPA | Increase the CT ratio to 1200/5. This would involve changing taps on the CT, adjusting the scaling on a panel meter, and changing relay settings. | [11 empty] | 505420-338170 | 5000 | 2009-03-06 | [38 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T12692213SP | TO->FROM | HERGETT - JONESBORO 161KV CKT 1 | S | EES | SWPA | EES_ARK | EMINTH | 0 | 338170 | 5JONES 161.00 | 505420 | HERGETT5 161.00 | 0 |  | 1 | 13SP | 148 | 148 | 162.7 | 168.5 | 168.1113 | 168.4818 | [7 empty] | CATEGORYB | SINGLE | HARISBURG TAP - MARKED TREE 161KV CKT 1 | 0 | 338165 | 5MTREE 161.00 | 338167 | 5HRSBRG* 161.00 | 0 |  | 1 | 249.3531 |  | EES | HERGETT - JONESBORO 161KV CKT 1 EES | Indeterminate | [52 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T12712213SP | TO->FROM | HERGETT - JONESBORO 161KV CKT 1 | S | EES | SWPA | EES_ARK | EMINTH | 0 | 338170 | 5JONES 161.00 | 505420 | HERGETT5 161.00 | 0 |  | 1 | 13SP | 148 | 148 | 156.9 | 162.6 | 162.1698 | 162.5284 | [7 empty] | CATEGORYB | SINGLE | HARISBURG TAP - TRUMANN 161KV CKT 1 | 0 | 338167 | 5HRSBRG* 161.00 | 338169 | 5TRUMAN 161.00 | 0 |  | 1 | 240.542 |  | SWPA | HERGETT - JONESBORO 161KV CKT 1 SWPA | Increase the CT ratio to 1200/5. This would involve changing taps on the CT, adjusting the scaling on a panel meter, and changing relay settings. | [11 empty] | 505420-338170 | 5000 | 2009-03-06 | [38 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T12712213SP | TO->FROM | HERGETT - JONESBORO 161KV CKT 1 | S | EES | SWPA | EES_ARK | EMINTH | 0 | 338170 | 5JONES 161.00 | 505420 | HERGETT5 161.00 | 0 |  | 1 | 13SP | 148 | 148 | 156.9 | 162.6 | 162.1698 | 162.5284 | [7 empty] | CATEGORYB | SINGLE | HARISBURG TAP - TRUMANN 161KV CKT 1 | 0 | 338167 | 5HRSBRG* 161.00 | 338169 | 5TRUMAN 161.00 | 0 |  | 1 | 240.542 |  | EES | HERGETT - JONESBORO 161KV CKT 1 EES | Indeterminate | [52 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T12732213SP | TO->FROM | HERGETT - JONESBORO 161KV CKT 1 | S | EES | SWPA | EES_ARK | EMINTH | 0 | 338170 | 5JONES 161.00 | 505420 | HERGETT5 161.00 | 0 |  | 1 | 13SP | 148 | 148 | 149.9 | 155.6 | 155.1979 | 155.546 | [7 empty] | CATEGORYB | SINGLE | TRUMANN - TRUMANN WEST AECC 161KV CKT 1 | 0 | 338169 | 5TRUMAN 161.00 | 338707 | 5TRUM-W# 161.00 | 0 |  | 1 | 230.2081 |  | SWPA | HERGETT - JONESBORO 161KV CKT 1 SWPA | Increase the CT ratio to 1200/5. This would involve changing taps on the CT, adjusting the scaling on a panel meter, and changing relay settings. | [11 empty] | 505420-338170 | 5000 | 2009-03-06 | [38 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T12732213SP | TO->FROM | HERGETT - JONESBORO 161KV CKT 1 | S | EES | SWPA | EES_ARK | EMINTH | 0 | 338170 | 5JONES 161.00 | 505420 | HERGETT5 161.00 | 0 |  | 1 | 13SP | 148 | 148 | 149.9 | 155.6 | 155.1979 | 155.546 | [7 empty] | CATEGORYB | SINGLE | TRUMANN - TRUMANN WEST AECC 161KV CKT 1 | 0 | 338169 | 5TRUMAN 161.00 | 338707 | 5TRUM-W# 161.00 | 0 |  | 1 | 230.2081 |  | EES | HERGETT - JONESBORO 161KV CKT 1 EES | Indeterminate | [52 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T12802213SP | TO->FROM | HERGETT - JONESBORO 161KV CKT 1 | S | EES | SWPA | EES_ARK | EMINTH | 0 | 338170 | 5JONES 161.00 | 505420 | HERGETT5 161.00 | 0 |  | 1 | 13SP | 148 | 148 | 113.3 | 113.9 | 113.7742 | 114.1461 | [7 empty] | CATEGORYB | SINGLE | JONESBORO - JONESBORO AECC 161KV CKT 1 | 0 | 338170 | 5JONES 161.00 | 338702 | 5JONE-W# 161.00 | 0 |  | 1 | 168.9362 |  | EES | HERGETT - JONESBORO 161KV CKT 1 EES | Indeterminate | [52 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T12802213SP | TO->FROM | HERGETT - JONESBORO 161KV CKT 1 | S | EES | SWPA | EES_ARK | EMINTH | 0 | 338170 | 5JONES 161.00 | 505420 | HERGETT5 161.00 | 0 |  | 1 | 13SP | 148 | 148 | 113.3 | 113.9 | 113.7742 | 114.1461 | [7 empty] | CATEGORYB | SINGLE | JONESBORO - JONESBORO AECC 161KV CKT 1 | 0 | 338170 | 5JONES 161.00 | 338702 | 5JONE-W# 161.00 | 0 |  | 1 | 168.9362 |  | SWPA | HERGETT - JONESBORO 161KV CKT 1 SWPA | Increase the CT ratio to 1200/5. This would involve changing taps on the CT, adjusting the scaling on a panel meter, and changing relay settings. | [11 empty] | 505420-338170 | 5000 | 2009-03-06 | [38 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T112213SP | TO->FROM | HERGETT - JONESBORO 161KV CKT 1 | S | EES | SWPA | EES_ARK | EMINTH | 0 | 338170 | 5JONES 161.00 | 505420 | HERGETT5 161.00 | 0 |  | 1 | 13SP | 148 | 148 | 107.5 | 108 | 107.9004 | 108.2683 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | 160.2371 |  | SWPA | HERGETT - JONESBORO 161KV CKT 1 SWPA | Increase the CT ratio to 1200/5. This would involve changing taps on the CT, adjusting the scaling on a panel meter, and changing relay settings. | [11 empty] | 505420-338170 | 5000 | 2009-03-06 | [38 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T112213SP | TO->FROM | HERGETT - JONESBORO 161KV CKT 1 | S | EES | SWPA | EES_ARK | EMINTH | 0 | 338170 | 5JONES 161.00 | 505420 | HERGETT5 161.00 | 0 |  | 1 | 13SP | 148 | 148 | 107.5 | 108 | 107.9004 | 108.2683 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | 160.2371 |  | EES | HERGETT - JONESBORO 161KV CKT 1 EES | Indeterminate | [52 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T4542213WP | TO->FROM | HERGETT - JONESBORO 161KV CKT 1 | S | EES | SWPA | EES_ARK | EMINTH | 0 | 338170 | 5JONES 161.00 | 505420 | HERGETT5 161.00 | 0 |  | 1 | 13WP | 148 | 148 | 119.1 | 123.7 | 123.3056 | 123.7047 | [7 empty] | CATEGORYB | SINGLE | HARISBURG TAP - MARKED TREE 161KV CKT 1 | 0 | 338165 | 5MTREE 161.00 | 338167 | 5HRSBRG* 161.00 | 0 |  | 1 | 183.083 |  | EES | HERGETT - JONESBORO 161KV CKT 1 EES | Indeterminate | [52 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T4542213WP | TO->FROM | HERGETT - JONESBORO 161KV CKT 1 | S | EES | SWPA | EES_ARK | EMINTH | 0 | 338170 | 5JONES 161.00 | 505420 | HERGETT5 161.00 | 0 |  | 1 | 13WP | 148 | 148 | 119.1 | 123.7 | 123.3056 | 123.7047 | [7 empty] | CATEGORYB | SINGLE | HARISBURG TAP - MARKED TREE 161KV CKT 1 | 0 | 338165 | 5MTREE 161.00 | 338167 | 5HRSBRG* 161.00 | 0 |  | 1 | 183.083 |  | SWPA | HERGETT - JONESBORO 161KV CKT 1 SWPA | Increase the CT ratio to 1200/5. This would involve changing taps on the CT, adjusting the scaling on a panel meter, and changing relay settings. | [11 empty] | 505420-338170 | 5000 | 2009-03-06 | [38 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T4552213WP | TO->FROM | HERGETT - JONESBORO 161KV CKT 1 | S | EES | SWPA | EES_ARK | EMINTH | 0 | 338170 | 5JONES 161.00 | 505420 | HERGETT5 161.00 | 0 |  | 1 | 13WP | 148 | 148 | 114.8 | 119.4 | 119.0138 | 119.4008 | [7 empty] | CATEGORYB | SINGLE | HARISBURG TAP - TRUMANN 161KV CKT 1 | 0 | 338167 | 5HRSBRG* 161.00 | 338169 | 5TRUMAN 161.00 | 0 |  | 1 | 176.7132 |  | SWPA | HERGETT - JONESBORO 161KV CKT 1 SWPA | Increase the CT ratio to 1200/5. This would involve changing taps on the CT, adjusting the scaling on a panel meter, and changing relay settings. | [11 empty] | 505420-338170 | 5000 | 2009-03-06 | [38 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T4552213WP | TO->FROM | HERGETT - JONESBORO 161KV CKT 1 | S | EES | SWPA | EES_ARK | EMINTH | 0 | 338170 | 5JONES 161.00 | 505420 | HERGETT5 161.00 | 0 |  | 1 | 13WP | 148 | 148 | 114.8 | 119.4 | 119.0138 | 119.4008 | [7 empty] | CATEGORYB | SINGLE | HARISBURG TAP - TRUMANN 161KV CKT 1 | 0 | 338167 | 5HRSBRG* 161.00 | 338169 | 5TRUMAN 161.00 | 0 |  | 1 | 176.7132 |  | EES | HERGETT - JONESBORO 161KV CKT 1 EES | Indeterminate | [52 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T4562213WP | TO->FROM | HERGETT - JONESBORO 161KV CKT 1 | S | EES | SWPA | EES_ARK | EMINTH | 0 | 338170 | 5JONES 161.00 | 505420 | HERGETT5 161.00 | 0 |  | 1 | 13WP | 148 | 148 | 109.6 | 114.1 | 113.7179 | 114.0509 | [7 empty] | CATEGORYB | SINGLE | TRUMANN - TRUMANN WEST AECC 161KV CKT 1 | 0 | 338169 | 5TRUMAN 161.00 | 338707 | 5TRUM-W# 161.00 | 0 |  | 1 | 168.7953 |  | SWPA | HERGETT - JONESBORO 161KV CKT 1 SWPA | Increase the CT ratio to 1200/5. This would involve changing taps on the CT, adjusting the scaling on a panel meter, and changing relay settings. | [11 empty] | 505420-338170 | 5000 | 2009-03-06 | [38 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T4562213WP | TO->FROM | HERGETT - JONESBORO 161KV CKT 1 | S | EES | SWPA | EES_ARK | EMINTH | 0 | 338170 | 5JONES 161.00 | 505420 | HERGETT5 161.00 | 0 |  | 1 | 13WP | 148 | 148 | 109.6 | 114.1 | 113.7179 | 114.0509 | [7 empty] | CATEGORYB | SINGLE | TRUMANN - TRUMANN WEST AECC 161KV CKT 1 | 0 | 338169 | 5TRUMAN 161.00 | 338707 | 5TRUM-W# 161.00 | 0 |  | 1 | 168.7953 |  | EES | HERGETT - JONESBORO 161KV CKT 1 EES | Indeterminate | [52 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T21842218SP | TO->FROM | HERGETT - JONESBORO 161KV CKT 1 | S | EES | SWPA | EES_ARK | EMINTH | 0 | 338170 | 5JONES 161.00 | 505420 | HERGETT5 161.00 | 0 |  | 1 | 18SP | 148 | 148 | 186.6 | 193.9 | 193.3399 | 193.7337 | [7 empty] | CATEGORYB | SINGLE | HARISBURG TAP - MARKED TREE 161KV CKT 1 | 0 | 338165 | 5MTREE 161.00 | 338167 | 5HRSBRG* 161.00 | 0 |  | 1 | 286.7259 |  | EES | HERGETT - JONESBORO 161KV CKT 1 EES | Indeterminate | [52 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T21842218SP | TO->FROM | HERGETT - JONESBORO 161KV CKT 1 | S | EES | SWPA | EES_ARK | EMINTH | 0 | 338170 | 5JONES 161.00 | 505420 | HERGETT5 161.00 | 0 |  | 1 | 18SP | 148 | 148 | 186.6 | 193.9 | 193.3399 | 193.7337 | [7 empty] | CATEGORYB | SINGLE | HARISBURG TAP - MARKED TREE 161KV CKT 1 | 0 | 338165 | 5MTREE 161.00 | 338167 | 5HRSBRG* 161.00 | 0 |  | 1 | 286.7259 |  | SWPA | HERGETT - JONESBORO 161KV CKT 1 SWPA | Increase the CT ratio to 1200/5. This would involve changing taps on the CT, adjusting the scaling on a panel meter, and changing relay settings. | [11 empty] | 505420-338170 | 5000 | 2009-03-06 | [38 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T21872218SP | TO->FROM | HERGETT - JONESBORO 161KV CKT 1 | S | EES | SWPA | EES_ARK | EMINTH | 0 | 338170 | 5JONES 161.00 | 505420 | HERGETT5 161.00 | 0 |  | 1 | 18SP | 148 | 148 | 180.0 | 187.2 | 186.5947 | 186.9646 | [7 empty] | CATEGORYB | SINGLE | HARISBURG TAP - TRUMANN 161KV CKT 1 | 0 | 338167 | 5HRSBRG* 161.00 | 338169 | 5TRUMAN 161.00 | 0 |  | 1 | 276.7076 |  | EES | HERGETT - JONESBORO 161KV CKT 1 EES | Indeterminate | [52 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T21872218SP | TO->FROM | HERGETT - JONESBORO 161KV CKT 1 | S | EES | SWPA | EES_ARK | EMINTH | 0 | 338170 | 5JONES 161.00 | 505420 | HERGETT5 161.00 | 0 |  | 1 | 18SP | 148 | 148 | 180.0 | 187.2 | 186.5947 | 186.9646 | [7 empty] | CATEGORYB | SINGLE | HARISBURG TAP - TRUMANN 161KV CKT 1 | 0 | 338167 | 5HRSBRG* 161.00 | 338169 | 5TRUMAN 161.00 | 0 |  | 1 | 276.7076 |  | SWPA | HERGETT - JONESBORO 161KV CKT 1 SWPA | Increase the CT ratio to 1200/5. This would involve changing taps on the CT, adjusting the scaling on a panel meter, and changing relay settings. | [11 empty] | 505420-338170 | 5000 | 2009-03-06 | [38 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T21902218SP | TO->FROM | HERGETT - JONESBORO 161KV CKT 1 | S | EES | SWPA | EES_ARK | EMINTH | 0 | 338170 | 5JONES 161.00 | 505420 | HERGETT5 161.00 | 0 |  | 1 | 18SP | 148 | 148 | 171.9 | 178.8 | 178.256 | 178.5888 | [7 empty] | CATEGORYB | SINGLE | TRUMANN - TRUMANN WEST AECC 161KV CKT 1 | 0 | 338169 | 5TRUMAN 161.00 | 338707 | 5TRUM-W# 161.00 | 0 |  | 1 | 264.3114 |  | EES | HERGETT - JONESBORO 161KV CKT 1 EES | Indeterminate | [52 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T21902218SP | TO->FROM | HERGETT - JONESBORO 161KV CKT 1 | S | EES | SWPA | EES_ARK | EMINTH | 0 | 338170 | 5JONES 161.00 | 505420 | HERGETT5 161.00 | 0 |  | 1 | 18SP | 148 | 148 | 171.9 | 178.8 | 178.256 | 178.5888 | [7 empty] | CATEGORYB | SINGLE | TRUMANN - TRUMANN WEST AECC 161KV CKT 1 | 0 | 338169 | 5TRUMAN 161.00 | 338707 | 5TRUM-W# 161.00 | 0 |  | 1 | 264.3114 |  | SWPA | HERGETT - JONESBORO 161KV CKT 1 SWPA | Increase the CT ratio to 1200/5. This would involve changing taps on the CT, adjusting the scaling on a panel meter, and changing relay settings. | [11 empty] | 505420-338170 | 5000 | 2009-03-06 | [38 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T22042218SP | TO->FROM | HERGETT - JONESBORO 161KV CKT 1 | S | EES | SWPA | EES_ARK | EMINTH | 0 | 338170 | 5JONES 161.00 | 505420 | HERGETT5 161.00 | 0 |  | 1 | 18SP | 148 | 148 | 124.2 | 125.1 | 124.9536 | 125.3916 | [7 empty] | CATEGORYB | SINGLE | JONESBORO - JONESBORO AECC 161KV CKT 1 | 0 | 338170 | 5JONES 161.00 | 338702 | 5JONE-W# 161.00 | 0 |  | 1 | 185.5796 |  | EES | HERGETT - JONESBORO 161KV CKT 1 EES | Indeterminate | [52 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T22042218SP | TO->FROM | HERGETT - JONESBORO 161KV CKT 1 | S | EES | SWPA | EES_ARK | EMINTH | 0 | 338170 | 5JONES 161.00 | 505420 | HERGETT5 161.00 | 0 |  | 1 | 18SP | 148 | 148 | 124.2 | 125.1 | 124.9536 | 125.3916 | [7 empty] | CATEGORYB | SINGLE | JONESBORO - JONESBORO AECC 161KV CKT 1 | 0 | 338170 | 5JONES 161.00 | 338702 | 5JONE-W# 161.00 | 0 |  | 1 | 185.5796 |  | SWPA | HERGETT - JONESBORO 161KV CKT 1 SWPA | Increase the CT ratio to 1200/5. This would involve changing taps on the CT, adjusting the scaling on a panel meter, and changing relay settings. | [11 empty] | 505420-338170 | 5000 | 2009-03-06 | [38 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T352218SP | TO->FROM | HERGETT - JONESBORO 161KV CKT 1 | S | EES | SWPA | EES_ARK | EMINTH | 0 | 338170 | 5JONES 161.00 | 505420 | HERGETT5 161.00 | 0 |  | 1 | 18SP | 148 | 148 | 117.5 | 118.4 | 118.2348 | 118.6689 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | 175.63 |  | SWPA | HERGETT - JONESBORO 161KV CKT 1 SWPA | Increase the CT ratio to 1200/5. This would involve changing taps on the CT, adjusting the scaling on a panel meter, and changing relay settings. | [11 empty] | 505420-338170 | 5000 | 2009-03-06 | [38 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T352218SP | TO->FROM | HERGETT - JONESBORO 161KV CKT 1 | S | EES | SWPA | EES_ARK | EMINTH | 0 | 338170 | 5JONES 161.00 | 505420 | HERGETT5 161.00 | 0 |  | 1 | 18SP | 148 | 148 | 117.5 | 118.4 | 118.2348 | 118.6689 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | 175.63 |  | EES | HERGETT - JONESBORO 161KV CKT 1 EES | Indeterminate | [52 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 1 | 2008AGP1AFS31T4631118SP | TO->FROM | HAYS PLANT - SOUTH HAYS 115KV CKT 1 | S | MIDW | MIDW | REG E-IL | REG E-IL | 0 | 530553 | S HAYS 3 115.00 | 530562 | HAYS 3 115.00 | 0 |  | 1 | 18SP | 80 | 88 |  |  | 97.506 | 101.2112 | [7 empty] | CATEGORYB | SINGLE | KNOLL 230 230/115KV TRANSFORMER CKT 1 | 0 | 530558 | KNOLL 6 230.00 | 530561 | KNOLL 3 115.00 | 0 |  | 1 | 89.0659 |  | MIDW | HAYS PLANT - SOUTH HAYS 115KV CKT 1 | Reconductor line | 133 | 147 |  |  | 3.25 | 18 | 18 |  | 0.0053761 | 0.018978 | 0.0023048 | 562.5k per mile | 1828125 | 2008-01-01 | [38 empty] | 2018-06-01 | 2014-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 1 | 2008AGP1AFS31T4631118SP | TO->FROM | HAYS PLANT - SOUTH HAYS 115KV CKT 1 | S | MIDW | MIDW | REG E-IL | REG E-IL | 0 | 530553 | S HAYS 3 115.00 | 530562 | HAYS 3 115.00 | 0 |  | 1 | 18SP | 80 | 88 |  |  | 97.506 | 101.2112 | [7 empty] | CATEGORYB | SINGLE | KNOLL 230 230/115KV TRANSFORMER CKT 1 | 0 | 530558 | KNOLL 6 230.00 | 530561 | KNOLL 3 115.00 | 0 |  | 1 | 89.0659 |  | MIDW | HAYS PLANT - VINE STREET 115KV CKT 1 | Reconductor line | 133 | 147 |  |  | 0.3 | 18 | 18 |  | 0.00084886 | 0.0029653 | 0.00036392 | 562.5k per mile | 168750 | 2008-01-01 | [38 empty] | 2018-06-01 | 2014-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T1141309FA | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | CP | MKEC | MKEC |  |  | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 09FA | 95.6 | 95.6 |  |  | 95.6467 | 109.8196 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - PRATT 115KV CKT 1 | 0 | 539673 | MED-LDG3 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 | 104.9875 |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 | Replace Terminal Equipment |  | 105.2 | [9 empty] | Wavetrap 225k Switch or Terminal Jumper 112.5k | [40 empty] | 2009-10-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T571309FA | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | CP | MKEC | MKEC |  |  | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 09FA | 95.6 | 95.6 |  |  | 89.4357 | 103.9904 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - HOLCOMB 345KV CKT 1 | 0 | 523853 | FINNEY7 345.00 | 531449 | HOLCOMB7 345.00 | 0 |  | 1 | 99.4148 |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 | Replace Terminal Equipment |  | 105.2 | [9 empty] | Wavetrap 225k Switch or Terminal Jumper 112.5k | [40 empty] | 2009-10-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T5171309FA | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | CP | MKEC | MKEC |  |  | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 09FA | 95.6 | 95.6 |  |  | 89.7765 | 103.6678 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05A | 0 | 0 |  | 0 |  | 0 |  |  | 99.1064 |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 | Replace Terminal Equipment |  | 105.2 | [9 empty] | Wavetrap 225k Switch or Terminal Jumper 112.5k | [40 empty] | 2009-10-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T1111309WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | CP | MKEC | MKEC |  |  | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 09WP | 95.6 | 95.6 |  |  | 85.5687 | 102.6747 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - PRATT 115KV CKT 1 | 0 | 539673 | MED-LDG3 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 | 98.157 |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 | Replace Terminal Equipment |  | 105.2 | [9 empty] | Wavetrap 225k Switch or Terminal Jumper 112.5k | [40 empty] | 2009-10-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T884409AP | TO->FROM | HALE CO INTERCHANGE - KRESS INTERCHANGE 115KV CKT 1 | S | SPS | SPS | SPS-CNPL | SPS-CNPL | 0 | 525192 | KRESS_INT 3 115.00 | 525454 | HALE_CNTY 3 115.00 | 0 |  | 1 | 09AP | 85 | 96 |  |  | 104.7759 | 108.6752 | [7 empty] | CATEGORYB | SINGLE | SWISHER COUNTY INTERCHANGE - TUCO INTERCHANGE 230KV CKT 1 | 0 | 525213 | SWISHER 6 230.00 | 525830 | TUCO_INT 6 230.00 | 0 |  | 1 | 104.3282 |  | SPS | HALE CO INTERCHANGE - KRESS INTERCHANGE 115KV CKT 1 | Replace Terminal Equipment | [12 empty] | 225000 | 2008-01-01 | [38 empty] | 2009-04-01 | 2011-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 1 | 2008AGP1AFS31T8651118SP | FROM->TO | GRIMES - WALDEN 138KV CKT 1 | S | EES | EES | EES_TEXAS | EES_TEXAS | 0 | 334026 | 4GRIMES 138.00 | 334040 | 4WALDEN 138.00 | 0 |  | 1 | 18SP | 191 | 191 |  |  | 111.4303 | 112.3986 | [7 empty] | CATEGORYB | SINGLE | CHINA - CHINA - JACNTO SERIES CAPACITOR 230KV CKT 1 | 0 | 334204 | 6CHINA 230.00 | 334205 | CHJC_SER 230.00 | 0 |  | 1 | 214.6813 |  | EES | GRIMES - WALDEN 138KV CKT 1 | Rebuild Transmission Line 29.71 miles | [12 empty] | 22282500 | [39 empty] | 2017-06-01 | 2017-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 1 | 2008AGP1AFS31T8921118SP | FROM->TO | GRIMES - WALDEN 138KV CKT 1 | S | EES | EES | EES_TEXAS | EES_TEXAS | 0 | 334026 | 4GRIMES 138.00 | 334040 | 4WALDEN 138.00 | 0 |  | 1 | 18SP | 191 | 191 |  |  | -999 | 112.2372 | [7 empty] | CATEGORYB | SINGLE | CHINA - JACNTO SERIES CAPACITOR - JACINTO 230KV CKT 1 | 0 | 334205 | CHJC_SER 230.00 | 334206 | 6JACINTO 230.00 | 0 |  | 1 | 214.373 |  | EES | GRIMES - WALDEN 138KV CKT 1 | Rebuild Transmission Line 29.71 miles | [12 empty] | 22282500 | [39 empty] | 2017-06-01 | 2017-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V1575509SH |  | GREENLEAF 115KV | EXP | MKEC |  |  |  |  | 539665 | GRNLEAF3 115.00 | [5 empty] | 09SH | [6 empty] | 0.86733 | 0.8469 | 0.86593 | 0.7855 | 0.99583 | 0.9 | 1.05 | CATEGORYB | SINGLE | KELLY - SOUTH SENECA 115KV CKT 1 | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 3 | 2008AGP1AFS31V2921309SP |  | GREENLEAF 115KV | EXP | MKEC |  |  |  |  | 539665 | GRNLEAF3 115.00 | [5 empty] | 09SP | [6 empty] | 0.89287 | 0.76439 | 0.90339 | 0.56405 | 0.98511 | 0.9 | 1.05 | CATEGORYB | SINGLE | KELLY - SOUTH SENECA 115KV CKT 1 | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V3485509SP |  | GREENLEAF 115KV | EXP | MKEC |  |  |  |  | 539665 | GRNLEAF3 115.00 | [5 empty] | 09SP | [8 empty] | 0.8459 | 0.80902 | 0.97907 | 0.9 | 1.05 | CATEGORYB | SINGLE | CONCORDIA - ELMCREK6 230.00 230KV CKT 1 | 0 | 539639 | ELMCREK6 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V7325509SP |  | GREENLEAF 115KV | EXP | MKEC |  |  |  |  | 539665 | GRNLEAF3 115.00 | [5 empty] | 09SP | [8 empty] | 0.84596 | 0.8091 | 0.97907 | 0.9 | 1.05 | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539658 | CONCRD6 230.00 | 539657 | CONCORD3 115.00 | 539904 | CONCOD-T 13.800 | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FNSL | FDNS-Iteration limit exceeded | 3 | 2 | 2008AGP1AFS32V73213SP |  | GREENLEAF 115KV | EXP | MKEC |  |  |  |  | 539665 | GRNLEAF3 115.00 | [5 empty] | 13SP | [8 empty] | 1.0042 | 0.85676 | 1.0193 | 0.9 | 1.05 | CATEGORYB | SINGLE | EAST MANHATTAN - ELMCREK6 230.00 230KV CKT 1 | 0 | 539639 | ELMCREK6 230.00 | 532861 | EMANHAT6 230.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 4 | 2008AGP1AFS31T1893409SP | FROM->TO | GREENLEAF - KNOB HILL 115KV CKT 1 | EXP | MKEC | WERE |  | NCENTRAL | 0 | 539665 | GRNLEAF3 115.00 | 533332 | KNOB HL3 115.00 | 0 |  | 1 | 09SP | 92 | 92 |  |  | 78.8954 | 113.973 | [7 empty] | CATEGORYB | SINGLE | KELLY - SOUTH SENECA 115KV CKT 1 | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 104.8552 |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [6 empty] | 578 | 10739 | 1 | 1 | 2011 | 40801 | 41061 | 40392.0625 | 40544.25 | 2011-01-01 06:00 | 2013-06-01 | [21 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T8025510SP | FROM->TO | GRANDVIEW EAST - SAMPSON 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541223 | GRDVWE 5 161.00 | 541345 | SAMPSON5 161.00 | 0 |  | 1 | 10SP | 223 | 245 | 105.1 | 101.5 | 104.72 | 106.3333 | [7 empty] | CATEGORYB | SINGLE | PLEASANT HILL (P HILL) 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 541200 | PHILL 7 345.00 | 541225 | PHILL 5 161.00 | 541361 | PHILL T 13.800 | 1 | 260.5166 |  | MIPU | Grandview East - Sampson - Longview 161kV Ckt 1 | Replace wavetraps at Grandview East and Longview. | 233 | 265 |  |  |  | 6 | 6 | [5 empty] | 50000 | 2009-03-19 | [38 empty] | 2010-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 1 | 2008AGP1AFS31T993110WP | FROM->TO | GRANDVIEW EAST - SAMPSON 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541223 | GRDVWE 5 161.00 | 541345 | SAMPSON5 161.00 | 0 |  | 1 | 10WP | 223 | 245 |  |  | 96.7345 | 100.6361 | [7 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 | 246.5584 |  | MIPU | Grandview East - Sampson - Longview 161kV Ckt 1 | Replace wavetraps at Grandview East and Longview. | 233 | 265 |  |  |  | 6 | 6 | [5 empty] | 50000 | 2009-03-19 | [38 empty] | 2010-06-01 | 2010-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T6835509SP | TO->FROM | GRANDVIEW EAST - MARTIN CITY 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541210 | MARTCTY5 161.00 | 541223 | GRDVWE 5 161.00 | 0 |  | 1 | 09SP | 233 | 265 | 105.3 | 106.5 | 101.2036 | 100.3462 | [7 empty] | CATEGORYB | SINGLE | PLEASANT HILL (P HILL) 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 541200 | PHILL 7 345.00 | 541225 | PHILL 5 161.00 | 541361 | PHILL T 13.800 | 1 | 265.9174 |  | MIPU | Loma Vista - Montrose 161kV Tap into K.C. South | To tap the Montrose-LomaVista 161 kV Line into KC South 161 kV sub. | [5 empty] | 18 | 18 | [5 empty] | 2369625 | 2009-03-19 | [38 empty] | 2009-06-01 | 2010-11-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T8015510SP | TO->FROM | GRANDVIEW EAST - MARTIN CITY 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541210 | MARTCTY5 161.00 | 541223 | GRDVWE 5 161.00 | 0 |  | 1 | 10SP | 233 | 265 | 110.3 | 107 | 109.9516 | 111.5429 | [7 empty] | CATEGORYB | SINGLE | PLEASANT HILL (P HILL) 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 541200 | PHILL 7 345.00 | 541225 | PHILL 5 161.00 | 541361 | PHILL T 13.800 | 1 | 295.5887 |  | MIPU | Loma Vista - Montrose 161kV Tap into K.C. South | To tap the Montrose-LomaVista 161 kV Line into KC South 161 kV sub. | [5 empty] | 18 | 18 | [5 empty] | 2369625 | 2009-03-19 | [38 empty] | 2009-06-01 | 2010-11-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 1 | 2008AGP1AFS31T983110WP | TO->FROM | GRANDVIEW EAST - MARTIN CITY 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541210 | MARTCTY5 161.00 | 541223 | GRDVWE 5 161.00 | 0 |  | 1 | 10WP | 233 | 265 |  |  | 98.4039 | 102.0542 | [7 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 | 270.4436 |  | MIPU | Loma Vista - Montrose 161kV Tap into K.C. South | To tap the Montrose-LomaVista 161 kV Line into KC South 161 kV sub. | [5 empty] | 18 | 18 | [5 empty] | 2369625 | 2009-03-19 | [38 empty] | 2009-06-01 | 2010-11-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 1 | 2008AGP1AFS31T3183110WP | TO->FROM | GRANDVIEW EAST - MARTIN CITY 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541210 | MARTCTY5 161.00 | 541223 | GRDVWE 5 161.00 | 0 |  | 1 | 10WP | 233 | 265 |  |  | 97.1924 | 100.4007 | [7 empty] | CATEGORYB | SINGLE | PLEASANT HILL (P HILL) 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 541200 | PHILL 7 345.00 | 541225 | PHILL 5 161.00 | 541361 | PHILL T 13.800 | 1 | 266.0619 |  | MIPU | Loma Vista - Montrose 161kV Tap into K.C. South | To tap the Montrose-LomaVista 161 kV Line into KC South 161 kV sub. | [5 empty] | 18 | 18 | [5 empty] | 2369625 | 2009-03-19 | [38 empty] | 2009-06-01 | 2010-11-01
2008-AGP1 | AFS3 | CONT-0803 - Hoyt - Stranger 345kV |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T5463318SP | TO->FROM | GOODYEAR JUNCTION - NORTHLAND 115KV CKT 1 | REL | WERE | WERE | NEAST | NEAST | 0 | 533169 | NTHLAND3 115.00 | 533162 | GOODYR 3 115.00 | 0 |  | 1 | 18SP | 160 | 175 |  |  | 88.2133 | 101.3358 | [7 empty] | CATEGORYB | SINGLE | HOYT - STRANGER CREEK 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532772 | STRANGR7 345.00 | 0 |  | 1 | 177.3377 |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17313318SP |  | GOODLAND TAP 115KV | REL | SUNC |  | SEPC |  |  | 531443 | GODLNDT3 115.00 | [5 empty] | 18SP | [8 empty] | 0.92058 | 0.88833 | 1.0042 | 0.9 | 1.05 | CATEGORYB | SINGLE | MINGO (MINGO) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 531451 | MINGO 7 345.00 | 531429 | MINGO 3 115.00 | 531452 | MINGTER1 13.800 | 1 |  |  | SUNC | RULETON 115KV Capacitor | Install Second 12 Mvar cap bank at Ruleton 115kV | [12 empty] | 486000 | 2008-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17223318SP |  | GOODLAND 115KV | REL | SUNC |  | GREAT PL |  |  | 531353 | GOODLND3 115.00 | [5 empty] | 18SP | [8 empty] | 0.92062 | 0.88842 | 1.0048 | 0.9 | 1.05 | CATEGORYB | SINGLE | MINGO (MINGO) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 531451 | MINGO 7 345.00 | 531429 | MINGO 3 115.00 | 531452 | MINGTER1 13.800 | 1 |  |  | SUNC | RULETON 115KV Capacitor | Install Second 12 Mvar cap bank at Ruleton 115kV | [12 empty] | 486000 | 2008-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17183318SP |  | GOODLAN3 115KV | REL | MIDW |  | REG E-IL |  |  | 530612 | GOODLAN3 115.00 | [5 empty] | 18SP | [8 empty] | 0.92062 | 0.88842 | 1.0048 | 0.9 | 1.05 | CATEGORYB | SINGLE | MINGO (MINGO) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 531451 | MINGO 7 345.00 | 531429 | MINGO 3 115.00 | 531452 | MINGTER1 13.800 | 1 |  |  | SUNC | RULETON 115KV Capacitor | Install Second 12 Mvar cap bank at Ruleton 115kV | [12 empty] | 486000 | 2008-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V3475509SP |  | GLEN ELDER 115KV | EXP | MKEC |  |  |  |  | 539663 | GLENELD3 115.00 | [5 empty] | 09SP | [8 empty] | 0.85791 | 0.81555 | 0.97493 | 0.9 | 1.05 | CATEGORYB | SINGLE | CONCORDIA - ELMCREK6 230.00 230KV CKT 1 | 0 | 539639 | ELMCREK6 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V7315509SP |  | GLEN ELDER 115KV | EXP | MKEC |  |  |  |  | 539663 | GLENELD3 115.00 | [5 empty] | 09SP | [8 empty] | 0.85796 | 0.81562 | 0.97493 | 0.9 | 1.05 | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539658 | CONCRD6 230.00 | 539657 | CONCORD3 115.00 | 539904 | CONCOD-T 13.800 | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V2505509SP |  | GLEN ELDER 115KV | EXP | MKEC |  |  |  |  | 539663 | GLENELD3 115.00 | [5 empty] | 09SP | [8 empty] | 0.86862 | 0.82824 | 0.97493 | 0.9 | 1.05 | CATEGORYB | SINGLE | EAST MANHATTAN - ELMCREK6 230.00 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 539639 | ELMCREK6 230.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FNSL | FDNS-Iteration limit exceeded | 3 | 2 | 2008AGP1AFS32V63213SP |  | GLEN ELDER 115KV | EXP | MKEC |  |  |  |  | 539663 | GLENELD3 115.00 | [5 empty] | 13SP | [8 empty] | 0.99446 | 0.77701 | 1.0006 | 0.9 | 1.05 | CATEGORYB | SINGLE | EAST MANHATTAN - ELMCREK6 230.00 230KV CKT 1 | 0 | 539639 | ELMCREK6 230.00 | 532861 | EMANHAT6 230.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T1544409G | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | PL | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 09G | 124 | 124 |  |  | 88.3169 | 111.678 | [7 empty] | CATEGORYB | SINGLE | MOORELAND - MOREWOOD SW 138KV CKT 1 | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 138.4807 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T1172409SH | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | PL | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 09SH | 124 | 124 |  |  | 78.8616 | 102.3183 | [7 empty] | CATEGORYB | SINGLE | MOORELAND - MOREWOOD SW 138KV CKT 1 | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 126.8747 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T1492409SP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | PL | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 09SP | 124 | 124 |  |  | 89.6381 | 113.1224 | [7 empty] | CATEGORYB | SINGLE | MOORELAND - MOREWOOD SW 138KV CKT 1 | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 140.2718 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T1444409WP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | PL | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 09WP | 124 | 124 |  |  | 95.8045 | 119.4842 | [7 empty] | CATEGORYB | SINGLE | MOORELAND - MOREWOOD SW 138KV CKT 1 | 0 | 520999 | MOORLND4 138.00 | 521001 | MORWODS4 138.00 | 0 |  | 1 | 148.1604 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T884409WP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | PL | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 09WP | 124 | 124 |  |  | 86.3327 | 108.7639 | [7 empty] | CATEGORYB | SINGLE | DEWEY - SOUTHARD 138KV CKT 1 | 0 | 514787 | DEWEY 4 138.00 | 514822 | SOUTHRD4 138.00 | 0 |  | 1 | 134.8672 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T1234409WP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | PL | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 09WP | 124 | 124 |  |  | 85.2769 | 106.4679 | [7 empty] | CATEGORYB | SINGLE | CEDARDALE - MOORELAND 138KV CKT 1 | 0 | 520848 | CEDRDAL4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 132.0202 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T1691310SP | FROM->TO | GILL ENERGY CENTER WEST - WACO 138KV CKT 1 | REL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533045 | GILL W 4 138.00 | 533072 | WACO 4 138.00 | 0 |  | 1 | 10SP | 232 | 232 | 100.3 | 101 | 100.9145 | 101.0758 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 | 234.4959 |  | WERE | GILL ENERGY CENTER WEST - WACO 138KV CKT 1 | Tear down and rebuild Gill - Waco with bundled 1192.5 ACSR conductor |  |  |  |  | 1.87 | [7 empty] | 1000000 | 2007-01-01 | [38 empty] | 2010-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T3031313SP | FROM->TO | GILL ENERGY CENTER WEST - WACO 138KV CKT 1 | REL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533045 | GILL W 4 138.00 | 533072 | WACO 4 138.00 | 0 |  | 1 | 13SP | 232 | 232 | 123.9 | 124.8 | 124.0554 | 124.8667 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 | 289.6907 |  | WERE | GILL ENERGY CENTER WEST - WACO 138KV CKT 1 | Tear down and rebuild Gill - Waco with bundled 1192.5 ACSR conductor |  |  |  |  | 1.87 | [7 empty] | 1000000 | 2007-01-01 | [38 empty] | 2010-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T1141313WP | FROM->TO | GILL ENERGY CENTER WEST - WACO 138KV CKT 1 | REL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533045 | GILL W 4 138.00 | 533072 | WACO 4 138.00 | 0 |  | 1 | 13WP | 232 | 232 | 100.3 | 100.2 | 99.4563 | 100.3389 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 | 232.7862 |  | WERE | GILL ENERGY CENTER WEST - WACO 138KV CKT 1 | Tear down and rebuild Gill - Waco with bundled 1192.5 ACSR conductor |  |  |  |  | 1.87 | [7 empty] | 1000000 | 2007-01-01 | [38 empty] | 2010-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T5201318SP | FROM->TO | GILL ENERGY CENTER WEST - WACO 138KV CKT 1 | REL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533045 | GILL W 4 138.00 | 533072 | WACO 4 138.00 | 0 |  | 1 | 18SP | 232 | 232 | 127.4 | 127.9 | 127.3283 | 128.0435 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 | 297.0609 |  | WERE | GILL ENERGY CENTER WEST - WACO 138KV CKT 1 | Tear down and rebuild Gill - Waco with bundled 1192.5 ACSR conductor |  |  |  |  | 1.87 | [7 empty] | 1000000 | 2007-01-01 | [38 empty] | 2010-06-01 | 2012-06-01
2006-AG1 | 2006-AG1 | [7 empty] | 55919559201559575599913316SP |  | FT SUPPLY 138/69KV TRANSFORMER CKT 1 | U | WFEC | WFEC |  |  | 1 | 520920 | FTSUPLY4 138 | 520919 | FTSUPLY269.0 | 521182 |  | 2 | 16SP |  | 70 | [12 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | WFEC | FT SUPPLY 138/69KV TRANSFORMER CKT 1 | Install 2nd 70 MVA auto at Ft Supply | 70 | 70 |  |  |  | 12 | 18 |  |  |  |  | Use RS from Ft Supply Auto | 2000000 | [39 empty] | 2006-12-01 | 2008-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 3 | 2008AGP1AFS31V16962318SP |  | FT SMITH 500KV | REL | OKGE |  | FT SMITH |  |  | 515305 | FTSMITH8 500.00 | [5 empty] | 18SP | [7 empty] | 0.89531 | 0.92185 | 0.89558 | 0.99306 | 0.9 | 1.05 | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 337909 | 8ANO 50 500.00 | 515305 | FTSMITH8 500.00 | 0 |  | 1 |  |  | OKGE | FT SMITH CAP BANK | Install a cap bank at the FT Smith 345 bus | [12 empty] | 500000 | [39 empty] | 2014-06-01 | 2014-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T282409AP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | S | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 09AP | 133 | 153 |  |  | 55.4721 | 114.5181 | [7 empty] | CATEGORYB | SINGLE | IODINE - WOODWARD 138KV CKT 1 | 0 | 514785 | WOODWRD4 138.00 | 514796 | IODINE-4 138.00 | 0 |  | 1 | 175.2127 |  | OKGE | FPL SWITCH - WOODWARD 138KV CKT 1 | Reconductor/rebuild 12.07 miles of line to 795AS33. | 268 | 287 | 287 | 287 | 12.08 | 18 | 10 |  | 0.00815 | 0.0475 | 0.0132 |  | 3700000 | 2008-07-30 | [38 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T332409AP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | S | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 09AP | 133 | 153 |  |  | 54.3032 | 113.2812 | [7 empty] | CATEGORYB | SINGLE | DEWEY - IODINE 138KV CKT 1 | 0 | 514787 | DEWEY 4 138.00 | 514796 | IODINE-4 138.00 | 0 |  | 1 | 173.3202 |  | OKGE | FPL SWITCH - WOODWARD 138KV CKT 1 | Reconductor/rebuild 12.07 miles of line to 795AS33. | 268 | 287 | 287 | 287 | 12.08 | 18 | 10 |  | 0.00815 | 0.0475 | 0.0132 |  | 3700000 | 2008-07-30 | [38 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T952209AP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | S | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 09AP | 133 | 153 |  |  | 51.916 | 103.8724 | [7 empty] | CATEGORYB | SINGLE | WOODWARD (WOODWRD2) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 514782 | WODWRD 2 69.000 | 514785 | WOODWRD4 138.00 | 515771 | WOODWR21 13.200 | 1 | 158.9248 |  | OKGE | FPL SWITCH - WOODWARD 138KV CKT 1 | Reconductor/rebuild 12.07 miles of line to 795AS33. | 268 | 287 | 287 | 287 | 12.08 | 18 | 10 |  | 0.00815 | 0.0475 | 0.0132 |  | 3700000 | 2008-07-30 | [38 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 4 | 3 | 2008AGP1AFS31T2844309FA | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | S | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 09FA | 133 | 153 |  |  | 52.977 | 106.7071 | [7 empty] | CATEGORYB | SINGLE | WOODWARD (WOODWRD2) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 514782 | WODWRD 2 69.000 | 514785 | WOODWRD4 138.00 | 515771 | WOODWR21 13.200 | 1 | 163.2619 |  | OKGE | FPL SWITCH - WOODWARD 138KV CKT 1 | Reconductor/rebuild 12.07 miles of line to 795AS33. | 268 | 287 | 287 | 287 | 12.08 | 18 | 10 |  | 0.00815 | 0.0475 | 0.0132 |  | 3700000 | 2008-07-30 | [38 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T584409FA | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | S | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 09FA | 133 | 153 |  |  | 43.8399 | 102.966 | [7 empty] | CATEGORYB | SINGLE | IODINE - WOODWARD 138KV CKT 1 | 0 | 514785 | WOODWRD4 138.00 | 514796 | IODINE-4 138.00 | 0 |  | 1 | 157.538 |  | OKGE | FPL SWITCH - WOODWARD 138KV CKT 1 | Reconductor/rebuild 12.07 miles of line to 795AS33. | 268 | 287 | 287 | 287 | 12.08 | 18 | 10 |  | 0.00815 | 0.0475 | 0.0132 |  | 3700000 | 2008-07-30 | [38 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T624409FA | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | S | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 09FA | 133 | 153 |  |  | 42.0646 | 100.9314 | [7 empty] | CATEGORYB | SINGLE | DEWEY - IODINE 138KV CKT 1 | 0 | 514787 | DEWEY 4 138.00 | 514796 | IODINE-4 138.00 | 0 |  | 1 | 154.425 |  | OKGE | FPL SWITCH - WOODWARD 138KV CKT 1 | Reconductor/rebuild 12.07 miles of line to 795AS33. | 268 | 287 | 287 | 287 | 12.08 | 18 | 10 |  | 0.00815 | 0.0475 | 0.0132 |  | 3700000 | 2008-07-30 | [38 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T2595509G | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | S | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 09G | 133 | 153 |  |  | 49.1936 | 102.126 | [7 empty] | CATEGORYB | SINGLE | WOODWARD (WOODWRD2) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 514782 | WODWRD 2 69.000 | 514785 | WOODWRD4 138.00 | 515771 | WOODWR21 13.200 | 1 | 156.2528 |  | OKGE | FPL SWITCH - WOODWARD 138KV CKT 1 | Reconductor/rebuild 12.07 miles of line to 795AS33. | 268 | 287 | 287 | 287 | 12.08 | 18 | 10 |  | 0.00815 | 0.0475 | 0.0132 |  | 3700000 | 2008-07-30 | [38 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T852409G | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | S | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 09G | 133 | 153 |  |  | 41.0392 | 100.6857 | [7 empty] | CATEGORYB | SINGLE | IODINE - WOODWARD 138KV CKT 1 | 0 | 514785 | WOODWRD4 138.00 | 514796 | IODINE-4 138.00 | 0 |  | 1 | 154.0491 |  | OKGE | FPL SWITCH - WOODWARD 138KV CKT 1 | Reconductor/rebuild 12.07 miles of line to 795AS33. | 268 | 287 | 287 | 287 | 12.08 | 18 | 10 |  | 0.00815 | 0.0475 | 0.0132 |  | 3700000 | 2008-07-30 | [38 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T10905513SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | S | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 13SP | 133 | 153 |  |  | 67.9722 | 105.1154 | [7 empty] | CATEGORYB | SINGLE | WOODWARD (WOODWRD2) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 514782 | WODWRD 2 69.000 | 514785 | WOODWRD4 138.00 | 515771 | WOODWR21 13.200 | 1 | 160.8266 |  | OKGE | FPL SWITCH - WOODWARD 138KV CKT 1 | Reconductor/rebuild 12.07 miles of line to 795AS33. | 268 | 287 | 287 | 287 | 12.08 | 18 | 10 |  | 0.00815 | 0.0475 | 0.0132 |  | 3700000 | 2008-07-30 | [38 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V3305509SP |  | FORT SCOTT 69KV | EXP | WERE |  | SEAST |  |  | 533635 | FTSCOTT2 69.000 | [5 empty] | 09SP | [6 empty] | 0.92314 | 0.92214 | 0.94631 | 0.91548 | 1.0048 | 0.93 | 1.05 | CATEGORYB | SINGLE | LITCHFIELD - PITNAC 69KV CKT 1 | 0 | 533765 | LITCH 2 69.000 | 533769 | PITNAC 2 69.000 | 0 |  | 1 |  |  | WERE | Fort Scott 161/69kV Transformer CKT 1 | New 161/69 kV transformer at Ft Scott. | 100 | 110 |  |  |  | 18 | 18 | [5 empty] | 1400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 2 | 2008AGP1AFS31V9123213SP |  | FORT JUNCTION SWITCHING STATION 115KV | REL | WERE |  | NCENTRAL |  |  | 533328 | FT JCT 3 115.00 | [5 empty] | 13SP | [8 empty] | 0.9461 | 0.92596 | 0.96862 | 0.93 | 1.05 | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 | CONT-0633 - East Manhattan 230-115kV XFMR | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17463318SP |  | FORT JUNCTION SWITCHING STATION 115KV | REL | WERE |  | NCENTRAL |  |  | 533328 | FT JCT 3 115.00 | [5 empty] | 18SP | [6 empty] | 0.92721 | 0.91636 | 0.90089 | 0.85227 | 0.95811 | 0.93 | 1.05 | CATEGORYB | SINGLE | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17663318SP |  | FORT JUNCTION SWITCHING STATION 115KV | REL | WERE |  | NCENTRAL |  |  | 533328 | FT JCT 3 115.00 | [5 empty] | 18SP | [8 empty] | 0.94429 | 0.90344 | 0.95811 | 0.93 | 1.05 | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T3742210SP | FROM->TO | FORT JUNCTION SWITCHING STATION - WEST JUNCTION CITY JUNCTION (EAST) 115KV CKT 2 | EXP | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533328 | FT JCT 3 115.00 | 533343 | WJCCTYE3 115.00 | 0 |  | 2 | 10SP | 92 | 92 |  | 104.5 | 102.077 | 106.5544 | [7 empty] | CATEGORYB | SINGLE | FORT JUNCTION SWITCHING STATION - JUNCTION CITY 115KV CKT 1 | 0 | 533328 | FT JCT 3 115.00 | 533330 | JCTCTY 3 115.00 | 0 |  | 1 | 98.03 |  | WERE | FORT JUNCTION SWITCHING STATION - WEST JUNCTION CITY JUNCTION 115KV CKT 1 | Build new Ft Jct. - W. Jct City line that follows the path of the JEC - Summit 345kV. Remove old double circuit and WJCTYE - WJCTCTY 115 kV | [52 empty] | 2010-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T4662213SP | FROM->TO | FORT JUNCTION SWITCHING STATION - WEST JUNCTION CITY JUNCTION (EAST) 115KV CKT 2 | EXP | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533328 | FT JCT 3 115.00 | 533343 | WJCCTYE3 115.00 | 0 |  | 2 | 13SP | 92 | 92 |  |  | 104.7118 | 109.4168 | [7 empty] | CATEGORYB | SINGLE | FORT JUNCTION SWITCHING STATION - JUNCTION CITY 115KV CKT 1 | 0 | 533328 | FT JCT 3 115.00 | 533330 | JCTCTY 3 115.00 | 0 |  | 1 | 100.6635 |  | WERE | FORT JUNCTION SWITCHING STATION - WEST JUNCTION CITY JUNCTION 115KV CKT 1 | Build new Ft Jct. - W. Jct City line that follows the path of the JEC - Summit 345kV. Remove old double circuit and WJCTYE - WJCTCTY 115 kV | [52 empty] | 2010-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 3 | 2008AGP1AFS31T5472318SP | FROM->TO | FORT JUNCTION SWITCHING STATION - WEST JUNCTION CITY JUNCTION (EAST) 115KV CKT 2 | EXP | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533328 | FT JCT 3 115.00 | 533343 | WJCCTYE3 115.00 | 0 |  | 2 | 18SP | 92 | 92 |  |  | 98.9859 | 104.9374 | [7 empty] | CATEGORYB | SINGLE | FORT JUNCTION SWITCHING STATION - JUNCTION CITY 115KV CKT 1 | 0 | 533328 | FT JCT 3 115.00 | 533330 | JCTCTY 3 115.00 | 0 |  | 1 | 96.5424 |  | WERE | FORT JUNCTION SWITCHING STATION - WEST JUNCTION CITY JUNCTION 115KV CKT 1 | Build new Ft Jct. - W. Jct City line that follows the path of the JEC - Summit 345kV. Remove old double circuit and WJCTYE - WJCTCTY 115 kV | [52 empty] | 2010-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T3732210SP | FROM->TO | FORT JUNCTION SWITCHING STATION - WEST JUNCTION CITY JUNCTION (EAST) 115KV CKT 1 | EXP | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533328 | FT JCT 3 115.00 | 533343 | WJCCTYE3 115.00 | 0 |  | 1 | 10SP | 92 | 92 |  | 104.5 | 102.077 | 106.5544 | [7 empty] | CATEGORYB | SINGLE | FORT JUNCTION SWITCHING STATION - JUNCTION CITY 115KV CKT 1 | 0 | 533328 | FT JCT 3 115.00 | 533330 | JCTCTY 3 115.00 | 0 |  | 1 | 98.03 |  | WERE | FORT JUNCTION SWITCHING STATION - WEST JUNCTION CITY JUNCTION 115KV CKT 1 | Build new Ft Jct. - W. Jct City line that follows the path of the JEC - Summit 345kV. Remove old double circuit and WJCTYE - WJCTCTY 115 kV | [52 empty] | 2010-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T4652213SP | FROM->TO | FORT JUNCTION SWITCHING STATION - WEST JUNCTION CITY JUNCTION (EAST) 115KV CKT 1 | EXP | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533328 | FT JCT 3 115.00 | 533343 | WJCCTYE3 115.00 | 0 |  | 1 | 13SP | 92 | 92 |  |  | 104.7118 | 109.4168 | [7 empty] | CATEGORYB | SINGLE | FORT JUNCTION SWITCHING STATION - JUNCTION CITY 115KV CKT 1 | 0 | 533328 | FT JCT 3 115.00 | 533330 | JCTCTY 3 115.00 | 0 |  | 1 | 100.6635 |  | WERE | FORT JUNCTION SWITCHING STATION - WEST JUNCTION CITY JUNCTION 115KV CKT 1 | Build new Ft Jct. - W. Jct City line that follows the path of the JEC - Summit 345kV. Remove old double circuit and WJCTYE - WJCTCTY 115 kV | [52 empty] | 2010-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 3 | 2008AGP1AFS31T5462318SP | FROM->TO | FORT JUNCTION SWITCHING STATION - WEST JUNCTION CITY JUNCTION (EAST) 115KV CKT 1 | EXP | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533328 | FT JCT 3 115.00 | 533343 | WJCCTYE3 115.00 | 0 |  | 1 | 18SP | 92 | 92 |  |  | 98.9859 | 104.9374 | [7 empty] | CATEGORYB | SINGLE | FORT JUNCTION SWITCHING STATION - JUNCTION CITY 115KV CKT 1 | 0 | 533328 | FT JCT 3 115.00 | 533330 | JCTCTY 3 115.00 | 0 |  | 1 | 96.5424 |  | WERE | FORT JUNCTION SWITCHING STATION - WEST JUNCTION CITY JUNCTION 115KV CKT 1 | Build new Ft Jct. - W. Jct City line that follows the path of the JEC - Summit 345kV. Remove old double circuit and WJCTYE - WJCTCTY 115 kV | [52 empty] | 2010-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T271309AP | FROM->TO | FLATRDG3 138.00 - HARPER 138KV CKT 1 | CP | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 09AP | 105.2 | 105.2 |  |  | 99.3735 | 100.0864 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - PRATT 115KV CKT 1 | 0 | 539673 | MED-LDG3 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 | 105.2909 |  | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 | [50 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T1131309FA | FROM->TO | FLATRDG3 138.00 - HARPER 138KV CKT 1 | CP | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 09FA | 105.2 | 105.2 |  |  | 110.6075 | 124.2645 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - PRATT 115KV CKT 1 | 0 | 539673 | MED-LDG3 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 | 130.7263 |  | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 | [50 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T561309FA | FROM->TO | FLATRDG3 138.00 - HARPER 138KV CKT 1 | CP | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 09FA | 105.2 | 105.2 |  |  | 106.0143 | 119.4549 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - HOLCOMB 345KV CKT 1 | 0 | 523853 | FINNEY7 345.00 | 531449 | HOLCOMB7 345.00 | 0 |  | 1 | 125.6666 |  | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 | [50 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T5161309FA | FROM->TO | FLATRDG3 138.00 - HARPER 138KV CKT 1 | CP | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 09FA | 105.2 | 105.2 |  |  | 106.3677 | 119.1795 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05A | 0 | 0 |  | 0 |  | 0 |  |  | 125.3768 |  | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 | [50 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T1211309FA | FROM->TO | FLATRDG3 138.00 - HARPER 138KV CKT 1 | CP | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 09FA | 105.2 | 105.2 |  |  | 104.197 | 113.6637 | [7 empty] | CATEGORYB | SINGLE | NORTH JUDSON LARGE SUB - SPEARVILLE 115KV CKT 1 | 0 | 539694 | SPEARVL3 115.00 | 539771 | NOR-JUD3 115.00 | 0 |  | 1 | 119.5742 |  | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 | [50 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FNSL | FDNS-Iteration limit exceeded | 1 | 3 | 2008AGP1AFS32T61309FA | FROM->TO | FLATRDG3 138.00 - HARPER 138KV CKT 1 | CP | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 09FA | 105.2 | 105.2 |  |  | 103.7808 | 113.1818 | [7 empty] | CATEGORYB | SINGLE | SPEARVILLE (SPEARVL6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539694 | SPEARVL3 115.00 | 539695 | SPEARVL6 230.00 | 539935 | SPERVLTT 13.800 | 1 | 119.0673 |  | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 | [50 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 | CONT-0301 - Rose Hill - Wolf Creek 345kV |  |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T731309FA | FROM->TO | FLATRDG3 138.00 - HARPER 138KV CKT 1 | CP | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 09FA | 105.2 | 105.2 |  |  | 92.0937 | 106.1524 | [7 empty] | CATEGORYB | SINGLE | ROSE HILL - WOLF CREEK 345KV CKT 1 | 0 | 532794 | ROSEHIL7 345.00 | 532797 | WOLFCRK7 345.00 | 0 |  | 1 | 111.6723 |  | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 | [50 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV |  |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T951309FA | FROM->TO | FLATRDG3 138.00 - HARPER 138KV CKT 1 | CP | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 09FA | 105.2 | 105.2 |  |  | 91.436 | 105.7312 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 | 111.2292 |  | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 | [50 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 | CONT-0400 - JEC - Hoyt 345kV |  |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T681309FA | FROM->TO | FLATRDG3 138.00 - HARPER 138KV CKT 1 | CP | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 09FA | 105.2 | 105.2 |  |  | 90.4515 | 105.3166 | [7 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 | 110.7931 |  | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 | [50 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 | CONT-0300 - Benton - Wolf Creek 345kV |  |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T711309FA | FROM->TO | FLATRDG3 138.00 - HARPER 138KV CKT 1 | CP | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 09FA | 105.2 | 105.2 |  |  | 90.9067 | 105.0739 | [7 empty] | CATEGORYB | SINGLE | BENTON - WOLF CREEK 345KV CKT 1 | 0 | 532791 | BENTON 7 345.00 | 532797 | WOLFCRK7 345.00 | 0 |  | 1 | 110.5377 |  | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 | [50 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 | CONT-0802 - Wichita - OG&E (Woodring) 345kV |  |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T511309FA | FROM->TO | FLATRDG3 138.00 - HARPER 138KV CKT 1 | CP | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 09FA | 105.2 | 105.2 |  |  | 90.3542 | 104.8906 | [7 empty] | CATEGORYB | SINGLE | WICHITA - WOODRING 345KV CKT 1 | 0 | 514715 | WOODRNG7 345.00 | 532796 | WICHITA7 345.00 | 0 |  | 1 | 110.3449 |  | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 | [50 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T11309FA | FROM->TO | FLATRDG3 138.00 - HARPER 138KV CKT 1 | CP | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 09FA | 105.2 | 105.2 |  |  | 86.8414 | 101.1299 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | 106.3887 |  | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 | [50 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 3 | 2008AGP1AFS31T1004309G | FROM->TO | FLATRDG3 138.00 - HARPER 138KV CKT 1 | CP | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 09G | 105.2 | 105.2 |  |  | 108.7204 | 106.5539 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - PRATT 115KV CKT 1 | 0 | 539673 | MED-LDG3 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 | 112.0947 |  | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 | [50 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 3 | 2008AGP1AFS31T694309G | FROM->TO | FLATRDG3 138.00 - HARPER 138KV CKT 1 | CP | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 09G | 105.2 | 105.2 |  |  | 105.4883 | 102.0533 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - HOLCOMB 345KV CKT 1 | 0 | 523853 | FINNEY7 345.00 | 531449 | HOLCOMB7 345.00 | 0 |  | 1 | 107.3601 |  | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 | [50 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 3 | 2008AGP1AFS31T4894309G | FROM->TO | FLATRDG3 138.00 - HARPER 138KV CKT 1 | CP | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 09G | 105.2 | 105.2 |  |  | 105.3145 | 100.5922 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05A | 0 | 0 |  | 0 |  | 0 |  |  | 105.823 |  | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 | [50 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T1641309SH | FROM->TO | FLATRDG3 138.00 - HARPER 138KV CKT 1 | CP | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 09SH | 105.2 | 105.2 |  |  | 99.7472 | 102.4545 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - PRATT 115KV CKT 1 | 0 | 539673 | MED-LDG3 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 | 107.7821 |  | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 | [50 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T1101309WP | FROM->TO | FLATRDG3 138.00 - HARPER 138KV CKT 1 | CP | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 09WP | 105.2 | 105.2 |  | 108.5 | 101.4354 | 117.9606 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - PRATT 115KV CKT 1 | 0 | 539673 | MED-LDG3 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 | 124.0946 |  | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 | [50 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FNSL | FDNS-Iteration limit exceeded | FDNS |  | 1 | 3 | 2008AGP1AFS31T751309WP | FROM->TO | FLATRDG3 138.00 - HARPER 138KV CKT 1 | CP | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 09WP | 105.2 | 105.2 |  | 105.2 | 97.9119 | 114.3218 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - HOLCOMB 345KV CKT 1 | 0 | 523853 | FINNEY7 345.00 | 531449 | HOLCOMB7 345.00 | 0 |  | 1 | 120.2665 |  | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 | [50 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T6683309WP | FROM->TO | FLATRDG3 138.00 - HARPER 138KV CKT 1 | CP | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 09WP | 105.2 | 105.2 |  | 105.7 | 98.1844 | 113.5804 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05A | 0 | 0 |  | 0 |  | 0 |  |  | 119.4866 |  | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 | [50 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T1151309WP | FROM->TO | FLATRDG3 138.00 - HARPER 138KV CKT 1 | CP | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 09WP | 105.2 | 105.2 |  |  | 90.678 | 108.0873 | [7 empty] | CATEGORYB | SINGLE | NORTH JUDSON LARGE SUB - SPEARVILLE 115KV CKT 1 | 0 | 539694 | SPEARVL3 115.00 | 539771 | NOR-JUD3 115.00 | 0 |  | 1 | 113.7078 |  | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 | [50 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T4331309WP | FROM->TO | FLATRDG3 138.00 - HARPER 138KV CKT 1 | CP | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 09WP | 105.2 | 105.2 |  |  | 90.0714 | 107.6258 | [7 empty] | CATEGORYB | SINGLE | SPEARVILLE (SPEARVL6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539694 | SPEARVL3 115.00 | 539695 | SPEARVL6 230.00 | 539935 | SPERVLTT 13.800 | 1 | 113.2223 |  | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 | [50 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 | CONT-0301 - Rose Hill - Wolf Creek 345kV |  |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T841309WP | FROM->TO | FLATRDG3 138.00 - HARPER 138KV CKT 1 | CP | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 09WP | 105.2 | 105.2 |  |  | 83.8866 | 101.0615 | [7 empty] | CATEGORYB | SINGLE | ROSE HILL - WOLF CREEK 345KV CKT 1 | 0 | 532794 | ROSEHIL7 345.00 | 532797 | WOLFCRK7 345.00 | 0 |  | 1 | 106.3167 |  | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 | [50 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 | CONT-0400 - JEC - Hoyt 345kV |  |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T811309WP | FROM->TO | FLATRDG3 138.00 - HARPER 138KV CKT 1 | CP | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 09WP | 105.2 | 105.2 |  |  | 82.939 | 100.6058 | [7 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 | 105.8373 |  | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 | [50 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV |  |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T971309WP | FROM->TO | FLATRDG3 138.00 - HARPER 138KV CKT 1 | CP | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 09WP | 105.2 | 105.2 |  |  | 83.1775 | 100.4021 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 | 105.623 |  | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 | [50 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 | CONT-0300 - Benton - Wolf Creek 345kV |  |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T831309WP | FROM->TO | FLATRDG3 138.00 - HARPER 138KV CKT 1 | CP | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 09WP | 105.2 | 105.2 |  |  | 82.8531 | 100 | [7 empty] | CATEGORYB | SINGLE | BENTON - WOLF CREEK 345KV CKT 1 | 0 | 532791 | BENTON 7 345.00 | 532797 | WOLFCRK7 345.00 | 0 |  | 1 | 105.2 |  | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 | [50 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T971310WP | FROM->TO | FLATRDG3 138.00 - HARPER 138KV CKT 1 | CP | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 10WP | 105.2 | 105.2 |  | 105.7 | 99.3949 | 114.4606 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - PRATT 115KV CKT 1 | 0 | 539673 | MED-LDG3 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 | 120.4126 |  | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 | [50 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T813310WP | FROM->TO | FLATRDG3 138.00 - HARPER 138KV CKT 1 | CP | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 10WP | 105.2 | 105.2 |  | 105.7 | 98.5404 | 114.0964 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - HOLCOMB 345KV CKT 1 | 0 | 523853 | FINNEY7 345.00 | 531449 | HOLCOMB7 345.00 | 0 |  | 1 | 120.0294 |  | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 | [50 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T5963310WP | FROM->TO | FLATRDG3 138.00 - HARPER 138KV CKT 1 | CP | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 10WP | 105.2 | 105.2 |  | 106.8 | 99.072 | 113.8366 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05B | 0 | 0 |  | 0 |  | 0 |  |  | 119.7561 |  | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 | [50 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T1223310WP | FROM->TO | FLATRDG3 138.00 - HARPER 138KV CKT 1 | CP | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 10WP | 105.2 | 105.2 |  |  | 88.3096 | 105.6283 | [7 empty] | CATEGORYB | SINGLE | NORTH JUDSON LARGE SUB - SPEARVILLE 115KV CKT 1 | 0 | 539694 | SPEARVL3 115.00 | 539771 | NOR-JUD3 115.00 | 0 |  | 1 | 111.121 |  | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 | [50 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T3963310WP | FROM->TO | FLATRDG3 138.00 - HARPER 138KV CKT 1 | CP | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 10WP | 105.2 | 105.2 |  |  | 87.6671 | 104.784 | [7 empty] | CATEGORYB | SINGLE | SPEARVILLE (SPEARVL6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539694 | SPEARVL3 115.00 | 539695 | SPEARVL6 230.00 | 539935 | SPERVLTT 13.800 | 1 | 110.2328 |  | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 | [50 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T1643313WP | FROM->TO | FLATRDG3 138.00 - HARPER 138KV CKT 1 | CP | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 13WP | 105.2 | 105.2 |  | 102.4 | 97.3704 | 112.6462 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - PRATT 115KV CKT 1 | 0 | 539673 | MED-LDG3 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 | 118.5038 |  | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 | [50 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T1283313WP | FROM->TO | FLATRDG3 138.00 - HARPER 138KV CKT 1 | CP | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 13WP | 105.2 | 105.2 |  | 100.6 | 98.096 | 110.0365 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - HOLCOMB 345KV CKT 1 | 0 | 523853 | FINNEY7 345.00 | 531449 | HOLCOMB7 345.00 | 0 |  | 1 | 115.7584 |  | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 | [50 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T6643313WP | FROM->TO | FLATRDG3 138.00 - HARPER 138KV CKT 1 | CP | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 13WP | 105.2 | 105.2 |  | 100.8 | 97.6865 | 109.102 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05B | 0 | 0 |  | 0 |  | 0 |  |  | 114.7753 |  | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 | [50 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T1693313WP | FROM->TO | FLATRDG3 138.00 - HARPER 138KV CKT 1 | CP | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 13WP | 105.2 | 105.2 |  |  | 87.989 | 101.2876 | [7 empty] | CATEGORYB | SINGLE | NORTH JUDSON LARGE SUB - SPEARVILLE 115KV CKT 1 | 0 | 539694 | SPEARVL3 115.00 | 539771 | NOR-JUD3 115.00 | 0 |  | 1 | 106.5546 |  | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 | [50 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T4763313WP | FROM->TO | FLATRDG3 138.00 - HARPER 138KV CKT 1 | CP | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 13WP | 105.2 | 105.2 |  |  | 87.3571 | 100.3294 | [7 empty] | CATEGORYB | SINGLE | SPEARVILLE (SPEARVL6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539694 | SPEARVL3 115.00 | 539695 | SPEARVL6 230.00 | 539935 | SPERVLTT 13.800 | 1 | 105.5465 |  | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 | [50 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 1 | 2008AGP1AFS31T41118SP | TO->FROM | FIXICO TAP - MAUD 138KV CKT 1 | S | OKGE | AEPW | SHAWNEE | EASTERN | 0 | 515055 | MAUD 4 138.00 | 510877 | FIXCT4 138.00 | 0 |  | 1 | 18SP | 88 | 107 |  | 103 | 104.8261 | 106.9894 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | 114.4787 |  | OKGE | FIXICO TAP - MAUD 138KV CKT 1 OKGE Displacement | Build another 1.43 mile line from Fixico to the location of Fixico Tap and install dead end structures in the area of Fixico Tap. Install another breaker in Fixico and remove Fixico Tap. This will loop the 138kV line through Fixico and eliminate the tap | 88 | 107 |  |  | 1.43 | 24 | [5 empty] | New line will be Fixico - Maud and Fixico - Weleetka | 2530000 | 2008-10-08 | [38 empty] | 2010-06-01 | 2014-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 1 | 1 | 2008AGP1AFS31T21161118SP | TO->FROM | FIXICO TAP - MAUD 138KV CKT 1 | S | OKGE | AEPW | SHAWNEE | EASTERN | 0 | 515055 | MAUD 4 138.00 | 510877 | FIXCT4 138.00 | 0 |  | 1 | 18SP | 88 | 107 |  | 101.9 | 103.2842 | 105.3479 | [7 empty] | CATEGORYB | SINGLE | MAUD (MAUD1) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 515054 | MAUD 2 69.000 | 515055 | MAUD 4 138.00 | 515736 | MAUD 1 13.200 | 1 | 112.7223 |  | OKGE | FIXICO TAP - MAUD 138KV CKT 1 OKGE Displacement | Build another 1.43 mile line from Fixico to the location of Fixico Tap and install dead end structures in the area of Fixico Tap. Install another breaker in Fixico and remove Fixico Tap. This will loop the 138kV line through Fixico and eliminate the tap | 88 | 107 |  |  | 1.43 | 24 | [5 empty] | New line will be Fixico - Maud and Fixico - Weleetka | 2530000 | 2008-10-08 | [38 empty] | 2010-06-01 | 2014-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 1 | 2008AGP1AFS31T3531118SP | TO->FROM | FIXICO TAP - MAUD 138KV CKT 1 | S | OKGE | AEPW | SHAWNEE | EASTERN | 0 | 515055 | MAUD 4 138.00 | 510877 | FIXCT4 138.00 | 0 |  | 1 | 18SP | 88 | 107 |  |  | 98.3443 | 100.4981 | [7 empty] | CATEGORYB | SINGLE | FOREST HILL - MAUD 138KV CKT 1 | 0 | 515055 | MAUD 4 138.00 | 515075 | FRSTHIL4 138.00 | 0 |  | 1 | 107.533 |  | OKGE | FIXICO TAP - MAUD 138KV CKT 1 OKGE Displacement | Build another 1.43 mile line from Fixico to the location of Fixico Tap and install dead end structures in the area of Fixico Tap. Install another breaker in Fixico and remove Fixico Tap. This will loop the 138kV line through Fixico and eliminate the tap | 88 | 107 |  |  | 1.43 | 24 | [5 empty] | New line will be Fixico - Maud and Fixico - Weleetka | 2530000 | 2008-10-08 | [38 empty] | 2010-06-01 | 2014-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31V17072218SP |  | FIXICO 138KV | REL | OKGE |  | SHAWNEE |  |  | 515078 | FIXICO 4 138.00 | [5 empty] | 18SP | [6 empty] | 0.88996 | 0.88101 | 0.90834 | 0.88133 | 0.98744 | 0.9 | 1.05 | CATEGORYB | NONSINGLE | OGE3TERM36 | 0 | 0 |  | 0 |  | 0 |  |  |  |  | OKGE | EL RENO 69KV CAP BANK | Install 12 Mvar Capacitor at El Reno 69 kV bus | [52 empty] | 2011-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T6234209SP | FROM->TO | FAIRVIEW - MADISONVILLE 230KV CKT 1 | S | EES | CELE | EES_ELL-S | CLE_EAST | 0 | 336138 | 6FAIRVW 230.00 | 500510 | MADISON6 230.00 | 0 |  | 1 | 09SP | 454 | 454 | 122.5 | 121.3 | 118.8514 | 119.1619 | [7 empty] | CATEGORYB | SINGLE | FRONT STREET - MICHOUD 230KV CKT 1 | 0 | 500360 | FRONTST6 230.00 | 336462 | 6MICHO 230.00 | 0 |  | 1 | 540.995 |  | EES | FAIRVIEW - MADISONVILLE 230KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T11924209SP | FROM->TO | FAIRVIEW - MADISONVILLE 230KV CKT 1 | S | EES | CELE | EES_ELL-S | CLE_EAST | 0 | 336138 | 6FAIRVW 230.00 | 500510 | MADISON6 230.00 | 0 |  | 1 | 09SP | 454 | 454 | 122.3 | 120.8 | 117.0864 | 116.9182 | [7 empty] | CATEGORYB | NONSINGLE | CELE-WELLOP1 | 0 | 0 |  | 0 |  | 0 |  |  | 530.8086 |  | EES | FAIRVIEW - MADISONVILLE 230KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T4074209SP | FROM->TO | FAIRVIEW - MADISONVILLE 230KV CKT 1 | S | EES | CELE | EES_ELL-S | CLE_EAST | 0 | 336138 | 6FAIRVW 230.00 | 500510 | MADISON6 230.00 | 0 |  | 1 | 09SP | 454 | 454 | 121.8 | 120.3 | 116.6386 | 116.4726 | [7 empty] | CATEGORYB | SINGLE | FRANKLIN - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 336562 | 8FRKLIN 500.00 | 0 |  | 1 | 528.7856 |  | EES | FAIRVIEW - MADISONVILLE 230KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T3664209SP | FROM->TO | FAIRVIEW - MADISONVILLE 230KV CKT 1 | S | EES | CELE | EES_ELL-S | CLE_EAST | 0 | 336138 | 6FAIRVW 230.00 | 500510 | MADISON6 230.00 | 0 |  | 1 | 09SP | 454 | 454 | 118.7 | 118 | 115.7318 | 115.7702 | [7 empty] | CATEGORYB | SINGLE | 6FRNSTL - SORRENTO 230KV CKT 1 | 0 | 303204 | 6FRNSTL 230.00 | 336060 | 6SORR 2 230.00 | 0 |  | 1 | 525.5967 |  | EES | FAIRVIEW - MADISONVILLE 230KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T9242210SP | FROM->TO | FAIRVIEW - MADISONVILLE 230KV CKT 1 | S | EES | CELE | EES_ELL-S | CLE_EAST | 0 | 336138 | 6FAIRVW 230.00 | 500510 | MADISON6 230.00 | 0 |  | 1 | 10SP | 454 | 454 | 118.1 | 118.4 | 116.3251 | 117.3071 | [7 empty] | CATEGORYB | SINGLE | FRONT STREET - MICHOUD 230KV CKT 1 | 0 | 500360 | FRONTST6 230.00 | 336462 | 6MICHO 230.00 | 0 |  | 1 | 532.5742 |  | EES | FAIRVIEW - MADISONVILLE 230KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T5102210SP | FROM->TO | FAIRVIEW - MADISONVILLE 230KV CKT 1 | S | EES | CELE | EES_ELL-S | CLE_EAST | 0 | 336138 | 6FAIRVW 230.00 | 500510 | MADISON6 230.00 | 0 |  | 1 | 10SP | 454 | 454 | 116.7 | 116.9 | 114.9001 | 115.6369 | [7 empty] | CATEGORYB | SINGLE | 6FRNSTL - SORRENTO 230KV CKT 1 | 0 | 303204 | 6FRNSTL 230.00 | 336060 | 6SORR 2 230.00 | 0 |  | 1 | 524.9915 |  | EES | FAIRVIEW - MADISONVILLE 230KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T16282210SP | FROM->TO | FAIRVIEW - MADISONVILLE 230KV CKT 1 | S | EES | CELE | EES_ELL-S | CLE_EAST | 0 | 336138 | 6FAIRVW 230.00 | 500510 | MADISON6 230.00 | 0 |  | 1 | 10SP | 454 | 454 | 117.3 | 116.9 | 113.4695 | 114.4216 | [7 empty] | CATEGORYB | NONSINGLE | CELE-WELLOP1 | 0 | 0 |  | 0 |  | 0 |  |  | 519.4741 |  | EES | FAIRVIEW - MADISONVILLE 230KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T5562210SP | FROM->TO | FAIRVIEW - MADISONVILLE 230KV CKT 1 | S | EES | CELE | EES_ELL-S | CLE_EAST | 0 | 336138 | 6FAIRVW 230.00 | 500510 | MADISON6 230.00 | 0 |  | 1 | 10SP | 454 | 454 | 116.8 | 116.5 | 113.0499 | 113.9836 | [7 empty] | CATEGORYB | SINGLE | FRANKLIN - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 336562 | 8FRKLIN 500.00 | 0 |  | 1 | 517.4855 |  | EES | FAIRVIEW - MADISONVILLE 230KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T14672213SP | FROM->TO | FAIRVIEW - MADISONVILLE 230KV CKT 1 | S | EES | CELE | EES_ELL-S | CLE_EAST | 0 | 336138 | 6FAIRVW 230.00 | 500510 | MADISON6 230.00 | 0 |  | 1 | 13SP | 454 | 454 | 138.3 | 138.4 | 136.2051 | 136.788 | [7 empty] | CATEGORYB | SINGLE | FRONT STREET - MICHOUD 230KV CKT 1 | 0 | 500360 | FRONTST6 230.00 | 336462 | 6MICHO 230.00 | 0 |  | 1 | 621.0175 |  | EES | FAIRVIEW - MADISONVILLE 230KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T6832213SP | FROM->TO | FAIRVIEW - MADISONVILLE 230KV CKT 1 | S | EES | CELE | EES_ELL-S | CLE_EAST | 0 | 336138 | 6FAIRVW 230.00 | 500510 | MADISON6 230.00 | 0 |  | 1 | 13SP | 454 | 454 | 136.3 | 136.2 | 134.2454 | 134.6114 | [7 empty] | CATEGORYB | SINGLE | 6FRNSTL - SORRENTO 230KV CKT 1 | 0 | 303204 | 6FRNSTL 230.00 | 336060 | 6SORR 2 230.00 | 0 |  | 1 | 611.1358 |  | EES | FAIRVIEW - MADISONVILLE 230KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T14652213SP | FROM->TO | FAIRVIEW - MADISONVILLE 230KV CKT 1 | S | EES | CELE | EES_ELL-S | CLE_EAST | 0 | 336138 | 6FAIRVW 230.00 | 500510 | MADISON6 230.00 | 0 |  | 1 | 13SP | 454 | 454 | 132.4 | 132.6 | 130.3743 | 130.9583 | [7 empty] | CATEGORYB | SINGLE | FRONT STREET - SLIDELL 230KV CKT 1 | 0 | 500360 | FRONTST6 230.00 | 336137 | 6SLIDEL 230.00 | 0 |  | 1 | 594.5507 |  | EES | FAIRVIEW - MADISONVILLE 230KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T8272213SP | FROM->TO | FAIRVIEW - MADISONVILLE 230KV CKT 1 | S | EES | CELE | EES_ELL-S | CLE_EAST | 0 | 336138 | 6FAIRVW 230.00 | 500510 | MADISON6 230.00 | 0 |  | 1 | 13SP | 454 | 454 | 101.4 | 101.5 | 99.9439 | 100.3393 | [7 empty] | CATEGORYB | SINGLE | BAYOU STEEL - LITTLE GYPSY 230KV CKT 1 | 0 | 336190 | 6GYPSY 230.00 | 336192 | 6BAYSTL 230.00 | 0 |  | 1 | 455.5404 |  | EES | FAIRVIEW - MADISONVILLE 230KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T6224209SP | TO->FROM | FAIRVIEW - LITTLE GYPSY 230KV CKT 1 | S | EES | EES | EES_ELL-S | EES_ELL-S | 0 | 336190 | 6GYPSY 230.00 | 336138 | 6FAIRVW 230.00 | 0 |  | 1 | 09SP | 454 | 454 | 123.2 | 121.9 | 119.4827 | 119.7948 | [7 empty] | CATEGORYB | SINGLE | FRONT STREET - MICHOUD 230KV CKT 1 | 0 | 500360 | FRONTST6 230.00 | 336462 | 6MICHO 230.00 | 0 |  | 1 | 543.8684 |  | EES | FAIRVIEW - LITTLE GYPSY 230KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T11914209SP | TO->FROM | FAIRVIEW - LITTLE GYPSY 230KV CKT 1 | S | EES | EES | EES_ELL-S | EES_ELL-S | 0 | 336190 | 6GYPSY 230.00 | 336138 | 6FAIRVW 230.00 | 0 |  | 1 | 09SP | 454 | 454 | 122.9 | 121.4 | 117.7072 | 117.5377 | [7 empty] | CATEGORYB | NONSINGLE | CELE-WELLOP1 | 0 | 0 |  | 0 |  | 0 |  |  | 533.6211 |  | EES | FAIRVIEW - LITTLE GYPSY 230KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T4064209SP | TO->FROM | FAIRVIEW - LITTLE GYPSY 230KV CKT 1 | S | EES | EES | EES_ELL-S | EES_ELL-S | 0 | 336190 | 6GYPSY 230.00 | 336138 | 6FAIRVW 230.00 | 0 |  | 1 | 09SP | 454 | 454 | 122.5 | 121 | 117.2582 | 117.0912 | [7 empty] | CATEGORYB | SINGLE | FRANKLIN - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 336562 | 8FRKLIN 500.00 | 0 |  | 1 | 531.5941 |  | EES | FAIRVIEW - LITTLE GYPSY 230KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T3654209SP | TO->FROM | FAIRVIEW - LITTLE GYPSY 230KV CKT 1 | S | EES | EES | EES_ELL-S | EES_ELL-S | 0 | 336190 | 6GYPSY 230.00 | 336138 | 6FAIRVW 230.00 | 0 |  | 1 | 09SP | 454 | 454 | 119.4 | 118.6 | 116.348 | 116.3865 | [7 empty] | CATEGORYB | SINGLE | 6FRNSTL - SORRENTO 230KV CKT 1 | 0 | 303204 | 6FRNSTL 230.00 | 336060 | 6SORR 2 230.00 | 0 |  | 1 | 528.3947 |  | EES | FAIRVIEW - LITTLE GYPSY 230KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T9232210SP | TO->FROM | FAIRVIEW - LITTLE GYPSY 230KV CKT 1 | S | EES | EES | EES_ELL-S | EES_ELL-S | 0 | 336190 | 6GYPSY 230.00 | 336138 | 6FAIRVW 230.00 | 0 |  | 1 | 10SP | 454 | 454 | 118.7 | 119.1 | 116.9428 | 117.9301 | [7 empty] | CATEGORYB | SINGLE | FRONT STREET - MICHOUD 230KV CKT 1 | 0 | 500360 | FRONTST6 230.00 | 336462 | 6MICHO 230.00 | 0 |  | 1 | 535.4027 |  | EES | FAIRVIEW - LITTLE GYPSY 230KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T5092210SP | TO->FROM | FAIRVIEW - LITTLE GYPSY 230KV CKT 1 | S | EES | EES | EES_ELL-S | EES_ELL-S | 0 | 336190 | 6GYPSY 230.00 | 336138 | 6FAIRVW 230.00 | 0 |  | 1 | 10SP | 454 | 454 | 117.3 | 117.5 | 115.507 | 116.2479 | [7 empty] | CATEGORYB | SINGLE | 6FRNSTL - SORRENTO 230KV CKT 1 | 0 | 303204 | 6FRNSTL 230.00 | 336060 | 6SORR 2 230.00 | 0 |  | 1 | 527.7655 |  | EES | FAIRVIEW - LITTLE GYPSY 230KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T16272210SP | TO->FROM | FAIRVIEW - LITTLE GYPSY 230KV CKT 1 | S | EES | EES | EES_ELL-S | EES_ELL-S | 0 | 336190 | 6GYPSY 230.00 | 336138 | 6FAIRVW 230.00 | 0 |  | 1 | 10SP | 454 | 454 | 117.9 | 117.5 | 114.0729 | 115.0303 | [7 empty] | CATEGORYB | NONSINGLE | CELE-WELLOP1 | 0 | 0 |  | 0 |  | 0 |  |  | 522.2375 |  | EES | FAIRVIEW - LITTLE GYPSY 230KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T5552210SP | TO->FROM | FAIRVIEW - LITTLE GYPSY 230KV CKT 1 | S | EES | EES | EES_ELL-S | EES_ELL-S | 0 | 336190 | 6GYPSY 230.00 | 336138 | 6FAIRVW 230.00 | 0 |  | 1 | 10SP | 454 | 454 | 117.5 | 117.1 | 113.6502 | 114.5889 | [7 empty] | CATEGORYB | SINGLE | FRANKLIN - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 336562 | 8FRKLIN 500.00 | 0 |  | 1 | 520.2336 |  | EES | FAIRVIEW - LITTLE GYPSY 230KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T14662213SP | TO->FROM | FAIRVIEW - LITTLE GYPSY 230KV CKT 1 | S | EES | EES | EES_ELL-S | EES_ELL-S | 0 | 336190 | 6GYPSY 230.00 | 336138 | 6FAIRVW 230.00 | 0 |  | 1 | 13SP | 454 | 454 | 139.0 | 139.1 | 136.9304 | 137.5165 | [7 empty] | CATEGORYB | SINGLE | FRONT STREET - MICHOUD 230KV CKT 1 | 0 | 500360 | FRONTST6 230.00 | 336462 | 6MICHO 230.00 | 0 |  | 1 | 624.3249 |  | EES | FAIRVIEW - LITTLE GYPSY 230KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T6812213SP | TO->FROM | FAIRVIEW - LITTLE GYPSY 230KV CKT 1 | S | EES | EES | EES_ELL-S | EES_ELL-S | 0 | 336190 | 6GYPSY 230.00 | 336138 | 6FAIRVW 230.00 | 0 |  | 1 | 13SP | 454 | 454 | 137.0 | 137 | 134.9903 | 135.3595 | [7 empty] | CATEGORYB | SINGLE | 6FRNSTL - SORRENTO 230KV CKT 1 | 0 | 303204 | 6FRNSTL 230.00 | 336060 | 6SORR 2 230.00 | 0 |  | 1 | 614.5321 |  | EES | FAIRVIEW - LITTLE GYPSY 230KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T14642213SP | TO->FROM | FAIRVIEW - LITTLE GYPSY 230KV CKT 1 | S | EES | EES | EES_ELL-S | EES_ELL-S | 0 | 336190 | 6GYPSY 230.00 | 336138 | 6FAIRVW 230.00 | 0 |  | 1 | 13SP | 454 | 454 | 133.1 | 133.3 | 131.0671 | 131.6542 | [7 empty] | CATEGORYB | SINGLE | FRONT STREET - SLIDELL 230KV CKT 1 | 0 | 500360 | FRONTST6 230.00 | 336137 | 6SLIDEL 230.00 | 0 |  | 1 | 597.7101 |  | EES | FAIRVIEW - LITTLE GYPSY 230KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 3 | 2008AGP1AFS31T704309FA | TO->FROM | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533368 | EXIDE J3 115.00 | 0 |  | 1 | 09FA | 181 | 196 | 100.3 | 103.8 | 105.8246 | 108.3247 | [7 empty] | CATEGORYB | SINGLE | NORTHVIEW - SUMMIT 115KV CKT 1 | 0 | 533371 | NORTHVW3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 | 212.3164 |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [52 empty] | 2009-04-01 | 2009-12-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T574209FA | TO->FROM | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533368 | EXIDE J3 115.00 | 0 |  | 1 | 09FA | 181 | 196 |  |  | 97.4257 | 100.6597 | [7 empty] | CATEGORYB | SINGLE | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 0 | 532872 | EMCPHER6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 197.293 |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [52 empty] | 2009-04-01 | 2009-12-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 2 | 2008AGP1AFS31T1671209G | TO->FROM | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533368 | EXIDE J3 115.00 | 0 |  | 1 | 09G | 181 | 196 |  |  | 101.8173 | 104.3959 | [7 empty] | CATEGORYB | SINGLE | NORTHVIEW - SUMMIT 115KV CKT 1 | 0 | 533371 | NORTHVW3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 | 204.616 |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [52 empty] | 2009-04-01 | 2009-12-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T1644209G | TO->FROM | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533368 | EXIDE J3 115.00 | 0 |  | 1 | 09G | 181 | 196 |  |  | 97.8301 | 101.6511 | [7 empty] | CATEGORYB | SINGLE | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 0 | 532872 | EMCPHER6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 199.2362 |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [52 empty] | 2009-04-01 | 2009-12-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T1984209SH | TO->FROM | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533368 | EXIDE J3 115.00 | 0 |  | 1 | 09SH | 181 | 196 | 107.4 | 108.5 | 110.6444 | 113.2769 | [7 empty] | CATEGORYB | SINGLE | NORTHVIEW - SUMMIT 115KV CKT 1 | 0 | 533371 | NORTHVW3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 | 222.0227 |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [52 empty] | 2009-04-01 | 2009-12-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T1784209SH | TO->FROM | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533368 | EXIDE J3 115.00 | 0 |  | 1 | 09SH | 181 | 196 |  |  | 98.8252 | 102.4105 | [7 empty] | CATEGORYB | SINGLE | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 0 | 532872 | EMCPHER6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 200.7246 |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [52 empty] | 2009-04-01 | 2009-12-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 2 | 2008AGP1AFS31T2483209SP | TO->FROM | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533368 | EXIDE J3 115.00 | 0 |  | 1 | 09SP | 181 | 196 | 123.0 | 124.8 | 125.8167 | 128.0348 | [7 empty] | CATEGORYB | SINGLE | NORTHVIEW - SUMMIT 115KV CKT 1 | 0 | 533371 | NORTHVW3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 | 250.9482 |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [52 empty] | 2009-04-01 | 2009-12-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T2464209SP | TO->FROM | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533368 | EXIDE J3 115.00 | 0 |  | 1 | 09SP | 181 | 196 | 103.0 | 105.4 | 106.82 | 110.6951 | [7 empty] | CATEGORYB | SINGLE | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 0 | 532872 | EMCPHER6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 216.9624 |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [52 empty] | 2009-04-01 | 2009-12-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T8444209SP | TO->FROM | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533381 | SUMMIT 3 115.00 | 533368 | EXIDE J3 115.00 | 0 |  | 1 | 09SP | 181 | 196 |  | 101.3 | 101.6047 | 104.0593 | [7 empty] | CATEGORYB | SINGLE | EAST MCPHERSON (EMCPHR1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532872 | EMCPHER6 230.00 | 533417 | EMCPHER3 115.00 | 532894 | EMCPHER1 13.800 | 1 | 203.9562 |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [52 empty] | 2009-04-01 | 2009-12-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 3 | 2008AGP1AFS31T694309FA | FROM->TO | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533368 | EXIDE J3 115.00 | 533372 | PHILIPS3 115.00 | 0 |  | 1 | 09FA | 181 | 196 |  |  | 99.942 | 102.441 | [7 empty] | CATEGORYB | SINGLE | NORTHVIEW - SUMMIT 115KV CKT 1 | 0 | 533371 | NORTHVW3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 | 200.7844 |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [52 empty] | 2009-04-01 | 2009-12-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T1974209SH | FROM->TO | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533368 | EXIDE J3 115.00 | 533372 | PHILIPS3 115.00 | 0 |  | 1 | 09SH | 181 | 196 | 101.9 | 103 | 105.1386 | 107.771 | [7 empty] | CATEGORYB | SINGLE | NORTHVIEW - SUMMIT 115KV CKT 1 | 0 | 533371 | NORTHVW3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 | 211.2312 |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [52 empty] | 2009-04-01 | 2009-12-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T2754209SP | FROM->TO | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533368 | EXIDE J3 115.00 | 533372 | PHILIPS3 115.00 | 0 |  | 1 | 09SP | 181 | 196 | 117.4 | 119.1 | 119.6659 | 122.3842 | [7 empty] | CATEGORYB | SINGLE | NORTHVIEW - SUMMIT 115KV CKT 1 | 0 | 533371 | NORTHVW3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 | 239.873 |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [52 empty] | 2009-04-01 | 2009-12-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T2454209SP | FROM->TO | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | EXP | WERE | WERE | WEST | WEST | 0 | 533368 | EXIDE J3 115.00 | 533372 | PHILIPS3 115.00 | 0 |  | 1 | 09SP | 181 | 196 |  | 100 | 101.4095 | 105.2704 | [7 empty] | CATEGORYB | SINGLE | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 0 | 532872 | EMCPHER6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 206.33 |  | WERE | Summit - NE Saline 115 kV | Build 6.5-mile Summit-Southgate 115 kV, 1192.5 kcmil ACSR Tear down Northview-South Gate 115 kV | [52 empty] | 2009-04-01 | 2009-12-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T6624209SP | FROM->TO | EVERTON - HARRISON-EAST 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 338107 | 5EVRTON 161.00 | 338104 | 5HARR-E 161.00 | 0 |  | 1 | 09SP | 167 | 167 | 100.4 | 107.7 | 105.5711 | 101.8814 | [7 empty] | CATEGORYB | SINGLE | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 170.1419 |  | EES | EVERTON - HARRISON-EAST 161KV CKT 1 | Replace switches @ Harrison East | [12 empty] | 200000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T5254209SP | FROM->TO | EVERTON - HARRISON-EAST 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 338107 | 5EVRTON 161.00 | 338104 | 5HARR-E 161.00 | 0 |  | 1 | 09SP | 167 | 167 |  | 106.3 | 104.1421 | 100.4608 | [7 empty] | CATEGORYB | SINGLE | BULL SHOALS HES - FLIPPIN 161KV CKT 1 | 0 | 338122 | 5FLIPN 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 167.7695 |  | EES | EVERTON - HARRISON-EAST 161KV CKT 1 | Replace switches @ Harrison East | [12 empty] | 200000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T3804209WP | FROM->TO | EVERTON - HARRISON-EAST 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 338107 | 5EVRTON 161.00 | 338104 | 5HARR-E 161.00 | 0 |  | 1 | 09WP | 167 | 167 |  | 104 | 102.9659 | 103.5247 | [7 empty] | CATEGORYB | SINGLE | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 172.8862 |  | EES | EVERTON - HARRISON-EAST 161KV CKT 1 | Replace switches @ Harrison East | [12 empty] | 200000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T3084209WP | FROM->TO | EVERTON - HARRISON-EAST 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 338107 | 5EVRTON 161.00 | 338104 | 5HARR-E 161.00 | 0 |  | 1 | 09WP | 167 | 167 |  | 102.9 | 101.8693 | 102.4278 | [7 empty] | CATEGORYB | SINGLE | BULL SHOALS HES - FLIPPIN 161KV CKT 1 | 0 | 338122 | 5FLIPN 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 171.0544 |  | EES | EVERTON - HARRISON-EAST 161KV CKT 1 | Replace switches @ Harrison East | [12 empty] | 200000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T9862210SP | FROM->TO | EVERTON - HARRISON-EAST 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 338107 | 5EVRTON 161.00 | 338104 | 5HARR-E 161.00 | 0 |  | 1 | 10SP | 167 | 167 | 105.9 | 118.9 | 119.3746 | 116.6768 | [7 empty] | CATEGORYB | SINGLE | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 194.8503 |  | EES | EVERTON - HARRISON-EAST 161KV CKT 1 | Replace switches @ Harrison East | [12 empty] | 200000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T7472210SP | FROM->TO | EVERTON - HARRISON-EAST 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 338107 | 5EVRTON 161.00 | 338104 | 5HARR-E 161.00 | 0 |  | 1 | 10SP | 167 | 167 | 104.5 | 117.5 | 117.9199 | 115.2206 | [7 empty] | CATEGORYB | SINGLE | BULL SHOALS HES - FLIPPIN 161KV CKT 1 | 0 | 338122 | 5FLIPN 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 192.4184 |  | EES | EVERTON - HARRISON-EAST 161KV CKT 1 | Replace switches @ Harrison East | [12 empty] | 200000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T7452210SP | FROM->TO | EVERTON - HARRISON-EAST 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 338107 | 5EVRTON 161.00 | 338104 | 5HARR-E 161.00 | 0 |  | 1 | 10SP | 167 | 167 | 101.0 | 114.1 | 114.533 | 111.8444 | [7 empty] | CATEGORYB | SINGLE | FLIPPIN - SUMMIT 161KV CKT 1 | 0 | 338121 | 5SUMMIT 161.00 | 338122 | 5FLIPN 161.00 | 0 |  | 1 | 186.7801 |  | EES | EVERTON - HARRISON-EAST 161KV CKT 1 | Replace switches @ Harrison East | [12 empty] | 200000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T6074210WP | FROM->TO | EVERTON - HARRISON-EAST 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 338107 | 5EVRTON 161.00 | 338104 | 5HARR-E 161.00 | 0 |  | 1 | 10WP | 167 | 167 | 105.6 | 118.1 | 117.128 | 113.9806 | [7 empty] | CATEGORYB | SINGLE | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 190.3476 |  | EES | EVERTON - HARRISON-EAST 161KV CKT 1 | Replace switches @ Harrison East | [12 empty] | 200000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T4614210WP | FROM->TO | EVERTON - HARRISON-EAST 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 338107 | 5EVRTON 161.00 | 338104 | 5HARR-E 161.00 | 0 |  | 1 | 10WP | 167 | 167 | 104.5 | 117 | 116.0269 | 112.8795 | [7 empty] | CATEGORYB | SINGLE | BULL SHOALS HES - FLIPPIN 161KV CKT 1 | 0 | 338122 | 5FLIPN 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 188.5088 |  | EES | EVERTON - HARRISON-EAST 161KV CKT 1 | Replace switches @ Harrison East | [12 empty] | 200000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T4564210WP | FROM->TO | EVERTON - HARRISON-EAST 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 338107 | 5EVRTON 161.00 | 338104 | 5HARR-E 161.00 | 0 |  | 1 | 10WP | 167 | 167 | 101.9 | 114.5 | 113.4738 | 110.3251 | [7 empty] | CATEGORYB | SINGLE | FLIPPIN - SUMMIT 161KV CKT 1 | 0 | 338121 | 5SUMMIT 161.00 | 338122 | 5FLIPN 161.00 | 0 |  | 1 | 184.2429 |  | EES | EVERTON - HARRISON-EAST 161KV CKT 1 | Replace switches @ Harrison East | [12 empty] | 200000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T15852213SP | FROM->TO | EVERTON - HARRISON-EAST 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 338107 | 5EVRTON 161.00 | 338104 | 5HARR-E 161.00 | 0 |  | 1 | 13SP | 167 | 167 | 111.7 | 124.4 | 124.7072 | 120.9023 | [7 empty] | CATEGORYB | SINGLE | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 201.9068 |  | EES | EVERTON - HARRISON-EAST 161KV CKT 1 | Replace switches @ Harrison East | [12 empty] | 200000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T11682213SP | FROM->TO | EVERTON - HARRISON-EAST 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 338107 | 5EVRTON 161.00 | 338104 | 5HARR-E 161.00 | 0 |  | 1 | 13SP | 167 | 167 | 110.1 | 122.9 | 123.165 | 119.3559 | [7 empty] | CATEGORYB | SINGLE | BULL SHOALS HES - FLIPPIN 161KV CKT 1 | 0 | 338122 | 5FLIPN 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 199.3244 |  | EES | EVERTON - HARRISON-EAST 161KV CKT 1 | Replace switches @ Harrison East | [12 empty] | 200000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T11652213SP | FROM->TO | EVERTON - HARRISON-EAST 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 338107 | 5EVRTON 161.00 | 338104 | 5HARR-E 161.00 | 0 |  | 1 | 13SP | 167 | 167 | 106.3 | 119.1 | 119.3352 | 115.5136 | [7 empty] | CATEGORYB | SINGLE | FLIPPIN - SUMMIT 161KV CKT 1 | 0 | 338121 | 5SUMMIT 161.00 | 338122 | 5FLIPN 161.00 | 0 |  | 1 | 192.9077 |  | EES | EVERTON - HARRISON-EAST 161KV CKT 1 | Replace switches @ Harrison East | [12 empty] | 200000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T5634213WP | FROM->TO | EVERTON - HARRISON-EAST 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 338107 | 5EVRTON 161.00 | 338104 | 5HARR-E 161.00 | 0 |  | 1 | 13WP | 167 | 167 | 103.0 | 114.6 | 113.4431 | 111.8353 | [7 empty] | CATEGORYB | SINGLE | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 186.7649 |  | EES | EVERTON - HARRISON-EAST 161KV CKT 1 | Replace switches @ Harrison East | [12 empty] | 200000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T3914213WP | FROM->TO | EVERTON - HARRISON-EAST 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 338107 | 5EVRTON 161.00 | 338104 | 5HARR-E 161.00 | 0 |  | 1 | 13WP | 167 | 167 | 101.8 | 113.4 | 112.3016 | 110.6801 | [7 empty] | CATEGORYB | SINGLE | BULL SHOALS HES - FLIPPIN 161KV CKT 1 | 0 | 338122 | 5FLIPN 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 184.8358 |  | EES | EVERTON - HARRISON-EAST 161KV CKT 1 | Replace switches @ Harrison East | [12 empty] | 200000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T3884213WP | FROM->TO | EVERTON - HARRISON-EAST 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 338107 | 5EVRTON 161.00 | 338104 | 5HARR-E 161.00 | 0 |  | 1 | 13WP | 167 | 167 |  | 110.5 | 109.4237 | 107.7848 | [7 empty] | CATEGORYB | SINGLE | FLIPPIN - SUMMIT 161KV CKT 1 | 0 | 338121 | 5SUMMIT 161.00 | 338122 | 5FLIPN 161.00 | 0 |  | 1 | 180.0006 |  | EES | EVERTON - HARRISON-EAST 161KV CKT 1 | Replace switches @ Harrison East | [12 empty] | 200000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T26752218SP | FROM->TO | EVERTON - HARRISON-EAST 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 338107 | 5EVRTON 161.00 | 338104 | 5HARR-E 161.00 | 0 |  | 1 | 18SP | 167 | 167 |  | 105.1 | 105.5668 | 100.5597 | [7 empty] | CATEGORYB | SINGLE | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 167.9347 |  | EES | EVERTON - HARRISON-EAST 161KV CKT 1 | Replace switches @ Harrison East | [12 empty] | 200000 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 | 5238 - EUFXFRWELXFR | FDNS |  | FDNS |  | 3 | 2 | 2008AGP1AFS31T3753209WP | FROM->TO | EUFAULA (EUFAULA1) 161/138/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505570 | EUFAULA5 161.00 | 505574 | EUFAULA4 138.00 | 505576 | EUF #1 1 13.800 | 1 | 09WP | 105 | 105 | 117.9 | 122.1 | 126.6634 | 124.0009 | [7 empty] | CATEGORYB | SINGLE | WELEETKA (WLK X1) 161/138/13.8KV TRANSFORMER CKT 1 | 1 | 505590 | WELEETK5 161.00 | 505592 | WELEETK4 138.00 | 505591 | WLK X1 1 13.800 | 1 | 130.2009 |  | SWPA | EUFAULA (EUFAULA1) 161/138/13.8KV TRANSFORMER CKT 1 | Replace Eufaula Transformer | 200 | 200 | 200 | 200 |  | 18 | 2 | [5 empty] | 3000000 | [39 empty] | 2009-12-01 | 2009-12-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 2 | 2008AGP1AFS31T443209WP | FROM->TO | EUFAULA (EUFAULA1) 161/138/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505570 | EUFAULA5 161.00 | 505574 | EUFAULA4 138.00 | 505576 | EUF #1 1 13.800 | 1 | 09WP | 105 | 105 | 117.7 | 121.9 | 126.3741 | 123.8211 | [7 empty] | CATEGORYB | SINGLE | GORE - WELEETKA 161KV CKT 1 | 0 | 505552 | GORE 5 161.00 | 505590 | WELEETK5 161.00 | 0 |  | 1 | 130.0122 |  | SWPA | EUFAULA (EUFAULA1) 161/138/13.8KV TRANSFORMER CKT 1 | Replace Eufaula Transformer | 200 | 200 | 200 | 200 |  | 18 | 2 | [5 empty] | 3000000 | [39 empty] | 2009-12-01 | 2009-12-01
2008-AGP1 | AFS3 | 5238 - EUFXFRWELXFR | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T6722210WP | FROM->TO | EUFAULA (EUFAULA1) 161/138/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505570 | EUFAULA5 161.00 | 505574 | EUFAULA4 138.00 | 505576 | EUF #1 1 13.800 | 1 | 10WP | 105 | 105 | 120.0 | 123.7 | 125.7091 | 122.3372 | [7 empty] | CATEGORYB | SINGLE | WELEETKA (WLK X1) 161/138/13.8KV TRANSFORMER CKT 1 | 1 | 505590 | WELEETK5 161.00 | 505592 | WELEETK4 138.00 | 505591 | WLK X1 1 13.800 | 1 | 128.4541 |  | SWPA | EUFAULA (EUFAULA1) 161/138/13.8KV TRANSFORMER CKT 1 | Replace Eufaula Transformer | 200 | 200 | 200 | 200 |  | 18 | 2 | [5 empty] | 3000000 | [39 empty] | 2009-12-01 | 2009-12-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T612210WP | FROM->TO | EUFAULA (EUFAULA1) 161/138/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505570 | EUFAULA5 161.00 | 505574 | EUFAULA4 138.00 | 505576 | EUF #1 1 13.800 | 1 | 10WP | 105 | 105 | 119.7 | 123.5 | 125.4225 | 122.0831 | [7 empty] | CATEGORYB | SINGLE | GORE - WELEETKA 161KV CKT 1 | 0 | 505552 | GORE 5 161.00 | 505590 | WELEETK5 161.00 | 0 |  | 1 | 128.1873 |  | SWPA | EUFAULA (EUFAULA1) 161/138/13.8KV TRANSFORMER CKT 1 | Replace Eufaula Transformer | 200 | 200 | 200 | 200 |  | 18 | 2 | [5 empty] | 3000000 | [39 empty] | 2009-12-01 | 2009-12-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T11122210WP | FROM->TO | EUFAULA (EUFAULA1) 161/138/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505570 | EUFAULA5 161.00 | 505574 | EUFAULA4 138.00 | 505576 | EUF #1 1 13.800 | 1 | 10WP | 105 | 105 | 115.8 | 119.9 | 121.3693 | 117.3209 | [7 empty] | CATEGORYB | NONSINGLE | OGE3TERM44 | 0 | 0 |  | 0 |  | 0 |  |  | 123.1869 |  | SWPA | EUFAULA (EUFAULA1) 161/138/13.8KV TRANSFORMER CKT 1 | Replace Eufaula Transformer | 200 | 200 | 200 | 200 |  | 18 | 2 | [5 empty] | 3000000 | [39 empty] | 2009-12-01 | 2009-12-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T1142210WP | FROM->TO | EUFAULA (EUFAULA1) 161/138/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505570 | EUFAULA5 161.00 | 505574 | EUFAULA4 138.00 | 505576 | EUF #1 1 13.800 | 1 | 10WP | 105 | 105 | 115.7 | 119.9 | 121.2959 | 117.2828 | [7 empty] | CATEGORYB | SINGLE | HOWE INT - WISTER 69KV CKT 1 | 0 | 510878 | WISTER-2 69.000 | 515259 | HOWEIN 2 69.000 | 0 |  | 1 | 123.1469 |  | SWPA | EUFAULA (EUFAULA1) 161/138/13.8KV TRANSFORMER CKT 1 | Replace Eufaula Transformer | 200 | 200 | 200 | 200 |  | 18 | 2 | [5 empty] | 3000000 | [39 empty] | 2009-12-01 | 2009-12-01
2008-AGP1 | AFS3 | CONT-Okmulgee - Weleetka Operating Procedure | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T1202210WP | FROM->TO | EUFAULA (EUFAULA1) 161/138/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505570 | EUFAULA5 161.00 | 505574 | EUFAULA4 138.00 | 505576 | EUF #1 1 13.800 | 1 | 10WP | 105 | 105 | 104.8 | 107.2 | 108.5488 | 106.2614 | [7 empty] | CATEGORYB | SINGLE | KELCO - OKMULGEE 138KV CKT 1 | 0 | 510898 | OKMULGE4 138.00 | 510931 | KELCO 4 138.00 | 0 |  | 1 | 111.5745 |  | SWPA | EUFAULA (EUFAULA1) 161/138/13.8KV TRANSFORMER CKT 1 | Replace Eufaula Transformer | 200 | 200 | 200 | 200 |  | 18 | 2 | [5 empty] | 3000000 | [39 empty] | 2009-12-01 | 2009-12-01
2008-AGP1 | AFS3 | CONT-TOD Dolett OP Guide | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T282210WP | FROM->TO | EUFAULA (EUFAULA1) 161/138/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505570 | EUFAULA5 161.00 | 505574 | EUFAULA4 138.00 | 505576 | EUF #1 1 13.800 | 1 | 10WP | 105 | 105 | 104.3 | 107.2 | 108.313 | 105.759 | [7 empty] | CATEGORYB | SINGLE | DOLET HILLS - SOUTHWEST SHREVEPORT 345KV CKT 1 | 0 | 500250 | DOLHILL7 345.00 | 507760 | SW SHV 7 345.00 | 0 |  | 1 | 111.047 |  | SWPA | EUFAULA (EUFAULA1) 161/138/13.8KV TRANSFORMER CKT 1 | Replace Eufaula Transformer | 200 | 200 | 200 | 200 |  | 18 | 2 | [5 empty] | 3000000 | [39 empty] | 2009-12-01 | 2009-12-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T62210WP | FROM->TO | EUFAULA (EUFAULA1) 161/138/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505570 | EUFAULA5 161.00 | 505574 | EUFAULA4 138.00 | 505576 | EUF #1 1 13.800 | 1 | 10WP | 105 | 105 | 100.7 | 103.9 | 105.3061 | 102.4906 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | 107.6151 |  | SWPA | EUFAULA (EUFAULA1) 161/138/13.8KV TRANSFORMER CKT 1 | Replace Eufaula Transformer | 200 | 200 | 200 | 200 |  | 18 | 2 | [5 empty] | 3000000 | [39 empty] | 2009-12-01 | 2009-12-01
2008-AGP1 | AFS3 | 5238 - EUFXFRWELXFR | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T6312213WP | FROM->TO | EUFAULA (EUFAULA1) 161/138/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505570 | EUFAULA5 161.00 | 505574 | EUFAULA4 138.00 | 505576 | EUF #1 1 13.800 | 1 | 13WP | 105 | 105 | 117.3 | 118.2 | 121.7585 | 118.5992 | [7 empty] | CATEGORYB | SINGLE | WELEETKA (WLK X1) 161/138/13.8KV TRANSFORMER CKT 1 | 1 | 505590 | WELEETK5 161.00 | 505592 | WELEETK4 138.00 | 505591 | WLK X1 1 13.800 | 1 | 124.5292 |  | SWPA | EUFAULA (EUFAULA1) 161/138/13.8KV TRANSFORMER CKT 1 | Replace Eufaula Transformer | 200 | 200 | 200 | 200 |  | 18 | 2 | [5 empty] | 3000000 | [39 empty] | 2009-12-01 | 2009-12-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T822213WP | FROM->TO | EUFAULA (EUFAULA1) 161/138/13.8KV TRANSFORMER CKT 1 | REL | SWPA |  | EMINTH |  | 2 | 505570 | EUFAULA5 161.00 | 505574 | EUFAULA4 138.00 | 505576 | EUF #1 1 13.800 | 1 | 13WP | 105 | 105 | 117.0 | 118 | 121.5216 | 118.3626 | [7 empty] | CATEGORYB | SINGLE | GORE - WELEETKA 161KV CKT 1 | 0 | 505552 | GORE 5 161.00 | 505590 | WELEETK5 161.00 | 0 |  | 1 | 124.2807 |  | SWPA | EUFAULA (EUFAULA1) 161/138/13.8KV TRANSFORMER CKT 1 | Replace Eufaula Transformer | 200 | 200 | 200 | 200 |  | 18 | 2 | [5 empty] | 3000000 | [39 empty] | 2009-12-01 | 2009-12-01
GEN-2001-024 | Mattison | [7 empty] | 506957504010012SP | TO->FROM | ELMSPRGS 5 161.00 - TONTITOWN 161KV CKT 1 | U | AEPW | AEPW | FAYETTEV | FAYTAECC | 0 | 506957 | TONTITN5 161.00 | 504010 | ELMSPRGS 5 161.00 | 0 |  | 1 |  | 451 | 592 |  |  | 362.25 | [9 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | AEPW | ELMSPRGS 5 161.00 - TONTITOWN 161KV CKT 1 | Add one 161KV terminal for Tontitown | [12 empty] | 537700 | [39 empty] | 2008-06-01 | 2008-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V8515513SP |  | EL RENO 69KV | REL | OKGE |  |  |  |  | 514818 | ELRENO 2 69.000 | [5 empty] | 13SP | [8 empty] | 0.90584 | 0.86982 | 0.98845 | 0.9 | 1.05 | CATEGORYB | SINGLE | EL RENO (ELRENO5) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 514819 | EL-RENO4 138.00 | 514818 | ELRENO 2 69.000 | 515722 | EL RENO1 13.200 | 1 |  |  | OKGE | EL RENO 69KV CAP BANK | Install 12 Mvar Capacitor at El Reno 69 kV bus | [52 empty] | 2011-06-01 | 2011-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 4 | 1 | 2008AGP1AFS31V10914118SP |  | EL RENO 69KV | REL | OKGE |  |  |  |  | 514818 | ELRENO 2 69.000 | [5 empty] | 18SP | [6 empty] | 0.88726 | 0.8913 | 0.86135 | 0.83949 | 0.98197 | 0.9 | 1.05 | CATEGORYB | SINGLE | EL RENO (ELRENO5) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 514819 | EL-RENO4 138.00 | 514818 | ELRENO 2 69.000 | 515722 | EL RENO1 13.200 | 1 |  |  | OKGE | EL RENO 69KV CAP BANK | Install 12 Mvar Capacitor at El Reno 69 kV bus | [52 empty] | 2011-06-01 | 2011-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 1 | 1 | 2008AGP1AFS31T21321118SP | FROM->TO | EL RENO - OKARCHE 69KV CKT 1 | S | OKGE | OKGE |  |  | 0 | 514818 | ELRENO 2 69.000 | 514811 | OKARCHE2 69.000 | 0 |  | 1 | 18SP | 48 | 48 |  |  | 106.9825 | 116.2774 | [7 empty] | CATEGORYB | SINGLE | DOVER SW (DOVER) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 520881 | DOVERSW2 69.000 | 520882 | DOVERSW4 138.00 | 521166 | DVRTERT 13.800 | 1 | 55.8132 |  | OKGE | EL RENO - OKARCHE 69KV CKT 1 | Increase CTR and possible relay upgrade | 67 | 76 | 86 | 93 |  | 14 | 8 |  |  |  |  | Increase CTR and change out line relays at El Reno. The new Summer Rate A would be 67MVA, Rate B 76MVA. The new winter Rate A would be 86MVA, Rate B 93MVA. Estimated cost $400,000. | 250000 | 2008-07-30 | [38 empty] | 2015-06-01 | 2015-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 4 | 2008AGP1AFS31T963410WP | TO->FROM | ECKLES - SIBLEYPL 161.00 161KV CKT 1 | S | MIPU | INDN |  | INDN | 0 | 541250 | SIBLEYPL 161.00 | 548808 | ECKLES-161 161.00 | 0 |  | 1 | 10WP | 251 | 276 |  |  | 97.8555 | 102.5558 | [7 empty] | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEYPL 161.00 161KV CKT 1 | 0 | 541235 | DUNCAN 5 161.00 | 541250 | SIBLEYPL 161.00 | 0 |  | 1 | 283.054 | Eckles to Sibley loading is under further investigation. Potential for operations guide. | INDN | ECKLES - SIBLEYPL 161.00 161KV CKT 1 | Reconductor |  |  |  |  | 3.09 | 12 | 12 | [5 empty] | 3500000 | [39 empty] | 2010-12-01 | 2011-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 1 | 2008AGP1AFS31T851110WP | TO->FROM | ECKLES - SIBLEYPL 161.00 161KV CKT 1 | S | MIPU | INDN |  | INDN | 0 | 541250 | SIBLEYPL 161.00 | 548808 | ECKLES-161 161.00 | 0 |  | 1 | 10WP | 251 | 276 |  |  | 96.5431 | 101.365 | [7 empty] | CATEGORYB | SINGLE | BIRMINGHAM - HAWTHORN 161KV CKT 1 | 0 | 542973 | HAWTHRN5 161.00 | 543020 | BRMGHAM5 161.00 | 0 |  | 1 | 279.7674 | Eckles to Sibley loading is under further investigation. Potential for operations guide. | INDN | ECKLES - SIBLEYPL 161.00 161KV CKT 1 | Reconductor |  |  |  |  | 3.09 | 12 | 12 | [5 empty] | 3500000 | [39 empty] | 2010-12-01 | 2011-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 1 | 2008AGP1AFS31T1393113WP | TO->FROM | ECKLES - SIBLEYPL 161.00 161KV CKT 1 | S | MIPU | INDN |  | INDN | 0 | 541250 | SIBLEYPL 161.00 | 548808 | ECKLES-161 161.00 | 0 |  | 1 | 13WP | 251 | 276 |  |  | 101.1127 | 106.2652 | [7 empty] | CATEGORYB | SINGLE | BIRMINGHAM - HAWTHORN 161KV CKT 1 | 0 | 542973 | HAWTHRN5 161.00 | 543020 | BRMGHAM5 161.00 | 0 |  | 1 | 293.2919 | Eckles to Sibley loading is under further investigation. Potential for operations guide. | INDN | ECKLES - SIBLEYPL 161.00 161KV CKT 1 | Reconductor |  |  |  |  | 3.09 | 12 | 12 | [5 empty] | 3500000 | [39 empty] | 2010-12-01 | 2011-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 1 | 2008AGP1AFS31T1363113WP | TO->FROM | ECKLES - SIBLEYPL 161.00 161KV CKT 1 | S | MIPU | INDN |  | INDN | 0 | 541250 | SIBLEYPL 161.00 | 548808 | ECKLES-161 161.00 | 0 |  | 1 | 13WP | 251 | 276 |  | 100.8 | 101.8494 | 105.9156 | [7 empty] | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEYPL 161.00 161KV CKT 1 | 0 | 541235 | DUNCAN 5 161.00 | 541250 | SIBLEYPL 161.00 | 0 |  | 1 | 292.3271 | Eckles to Sibley loading is under further investigation. Potential for operations guide. | INDN | ECKLES - SIBLEYPL 161.00 161KV CKT 1 | Reconductor |  |  |  |  | 3.09 | 12 | 12 | [5 empty] | 3500000 | [39 empty] | 2010-12-01 | 2011-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 4 | 2008AGP1AFS31T3371413WP | TO->FROM | ECKLES - SIBLEYPL 161.00 161KV CKT 1 | S | MIPU | INDN |  | INDN | 0 | 541250 | SIBLEYPL 161.00 | 548808 | ECKLES-161 161.00 | 0 |  | 1 | 13WP | 251 | 276 |  |  | 98.9079 | 103.9022 | [7 empty] | CATEGORYB | SINGLE | CLINTON - MONTROSE 161KV CKT 1 | 0 | 542995 | MONTROS5 161.00 | 300071 | 5CLINTN 161.00 | 0 |  | 1 | 286.7701 | Eckles to Sibley loading is under further investigation. Potential for operations guide. | INDN | ECKLES - SIBLEYPL 161.00 161KV CKT 1 | Reconductor |  |  |  |  | 3.09 | 12 | 12 | [5 empty] | 3500000 | [39 empty] | 2010-12-01 | 2011-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 4 | 2008AGP1AFS31T4993418SP | FROM->TO | EAST PLANT INTERCHANGE - PIERCE STREET TAP 115KV CKT 1 | S | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524162 | EAST_PLANT3 115.00 | 524185 | PIERCT3 115.00 | 0 |  | 1 | 18SP | 146 | 161 |  |  | 97.5078 | 101.3717 | [7 empty] | CATEGORYB | SINGLE | EAST PLANT INTERCHANGE - MANHATTAN SUB 115KV CKT 1 | 0 | 524162 | EAST_PLANT3 115.00 | 524224 | MANHATTAN 3115.00 | 0 |  | 1 | 163.2084 |  | SPS | EAST PLANT INTERCHANGE - PIERCE STREET TAP 115KV CKT 1 | Replace Terminal Equipment | [12 empty] | 225000 | 2008-01-01 | [38 empty] | 2018-06-01 | 2014-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 4 | 2008AGP1AFS31T4973418SP | FROM->TO | EAST PLANT INTERCHANGE - MANHATTAN SUB 115KV CKT 1 | S | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524162 | EAST_PLANT3 115.00 | 524224 | MANHATTAN 3115.00 | 0 |  | 1 | 18SP | 120 | 154 | 100.7 | 100.7 | 101.0313 | 105.1118 | [7 empty] | CATEGORYB | SINGLE | EAST PLANT INTERCHANGE - PIERCE STREET TAP 115KV CKT 1 | 0 | 524162 | EAST_PLANT3 115.00 | 524185 | PIERCT3 115.00 | 0 |  | 1 | 161.8722 |  | SPS | EAST PLANT INTERCHANGE - MANHATTAN SUB 115KV CKT 1 Displacement | Replace Terminal Equipment | [12 empty] | 225000 | 2008-01-01 | [38 empty] | 2015-06-01 | 2014-06-01
2008-AGP1 | AFS3 | CONT-0900 - JEC - East Manhattan 230kV | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V6945518SP |  | EAST MANHATTAN 230KV | EXP | WERE |  | NCENTRAL |  |  | 532861 | EMANHAT6 230.00 | [5 empty] | 18SP | [6 empty] | 0.91572 | 0.89984 | 0.92407 | 0.89859 | 0.99497 | 0.95 | 1.05 | CATEGORYB | SINGLE | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 0 | 532852 | JEC 6 230.00 | 532861 | EMANHAT6 230.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | CONT-0633 - East Manhattan 230-115kV XFMR | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17453318SP |  | EAST MANHATTAN 115KV | REL | WERE |  | NCENTRAL |  |  | 533326 | EMANHAT3 115.00 | [5 empty] | 18SP | [6 empty] | 0.91027 | 0.90049 | 0.89654 | 0.84505 | 1.0017 | 0.93 | 1.05 | CATEGORYB | SINGLE | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T9102209SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | REL | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 09SP | 280 | 308 |  |  | 102.8518 | 102.9556 | [7 empty] | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539657 | CONCORD3 115.00 | 539658 | CONCRD6 230.00 | 539904 | CONCOD-T 13.800 | 1 | 317.1032 |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T3342210SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | REL | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 10SP | 280 | 308 |  | 108.4 | 106.2968 | 110.2131 | [7 empty] | CATEGORYB | SINGLE | MCDOWELL CREEK - MORRIS COUNTY 230KV CKT 1 | 0 | 532862 | MCDOWEL6 230.00 | 532863 | MORRIS 6 230.00 | 0 |  | 1 | 339.4563 |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T12612210SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | REL | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 10SP | 280 | 308 |  | 108.4 | 106.278 | 110.1891 | [7 empty] | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 | 339.3824 |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T162210SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | REL | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 10SP | 280 | 308 |  | 104.2 | 103.0037 | 107.5288 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | 331.1887 |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 | CONT-0618 - Auburn Road 230-115kV XFMR | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T12552210SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | REL | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 10SP | 280 | 308 |  | 102 | 100.613 | 105.1166 | [7 empty] | CATEGORYB | SINGLE | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 323.7591 |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 | CONT-0800 - Stranger Creek - Craig 345kV |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T3282210SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | REL | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 10SP | 280 | 308 |  |  | 96.4208 | 100.4883 | [7 empty] | CATEGORYB | SINGLE | CRAIG - STRANGER CREEK 345KV CKT 1 | 0 | 532772 | STRANGR7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 | 309.504 |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T19182213SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | REL | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 13SP | 280 | 308 |  | 103.9 | 106.8482 | 110.7362 | [7 empty] | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 | 341.0675 |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T4412213SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | REL | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 13SP | 280 | 308 |  | 104 | 106.8678 | 110.7223 | [7 empty] | CATEGORYB | SINGLE | MCDOWELL CREEK - MORRIS COUNTY 230KV CKT 1 | 0 | 532862 | MCDOWEL6 230.00 | 532863 | MORRIS 6 230.00 | 0 |  | 1 | 341.0247 |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T222213SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | REL | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 13SP | 280 | 308 |  | 100.4 | 102.2922 | 106.8108 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | 328.9773 |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 | CONT-0618 - Auburn Road 230-115kV XFMR |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T19082213SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | REL | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 13SP | 280 | 308 |  |  | 100.2307 | 104.7217 | [7 empty] | CATEGORYB | SINGLE | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 322.5428 |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 2 | 2008AGP1AFS31T30683218SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | REL | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 18SP | 280 | 308 |  | 104.5 | 105.1189 | 109.1476 | [7 empty] | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539657 | CONCORD3 115.00 | 539658 | CONCRD6 230.00 | 539904 | CONCOD-T 13.800 | 1 | 336.1746 |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 2 | 2008AGP1AFS31T6313218SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | REL | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 18SP | 280 | 308 |  | 105 | 106.5768 | 108.9727 | [7 empty] | CATEGORYB | SINGLE | MCDOWELL CREEK - MORRIS COUNTY 230KV CKT 1 | 0 | 532862 | MCDOWEL6 230.00 | 532863 | MORRIS 6 230.00 | 0 |  | 1 | 335.6359 |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T472218SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | REL | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 18SP | 280 | 308 |  | 100.4 | 101.27 | 104.8164 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | 322.8345 |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 | CONT-0618 - Auburn Road 230-115kV XFMR |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T30792218SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | REL | WERE |  | NCENTRAL |  | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 18SP | 280 | 308 |  |  | 99.3877 | 103.0125 | [7 empty] | CATEGORYB | SINGLE | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 317.2785 |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T3722210SP | FROM->TO | EAST MANHATTAN - MCDOWELL CREEK SWITCHING STATION 115KV CKT 1 | REL | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533326 | EMANHAT3 115.00 | 533335 | MCDOWEL3 115.00 | 0 |  | 1 | 10SP | 179 | 179 |  | 101.2 | 100.2568 | 105.7745 | [7 empty] | CATEGORYB | SINGLE | EAST MANHATTAN - MATTERS CORNER 115KV CKT 1 | 0 | 533326 | EMANHAT3 115.00 | 533334 | MATTERS3 115.00 | 0 |  | 1 | 189.3364 |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T4642213SP | FROM->TO | EAST MANHATTAN - MCDOWELL CREEK SWITCHING STATION 115KV CKT 1 | REL | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533326 | EMANHAT3 115.00 | 533335 | MCDOWEL3 115.00 | 0 |  | 1 | 13SP | 179 | 179 |  |  | 99.4176 | 104.951 | [7 empty] | CATEGORYB | SINGLE | EAST MANHATTAN - MATTERS CORNER 115KV CKT 1 | 0 | 533326 | EMANHAT3 115.00 | 533334 | MATTERS3 115.00 | 0 |  | 1 | 187.8623 |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T6952218SP | FROM->TO | EAST MANHATTAN - MCDOWELL CREEK SWITCHING STATION 115KV CKT 1 | REL | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533326 | EMANHAT3 115.00 | 533335 | MCDOWEL3 115.00 | 0 |  | 1 | 18SP | 179 | 179 |  |  | 98.4585 | 100.7454 | [7 empty] | CATEGORYB | SINGLE | EAST MANHATTAN - MATTERS CORNER 115KV CKT 1 | 0 | 533326 | EMANHAT3 115.00 | 533334 | MATTERS3 115.00 | 0 |  | 1 | 180.3343 |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17743318SP |  | EAST ABILENE 115KV | REL | WERE |  | WEST |  |  | 533365 | EABILEN3 115.00 | [5 empty] | 18SP | [8 empty] | 0.94398 | 0.90543 | 0.94373 | 0.93 | 1.05 | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
GEN-2001-024 | Mattison | [7 empty] | 506957506927012SP | TO->FROM | DYESS - TONTITOWN 161KV CKT 1 | U | AEPW | AEPW | FAYETTEV | FAYETTEV | 0 | 506957 | TONTITN5 161.00 | 506927 | DYESS 5 161.00 | 0 |  | 1 |  | 451 | 592 |  |  | 238.5 | [9 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | AEPW | DYESS - TONTITOWN 161KV CKT 1 | Add one 161KV terminal for Tontitown | [12 empty] | 537700 | [39 empty] | 2008-06-01 | 2008-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 3 | 2008AGP1AFS31T10422309SP | TO->FROM | DOC BONIN - LABBE 230KV CKT 1 | S | LAFA | LAFA | LAFA | LAFA | 0 | 502421 | LABBE 230.00 | 502403 | BONIN 6 230.00 | 0 |  | 1 | 09SP | 655 | 785 | 114.5 | 111.7 | 111.7818 | 114.0769 | [7 empty] | CATEGORYB | NONSINGLE | SERCW-21 | 0 | 0 |  | 0 |  | 0 |  |  | 895.5036 |  | LAFA | DOC BONIN - LABBE 230KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T16491313SP | TO->FROM | DOC BONIN - LABBE 230KV CKT 1 | S | LAFA | LAFA | LAFA | LAFA | 0 | 502421 | LABBE 230.00 | 502403 | BONIN 6 230.00 | 0 |  | 1 | 13SP | 655 | 785 | 127.8 | 123.2 | 123.4142 | 128.1552 | [7 empty] | CATEGORYB | NONSINGLE | SERCW-21 | 0 | 0 |  | 0 |  | 0 |  |  | 1006.0183 |  | LAFA | DOC BONIN - LABBE 230KV CKT 1 | Indeterminate | [52 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T4272209WP | FROM->TO | DIANA - LONE STAR SOUTH 138KV CKT 1 | EXP | AEPW | AEPW | NWLANTEC | MTPL | 0 | 508831 | DIANA 4 138.00 | 508297 | LSSOUTH4 138.00 | 0 |  | 1 | 09WP | 287 | 287 |  |  | 100.4905 | 100.2443 | [7 empty] | CATEGORYB | SINGLE | WILKES (WILKES) 345/138/13.2KV TRANSFORMER CKT 1 | 1 | 508840 | WILKES 4 138.00 | 508841 | WILKES 7 345.00 | 508826 | WILKES-1 13.200 | 1 | 287.7011 |  | AEPW | DIANA - LONE STAR SOUTH 138KV CKT 1 | Replace 138 kV switch 10387 at Diana on the line to Lone Star South. | 248 | 287 | 287 | 316 |  | 12 | 4 | [5 empty] | 150000 | 2008-07-16 | [38 empty] | 2009-12-01 | 2010-12-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T7032210WP | FROM->TO | DIANA - LONE STAR SOUTH 138KV CKT 1 | EXP | AEPW | AEPW | NWLANTEC | MTPL | 0 | 508831 | DIANA 4 138.00 | 508297 | LSSOUTH4 138.00 | 0 |  | 1 | 10WP | 287 | 287 |  |  | 100.1786 | 101.5868 | [7 empty] | CATEGORYB | SINGLE | WILKES (WILKES) 345/138/13.2KV TRANSFORMER CKT 1 | 1 | 508840 | WILKES 4 138.00 | 508841 | WILKES 7 345.00 | 508826 | WILKES-1 13.200 | 1 | 291.5541 |  | AEPW | DIANA - LONE STAR SOUTH 138KV CKT 1 | Replace 138 kV switch 10387 at Diana on the line to Lone Star South. | 248 | 287 | 287 | 316 |  | 12 | 4 | [5 empty] | 150000 | 2008-07-16 | [38 empty] | 2009-12-01 | 2010-12-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 2 | 2008AGP1AFS31T5451218SP | FROM->TO | DEAF SMITH COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 1 | S | SPS | SPS | SPS-CLHF | SPS-CLHF | 0 | 524623 | DEAFSMITH 6 230.00 | 524622 | DEAFSMITH 3 115.00 | 0 |  | 1 | 18SP | 149 | 171 | 102.3 | 102 | 101.9877 | 104.9752 | [7 empty] | CATEGORYB | SINGLE | DEAF SMITH COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 2 | 0 | 524622 | DEAFSMITH 3 115.00 | 524623 | DEAFSMITH 6 230.00 | 0 |  | 2 | 179.5076 |  | SPS | DEAF SMITH COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 3 Displacement | Add third 230/115 kV auto (150/175.2 MVA) | [5 empty] | 30 | 30 | [5 empty] | 2250000 | 2008-01-01 | [38 empty] | 2014-06-01 | 2014-06-01
2008-AGP1 | AFS3 | 5267 - RUSDARANOFTS | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T11962210SP | TO->FROM | DARDANELLE - RUSSELLVILLE SOUTH 161KV CKT 1 | CP | EES | SWPA | EES_ARK | EMINTH | 0 | 337904 | 5RUSL-S 161.00 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 10SP | 335 | 335 |  | 121.2 | 113.2343 | 117.6206 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 | 394.029 |  | SWPA | DARDANELLE - RUSSELLVILLE SOUTH 161KV CKT 1 SWPA | Replace wave trap, disconnect switches, current transformers, and breaker. Bus will limit rating to 1340 amps. | 374 | 374 |  |  |  | 12 | 2 | [5 empty] | 2500000 | 2008-07-18 | [38 empty] | 2010-06-01 | 2013-06-01
2008-AGP1 | AFS3 | 5267 - RUSDARANOFTS | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T7692210WP | TO->FROM | DARDANELLE - RUSSELLVILLE SOUTH 161KV CKT 1 | CP | EES | SWPA | EES_ARK | EMINTH | 0 | 337904 | 5RUSL-S 161.00 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 10WP | 335 | 335 |  | 119.6 | 113.3836 | 115.9591 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 | 388.463 |  | SWPA | DARDANELLE - RUSSELLVILLE SOUTH 161KV CKT 1 SWPA | Replace wave trap, disconnect switches, current transformers, and breaker. Bus will limit rating to 1340 amps. | 374 | 374 |  |  |  | 12 | 2 | [5 empty] | 2500000 | 2008-07-18 | [38 empty] | 2010-06-01 | 2013-06-01
2008-AGP1 | AFS3 | 5267 - RUSDARANOFTS | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T18432213SP | TO->FROM | DARDANELLE - RUSSELLVILLE SOUTH 161KV CKT 1 | CP | EES | SWPA | EES_ARK | EMINTH | 0 | 337904 | 5RUSL-S 161.00 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 13SP | 374 | 374 |  | 114.7 | 107.285 | 109.5165 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 | 409.5917 |  | SWPA | DARDANELLE - RUSSELLVILLE SOUTH 161KV CKT 1 SWPA | Replace wave trap, disconnect switches, current transformers, and breaker. Bus will limit rating to 1340 amps. | 374 | 374 |  |  |  | 12 | 2 | [5 empty] | 2500000 | 2008-07-18 | [38 empty] | 2010-06-01 | 2013-06-01
2008-AGP1 | AFS3 | 5267 - RUSDARANOFTS | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T30122218SP | TO->FROM | DARDANELLE - RUSSELLVILLE SOUTH 161KV CKT 1 | CP | EES | SWPA | EES_ARK | EMINTH | 0 | 337904 | 5RUSL-S 161.00 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 18SP | 374 | 374 |  | 109 | 102.8756 | 103.5966 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 | 387.4513 |  | SWPA | DARDANELLE - RUSSELLVILLE SOUTH 161KV CKT 1 SWPA | Replace wave trap, disconnect switches, current transformers, and breaker. Bus will limit rating to 1340 amps. | 374 | 374 |  |  |  | 12 | 2 | [5 empty] | 2500000 | 2008-07-18 | [38 empty] | 2010-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T4282218SP | TO->FROM | CPP TRANSF #2 - PRYOR FOUNDRY SOUTH 69KV CKT 1 | REL | GRDA | GRDA | GR-LIN | GR-SIN | 0 | 512681 | FNDRY#S2 69.000 | 512661 | CPPXF#22 69.000 | 0 |  | 1 | 18SP | 72 | 72 | 115.2 | 115.9 | 116.1119 | 115.8116 | [7 empty] | CATEGORYB | SINGLE | MAID - REDDEN 69KV CKT 1 | 0 | 512626 | MAID 2 69.000 | 512698 | REDDEN 2 69.000 | 0 |  | 1 | 83.3844 |  | GRDA | CPP TRANSF #2 - PRYOR FOUNDRY SOUTH 69KV CKT 1 | Replace 600A switch with 1200A switch | 85 | 97 | [50 empty] | 2016-06-01 | 2016-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 4 | 2008AGP1AFS31T3121418SP | FROM->TO | CPP TRANSF #2 - CPP TRANSF #3 69KV CKT 1 | S | GRDA | GRDA | GR-SIN | GR-SIN | 0 | 512661 | CPPXF#22 69.000 | 512684 | CPPXF#32 69.000 | 0 |  | 1 | 18SP | 72 | 72 |  |  | 86.642 | 100 | [7 empty] | CATEGORYB | SINGLE | MAID - REDDEN 69KV CKT 1 | 0 | 512626 | MAID 2 69.000 | 512698 | REDDEN 2 69.000 | 0 |  | 1 | 72 |  | GRDA | CPP TRANSF #2 - CPP TRANSF #3 69KV CKT 1 | Replace terminal equipment | [12 empty] | 500000 | [39 empty] | 2018-06-01 | 2018-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V3465509SP |  | CONCORDIA 115KV | EXP | MKEC |  |  |  |  | 539657 | CONCORD3 115.00 | [5 empty] | 09SP | [8 empty] | 0.83989 | 0.79694 | 0.9936 | 0.9 | 1.05 | CATEGORYB | SINGLE | CONCORDIA - ELMCREK6 230.00 230KV CKT 1 | 0 | 539639 | ELMCREK6 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V7305509SP |  | CONCORDIA 115KV | EXP | MKEC |  |  |  |  | 539657 | CONCORD3 115.00 | [5 empty] | 09SP | [8 empty] | 0.83995 | 0.79701 | 0.9936 | 0.9 | 1.05 | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539658 | CONCRD6 230.00 | 539657 | CONCORD3 115.00 | 539904 | CONCOD-T 13.800 | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V2495509SP |  | CONCORDIA 115KV | EXP | MKEC |  |  |  |  | 539657 | CONCORD3 115.00 | [5 empty] | 09SP | [8 empty] | 0.85266 | 0.81172 | 0.9936 | 0.9 | 1.05 | CATEGORYB | SINGLE | EAST MANHATTAN - ELMCREK6 230.00 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 539639 | ELMCREK6 230.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FNSL | FDNS-Iteration limit exceeded | 3 | 2 | 2008AGP1AFS32V53213SP |  | CONCORDIA 115KV | EXP | MKEC |  |  |  |  | 539657 | CONCORD3 115.00 | [5 empty] | 13SP | [8 empty] | 1.0368 | 0.78413 | 1.0309 | 0.9 | 1.05 | CATEGORYB | SINGLE | EAST MANHATTAN - ELMCREK6 230.00 230KV CKT 1 | 0 | 539639 | ELMCREK6 230.00 | 532861 | EMANHAT6 230.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | CONT-0633 - East Manhattan 230-115kV XFMR |  |  | FDNS |  | 3 | 2 | 2008AGP1AFS31T30193218SP | FROM->TO | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | REL | MKEC |  |  |  | 1 | 539658 | CONCRD6 230.00 | 539657 | CONCORD3 115.00 | 539904 | CONCOD-T 13.800 | 1 | 18SP | 205 | 205 |  |  | 92.1085 | 103.6387 | [7 empty] | CATEGORYB | SINGLE | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 212.4593 |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T3982210SP | FROM->TO | CONCORDIA - JEWELL 3 115KV CKT 1 | EXP | MKEC | MKEC |  |  | 0 | 539657 | CONCORD3 115.00 | 539669 | JEWELL 3 115.00 | 0 |  | 1 | 10SP | 83.9 | 89.6 |  |  | 95.9735 | 101.4131 | [7 empty] | CATEGORYB | SINGLE | BELOIT - CONCORDIA 115KV CKT 1 | 0 | 539650 | BELOIT 3 115.00 | 539657 | CONCORD3 115.00 | 0 |  | 1 | 90.8661 |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T4932213SP | FROM->TO | CONCORDIA - JEWELL 3 115KV CKT 1 | EXP | MKEC | MKEC |  |  | 0 | 539657 | CONCORD3 115.00 | 539669 | JEWELL 3 115.00 | 0 |  | 1 | 13SP | 83.9 | 89.6 |  |  | 96.3181 | 102.3112 | [7 empty] | CATEGORYB | SINGLE | BELOIT - CONCORDIA 115KV CKT 1 | 0 | 539650 | BELOIT 3 115.00 | 539657 | CONCORD3 115.00 | 0 |  | 1 | 91.6708 |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T7322218SP | FROM->TO | CONCORDIA - JEWELL 3 115KV CKT 1 | EXP | MKEC | MKEC |  |  | 0 | 539657 | CONCORD3 115.00 | 539669 | JEWELL 3 115.00 | 0 |  | 1 | 18SP | 83.9 | 89.6 |  |  | 101.1955 | 104.4986 | [7 empty] | CATEGORYB | SINGLE | BELOIT - CONCORDIA 115KV CKT 1 | 0 | 539650 | BELOIT 3 115.00 | 539657 | CONCORD3 115.00 | 0 |  | 1 | 93.6307 |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17143318SP |  | COLBY 115KV | REL | MIDW |  | REG E-IL |  |  | 530555 | COLBY 3 115.00 | [5 empty] | 18SP | [8 empty] | 0.91592 | 0.88806 | 1.0175 | 0.9 | 1.05 | CATEGORYB | SINGLE | MINGO (MINGO) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 531451 | MINGO 7 345.00 | 531429 | MINGO 3 115.00 | 531452 | MINGTER1 13.800 | 1 |  |  | SUNC | RULETON 115KV Capacitor | Install Second 12 Mvar cap bank at Ruleton 115kV | [12 empty] | 486000 | 2008-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 3 | 2008AGP1AFS31T462309FA | TO->FROM | COFFEYVILLE TAP - NORTH BARTLESVILLE 138KV CKT 1 | CP | AEPW | AEPW | TS-KAMO | NORTHERN | 0 | 510386 | NBVILLE4 138.00 | 510422 | COFFEYT4 138.00 | 0 |  | 1 | 09FA | 237 | 265 |  |  | 97.0163 | 100.2943 | [7 empty] | CATEGORYB | SINGLE | DELAWARE - NORTHEAST STATION 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 510406 | N.E.S.-7 345.00 | 0 |  | 1 | 265.7799 |  | AEPW | COFFEYVILLE TAP - NORTH BARTLESVILLE 138KV CKT 1 | Rebuild 13.11 miles of 795 ACSR with 1590 ACSR. | 287 | 287 | 287 | 287 | 13.11 | 24 | 9 |  | 0.00468 | 0.04865 | 0.01512 | New Limits will be switches on both ends | 13100000 | 2007-09-18 | [38 empty] | 2009-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T581309SH | TO->FROM | COFFEYVILLE TAP - NORTH BARTLESVILLE 138KV CKT 1 | CP | AEPW | AEPW | TS-KAMO | NORTHERN | 0 | 510386 | NBVILLE4 138.00 | 510422 | COFFEYT4 138.00 | 0 |  | 1 | 09SH | 202 | 235 |  | 103.7 | 106.9981 | 109.2425 | [7 empty] | CATEGORYB | SINGLE | DELAWARE - NORTHEAST STATION 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 510406 | N.E.S.-7 345.00 | 0 |  | 1 | 256.7199 |  | AEPW | COFFEYVILLE TAP - NORTH BARTLESVILLE 138KV CKT 1 | Rebuild 13.11 miles of 795 ACSR with 1590 ACSR. | 287 | 287 | 287 | 287 | 13.11 | 24 | 9 |  | 0.00468 | 0.04865 | 0.01512 | New Limits will be switches on both ends | 13100000 | 2007-09-18 | [38 empty] | 2009-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 3 | 2008AGP1AFS31T744309SP | TO->FROM | COFFEYVILLE TAP - NORTH BARTLESVILLE 138KV CKT 1 | CP | AEPW | AEPW | TS-KAMO | NORTHERN | 0 | 510386 | NBVILLE4 138.00 | 510422 | COFFEYT4 138.00 | 0 |  | 1 | 09SP | 202 | 235 |  |  | 99.1833 | 101.3907 | [7 empty] | CATEGORYB | SINGLE | DELAWARE - NORTHEAST STATION 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 510406 | N.E.S.-7 345.00 | 0 |  | 1 | 238.2681 |  | AEPW | COFFEYVILLE TAP - NORTH BARTLESVILLE 138KV CKT 1 | Rebuild 13.11 miles of 795 ACSR with 1590 ACSR. | 287 | 287 | 287 | 287 | 13.11 | 24 | 9 |  | 0.00468 | 0.04865 | 0.01512 | New Limits will be switches on both ends | 13100000 | 2007-09-18 | [38 empty] | 2009-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T1023310SP | TO->FROM | COFFEYVILLE TAP - NORTH BARTLESVILLE 138KV CKT 1 | CP | AEPW | AEPW | TS-KAMO | NORTHERN | 0 | 510386 | NBVILLE4 138.00 | 510422 | COFFEYT4 138.00 | 0 |  | 1 | 10SP | 202 | 235 |  |  | 96.3533 | 103.5477 | [7 empty] | CATEGORYB | SINGLE | DELAWARE - NORTHEAST STATION 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 510406 | N.E.S.-7 345.00 | 0 |  | 1 | 243.3371 |  | AEPW | COFFEYVILLE TAP - NORTH BARTLESVILLE 138KV CKT 1 | Rebuild 13.11 miles of 795 ACSR with 1590 ACSR. | 287 | 287 | 287 | 287 | 13.11 | 24 | 9 |  | 0.00468 | 0.04865 | 0.01512 | New Limits will be switches on both ends | 13100000 | 2007-09-18 | [38 empty] | 2009-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T633310WP | TO->FROM | COFFEYVILLE TAP - NORTH BARTLESVILLE 138KV CKT 1 | CP | AEPW | AEPW | TS-KAMO | NORTHERN | 0 | 510386 | NBVILLE4 138.00 | 510422 | COFFEYT4 138.00 | 0 |  | 1 | 10WP | 237 | 265 |  |  | 96.486 | 105.2879 | [7 empty] | CATEGORYB | SINGLE | DELAWARE - NORTHEAST STATION 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 510406 | N.E.S.-7 345.00 | 0 |  | 1 | 279.0129 |  | AEPW | COFFEYVILLE TAP - NORTH BARTLESVILLE 138KV CKT 1 | Rebuild 13.11 miles of 795 ACSR with 1590 ACSR. | 287 | 287 | 287 | 287 | 13.11 | 24 | 9 |  | 0.00468 | 0.04865 | 0.01512 | New Limits will be switches on both ends | 13100000 | 2007-09-18 | [38 empty] | 2009-06-01 | 2011-06-01
2008-AGP1 | AFS3 | 5078 - SCODEADELNEO | FDNS |  | FDNS |  | 2 | 3 | 2008AGP1AFS31T482309FA | FROM->TO | COFFEYVILLE TAP - DEARING 138KV CKT 1 | CP | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 09FA | 202 | 232 |  | 100.7 | 101.7927 | 106.2607 | [7 empty] | CATEGORYB | SINGLE | DELAWARE - NEOSHO 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 532793 | NEOSHO 7 345.00 | 0 |  | 1 | 246.5248 | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | WERE | COFFEYVILLE TAP - DEARING 138KV CKT 1 WERE #2 | Replace Disconnect Switches, Wavetrap, Breaker, Jumpers | 382 | 382 | 382 | 382 | [8 empty] | 200000 | 2007-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | 5078 - SCODEADELNEO | FDNS |  | FDNS |  | 2 | 3 | 2008AGP1AFS31T482309FA | FROM->TO | COFFEYVILLE TAP - DEARING 138KV CKT 1 | CP | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 09FA | 202 | 232 |  | 100.7 | 101.7927 | 106.2607 | [7 empty] | CATEGORYB | SINGLE | DELAWARE - NEOSHO 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 532793 | NEOSHO 7 345.00 | 0 |  | 1 | 246.5248 | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | WERE | COFFEYVILLE TAP - DEARING 138KV CKT 1 WERE | Tie Line, Rebuild 3.93 miles of 795 ACSR with 1590 ACSR. | 287 | 287 | 287 | 287 | 3.93 | 15 | 6 |  | 0.0014061 | 0.013834 | 0.0047953 |  | 3000000 | 2006-06-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | 5078 - SCODEADELNEO | FDNS |  | FDNS |  | 2 | 3 | 2008AGP1AFS31T482309FA | FROM->TO | COFFEYVILLE TAP - DEARING 138KV CKT 1 | CP | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 09FA | 202 | 232 |  | 100.7 | 101.7927 | 106.2607 | [7 empty] | CATEGORYB | SINGLE | DELAWARE - NEOSHO 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 532793 | NEOSHO 7 345.00 | 0 |  | 1 | 246.5248 | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | AEPW | COFFEYVILLE TAP - DEARING 138KV CKT 1 AEPW | Tie Line, Reconductor 1.09 miles of 795 ACSR with 1590 ACSR. | 368 | 512 | 434 | 555 | 1.09 | 15 | 6 |  | 0.00039 | 0.003837 | 0.00133 | AEP: The limiting factor is the AEP portion of 795 ACSR conductor. New ratings are for AEP only. The new limit is the 1590 ACSR conductor. | 950000 | 2007-04-13 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 4 | 3 | 2008AGP1AFS31T3014309FA | FROM->TO | COFFEYVILLE TAP - DEARING 138KV CKT 1 | CP | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 09FA | 202 | 232 |  |  | 100.0162 | 101.023 | [7 empty] | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 | 234.3734 | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | WERE | COFFEYVILLE TAP - DEARING 138KV CKT 1 WERE #2 | Replace Disconnect Switches, Wavetrap, Breaker, Jumpers | 382 | 382 | 382 | 382 | [8 empty] | 200000 | 2007-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 4 | 3 | 2008AGP1AFS31T3014309FA | FROM->TO | COFFEYVILLE TAP - DEARING 138KV CKT 1 | CP | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 09FA | 202 | 232 |  |  | 100.0162 | 101.023 | [7 empty] | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 | 234.3734 | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | WERE | COFFEYVILLE TAP - DEARING 138KV CKT 1 WERE | Tie Line, Rebuild 3.93 miles of 795 ACSR with 1590 ACSR. | 287 | 287 | 287 | 287 | 3.93 | 15 | 6 |  | 0.0014061 | 0.013834 | 0.0047953 |  | 3000000 | 2006-06-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 4 | 3 | 2008AGP1AFS31T3014309FA | FROM->TO | COFFEYVILLE TAP - DEARING 138KV CKT 1 | CP | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 09FA | 202 | 232 |  |  | 100.0162 | 101.023 | [7 empty] | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 | 234.3734 | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | AEPW | COFFEYVILLE TAP - DEARING 138KV CKT 1 AEPW | Tie Line, Reconductor 1.09 miles of 795 ACSR with 1590 ACSR. | 368 | 512 | 434 | 555 | 1.09 | 15 | 6 |  | 0.00039 | 0.003837 | 0.00133 | AEP: The limiting factor is the AEP portion of 795 ACSR conductor. New ratings are for AEP only. The new limit is the 1590 ACSR conductor. | 950000 | 2007-04-13 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | 5078 - SCODEADELNEO |  |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T621309SH | FROM->TO | COFFEYVILLE TAP - DEARING 138KV CKT 1 | CP | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 09SH | 202 | 232 |  |  | 101.4859 | 104.4201 | [7 empty] | CATEGORYB | SINGLE | DELAWARE - NEOSHO 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 532793 | NEOSHO 7 345.00 | 0 |  | 1 | 242.2546 | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | WERE | COFFEYVILLE TAP - DEARING 138KV CKT 1 WERE | Tie Line, Rebuild 3.93 miles of 795 ACSR with 1590 ACSR. | 287 | 287 | 287 | 287 | 3.93 | 15 | 6 |  | 0.0014061 | 0.013834 | 0.0047953 |  | 3000000 | 2006-06-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | 5078 - SCODEADELNEO |  |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T621309SH | FROM->TO | COFFEYVILLE TAP - DEARING 138KV CKT 1 | CP | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 09SH | 202 | 232 |  |  | 101.4859 | 104.4201 | [7 empty] | CATEGORYB | SINGLE | DELAWARE - NEOSHO 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 532793 | NEOSHO 7 345.00 | 0 |  | 1 | 242.2546 | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | WERE | COFFEYVILLE TAP - DEARING 138KV CKT 1 WERE #2 | Replace Disconnect Switches, Wavetrap, Breaker, Jumpers | 382 | 382 | 382 | 382 | [8 empty] | 200000 | 2007-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | 5078 - SCODEADELNEO |  |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T621309SH | FROM->TO | COFFEYVILLE TAP - DEARING 138KV CKT 1 | CP | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 09SH | 202 | 232 |  |  | 101.4859 | 104.4201 | [7 empty] | CATEGORYB | SINGLE | DELAWARE - NEOSHO 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 532793 | NEOSHO 7 345.00 | 0 |  | 1 | 242.2546 | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | AEPW | COFFEYVILLE TAP - DEARING 138KV CKT 1 AEPW | Tie Line, Reconductor 1.09 miles of 795 ACSR with 1590 ACSR. | 368 | 512 | 434 | 555 | 1.09 | 15 | 6 |  | 0.00039 | 0.003837 | 0.00133 | AEP: The limiting factor is the AEP portion of 795 ACSR conductor. New ratings are for AEP only. The new limit is the 1590 ACSR conductor. | 950000 | 2007-04-13 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 4 | 3 | 2008AGP1AFS31T4334309SH | FROM->TO | COFFEYVILLE TAP - DEARING 138KV CKT 1 | CP | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 09SH | 202 | 232 |  | 101.1 | 102.8123 | 104.0533 | [7 empty] | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 | 241.4037 | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | WERE | COFFEYVILLE TAP - DEARING 138KV CKT 1 WERE | Tie Line, Rebuild 3.93 miles of 795 ACSR with 1590 ACSR. | 287 | 287 | 287 | 287 | 3.93 | 15 | 6 |  | 0.0014061 | 0.013834 | 0.0047953 |  | 3000000 | 2006-06-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 4 | 3 | 2008AGP1AFS31T4334309SH | FROM->TO | COFFEYVILLE TAP - DEARING 138KV CKT 1 | CP | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 09SH | 202 | 232 |  | 101.1 | 102.8123 | 104.0533 | [7 empty] | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 | 241.4037 | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | WERE | COFFEYVILLE TAP - DEARING 138KV CKT 1 WERE #2 | Replace Disconnect Switches, Wavetrap, Breaker, Jumpers | 382 | 382 | 382 | 382 | [8 empty] | 200000 | 2007-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 4 | 3 | 2008AGP1AFS31T4334309SH | FROM->TO | COFFEYVILLE TAP - DEARING 138KV CKT 1 | CP | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 09SH | 202 | 232 |  | 101.1 | 102.8123 | 104.0533 | [7 empty] | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 | 241.4037 | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | AEPW | COFFEYVILLE TAP - DEARING 138KV CKT 1 AEPW | Tie Line, Reconductor 1.09 miles of 795 ACSR with 1590 ACSR. | 368 | 512 | 434 | 555 | 1.09 | 15 | 6 |  | 0.00039 | 0.003837 | 0.00133 | AEP: The limiting factor is the AEP portion of 795 ACSR conductor. New ratings are for AEP only. The new limit is the 1590 ACSR conductor. | 950000 | 2007-04-13 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T7041309SP | FROM->TO | COFFEYVILLE TAP - DEARING 138KV CKT 1 | CP | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 09SP | 202 | 232 | 102.3 | 108.3 | 109.8648 | 109.6501 | [7 empty] | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 | 254.3882 | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | WERE | COFFEYVILLE TAP - DEARING 138KV CKT 1 WERE | Tie Line, Rebuild 3.93 miles of 795 ACSR with 1590 ACSR. | 287 | 287 | 287 | 287 | 3.93 | 15 | 6 |  | 0.0014061 | 0.013834 | 0.0047953 |  | 3000000 | 2006-06-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T7041309SP | FROM->TO | COFFEYVILLE TAP - DEARING 138KV CKT 1 | CP | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 09SP | 202 | 232 | 102.3 | 108.3 | 109.8648 | 109.6501 | [7 empty] | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 | 254.3882 | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | WERE | COFFEYVILLE TAP - DEARING 138KV CKT 1 WERE #2 | Replace Disconnect Switches, Wavetrap, Breaker, Jumpers | 382 | 382 | 382 | 382 | [8 empty] | 200000 | 2007-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T7041309SP | FROM->TO | COFFEYVILLE TAP - DEARING 138KV CKT 1 | CP | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 09SP | 202 | 232 | 102.3 | 108.3 | 109.8648 | 109.6501 | [7 empty] | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1 | 254.3882 | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | AEPW | COFFEYVILLE TAP - DEARING 138KV CKT 1 AEPW | Tie Line, Reconductor 1.09 miles of 795 ACSR with 1590 ACSR. | 368 | 512 | 434 | 555 | 1.09 | 15 | 6 |  | 0.00039 | 0.003837 | 0.00133 | AEP: The limiting factor is the AEP portion of 795 ACSR conductor. New ratings are for AEP only. The new limit is the 1590 ACSR conductor. | 950000 | 2007-04-13 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | 5078 - SCODEADELNEO | FDNS |  | FDNS |  | 4 | 3 | 2008AGP1AFS31T584309WP | FROM->TO | COFFEYVILLE TAP - DEARING 138KV CKT 1 | CP | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 09WP | 202 | 232 |  | 101.4 | 102.8925 | 104.2489 | [7 empty] | CATEGORYB | SINGLE | DELAWARE - NEOSHO 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 532793 | NEOSHO 7 345.00 | 0 |  | 1 | 241.8575 | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | WERE | COFFEYVILLE TAP - DEARING 138KV CKT 1 WERE #2 | Replace Disconnect Switches, Wavetrap, Breaker, Jumpers | 382 | 382 | 382 | 382 | [8 empty] | 200000 | 2007-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | 5078 - SCODEADELNEO | FDNS |  | FDNS |  | 4 | 3 | 2008AGP1AFS31T584309WP | FROM->TO | COFFEYVILLE TAP - DEARING 138KV CKT 1 | CP | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 09WP | 202 | 232 |  | 101.4 | 102.8925 | 104.2489 | [7 empty] | CATEGORYB | SINGLE | DELAWARE - NEOSHO 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 532793 | NEOSHO 7 345.00 | 0 |  | 1 | 241.8575 | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | AEPW | COFFEYVILLE TAP - DEARING 138KV CKT 1 AEPW | Tie Line, Reconductor 1.09 miles of 795 ACSR with 1590 ACSR. | 368 | 512 | 434 | 555 | 1.09 | 15 | 6 |  | 0.00039 | 0.003837 | 0.00133 | AEP: The limiting factor is the AEP portion of 795 ACSR conductor. New ratings are for AEP only. The new limit is the 1590 ACSR conductor. | 950000 | 2007-04-13 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | 5078 - SCODEADELNEO | FDNS |  | FDNS |  | 4 | 3 | 2008AGP1AFS31T584309WP | FROM->TO | COFFEYVILLE TAP - DEARING 138KV CKT 1 | CP | AEPW | WERE | NORTHERN | SEAST | 0 | 510422 | COFFEYT4 138.00 | 533002 | DEARING4 138.00 | 0 |  | 1 | 09WP | 202 | 232 |  | 101.4 | 102.8925 | 104.2489 | [7 empty] | CATEGORYB | SINGLE | DELAWARE - NEOSHO 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 532793 | NEOSHO 7 345.00 | 0 |  | 1 | 241.8575 | Per MW-Mile files, 78% WR, 22% AEP of 5.02 miles. | WERE | COFFEYVILLE TAP - DEARING 138KV CKT 1 WERE | Tie Line, Rebuild 3.93 miles of 795 ACSR with 1590 ACSR. | 287 | 287 | 287 | 287 | 3.93 | 15 | 6 |  | 0.0014061 | 0.013834 | 0.0047953 |  | 3000000 | 2006-06-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | 5263 - COCCOUCOCVIL |  |  | FDNS |  | 2 | 1 | 2008AGP1AFS31T202113WP | FROM->TO | COCODRIE 230/138KV TRANSFORMER CKT 1 | S | CELE | CELE | CLE_CENTRAL | CLE_CENTRAL | 0 | 500190 | COCODR 6 230.00 | 500230 | COUGH 4 138.00 | 0 |  | 1 | 13WP | 386 | 425 |  |  | 103.2724 | 102.2023 | [7 empty] | CATEGORYB | SINGLE | COCODRIE - VILLE PLATTE 230KV CKT 1 | 0 | 500190 | COCODR 6 230.00 | 500880 | VILPLT 6 230.00 | 0 |  | 1 | 434.3598 |  | CELE | COCODRIE 230/138KV TRANSFORMER CKT 1 | Replace Cocodrie 230/138 kV Auto XFMR | 504 | 504 | [10 empty] | 6000000 | [39 empty] | 2010-06-01 | 2011-06-01
2008-AGP1 | AFS3 | 5263 - COCCOUCOCVIL |  |  | FDNS |  | 2 | 1 | 2008AGP1AFS31T692118SP | FROM->TO | COCODRIE 230/138KV TRANSFORMER CKT 1 | S | CELE | CELE | CLE_CENTRAL | CLE_CENTRAL | 0 | 500190 | COCODR 6 230.00 | 500230 | COUGH 4 138.00 | 0 |  | 1 | 18SP | 386 | 425 |  |  | 105.1367 | 104.0256 | [7 empty] | CATEGORYB | SINGLE | COCODRIE - VILLE PLATTE 230KV CKT 1 | 0 | 500190 | COCODR 6 230.00 | 500880 | VILPLT 6 230.00 | 0 |  | 1 | 442.1088 |  | CELE | COCODRIE 230/138KV TRANSFORMER CKT 1 | Replace Cocodrie 230/138 kV Auto XFMR | 504 | 504 | [10 empty] | 6000000 | [39 empty] | 2010-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V1565509SH |  | CLIFTON 115KV | EXP | MKEC |  |  |  |  | 539656 | CLIFTON3 115.00 | [5 empty] | 09SH | [7 empty] | 0.8871 | 0.90133 | 0.8374 | 0.99978 | 0.9 | 1.05 | CATEGORYB | SINGLE | KELLY - SOUTH SENECA 115KV CKT 1 | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 3 | 2008AGP1AFS31V2891309SP |  | CLIFTON 115KV | EXP | MKEC |  |  |  |  | 539656 | CLIFTON3 115.00 | [5 empty] | 09SP | [7 empty] | 0.83929 | 0.95029 | 0.65842 | 0.99154 | 0.9 | 1.05 | CATEGORYB | SINGLE | KELLY - SOUTH SENECA 115KV CKT 1 | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V3455509SP |  | CLIFTON 115KV | EXP | MKEC |  |  |  |  | 539656 | CLIFTON3 115.00 | [5 empty] | 09SP | [8 empty] | 0.84125 | 0.80149 | 0.98344 | 0.9 | 1.05 | CATEGORYB | SINGLE | CONCORDIA - ELMCREK6 230.00 230KV CKT 1 | 0 | 539639 | ELMCREK6 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V7295509SP |  | CLIFTON 115KV | EXP | MKEC |  |  |  |  | 539656 | CLIFTON3 115.00 | [5 empty] | 09SP | [8 empty] | 0.84131 | 0.80156 | 0.98344 | 0.9 | 1.05 | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539658 | CONCRD6 230.00 | 539657 | CONCORD3 115.00 | 539904 | CONCOD-T 13.800 | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FNSL | FDNS-Iteration limit exceeded | 3 | 2 | 2008AGP1AFS32V43213SP |  | CLIFTON 115KV | EXP | MKEC |  |  |  |  | 539656 | CLIFTON3 115.00 | [5 empty] | 13SP | [8 empty] | 1.0218 | 0.82102 | 1.0219 | 0.9 | 1.05 | CATEGORYB | SINGLE | EAST MANHATTAN - ELMCREK6 230.00 230KV CKT 1 | 0 | 539639 | ELMCREK6 230.00 | 532861 | EMANHAT6 230.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T695509SH | FROM->TO | CLIFTON - GREENLEAF 115KV CKT 1 | EXP | MKEC | MKEC |  |  | 0 | 539656 | CLIFTON3 115.00 | 539665 | GRNLEAF3 115.00 | 0 |  | 1 | 09SH | 83.9 | 89.6 |  |  | 88.4878 | 103.8564 | [7 empty] | CATEGORYB | SINGLE | KELLY - SOUTH SENECA 115KV CKT 1 | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 93.0553 |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 4 | 2008AGP1AFS31T1913409SP | FROM->TO | CLIFTON - GREENLEAF 115KV CKT 1 | EXP | MKEC | MKEC |  |  | 0 | 539656 | CLIFTON3 115.00 | 539665 | GRNLEAF3 115.00 | 0 |  | 1 | 09SP | 83.9 | 89.6 |  |  | 95.7502 | 143.4761 | [7 empty] | CATEGORYB | SINGLE | KELLY - SOUTH SENECA 115KV CKT 1 | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 128.5546 |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T685509SH | TO->FROM | CLIFTON - CONCORDIA 115KV CKT 1 | EXP | MKEC | MKEC |  |  | 0 | 539657 | CONCORD3 115.00 | 539656 | CLIFTON3 115.00 | 0 |  | 1 | 09SH | 83.9 | 89.6 |  | 100.8 | 96.3429 | 111.7173 | [7 empty] | CATEGORYB | SINGLE | KELLY - SOUTH SENECA 115KV CKT 1 | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 100.0987 |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 4 | 2008AGP1AFS31T1903409SP | TO->FROM | CLIFTON - CONCORDIA 115KV CKT 1 | EXP | MKEC | MKEC |  |  | 0 | 539657 | CONCORD3 115.00 | 539656 | CLIFTON3 115.00 | 0 |  | 1 | 09SP | 83.9 | 89.6 |  |  | 62.4355 | 156.6466 | [7 empty] | CATEGORYB | SINGLE | KELLY - SOUTH SENECA 115KV CKT 1 | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | 140.3554 |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T1642210SP | FROM->TO | CLAYTON - SARDIS 138KV CKT 1 | S | AEPW | AEPW | EASTERN | TS-WFEC | 0 | 510919 | CLAYTON4 138.00 | 510926 | SARDIS 4 138.00 | 0 |  | 1 | 10SP | 88 | 107 |  | 100.9 | 110.5667 | 102.6569 | [7 empty] | CATEGORYB | SINGLE | PITTSBURG - VALLIANT 345KV CKT 1 | 0 | 510907 | PITTSB-7 345.00 | 510911 | VALIANT7 345.00 | 0 |  | 1 | 109.8429 |  | AEPW | CLAYTON - SARDIS 138KV CKT 1 | Interim redispatch | [52 empty] | 2010-06-01 | 2012-06-01
2008-AGP1 | AFS3 | 5003 - BRKCLAVALPIT | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T1652210SP | TO->FROM | CLAYTON - NASHOBA 138KV CKT 1 | S | AEPW | AEPW | TS-WFEC | EASTERN | 0 | 510927 | NASHOBA4 138.00 | 510919 | CLAYTON4 138.00 | 0 |  | 1 | 10SP | 88 | 107 |  | 104.3 | 113.9642 | 106.0701 | [7 empty] | CATEGORYB | SINGLE | PITTSBURG - VALLIANT 345KV CKT 1 | 0 | 510907 | PITTSB-7 345.00 | 510911 | VALIANT7 345.00 | 0 |  | 1 | 113.495 |  | AEPW | CLAYTON - NASHOBA 138KV CKT 1 | Interim redispatch | [52 empty] | 2010-06-01 | 2012-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 2 | 2008AGP1AFS31V9113213SP |  | CLAY CENTER JUNCTION 115KV | REL | WERE |  | NCENTRAL |  |  | 533323 | CLAYCTR3 115.00 | [5 empty] | 13SP | [8 empty] | 0.91043 | 0.88913 | 0.92711 | 0.93 | 1.05 | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17653318SP |  | CLAY CENTER JUNCTION 115KV | REL | WERE |  | NCENTRAL |  |  | 533323 | CLAYCTR3 115.00 | [5 empty] | 18SP | [8 empty] | 0.91019 | 0.86786 | 0.91745 | 0.93 | 1.05 | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 1 | 2008AGP1AFS31T3683118SP | TO->FROM | CLASSEN - SW 5TAP 138KV CKT 1 | S | OKGE | OKGE |  |  | 0 | 514921 | SW 5TAP4 138.00 | 514922 | CLASSEN4 138.00 | 0 |  | 1 | 18SP | 191 | 191 |  |  | 95.9174 | 100.4309 | [7 empty] | CATEGORYB | SINGLE | COUNCIL - MUSTANG 138KV CKT 1 | 0 | 514861 | MUSTANG4 138.00 | 514865 | COUNCIL4 138.00 | 0 |  | 1 | 191.823 |  | OKGE | CLASSEN - SW 5TAP 138KV CKT 1 | Replace 800A trap at Classen | 268 | 287 | 287 | 308 |  | 12 | 8 | [5 empty] | 50000 | 2005-07-12 | [38 empty] | 2018-06-01 | 2018-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 2 | 1 | 2008AGP1AFS31T3262109SH | FROM->TO | CLAREMORE (CLRAUTO2) 161/69/13.8KV TRANSFORMER CKT 2 | EXP | GRDA |  | GRDA |  | 2 | 512651 | CLARMR 5 161.00 | 512679 | CLARMR 2 69.000 | 512815 | CLARMR2 13.800 | 2 | 09SH | 84 | 105 | 106.9 | 109.9 | 114.1599 | 114.502 | [7 empty] | CATEGORYB | SINGLE | CLAREMORE (CLRAUTO1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 512651 | CLARMR 5 161.00 | 512679 | CLARMR 2 69.000 | 512814 | CLARMR1 13.800 | 1 | 120.2271 |  | GRDA | CLAREMORE (CLRAUTO2) 161/69/13.8KV TRANSFORMER CKT 2 | Upgrade both existing transformers | [11 empty] | $6 million total for 2 xfmrs | 6000000 | [39 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 2 | 1 | 2008AGP1AFS31T5632109SP | FROM->TO | CLAREMORE (CLRAUTO2) 161/69/13.8KV TRANSFORMER CKT 2 | EXP | GRDA |  | GRDA |  | 2 | 512651 | CLARMR 5 161.00 | 512679 | CLARMR 2 69.000 | 512815 | CLARMR2 13.800 | 2 | 09SP | 84 | 105 | 103.7 | 111.3 | 115.4492 | 115.7723 | [7 empty] | CATEGORYB | SINGLE | CLAREMORE (CLRAUTO1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 512651 | CLARMR 5 161.00 | 512679 | CLARMR 2 69.000 | 512814 | CLARMR1 13.800 | 1 | 121.5609 |  | GRDA | CLAREMORE (CLRAUTO2) 161/69/13.8KV TRANSFORMER CKT 2 | Upgrade both existing transformers | [11 empty] | $6 million total for 2 xfmrs | 6000000 | [39 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 4 | 1 | 2008AGP1AFS31T5864110SP | FROM->TO | CLAREMORE (CLRAUTO2) 161/69/13.8KV TRANSFORMER CKT 2 | EXP | GRDA |  | GRDA |  | 2 | 512651 | CLARMR 5 161.00 | 512679 | CLARMR 2 69.000 | 512815 | CLARMR2 13.800 | 2 | 10SP | 84 | 105 | 102.7 | 109 | 96.4129 | 109.4097 | [7 empty] | CATEGORYB | SINGLE | CLAREMORE (CLRAUTO1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 512651 | CLARMR 5 161.00 | 512679 | CLARMR 2 69.000 | 512814 | CLARMR1 13.800 | 1 | 114.8802 |  | GRDA | CLAREMORE (CLRAUTO2) 161/69/13.8KV TRANSFORMER CKT 2 | Upgrade both existing transformers | [11 empty] | $6 million total for 2 xfmrs | 6000000 | [39 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 1 | 1 | 2008AGP1AFS31T10151113SP | FROM->TO | CLAREMORE (CLRAUTO2) 161/69/13.8KV TRANSFORMER CKT 2 | EXP | GRDA |  | GRDA |  | 2 | 512651 | CLARMR 5 161.00 | 512679 | CLARMR 2 69.000 | 512815 | CLARMR2 13.800 | 2 | 13SP | 84 | 105 | 113.4 | 115 | 102.8579 | 119.2833 | [7 empty] | CATEGORYB | SINGLE | CLAREMORE (CLRAUTO1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 512651 | CLARMR 5 161.00 | 512679 | CLARMR 2 69.000 | 512814 | CLARMR1 13.800 | 1 | 125.2475 |  | GRDA | CLAREMORE (CLRAUTO2) 161/69/13.8KV TRANSFORMER CKT 2 | Upgrade both existing transformers | [11 empty] | $6 million total for 2 xfmrs | 6000000 | [39 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 1 | 4 | 2008AGP1AFS31T22091418SP | FROM->TO | CLAREMORE (CLRAUTO2) 161/69/13.8KV TRANSFORMER CKT 2 | EXP | GRDA |  | GRDA |  | 2 | 512651 | CLARMR 5 161.00 | 512679 | CLARMR 2 69.000 | 512815 | CLARMR2 13.800 | 2 | 18SP | 84 | 105 | 113.9 | 116.9 | 105.0382 | 120.6525 | [7 empty] | CATEGORYB | SINGLE | CLAREMORE (CLRAUTO1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 512651 | CLARMR 5 161.00 | 512679 | CLARMR 2 69.000 | 512814 | CLARMR1 13.800 | 1 | 126.6851 |  | GRDA | CLAREMORE (CLRAUTO2) 161/69/13.8KV TRANSFORMER CKT 2 | Upgrade both existing transformers | [11 empty] | $6 million total for 2 xfmrs | 6000000 | [39 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 2 | 1 | 2008AGP1AFS31T3282109SH | FROM->TO | CLAREMORE (CLRAUTO1) 161/69/13.8KV TRANSFORMER CKT 1 | EXP | GRDA |  | GRDA |  | 2 | 512651 | CLARMR 5 161.00 | 512679 | CLARMR 2 69.000 | 512814 | CLARMR1 13.800 | 1 | 09SH | 84 | 105 | 106.6 | 109.6 | 113.8636 | 114.2041 | [7 empty] | CATEGORYB | SINGLE | CLAREMORE (CLRAUTO2) 161/69/13.8KV TRANSFORMER CKT 2 | 1 | 512651 | CLARMR 5 161.00 | 512679 | CLARMR 2 69.000 | 512815 | CLARMR2 13.800 | 2 | 119.9143 |  | GRDA | CLAREMORE (CLRAUTO1) 161/69/13.8KV TRANSFORMER CKT 1 | Upgrade both existing transformers | [11 empty] | $6 million total for 2 xfmrs | 6000000 | [39 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 2 | 1 | 2008AGP1AFS31T5652109SP | FROM->TO | CLAREMORE (CLRAUTO1) 161/69/13.8KV TRANSFORMER CKT 1 | EXP | GRDA |  | GRDA |  | 2 | 512651 | CLARMR 5 161.00 | 512679 | CLARMR 2 69.000 | 512814 | CLARMR1 13.800 | 1 | 09SP | 84 | 105 | 103.3 | 111 | 115.1542 | 115.4761 | [7 empty] | CATEGORYB | SINGLE | CLAREMORE (CLRAUTO2) 161/69/13.8KV TRANSFORMER CKT 2 | 1 | 512651 | CLARMR 5 161.00 | 512679 | CLARMR 2 69.000 | 512815 | CLARMR2 13.800 | 2 | 121.2499 |  | GRDA | CLAREMORE (CLRAUTO1) 161/69/13.8KV TRANSFORMER CKT 1 | Upgrade both existing transformers | [11 empty] | $6 million total for 2 xfmrs | 6000000 | [39 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 4 | 1 | 2008AGP1AFS31T5884110SP | FROM->TO | CLAREMORE (CLRAUTO1) 161/69/13.8KV TRANSFORMER CKT 1 | EXP | GRDA |  | GRDA |  | 2 | 512651 | CLARMR 5 161.00 | 512679 | CLARMR 2 69.000 | 512814 | CLARMR1 13.800 | 1 | 10SP | 84 | 105 | 102.3 | 108.7 | 96.1291 | 109.1053 | [7 empty] | CATEGORYB | SINGLE | CLAREMORE (CLRAUTO2) 161/69/13.8KV TRANSFORMER CKT 2 | 1 | 512651 | CLARMR 5 161.00 | 512679 | CLARMR 2 69.000 | 512815 | CLARMR2 13.800 | 2 | 114.5606 |  | GRDA | CLAREMORE (CLRAUTO1) 161/69/13.8KV TRANSFORMER CKT 1 | Upgrade both existing transformers | [11 empty] | $6 million total for 2 xfmrs | 6000000 | [39 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 1 | 1 | 2008AGP1AFS31T10171113SP | FROM->TO | CLAREMORE (CLRAUTO1) 161/69/13.8KV TRANSFORMER CKT 1 | EXP | GRDA |  | GRDA |  | 2 | 512651 | CLARMR 5 161.00 | 512679 | CLARMR 2 69.000 | 512814 | CLARMR1 13.800 | 1 | 13SP | 84 | 105 | 113.1 | 114.7 | 102.5661 | 118.9676 | [7 empty] | CATEGORYB | SINGLE | CLAREMORE (CLRAUTO2) 161/69/13.8KV TRANSFORMER CKT 2 | 1 | 512651 | CLARMR 5 161.00 | 512679 | CLARMR 2 69.000 | 512815 | CLARMR2 13.800 | 2 | 124.916 |  | GRDA | CLAREMORE (CLRAUTO1) 161/69/13.8KV TRANSFORMER CKT 1 | Upgrade both existing transformers | [11 empty] | $6 million total for 2 xfmrs | 6000000 | [39 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 1 | 4 | 2008AGP1AFS31T22111418SP | FROM->TO | CLAREMORE (CLRAUTO1) 161/69/13.8KV TRANSFORMER CKT 1 | EXP | GRDA |  | GRDA |  | 2 | 512651 | CLARMR 5 161.00 | 512679 | CLARMR 2 69.000 | 512814 | CLARMR1 13.800 | 1 | 18SP | 84 | 105 | 113.6 | 116.6 | 104.7465 | 120.3419 | [7 empty] | CATEGORYB | SINGLE | CLAREMORE (CLRAUTO2) 161/69/13.8KV TRANSFORMER CKT 2 | 1 | 512651 | CLARMR 5 161.00 | 512679 | CLARMR 2 69.000 | 512815 | CLARMR2 13.800 | 2 | 126.359 |  | GRDA | CLAREMORE (CLRAUTO1) 161/69/13.8KV TRANSFORMER CKT 1 | Upgrade both existing transformers | [11 empty] | $6 million total for 2 xfmrs | 6000000 | [39 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V9463313SP |  | CITY OF ST.FRANCIS 115KV | REL | SUNC |  | SEPC |  |  | 531441 | CSTFRAN3 115.00 | [5 empty] | 13SP | [8 empty] | 0.92912 | 0.89917 | 1.002 | 0.9 | 1.05 | CATEGORYB | SINGLE | MINGO (MINGO) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 531451 | MINGO 7 345.00 | 531429 | MINGO 3 115.00 | 531452 | MINGTER1 13.800 | 1 |  |  | SUNC | RULETON 115KV Capacitor | Install Second 12 Mvar cap bank at Ruleton 115kV | [12 empty] | 486000 | 2008-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17303318SP |  | CITY OF ST.FRANCIS 115KV | REL | SUNC |  | SEPC |  |  | 531441 | CSTFRAN3 115.00 | [5 empty] | 18SP | [8 empty] | 0.91655 | 0.88427 | 0.99067 | 0.9 | 1.05 | CATEGORYB | SINGLE | MINGO (MINGO) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 531451 | MINGO 7 345.00 | 531429 | MINGO 3 115.00 | 531452 | MINGTER1 13.800 | 1 |  |  | SUNC | RULETON 115KV Capacitor | Install Second 12 Mvar cap bank at Ruleton 115kV | [12 empty] | 486000 | 2008-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V9473313SP |  | CITY OF GOODLAND 115KV | REL | SUNC |  | SEPC |  |  | 531444 | GOODCTY3 115.00 | [5 empty] | 13SP | [8 empty] | 0.92826 | 0.89874 | 1.0111 | 0.9 | 1.05 | CATEGORYB | SINGLE | MINGO (MINGO) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 531451 | MINGO 7 345.00 | 531429 | MINGO 3 115.00 | 531452 | MINGTER1 13.800 | 1 |  |  | SUNC | RULETON 115KV Capacitor | Install Second 12 Mvar cap bank at Ruleton 115kV | [12 empty] | 486000 | 2008-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17323318SP |  | CITY OF GOODLAND 115KV | REL | SUNC |  | SEPC |  |  | 531444 | GOODCTY3 115.00 | [5 empty] | 18SP | [8 empty] | 0.91636 | 0.88395 | 1.0003 | 0.9 | 1.05 | CATEGORYB | SINGLE | MINGO (MINGO) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 531451 | MINGO 7 345.00 | 531429 | MINGO 3 115.00 | 531452 | MINGTER1 13.800 | 1 |  |  | SUNC | RULETON 115KV Capacitor | Install Second 12 Mvar cap bank at Ruleton 115kV | [12 empty] | 486000 | 2008-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2008-AGP1 | AFS3 | 1100 - 17th Street - Chisholm 138kV | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T2802209SP | FROM->TO | CHISHOLM - RIPLEY 69KV CKT 1 | REL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533786 | CHISHLM2 69.000 | 533832 | RIPLEYM2 69.000 | 0 |  | 1 | 09SP | 116 | 128 | 109.3 | 109.3 | 109.4275 | 109.4099 | [7 empty] | CATEGORYB | SINGLE | CHISHOLM - SEVENTEENTH 138KV CKT 1 | 0 | 533035 | CHISHLM4 138.00 | 533064 | 17TH 4 138.00 | 0 |  | 1 | 140.0447 |  | WERE | CHISHOLM - RIPLEY 69KV CKT 1 | Tear down and rebuild 2.40 Chisholm - Ripley 69 kV with 1192.5 ACSR | [52 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | 1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T2892209SP | FROM->TO | CHISHOLM - RIPLEY 69KV CKT 1 | REL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533786 | CHISHLM2 69.000 | 533832 | RIPLEYM2 69.000 | 0 |  | 1 | 09SP | 116 | 128 | 105.0 | 105.2 | 105.3256 | 105.371 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 | 134.8749 |  | WERE | CHISHOLM - RIPLEY 69KV CKT 1 | Tear down and rebuild 2.40 Chisholm - Ripley 69 kV with 1192.5 ACSR | [52 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | CONT-0600 - 17th Street 138-69kV XFMR | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T9002209SP | FROM->TO | CHISHOLM - RIPLEY 69KV CKT 1 | REL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533786 | CHISHLM2 69.000 | 533832 | RIPLEYM2 69.000 | 0 |  | 1 | 09SP | 116 | 128 | 103.9 | 103.7 | 103.7649 | 103.8966 | [7 empty] | CATEGORYB | SINGLE | SEVENTEENTH (17TH 4X) 138/69/11.295KV TRANSFORMER CKT 1 | 1 | 533064 | 17TH 4 138.00 | 533840 | 17TH 2 69.000 | 533112 | 17TH 1 11.295 | 1 | 132.9876 |  | WERE | CHISHOLM - RIPLEY 69KV CKT 1 | Tear down and rebuild 2.40 Chisholm - Ripley 69 kV with 1192.5 ACSR | [52 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 2 | 2008AGP1AFS31V9193213SP |  | CHAPMAN 115KV | REL | WERE |  | WEST |  |  | 533362 | CHAPMAN3 115.00 | [5 empty] | 13SP | [8 empty] | 0.93965 | 0.91939 | 0.95585 | 0.93 | 1.05 | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17733318SP |  | CHAPMAN 115KV | REL | WERE |  | WEST |  |  | 533362 | CHAPMAN3 115.00 | [5 empty] | 18SP | [8 empty] | 0.93995 | 0.89959 | 0.94709 | 0.93 | 1.05 | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T12593310SP | FROM->TO | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | REL | WERE | WERE | WEST | NCENTRAL | 0 | 533362 | CHAPMAN3 115.00 | 533323 | CLAYCTR3 115.00 | 0 |  | 1 | 10SP | 25 | 25 |  | 108.2 | 106.7053 | 108.9335 | [7 empty] | CATEGORYB | GENOUT | GEN533323 DF-CLAY CENTER JUNCTION | 0 | 0 |  | 0 |  | 0 |  |  | 27.2334 |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 |  | 6 | 1 | No | [44 empty] | 2010-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 2 | 2008AGP1AFS31T24573213SP | FROM->TO | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | REL | WERE | WERE | WEST | NCENTRAL | 0 | 533362 | CHAPMAN3 115.00 | 533323 | CLAYCTR3 115.00 | 0 |  | 1 | 13SP | 25 | 25 | 100.7 | 148 | 149.7348 | 152.7022 | [7 empty] | CATEGORYB | GENOUT | GEN533323 DF-CLAY CENTER JUNCTION | 0 | 0 |  | 0 |  | 0 |  |  | 38.1755 |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 |  | 6 | 1 | No | [44 empty] | 2010-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 2 | 2008AGP1AFS31T73213SP | FROM->TO | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | REL | WERE | WERE | WEST | NCENTRAL | 0 | 533362 | CHAPMAN3 115.00 | 533323 | CLAYCTR3 115.00 | 0 |  | 1 | 13SP | 25 | 25 |  | 122.3 | 124.0838 | 127.0328 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | 31.7582 |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 |  | 6 | 1 | No | [44 empty] | 2010-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 2 | 2008AGP1AFS31T11733213WP | FROM->TO | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | REL | WERE | WERE | WEST | NCENTRAL | 0 | 533362 | CHAPMAN3 115.00 | 533323 | CLAYCTR3 115.00 | 0 |  | 1 | 13WP | 25 | 25 |  | 114.3 | 112.5849 | 114.8089 | [7 empty] | CATEGORYB | GENOUT | GEN533323 DF-CLAY CENTER JUNCTION | 0 | 0 |  | 0 |  | 0 |  |  | 28.7022 |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 |  | 6 | 1 | No | [44 empty] | 2010-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T36683318SP | FROM->TO | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | REL | WERE | WERE | WEST | NCENTRAL | 0 | 533362 | CHAPMAN3 115.00 | 533323 | CLAYCTR3 115.00 | 0 |  | 1 | 18SP | 25 | 25 | 103.1 | 150.7 | 152.5539 | 160.2089 | [7 empty] | CATEGORYB | GENOUT | GEN533323 DF-CLAY CENTER JUNCTION | 0 | 0 |  | 0 |  | 0 |  |  | 40.0522 |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 |  | 6 | 1 | No | [44 empty] | 2010-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T113318SP | FROM->TO | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | REL | WERE | WERE | WEST | NCENTRAL | 0 | 533362 | CHAPMAN3 115.00 | 533323 | CLAYCTR3 115.00 | 0 |  | 1 | 18SP | 25 | 25 |  | 124.9 | 126.8317 | 131.6353 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | 32.9088 |  | WERE | CHAPMAN - CLAY CENTER JUNCTION 115KV CKT 1 | Reset terminal equipment | 72 | 72 | 72 | 72 |  | 6 | 1 | No | [44 empty] | 2010-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 1 | 2008AGP1AFS31T801113SP | FROM->TO | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | S | AEPW | AEPW | FAYETTEV | FAYTAECC | 0 | 506944 | CHAMSPR5 161.00 | 504020 | FARMNGTN 5 161.00 | 0 |  | 1 | 13SP | 294 | 353 |  |  | 99.0566 | 102.1604 | [7 empty] | CATEGORYB | SINGLE | CHAMBER SPRINGS - TONTITOWN 345KV CKT 1 | 0 | 506945 | CHAMSPR7 345.00 | 506959 | TONTITN7 345.00 | 0 |  | 1 | 360.6262 |  | AEPW | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | Rebuild 10.24 miles with 2156 ACSR, replace Chamber Springs wavetrap, replace Farmington AECC bus, and reset relays. | 558 | 558 | 558 | 558 | 10.24 | 24 | 12 |  | 0.00201 | 0.02827 | 0.01602 | New limit will be a switch at Chamber Springs. | 11000000 | 2008-09-09 | [38 empty] | 2012-06-01 | 2012-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 1 | 1 | 2008AGP1AFS31T9211113SP | FROM->TO | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | S | AEPW | AEPW | FAYETTEV | FAYTAECC | 0 | 506944 | CHAMSPR5 161.00 | 504020 | FARMNGTN 5 161.00 | 0 |  | 1 | 13SP | 294 | 353 |  |  | 98.9988 | 102.108 | [7 empty] | CATEGORYB | SINGLE | TONTITOWN () 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 506957 | TONTITN5 161.00 | 506959 | TONTITN7 345.00 | 506958 | TONTITN1 13.800 | 1 | 360.4412 |  | AEPW | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | Rebuild 10.24 miles with 2156 ACSR, replace Chamber Springs wavetrap, replace Farmington AECC bus, and reset relays. | 558 | 558 | 558 | 558 | 10.24 | 24 | 12 |  | 0.00201 | 0.02827 | 0.01602 | New limit will be a switch at Chamber Springs. | 11000000 | 2008-09-09 | [38 empty] | 2012-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 1 | 2008AGP1AFS31T23113SP | FROM->TO | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | S | AEPW | AEPW | FAYETTEV | FAYTAECC | 0 | 506944 | CHAMSPR5 161.00 | 504020 | FARMNGTN 5 161.00 | 0 |  | 1 | 13SP | 294 | 353 |  |  | 98.5538 | 101.0564 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | 356.7291 |  | AEPW | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | Rebuild 10.24 miles with 2156 ACSR, replace Chamber Springs wavetrap, replace Farmington AECC bus, and reset relays. | 558 | 558 | 558 | 558 | 10.24 | 24 | 12 |  | 0.00201 | 0.02827 | 0.01602 | New limit will be a switch at Chamber Springs. | 11000000 | 2008-09-09 | [38 empty] | 2012-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 1 | 2008AGP1AFS31T843113SP | FROM->TO | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | S | AEPW | AEPW | FAYETTEV | FAYTAECC | 0 | 506944 | CHAMSPR5 161.00 | 504020 | FARMNGTN 5 161.00 | 0 |  | 1 | 13SP | 294 | 353 |  |  | 98.3225 | 100.7592 | [7 empty] | CATEGORYB | SINGLE | ELM SPRINGS REC - TONTITOWN 161KV CKT 1 | 0 | 504010 | ELMSPRGS 5 161.00 | 506957 | TONTITN5 161.00 | 0 |  | 1 | 355.68 |  | AEPW | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | Rebuild 10.24 miles with 2156 ACSR, replace Chamber Springs wavetrap, replace Farmington AECC bus, and reset relays. | 558 | 558 | 558 | 558 | 10.24 | 24 | 12 |  | 0.00201 | 0.02827 | 0.01602 | New limit will be a switch at Chamber Springs. | 11000000 | 2008-09-09 | [38 empty] | 2012-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 1 | 2008AGP1AFS31T2151118SP | FROM->TO | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | S | AEPW | AEPW | FAYETTEV | FAYTAECC | 0 | 506944 | CHAMSPR5 161.00 | 504020 | FARMNGTN 5 161.00 | 0 |  | 1 | 18SP | 294 | 353 |  |  | 99.5971 | 101.2508 | [7 empty] | CATEGORYB | SINGLE | CHAMBER SPRINGS - TONTITOWN 345KV CKT 1 | 0 | 506945 | CHAMSPR7 345.00 | 506959 | TONTITN7 345.00 | 0 |  | 1 | 357.4153 |  | AEPW | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | Rebuild 10.24 miles with 2156 ACSR, replace Chamber Springs wavetrap, replace Farmington AECC bus, and reset relays. | 558 | 558 | 558 | 558 | 10.24 | 24 | 12 |  | 0.00201 | 0.02827 | 0.01602 | New limit will be a switch at Chamber Springs. | 11000000 | 2008-09-09 | [38 empty] | 2012-06-01 | 2012-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 1 | 1 | 2008AGP1AFS31T19581118SP | FROM->TO | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | S | AEPW | AEPW | FAYETTEV | FAYTAECC | 0 | 506944 | CHAMSPR5 161.00 | 504020 | FARMNGTN 5 161.00 | 0 |  | 1 | 18SP | 294 | 353 |  |  | 99.5381 | 101.1985 | [7 empty] | CATEGORYB | SINGLE | TONTITOWN () 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 506957 | TONTITN5 161.00 | 506959 | TONTITN7 345.00 | 506958 | TONTITN1 13.800 | 1 | 357.2307 |  | AEPW | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | Rebuild 10.24 miles with 2156 ACSR, replace Chamber Springs wavetrap, replace Farmington AECC bus, and reset relays. | 558 | 558 | 558 | 558 | 10.24 | 24 | 12 |  | 0.00201 | 0.02827 | 0.01602 | New limit will be a switch at Chamber Springs. | 11000000 | 2008-09-09 | [38 empty] | 2012-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 1 | 2008AGP1AFS31T1823118SP | FROM->TO | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | S | AEPW | AEPW | FAYETTEV | FAYTAECC | 0 | 506944 | CHAMSPR5 161.00 | 504020 | FARMNGTN 5 161.00 | 0 |  | 1 | 18SP | 294 | 353 |  |  | 99.0486 | 100.6706 | [7 empty] | CATEGORYB | SINGLE | ELM SPRINGS REC - TONTITOWN 161KV CKT 1 | 0 | 504010 | ELMSPRGS 5 161.00 | 506957 | TONTITN5 161.00 | 0 |  | 1 | 355.3672 |  | AEPW | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | Rebuild 10.24 miles with 2156 ACSR, replace Chamber Springs wavetrap, replace Farmington AECC bus, and reset relays. | 558 | 558 | 558 | 558 | 10.24 | 24 | 12 |  | 0.00201 | 0.02827 | 0.01602 | New limit will be a switch at Chamber Springs. | 11000000 | 2008-09-09 | [38 empty] | 2012-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31V2582218SP |  | CENTER HILL 161KV | REL | SWPA |  | EMINTH |  |  | 505416 | CENTR H5 161.00 | [5 empty] | 18SP | [7 empty] | 0.84709 | 0.8511 | 0.82445 | 0.97778 | 0.9 | 1.05 | CATEGORYB | SINGLE | KENNETT - NEW MADRID 161KV CKT 1 | 0 | 505400 | N MADRD5 161.00 | 505410 | KENNETT5 161.00 | 0 |  | 1 |  |  | SWPA | KENNETT CAP BANK 1 161KV CAP BANK | Install Additional Cap Bank at Kennett | [52 empty] | 2014-06-01 | 2014-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V5345509SH |  | CENT 4 138.00 138KV | S | OKGE |  | ENID |  |  | 515363 | CENT 4 138.00 | [5 empty] | 09SH | [8 empty] | 1.0385 | 1.0659 | 1.0459 | 0.9 | 1.05 | CATEGORYB | GENOUT | GEN515364 1-CENT 11 0.6000 | 0 | 337909 | 8ANO 50 500.00 | 515305 | FTSMITH8 500.00 | 0 |  | 1 |  |  | OKGE | WOODWARD 138KV REACTOR | Install a reactor bank in the Woodward Area. | [12 empty] | 700000 | 2008-07-29 | [38 empty] | 2009-04-01 | 2011-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31V8082209AP |  | CEDAR AVE GRACE 69KV | S | OKGE |  | ENID |  |  | 514781 | CEDARAV2 69.000 | [5 empty] | 09AP | [8 empty] | 1.0369 | 1.0613 | 1.0356 | 0.9 | 1.05 | CATEGORYB | GENOUT | GEN515364 1-CENT 11 0.6000 | 0 | 337909 | 8ANO 50 500.00 | 515305 | FTSMITH8 500.00 | 0 |  | 1 |  |  | OKGE | WOODWARD 138KV REACTOR | Install a reactor bank in the Woodward Area. | [12 empty] | 700000 | 2008-07-29 | [38 empty] | 2009-04-01 | 2011-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T454409AP | FROM->TO | CARTER JCT - MOORELAND 69KV CKT 1 | PL | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521197 | CRTSJCT2 69.000 | 520995 | MOORLND2 69.000 | 0 |  | 1 | 09AP | 53 | 65 |  |  | 64.7288 | 105.622 | [7 empty] | CATEGORYB | SINGLE | FPL SWITCH - MOORELAND 138KV CKT 1 | 0 | 515785 | WINDFRM4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 68.6543 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T1214409G | TO->FROM | CANTON - TALOGA 69KV CKT 1 | PL | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521064 | TALOGA 2 69.000 | 520843 | CANTON-2 69.000 | 0 |  | 1 | 09G | 33 | 39 |  |  | 87.5767 | 112.817 | [7 empty] | CATEGORYB | SINGLE | CEDARDALE - MOORELAND 138KV CKT 1 | 0 | 520848 | CEDRDAL4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 43.9986 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T1244409G | TO->FROM | CANTON - TALOGA 69KV CKT 1 | PL | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521064 | TALOGA 2 69.000 | 520843 | CANTON-2 69.000 | 0 |  | 1 | 09G | 33 | 39 |  |  | 85.8476 | 111.0099 | [7 empty] | CATEGORYB | SINGLE | CEDARDALE - OKEENE 138KV CKT 1 | 0 | 520848 | CEDRDAL4 138.00 | 521016 | OKEENE 4 138.00 | 0 |  | 1 | 43.2939 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T972409SH | TO->FROM | CANTON - TALOGA 69KV CKT 1 | PL | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521064 | TALOGA 2 69.000 | 520843 | CANTON-2 69.000 | 0 |  | 1 | 09SH | 33 | 39 |  |  | 78.6453 | 103.4646 | [7 empty] | CATEGORYB | SINGLE | CEDARDALE - MOORELAND 138KV CKT 1 | 0 | 520848 | CEDRDAL4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 40.3512 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T992409SH | TO->FROM | CANTON - TALOGA 69KV CKT 1 | PL | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521064 | TALOGA 2 69.000 | 520843 | CANTON-2 69.000 | 0 |  | 1 | 09SH | 33 | 39 |  |  | 76.9845 | 101.7327 | [7 empty] | CATEGORYB | SINGLE | CEDARDALE - OKEENE 138KV CKT 1 | 0 | 520848 | CEDRDAL4 138.00 | 521016 | OKEENE 4 138.00 | 0 |  | 1 | 39.6758 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T1312409SP | TO->FROM | CANTON - TALOGA 69KV CKT 1 | PL | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521064 | TALOGA 2 69.000 | 520843 | CANTON-2 69.000 | 0 |  | 1 | 09SP | 33 | 39 |  |  | 88.7878 | 114.5371 | [7 empty] | CATEGORYB | SINGLE | CEDARDALE - MOORELAND 138KV CKT 1 | 0 | 520848 | CEDRDAL4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 44.6695 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T1332409SP | TO->FROM | CANTON - TALOGA 69KV CKT 1 | PL | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521064 | TALOGA 2 69.000 | 520843 | CANTON-2 69.000 | 0 |  | 1 | 09SP | 33 | 39 |  |  | 86.496 | 112.1951 | [7 empty] | CATEGORYB | SINGLE | CEDARDALE - OKEENE 138KV CKT 1 | 0 | 520848 | CEDRDAL4 138.00 | 521016 | OKEENE 4 138.00 | 0 |  | 1 | 43.7561 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T1244409WP | TO->FROM | CANTON - TALOGA 69KV CKT 1 | PL | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521064 | TALOGA 2 69.000 | 520843 | CANTON-2 69.000 | 0 |  | 1 | 09WP | 42 | 46 |  |  | 81.5179 | 103.0395 | [7 empty] | CATEGORYB | SINGLE | CEDARDALE - MOORELAND 138KV CKT 1 | 0 | 520848 | CEDRDAL4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 47.3982 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T1274409WP | TO->FROM | CANTON - TALOGA 69KV CKT 1 | PL | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521064 | TALOGA 2 69.000 | 520843 | CANTON-2 69.000 | 0 |  | 1 | 09WP | 42 | 46 |  |  | 79.9523 | 101.4308 | [7 empty] | CATEGORYB | SINGLE | CEDARDALE - OKEENE 138KV CKT 1 | 0 | 520848 | CEDRDAL4 138.00 | 521016 | OKEENE 4 138.00 | 0 |  | 1 | 46.6582 |  | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 Kv, Install 345/138 kV XF, Build .5 miles of 138 kV and install terminal equipment, Tap Iodine to Woodward 138 kV line | [52 empty] | 2009-04-01 | 2010-01-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T11932210SP | FROM->TO | CALICO ROCK - NORFORK 161KV CKT 1 | CP | EES | SWPA | EES_ARK | EMINTH | 0 | 338130 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 10SP | 148 | 148 |  | 116.8 | 115.0059 | 114.5077 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 | 169.4714 |  | SWPA | CALICO ROCK - NORFORK 161KV CKT 1 SWPA | Replace bus, CTs, & Wave Trap @ Norfork | [12 empty] | 2000000 | 2008-08-11 | [38 empty] | 2010-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T11932210SP | FROM->TO | CALICO ROCK - NORFORK 161KV CKT 1 | S | EES | SWPA | EES_ARK | EMINTH | 0 | 338130 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 10SP | 148 | 148 |  | 116.8 | 115.0059 | 114.5077 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 | 169.4714 |  | EES | CALICO ROCK - NORFORK 161KV CKT 1 EES | Indeterminate | [52 empty] | 2010-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T7672210WP | FROM->TO | CALICO ROCK - NORFORK 161KV CKT 1 | CP | EES | SWPA | EES_ARK | EMINTH | 0 | 338130 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 10WP | 148 | 148 |  | 128.9 | 127.371 | 125.275 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 | 185.407 |  | SWPA | CALICO ROCK - NORFORK 161KV CKT 1 SWPA | Replace bus, CTs, & Wave Trap @ Norfork | [12 empty] | 2000000 | 2008-08-11 | [38 empty] | 2010-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T7672210WP | FROM->TO | CALICO ROCK - NORFORK 161KV CKT 1 | CP | EES | SWPA | EES_ARK | EMINTH | 0 | 338130 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 10WP | 148 | 148 |  | 128.9 | 127.371 | 125.275 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 | 185.407 |  | SWPA | CALICO ROCK - NORFORK 161KV CKT 1 SWPA | Replace bus, CTs, & Wave Trap @ Norfork | [12 empty] | 2000000 | 2008-08-11 | [38 empty] | 2010-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T7672210WP | FROM->TO | CALICO ROCK - NORFORK 161KV CKT 1 | S | EES | SWPA | EES_ARK | EMINTH | 0 | 338130 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 10WP | 148 | 148 |  | 128.9 | 127.371 | 125.275 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 | 185.407 |  | EES | CALICO ROCK - NORFORK 161KV CKT 1 EES | Indeterminate | [52 empty] | 2010-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T7672210WP | FROM->TO | CALICO ROCK - NORFORK 161KV CKT 1 | S | EES | SWPA | EES_ARK | EMINTH | 0 | 338130 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 10WP | 148 | 148 |  | 128.9 | 127.371 | 125.275 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 | 185.407 |  | EES | CALICO ROCK - NORFORK 161KV CKT 1 EES | Indeterminate | [52 empty] | 2010-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T18412213SP | FROM->TO | CALICO ROCK - NORFORK 161KV CKT 1 | CP | EES | SWPA | EES_ARK | EMINTH | 0 | 338130 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 13SP | 148 | 148 |  | 123.3 | 121.0006 | 119.5426 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 | 176.9231 |  | SWPA | CALICO ROCK - NORFORK 161KV CKT 1 SWPA | Replace bus, CTs, & Wave Trap @ Norfork | [12 empty] | 2000000 | 2008-08-11 | [38 empty] | 2010-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T18412213SP | FROM->TO | CALICO ROCK - NORFORK 161KV CKT 1 | S | EES | SWPA | EES_ARK | EMINTH | 0 | 338130 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 13SP | 148 | 148 |  | 123.3 | 121.0006 | 119.5426 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 | 176.9231 |  | EES | CALICO ROCK - NORFORK 161KV CKT 1 EES | Indeterminate | [52 empty] | 2010-06-01 | 2010-06-01
2008-AGP1 | AFS3 | CONT-Hayti-Blytheville 161kV Line Overload | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T5662213SP | FROM->TO | CALICO ROCK - NORFORK 161KV CKT 1 | CP | EES | SWPA | EES_ARK | EMINTH | 0 | 338130 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 13SP | 148 | 148 |  | 104.7 | 103.7958 | 102.0048 | [7 empty] | CATEGORYB | SINGLE | DELL 500 - NEW MADRID 500KV CKT 1 | 0 | 300035 | 8NEWMAD 500.00 | 338187 | 8DELL 5 500.00 | 0 |  | 1 | 150.9671 |  | SWPA | CALICO ROCK - NORFORK 161KV CKT 1 SWPA | Replace bus, CTs, & Wave Trap @ Norfork | [12 empty] | 2000000 | 2008-08-11 | [38 empty] | 2010-06-01 | 2011-06-01
2008-AGP1 | AFS3 | CONT-Hayti-Blytheville 161kV Line Overload | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T5662213SP | FROM->TO | CALICO ROCK - NORFORK 161KV CKT 1 | S | EES | SWPA | EES_ARK | EMINTH | 0 | 338130 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 13SP | 148 | 148 |  | 104.7 | 103.7958 | 102.0048 | [7 empty] | CATEGORYB | SINGLE | DELL 500 - NEW MADRID 500KV CKT 1 | 0 | 300035 | 8NEWMAD 500.00 | 338187 | 8DELL 5 500.00 | 0 |  | 1 | 150.9671 |  | EES | CALICO ROCK - NORFORK 161KV CKT 1 EES | Indeterminate | [52 empty] | 2010-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T30102218SP | FROM->TO | CALICO ROCK - NORFORK 161KV CKT 1 | CP | EES | SWPA | EES_ARK | EMINTH | 0 | 338130 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 18SP | 148 | 148 |  | 124.2 | 121.6393 | 119.5419 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 | 176.922 |  | SWPA | CALICO ROCK - NORFORK 161KV CKT 1 SWPA | Replace bus, CTs, & Wave Trap @ Norfork | [12 empty] | 2000000 | 2008-08-11 | [38 empty] | 2010-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T30102218SP | FROM->TO | CALICO ROCK - NORFORK 161KV CKT 1 | S | EES | SWPA | EES_ARK | EMINTH | 0 | 338130 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 18SP | 148 | 148 |  | 124.2 | 121.6393 | 119.5419 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 | 176.922 |  | EES | CALICO ROCK - NORFORK 161KV CKT 1 EES | Indeterminate | [52 empty] | 2010-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T21232218SP | FROM->TO | CALICO ROCK - NORFORK 161KV CKT 1 | CP | EES | SWPA | EES_ARK | EMINTH | 0 | 338130 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 18SP | 148 | 148 |  | 114.7 | 114.0165 | 111.4423 | [7 empty] | CATEGORYB | SINGLE | DELL 500 - INDEPENDENCE 500KV CKT 1 | 0 | 338145 | 8ISES 5 500.00 | 338187 | 8DELL 5 500.00 | 0 |  | 1 | 164.9346 |  | SWPA | CALICO ROCK - NORFORK 161KV CKT 1 SWPA | Replace bus, CTs, & Wave Trap @ Norfork | [12 empty] | 2000000 | 2008-08-11 | [38 empty] | 2010-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T21232218SP | FROM->TO | CALICO ROCK - NORFORK 161KV CKT 1 | S | EES | SWPA | EES_ARK | EMINTH | 0 | 338130 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 18SP | 148 | 148 |  | 114.7 | 114.0165 | 111.4423 | [7 empty] | CATEGORYB | SINGLE | DELL 500 - INDEPENDENCE 500KV CKT 1 | 0 | 338145 | 8ISES 5 500.00 | 338187 | 8DELL 5 500.00 | 0 |  | 1 | 164.9346 |  | EES | CALICO ROCK - NORFORK 161KV CKT 1 EES | Indeterminate | [52 empty] | 2010-06-01 | 2010-06-01
2008-AGP1 | AFS3 | CONT-Hayti-Blytheville 161kV Line Overload | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T8732218SP | FROM->TO | CALICO ROCK - NORFORK 161KV CKT 1 | CP | EES | SWPA | EES_ARK | EMINTH | 0 | 338130 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 18SP | 148 | 148 |  | 103.9 | 102.8746 | 100.4917 | [7 empty] | CATEGORYB | SINGLE | DELL 500 - NEW MADRID 500KV CKT 1 | 0 | 300035 | 8NEWMAD 500.00 | 338187 | 8DELL 5 500.00 | 0 |  | 1 | 148.7277 |  | SWPA | CALICO ROCK - NORFORK 161KV CKT 1 SWPA | Replace bus, CTs, & Wave Trap @ Norfork | [12 empty] | 2000000 | 2008-08-11 | [38 empty] | 2010-06-01 | 2011-06-01
2008-AGP1 | AFS3 | CONT-Hayti-Blytheville 161kV Line Overload | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T8732218SP | FROM->TO | CALICO ROCK - NORFORK 161KV CKT 1 | S | EES | SWPA | EES_ARK | EMINTH | 0 | 338130 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 18SP | 148 | 148 |  | 103.9 | 102.8746 | 100.4917 | [7 empty] | CATEGORYB | SINGLE | DELL 500 - NEW MADRID 500KV CKT 1 | 0 | 300035 | 8NEWMAD 500.00 | 338187 | 8DELL 5 500.00 | 0 |  | 1 | 148.7277 |  | EES | CALICO ROCK - NORFORK 161KV CKT 1 EES | Indeterminate | [52 empty] | 2010-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T20512218SP | FROM->TO | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | EXP | SWPA | EES | EMINTH | EES_ARK | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 18SP | 167 | 167 |  | 113 | 112.5724 | 109.1441 | [7 empty] | CATEGORYB | SINGLE | HILLTOP - ST JOE 161KV CKT 1 | 0 | 338108 | 5ST_JOE 161.00 | 338110 | 5HILLTOP 161.00 | 0 |  | 1 | 182.2706 |  | SWPA | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 SWPA | Replace buswork in Bull Shoals switchyard. | 335 | 335 |  |  |  | 18 | [6 empty] | 2800000 | 2008-05-28 | [38 empty] | 2018-06-01 | 2018-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T20512218SP | FROM->TO | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | S | SWPA | EES | EMINTH | EES_ARK | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 18SP | 167 | 167 |  | 113 | 112.5724 | 109.1441 | [7 empty] | CATEGORYB | SINGLE | HILLTOP - ST JOE 161KV CKT 1 | 0 | 338108 | 5ST_JOE 161.00 | 338110 | 5HILLTOP 161.00 | 0 |  | 1 | 182.2706 |  | EES | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 EES | Indeterminate | [52 empty] | 2018-06-01 | 2018-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T20502218SP | FROM->TO | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | EXP | SWPA | EES | EMINTH | EES_ARK | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 18SP | 167 | 167 |  | 112.3 | 111.8335 | 108.4045 | [7 empty] | CATEGORYB | SINGLE | EVERTON - ST JOE 161KV CKT 1 | 0 | 338107 | 5EVRTON 161.00 | 338108 | 5ST_JOE 161.00 | 0 |  | 1 | 181.0355 |  | SWPA | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 SWPA | Replace buswork in Bull Shoals switchyard. | 335 | 335 |  |  |  | 18 | [6 empty] | 2800000 | 2008-05-28 | [38 empty] | 2018-06-01 | 2018-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T20502218SP | FROM->TO | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | S | SWPA | EES | EMINTH | EES_ARK | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 18SP | 167 | 167 |  | 112.3 | 111.8335 | 108.4045 | [7 empty] | CATEGORYB | SINGLE | EVERTON - ST JOE 161KV CKT 1 | 0 | 338107 | 5EVRTON 161.00 | 338108 | 5ST_JOE 161.00 | 0 |  | 1 | 181.0355 |  | EES | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 EES | Indeterminate | [52 empty] | 2018-06-01 | 2018-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T20472218SP | FROM->TO | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | EXP | SWPA | EES | EMINTH | EES_ARK | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 18SP | 167 | 167 |  | 110.1 | 109.5979 | 106.1655 | [7 empty] | CATEGORYB | SINGLE | EVERTON - HARRISON-EAST 161KV CKT 1 | 0 | 338104 | 5HARR-E 161.00 | 338107 | 5EVRTON 161.00 | 0 |  | 1 | 177.2964 |  | SWPA | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 SWPA | Replace buswork in Bull Shoals switchyard. | 335 | 335 |  |  |  | 18 | [6 empty] | 2800000 | 2008-05-28 | [38 empty] | 2018-06-01 | 2018-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T20472218SP | FROM->TO | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 | S | SWPA | EES | EMINTH | EES_ARK | 0 | 505460 | BULL SH5 161.00 | 338123 | 5BULLSH* 161.00 | 0 |  | 1 | 18SP | 167 | 167 |  | 110.1 | 109.5979 | 106.1655 | [7 empty] | CATEGORYB | SINGLE | EVERTON - HARRISON-EAST 161KV CKT 1 | 0 | 338104 | 5HARR-E 161.00 | 338107 | 5EVRTON 161.00 | 0 |  | 1 | 177.2964 |  | EES | BULL SHOALS - BULL SHOALS HES 161KV CKT 1 EES | Indeterminate | [52 empty] | 2018-06-01 | 2018-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T674409FA | FROM->TO | BUFFALO - WEST 69KV CKT 1 | CP | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520835 | BUFFALO2 69.000 | 521093 | WEST 2 69.000 | 0 |  | 1 | 09FA | 24 | 24 |  |  | 86.5187 | 101.3591 | [7 empty] | CATEGORYB | SINGLE | KNOBHILL - MOORELAND 138KV CKT 1 | 0 | 514795 | KNOBHIL4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 24.3262 |  | WFEC | BUFFALO - WEST 69KV CKT 1 | Upgrade CT's at Buffalo Switchyard; 200 to 600Amp; new limit 336.4 Conductor | 53 | 65 | 69 | 72 | [8 empty] | 75000 | 2008-08-11 | [38 empty] | 2009-04-01 | 2011-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T2804409FA | FROM->TO | BUFFALO - WEST 69KV CKT 1 | CP | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520835 | BUFFALO2 69.000 | 521093 | WEST 2 69.000 | 0 |  | 1 | 09FA | 24 | 24 |  |  | 86.4377 | 101.2974 | [7 empty] | CATEGORYB | SINGLE | KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 514794 | KNOBHIL2 69.000 | 514795 | KNOBHIL4 138.00 | 515732 | KNOBHIL1 13.200 | 1 | 24.3114 |  | WFEC | BUFFALO - WEST 69KV CKT 1 | Upgrade CT's at Buffalo Switchyard; 200 to 600Amp; new limit 336.4 Conductor | 53 | 65 | 69 | 72 | [8 empty] | 75000 | 2008-08-11 | [38 empty] | 2009-04-01 | 2011-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T994409G | FROM->TO | BUFFALO - WEST 69KV CKT 1 | CP | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520835 | BUFFALO2 69.000 | 521093 | WEST 2 69.000 | 0 |  | 1 | 09G | 24 | 24 |  |  | 115.2476 | 132.1401 | [7 empty] | CATEGORYB | SINGLE | KNOBHILL - MOORELAND 138KV CKT 1 | 0 | 514795 | KNOBHIL4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 31.7136 |  | WFEC | BUFFALO - WEST 69KV CKT 1 | Upgrade CT's at Buffalo Switchyard; 200 to 600Amp; new limit 336.4 Conductor | 53 | 65 | 69 | 72 | [8 empty] | 75000 | 2008-08-11 | [38 empty] | 2009-04-01 | 2011-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T3864409G | FROM->TO | BUFFALO - WEST 69KV CKT 1 | CP | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520835 | BUFFALO2 69.000 | 521093 | WEST 2 69.000 | 0 |  | 1 | 09G | 24 | 24 |  |  | 115.2029 | 132.0333 | [7 empty] | CATEGORYB | SINGLE | KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 514794 | KNOBHIL2 69.000 | 514795 | KNOBHIL4 138.00 | 515732 | KNOBHIL1 13.200 | 1 | 31.688 |  | WFEC | BUFFALO - WEST 69KV CKT 1 | Upgrade CT's at Buffalo Switchyard; 200 to 600Amp; new limit 336.4 Conductor | 53 | 65 | 69 | 72 | [8 empty] | 75000 | 2008-08-11 | [38 empty] | 2009-04-01 | 2011-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T792409SH | FROM->TO | BUFFALO - WEST 69KV CKT 1 | CP | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520835 | BUFFALO2 69.000 | 521093 | WEST 2 69.000 | 0 |  | 1 | 09SH | 24 | 24 |  |  | 111.313 | 126.4142 | [7 empty] | CATEGORYB | SINGLE | KNOBHILL - MOORELAND 138KV CKT 1 | 0 | 514795 | KNOBHIL4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 30.3394 |  | WFEC | BUFFALO - WEST 69KV CKT 1 | Upgrade CT's at Buffalo Switchyard; 200 to 600Amp; new limit 336.4 Conductor | 53 | 65 | 69 | 72 | [8 empty] | 75000 | 2008-08-11 | [38 empty] | 2009-04-01 | 2011-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T3882409SH | FROM->TO | BUFFALO - WEST 69KV CKT 1 | CP | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520835 | BUFFALO2 69.000 | 521093 | WEST 2 69.000 | 0 |  | 1 | 09SH | 24 | 24 |  |  | 111.2753 | 126.3588 | [7 empty] | CATEGORYB | SINGLE | KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 514794 | KNOBHIL2 69.000 | 514795 | KNOBHIL4 138.00 | 515732 | KNOBHIL1 13.200 | 1 | 30.3261 |  | WFEC | BUFFALO - WEST 69KV CKT 1 | Upgrade CT's at Buffalo Switchyard; 200 to 600Amp; new limit 336.4 Conductor | 53 | 65 | 69 | 72 | [8 empty] | 75000 | 2008-08-11 | [38 empty] | 2009-04-01 | 2011-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T1122409SP | FROM->TO | BUFFALO - WEST 69KV CKT 1 | CP | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520835 | BUFFALO2 69.000 | 521093 | WEST 2 69.000 | 0 |  | 1 | 09SP | 24 | 24 |  |  | 118.798 | 134.359 | [7 empty] | CATEGORYB | SINGLE | KNOBHILL - MOORELAND 138KV CKT 1 | 0 | 514795 | KNOBHIL4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 32.2462 |  | WFEC | BUFFALO - WEST 69KV CKT 1 | Upgrade CT's at Buffalo Switchyard; 200 to 600Amp; new limit 336.4 Conductor | 53 | 65 | 69 | 72 | [8 empty] | 75000 | 2008-08-11 | [38 empty] | 2009-04-01 | 2011-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 2 | 4 | 2008AGP1AFS31T6362409SP | FROM->TO | BUFFALO - WEST 69KV CKT 1 | CP | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520835 | BUFFALO2 69.000 | 521093 | WEST 2 69.000 | 0 |  | 1 | 09SP | 24 | 24 |  |  | 118.7492 | 134.2518 | [7 empty] | CATEGORYB | SINGLE | KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 514794 | KNOBHIL2 69.000 | 514795 | KNOBHIL4 138.00 | 515732 | KNOBHIL1 13.200 | 1 | 32.2204 |  | WFEC | BUFFALO - WEST 69KV CKT 1 | Upgrade CT's at Buffalo Switchyard; 200 to 600Amp; new limit 336.4 Conductor | 53 | 65 | 69 | 72 | [8 empty] | 75000 | 2008-08-11 | [38 empty] | 2009-04-01 | 2011-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T994409WP | FROM->TO | BUFFALO - WEST 69KV CKT 1 | CP | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520835 | BUFFALO2 69.000 | 521093 | WEST 2 69.000 | 0 |  | 1 | 09WP | 24 | 24 |  | 114.6 | 114.7571 | 129.7794 | [7 empty] | CATEGORYB | SINGLE | KNOBHILL - MOORELAND 138KV CKT 1 | 0 | 514795 | KNOBHIL4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 31.1471 |  | WFEC | BUFFALO - WEST 69KV CKT 1 | Upgrade CT's at Buffalo Switchyard; 200 to 600Amp; new limit 336.4 Conductor | 53 | 65 | 69 | 72 | [8 empty] | 75000 | 2008-08-11 | [38 empty] | 2009-04-01 | 2011-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T3834409WP | FROM->TO | BUFFALO - WEST 69KV CKT 1 | CP | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 520835 | BUFFALO2 69.000 | 521093 | WEST 2 69.000 | 0 |  | 1 | 09WP | 24 | 24 |  | 114.6 | 114.7175 | 129.7189 | [7 empty] | CATEGORYB | SINGLE | KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 514794 | KNOBHIL2 69.000 | 514795 | KNOBHIL4 138.00 | 515732 | KNOBHIL1 13.200 | 1 | 31.1325 |  | WFEC | BUFFALO - WEST 69KV CKT 1 | Upgrade CT's at Buffalo Switchyard; 200 to 600Amp; new limit 336.4 Conductor | 53 | 65 | 69 | 72 | [8 empty] | 75000 | 2008-08-11 | [38 empty] | 2009-04-01 | 2011-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17173318SP |  | BRWSTR 3 115KV | REL | MIDW |  | REG E-IL |  |  | 530610 | BRWSTR 3 115.00 | [5 empty] | 18SP | [8 empty] | 0.92134 | 0.89006 | 1.0152 | 0.9 | 1.05 | CATEGORYB | SINGLE | MINGO (MINGO) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 531451 | MINGO 7 345.00 | 531429 | MINGO 3 115.00 | 531452 | MINGTER1 13.800 | 1 |  |  | SUNC | RULETON 115KV Capacitor | Install Second 12 Mvar cap bank at Ruleton 115kV | [12 empty] | 486000 | 2008-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 2 | 2008AGP1AFS31T1273209WP | TO->FROM | BROWN - TUPELO 138KV CKT 1 | S | SWPA | SWPA | EMINTH | EMINTH | 0 | 505600 | TUPELO 4 138.00 | 505602 | S BROWN4 138.00 | 0 |  | 1 | 09WP | 100 | 100 |  |  | 89.4524 | 100.0543 | [7 empty] | CATEGORYB | SINGLE | FROGVILLE - HUGO POWER PLANT 138KV CKT 1 | 0 | 520918 | FROGVIL4 138.00 | 520948 | HUGO PP4 138.00 | 0 |  | 1 | 100.0543 |  | SWPA | BROWN - TUPELO 138KV CKT 1 | Remove wavetrap. | 147 | 147 | [50 empty] | 2009-12-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 1 | 2008AGP1AFS31T9671110SP | FROM->TO | BROOKLINE (BRKLTX1) 345/161/13.2KV TRANSFORMER CKT 1 | S | SPRM |  | SPRM |  | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549988 | BRKLNE XF1 113.200 | 1 | 10SP | 400 | 400 |  |  | 96.4905 | 100 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SPRM-OP2 | 0 | 0 |  | 0 |  | 0 |  |  | 400 | Owned by AECI |  | Interim Redispatch | The op-guide in place for the overload of the brookline transformers becomes effective with the addition of Southwest #2 in 2010 winter | [12 empty] | 0 | 2010-06-01 | [38 empty] | 2010-06-01 | 2010-12-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 1 | 2008AGP1AFS31T821113SP | TO->FROM | BROKEN ARROW NORTH - SOUTH TAP - ONETA 138KV CKT 1 | S | AEPW | AEPW | TULSA | TULSA | 0 | 509806 | ONETA--4 138.00 | 509786 | BA.N-ST4 138.00 | 0 |  | 1 | 13SP | 202 | 235 |  |  | 84.9665 | 104.563 | [7 empty] | CATEGORYB | SINGLE | CHAMBER SPRINGS - CLARKSVILLE 345KV CKT 1 | 0 | 506945 | CHAMSPR7 345.00 | 509745 | CLARKSV7 345.00 | 0 |  | 1 | 245.7231 |  | AEPW | BROKEN ARROW NORTH - SOUTH TAP - ONETA 138KV CKT 1 | Rebuild 4.33 of 795 ACSR with 1590 ACSR. Replace Oneta wavetrap & Jumpers | 478 | 478 | 478 | 478 | 4.33 | 20 | 12 |  | 0.00292 | 0.016174 | 0.00489 | New limit will be Oneta breaker 1321A | 4600000 | 2008-07-29 | [38 empty] | 2011-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 1 | 2008AGP1AFS31T15381113SP | TO->FROM | BROKEN ARROW NORTH - SOUTH TAP - ONETA 138KV CKT 1 | S | AEPW | AEPW | TULSA | TULSA | 0 | 509806 | ONETA--4 138.00 | 509786 | BA.N-ST4 138.00 | 0 |  | 1 | 13SP | 202 | 235 |  |  | 83.7554 | 101.0531 | [7 empty] | CATEGORYB | GENOUT | GEN511839 1-NORTHEASTERN STATION #2 | 0 | 0 |  | 0 |  | 0 |  |  | 237.4748 |  | AEPW | BROKEN ARROW NORTH - SOUTH TAP - ONETA 138KV CKT 1 | Rebuild 4.33 of 795 ACSR with 1590 ACSR. Replace Oneta wavetrap & Jumpers | 478 | 478 | 478 | 478 | 4.33 | 20 | 12 |  | 0.00292 | 0.016174 | 0.00489 | New limit will be Oneta breaker 1321A | 4600000 | 2008-07-29 | [38 empty] | 2011-06-01 | 2012-06-01
2008-AGP1 | AFS3 | 5241 - ONEBANNESTUL |  |  | FDNS |  | 1 | 1 | 2008AGP1AFS31T1221113SP | TO->FROM | BROKEN ARROW NORTH - SOUTH TAP - ONETA 138KV CKT 1 | S | AEPW | AEPW | TULSA | TULSA | 0 | 509806 | ONETA--4 138.00 | 509786 | BA.N-ST4 138.00 | 0 |  | 1 | 13SP | 202 | 235 |  |  | 81.5933 | 100.1854 | [7 empty] | CATEGORYB | SINGLE | NORTHEAST STATION - TULSA NORTH 345KV CKT 1 | 0 | 509852 | T.NO.--7 345.00 | 510406 | N.E.S.-7 345.00 | 0 |  | 1 | 235.4357 |  | AEPW | BROKEN ARROW NORTH - SOUTH TAP - ONETA 138KV CKT 1 | Rebuild 4.33 of 795 ACSR with 1590 ACSR. Replace Oneta wavetrap & Jumpers | 478 | 478 | 478 | 478 | 4.33 | 20 | 12 |  | 0.00292 | 0.016174 | 0.00489 | New limit will be Oneta breaker 1321A | 4600000 | 2008-07-29 | [38 empty] | 2011-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 1 | 2008AGP1AFS31T2104118SP | TO->FROM | BROKEN ARROW NORTH - SOUTH TAP - ONETA 138KV CKT 1 | S | AEPW | AEPW | TULSA | TULSA | 0 | 509806 | ONETA--4 138.00 | 509786 | BA.N-ST4 138.00 | 0 |  | 1 | 18SP | 202 | 235 |  |  | 97.4979 | 109.4152 | [7 empty] | CATEGORYB | SINGLE | CHAMBER SPRINGS - CLARKSVILLE 345KV CKT 1 | 0 | 506945 | CHAMSPR7 345.00 | 509745 | CLARKSV7 345.00 | 0 |  | 1 | 257.1257 |  | AEPW | BROKEN ARROW NORTH - SOUTH TAP - ONETA 138KV CKT 1 | Rebuild 4.33 of 795 ACSR with 1590 ACSR. Replace Oneta wavetrap & Jumpers | 478 | 478 | 478 | 478 | 4.33 | 20 | 12 |  | 0.00292 | 0.016174 | 0.00489 | New limit will be Oneta breaker 1321A | 4600000 | 2008-07-29 | [38 empty] | 2011-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 1 | 2008AGP1AFS31T27764118SP | TO->FROM | BROKEN ARROW NORTH - SOUTH TAP - ONETA 138KV CKT 1 | S | AEPW | AEPW | TULSA | TULSA | 0 | 509806 | ONETA--4 138.00 | 509786 | BA.N-ST4 138.00 | 0 |  | 1 | 18SP | 202 | 235 |  |  | 92.9578 | 103.4925 | [7 empty] | CATEGORYB | GENOUT | GEN511839 1-NORTHEASTERN STATION #2 | 0 | 0 |  | 0 |  | 0 |  |  | 243.2074 |  | AEPW | BROKEN ARROW NORTH - SOUTH TAP - ONETA 138KV CKT 1 | Rebuild 4.33 of 795 ACSR with 1590 ACSR. Replace Oneta wavetrap & Jumpers | 478 | 478 | 478 | 478 | 4.33 | 20 | 12 |  | 0.00292 | 0.016174 | 0.00489 | New limit will be Oneta breaker 1321A | 4600000 | 2008-07-29 | [38 empty] | 2011-06-01 | 2012-06-01
2008-AGP1 | AFS3 | 5241 - ONEBANNESTUL |  |  | FDNS |  | 4 | 1 | 2008AGP1AFS31T2644118SP | TO->FROM | BROKEN ARROW NORTH - SOUTH TAP - ONETA 138KV CKT 1 | S | AEPW | AEPW | TULSA | TULSA | 0 | 509806 | ONETA--4 138.00 | 509786 | BA.N-ST4 138.00 | 0 |  | 1 | 18SP | 202 | 235 |  |  | 91.0338 | 102.9104 | [7 empty] | CATEGORYB | SINGLE | NORTHEAST STATION - TULSA NORTH 345KV CKT 1 | 0 | 509852 | T.NO.--7 345.00 | 510406 | N.E.S.-7 345.00 | 0 |  | 1 | 241.8394 |  | AEPW | BROKEN ARROW NORTH - SOUTH TAP - ONETA 138KV CKT 1 | Rebuild 4.33 of 795 ACSR with 1590 ACSR. Replace Oneta wavetrap & Jumpers | 478 | 478 | 478 | 478 | 4.33 | 20 | 12 |  | 0.00292 | 0.016174 | 0.00489 | New limit will be Oneta breaker 1321A | 4600000 | 2008-07-29 | [38 empty] | 2011-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 1 | 2008AGP1AFS31T2594118SP | TO->FROM | BROKEN ARROW NORTH - SOUTH TAP - ONETA 138KV CKT 1 | S | AEPW | AEPW | TULSA | TULSA | 0 | 509806 | ONETA--4 138.00 | 509786 | BA.N-ST4 138.00 | 0 |  | 1 | 18SP | 202 | 235 |  |  | 89.7036 | 101.5628 | [7 empty] | CATEGORYB | SINGLE | 21ST STREET TAP - TULSA SOUTHEAST 138KV CKT 1 | 0 | 509811 | T.S.E.-4 138.00 | 509828 | 21STTAP4 138.00 | 0 |  | 1 | 238.6726 |  | AEPW | BROKEN ARROW NORTH - SOUTH TAP - ONETA 138KV CKT 1 | Rebuild 4.33 of 795 ACSR with 1590 ACSR. Replace Oneta wavetrap & Jumpers | 478 | 478 | 478 | 478 | 4.33 | 20 | 12 |  | 0.00292 | 0.016174 | 0.00489 | New limit will be Oneta breaker 1321A | 4600000 | 2008-07-29 | [38 empty] | 2011-06-01 | 2012-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 4 | 1 | 2008AGP1AFS31T19214118SP | TO->FROM | BROKEN ARROW NORTH - SOUTH TAP - ONETA 138KV CKT 1 | S | AEPW | AEPW | TULSA | TULSA | 0 | 509806 | ONETA--4 138.00 | 509786 | BA.N-ST4 138.00 | 0 |  | 1 | 18SP | 202 | 235 |  |  | 89.6556 | 100.6431 | [7 empty] | CATEGORYB | SINGLE | TULSA NORTH (TULSA N) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 509817 | T.NO.--4 138.00 | 509852 | T.NO.--7 345.00 | 509883 | TNO1-1 13.800 | 1 | 236.5113 |  | AEPW | BROKEN ARROW NORTH - SOUTH TAP - ONETA 138KV CKT 1 | Rebuild 4.33 of 795 ACSR with 1590 ACSR. Replace Oneta wavetrap & Jumpers | 478 | 478 | 478 | 478 | 4.33 | 20 | 12 |  | 0.00292 | 0.016174 | 0.00489 | New limit will be Oneta breaker 1321A | 4600000 | 2008-07-29 | [38 empty] | 2011-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 1 | 2008AGP1AFS31T2094118SP | FROM->TO | BROKEN ARROW NORTH - SOUTH TAP - LYNN LANE TAP 138KV CKT 1 | S | AEPW | AEPW | TULSA | TULSA | 0 | 509786 | BA.N-ST4 138.00 | 509804 | LLANETP4 138.00 | 0 |  | 1 | 18SP | 202 | 235 |  |  | 88.2641 | 100.1932 | [7 empty] | CATEGORYB | SINGLE | CHAMBER SPRINGS - CLARKSVILLE 345KV CKT 1 | 0 | 506945 | CHAMSPR7 345.00 | 509745 | CLARKSV7 345.00 | 0 |  | 1 | 235.454 |  | AEPW | BROKEN ARROW NORTH - SOUTH TAP - LYNN LANE TAP 138KV CKT 1 | Rebuild 4.63 miles of 795 ACSR with 1590 ACSR | 225 | 262 | 264 | 295 | 4.63 | 20 | 12 |  | 0.00166 | 0.016861 | 0.00551 | Limit will be 954 ACSR conductor | 5000000 | 2008-07-29 | [38 empty] | 2018-06-01 | 2018-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 3 | 2008AGP1AFS31T2224318SP | FROM->TO | BROADMOOR - FERN STREET 69KV CKT 1 | REL | AEPW | AEPW | SHREVEPO | SHREVEPO | 0 | 507716 | BROADMR2 69.000 | 507724 | FERN 2 69.000 | 0 |  | 1 | 18SP | 51 | 59 | 100.6 | 112.6 | 112.4018 | 112.4719 | [7 empty] | CATEGORYB | SINGLE | FORBING TAP - SOUTH SHREVEPORT 69KV CKT 1 | 0 | 507728 | FORBNGT2 69.000 | 507754 | S SHV 2 69.000 | 0 |  | 1 | 66.3584 |  | AEPW | BROADMOOR - FERN STREET 69KV CKT 1 | Rebuild 2 miles of 266 ACSR with 795 ACSR and replace Fern Street Switches. | 90 | 105 | 106 | 118 | 2 | 24 | 6 |  | 0.01336 | 0.06572 | 0.00131 | New limits will 666 ACSR line conductor | 2200000 | 2008-06-18 | [38 empty] | 2016-06-01 | 2016-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 3 | 2008AGP1AFS31T2214318SP | FROM->TO | BROADMOOR - FERN STREET 69KV CKT 1 | REL | AEPW | AEPW | SHREVEPO | SHREVEPO | 0 | 507716 | BROADMR2 69.000 | 507724 | FERN 2 69.000 | 0 |  | 1 | 18SP | 51 | 59 |  | 110.9 | 110.6306 | 110.7009 | [7 empty] | CATEGORYB | SINGLE | ELLERBE ROAD - FORBING TAP 69KV CKT 1 | 0 | 507723 | ELLERBE2 69.000 | 507728 | FORBNGT2 69.000 | 0 |  | 1 | 65.3135 |  | AEPW | BROADMOOR - FERN STREET 69KV CKT 1 | Rebuild 2 miles of 266 ACSR with 795 ACSR and replace Fern Street Switches. | 90 | 105 | 106 | 118 | 2 | 24 | 6 |  | 0.01336 | 0.06572 | 0.00131 | New limits will 666 ACSR line conductor | 2200000 | 2008-06-18 | [38 empty] | 2016-06-01 | 2016-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17213318SP |  | BREWSTER 115KV | REL | SUNC |  | GREAT PL |  |  | 531351 | BREWSTR3 115.00 | [5 empty] | 18SP | [8 empty] | 0.92134 | 0.89006 | 1.0152 | 0.9 | 1.05 | CATEGORYB | SINGLE | MINGO (MINGO) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 531451 | MINGO 7 345.00 | 531429 | MINGO 3 115.00 | 531452 | MINGTER1 13.800 | 1 |  |  | SUNC | RULETON 115KV Capacitor | Install Second 12 Mvar cap bank at Ruleton 115kV | [12 empty] | 486000 | 2008-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T1011309FA | TO->FROM | BPU - CITY OF MCPHERSON JOHNS-MANVILLE - EAST MCPHERSON SWITCHING STATION 115KV CKT 1 | REL | WERE | WERE | WEST | WEST | 0 | 533417 | EMCPHER3 115.00 | 533426 | MANVILE3 115.00 | 0 |  | 1 | 09FA | 84 | 84 |  | 101.2 | 102.9931 | 108.9821 | [7 empty] | CATEGORYB | SINGLE | EAST MCPHERSON SWITCHING STATION - REFINRY3 115.00 115KV CKT 1 | 0 | 533417 | EMCPHER3 115.00 | 533427 | REFINRY3 115.00 | 0 |  | 1 | 91.545 | Line is owned by the City of McPherson | WERE | BPU - CITY OF MCPHERSON JOHNS-MANVILLE - EAST MCPHERSON SWITCHING STATION 115KV CKT 1 | Rebuild Line | 248 | 248 |  |  | 5.7 | 24 | 24 |  | 0.00392 | 0.03057 | 0.00456 | Line owned by City of McPherson Board of Public Utilities | [40 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 3 | 2008AGP1AFS31T894309G | TO->FROM | BPU - CITY OF MCPHERSON JOHNS-MANVILLE - EAST MCPHERSON SWITCHING STATION 115KV CKT 1 | REL | WERE | WERE | WEST | WEST | 0 | 533417 | EMCPHER3 115.00 | 533426 | MANVILE3 115.00 | 0 |  | 1 | 09G | 84 | 84 |  |  | 101.0981 | 103.7799 | [7 empty] | CATEGORYB | SINGLE | EAST MCPHERSON SWITCHING STATION - REFINRY3 115.00 115KV CKT 1 | 0 | 533417 | EMCPHER3 115.00 | 533427 | REFINRY3 115.00 | 0 |  | 1 | 87.1751 | Line is owned by the City of McPherson | WERE | BPU - CITY OF MCPHERSON JOHNS-MANVILLE - EAST MCPHERSON SWITCHING STATION 115KV CKT 1 | Rebuild Line | 248 | 248 |  |  | 5.7 | 24 | 24 |  | 0.00392 | 0.03057 | 0.00456 | Line owned by City of McPherson Board of Public Utilities | [40 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T1603309SH | TO->FROM | BPU - CITY OF MCPHERSON JOHNS-MANVILLE - EAST MCPHERSON SWITCHING STATION 115KV CKT 1 | REL | WERE | WERE | WEST | WEST | 0 | 533417 | EMCPHER3 115.00 | 533426 | MANVILE3 115.00 | 0 |  | 1 | 09SH | 84 | 84 |  |  | 105.2213 | 107.0917 | [7 empty] | CATEGORYB | SINGLE | EAST MCPHERSON SWITCHING STATION - REFINRY3 115.00 115KV CKT 1 | 0 | 533417 | EMCPHER3 115.00 | 533427 | REFINRY3 115.00 | 0 |  | 1 | 89.957 | Line is owned by the City of McPherson | WERE | BPU - CITY OF MCPHERSON JOHNS-MANVILLE - EAST MCPHERSON SWITCHING STATION 115KV CKT 1 | Rebuild Line | 248 | 248 |  |  | 5.7 | 24 | 24 |  | 0.00392 | 0.03057 | 0.00456 | Line owned by City of McPherson Board of Public Utilities | [40 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T1813309SP | TO->FROM | BPU - CITY OF MCPHERSON JOHNS-MANVILLE - EAST MCPHERSON SWITCHING STATION 115KV CKT 1 | REL | WERE | WERE | WEST | WEST | 0 | 533417 | EMCPHER3 115.00 | 533426 | MANVILE3 115.00 | 0 |  | 1 | 09SP | 84 | 84 | 106.2 | 108.8 | 112.8548 | 114.3854 | [7 empty] | CATEGORYB | SINGLE | EAST MCPHERSON SWITCHING STATION - REFINRY3 115.00 115KV CKT 1 | 0 | 533417 | EMCPHER3 115.00 | 533427 | REFINRY3 115.00 | 0 |  | 1 | 96.0837 | Line is owned by the City of McPherson | WERE | BPU - CITY OF MCPHERSON JOHNS-MANVILLE - EAST MCPHERSON SWITCHING STATION 115KV CKT 1 | Rebuild Line | 248 | 248 |  |  | 5.7 | 24 | 24 |  | 0.00392 | 0.03057 | 0.00456 | Line owned by City of McPherson Board of Public Utilities | [40 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T1053309WP | TO->FROM | BPU - CITY OF MCPHERSON JOHNS-MANVILLE - EAST MCPHERSON SWITCHING STATION 115KV CKT 1 | REL | WERE | WERE | WEST | WEST | 0 | 533417 | EMCPHER3 115.00 | 533426 | MANVILE3 115.00 | 0 |  | 1 | 09WP | 84 | 84 |  | 100.6 | 99.0995 | 105.1643 | [7 empty] | CATEGORYB | SINGLE | EAST MCPHERSON SWITCHING STATION - REFINRY3 115.00 115KV CKT 1 | 0 | 533417 | EMCPHER3 115.00 | 533427 | REFINRY3 115.00 | 0 |  | 1 | 88.338 | Line is owned by the City of McPherson | WERE | BPU - CITY OF MCPHERSON JOHNS-MANVILLE - EAST MCPHERSON SWITCHING STATION 115KV CKT 1 | Rebuild Line | 248 | 248 |  |  | 5.7 | 24 | 24 |  | 0.00392 | 0.03057 | 0.00456 | Line owned by City of McPherson Board of Public Utilities | [40 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T2533310SP | TO->FROM | BPU - CITY OF MCPHERSON JOHNS-MANVILLE - EAST MCPHERSON SWITCHING STATION 115KV CKT 1 | REL | WERE | WERE | WEST | WEST | 0 | 533417 | EMCPHER3 115.00 | 533426 | MANVILE3 115.00 | 0 |  | 1 | 10SP | 84 | 84 | 101.8 | 118.8 | 115.4569 | 122.4669 | [7 empty] | CATEGORYB | SINGLE | EAST MCPHERSON SWITCHING STATION - REFINRY3 115.00 115KV CKT 1 | 0 | 533417 | EMCPHER3 115.00 | 533427 | REFINRY3 115.00 | 0 |  | 1 | 102.8722 | Line is owned by the City of McPherson | WERE | BPU - CITY OF MCPHERSON JOHNS-MANVILLE - EAST MCPHERSON SWITCHING STATION 115KV CKT 1 | Rebuild Line | 248 | 248 |  |  | 5.7 | 24 | 24 |  | 0.00392 | 0.03057 | 0.00456 | Line owned by City of McPherson Board of Public Utilities | [40 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T3553313SP | TO->FROM | BPU - CITY OF MCPHERSON JOHNS-MANVILLE - EAST MCPHERSON SWITCHING STATION 115KV CKT 1 | REL | WERE | WERE | WEST | WEST | 0 | 533417 | EMCPHER3 115.00 | 533426 | MANVILE3 115.00 | 0 |  | 1 | 13SP | 84 | 84 |  | 122.6 | 119.3312 | 127.5361 | [7 empty] | CATEGORYB | SINGLE | EAST MCPHERSON SWITCHING STATION - REFINRY3 115.00 115KV CKT 1 | 0 | 533417 | EMCPHER3 115.00 | 533427 | REFINRY3 115.00 | 0 |  | 1 | 107.1303 | Line is owned by the City of McPherson | WERE | BPU - CITY OF MCPHERSON JOHNS-MANVILLE - EAST MCPHERSON SWITCHING STATION 115KV CKT 1 | Rebuild Line | 248 | 248 |  |  | 5.7 | 24 | 24 |  | 0.00392 | 0.03057 | 0.00456 | Line owned by City of McPherson Board of Public Utilities | [40 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T1563313WP | TO->FROM | BPU - CITY OF MCPHERSON JOHNS-MANVILLE - EAST MCPHERSON SWITCHING STATION 115KV CKT 1 | REL | WERE | WERE | WEST | WEST | 0 | 533417 | EMCPHER3 115.00 | 533426 | MANVILE3 115.00 | 0 |  | 1 | 13WP | 84 | 84 |  |  | 93.8167 | 104.2715 | [7 empty] | CATEGORYB | SINGLE | EAST MCPHERSON SWITCHING STATION - REFINRY3 115.00 115KV CKT 1 | 0 | 533417 | EMCPHER3 115.00 | 533427 | REFINRY3 115.00 | 0 |  | 1 | 87.5881 | Line is owned by the City of McPherson | WERE | BPU - CITY OF MCPHERSON JOHNS-MANVILLE - EAST MCPHERSON SWITCHING STATION 115KV CKT 1 | Rebuild Line | 248 | 248 |  |  | 5.7 | 24 | 24 |  | 0.00392 | 0.03057 | 0.00456 | Line owned by City of McPherson Board of Public Utilities | [40 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T5913318SP | TO->FROM | BPU - CITY OF MCPHERSON JOHNS-MANVILLE - EAST MCPHERSON SWITCHING STATION 115KV CKT 1 | REL | WERE | WERE | WEST | WEST | 0 | 533417 | EMCPHER3 115.00 | 533426 | MANVILE3 115.00 | 0 |  | 1 | 18SP | 84 | 84 |  |  | 125.5957 | 135.6593 | [7 empty] | CATEGORYB | SINGLE | EAST MCPHERSON SWITCHING STATION - REFINRY3 115.00 115KV CKT 1 | 0 | 533417 | EMCPHER3 115.00 | 533427 | REFINRY3 115.00 | 0 |  | 1 | 113.9538 | Line is owned by the City of McPherson | WERE | BPU - CITY OF MCPHERSON JOHNS-MANVILLE - EAST MCPHERSON SWITCHING STATION 115KV CKT 1 | Rebuild Line | 248 | 248 |  |  | 5.7 | 24 | 24 |  | 0.00392 | 0.03057 | 0.00456 | Line owned by City of McPherson Board of Public Utilities | [40 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T5923318SP | TO->FROM | BPU - CITY OF MCPHERSON JOHNS-MANVILLE - EAST MCPHERSON SWITCHING STATION 115KV CKT 1 | REL | WERE | WERE | WEST | WEST | 0 | 533417 | EMCPHER3 115.00 | 533426 | MANVILE3 115.00 | 0 |  | 1 | 18SP | 84 | 84 |  |  | 94.5433 | 101.5796 | [7 empty] | CATEGORYB | SINGLE | BPU - CITY OF MCPHERSON PLANT - REFINRY3 115.00 115KV CKT 1 | 0 | 533427 | REFINRY3 115.00 | 533428 | MCPHER 3 115.00 | 0 |  | 1 | 85.3269 | Line is owned by the City of McPherson | WERE | BPU - CITY OF MCPHERSON JOHNS-MANVILLE - EAST MCPHERSON SWITCHING STATION 115KV CKT 1 | Rebuild Line | 248 | 248 |  |  | 5.7 | 24 | 24 |  | 0.00392 | 0.03057 | 0.00456 | Line owned by City of McPherson Board of Public Utilities | [40 empty] | 2009-04-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 1 | 2008AGP1AFS31T1011110SP | TO->FROM | BONANZA - BONANZA TAP 161KV CKT 1 | EXP | OKGE | AEPW | MUSKOGEE | GRENWOOD | 0 | 515261 | BONANZT5 161.00 | 507182 | BONANZA5 161.00 | 0 |  | 1 | 10SP | 177 | 177 |  |  | 98.7243 | 101.3517 | [7 empty] | CATEGORYB | SINGLE | AES - TARBY 161KV CKT 1 | 0 | 515262 | AES 5 161.00 | 515264 | TARBY 5 161.00 | 0 |  | 1 | 179.3925 |  | AEPW | BONANZA - BONANZA TAP 161KV CKT 1 | Rebuild 0.06 miles of 397 ACSR with 1272 ACSR & reset relay & CTs @ Bonanza or Bonanza T-Excelsior-Midland-N. Huntington 161 kV loop | 335 | 335 | 335 | 335 | 0.06 | 12 | 2 |  | 2e-05 | 0.000162 | 0.0001 | AEP: The limiting factor is 0.06 miles of 397.5 ACSR conductor. New limit for AEP will be Circuit Switcher @ Bonanza. OKGE: OG&E conductor is 795MCM ACSR up to point of interconnection rated at 236/274 MVA. Expansion Plan Project in-Service 6/1/11 | 325000 | 2006-11-14 | [38 empty] | 2010-06-01 | 2010-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T5772209SH | TO->FROM | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541235 | DUNCAN 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 | 09SH | 229 | 260 |  |  | 102.571 | 102.2395 | [7 empty] | CATEGORYB | SINGLE | PLEASANT HILL (P HILL) 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 541200 | PHILL 7 345.00 | 541225 | PHILL 5 161.00 | 541361 | PHILL T 13.800 | 1 | 265.8227 |  | MIPU | Loma Vista - Montrose 161kV Tap into K.C. South | To tap the Montrose-LomaVista 161 kV Line into KC South 161 kV sub. | [5 empty] | 18 | 18 | [5 empty] | 2369625 | 2009-03-19 | [38 empty] | 2009-06-01 | 2010-11-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 2 | 3 | 2008AGP1AFS31T7482309SP | TO->FROM | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541235 | DUNCAN 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 | 09SP | 229 | 260 | 109.7 | 109.4 | 110.3414 | 110.0812 | [7 empty] | CATEGORYB | SINGLE | PLEASANT HILL (P HILL) 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 541200 | PHILL 7 345.00 | 541225 | PHILL 5 161.00 | 541361 | PHILL T 13.800 | 1 | 286.2111 |  | MIPU | Loma Vista - Montrose 161kV Tap into K.C. South | To tap the Montrose-LomaVista 161 kV Line into KC South 161 kV sub. | [5 empty] | 18 | 18 | [5 empty] | 2369625 | 2009-03-19 | [38 empty] | 2009-06-01 | 2010-11-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T9183310SP | TO->FROM | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541235 | DUNCAN 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 | 10SP | 229 | 260 | 113.8 | 119.8 | 119.4878 | 119.7844 | [7 empty] | CATEGORYB | SINGLE | PLEASANT HILL (P HILL) 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 541200 | PHILL 7 345.00 | 541225 | PHILL 5 161.00 | 541361 | PHILL T 13.800 | 1 | 311.4394 |  | MIPU | Loma Vista - Montrose 161kV Tap into K.C. South | To tap the Montrose-LomaVista 161 kV Line into KC South 161 kV sub. | [5 empty] | 18 | 18 | [5 empty] | 2369625 | 2009-03-19 | [38 empty] | 2009-06-01 | 2010-11-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 3 | 2008AGP1AFS31T2652310SP | TO->FROM | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541235 | DUNCAN 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 | 10SP | 229 | 260 | 102.9 | 107.6 | 107.5441 | 107.7183 | [7 empty] | CATEGORYB | SINGLE | ORRICK - SIBLEYPL 161.00 161KV CKT 1 | 0 | 541244 | ORRICK 5 161.00 | 541250 | SIBLEYPL 161.00 | 0 |  | 1 | 280.0676 |  | MIPU | Loma Vista - Montrose 161kV Tap into K.C. South | To tap the Montrose-LomaVista 161 kV Line into KC South 161 kV sub. | [5 empty] | 18 | 18 | [5 empty] | 2369625 | 2009-03-19 | [38 empty] | 2009-06-01 | 2010-11-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 3 | 2008AGP1AFS31T2642310SP | TO->FROM | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541235 | DUNCAN 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 | 10SP | 229 | 260 | 101.3 | 105.9 | 105.9981 | 106.0654 | [7 empty] | CATEGORYB | SINGLE | ORRICK - RICHMOND 161KV CKT 1 | 0 | 541236 | RICHMND5 161.00 | 541244 | ORRICK 5 161.00 | 0 |  | 1 | 275.77 |  | MIPU | Loma Vista - Montrose 161kV Tap into K.C. South | To tap the Montrose-LomaVista 161 kV Line into KC South 161 kV sub. | [5 empty] | 18 | 18 | [5 empty] | 2369625 | 2009-03-19 | [38 empty] | 2009-06-01 | 2010-11-01
2008-AGP1 | AFS3 | CONT-LaCygne West Gardner 345kv | FDNS |  | FDNS |  | 2 | 3 | 2008AGP1AFS31T2742310SP | TO->FROM | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541235 | DUNCAN 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 | 10SP | 229 | 260 |  | 100.6 | 100.4948 | 100.9602 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 | 262.4965 |  | MIPU | Loma Vista - Montrose 161kV Tap into K.C. South | To tap the Montrose-LomaVista 161 kV Line into KC South 161 kV sub. | [5 empty] | 18 | 18 | [5 empty] | 2369625 | 2009-03-19 | [38 empty] | 2009-06-01 | 2010-11-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 4 | 3 | 2008AGP1AFS31T13024313SP | TO->FROM | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541235 | DUNCAN 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 | 13SP | 229 | 260 |  | 100.9 | 103.0825 | 101.8203 | [7 empty] | CATEGORYB | SINGLE | PLEASANT HILL (P HILL) 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 541200 | PHILL 7 345.00 | 541225 | PHILL 5 161.00 | 541361 | PHILL T 13.800 | 1 | 264.7328 |  | MIPU | Loma Vista - Montrose 161kV Tap into K.C. South | To tap the Montrose-LomaVista 161 kV Line into KC South 161 kV sub. | [5 empty] | 18 | 18 | [5 empty] | 2369625 | 2009-03-19 | [38 empty] | 2009-06-01 | 2010-11-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 3 | 2008AGP1AFS31T5024318SP | TO->FROM | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541235 | DUNCAN 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 | 18SP | 229 | 260 |  | 102.2 | 104.142 | 104.2014 | [7 empty] | CATEGORYB | SINGLE | GREENWOOD ENERGY CENTER - LEES SUMMIT EAST 161KV CKT 1 | 0 | 541218 | GRNWD 5 161.00 | 541233 | LEESUM 5 161.00 | 0 |  | 1 | 270.9236 |  | MIPU | Loma Vista - Montrose 161kV Tap into K.C. South | To tap the Montrose-LomaVista 161 kV Line into KC South 161 kV sub. | [5 empty] | 18 | 18 | [5 empty] | 2369625 | 2009-03-19 | [38 empty] | 2009-06-01 | 2010-11-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 3 | 2008AGP1AFS31T5094318SP | TO->FROM | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541235 | DUNCAN 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 | 18SP | 229 | 260 |  | 100.6 | 103.4069 | 103.5601 | [7 empty] | CATEGORYB | SINGLE | ORRICK - SIBLEYPL 161.00 161KV CKT 1 | 0 | 541244 | ORRICK 5 161.00 | 541250 | SIBLEYPL 161.00 | 0 |  | 1 | 269.2563 |  | MIPU | Loma Vista - Montrose 161kV Tap into K.C. South | To tap the Montrose-LomaVista 161 kV Line into KC South 161 kV sub. | [5 empty] | 18 | 18 | [5 empty] | 2369625 | 2009-03-19 | [38 empty] | 2009-06-01 | 2010-11-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 3 | 2008AGP1AFS31T5064318SP | TO->FROM | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541235 | DUNCAN 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 | 18SP | 229 | 260 |  |  | 101.0572 | 101.216 | [7 empty] | CATEGORYB | SINGLE | ORRICK - RICHMOND 161KV CKT 1 | 0 | 541236 | RICHMND5 161.00 | 541244 | ORRICK 5 161.00 | 0 |  | 1 | 263.1616 |  | MIPU | Loma Vista - Montrose 161kV Tap into K.C. South | To tap the Montrose-LomaVista 161 kV Line into KC South 161 kV sub. | [5 empty] | 18 | 18 | [5 empty] | 2369625 | 2009-03-19 | [38 empty] | 2009-06-01 | 2010-11-01
2008-AGP1 | AFS3 | 1901 - HSBIS_ELDXF | FDNS |  | FDNS |  | 3 | 2 | 2008AGP1AFS31T3933209SH | TO->FROM | BISMARK - HOT SPRINGS WEST BUS 115KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 337685 | 3HSEHVW 115.00 | 337678 | 3BISMRK 115.00 | 0 |  | 1 | 09SH | 98 | 98 | 113.2 | 120.9 | 114.2606 | 126.476 | [7 empty] | CATEGORYB | SINGLE | ELDORADO EHV - LONGWOOD 345KV CKT 1 | 0 | 508809 | LONGWD 7 345.00 | 337562 | 7ELDEHV 345.00 | 0 |  | 1 | 123.9465 |  | EES | BISMARK - HOT SPRINGS WEST BUS 115KV CKT 1 | Rebuild Transmission Line 19.61 miles | [52 empty] | 2009-04-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 2 | 2008AGP1AFS31T2583209SH | TO->FROM | BISMARK - HOT SPRINGS WEST BUS 115KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 337685 | 3HSEHVW 115.00 | 337678 | 3BISMRK 115.00 | 0 |  | 1 | 09SH | 98 | 98 | 113.1 | 120.8 | 114.232 | 126.4443 | [7 empty] | CATEGORYB | SINGLE | ELDORADO EHV 500/345KV TRANSFORMER CKT 1 | 0 | 337561 | 8ELDEHV 500.00 | 337562 | 7ELDEHV 345.00 | 0 |  | 1 | 123.9154 |  | EES | BISMARK - HOT SPRINGS WEST BUS 115KV CKT 1 | Rebuild Transmission Line 19.61 miles | [52 empty] | 2009-04-01 | 2013-06-01
2008-AGP1 | AFS3 | 1901 - HSBIS_ELDXF | FDNS |  | FDNS |  | 3 | 1 | 2008AGP1AFS31T5433109SP | TO->FROM | BISMARK - HOT SPRINGS WEST BUS 115KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 337685 | 3HSEHVW 115.00 | 337678 | 3BISMRK 115.00 | 0 |  | 1 | 09SP | 98 | 98 | 100.8 | 107.9 | 97.8523 | 110.002 | [7 empty] | CATEGORYB | SINGLE | ELDORADO EHV - LONGWOOD 345KV CKT 1 | 0 | 508809 | LONGWD 7 345.00 | 337562 | 7ELDEHV 345.00 | 0 |  | 1 | 107.802 |  | EES | BISMARK - HOT SPRINGS WEST BUS 115KV CKT 1 | Rebuild Transmission Line 19.61 miles | [52 empty] | 2009-04-01 | 2013-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V9443313SP |  | BIRD CITY 115KV | REL | SUNC |  | NORTON-D |  |  | 531365 | BIRDCTY3 115.00 | [5 empty] | 13SP | [8 empty] | 0.92896 | 0.8995 | 0.99784 | 0.9 | 1.05 | CATEGORYB | SINGLE | MINGO (MINGO) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 531451 | MINGO 7 345.00 | 531429 | MINGO 3 115.00 | 531452 | MINGTER1 13.800 | 1 |  |  | SUNC | RULETON 115KV Capacitor | Install Second 12 Mvar cap bank at Ruleton 115kV | [12 empty] | 486000 | 2008-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17263318SP |  | BIRD CITY 115KV | REL | SUNC |  | NORTON-D |  |  | 531365 | BIRDCTY3 115.00 | [5 empty] | 18SP | [8 empty] | 0.916 | 0.88455 | 0.99001 | 0.9 | 1.05 | CATEGORYB | SINGLE | MINGO (MINGO) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 531451 | MINGO 7 345.00 | 531429 | MINGO 3 115.00 | 531452 | MINGTER1 13.800 | 1 |  |  | SUNC | RULETON 115KV Capacitor | Install Second 12 Mvar cap bank at Ruleton 115kV | [12 empty] | 486000 | 2008-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T1662210SP | FROM->TO | BETHEL - NASHOBA 138KV CKT 1 | S | AEPW | AEPW | TS-WFEC | TS-WFEC | 0 | 510928 | BETHEL 4 138.00 | 510927 | NASHOBA4 138.00 | 0 |  | 1 | 10SP | 88 | 107 |  | 105.8 | 115.481 | 107.5687 | [7 empty] | CATEGORYB | SINGLE | PITTSBURG - VALLIANT 345KV CKT 1 | 0 | 510907 | PITTSB-7 345.00 | 510911 | VALIANT7 345.00 | 0 |  | 1 | 115.0985 |  | AEPW | BETHEL - NASHOBA 138KV CKT 1 | Interim redispatch | [52 empty] | 2010-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T1632210SP | TO->FROM | BETHEL - BROKEN BOW 138KV CKT 1 | S | SWPA | AEPW | EMINTH | TS-WFEC | 0 | 505614 | BRKN BW4 138.00 | 510928 | BETHEL 4 138.00 | 0 |  | 1 | 10SP | 88 | 107 |  | 110.9 | 120.6271 | 112.6674 | [7 empty] | CATEGORYB | SINGLE | PITTSBURG - VALLIANT 345KV CKT 1 | 0 | 510907 | PITTSB-7 345.00 | 510911 | VALIANT7 345.00 | 0 |  | 1 | 120.5541 |  | AEPW | BETHEL - BROKEN BOW 138KV CKT 1 | Interim redispatch | [52 empty] | 2010-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 1 | 2008AGP1AFS31T931109G | FROM->TO | BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541340 | BELTONS5 161.00 | 541259 | TURNER 5 161.00 | 0 |  | 1 | 09G | 233 | 265 |  | 103.6 | 103.658 | 104.8771 | [7 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 | 277.9243 |  | MIPU | South Harper 161 kV cut-in to Stilwell-Archie JCT 161 kV line | To tap Stilwell-Archie JCT 161 kV line into South Harper 161 kV sub and make it two new 161 kV sections: Stilwell-South Harper and Archie JCT- South Harper . | [5 empty] | 18 | 18 | [5 empty] | 2259673 | 2009-03-19 | [38 empty] | 2009-04-01 | 2010-10-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 1 | 2008AGP1AFS31T1001109SH | FROM->TO | BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541340 | BELTONS5 161.00 | 541259 | TURNER 5 161.00 | 0 |  | 1 | 09SH | 233 | 265 | 107.1 | 107.1 | 106.1301 | 107.6116 | [7 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 | 285.1707 |  | MIPU | South Harper 161 kV cut-in to Stilwell-Archie JCT 161 kV line | To tap Stilwell-Archie JCT 161 kV line into South Harper 161 kV sub and make it two new 161 kV sections: Stilwell-South Harper and Archie JCT- South Harper . | [5 empty] | 18 | 18 | [5 empty] | 2259673 | 2009-03-19 | [38 empty] | 2009-04-01 | 2010-10-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 1 | 2008AGP1AFS31T1701109SP | FROM->TO | BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541340 | BELTONS5 161.00 | 541259 | TURNER 5 161.00 | 0 |  | 1 | 09SP | 233 | 265 | 110.5 | 112.4 | 112.4319 | 113.6944 | [7 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 | 301.2902 |  | MIPU | South Harper 161 kV cut-in to Stilwell-Archie JCT 161 kV line | To tap Stilwell-Archie JCT 161 kV line into South Harper 161 kV sub and make it two new 161 kV sections: Stilwell-South Harper and Archie JCT- South Harper . | [5 empty] | 18 | 18 | [5 empty] | 2259673 | 2009-03-19 | [38 empty] | 2009-04-01 | 2010-10-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 1 | 1 | 2008AGP1AFS31T1751109SP | FROM->TO | BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541340 | BELTONS5 161.00 | 541259 | TURNER 5 161.00 | 0 |  | 1 | 09SP | 233 | 265 |  |  | 99.394 | 100.0619 | [7 empty] | CATEGORYB | SINGLE | REDEL - STILWELL 161KV CKT 1 | 0 | 542969 | STILWEL5 161.00 | 543053 | REDEL 5 161.00 | 0 |  | 1 | 265.164 |  | MIPU | South Harper 161 kV cut-in to Stilwell-Archie JCT 161 kV line | To tap Stilwell-Archie JCT 161 kV line into South Harper 161 kV sub and make it two new 161 kV sections: Stilwell-South Harper and Archie JCT- South Harper . | [5 empty] | 18 | 18 | [5 empty] | 2259673 | 2009-03-19 | [38 empty] | 2009-04-01 | 2010-10-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 1 | 2008AGP1AFS31T951109WP | FROM->TO | BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541340 | BELTONS5 161.00 | 541259 | TURNER 5 161.00 | 0 |  | 1 | 09WP | 233 | 265 |  | 107.5 | 105.939 | 109.7064 | [7 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 | 290.722 |  | MIPU | South Harper 161 kV cut-in to Stilwell-Archie JCT 161 kV line | To tap Stilwell-Archie JCT 161 kV line into South Harper 161 kV sub and make it two new 161 kV sections: Stilwell-South Harper and Archie JCT- South Harper . | [5 empty] | 18 | 18 | [5 empty] | 2259673 | 2009-03-19 | [38 empty] | 2009-04-01 | 2010-10-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 1 | 2008AGP1AFS31T2143110SP | FROM->TO | BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541340 | BELTONS5 161.00 | 541259 | TURNER 5 161.00 | 0 |  | 1 | 10SP | 233 | 265 |  | 112.6 | 110.7624 | 115.8451 | [7 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 | 306.9895 |  | MIPU | South Harper 161 kV cut-in to Stilwell-Archie JCT 161 kV line | To tap Stilwell-Archie JCT 161 kV line into South Harper 161 kV sub and make it two new 161 kV sections: Stilwell-South Harper and Archie JCT- South Harper . | [5 empty] | 18 | 18 | [5 empty] | 2259673 | 2009-03-19 | [38 empty] | 2009-04-01 | 2010-10-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 1 | 2008AGP1AFS31T2243110SP | FROM->TO | BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541340 | BELTONS5 161.00 | 541259 | TURNER 5 161.00 | 0 |  | 1 | 10SP | 233 | 265 |  | 100.7 | 98.7233 | 102.9112 | [7 empty] | CATEGORYB | SINGLE | REDEL - STILWELL 161KV CKT 1 | 0 | 542969 | STILWEL5 161.00 | 543053 | REDEL 5 161.00 | 0 |  | 1 | 272.7147 |  | MIPU | South Harper 161 kV cut-in to Stilwell-Archie JCT 161 kV line | To tap Stilwell-Archie JCT 161 kV line into South Harper 161 kV sub and make it two new 161 kV sections: Stilwell-South Harper and Archie JCT- South Harper . | [5 empty] | 18 | 18 | [5 empty] | 2259673 | 2009-03-19 | [38 empty] | 2009-04-01 | 2010-10-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 4 | 2008AGP1AFS31T903410WP | FROM->TO | BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541340 | BELTONS5 161.00 | 541259 | TURNER 5 161.00 | 0 |  | 1 | 10WP | 233 | 265 |  |  | 97.1656 | 102.1022 | [7 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 | 270.5708 |  | MIPU | South Harper 161 kV cut-in to Stilwell-Archie JCT 161 kV line | To tap Stilwell-Archie JCT 161 kV line into South Harper 161 kV sub and make it two new 161 kV sections: Stilwell-South Harper and Archie JCT- South Harper . | [5 empty] | 18 | 18 | [5 empty] | 2259673 | 2009-03-19 | [38 empty] | 2009-04-01 | 2010-10-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T3451313SP | FROM->TO | BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541340 | BELTONS5 161.00 | 541259 | TURNER 5 161.00 | 0 |  | 1 | 13SP | 233 | 265 |  | 109 | 107.5601 | 112.245 | [7 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 | 297.4493 |  | MIPU | South Harper 161 kV cut-in to Stilwell-Archie JCT 161 kV line | To tap Stilwell-Archie JCT 161 kV line into South Harper 161 kV sub and make it two new 161 kV sections: Stilwell-South Harper and Archie JCT- South Harper . | [5 empty] | 18 | 18 | [5 empty] | 2259673 | 2009-03-19 | [38 empty] | 2009-04-01 | 2010-10-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T3561313SP | FROM->TO | BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541340 | BELTONS5 161.00 | 541259 | TURNER 5 161.00 | 0 |  | 1 | 13SP | 233 | 265 |  | 104.7 | 102.822 | 106.5567 | [7 empty] | CATEGORYB | SINGLE | REDEL - STILWELL 161KV CKT 1 | 0 | 542969 | STILWEL5 161.00 | 543053 | REDEL 5 161.00 | 0 |  | 1 | 282.3753 |  | MIPU | South Harper 161 kV cut-in to Stilwell-Archie JCT 161 kV line | To tap Stilwell-Archie JCT 161 kV line into South Harper 161 kV sub and make it two new 161 kV sections: Stilwell-South Harper and Archie JCT- South Harper . | [5 empty] | 18 | 18 | [5 empty] | 2259673 | 2009-03-19 | [38 empty] | 2009-04-01 | 2010-10-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T3511313SP | FROM->TO | BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541340 | BELTONS5 161.00 | 541259 | TURNER 5 161.00 | 0 |  | 1 | 13SP | 233 | 265 |  | 104.1 | 102.493 | 105.3004 | [7 empty] | CATEGORYB | SINGLE | BELTON SOUTH 161/69KV TRANSFORMER CKT 1 | 0 | 541290 | BELTONS2 69.000 | 541340 | BELTONS5 161.00 | 0 |  | 1 | 279.0461 |  | MIPU | South Harper 161 kV cut-in to Stilwell-Archie JCT 161 kV line | To tap Stilwell-Archie JCT 161 kV line into South Harper 161 kV sub and make it two new 161 kV sections: Stilwell-South Harper and Archie JCT- South Harper . | [5 empty] | 18 | 18 | [5 empty] | 2259673 | 2009-03-19 | [38 empty] | 2009-04-01 | 2010-10-01
2008-AGP1 | AFS3 | CONT-LaCygne Stilwell 345kv | FDNS |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T3541313SP | FROM->TO | BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541340 | BELTONS5 161.00 | 541259 | TURNER 5 161.00 | 0 |  | 1 | 13SP | 233 | 265 |  | 102.4 | 100.4306 | 104.0056 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - WEST GARDNER 345KV CKT 1 | 0 | 542965 | W.GRDNR7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 | 275.6148 |  | MIPU | South Harper 161 kV cut-in to Stilwell-Archie JCT 161 kV line | To tap Stilwell-Archie JCT 161 kV line into South Harper 161 kV sub and make it two new 161 kV sections: Stilwell-South Harper and Archie JCT- South Harper . | [5 empty] | 18 | 18 | [5 empty] | 2259673 | 2009-03-19 | [38 empty] | 2009-04-01 | 2010-10-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T13191313SP | FROM->TO | BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541340 | BELTONS5 161.00 | 541259 | TURNER 5 161.00 | 0 |  | 1 | 13SP | 233 | 265 |  | 100.4 | 98.5236 | 101.7955 | [7 empty] | CATEGORYB | SINGLE | STILWELL (STLWL 22) 345/161/13.8KV TRANSFORMER CKT 22 | 1 | 542968 | STILWEL7 345.00 | 542969 | STILWEL5 161.00 | 543648 | STIL T22 13.800 | 22 | 269.7581 |  | MIPU | South Harper 161 kV cut-in to Stilwell-Archie JCT 161 kV line | To tap Stilwell-Archie JCT 161 kV line into South Harper 161 kV sub and make it two new 161 kV sections: Stilwell-South Harper and Archie JCT- South Harper . | [5 empty] | 18 | 18 | [5 empty] | 2259673 | 2009-03-19 | [38 empty] | 2009-04-01 | 2010-10-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T81313SP | FROM->TO | BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541340 | BELTONS5 161.00 | 541259 | TURNER 5 161.00 | 0 |  | 1 | 13SP | 233 | 265 |  | 100.3 | 98.6143 | 101.5342 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | 269.0656 |  | MIPU | South Harper 161 kV cut-in to Stilwell-Archie JCT 161 kV line | To tap Stilwell-Archie JCT 161 kV line into South Harper 161 kV sub and make it two new 161 kV sections: Stilwell-South Harper and Archie JCT- South Harper . | [5 empty] | 18 | 18 | [5 empty] | 2259673 | 2009-03-19 | [38 empty] | 2009-04-01 | 2010-10-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 1 | 2008AGP1AFS31T1283113WP | FROM->TO | BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541340 | BELTONS5 161.00 | 541259 | TURNER 5 161.00 | 0 |  | 1 | 13WP | 233 | 265 |  | 102.9 | 100.2671 | 105.9577 | [7 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 | 280.7879 |  | MIPU | South Harper 161 kV cut-in to Stilwell-Archie JCT 161 kV line | To tap Stilwell-Archie JCT 161 kV line into South Harper 161 kV sub and make it two new 161 kV sections: Stilwell-South Harper and Archie JCT- South Harper . | [5 empty] | 18 | 18 | [5 empty] | 2259673 | 2009-03-19 | [38 empty] | 2009-04-01 | 2010-10-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T5641318SP | FROM->TO | BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541340 | BELTONS5 161.00 | 541259 | TURNER 5 161.00 | 0 |  | 1 | 18SP | 233 | 265 |  | 111.7 | 112.8272 | 114.5503 | [7 empty] | CATEGORYB | SINGLE | PECULIAR - PLEASANT HILL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 541200 | PHILL 7 345.00 | 0 |  | 1 | 303.5583 |  | MIPU | South Harper 161 kV cut-in to Stilwell-Archie JCT 161 kV line | To tap Stilwell-Archie JCT 161 kV line into South Harper 161 kV sub and make it two new 161 kV sections: Stilwell-South Harper and Archie JCT- South Harper . | [5 empty] | 18 | 18 | [5 empty] | 2259673 | 2009-03-19 | [38 empty] | 2009-04-01 | 2010-10-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T6483318SP | FROM->TO | BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541340 | BELTONS5 161.00 | 541259 | TURNER 5 161.00 | 0 |  | 1 | 18SP | 233 | 265 |  | 108.8 | 106.1131 | 110.9825 | [7 empty] | CATEGORYB | SINGLE | REDEL - STILWELL 161KV CKT 1 | 0 | 542969 | STILWEL5 161.00 | 543053 | REDEL 5 161.00 | 0 |  | 1 | 294.1036 |  | MIPU | South Harper 161 kV cut-in to Stilwell-Archie JCT 161 kV line | To tap Stilwell-Archie JCT 161 kV line into South Harper 161 kV sub and make it two new 161 kV sections: Stilwell-South Harper and Archie JCT- South Harper . | [5 empty] | 18 | 18 | [5 empty] | 2259673 | 2009-03-19 | [38 empty] | 2009-04-01 | 2010-10-01
2008-AGP1 | AFS3 | CONT-LaCygne Stilwell 345kv | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T6443318SP | FROM->TO | BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541340 | BELTONS5 161.00 | 541259 | TURNER 5 161.00 | 0 |  | 1 | 18SP | 233 | 265 |  | 106.3 | 103.4296 | 108.3884 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - WEST GARDNER 345KV CKT 1 | 0 | 542965 | W.GRDNR7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 | 287.2293 |  | MIPU | South Harper 161 kV cut-in to Stilwell-Archie JCT 161 kV line | To tap Stilwell-Archie JCT 161 kV line into South Harper 161 kV sub and make it two new 161 kV sections: Stilwell-South Harper and Archie JCT- South Harper . | [5 empty] | 18 | 18 | [5 empty] | 2259673 | 2009-03-19 | [38 empty] | 2009-04-01 | 2010-10-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T6413318SP | FROM->TO | BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541340 | BELTONS5 161.00 | 541259 | TURNER 5 161.00 | 0 |  | 1 | 18SP | 233 | 265 |  | 106.3 | 104.1354 | 107.9858 | [7 empty] | CATEGORYB | SINGLE | BELTON SOUTH 161/69KV TRANSFORMER CKT 1 | 0 | 541290 | BELTONS2 69.000 | 541340 | BELTONS5 161.00 | 0 |  | 1 | 286.1624 |  | MIPU | South Harper 161 kV cut-in to Stilwell-Archie JCT 161 kV line | To tap Stilwell-Archie JCT 161 kV line into South Harper 161 kV sub and make it two new 161 kV sections: Stilwell-South Harper and Archie JCT- South Harper . | [5 empty] | 18 | 18 | [5 empty] | 2259673 | 2009-03-19 | [38 empty] | 2009-04-01 | 2010-10-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T26753318SP | FROM->TO | BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541340 | BELTONS5 161.00 | 541259 | TURNER 5 161.00 | 0 |  | 1 | 18SP | 233 | 265 |  | 104.1 | 101.4872 | 105.9536 | [7 empty] | CATEGORYB | SINGLE | STILWELL (STLWL 22) 345/161/13.8KV TRANSFORMER CKT 22 | 1 | 542968 | STILWEL7 345.00 | 542969 | STILWEL5 161.00 | 543648 | STIL T22 13.800 | 22 | 280.777 |  | MIPU | South Harper 161 kV cut-in to Stilwell-Archie JCT 161 kV line | To tap Stilwell-Archie JCT 161 kV line into South Harper 161 kV sub and make it two new 161 kV sections: Stilwell-South Harper and Archie JCT- South Harper . | [5 empty] | 18 | 18 | [5 empty] | 2259673 | 2009-03-19 | [38 empty] | 2009-04-01 | 2010-10-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T153318SP | FROM->TO | BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541340 | BELTONS5 161.00 | 541259 | TURNER 5 161.00 | 0 |  | 1 | 18SP | 233 | 265 |  | 104.2 | 101.7783 | 105.8756 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | 280.5703 |  | MIPU | South Harper 161 kV cut-in to Stilwell-Archie JCT 161 kV line | To tap Stilwell-Archie JCT 161 kV line into South Harper 161 kV sub and make it two new 161 kV sections: Stilwell-South Harper and Archie JCT- South Harper . | [5 empty] | 18 | 18 | [5 empty] | 2259673 | 2009-03-19 | [38 empty] | 2009-04-01 | 2010-10-01
2008-AGP1 | AFS3 | CONT-0800 - Stranger Creek - Craig 345kV |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T5503318SP | FROM->TO | BELTON SOUTH - TURNER ROAD SUBSTATION 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541340 | BELTONS5 161.00 | 541259 | TURNER 5 161.00 | 0 |  | 1 | 18SP | 233 | 265 |  |  | 95.2487 | 100.2626 | [7 empty] | CATEGORYB | SINGLE | CRAIG - STRANGER CREEK 345KV CKT 1 | 0 | 532772 | STRANGR7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 | 265.6959 |  | MIPU | South Harper 161 kV cut-in to Stilwell-Archie JCT 161 kV line | To tap Stilwell-Archie JCT 161 kV line into South Harper 161 kV sub and make it two new 161 kV sections: Stilwell-South Harper and Archie JCT- South Harper . | [5 empty] | 18 | 18 | [5 empty] | 2259673 | 2009-03-19 | [38 empty] | 2009-04-01 | 2010-10-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V3445509SP |  | BELOIT 115KV | EXP | MKEC |  |  |  |  | 539650 | BELOIT 3 115.00 | [5 empty] | 09SP | [8 empty] | 0.84646 | 0.80206 | 0.9774 | 0.9 | 1.05 | CATEGORYB | SINGLE | CONCORDIA - ELMCREK6 230.00 230KV CKT 1 | 0 | 539639 | ELMCREK6 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V7285509SP |  | BELOIT 115KV | EXP | MKEC |  |  |  |  | 539650 | BELOIT 3 115.00 | [5 empty] | 09SP | [8 empty] | 0.84651 | 0.80213 | 0.9774 | 0.9 | 1.05 | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539658 | CONCRD6 230.00 | 539657 | CONCORD3 115.00 | 539904 | CONCOD-T 13.800 | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V2475509SP |  | BELOIT 115KV | EXP | MKEC |  |  |  |  | 539650 | BELOIT 3 115.00 | [5 empty] | 09SP | [8 empty] | 0.85811 | 0.81578 | 0.9774 | 0.9 | 1.05 | CATEGORYB | SINGLE | EAST MANHATTAN - ELMCREK6 230.00 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 539639 | ELMCREK6 230.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FNSL | FDNS-Iteration limit exceeded | 3 | 2 | 2008AGP1AFS32V33213SP |  | BELOIT 115KV | EXP | MKEC |  |  |  |  | 539650 | BELOIT 3 115.00 | [5 empty] | 13SP | [8 empty] | 1.0054 | 0.76848 | 1.0072 | 0.9 | 1.05 | CATEGORYB | SINGLE | EAST MANHATTAN - ELMCREK6 230.00 230KV CKT 1 | 0 | 539639 | ELMCREK6 230.00 | 532861 | EMANHAT6 230.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V7475518SP |  | BELOIT 115KV | EXP | MKEC |  |  |  |  | 539650 | BELOIT 3 115.00 | [5 empty] | 18SP | [8 empty] | 0.90935 | 0.88637 | 0.97418 | 0.9 | 1.05 | CATEGORYB | SINGLE | BELOIT - CONCORDIA 115KV CKT 1 | 0 | 539657 | CONCORD3 115.00 | 539650 | BELOIT 3 115.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 2 | 2008AGP1AFS31T3083210SP | FROM->TO | BEATRCE7 115.00 - HARBINE7 115.00 115KV CKT 1 | S | NPPD | NPPD | BROOKFLD | BROOKFLD | 0 | 640076 | BEATRCE7 115.00 | 640208 | HARBINE7 115.00 | 0 |  | 1 | 10SP | 80 | 88 |  | 102.3 | 101.7364 | 109.3845 | [7 empty] | CATEGORYB | SINGLE | CONCORDIA - ELMCREK6 230.00 230KV CKT 1 | 0 | 539639 | ELMCREK6 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 | 96.2584 |  | NPPD | BEATRCE7 115.00 - HARBINE7 115.00 115KV CKT 1 | Indeterminate | [52 empty] | 2010-06-01 | 2010-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 2 | 2008AGP1AFS31T11053210SP | FROM->TO | BEATRCE7 115.00 - HARBINE7 115.00 115KV CKT 1 | S | NPPD | NPPD | BROOKFLD | BROOKFLD | 0 | 640076 | BEATRCE7 115.00 | 640208 | HARBINE7 115.00 | 0 |  | 1 | 10SP | 80 | 88 |  | 102.3 | 101.7328 | 109.3739 | [7 empty] | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539657 | CONCORD3 115.00 | 539658 | CONCRD6 230.00 | 539904 | CONCOD-T 13.800 | 1 | 96.249 |  | NPPD | BEATRCE7 115.00 - HARBINE7 115.00 115KV CKT 1 | Indeterminate | [52 empty] | 2010-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T1625510SP | FROM->TO | BEATRCE7 115.00 - HARBINE7 115.00 115KV CKT 1 | S | NPPD | NPPD | BROOKFLD | BROOKFLD | 0 | 640076 | BEATRCE7 115.00 | 640208 | HARBINE7 115.00 | 0 |  | 1 | 10SP | 80 | 88 |  | 108.7 | 106.676 | 106.4001 | [7 empty] | CATEGORYB | SINGLE | EAST MANHATTAN - ELMCREK6 230.00 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 539639 | ELMCREK6 230.00 | 0 |  | 1 | 93.6321 |  | NPPD | BEATRCE7 115.00 - HARBINE7 115.00 115KV CKT 1 | Indeterminate | [52 empty] | 2010-06-01 | 2010-06-01
2008-AGP1 | AFS3 | 5073 - BVSNBVNESDEL | FDNS |  | FDNS |  | 2 | 3 | 2008AGP1AFS31T452309FA | FROM->TO | BARTLESVILLE SOUTHEAST - NORTH BARTLESVILLE 138KV CKT 1 | CP | AEPW | AEPW | NORTHERN | TS-KAMO | 0 | 510391 | BV-SE--4 138.00 | 510386 | NBVILLE4 138.00 | 0 |  | 1 | 09FA | 215 | 237 |  | 109.1 | 110.0776 | 113.7458 | [7 empty] | CATEGORYB | SINGLE | DELAWARE - NORTHEAST STATION 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 510406 | N.E.S.-7 345.00 | 0 |  | 1 | 269.5775 |  | AEPW | BARTLESVILLE SOUTHEAST - NORTH BARTLESVILLE 138KV CKT 1 | Rebuild 8.37 miles of 795 ACSR with 1590 ACSR & reset relays @ BSE | 280 | 287 | 287 | 287 | 8.37 | 24 | 9 |  | 0.00286 | 0.030814 | 0.0097 | New limits will be wavetrap jumpers, breakers & switches | 8400000 | 2007-08-13 | [38 empty] | 2009-04-01 | 2011-06-01
2008-AGP1 | AFS3 | 5073 - BVSNBVNESDEL |  |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T401309G | FROM->TO | BARTLESVILLE SOUTHEAST - NORTH BARTLESVILLE 138KV CKT 1 | CP | AEPW | AEPW | NORTHERN | TS-KAMO | 0 | 510391 | BV-SE--4 138.00 | 510386 | NBVILLE4 138.00 | 0 |  | 1 | 09G | 215 | 237 |  |  | 100.7201 | 105.1508 | [7 empty] | CATEGORYB | SINGLE | DELAWARE - NORTHEAST STATION 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 510406 | N.E.S.-7 345.00 | 0 |  | 1 | 249.2074 |  | AEPW | BARTLESVILLE SOUTHEAST - NORTH BARTLESVILLE 138KV CKT 1 | Rebuild 8.37 miles of 795 ACSR with 1590 ACSR & reset relays @ BSE | 280 | 287 | 287 | 287 | 8.37 | 24 | 9 |  | 0.00286 | 0.030814 | 0.0097 | New limits will be wavetrap jumpers, breakers & switches | 8400000 | 2007-08-13 | [38 empty] | 2009-04-01 | 2011-06-01
2008-AGP1 | AFS3 | 5073 - BVSNBVNESDEL | FDNS |  | FDNS |  | 1 | 3 | 2008AGP1AFS31T571309SH | FROM->TO | BARTLESVILLE SOUTHEAST - NORTH BARTLESVILLE 138KV CKT 1 | CP | AEPW | AEPW | NORTHERN | TS-KAMO | 0 | 510391 | BV-SE--4 138.00 | 510386 | NBVILLE4 138.00 | 0 |  | 1 | 09SH | 202 | 235 |  | 105.8 | 109.0701 | 111.3204 | [7 empty] | CATEGORYB | SINGLE | DELAWARE - NORTHEAST STATION 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 510406 | N.E.S.-7 345.00 | 0 |  | 1 | 261.6029 |  | AEPW | BARTLESVILLE SOUTHEAST - NORTH BARTLESVILLE 138KV CKT 1 | Rebuild 8.37 miles of 795 ACSR with 1590 ACSR & reset relays @ BSE | 280 | 287 | 287 | 287 | 8.37 | 24 | 9 |  | 0.00286 | 0.030814 | 0.0097 | New limits will be wavetrap jumpers, breakers & switches | 8400000 | 2007-08-13 | [38 empty] | 2009-04-01 | 2011-06-01
2008-AGP1 | AFS3 | 5073 - BVSNBVNESDEL |  |  | FDNS |  | 4 | 3 | 2008AGP1AFS31T734309SP | FROM->TO | BARTLESVILLE SOUTHEAST - NORTH BARTLESVILLE 138KV CKT 1 | CP | AEPW | AEPW | NORTHERN | TS-KAMO | 0 | 510391 | BV-SE--4 138.00 | 510386 | NBVILLE4 138.00 | 0 |  | 1 | 09SP | 202 | 235 |  |  | 101.629 | 103.8471 | [7 empty] | CATEGORYB | SINGLE | DELAWARE - NORTHEAST STATION 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 510406 | N.E.S.-7 345.00 | 0 |  | 1 | 244.0407 |  | AEPW | BARTLESVILLE SOUTHEAST - NORTH BARTLESVILLE 138KV CKT 1 | Rebuild 8.37 miles of 795 ACSR with 1590 ACSR & reset relays @ BSE | 280 | 287 | 287 | 287 | 8.37 | 24 | 9 |  | 0.00286 | 0.030814 | 0.0097 | New limits will be wavetrap jumpers, breakers & switches | 8400000 | 2007-08-13 | [38 empty] | 2009-04-01 | 2011-06-01
2008-AGP1 | AFS3 | 5073 - BVSNBVNESDEL | FDNS |  | FDNS |  | 2 | 3 | 2008AGP1AFS31T562309WP | FROM->TO | BARTLESVILLE SOUTHEAST - NORTH BARTLESVILLE 138KV CKT 1 | CP | AEPW | AEPW | NORTHERN | TS-KAMO | 0 | 510391 | BV-SE--4 138.00 | 510386 | NBVILLE4 138.00 | 0 |  | 1 | 09WP | 215 | 237 |  | 110.9 | 110.5661 | 112.8883 | [7 empty] | CATEGORYB | SINGLE | DELAWARE - NORTHEAST STATION 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 510406 | N.E.S.-7 345.00 | 0 |  | 1 | 267.5453 |  | AEPW | BARTLESVILLE SOUTHEAST - NORTH BARTLESVILLE 138KV CKT 1 | Rebuild 8.37 miles of 795 ACSR with 1590 ACSR & reset relays @ BSE | 280 | 287 | 287 | 287 | 8.37 | 24 | 9 |  | 0.00286 | 0.030814 | 0.0097 | New limits will be wavetrap jumpers, breakers & switches | 8400000 | 2007-08-13 | [38 empty] | 2009-04-01 | 2011-06-01
2008-AGP1 | AFS3 | 5073 - BVSNBVNESDEL |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T1013310SP | FROM->TO | BARTLESVILLE SOUTHEAST - NORTH BARTLESVILLE 138KV CKT 1 | CP | AEPW | AEPW | NORTHERN | TS-KAMO | 0 | 510391 | BV-SE--4 138.00 | 510386 | NBVILLE4 138.00 | 0 |  | 1 | 10SP | 202 | 235 |  |  | 99.0372 | 106.2486 | [7 empty] | CATEGORYB | SINGLE | DELAWARE - NORTHEAST STATION 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 510406 | N.E.S.-7 345.00 | 0 |  | 1 | 249.6842 |  | AEPW | BARTLESVILLE SOUTHEAST - NORTH BARTLESVILLE 138KV CKT 1 | Rebuild 8.37 miles of 795 ACSR with 1590 ACSR & reset relays @ BSE | 280 | 287 | 287 | 287 | 8.37 | 24 | 9 |  | 0.00286 | 0.030814 | 0.0097 | New limits will be wavetrap jumpers, breakers & switches | 8400000 | 2007-08-13 | [38 empty] | 2009-04-01 | 2011-06-01
2008-AGP1 | AFS3 | 5073 - BVSNBVNESDEL | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T623310WP | FROM->TO | BARTLESVILLE SOUTHEAST - NORTH BARTLESVILLE 138KV CKT 1 | CP | AEPW | AEPW | NORTHERN | TS-KAMO | 0 | 510391 | BV-SE--4 138.00 | 510386 | NBVILLE4 138.00 | 0 |  | 1 | 10WP | 215 | 237 |  | 111.5 | 109.8539 | 119.7172 | [7 empty] | CATEGORYB | SINGLE | DELAWARE - NORTHEAST STATION 345KV CKT 1 | 0 | 510380 | DELWARE7 345.00 | 510406 | N.E.S.-7 345.00 | 0 |  | 1 | 283.7298 |  | AEPW | BARTLESVILLE SOUTHEAST - NORTH BARTLESVILLE 138KV CKT 1 | Rebuild 8.37 miles of 795 ACSR with 1590 ACSR & reset relays @ BSE | 280 | 287 | 287 | 287 | 8.37 | 24 | 9 |  | 0.00286 | 0.030814 | 0.0097 | New limits will be wavetrap jumpers, breakers & switches | 8400000 | 2007-08-13 | [38 empty] | 2009-04-01 | 2011-06-01
GEN-2006-010 | Turk | [7 empty] | 508054508075012SP | FROM->TO | BANN - RED SPRINGS REC 138KV CKT 1 | U | AEPW | AEPW | TEXARK | TXARNTEC | 0 | 508054 | BANN 4 138.00 | 508075 | REDSPRG4 138.00 | 0 |  | 1 |  | 224 | 261 |  |  | 72.8 | [9 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | AEPW | BANN - RED SPRINGS REC 138KV CKT 1 | Replace 138 kV breakers 3300 & 3310 | [11 empty] | 300000 | 300000 | [39 empty] | 2012-07-01 | 2012-07-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V1515509SH |  | BAILEYVILLE N.M. STATION (NEMAHA MARSHALL R 115KV | EXP | WERE |  | NCENTRAL |  |  | 533322 | BAILEYV3 115.00 | [5 empty] | 09SH | [6 empty] | 0.80626 | 0.7779 | 0.80677 | 0.69803 | 0.99788 | 0.93 | 1.05 | CATEGORYB | SINGLE | KELLY - SOUTH SENECA 115KV CKT 1 | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 3 | 2008AGP1AFS31V2831309SP |  | BAILEYVILLE N.M. STATION (NEMAHA MARSHALL R 115KV | EXP | WERE |  | NCENTRAL |  |  | 533322 | BAILEYV3 115.00 | [5 empty] | 09SP | [6 empty] | 0.81985 | 0.64187 | 0.82713 | 0.42676 | 0.99533 | 0.93 | 1.05 | CATEGORYB | SINGLE | KELLY - SOUTH SENECA 115KV CKT 1 | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 |  |  |  | 2009-04-01 | 2009-04-01 | 2009-04-01 | 41640 | 41640 | 1 | 1 | 2014 | 41897 | 42156 | 40179 | 41640 | 2014-01-01 | 2010-06-01 | [13 empty] | Ph1: 10.8 Mvar cap bank at Seneca 115 kV 09S. Ph2: Knob Hill -S. Beatrice 115 kV 10S | [7 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31V3155509SP |  | BAILEYVILLE N.M. STATION (NEMAHA MARSHALL R 115KV | EXP | WERE |  | NCENTRAL |  |  | 533322 | BAILEYV3 115.00 | [5 empty] | 09SP | [8 empty] | 0.88093 | 0.86023 | 0.99491 | 0.93 | 1.05 | CATEGORYB | SINGLE | BAILEYVILLE N.M. STATION (NEMAHA MARSHALL R - SOUTH SENECA 115KV CKT 1 | 0 | 533337 | SENECA 3 115.00 | 533322 | BAILEYV3 115.00 | 0 |  | 1 |  |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T1715509SP | TO->FROM | BAILEYVILLE N.M. STATION (NEMAHA MARSHALL R - SOUTH SENECA 115KV CKT 1 | EXP | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533337 | SENECA 3 115.00 | 533322 | BAILEYV3 115.00 | 0 |  | 1 | 09SP | 92 | 92 |  |  | 109.5486 | 115.0795 | [7 empty] | CATEGORYB | SINGLE | CONCORDIA - ELMCREK6 230.00 230KV CKT 1 | 0 | 539639 | ELMCREK6 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 | 105.8731 |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 |  |  |  | 2009-04-01 | 2009-04-01 | 2009-04-01 | 41640 | 41640 | 1 | 1 | 2014 | 41897 | 42156 | 40179 | 41640 | 2014-01-01 | 2010-06-01 | [13 empty] | Ph1: 10.8 Mvar cap bank at Seneca 115 kV 09S. Ph2: Knob Hill -S. Beatrice 115 kV 10S | [7 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T6775509SP | TO->FROM | BAILEYVILLE N.M. STATION (NEMAHA MARSHALL R - SOUTH SENECA 115KV CKT 1 | EXP | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533337 | SENECA 3 115.00 | 533322 | BAILEYV3 115.00 | 0 |  | 1 | 09SP | 92 | 92 |  |  | 109.5438 | 115.0731 | [7 empty] | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539657 | CONCORD3 115.00 | 539658 | CONCRD6 230.00 | 539904 | CONCOD-T 13.800 | 1 | 105.8672 |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T1315509SP | TO->FROM | BAILEYVILLE N.M. STATION (NEMAHA MARSHALL R - SOUTH SENECA 115KV CKT 1 | EXP | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533337 | SENECA 3 115.00 | 533322 | BAILEYV3 115.00 | 0 |  | 1 | 09SP | 92 | 92 |  |  | 109.2211 | 114.4027 | [7 empty] | CATEGORYB | SINGLE | EAST MANHATTAN - ELMCREK6 230.00 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 539639 | ELMCREK6 230.00 | 0 |  | 1 | 105.2505 |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 |  |  |  | 2009-04-01 | 2009-04-01 | 2009-04-01 | 41640 | 41640 | 1 | 1 | 2014 | 41897 | 42156 | 40179 | 41640 | 2014-01-01 | 2010-06-01 | [13 empty] | Ph1: 10.8 Mvar cap bank at Seneca 115 kV 09S. Ph2: Knob Hill -S. Beatrice 115 kV 10S | [7 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T1725509SP | FROM->TO | BAILEYVILLE N.M. STATION (NEMAHA MARSHALL R - SMITTYVILLE N.M. COOP (NEMAHA MARSHALL R.E. 115KV CKT 1 | EXP | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533322 | BAILEYV3 115.00 | 533338 | SMITTYV3 115.00 | 0 |  | 1 | 09SP | 92 | 92 |  |  | 107.0203 | 112.5159 | [7 empty] | CATEGORYB | SINGLE | CONCORDIA - ELMCREK6 230.00 230KV CKT 1 | 0 | 539639 | ELMCREK6 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 | 103.5146 |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T6785509SP | FROM->TO | BAILEYVILLE N.M. STATION (NEMAHA MARSHALL R - SMITTYVILLE N.M. COOP (NEMAHA MARSHALL R.E. 115KV CKT 1 | EXP | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533322 | BAILEYV3 115.00 | 533338 | SMITTYV3 115.00 | 0 |  | 1 | 09SP | 92 | 92 |  |  | 107.0156 | 112.5096 | [7 empty] | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539657 | CONCORD3 115.00 | 539658 | CONCRD6 230.00 | 539904 | CONCOD-T 13.800 | 1 | 103.5088 |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T1325509SP | FROM->TO | BAILEYVILLE N.M. STATION (NEMAHA MARSHALL R - SMITTYVILLE N.M. COOP (NEMAHA MARSHALL R.E. 115KV CKT 1 | EXP | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533322 | BAILEYV3 115.00 | 533338 | SMITTYV3 115.00 | 0 |  | 1 | 09SP | 92 | 92 |  |  | 106.7215 | 111.8489 | [7 empty] | CATEGORYB | SINGLE | EAST MANHATTAN - ELMCREK6 230.00 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 539639 | ELMCREK6 230.00 | 0 |  | 1 | 102.901 |  | WERE | Knob Hill - Steele City 115 kV | New 115 kV Line from Knob Hill to Kansas/Nebraska state line. | 223 | 245 | 223 | 245 |  | 48 | 48 | [5 empty] | 15400000 | 2008-01-01 | [38 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 3 | 1 | 2008AGP1AFS31T2783113SP | FROM->TO | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 13SP | 280 | 308 | 115.5 | 116.9 | 114.5444 | 121.9353 | [7 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 | 375.5607 |  | WERE | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 2 | Add second Auburn 230-115 kV transformer. | 280 | 308 | 280 | 308 |  | 12 | 2 | Y |  |  |  | See transformer #1 for NewR, NewX, NewB | 2250000 | 2004-06-24 | [38 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 | 0623 - Hoyt 345-115kV Xfmr | FDNS |  | FDNS |  | 3 | 2 | 2008AGP1AFS31T16023213SP | FROM->TO | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 13SP | 280 | 308 | 105.6 | 106.5 | 106.6425 | 111.8369 | [7 empty] | CATEGORYB | SINGLE | HOYT (HOYT 44X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532765 | HOYT 7 345.00 | 533163 | HOYT 3 115.00 | 532804 | HOYT 1 14.400 | 1 | 344.4576 |  | WERE | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 2 | Add second Auburn 230-115 kV transformer. | 280 | 308 | 280 | 308 |  | 12 | 2 | Y |  |  |  | See transformer #1 for NewR, NewX, NewB | 2250000 | 2004-06-24 | [38 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 | CONT-0633 - East Manhattan 230-115kV XFMR | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T19152213SP | FROM->TO | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 13SP | 280 | 308 |  | 100.4 | 101.6667 | 105.8271 | [7 empty] | CATEGORYB | SINGLE | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 325.9475 |  | WERE | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 2 | Add second Auburn 230-115 kV transformer. | 280 | 308 | 280 | 308 |  | 12 | 2 | Y |  |  |  | See transformer #1 for NewR, NewX, NewB | 2250000 | 2004-06-24 | [38 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 | CONT-0900 - JEC - East Manhattan 230kV | FDNS |  | FDNS |  | 2 | 1 | 2008AGP1AFS31T2592113SP | FROM->TO | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 13SP | 280 | 308 | 100.7 | 101.9 | 100.8393 | 105.0511 | [7 empty] | CATEGORYB | SINGLE | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 0 | 532852 | JEC 6 230.00 | 532861 | EMANHAT6 230.00 | 0 |  | 1 | 323.5574 |  | WERE | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 2 | Add second Auburn 230-115 kV transformer. | 280 | 308 | 280 | 308 |  | 12 | 2 | Y |  |  |  | See transformer #1 for NewR, NewX, NewB | 2250000 | 2004-06-24 | [38 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T3273313SP | FROM->TO | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 13SP | 280 | 308 |  |  | 95.1326 | 102.1591 | [7 empty] | CATEGORYB | SINGLE | AUBURN ROAD - SWISSVALE 230KV CKT 1 | 0 | 532851 | AUBURN 6 230.00 | 532856 | SWISVAL6 230.00 | 0 |  | 1 | 314.65 |  | WERE | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 2 | Add second Auburn 230-115 kV transformer. | 280 | 308 | 280 | 308 |  | 12 | 2 | Y |  |  |  | See transformer #1 for NewR, NewX, NewB | 2250000 | 2004-06-24 | [38 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 3 | 1 | 2008AGP1AFS31T4953118SP | FROM->TO | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 18SP | 280 | 308 | 119.6 | 121.4 | 115.5119 | 126.3194 | [7 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 | 389.0637 |  | WERE | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 2 | Add second Auburn 230-115 kV transformer. | 280 | 308 | 280 | 308 |  | 12 | 2 | Y |  |  |  | See transformer #1 for NewR, NewX, NewB | 2250000 | 2004-06-24 | [38 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 | 0623 - Hoyt 345-115kV Xfmr | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T25773318SP | FROM->TO | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 18SP | 280 | 308 | 107.1 | 111.2 | 107.2885 | 116.9561 | [7 empty] | CATEGORYB | SINGLE | HOYT (HOYT 44X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532765 | HOYT 7 345.00 | 533163 | HOYT 3 115.00 | 532804 | HOYT 1 14.400 | 1 | 360.2248 |  | WERE | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 2 | Add second Auburn 230-115 kV transformer. | 280 | 308 | 280 | 308 |  | 12 | 2 | Y |  |  |  | See transformer #1 for NewR, NewX, NewB | 2250000 | 2004-06-24 | [38 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 | CONT-0900 - JEC - East Manhattan 230kV | FDNS |  | FDNS |  | 3 | 1 | 2008AGP1AFS31T5123118SP | FROM->TO | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 18SP | 280 | 308 | 106.1 | 106.6 | 100.9874 | 109.6959 | [7 empty] | CATEGORYB | SINGLE | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 0 | 532852 | JEC 6 230.00 | 532861 | EMANHAT6 230.00 | 0 |  | 1 | 337.8634 |  | WERE | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 2 | Add second Auburn 230-115 kV transformer. | 280 | 308 | 280 | 308 |  | 12 | 2 | Y |  |  |  | See transformer #1 for NewR, NewX, NewB | 2250000 | 2004-06-24 | [38 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 | CONT-0633 - East Manhattan 230-115kV XFMR | FDNS |  | FDNS |  | 2 | 3 | 2008AGP1AFS31T26082318SP | FROM->TO | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 18SP | 280 | 308 | 100.1 | 103.2 | 101.0643 | 109.5644 | [7 empty] | CATEGORYB | SINGLE | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 337.4584 |  | WERE | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 2 | Add second Auburn 230-115 kV transformer. | 280 | 308 | 280 | 308 |  | 12 | 2 | Y |  |  |  | See transformer #1 for NewR, NewX, NewB | 2250000 | 2004-06-24 | [38 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T5543318SP | FROM->TO | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 18SP | 280 | 308 |  |  | 94.3875 | 103.4808 | [7 empty] | CATEGORYB | SINGLE | AUBURN ROAD - SWISSVALE 230KV CKT 1 | 0 | 532851 | AUBURN 6 230.00 | 532856 | SWISVAL6 230.00 | 0 |  | 1 | 318.7209 |  | WERE | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 2 | Add second Auburn 230-115 kV transformer. | 280 | 308 | 280 | 308 |  | 12 | 2 | Y |  |  |  | See transformer #1 for NewR, NewX, NewB | 2250000 | 2004-06-24 | [38 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T25953318SP | FROM->TO | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 18SP | 280 | 308 |  |  | 93.8903 | 103.3022 | [7 empty] | CATEGORYB | SINGLE | TECUMSEH HILL (TECH194X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532857 | TECHILL6 230.00 | 533182 | TECHILE3 115.00 | 532886 | TECHILL1 13.800 | 1 | 318.1708 |  | WERE | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 2 | Add second Auburn 230-115 kV transformer. | 280 | 308 | 280 | 308 |  | 12 | 2 | Y |  |  |  | See transformer #1 for NewR, NewX, NewB | 2250000 | 2004-06-24 | [38 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T5623318SP | FROM->TO | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 18SP | 280 | 308 |  |  | 93.8638 | 103.2494 | [7 empty] | CATEGORYB | SINGLE | SWISSVALE - TECUMSEH HILL 230KV CKT 1 | 0 | 532856 | SWISVAL6 230.00 | 532857 | TECHILL6 230.00 | 0 |  | 1 | 318.0081 |  | WERE | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 2 | Add second Auburn 230-115 kV transformer. | 280 | 308 | 280 | 308 |  | 12 | 2 | Y |  |  |  | See transformer #1 for NewR, NewX, NewB | 2250000 | 2004-06-24 | [38 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T393318SP | FROM->TO | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE |  | NEAST |  | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 18SP | 280 | 308 |  |  | 91.8152 | 100.552 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | 309.7002 |  | WERE | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 2 | Add second Auburn 230-115 kV transformer. | 280 | 308 | 280 | 308 |  | 12 | 2 | Y |  |  |  | See transformer #1 for NewR, NewX, NewB | 2250000 | 2004-06-24 | [38 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17133318SP |  | ATWOOD 115KV | REL | MIDW |  | REG E-IL |  |  | 530554 | ATWOOD 3 115.00 | [5 empty] | 18SP | [7 empty] | 0.89985 | 0.91583 | 0.88604 | 0.98916 | 0.9 | 1.05 | CATEGORYB | SINGLE | MINGO (MINGO) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 531451 | MINGO 7 345.00 | 531429 | MINGO 3 115.00 | 531452 | MINGTER1 13.800 | 1 |  |  | SUNC | RULETON 115KV Capacitor | Install Second 12 Mvar cap bank at Ruleton 115kV | [12 empty] | 486000 | 2008-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T1832213SP | FROM->TO | ASHDOWN WEST - CRAIG JUNCTION 138KV CKT 1 | REL | AEPW | AEPW | SARKAECC | EASTERN | 0 | 504124 | ASHDWN_W 4 138.00 | 510890 | CRAIGJT4 138.00 | 0 |  | 1 | 13SP | 202 | 235 |  | 103 | 113.9576 | 102.4107 | [7 empty] | CATEGORYB | SINGLE | LYDIA - VALLIANT 345KV CKT 1 | 0 | 508298 | LYDIA 7 345.00 | 510911 | VALIANT7 345.00 | 0 |  | 1 | 240.6651 |  | AEPW | ASHDOWN WEST - CRAIG JUNCTION 138KV CKT 1 | Rebuild 2.45 miles of 795 ACSR with 1590 ACSR and reset relays | 287 | 287 | 287 | 287 | 2.45 | 18 | 6 |  | 0.01434 | 0.13352 | 0.04001 | New limits would be a breaker at Craig Juntion and switches at both Craig Junction and Ashdown West | 2500000 | 2008-11-07 | [38 empty] | 2012-06-01 | 2012-06-01
GEN-2006-010 | Turk | [7 empty] | 507402507431012SP | FROM->TO | ASHDOWN REC (MILLWOOD) - PATTERSON 138KV CKT 1 | U | AEPW | AEPW | SARKAECC | SARK | 0 | 507402 | ASHDWNR4 138.00 | 507431 | PATTERS4 138.00 | 0 |  | 1 |  | 368 | 512 |  |  | 108.5 | [9 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | AEPW | ASHDOWN REC (MILLWOOD) - PATTERSON 138KV CKT 1 | Reconductor Line & Convert Line to 138 kV and convert Patterson station to breaker-and-a half cofiguration | [11 empty] | 6670000 | 6670000 | [39 empty] | 2012-07-01 | 2012-07-01
GEN-2006-010 | Turk | [7 empty] | 507428507402012SP | TO->FROM | ASHDOWN REC (MILLWOOD) - OKAY 138KV CKT 1 | U | AEPW | AEPW | SARK | SARKAECC | 0 | 507428 | OKAY 4 138.00 | 507402 | ASHDWNR4 138.00 | 0 |  | 1 |  | 368 | 512 |  |  | 116 | [9 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | AEPW | ASHDOWN REC (MILLWOOD) - OKAY 138KV CKT 1 | Recunductor and convert line to 138 kV and replace switches at Ashdown REC | [11 empty] | 11100000 | 11100000 | [39 empty] | 2012-07-01 | 2012-07-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 4 | 2008AGP1AFS31T22913418SP | FROM->TO | ARSENAL HILL (ARSHILL2) 138/69/14.5KV TRANSFORMER CKT 2 | CP | AEPW |  | SHREVEPO |  | 2 | 507711 | ARSHILL4 138.00 | 507710 | ARSHILL2 69.000 | 507714 | ARSH2-1 14.500 | 2 | 18SP | 200 | 240 |  |  | 99.2379 | 100.7944 | [7 empty] | CATEGORYB | SINGLE | ARSENAL HILL (ARSHILL1) 138/69/12.47KV TRANSFORMER CKT 1 | 1 | 507710 | ARSHILL2 69.000 | 507711 | ARSHILL4 138.00 | 507712 | ARSH1-1 12.470 | 1 | 241.9066 |  | AEPW | ARSENAL HILL (ARSHILL2) 138/69/14.5KV TRANSFORMER CKT 2 | Replace auto & 69 kV breaker and switches | 200 | 240 | 200 | 280 |  | 18 | 3 | [5 empty] | 2500000 | 2007-02-09 | [38 empty] | 2018-06-01 | 2018-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 4 | 2008AGP1AFS31T22923418SP | FROM->TO | ARSENAL HILL (ARSHILL1) 138/69/12.47KV TRANSFORMER CKT 1 | CP | AEPW |  | SHREVEPO |  | 2 | 507711 | ARSHILL4 138.00 | 507710 | ARSHILL2 69.000 | 507712 | ARSH1-1 12.470 | 1 | 18SP | 200 | 240 |  |  | 99.1256 | 100.6805 | [7 empty] | CATEGORYB | SINGLE | ARSENAL HILL (ARSHILL2) 138/69/14.5KV TRANSFORMER CKT 2 | 1 | 507710 | ARSHILL2 69.000 | 507711 | ARSHILL4 138.00 | 507714 | ARSH2-1 14.500 | 2 | 241.6332 |  | AEPW | ARSENAL HILL (ARSHILL1) 138/69/12.47KV TRANSFORMER CKT 1 | Replace auto & 69 kV breaker and switches | 200 | 240 | 200 | 280 |  | 18 | 3 | [5 empty] | 2500000 | 2007-02-09 | [38 empty] | 2018-06-01 | 2018-06-01
2008-AGP1 | AFS3 |  | FNSL | FDNS-Iteration limit exceeded | FNSL | FDNS-Iteration limit exceeded | 2 | 2 | 2008AGP1AFS32T52209SP | FROM->TO | ARKANSAS NUCLEAR ONE - RUSSELLVILLE NORTH 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 337912 | 5ANO 16 161.00 | 337906 | 5RUSL-N 161.00 | 0 |  | 1 | 09SP | 396 | 396 |  | 119.1 | 117.2757 | 114.5893 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 | 453.7736 |  | EES | ARKANSAS NUCLEAR ONE - RUSSELLVILLE NORTH 161KV CKT 1 | Rebuild Transmission Line 8.79 miles | [52 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T11872210SP | FROM->TO | ARKANSAS NUCLEAR ONE - RUSSELLVILLE NORTH 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 337912 | 5ANO 16 161.00 | 337906 | 5RUSL-N 161.00 | 0 |  | 1 | 10SP | 396 | 396 |  | 129.1 | 124.5272 | 127.06 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 | 503.1576 |  | EES | ARKANSAS NUCLEAR ONE - RUSSELLVILLE NORTH 161KV CKT 1 | Rebuild Transmission Line 8.79 miles | [52 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T7622210WP | FROM->TO | ARKANSAS NUCLEAR ONE - RUSSELLVILLE NORTH 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 337912 | 5ANO 16 161.00 | 337906 | 5RUSL-N 161.00 | 0 |  | 1 | 10WP | 396 | 396 |  | 116.7 | 113.2432 | 114.6287 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 | 453.9297 |  | EES | ARKANSAS NUCLEAR ONE - RUSSELLVILLE NORTH 161KV CKT 1 | Rebuild Transmission Line 8.79 miles | [52 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T18342213SP | FROM->TO | ARKANSAS NUCLEAR ONE - RUSSELLVILLE NORTH 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 337912 | 5ANO 16 161.00 | 337906 | 5RUSL-N 161.00 | 0 |  | 1 | 13SP | 396 | 396 |  | 139.4 | 134.2667 | 135.8366 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 | 537.9129 |  | EES | ARKANSAS NUCLEAR ONE - RUSSELLVILLE NORTH 161KV CKT 1 | Rebuild Transmission Line 8.79 miles | [52 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T7042213WP | FROM->TO | ARKANSAS NUCLEAR ONE - RUSSELLVILLE NORTH 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 337912 | 5ANO 16 161.00 | 337906 | 5RUSL-N 161.00 | 0 |  | 1 | 13WP | 396 | 396 |  | 114.9 | 110.9201 | 113.2174 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 | 448.3409 |  | EES | ARKANSAS NUCLEAR ONE - RUSSELLVILLE NORTH 161KV CKT 1 | Rebuild Transmission Line 8.79 miles | [52 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T30042218SP | FROM->TO | ARKANSAS NUCLEAR ONE - RUSSELLVILLE NORTH 161KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 337912 | 5ANO 16 161.00 | 337906 | 5RUSL-N 161.00 | 0 |  | 1 | 18SP | 396 | 396 |  | 146.5 | 141.5076 | 142.3931 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 | 563.8767 |  | EES | ARKANSAS NUCLEAR ONE - RUSSELLVILLE NORTH 161KV CKT 1 | Rebuild Transmission Line 8.79 miles | [52 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T3175509SH | FROM->TO | ARCADIA (ARCADIA3) 345/138/13.8KV TRANSFORMER CKT 1 | S | OKGE |  |  |  | 2 | 514908 | ARCADIA7 345.00 | 514907 | ARCADIA4 138.00 | 515704 | ARCADI31 13.800 | 1 | 09SH | 493 | 493 |  |  | 102.7556 | 103.3993 | [7 empty] | CATEGORYB | SINGLE | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514907 | ARCADIA4 138.00 | 514908 | ARCADIA7 345.00 | 515703 | ARCADI21 13.800 | 1 | 509.7585 |  | OKGE | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 Displacement | Add 3rd 345/138KV Auto and convert the 345kV and 138kV to a breaker and a half configuration. | [12 empty] | 13500000 | 2008-07-29 | [38 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T7265510SP | FROM->TO | ARCADIA (ARCADIA3) 345/138/13.8KV TRANSFORMER CKT 1 | S | OKGE |  |  |  | 2 | 514908 | ARCADIA7 345.00 | 514907 | ARCADIA4 138.00 | 515704 | ARCADI31 13.800 | 1 | 10SP | 493 | 493 |  |  | 60.6861 | 100.2224 | [7 empty] | CATEGORYB | SINGLE | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514907 | ARCADIA4 138.00 | 514908 | ARCADIA7 345.00 | 515703 | ARCADI21 13.800 | 1 | 494.0964 |  | OKGE | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 Displacement | Add 3rd 345/138KV Auto and convert the 345kV and 138kV to a breaker and a half configuration. | [12 empty] | 13500000 | 2008-07-29 | [38 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T22885518SP | FROM->TO | ARCADIA (ARCADIA3) 345/138/13.8KV TRANSFORMER CKT 1 | S | OKGE |  |  |  | 2 | 514908 | ARCADIA7 345.00 | 514907 | ARCADIA4 138.00 | 515704 | ARCADI31 13.800 | 1 | 18SP | 493 | 493 | 103.3 | 103.3 | 79.7425 | 104.1111 | [7 empty] | CATEGORYB | SINGLE | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514907 | ARCADIA4 138.00 | 514908 | ARCADIA7 345.00 | 515703 | ARCADI21 13.800 | 1 | 513.2677 |  | OKGE | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 Displacement | Add 3rd 345/138KV Auto and convert the 345kV and 138kV to a breaker and a half configuration. | [12 empty] | 13500000 | 2008-07-29 | [38 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T3195509SH | FROM->TO | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 | S | OKGE |  |  |  | 2 | 514908 | ARCADIA7 345.00 | 514907 | ARCADIA4 138.00 | 515703 | ARCADI21 13.800 | 1 | 09SH | 493 | 493 |  |  | 105.6752 | 106.3278 | [7 empty] | CATEGORYB | SINGLE | ARCADIA (ARCADIA3) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514907 | ARCADIA4 138.00 | 514908 | ARCADIA7 345.00 | 515704 | ARCADI31 13.800 | 1 | 524.196 |  | OKGE | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 Displacement | Add 3rd 345/138KV Auto and convert the 345kV and 138kV to a breaker and a half configuration. | [12 empty] | 13500000 | 2008-07-29 | [38 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T445509SH | FROM->TO | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 | S | OKGE |  |  |  | 2 | 514908 | ARCADIA7 345.00 | 514907 | ARCADIA4 138.00 | 515703 | ARCADI21 13.800 | 1 | 09SH | 493 | 493 |  |  | 100.2163 | 100.1925 | [7 empty] | CATEGORYB | SINGLE | ARCADIA - NORTHWEST 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 514908 | ARCADIA7 345.00 | 0 |  | 1 | 493.949 |  | OKGE | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 Displacement | Add 3rd 345/138KV Auto and convert the 345kV and 138kV to a breaker and a half configuration. | [12 empty] | 13500000 | 2008-07-29 | [38 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T6075509SP | FROM->TO | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 | S | OKGE |  |  |  | 2 | 514908 | ARCADIA7 345.00 | 514907 | ARCADIA4 138.00 | 515703 | ARCADI21 13.800 | 1 | 09SP | 493 | 493 |  |  | 99.9831 | 100.6323 | [7 empty] | CATEGORYB | SINGLE | ARCADIA (ARCADIA3) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514907 | ARCADIA4 138.00 | 514908 | ARCADIA7 345.00 | 515704 | ARCADI31 13.800 | 1 | 496.1172 |  | OKGE | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 Displacement | Add 3rd 345/138KV Auto and convert the 345kV and 138kV to a breaker and a half configuration. | [12 empty] | 13500000 | 2008-07-29 | [38 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T7285510SP | FROM->TO | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 | S | OKGE |  |  |  | 2 | 514908 | ARCADIA7 345.00 | 514907 | ARCADIA4 138.00 | 515703 | ARCADI21 13.800 | 1 | 10SP | 493 | 493 |  |  | 62.4191 | 103.0653 | [7 empty] | CATEGORYB | SINGLE | ARCADIA (ARCADIA3) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514907 | ARCADIA4 138.00 | 514908 | ARCADIA7 345.00 | 515704 | ARCADI31 13.800 | 1 | 508.1119 |  | OKGE | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 Displacement | Add 3rd 345/138KV Auto and convert the 345kV and 138kV to a breaker and a half configuration. | [12 empty] | 13500000 | 2008-07-29 | [38 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T10925513SP | FROM->TO | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 | S | OKGE |  |  |  | 2 | 514908 | ARCADIA7 345.00 | 514907 | ARCADIA4 138.00 | 515703 | ARCADI21 13.800 | 1 | 13SP | 493 | 493 |  |  | 62.1952 | 102.1379 | [7 empty] | CATEGORYB | SINGLE | ARCADIA (ARCADIA3) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514907 | ARCADIA4 138.00 | 514908 | ARCADIA7 345.00 | 515704 | ARCADI31 13.800 | 1 | 503.5399 |  | OKGE | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 Displacement | Add 3rd 345/138KV Auto and convert the 345kV and 138kV to a breaker and a half configuration. | [12 empty] | 13500000 | 2008-07-29 | [38 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T1705513SP | FROM->TO | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 | S | OKGE |  |  |  | 2 | 514908 | ARCADIA7 345.00 | 514907 | ARCADIA4 138.00 | 515703 | ARCADI21 13.800 | 1 | 13SP | 493 | 493 |  |  | 55.9642 | 100.2445 | [7 empty] | CATEGORYB | SINGLE | ARCADIA - NORTHWEST 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 514908 | ARCADIA7 345.00 | 0 |  | 1 | 494.2054 |  | OKGE | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 Displacement | Add 3rd 345/138KV Auto and convert the 345kV and 138kV to a breaker and a half configuration. | [12 empty] | 13500000 | 2008-07-29 | [38 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T22905518SP | FROM->TO | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 | S | OKGE |  |  |  | 2 | 514908 | ARCADIA7 345.00 | 514907 | ARCADIA4 138.00 | 515703 | ARCADI21 13.800 | 1 | 18SP | 493 | 493 | 103.6 | 106.3 | 82.0234 | 107.0805 | [7 empty] | CATEGORYB | SINGLE | ARCADIA (ARCADIA3) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514907 | ARCADIA4 138.00 | 514908 | ARCADIA7 345.00 | 515704 | ARCADI31 13.800 | 1 | 527.9069 |  | OKGE | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 Displacement | Add 3rd 345/138KV Auto and convert the 345kV and 138kV to a breaker and a half configuration. | [12 empty] | 13500000 | 2008-07-29 | [38 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 5 | 5 | 2008AGP1AFS31T3755518SP | FROM->TO | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 | S | OKGE |  |  |  | 2 | 514908 | ARCADIA7 345.00 | 514907 | ARCADIA4 138.00 | 515703 | ARCADI21 13.800 | 1 | 18SP | 493 | 493 | 101.4 | 104.3 | 78.8255 | 103.1157 | [7 empty] | CATEGORYB | SINGLE | ARCADIA - NORTHWEST 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 514908 | ARCADIA7 345.00 | 0 |  | 1 | 508.3604 |  | OKGE | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 Displacement | Add 3rd 345/138KV Auto and convert the 345kV and 138kV to a breaker and a half configuration. | [12 empty] | 13500000 | 2008-07-29 | [38 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T4094213SP | TO->FROM | AQUARIUS - LITCHFIELD 69KV CKT 1 | CP | WERE | WERE | SEAST | SEAST | 0 | 533765 | LITCH 2 69.000 | 533756 | AQUARS 2 69.000 | 0 |  | 1 | 13SP | 72 | 72 | 101.5 | 106.2 | 106.6715 | 105.998 | [7 empty] | CATEGORYB | SINGLE | LITCHFIELD - ROUSE 69KV CKT 1 | 0 | 533765 | LITCH 2 69.000 | 533771 | ROUSE 2 69.000 | 0 |  | 1 | 76.3186 |  | WERE | LITCHFIELD - AQUARIUS - HUDSON JUNCTION 69KV CKT 1 Displacement | Replace 69 kV disconnect switches at Aquarius. | 80 | 80 | 80 | 80 | [8 empty] | 30000 | 2007-01-01 | [38 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T4084213SP | FROM->TO | AQUARIUS - HUDSON JUNCTION 69KV CKT 1 | CP | WERE | WERE | SEAST | SEAST | 0 | 533756 | AQUARS 2 69.000 | 533764 | HUDSJCT2 69.000 | 0 |  | 1 | 13SP | 72 | 72 | 100.5 | 105.2 | 105.6446 | 104.9712 | [7 empty] | CATEGORYB | SINGLE | LITCHFIELD - ROUSE 69KV CKT 1 | 0 | 533765 | LITCH 2 69.000 | 533771 | ROUSE 2 69.000 | 0 |  | 1 | 75.5793 |  | WERE | LITCHFIELD - AQUARIUS - HUDSON JUNCTION 69KV CKT 1 Displacement | Replace 69 kV disconnect switches at Aquarius. | 80 | 80 | 80 | 80 | [8 empty] | 30000 | 2007-01-01 | [38 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 2 | 2008AGP1AFS31V9103213SP |  | ANZIO 115KV | REL | WERE |  | NCENTRAL |  |  | 533321 | ANZIO 3 115.00 | [5 empty] | 13SP | [8 empty] | 0.94113 | 0.92069 | 0.96326 | 0.93 | 1.05 | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17643318SP |  | ANZIO 115KV | REL | WERE |  | NCENTRAL |  |  | 533321 | ANZIO 3 115.00 | [5 empty] | 18SP | [8 empty] | 0.93896 | 0.89745 | 0.95211 | 0.93 | 1.05 | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2006-AG1 | 2006-AG1 | [7 empty] | 53245532501SPP-AEPW-293216SP |  | ALUMAX TAP - BANN 138KV CKT 1 | U | AEPW | AEPW |  |  | 0 | 508049 | ALUMXT 4 138 | 508054 | BANN 4 138 | 0 |  | 1 | 16SP |  | 261 | [12 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | AEPW | ALUMAX TAP - BANN 138KV CKT 1 | Replace six (6) 138 kV switches, five at Bann & one at Alumax Tap. Rebuild 0.67 miles of 1024 ACAR with 2156 ACSR. Replace wavetrap & jumpers @ Bann. Replace breaker 3300 @ Bann. | 430 | 449 | 430 | 449 | 0.67 | 15 | 6 |  | 0.00018 | 0.002397 | 0.00081 | New limits are CTs and relay settings @ Bann | 1000000 | [39 empty] | 2008-06-01 | 2008-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 2 | 2008AGP1AFS31T3943209SH | TO->FROM | ALPINE AECC - BISMARK 115KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 337678 | 3BISMRK 115.00 | 338850 | 3ALPINE# 115.00 | 0 |  | 1 | 09SH | 98 | 98 | 103.6 | 111.2 | 104.6453 | 116.7098 | [7 empty] | CATEGORYB | SINGLE | ELDORADO EHV - LONGWOOD 345KV CKT 1 | 0 | 508809 | LONGWD 7 345.00 | 337562 | 7ELDEHV 345.00 | 0 |  | 1 | 114.3756 |  | EES | ALPINE AECC - BISMARK 115KV CKT 1 | Rebuild Transmission Line 14.88 miles | [52 empty] | 2009-04-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 2 | 2008AGP1AFS31T2593209SH | TO->FROM | ALPINE AECC - BISMARK 115KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 337678 | 3BISMRK 115.00 | 338850 | 3ALPINE# 115.00 | 0 |  | 1 | 09SH | 98 | 98 | 103.5 | 111.1 | 104.6178 | 116.673 | [7 empty] | CATEGORYB | SINGLE | ELDORADO EHV 500/345KV TRANSFORMER CKT 1 | 0 | 337561 | 8ELDEHV 500.00 | 337562 | 7ELDEHV 345.00 | 0 |  | 1 | 114.3395 |  | EES | ALPINE AECC - BISMARK 115KV CKT 1 | Rebuild Transmission Line 14.88 miles | [52 empty] | 2009-04-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 2 | 2008AGP1AFS31T3923209SH | FROM->TO | ALPINE AECC - AMITY SS 115KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 338850 | 3ALPINE# 115.00 | 337674 | 3AMITY * 115.00 | 0 |  | 1 | 09SH | 98 | 98 |  | 106.9 | 100.3789 | 112.3832 | [7 empty] | CATEGORYB | SINGLE | ELDORADO EHV - LONGWOOD 345KV CKT 1 | 0 | 508809 | LONGWD 7 345.00 | 337562 | 7ELDEHV 345.00 | 0 |  | 1 | 110.1355 |  | EES | ALPINE AECC - AMITY SS 115KV CKT 1 | Rebuild Transmission Line 2.88 miles | [52 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 2 | 2008AGP1AFS31T2573209SH | FROM->TO | ALPINE AECC - AMITY SS 115KV CKT 1 | S | EES | EES | EES_ARK | EES_ARK | 0 | 338850 | 3ALPINE# 115.00 | 337674 | 3AMITY * 115.00 | 0 |  | 1 | 09SH | 98 | 98 |  | 106.8 | 100.3518 | 112.3453 | [7 empty] | CATEGORYB | SINGLE | ELDORADO EHV 500/345KV TRANSFORMER CKT 1 | 0 | 337561 | 8ELDEHV 500.00 | 337562 | 7ELDEHV 345.00 | 0 |  | 1 | 110.0984 |  | EES | ALPINE AECC - AMITY SS 115KV CKT 1 | Rebuild Transmission Line 2.88 miles | [52 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T1643309SH | FROM->TO | ALLEN - LEHIGH TAP 69KV CKT 1 | CP | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 09SH | 32 | 32 |  | 113.8 | 112.1625 | 116.7397 | [7 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 | 37.3567 |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [38 empty] | 2009-06-01 | 2012-05-15
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T1633309SH | FROM->TO | ALLEN - LEHIGH TAP 69KV CKT 1 | CP | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 09SH | 32 | 32 |  | 103.1 | 101.5482 | 105.8118 | [7 empty] | CATEGORYB | SINGLE | ORCHARD - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533643 | ORCHARD2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 | 33.8598 |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [38 empty] | 2009-06-01 | 2012-05-15
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 1 | 2 | 2008AGP1AFS31T2331209SP | FROM->TO | ALLEN - LEHIGH TAP 69KV CKT 1 | CP | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 09SP | 32 | 32 |  | 130.1 | 142.0772 | 112.3184 | [7 empty] | CATEGORYB | SINGLE | TIOGA - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533646 | TIOGA 2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1 | 35.9419 |  | WERE | ALLEN - LEHIGH TAP 69KV CKT 1 | Tear down / Rebuild 5.69-mile line; 954 kcmil ACSR | 72 | 72 | 72 | 72 | 5.69 | 12 | 5 |  | 0.01209 | 0.08228 | 0.00175 | Terminal equipment limit | 2363907 | 2008-03-14 | [38 empty] | 2009-06-01 | 2012-05-15
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T2753310SP | TO->FROM | ALABAMA - LAKE ROAD 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541255 | LAKE RD5 161.00 | 541354 | ALABAMA5 161.00 | 0 |  | 1 | 10SP | 153 | 172 |  | 106.4 | 102.6539 | 110.8337 | [7 empty] | CATEGORYB | SINGLE | HAWTHORN - ST JOE 345KV CKT 1 | 0 | 541199 | ST JOE 3 345.00 | 542972 | HAWTH 7 345.00 | 0 |  | 1 | 190.634 | Replace wavetrap | MIPU | PLATTE CITY - SMITHVILLE 161KV CKT 1 #1 | Increase the normal/emergency ratings to 233/265 MVA by replacing wave trapes | 233 | 265 |  |  |  | 6 | 6 | [5 empty] | 50000 | 2009-03-19 | [38 empty] | 2010-06-01 | 2010-12-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T2753310SP | TO->FROM | ALABAMA - LAKE ROAD 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541255 | LAKE RD5 161.00 | 541354 | ALABAMA5 161.00 | 0 |  | 1 | 10SP | 153 | 172 |  | 106.4 | 102.6539 | 110.8337 | [7 empty] | CATEGORYB | SINGLE | HAWTHORN - ST JOE 345KV CKT 1 | 0 | 541199 | ST JOE 3 345.00 | 542972 | HAWTH 7 345.00 | 0 |  | 1 | 190.634 | re-set the over current relay to trip the Lake Road-Alabama section when flow goes above 172 MVA | SJLP | ALABAMA - LAKE ROAD 161KV CKT 1 | Reset the overcurrent relay at Alabama 161 kV substation to open Lake Road - Alabama 161 kV line upon reaching thermal limit of Lake Rd. - Alabama 161 kV line. | [5 empty] | 6 | 6 | [5 empty] | 20000 | 2009-03-19 | [38 empty] | 2010-06-01 | 2009-06-01
2008-AGP1 | AFS3 | CONT-1202 - Jarbalo - Stranger Creek 115kV |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T2803310SP | TO->FROM | ALABAMA - LAKE ROAD 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541255 | LAKE RD5 161.00 | 541354 | ALABAMA5 161.00 | 0 |  | 1 | 10SP | 153 | 172 |  |  | 95.0283 | 101.6536 | [7 empty] | CATEGORYB | SINGLE | IATAN - PLATTE CITY 161KV CKT 1 | 0 | 541221 | PLTCTY 5 161.00 | 541350 | IATAN5 161.00 | 0 |  | 1 | 174.8442 | re-set the over current relay to trip the Lake Road-Alabama section when flow goes above 172 MVA | SJLP | ALABAMA - LAKE ROAD 161KV CKT 1 | Reset the overcurrent relay at Alabama 161 kV substation to open Lake Road - Alabama 161 kV line upon reaching thermal limit of Lake Rd. - Alabama 161 kV line. | [5 empty] | 6 | 6 | [5 empty] | 20000 | 2009-03-19 | [38 empty] | 2010-06-01 | 2009-06-01
2008-AGP1 | AFS3 | CONT-1202 - Jarbalo - Stranger Creek 115kV |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T2803310SP | TO->FROM | ALABAMA - LAKE ROAD 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541255 | LAKE RD5 161.00 | 541354 | ALABAMA5 161.00 | 0 |  | 1 | 10SP | 153 | 172 |  |  | 95.0283 | 101.6536 | [7 empty] | CATEGORYB | SINGLE | IATAN - PLATTE CITY 161KV CKT 1 | 0 | 541221 | PLTCTY 5 161.00 | 541350 | IATAN5 161.00 | 0 |  | 1 | 174.8442 | Replace wavetrap | MIPU | PLATTE CITY - SMITHVILLE 161KV CKT 1 #1 | Increase the normal/emergency ratings to 233/265 MVA by replacing wave trapes | 233 | 265 |  |  |  | 6 | 6 | [5 empty] | 50000 | 2009-03-19 | [38 empty] | 2010-06-01 | 2010-12-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T6253318SP | TO->FROM | ALABAMA - LAKE ROAD 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541255 | LAKE RD5 161.00 | 541354 | ALABAMA5 161.00 | 0 |  | 1 | 18SP | 153 | 172 |  | 102.9 | 101.8301 | 110.1547 | [7 empty] | CATEGORYB | SINGLE | HAWTHORN - ST JOE 345KV CKT 1 | 0 | 541199 | ST JOE 3 345.00 | 542972 | HAWTH 7 345.00 | 0 |  | 1 | 189.4661 | re-set the over current relay to trip the Lake Road-Alabama section when flow goes above 172 MVA | SJLP | ALABAMA - LAKE ROAD 161KV CKT 1 | Reset the overcurrent relay at Alabama 161 kV substation to open Lake Road - Alabama 161 kV line upon reaching thermal limit of Lake Rd. - Alabama 161 kV line. | [5 empty] | 6 | 6 | [5 empty] | 20000 | 2009-03-19 | [38 empty] | 2010-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T6253318SP | TO->FROM | ALABAMA - LAKE ROAD 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541255 | LAKE RD5 161.00 | 541354 | ALABAMA5 161.00 | 0 |  | 1 | 18SP | 153 | 172 |  | 102.9 | 101.8301 | 110.1547 | [7 empty] | CATEGORYB | SINGLE | HAWTHORN - ST JOE 345KV CKT 1 | 0 | 541199 | ST JOE 3 345.00 | 542972 | HAWTH 7 345.00 | 0 |  | 1 | 189.4661 | Replace wavetrap | MIPU | PLATTE CITY - SMITHVILLE 161KV CKT 1 #1 | Increase the normal/emergency ratings to 233/265 MVA by replacing wave trapes | 233 | 265 |  |  |  | 6 | 6 | [5 empty] | 50000 | 2009-03-19 | [38 empty] | 2010-06-01 | 2010-12-01
2008-AGP1 | AFS3 | CONT-1202 - Jarbalo - Stranger Creek 115kV | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T6323318SP | TO->FROM | ALABAMA - LAKE ROAD 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541255 | LAKE RD5 161.00 | 541354 | ALABAMA5 161.00 | 0 |  | 1 | 18SP | 153 | 172 |  | 100.2 | 98.0803 | 105.5217 | [7 empty] | CATEGORYB | SINGLE | IATAN - PLATTE CITY 161KV CKT 1 | 0 | 541221 | PLTCTY 5 161.00 | 541350 | IATAN5 161.00 | 0 |  | 1 | 181.4973 | Replace wavetrap | MIPU | PLATTE CITY - SMITHVILLE 161KV CKT 1 #1 | Increase the normal/emergency ratings to 233/265 MVA by replacing wave trapes | 233 | 265 |  |  |  | 6 | 6 | [5 empty] | 50000 | 2009-03-19 | [38 empty] | 2010-06-01 | 2010-12-01
2008-AGP1 | AFS3 | CONT-1202 - Jarbalo - Stranger Creek 115kV | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T6323318SP | TO->FROM | ALABAMA - LAKE ROAD 161KV CKT 1 | EXP | MIPU | MIPU |  |  | 0 | 541255 | LAKE RD5 161.00 | 541354 | ALABAMA5 161.00 | 0 |  | 1 | 18SP | 153 | 172 |  | 100.2 | 98.0803 | 105.5217 | [7 empty] | CATEGORYB | SINGLE | IATAN - PLATTE CITY 161KV CKT 1 | 0 | 541221 | PLTCTY 5 161.00 | 541350 | IATAN5 161.00 | 0 |  | 1 | 181.4973 | re-set the over current relay to trip the Lake Road-Alabama section when flow goes above 172 MVA | SJLP | ALABAMA - LAKE ROAD 161KV CKT 1 | Reset the overcurrent relay at Alabama 161 kV substation to open Lake Road - Alabama 161 kV line upon reaching thermal limit of Lake Rd. - Alabama 161 kV line. | [5 empty] | 6 | 6 | [5 empty] | 20000 | 2009-03-19 | [38 empty] | 2010-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T1013309SH | FROM->TO | AFTON (AFTAUTO1) 161/69/13.8KV TRANSFORMER CKT 1 | EXP | GRDA |  | GRDA |  | 2 | 512632 | AFTON 5 161.00 | 512633 | AFTON 2 69.000 | 512845 | AFTON 13.800 | 1 | 09SH | 50 | 63 |  | 115.1 | 115.5289 | 119.8217 | [7 empty] | CATEGORYB | SINGLE | AFTON - MIAMI 161KV CKT 1 | 0 | 512631 | MIAMI 5 161.00 | 512632 | AFTON 5 161.00 | 0 |  | 1 | 75.4877 |  | GRDA | AFTON (AFTAUTO1) 161/69/13.8KV TRANSFORMER CKT 1 | Add a second 50 MVA Transformer at Afton Substation. | 75 | 84 | 75 | 84 |  | 18 | 5 |  | 0.001 | 0.14 |  |  | 890000 | 2006-06-01 | [38 empty] | 2009-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 3 | 2008AGP1AFS31T1022309SP | FROM->TO | AFTON (AFTAUTO1) 161/69/13.8KV TRANSFORMER CKT 1 | EXP | GRDA |  | GRDA |  | 2 | 512632 | AFTON 5 161.00 | 512633 | AFTON 2 69.000 | 512845 | AFTON 13.800 | 1 | 09SP | 50 | 63 |  | 114.4 | 115.0618 | 116.0237 | [7 empty] | CATEGORYB | SINGLE | AFTON - MIAMI 161KV CKT 1 | 0 | 512631 | MIAMI 5 161.00 | 512632 | AFTON 5 161.00 | 0 |  | 1 | 73.0949 |  | GRDA | AFTON (AFTAUTO1) 161/69/13.8KV TRANSFORMER CKT 1 | Add a second 50 MVA Transformer at Afton Substation. | 75 | 84 | 75 | 84 |  | 18 | 5 |  | 0.001 | 0.14 |  |  | 890000 | 2006-06-01 | [38 empty] | 2009-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T1383310SP | FROM->TO | AFTON (AFTAUTO1) 161/69/13.8KV TRANSFORMER CKT 1 | EXP | GRDA |  | GRDA |  | 2 | 512632 | AFTON 5 161.00 | 512633 | AFTON 2 69.000 | 512845 | AFTON 13.800 | 1 | 10SP | 50 | 63 |  |  | 98.076 | 101.9904 | [7 empty] | CATEGORYB | SINGLE | AFTON - MIAMI 161KV CKT 1 | 0 | 512631 | MIAMI 5 161.00 | 512632 | AFTON 5 161.00 | 0 |  | 1 | 64.254 |  | GRDA | AFTON (AFTAUTO1) 161/69/13.8KV TRANSFORMER CKT 1 | Add a second 50 MVA Transformer at Afton Substation. | 75 | 84 | 75 | 84 |  | 18 | 5 |  | 0.001 | 0.14 |  |  | 890000 | 2006-06-01 | [38 empty] | 2009-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T1003309SH | FROM->TO | AFTON - FAIRLAND EDE TAP 69KV CKT 1 | S | GRDA | GRDA | GRDA | GRDA | 0 | 512633 | AFTON 2 69.000 | 512708 | FAIRTAP2 69.000 | 0 |  | 1 | 09SH | 72 | 72 |  |  | 100.2991 | 103.4981 | [7 empty] | CATEGORYB | SINGLE | AFTON - MIAMI 161KV CKT 1 | 0 | 512631 | MIAMI 5 161.00 | 512632 | AFTON 5 161.00 | 0 |  | 1 | 74.5186 |  | GRDA | AFTON - FAIRLAND EDE TAP 69KV CKT 1 | Replace terminal equipment | [12 empty] | 500000 | [39 empty] | 2009-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T1063313WP | FROM->TO | AFTON - FAIRLAND EDE TAP 69KV CKT 1 | S | GRDA | GRDA | GRDA | GRDA | 0 | 512633 | AFTON 2 69.000 | 512708 | FAIRTAP2 69.000 | 0 |  | 1 | 13WP | 72 | 72 |  |  | 94.8853 | 102.4284 | [7 empty] | CATEGORYB | SINGLE | AFTON - MIAMI 161KV CKT 1 | 0 | 512631 | MIAMI 5 161.00 | 512632 | AFTON 5 161.00 | 0 |  | 1 | 73.7484 |  | GRDA | AFTON - FAIRLAND EDE TAP 69KV CKT 1 | Replace terminal equipment | [12 empty] | 500000 | [39 empty] | 2009-06-01 | 2011-06-01
2008-AGP1 | AFS3 | ISLAND-LOAD |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31V17723318SP |  | ABILENE ENERGY CENTER 115KV | REL | WERE |  | WEST |  |  | 533361 | AEC 3 115.00 | [5 empty] | 18SP | [8 empty] | 0.94545 | 0.90746 | 0.9433 | 0.93 | 1.05 | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 |  |  | WERE | East Manhattan to Mcdowell 230 kV | The East Manhattan-McDowell 115 kV is built as a 230 kV line, but is operated at 115 kV. Substation work will have to be performed in order to convert this line. | 358 | 358 | 358 | 358 | 15.65 | 12 | 6 | No | 0.00361 | 0.02365 | 0.05386 | [41 empty] | 2009-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 4 | 2008AGP1AFS31T8663413SP | FROM->TO | 7PALMYRA 345.00 345/161KV TRANSFORMER CKT 1 | S | AMMO | AMMO | AMRNMO | AMRNMO | 0 | 345436 | 7PALMYRA 345.00 | 345437 | 5PALMYRA 161.00 | 0 |  | 1 | 13SP | 336 | 370 | 108.0 | 108.8 | 108.908 | 110.7932 | [7 empty] | CATEGORYB | SINGLE | 7MONTGMRY 345.00 - 7SPENCER 345.00 345KV CKT 1 | 0 | 345230 | 7MONTGMRY 345.00 | 345992 | 7SPENCER 345.00 | 0 |  | 1 | 409.9348 |  | AMMO | 7PALMYRA 345.00 345/161KV TRANSFORMER CKT 1 | Indeterminate | [52 empty] | 2011-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 3 | 2 | 2008AGP1AFS31T23173218SP | FROM->TO | 7PALMYRA 345.00 345/161KV TRANSFORMER CKT 1 | S | AMMO | AMMO | AMRNMO | AMRNMO | 0 | 345436 | 7PALMYRA 345.00 | 345437 | 5PALMYRA 161.00 | 0 |  | 1 | 18SP | 336 | 370 | 109.5 | 106.4 | 106.1663 | 108.0406 | [7 empty] | CATEGORYB | SINGLE | 7MONTGMRY 345.00 - 7SPENCER 345.00 345KV CKT 1 | 0 | 345230 | 7MONTGMRY 345.00 | 345992 | 7SPENCER 345.00 | 0 |  | 1 | 399.7502 |  | AMMO | 7PALMYRA 345.00 345/161KV TRANSFORMER CKT 1 | Indeterminate | [52 empty] | 2011-06-01 | 2011-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 1 | 2008AGP1AFS31T3474118SP | TO->FROM | 5 TRIBES - PECAN CREEK 161KV CKT 1 | REL | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515234 | PECANCK5 161.00 | 515228 | 5TRIBES5 161.00 | 0 |  | 1 | 18SP | 272 | 312 | 105.1 | 105.6 | 105.1403 | 112.0308 | [7 empty] | CATEGORYB | SINGLE | AGENCY - PECAN CREEK 161KV CKT 1 | 0 | 515230 | AGENCY 5 161.00 | 515234 | PECANCK5 161.00 | 0 |  | 1 | 349.5361 |  | OKGE | 5 TRIBES - PECAN CREEK 161KV CKT 1 | Reconductor 4.07 miles of line to 1590AS52 and replace 2-wave traps, 1-161kV breaker, 3-switches @ Five Tribes & 5-switches, relaying @ Pecan Creek. | 471 | 542 | 558 | 558 | 4.07 | 20 | 12 |  | 0.00106 | 0.01081 | 0.00657 |  | 3000000 | 2008-07-29 | [38 empty] | 2016-06-01 | 2016-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 1 | 2008AGP1AFS31T3484118SP | FROM->TO | 5 TRIBES - HANCOCK 161KV CKT 1 | REL | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515228 | 5TRIBES5 161.00 | 515250 | HANCOK-5 161.00 | 0 |  | 1 | 18SP | 223 | 223 | 110.2 | 110.6 | 110.4008 | 118.6902 | [7 empty] | CATEGORYB | SINGLE | AGENCY - PECAN CREEK 161KV CKT 1 | 0 | 515230 | AGENCY 5 161.00 | 515234 | PECANCK5 161.00 | 0 |  | 1 | 264.6791 |  | OKGE | 5 TRIBES - HANCOCK 161KV CKT 1 | Replace 800A Wave Trap, increase Relay CTR to 1200-5A. | 272 | 312 | 335 | 335 |  | 12 | 8 | Y |  |  |  |  | 150000 | 2008-07-29 | [38 empty] | 2015-06-01 | 2015-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 1 | 2008AGP1AFS31T3494118SP | FROM->TO | 5 TRIBES - HANCOCK 161KV CKT 1 | REL | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515228 | 5TRIBES5 161.00 | 515250 | HANCOK-5 161.00 | 0 |  | 1 | 18SP | 223 | 223 | 104.0 | 104.2 | 104.3714 | 113.1018 | [7 empty] | CATEGORYB | SINGLE | AGENCY - EUCLID 161KV CKT 1 | 0 | 515230 | AGENCY 5 161.00 | 515251 | EUCLID 5 161.00 | 0 |  | 1 | 252.217 |  | OKGE | 5 TRIBES - HANCOCK 161KV CKT 1 | Replace 800A Wave Trap, increase Relay CTR to 1200-5A. | 272 | 312 | 335 | 335 |  | 12 | 8 | Y |  |  |  |  | 150000 | 2008-07-29 | [38 empty] | 2015-06-01 | 2015-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 4 | 1 | 2008AGP1AFS31T3504118SP | FROM->TO | 5 TRIBES - HANCOCK 161KV CKT 1 | REL | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515228 | 5TRIBES5 161.00 | 515250 | HANCOK-5 161.00 | 0 |  | 1 | 18SP | 223 | 223 |  |  | 96.5655 | 105.1314 | [7 empty] | CATEGORYB | SINGLE | EUCLID - MUSKOGEE PORT 161KV CKT 1 | 0 | 515232 | MSKPTAP5 161.00 | 515251 | EUCLID 5 161.00 | 0 |  | 1 | 234.443 |  | OKGE | 5 TRIBES - HANCOCK 161KV CKT 1 | Replace 800A Wave Trap, increase Relay CTR to 1200-5A. | 272 | 312 | 335 | 335 |  | 12 | 8 | Y |  |  |  |  | 150000 | 2008-07-29 | [38 empty] | 2015-06-01 | 2015-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T1584413SP | FROM->TO | 4LUTHER 138.00 138/69KV TRANSFORMER CKT 1 | S | AECI | AECI | KAMO-OK | KAMO-OK | 0 | 300135 | 4LUTHER 138.00 | 300856 | 2LUTHER 69.000 | 0 |  | 1 | 13SP | 56 | 56 | 108.7 | 130.5 | 133.027 | 147.6237 | [7 empty] | CATEGORYB | SINGLE | KINZE - STILLWATER KINZIE 138KV CKT 1 | 0 | 512710 | KINZEGR4 138.00 | 515008 | KINZE 4 138.00 | 0 |  | 1 | 82.6693 |  | AECI | 4LUTHER 138.00 138/69KV TRANSFORMER CKT 1 | Upgrade to 84 MVA transformer | [12 empty] | 2000000 | [39 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T3484418SP | FROM->TO | 4LUTHER 138.00 138/69KV TRANSFORMER CKT 1 | S | AECI | AECI | KAMO-OK | KAMO-OK | 0 | 300135 | 4LUTHER 138.00 | 300856 | 2LUTHER 69.000 | 0 |  | 1 | 18SP | 56 | 56 | 121.5 | 137.2 | 144.0822 | 150.6662 | [7 empty] | CATEGORYB | SINGLE | KINZE - STILLWATER KINZIE 138KV CKT 1 | 0 | 512710 | KINZEGR4 138.00 | 515008 | KINZE 4 138.00 | 0 |  | 1 | 84.3731 |  | AECI | 4LUTHER 138.00 138/69KV TRANSFORMER CKT 1 | Upgrade to 84 MVA transformer | [12 empty] | 2000000 | [39 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T3854418SP | FROM->TO | 4LUTHER 138.00 138/69KV TRANSFORMER CKT 1 | S | AECI | AECI | KAMO-OK | KAMO-OK | 0 | 300135 | 4LUTHER 138.00 | 300856 | 2LUTHER 69.000 | 0 |  | 1 | 18SP | 56 | 56 | 108.2 | 117.6 | 121.6155 | 125.8138 | [7 empty] | CATEGORYB | SINGLE | MCELROY - STILLWATER 138KV CKT 1 | 0 | 515009 | MCELROY4 138.00 | 515011 | STILWTR4 138.00 | 0 |  | 1 | 70.4557 |  | AECI | 4LUTHER 138.00 138/69KV TRANSFORMER CKT 1 | Upgrade to 84 MVA transformer | [12 empty] | 2000000 | [39 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 4 | 4 | 2008AGP1AFS31T3814418SP | FROM->TO | 4LUTHER 138.00 138/69KV TRANSFORMER CKT 1 | S | AECI | AECI | KAMO-OK | KAMO-OK | 0 | 300135 | 4LUTHER 138.00 | 300856 | 2LUTHER 69.000 | 0 |  | 1 | 18SP | 56 | 56 | 107.1 | 117.8 | 121.8044 | 124.5521 | [7 empty] | CATEGORYB | SINGLE | MORRISON - STILLWATER 138KV CKT 1 | 0 | 515006 | MORRISN4 138.00 | 515011 | STILWTR4 138.00 | 0 |  | 1 | 69.7492 |  | AECI | 4LUTHER 138.00 138/69KV TRANSFORMER CKT 1 | Upgrade to 84 MVA transformer | [12 empty] | 2000000 | [39 empty] | 2009-06-01 | 2010-06-01
2008-AGP1 | AFS3 | CONT-Webre - Richard 500kV | FDNS |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T3884209SP | TO->FROM | 4KSPRGS - LINE 642 TAP 138KV CKT 1 | S | EES | LAGN | EES_GSU-LA | LAGN_NATIVE | 0 | 335456 | 4L-642TP 138.00 | 303153 | 4KSPRGS 138.00 | 0 |  | 1 | 09SP | 289 | 289 | 102.1 | 100.3 | 108.807 | 113.868 | [7 empty] | CATEGORYB | SINGLE | WEBRE - WELLS 500KV CKT 1 | 0 | 335368 | 8WELLS 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | 329.0785 |  | EES | 4KSPRGS - LINE 642 TAP 138KV CKT 1 | Rebuild Transmission Line 0.1 miles | [12 empty] | 310060 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 | CONT-Webre - Richard 500kV | FDNS |  | FDNS |  | 1 | 2 | 2008AGP1AFS31T5211213SP | TO->FROM | 4KSPRGS - LINE 642 TAP 138KV CKT 1 | S | EES | LAGN | EES_GSU-LA | LAGN_NATIVE | 0 | 335456 | 4L-642TP 138.00 | 303153 | 4KSPRGS 138.00 | 0 |  | 1 | 13SP | 289 | 289 | 122.6 | 117.1 | 125.3256 | 134.8605 | [7 empty] | CATEGORYB | SINGLE | WEBRE - WELLS 500KV CKT 1 | 0 | 335368 | 8WELLS 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | 389.7469 |  | EES | 4KSPRGS - LINE 642 TAP 138KV CKT 1 | Rebuild Transmission Line 0.1 miles | [12 empty] | 310060 | [39 empty] | 2009-06-01 | 2013-06-01
2008-AGP1 | AFS3 | CONT-Webre - Richard 500kV |  |  | FDNS |  | 4 | 2 | 2008AGP1AFS31T3874209SP | FROM->TO | 4KSPRGS - CHAMPAGNE 138KV CKT 1 | S | LAGN | EES | LAGN_NATIVE | EES_GSU-LA | 0 | 303153 | 4KSPRGS 138.00 | 335455 | 4CHAMPNE 138.00 | 0 |  | 1 | 09SP | 289 | 289 |  |  | 98.2989 | 103.4301 | [7 empty] | CATEGORYB | SINGLE | WEBRE - WELLS 500KV CKT 1 | 0 | 335368 | 8WELLS 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | 298.913 |  | EES | 4KSPRGS - CHAMPAGNE 138KV CKT 1 | Rebuild Transmission Line 13.5 miles | [12 empty] | 15569784 | [39 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 | CONT-Webre - Richard 500kV | FDNS |  | FDNS |  | 1 | 2 | 2008AGP1AFS31T5201213SP | FROM->TO | 4KSPRGS - CHAMPAGNE 138KV CKT 1 | S | LAGN | EES | LAGN_NATIVE | EES_GSU-LA | 0 | 303153 | 4KSPRGS 138.00 | 335455 | 4CHAMPNE 138.00 | 0 |  | 1 | 13SP | 289 | 289 | 110.3 | 104.8 | 112.6963 | 121.983 | [7 empty] | CATEGORYB | SINGLE | WEBRE - WELLS 500KV CKT 1 | 0 | 335368 | 8WELLS 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | 352.5309 |  | EES | 4KSPRGS - CHAMPAGNE 138KV CKT 1 | Rebuild Transmission Line 13.5 miles | [12 empty] | 15569784 | [39 empty] | 2009-06-01 | 2009-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T7633310SP | TO->FROM | 4FISHERTP 138.00 - KEYSTONE DAM 138KV CKT 1 | S | SWPA | AECI | EMINTH | KAMO-OK | 0 | 505610 | KEYSTON4 138.00 | 300131 | 4FISHERTP 138.00 | 0 |  | 1 | 10SP | 174 | 174 |  |  | 96.909 | 101.4603 | [7 empty] | CATEGORYB | SINGLE | SILVER CITY - WEKIWA 138KV CKT 1 | 0 | 509757 | WEKIWA-4 138.00 | 300140 | 4SILVCTY 138.00 | 0 |  | 1 | 176.5409 | Limit is AECI/KAMO line. SWPA equipment good for 223 MVA | AECI | 4FISHERTP 138.00 - KEYSTONE DAM 138KV CKT 1 | 4.26 mile line designed for 75-C. If this can be uprated to 100-C | [12 empty] | 500000 | 2009-01-05 | [38 empty] | 2010-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  |  |  | FDNS |  | 3 | 3 | 2008AGP1AFS31T11773313SP | TO->FROM | 4FISHERTP 138.00 - KEYSTONE DAM 138KV CKT 1 | S | SWPA | AECI | EMINTH | KAMO-OK | 0 | 505610 | KEYSTON4 138.00 | 300131 | 4FISHERTP 138.00 | 0 |  | 1 | 13SP | 174 | 174 |  |  | 100.1634 | 104.9312 | [7 empty] | CATEGORYB | SINGLE | SILVER CITY - WEKIWA 138KV CKT 1 | 0 | 509757 | WEKIWA-4 138.00 | 300140 | 4SILVCTY 138.00 | 0 |  | 1 | 182.5803 | Limit is AECI/KAMO line. SWPA equipment good for 223 MVA | AECI | 4FISHERTP 138.00 - KEYSTONE DAM 138KV CKT 1 | 4.26 mile line designed for 75-C. If this can be uprated to 100-C | [12 empty] | 500000 | 2009-01-05 | [38 empty] | 2010-06-01 | 2012-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T5182218SP | TO->FROM | 3RDST - ARKOMA 161KV CKT 1 | REL | OKGE | OKGE | FT SMITH | FT SMITH | 0 | 515306 | ARKOMA 5 161.00 | 515308 | 3RDST 5 161.00 | 0 |  | 1 | 18SP | 313 | 335 |  | 102.9 | 96.8391 | 101.3154 | [7 empty] | CATEGORYB | SINGLE | AES - TARBY 161KV CKT 1 | 0 | 515262 | AES 5 161.00 | 515264 | TARBY 5 161.00 | 0 |  | 1 | 339.4066 |  | OKGE | 3RDST - ARKOMA 161KV CKT 1 | Replace 8-1200A switches & 2-wave traps. | 313 | 359 | 404 | 418 |  | 14 | 10 | Y |  |  |  |  | 1300000 | 2008-07-29 | [38 empty] | 2018-06-01 | 2018-06-01
2008-AGP1 | AFS3 |  | FDNS |  | FDNS |  | 2 | 2 | 2008AGP1AFS31T5202218SP | TO->FROM | 3RDST - ARKOMA 161KV CKT 1 | REL | OKGE | OKGE | FT SMITH | FT SMITH | 0 | 515306 | ARKOMA 5 161.00 | 515308 | 3RDST 5 161.00 | 0 |  | 1 | 18SP | 313 | 335 |  | 102.5 | 95.1543 | 100.841 | [7 empty] | CATEGORYB | SINGLE | FT SMITH - QUANEX TAP 161KV CKT 1 | 0 | 515300 | FTSMTHE5 161.00 | 515310 | QUANXTP5 161.00 | 0 |  | 1 | 337.8174 |  | OKGE | 3RDST - ARKOMA 161KV CKT 1 | Replace 8-1200A switches & 2-wave traps. | 313 | 359 | 404 | 418 |  | 14 | 10 | Y |  |  |  |  | 1300000 | 2008-07-29 | [38 empty] | 2018-06-01 | 2018-06-01