## tblALLFacilityLog
STUDYDES | STUDYDES2 | EVENTTYPE | AssessmentSOLUTIONTYPE | AssessmenFDNS-TERMINATION | SOLUTIONTYPE | FDNS-TERMINATION | GROUP | SCENARIO | FGName | DIRECTION | FacilityName | FacilityUpgradeCode | ModelArea1 | ModelArea2 | FZONENAME | TZONENAME | MONTFLAG | MONTFB | MONTFNAME | MONTTB1 | MONTTNAME1 | MONTTB2 | MONTTNAME2 | MONTCKT | Case | RATEA | RATEB | RATEC | Assessment Loading | BaseCaseLoading | TransferCaseLoading | NameOfBusWithMonitoredVoltage | Assessment Voltage | BaseCaseVoltage | TransferCaseVoltage | VINIT | VMIN | VMAX | CATEGORY | CONTTYPE | CONTNAME | CONTXFMRFLAG | CONTFB | CONTFNAME | CONTTB1 | CONTTNAME1 | CONTTB2 | CONTTNAME2 | CONTCKT | TransmissionProviderSystemImpactStudyNotesComments | RequiredRateB | TransmissionOwnerComments | OwnerDesignation | UpgradeName | UpgradeComponentWithinFacility | NewSummerA | NewSummerB | NewOtherA | NewOtherB | DistToConstruct | TotalLead | ConstructionLeadOnly | NewOrConstructWhileEnergized | NewR | NewX | NewB | CommentsRegardingUpgradeRequirements | NewCost | EffDate | NetPlantDate | ReusableEx_GrossValue | ReusableEx_NetValue | Reusable_EndofDepr | SalvageValue | NewCostWhileExpediting | EffDateExpedited | StartDeprExpedited | EndDeprExpedited | NetPlantDateExpedited | ReusableEx_GrossExpedited | ReusableEx_NetExpedited | Reusable_EndofDeprExpedited | SalvageValueExpedited | Generation 1 Owner & Unit (Name) | Generation 1 Redispatch Cost ($) | Generation 1 Redispatch Date (M/D/Y) | Generation 2 Owner & Unit (Name) | Generation 2 Redispatch Cost ($) | Generation 2 Redispatch Date (M/D/Y) | Generation 3 Owner & Unit (Name) | Generation 3 Redispatch Cost ($) | Generation 3 Redispatch Date (M/D/Y) | ActualCompletion | ActualNewCost | ActualNetPlantDate | ActualReusableEx_GrossValue | ActualReusableEx_NetValue | ActualReusable_EndofDepr | ActualSalvageValue | Actual_NewCostWhileExpediting | Actual_StartDeprExp | Actual_EndDeprExp | Actual_NetPlantDateExpedited | ActualReusableEx_GrossExpedited | ActualReusableEx_NetExpedited | ActualReusable_EndofDeprExpedited | Actual_SalvageValueExpedited | DUN | EOC | EarliestDate
2009-AGP2 | AFS6 | CONT-1208 - Auburn - South Gate 115kV | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T5375521SP | TO->FROM | 17TH & FAIRLAWN - INDIAN HILLS 115KV CKT 1 | REL | WERE | WERE | NEAST | NEAST | 0 | 533166 | INDIANH3 115.00 | 533175 | 17&FAIR3 115.00 | 0 |  | 1 | 21SP | 141 | 152 | 0 | 103.5 | 103.5062 | 103.7254 | [7 empty] | CATEGORYB | SINGLE | AUBURN ROAD - SHERWOD 115KV CKT 1 | 0 | 533151 | AUBURN 3 115.00 | 533194 | SHERWOD3 115.00 | 0 |  | 1 |  | 158 |  | WERE | 17TH & FAIRLAWN - INDIAN HILLS 115KV CKT 1 | Bundled 1192.5 kcmil ACSR Bunting. The line will be limited by terminal equipment. 240 MVA limit. | [52 empty] | 2017-06-01 | 2017-06-01 | 2016-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1805511WP | TO->FROM | ALBION - PETERSBURG 115KV CKT 1 | CP | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640318 | PETRSBG7 115.00 | 640054 | ALBION 7 115.00 | 0 |  | 1 | 11WP | 113 | 113 | 124 |  | 68.3446 | 103.2134 | [7 empty] | CATEGORYB | SINGLE | NELIGH - PETERSBURG 115KV CKT 1 | 0 | 640293 | NELIGH 7 115.00 | 640318 | PETRSBG7 115.00 | 0 |  | 1 |  | 117 |  | NPPD | PETERSBURG - MADISON 115KV CKT 1 | Build new 35 mile 115 kV line from Petersburg to Madison | 288 | 288 |  |  |  | 48 | 48 |  | 0.02568 | 0.18086 | 0.0285 |  | 28000000 | 2010-04-01 | [38 empty] | 2011-12-01 | 2015-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T4315512SP | TO->FROM | ALBION - PETERSBURG 115KV CKT 1 | CP | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640318 | PETRSBG7 115.00 | 640054 | ALBION 7 115.00 | 0 |  | 1 | 12SP | 113 | 113 | 124 |  | 69.7675 | 104.6651 | [7 empty] | CATEGORYB | SINGLE | NELIGH - PETERSBURG 115KV CKT 1 | 0 | 640293 | NELIGH 7 115.00 | 640318 | PETRSBG7 115.00 | 0 |  | 1 |  | 119 |  | NPPD | PETERSBURG - MADISON 115KV CKT 1 | Build new 35 mile 115 kV line from Petersburg to Madison | 288 | 288 |  |  |  | 48 | 48 |  | 0.02568 | 0.18086 | 0.0285 |  | 28000000 | 2010-04-01 | [38 empty] | 2011-12-01 | 2015-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1845512WP | TO->FROM | ALBION - PETERSBURG 115KV CKT 1 | CP | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640318 | PETRSBG7 115.00 | 640054 | ALBION 7 115.00 | 0 |  | 1 | 12WP | 113 | 113 | 124 |  | 67.9027 | 102.9061 | [7 empty] | CATEGORYB | SINGLE | NELIGH - PETERSBURG 115KV CKT 1 | 0 | 640293 | NELIGH 7 115.00 | 640318 | PETRSBG7 115.00 | 0 |  | 1 |  | 117 |  | NPPD | PETERSBURG - MADISON 115KV CKT 1 | Build new 35 mile 115 kV line from Petersburg to Madison | 288 | 288 |  |  |  | 48 | 48 |  | 0.02568 | 0.18086 | 0.0285 |  | 28000000 | 2010-04-01 | [38 empty] | 2011-12-01 | 2015-06-01
2006-AG1 | 2006-AG1 | [7 empty] | 2006-AG1AEPW5080495080541 |  | ALUMAX TAP - BANN 138KV CKT 1 | U | AEPW | AEPW |  |  | 0 | 508049 | ALUMXT 4 138 | 508054 | BANN 4 138 | 0 |  | 1 | 16SP |  | 261 | [12 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | AEPW | ALUMAX TAP - BANN 138KV CKT 1 | Replace six (6) 138 kV switches, five at Bann & one at Alumax Tap. Rebuild 0.67 miles of 1024 ACAR with 2156 ACSR. Replace wavetrap & jumpers @ Bann. Replace breaker 3300 @ Bann. | 430 | 449 | 430 | 449 | 0.67 | 15 | 6 |  | 0.00018 | 0.002397 | 0.00081 | New limits are CTs and relay settings @ Bann | 1000000 | [39 empty] | 2008-06-01 | 2008-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T10215511SP | FROM->TO | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 | CP | OKGE | OKGE |  |  | 2 | 514908 | ARCADIA7 345.00 | 514907 | ARCADIA4 138.00 | 515703 | ARCADI21 13.800 | 1 | 11SP | 493 | 493 | 0 | 100.1 | 100.0831 | 100.1066 | [7 empty] | CATEGORYB | SINGLE | ARCADIA (ARCADIA3) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514907 | ARCADIA4 138.00 | 514908 | ARCADIA7 345.00 | 515704 | ARCADI31 13.800 | 1 |  | 494 |  | OKGE | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 Accelerated | Add 3rd 345/138KV Auto and convert the 345kV and 138kV to a breaker and a half configuration. | [5 empty] | 36 | 24 | [5 empty] | 13500000 | 2008-07-29 | [38 empty] | 2011-06-01 | 2014-06-01 | 2014-02-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T10215511SP | FROM->TO | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 | CP | OKGE | OKGE |  |  | 2 | 514908 | ARCADIA7 345.00 | 514907 | ARCADIA4 138.00 | 515703 | ARCADI21 13.800 | 1 | 11SP | 493 | 493 | 0 | 100.1 | 100.0831 | 100.1066 | [7 empty] | CATEGORYB | SINGLE | ARCADIA (ARCADIA3) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514907 | ARCADIA4 138.00 | 514908 | ARCADIA7 345.00 | 515704 | ARCADI31 13.800 | 1 |  | 494 |  | OKGE | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 Accelerated | Add 3rd 345/138KV Auto and convert the 345kV and 138kV to a breaker and a half configuration. | [5 empty] | 36 | 24 | [5 empty] | 13500000 | 2008-07-29 | [38 empty] | 2011-06-01 | 2014-06-01 | 2014-02-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T11065512SP | FROM->TO | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 | CP | OKGE | OKGE |  |  | 2 | 514908 | ARCADIA7 345.00 | 514907 | ARCADIA4 138.00 | 515703 | ARCADI21 13.800 | 1 | 12SP | 493 | 493 | 0 | 99.4 | 99.4463 | 100.4826 | [7 empty] | CATEGORYB | SINGLE | ARCADIA (ARCADIA3) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514907 | ARCADIA4 138.00 | 514908 | ARCADIA7 345.00 | 515704 | ARCADI31 13.800 | 1 |  | 496 |  | OKGE | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 Accelerated | Add 3rd 345/138KV Auto and convert the 345kV and 138kV to a breaker and a half configuration. | [5 empty] | 36 | 24 | [5 empty] | 13500000 | 2008-07-29 | [38 empty] | 2011-06-01 | 2014-06-01 | 2014-02-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T11065512SP | FROM->TO | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 | CP | OKGE | OKGE |  |  | 2 | 514908 | ARCADIA7 345.00 | 514907 | ARCADIA4 138.00 | 515703 | ARCADI21 13.800 | 1 | 12SP | 493 | 493 | 0 | 99.4 | 99.4463 | 100.4826 | [7 empty] | CATEGORYB | SINGLE | ARCADIA (ARCADIA3) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514907 | ARCADIA4 138.00 | 514908 | ARCADIA7 345.00 | 515704 | ARCADI31 13.800 | 1 |  | 496 |  | OKGE | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 Accelerated | Add 3rd 345/138KV Auto and convert the 345kV and 138kV to a breaker and a half configuration. | [5 empty] | 36 | 24 | [5 empty] | 13500000 | 2008-07-29 | [38 empty] | 2011-06-01 | 2014-06-01 | 2014-02-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T11145516SP | FROM->TO | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 | CP | OKGE | OKGE |  |  | 2 | 514908 | ARCADIA7 345.00 | 514907 | ARCADIA4 138.00 | 515703 | ARCADI21 13.800 | 1 | 16SP | 493 | 493 | 0 | 101 | 101.0028 | 105.4648 | [7 empty] | CATEGORYB | SINGLE | ARCADIA (ARCADIA3) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514907 | ARCADIA4 138.00 | 514908 | ARCADIA7 345.00 | 515704 | ARCADI31 13.800 | 1 |  | 520 |  | OKGE | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 Accelerated | Add 3rd 345/138KV Auto and convert the 345kV and 138kV to a breaker and a half configuration. | [5 empty] | 36 | 24 | [5 empty] | 13500000 | 2008-07-29 | [38 empty] | 2011-06-01 | 2014-06-01 | 2014-02-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T11145516SP | FROM->TO | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 | CP | OKGE | OKGE |  |  | 2 | 514908 | ARCADIA7 345.00 | 514907 | ARCADIA4 138.00 | 515703 | ARCADI21 13.800 | 1 | 16SP | 493 | 493 | 0 | 101 | 101.0028 | 105.4648 | [7 empty] | CATEGORYB | SINGLE | ARCADIA (ARCADIA3) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514907 | ARCADIA4 138.00 | 514908 | ARCADIA7 345.00 | 515704 | ARCADI31 13.800 | 1 |  | 520 |  | OKGE | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 Accelerated | Add 3rd 345/138KV Auto and convert the 345kV and 138kV to a breaker and a half configuration. | [5 empty] | 36 | 24 | [5 empty] | 13500000 | 2008-07-29 | [38 empty] | 2011-06-01 | 2014-06-01 | 2014-02-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T19125521SP | FROM->TO | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 | CP | OKGE | OKGE |  |  | 2 | 514908 | ARCADIA7 345.00 | 514907 | ARCADIA4 138.00 | 515703 | ARCADI21 13.800 | 1 | 21SP | 493 | 493 | 0 | 108.1 | 108.0948 | 108.1899 | [7 empty] | CATEGORYB | SINGLE | ARCADIA (ARCADIA3) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514907 | ARCADIA4 138.00 | 514908 | ARCADIA7 345.00 | 515704 | ARCADI31 13.800 | 1 |  | 534 |  | OKGE | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 Accelerated | Add 3rd 345/138KV Auto and convert the 345kV and 138kV to a breaker and a half configuration. | [5 empty] | 36 | 24 | [5 empty] | 13500000 | 2008-07-29 | [38 empty] | 2011-06-01 | 2014-06-01 | 2014-02-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T19125521SP | FROM->TO | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 | CP | OKGE | OKGE |  |  | 2 | 514908 | ARCADIA7 345.00 | 514907 | ARCADIA4 138.00 | 515703 | ARCADI21 13.800 | 1 | 21SP | 493 | 493 | 0 | 108.1 | 108.0948 | 108.1899 | [7 empty] | CATEGORYB | SINGLE | ARCADIA (ARCADIA3) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514907 | ARCADIA4 138.00 | 514908 | ARCADIA7 345.00 | 515704 | ARCADI31 13.800 | 1 |  | 534 |  | OKGE | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 Accelerated | Add 3rd 345/138KV Auto and convert the 345kV and 138kV to a breaker and a half configuration. | [5 empty] | 36 | 24 | [5 empty] | 13500000 | 2008-07-29 | [38 empty] | 2011-06-01 | 2014-06-01 | 2014-02-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T11125516SP | FROM->TO | ARCADIA (ARCADIA3) 345/138/13.8KV TRANSFORMER CKT 1 | CP | OKGE | OKGE |  |  | 2 | 514908 | ARCADIA7 345.00 | 514907 | ARCADIA4 138.00 | 515704 | ARCADI31 13.800 | 1 | 16SP | 493 | 493 | 0 | 98.2 | 98.1652 | 102.5062 | [7 empty] | CATEGORYB | SINGLE | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514907 | ARCADIA4 138.00 | 514908 | ARCADIA7 345.00 | 515703 | ARCADI21 13.800 | 1 |  | 506 |  | OKGE | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 Accelerated | Add 3rd 345/138KV Auto and convert the 345kV and 138kV to a breaker and a half configuration. | [5 empty] | 36 | 24 | [5 empty] | 13500000 | 2008-07-29 | [38 empty] | 2011-06-01 | 2014-06-01 | 2014-02-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T11125516SP | FROM->TO | ARCADIA (ARCADIA3) 345/138/13.8KV TRANSFORMER CKT 1 | CP | OKGE | OKGE |  |  | 2 | 514908 | ARCADIA7 345.00 | 514907 | ARCADIA4 138.00 | 515704 | ARCADI31 13.800 | 1 | 16SP | 493 | 493 | 0 | 98.2 | 98.1652 | 102.5062 | [7 empty] | CATEGORYB | SINGLE | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514907 | ARCADIA4 138.00 | 514908 | ARCADIA7 345.00 | 515703 | ARCADI21 13.800 | 1 |  | 506 |  | OKGE | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 Accelerated | Add 3rd 345/138KV Auto and convert the 345kV and 138kV to a breaker and a half configuration. | [5 empty] | 36 | 24 | [5 empty] | 13500000 | 2008-07-29 | [38 empty] | 2011-06-01 | 2014-06-01 | 2014-02-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T19105521SP | FROM->TO | ARCADIA (ARCADIA3) 345/138/13.8KV TRANSFORMER CKT 1 | CP | OKGE | OKGE |  |  | 2 | 514908 | ARCADIA7 345.00 | 514907 | ARCADIA4 138.00 | 515704 | ARCADI31 13.800 | 1 | 21SP | 493 | 493 | 0 | 105.1 | 105.0595 | 105.1517 | [7 empty] | CATEGORYB | SINGLE | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514907 | ARCADIA4 138.00 | 514908 | ARCADIA7 345.00 | 515703 | ARCADI21 13.800 | 1 |  | 519 |  | OKGE | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 Accelerated | Add 3rd 345/138KV Auto and convert the 345kV and 138kV to a breaker and a half configuration. | [5 empty] | 36 | 24 | [5 empty] | 13500000 | 2008-07-29 | [38 empty] | 2011-06-01 | 2014-06-01 | 2014-02-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T19105521SP | FROM->TO | ARCADIA (ARCADIA3) 345/138/13.8KV TRANSFORMER CKT 1 | CP | OKGE | OKGE |  |  | 2 | 514908 | ARCADIA7 345.00 | 514907 | ARCADIA4 138.00 | 515704 | ARCADI31 13.800 | 1 | 21SP | 493 | 493 | 0 | 105.1 | 105.0595 | 105.1517 | [7 empty] | CATEGORYB | SINGLE | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514907 | ARCADIA4 138.00 | 514908 | ARCADIA7 345.00 | 515703 | ARCADI21 13.800 | 1 |  | 519 |  | OKGE | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 Accelerated | Add 3rd 345/138KV Auto and convert the 345kV and 138kV to a breaker and a half configuration. | [5 empty] | 36 | 24 | [5 empty] | 13500000 | 2008-07-29 | [38 empty] | 2011-06-01 | 2014-06-01 | 2014-02-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T3605511SP | TO->FROM | ARKANSAS CITY - PARIS 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533548 | PARIS 2 69.000 | 533542 | ARKCITY2 69.000 | 0 |  | 1 | 11SP | 72 | 72 | 0 |  | 72.4072 | 101.4259 | [7 empty] | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 |  | 74 |  | WERE | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | Tear down / Rebuild 11.63-mile Timber Tap-Winfield 69 kV line, 954 ACSR | 72 | 72 | 72 | 72 | 11.63 | 18 | 6 |  | 0.0309 | 0.2101 | 0.05164 | Line switches limit to 72 MVA. $790k per mile | 8161986 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T3605511SP | TO->FROM | ARKANSAS CITY - PARIS 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533548 | PARIS 2 69.000 | 533542 | ARKCITY2 69.000 | 0 |  | 1 | 11SP | 72 | 72 | 0 |  | 72.4072 | 101.4259 | [7 empty] | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 |  | 74 |  | WERE | RICHLAND - UDALL 69KV CKT 1 | Tear down / Rebuild 8.48-mile Richland-Udall 69 kV line using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 8.48 | 13 | 7 | N | 0.01789 | 0.12177 | 0.02589 | MVA limit is conductor $790k per mile | 6699200 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T3605511SP | TO->FROM | ARKANSAS CITY - PARIS 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533548 | PARIS 2 69.000 | 533542 | ARKCITY2 69.000 | 0 |  | 1 | 11SP | 72 | 72 | 0 |  | 72.4072 | 101.4259 | [7 empty] | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 |  | 74 |  | WERE | TIMBER JUNCTION - UDALL 69KV CKT 1 | Tear down / Rebuild Udall-Timber Jct 69 kV using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 2.01 | 4 | 2 | N | 0.00424 | 0.02886 | 0.00614 | MVA limit is conductor $790k per mile | 1587900 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
GEN-2006-010 | Turk | [7 empty] | GEN-2006-010AEPW5074285074021 |  | ASHDOWN REC (MILLWOOD) - OKAY 138KV CKT 1 | U | AEPW | AEPW | SARK | SARKAECC | 0 | 507428 | OKAY 4 138.00 | 507402 | ASHDWNR4 138.00 | 0 |  | 1 |  | 368 | 512 |  | 116 | [10 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | AEPW | ASHDOWN REC (MILLWOOD) - OKAY 138KV CKT 1 | Recunductor and convert line to 138 kV and replace switches at Ashdown REC | [11 empty] | 11100000 | 11100000 | [39 empty] | 2012-07-01 | 2012-07-01
GEN-2006-010 | Turk | [7 empty] | GEN-2006-010AEPW5074025074311 |  | ASHDOWN REC (MILLWOOD) - PATTERSON 138KV CKT 1 | U | AEPW | AEPW | SARKAECC | SARK | 0 | 507402 | ASHDWNR4 138.00 | 507431 | PATTERS4 138.00 | 0 |  | 1 |  | 368 | 512 |  | 108.5 | [10 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | AEPW | ASHDOWN REC (MILLWOOD) - PATTERSON 138KV CKT 1 | Reconductor Line & Convert Line to 138 kV and convert Patterson station to breaker-and-a half cofiguration | [11 empty] | 6670000 | 6670000 | [39 empty] | 2012-07-01 | 2012-07-01
2009-AGP2 | AFS6 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T3085516SP | TO->FROM | AUBURN ROAD - JEFFREY ENERGY CENTER 230KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 532852 | JEC 6 230.00 | 532851 | AUBURN 6 230.00 | 0 |  | 1 | 16SP | 565 | 565 | 0 | 102.1 | 102.1356 | 103.5674 | [7 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  | 586 |  | WERE | 18TH STREET - WREN 115KV CKT 1 | Close line that is normally open | [52 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T3085516SP | TO->FROM | AUBURN ROAD - JEFFREY ENERGY CENTER 230KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 532852 | JEC 6 230.00 | 532851 | AUBURN 6 230.00 | 0 |  | 1 | 16SP | 565 | 565 | 0 | 102.1 | 102.1356 | 103.5674 | [7 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  | 586 |  | WERE | 87th Street Interconnection | Add new substation by tapping Stranger-Craig 345kV, add 560MVA three winding transformer, new substation tapping 95th & Waverly-Monticello 115kV, tear down and rebuild existing line as new double circuit. | [52 empty] | 2013-06-01 | 2013-06-01
GEN-2006-010 | Turk | [7 empty] | GEN-2006-010AEPW5080545080751 |  | BANN - RED SPRINGS REC 138KV CKT 1 | U | AEPW | AEPW | TEXARK | TXARNTEC | 0 | 508054 | BANN 4 138.00 | 508075 | REDSPRG4 138.00 | 0 |  | 1 |  | 224 | 261 |  | 72.8 | [10 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | AEPW | BANN - RED SPRINGS REC 138KV CKT 1 | Replace 138 kV breakers 3300 & 3310 | [11 empty] | 300000 | 300000 | [39 empty] | 2012-07-01 | 2012-07-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T12605512SP | FROM->TO | BROOKLINE (BRKLTX1) 345/161/13.2KV TRANSFORMER CKT 1 | REL | SPRM | SPRM | SPRM | SPRM | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549988 | BRKLNE XF1 113.200 | 1 | 12SP | 400 | 400 | 0 | 104.5 | 104.5146 | 106.6525 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE (BRKLTX2) 345/161/13.2KV TRANSFORMER CKT 2 | 1 | 549969 | BROOKLINE 5161.00 | 549984 | BROOKLINE 7345.00 | 549989 | BRKLNE XF2 113.200 | 2 |  | 427 |  | AEP | Multi - Flint Creek – Centerton 345 kV and Centerton- East Centerton 161 kV | Install 345/161 kV transformer at Centerton. Install 22 miles of new 345 kV, 2-954 ACSR line. Install 2 miles of 161 kV from new Centerton Substation to East Centerton Substation. | [52 empty] | 2012-06-01 | 2014-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T12605512SP | FROM->TO | BROOKLINE (BRKLTX1) 345/161/13.2KV TRANSFORMER CKT 1 | REL | SPRM | SPRM | SPRM | SPRM | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549988 | BRKLNE XF1 113.200 | 1 | 12SP | 400 | 400 | 0 | 104.5 | 104.5146 | 106.6525 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE (BRKLTX2) 345/161/13.2KV TRANSFORMER CKT 2 | 1 | 549969 | BROOKLINE 5161.00 | 549984 | BROOKLINE 7345.00 | 549989 | BRKLNE XF2 113.200 | 2 |  | 427 |  | AEP | Multi - Centerton - Osage Creek 345 kV | Install 9 miles of 345 kV line from Shipe Road to East Rogers, Install 32 miles of 345 kV line from East Rogers to Osage Creek, and Install new 345/161 kV transformer at Osage Creek | [52 empty] | 2012-06-01 | 2016-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T12585512SP | FROM->TO | BROOKLINE (BRKLTX2) 345/161/13.2KV TRANSFORMER CKT 2 | REL | SPRM | SPRM | SPRM | SPRM | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549989 | BRKLNE XF2 113.200 | 2 | 12SP | 400 | 400 | 0 | 104.2 | 104.206 | 106.3355 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE (BRKLTX1) 345/161/13.2KV TRANSFORMER CKT 1 | 1 | 549969 | BROOKLINE 5161.00 | 549984 | BROOKLINE 7345.00 | 549988 | BRKLNE XF1 113.200 | 1 |  | 426 |  | AEP | Multi - Flint Creek – Centerton 345 kV and Centerton- East Centerton 161 kV | Install 345/161 kV transformer at Centerton. Install 22 miles of new 345 kV, 2-954 ACSR line. Install 2 miles of 161 kV from new Centerton Substation to East Centerton Substation. | [52 empty] | 2012-06-01 | 2014-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T12585512SP | FROM->TO | BROOKLINE (BRKLTX2) 345/161/13.2KV TRANSFORMER CKT 2 | REL | SPRM | SPRM | SPRM | SPRM | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549989 | BRKLNE XF2 113.200 | 2 | 12SP | 400 | 400 | 0 | 104.2 | 104.206 | 106.3355 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE (BRKLTX1) 345/161/13.2KV TRANSFORMER CKT 1 | 1 | 549969 | BROOKLINE 5161.00 | 549984 | BROOKLINE 7345.00 | 549988 | BRKLNE XF1 113.200 | 1 |  | 426 |  | AEP | Multi - Centerton - Osage Creek 345 kV | Install 9 miles of 345 kV line from Shipe Road to East Rogers, Install 32 miles of 345 kV line from East Rogers to Osage Creek, and Install new 345/161 kV transformer at Osage Creek | [52 empty] | 2012-06-01 | 2016-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T2845516SP | TO->FROM | BUCKEYE TAP - CUNNINGHAM STATION 115KV CKT 1 | REL | SPS | SPS | SPS-PECO | SPS-HOBB | 0 | 527864 | CUNNINHAM 3115.00 | 528348 | BUCKEYE_TP 3115.00 | 0 |  | 1 | 16SP | 141 | 141 | 0 | 124.8 | 124.7734 | 124.7716 | [7 empty] | CATEGORYB | SINGLE | LEA COUNTY REC-LOVINGTON INTERCHANGE 115/69KV TRANSFORMER CKT 1 | 0 | 528334 | LE-LOVINTON3115.00 | 528618 | LE-LOVINTON269.000 | 0 |  | 1 |  | 176 |  | SPS | BUCKEYE TAP - CUNNINGHAM STATION 115KV CKT 1 | Reconductor Buckeye tap to Cunningham 115 kV 8.55 miles with 795 ACSR and replace Line Trap, CT, Jupers and Switch at Cunningham | [52 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T4645521SP | TO->FROM | BUCKEYE TAP - CUNNINGHAM STATION 115KV CKT 1 | REL | SPS | SPS | SPS-PECO | SPS-HOBB | 0 | 527864 | CUNNINHAM 3115.00 | 528348 | BUCKEYE_TP 3115.00 | 0 |  | 1 | 21SP | 141 | 141 | 0 | 152.7 | 152.6604 | 152.6669 | [7 empty] | CATEGORYB | SINGLE | LEA COUNTY REC-LOVINGTON INTERCHANGE 115/69KV TRANSFORMER CKT 1 | 0 | 528334 | LE-LOVINTON3115.00 | 528618 | LE-LOVINTON269.000 | 0 |  | 1 |  | 216 |  | SPS | BUCKEYE TAP - CUNNINGHAM STATION 115KV CKT 1 | Reconductor Buckeye tap to Cunningham 115 kV 8.55 miles with 795 ACSR and replace Line Trap, CT, Jupers and Switch at Cunningham | [52 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61V4135521SP |  | BURLINGTON 69KV | REL | WFEC |  | AEP-IM |  |  | 520833 | BRLNGTN2 69.000 | [5 empty] | 21SP | [8 empty] | 0.90863 | 0.86528 | 0.95905 | 0.9 | 1.05 | CATEGORYB | SINGLE | FAIRVIEW - OKEENE 69KV CKT 1 | 0 | 521015 | OKEENE 2 69.000 | 520909 | FAIRVEW2 69.000 | 0 |  | 1 |  |  |  | WFEC | FAIRVIEW Capacitor 69KV | Install 18 Mvar capacitor at Fairview 69kV bus. | [52 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T2015511SP | TO->FROM | CANTON - TALOGA 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521064 | TALOGA 2 69.000 | 520843 | CANTON-2 69.000 | 0 |  | 1 | 11SP | 33 | 39 | 39 |  | 85.7988 | 126.0229 | [7 empty] | CATEGORYB | SINGLE | CEDARDALE - MOORELAND 138KV CKT 1 | 0 | 520848 | CEDRDAL4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 |  | 50 |  | WFEC | CANTON - TALOGA 69KV CKT 1 | UPGRADE CANTON TO TALOGA TO 336.4 | 106 | 132 |  |  | 9.7 |  |  |  | 0.04013 | 0.16101 | 0.00252 |  | 4800000 | 2010-12-06 | [38 empty] | 2011-06-01 | 2013-06-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T2055511SP | TO->FROM | CANTON - TALOGA 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521064 | TALOGA 2 69.000 | 520843 | CANTON-2 69.000 | 0 |  | 1 | 11SP | 33 | 39 | 39 |  | 84.0269 | 124.1266 | [7 empty] | CATEGORYB | SINGLE | CEDARDALE - OKEENE 138KV CKT 1 | 0 | 520848 | CEDRDAL4 138.00 | 521016 | OKEENE 4 138.00 | 0 |  | 1 |  | 49 |  | WFEC | CANTON - TALOGA 69KV CKT 1 | UPGRADE CANTON TO TALOGA TO 336.4 | 106 | 132 |  |  | 9.7 |  |  |  | 0.04013 | 0.16101 | 0.00252 |  | 4800000 | 2010-12-06 | [38 empty] | 2011-06-01 | 2013-06-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1925511SP | TO->FROM | CANTON - TALOGA 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521064 | TALOGA 2 69.000 | 520843 | CANTON-2 69.000 | 0 |  | 1 | 11SP | 33 | 39 | 39 |  | 70.5288 | 120.5473 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WWRDEHV7 345.00 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 48 |  | WFEC | CANTON - TALOGA 69KV CKT 1 | UPGRADE CANTON TO TALOGA TO 336.4 | 106 | 132 |  |  | 9.7 |  |  |  | 0.04013 | 0.16101 | 0.00252 |  | 4800000 | 2010-12-06 | [38 empty] | 2011-06-01 | 2013-06-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T805511WP | TO->FROM | CANTON - TALOGA 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521064 | TALOGA 2 69.000 | 520843 | CANTON-2 69.000 | 0 |  | 1 | 11WP | 42 | 46 | 46 |  | 61.0201 | 101.4053 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WWRDEHV7 345.00 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 47 |  | WFEC | CANTON - TALOGA 69KV CKT 1 | UPGRADE CANTON TO TALOGA TO 336.4 | 106 | 132 |  |  | 9.7 |  |  |  | 0.04013 | 0.16101 | 0.00252 |  | 4800000 | 2010-12-06 | [38 empty] | 2011-06-01 | 2013-06-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T5905511WP | TO->FROM | CANTON - TALOGA 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521064 | TALOGA 2 69.000 | 520843 | CANTON-2 69.000 | 0 |  | 1 | 11WP | 42 | 46 | 46 |  | 61.0194 | 101.3986 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  | 47 |  | WFEC | CANTON - TALOGA 69KV CKT 1 | UPGRADE CANTON TO TALOGA TO 336.4 | 106 | 132 |  |  | 9.7 |  |  |  | 0.04013 | 0.16101 | 0.00252 |  | 4800000 | 2010-12-06 | [38 empty] | 2011-06-01 | 2013-06-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T745511WP | TO->FROM | CANTON - TALOGA 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521064 | TALOGA 2 69.000 | 520843 | CANTON-2 69.000 | 0 |  | 1 | 11WP | 42 | 46 | 46 |  | 60.8996 | 100.9569 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 47 |  | WFEC | CANTON - TALOGA 69KV CKT 1 | UPGRADE CANTON TO TALOGA TO 336.4 | 106 | 132 |  |  | 9.7 |  |  |  | 0.04013 | 0.16101 | 0.00252 |  | 4800000 | 2010-12-06 | [38 empty] | 2011-06-01 | 2013-06-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T2285512SP | TO->FROM | CANTON - TALOGA 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521064 | TALOGA 2 69.000 | 520843 | CANTON-2 69.000 | 0 |  | 1 | 12SP | 33 | 39 | 39 |  | 86.8529 | 124.3987 | [7 empty] | CATEGORYB | SINGLE | CEDARDALE - MOORELAND 138KV CKT 1 | 0 | 520848 | CEDRDAL4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 |  | 49 |  | WFEC | CANTON - TALOGA 69KV CKT 1 | UPGRADE CANTON TO TALOGA TO 336.4 | 106 | 132 |  |  | 9.7 |  |  |  | 0.04013 | 0.16101 | 0.00252 |  | 4800000 | 2010-12-06 | [38 empty] | 2011-06-01 | 2013-06-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T11165512SP | TO->FROM | CANTON - TALOGA 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521064 | TALOGA 2 69.000 | 520843 | CANTON-2 69.000 | 0 |  | 1 | 12SP | 33 | 39 | 39 |  | 75.5813 | 123.9126 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  | 49 |  | WFEC | CANTON - TALOGA 69KV CKT 1 | UPGRADE CANTON TO TALOGA TO 336.4 | 106 | 132 |  |  | 9.7 |  |  |  | 0.04013 | 0.16101 | 0.00252 |  | 4800000 | 2010-12-06 | [38 empty] | 2011-06-01 | 2013-06-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T2175512SP | TO->FROM | CANTON - TALOGA 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521064 | TALOGA 2 69.000 | 520843 | CANTON-2 69.000 | 0 |  | 1 | 12SP | 33 | 39 | 39 |  | 75.573 | 123.9107 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WWRDEHV7 345.00 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 49 |  | WFEC | CANTON - TALOGA 69KV CKT 1 | UPGRADE CANTON TO TALOGA TO 336.4 | 106 | 132 |  |  | 9.7 |  |  |  | 0.04013 | 0.16101 | 0.00252 |  | 4800000 | 2010-12-06 | [38 empty] | 2011-06-01 | 2013-06-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T845512WP | TO->FROM | CANTON - TALOGA 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521064 | TALOGA 2 69.000 | 520843 | CANTON-2 69.000 | 0 |  | 1 | 12WP | 42 | 46 | 46 |  | 61.7198 | 107.5949 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WWRDEHV7 345.00 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 50 |  | WFEC | CANTON - TALOGA 69KV CKT 1 | UPGRADE CANTON TO TALOGA TO 336.4 | 106 | 132 |  |  | 9.7 |  |  |  | 0.04013 | 0.16101 | 0.00252 |  | 4800000 | 2010-12-06 | [38 empty] | 2011-06-01 | 2013-06-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T4615512WP | TO->FROM | CANTON - TALOGA 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521064 | TALOGA 2 69.000 | 520843 | CANTON-2 69.000 | 0 |  | 1 | 12WP | 42 | 46 | 46 |  | 61.7228 | 107.5189 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  | 50 |  | WFEC | CANTON - TALOGA 69KV CKT 1 | UPGRADE CANTON TO TALOGA TO 336.4 | 106 | 132 |  |  | 9.7 |  |  |  | 0.04013 | 0.16101 | 0.00252 |  | 4800000 | 2010-12-06 | [38 empty] | 2011-06-01 | 2013-06-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T725512WP | TO->FROM | CANTON - TALOGA 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521064 | TALOGA 2 69.000 | 520843 | CANTON-2 69.000 | 0 |  | 1 | 12WP | 42 | 46 | 46 |  | 61.5863 | 107.0683 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 50 |  | WFEC | CANTON - TALOGA 69KV CKT 1 | UPGRADE CANTON TO TALOGA TO 336.4 | 106 | 132 |  |  | 9.7 |  |  |  | 0.04013 | 0.16101 | 0.00252 |  | 4800000 | 2010-12-06 | [38 empty] | 2011-06-01 | 2013-06-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T2435516SP | TO->FROM | CANTON - TALOGA 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521064 | TALOGA 2 69.000 | 520843 | CANTON-2 69.000 | 0 |  | 1 | 16SP | 33 | 39 | 39 |  | 69.9096 | 101.8442 | [7 empty] | CATEGORYB | SINGLE | CEDARDALE - MOORELAND 138KV CKT 1 | 0 | 520848 | CEDRDAL4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 |  | 40 |  | WFEC | CANTON - TALOGA 69KV CKT 1 | UPGRADE CANTON TO TALOGA TO 336.4 | 106 | 132 |  |  | 9.7 |  |  |  | 0.04013 | 0.16101 | 0.00252 |  | 4800000 | 2010-12-06 | [38 empty] | 2011-06-01 | 2013-06-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T2465516SP | TO->FROM | CANTON - TALOGA 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521064 | TALOGA 2 69.000 | 520843 | CANTON-2 69.000 | 0 |  | 1 | 16SP | 33 | 39 | 39 |  | 68.3796 | 100.1844 | [7 empty] | CATEGORYB | SINGLE | CEDARDALE - OKEENE 138KV CKT 1 | 0 | 520848 | CEDRDAL4 138.00 | 521016 | OKEENE 4 138.00 | 0 |  | 1 |  | 40 |  | WFEC | CANTON - TALOGA 69KV CKT 1 | UPGRADE CANTON TO TALOGA TO 336.4 | 106 | 132 |  |  | 9.7 |  |  |  | 0.04013 | 0.16101 | 0.00252 |  | 4800000 | 2010-12-06 | [38 empty] | 2011-06-01 | 2013-06-01 | 2012-10-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T4015521SP | TO->FROM | CANYON EAST SUB - OSAGE SWITCHING STATION 115KV CKT 1 | REL | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524345 | OSAGE 3115.00 | 524523 | CANYON_EAST3115.00 | 0 |  | 1 | 21SP | 96 | 96 | 0 | 118.8 | 118.7731 | 119.6418 | [7 empty] | CATEGORYB | SINGLE | DEAF SMITH COUNTY INTERCHANGE - HEREFORD INTERCHANGE 115KV CKT 1 | 0 | 524606 | HEREFORD 3115.00 | 524622 | DEAFSMITH 3115.00 | 0 |  | 1 |  | 115 |  | SPS | BUSHLAND - NE HEREFORD 115KV CKT 1 | Build 35 miles of 115 kV line from Bushland to NE Hereford 524266-524567 rated 246/270 MVA summer normal/emergency rating | [52 empty] | 2019-06-01 | 2019-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T3855521SP | TO->FROM | CANYON EAST SUB - OSAGE SWITCHING STATION 115KV CKT 1 | REL | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524345 | OSAGE 3115.00 | 524523 | CANYON_EAST3115.00 | 0 |  | 1 | 21SP | 96 | 96 | 0 | 111.8 | 111.7893 | 114.0375 | [7 empty] | CATEGORYB | SINGLE | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 |  | 110 |  | SPS | BUSHLAND - NE HEREFORD 115KV CKT 1 | Build 35 miles of 115 kV line from Bushland to NE Hereford 524266-524567 rated 246/270 MVA summer normal/emergency rating | [52 empty] | 2019-06-01 | 2019-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T4325521SP | FROM->TO | CARLISLE INTERCHANGE 230/115KV TRANSFORMER CKT 1 | REL | SPS | SPS | SPS-CNPL | SPS-CNPL | 0 | 526161 | CARLISLE 6230.00 | 526160 | CARLISLE 3115.00 | 0 |  | 1 | 21SP | 168 | 168 | 0 | 103.1 | 103.0938 | 102.6836 | [7 empty] | CATEGORYB | SINGLE | ALLEN SUB - LUBBOCK SOUTH INTERCHANGE 115KV CKT 1 | 0 | 526213 | ALLEN 3115.00 | 526268 | LUBBCK_STH 3115.00 | 0 |  | 1 |  | 173 |  | SPS | CARLISLE INTERCHANGE 230/115KV TRANSFORMER CKT 1 | Upgrade the Carlisle Transformer to 252 MVA |  | 252 | [50 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T4485021SP | FROM->TO | CARLISLE INTERCHANGE 230/115KV TRANSFORMER CKT 1 | REL | SPS | SPS | SPS-CNPL | SPS-CNPL | 0 | 526161 | CARLISLE 6230.00 | 526160 | CARLISLE 3115.00 | 0 |  | 1 | 21SP | 168 | 168 | 0 | 101.8 | 101.8491 | 101.6114 | [7 empty] | CATEGORYB | SINGLE | WOLFFORTH INTERCHANGE - YUMA INTERCHANGE 115KV CKT 1 | 0 | 526475 | YUMA_INT 3115.00 | 526524 | WOLFFORTH 3115.00 | 0 |  | 1 |  | 171 |  | SPS | CARLISLE INTERCHANGE 230/115KV TRANSFORMER CKT 1 | Upgrade the Carlisle Transformer to 252 MVA |  | 252 | [50 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T3515521SP | FROM->TO | CARMEN - EAGLE CHIEF 69KV CKT 1 | S | WFEC | WFEC | AEP-IM | AEP-IM | 0 | 520845 | CARMEN 2 69.000 | 520890 | EAGLCHF2 69.000 | 0 |  | 1 | 21SP | 24 | 24 | 24 |  | 87.1002 | 100.2395 | [7 empty] | CATEGORYB | SINGLE | FAIRVIEW - OKEENE 69KV CKT 1 | 0 | 520909 | FAIRVEW2 69.000 | 521015 | OKEENE 2 69.000 | 0 |  | 1 |  | 25 |  | WFEC | CARMEN - EAGLE CHIEF 69KV CKT 1 | Reset CT ratio | [12 empty] | 100000 | [39 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61V4145521SP |  | CARMEN 69KV | REL | WFEC |  | AEP-IM |  |  | 520845 | CARMEN 2 69.000 | [5 empty] | 21SP | [7 empty] | 0.88708 | 0.88708 | 0.82948 | 0.95169 | 0.9 | 1.05 | CATEGORYB | SINGLE | FAIRVIEW - OKEENE 69KV CKT 1 | 0 | 521015 | OKEENE 2 69.000 | 520909 | FAIRVEW2 69.000 | 0 |  | 1 |  |  |  | WFEC | FAIRVIEW Capacitor 69KV | Install 18 Mvar capacitor at Fairview 69kV bus. | [52 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2535011SP | TO->FROM | CENTENNIAL - COWSKIN 138KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533038 | COWSKIN4 138.00 | 533034 | CENTENN4 138.00 | 0 |  | 1 | 11SP | 232 | 232 | 0 | 107.7 | 107.6935 | 108.3561 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  | 252 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T13035011SP | TO->FROM | CENTENNIAL - COWSKIN 138KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533038 | COWSKIN4 138.00 | 533034 | CENTENN4 138.00 | 0 |  | 1 | 11SP | 232 | 232 | 0 | 103.1 | 103.0795 | 103.7986 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 |  |  |  | 241 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2825012SP | TO->FROM | CENTENNIAL - COWSKIN 138KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533038 | COWSKIN4 138.00 | 533034 | CENTENN4 138.00 | 0 |  | 1 | 12SP | 232 | 232 | 0 | 103.6 | 103.6492 | 104.4857 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  | 243 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 | [7 empty] | 2009AGP2AFS4MANUAL112WP |  | CHAPMAN JUNCTION 115KV | PL | WERE |  | NCENTRAL |  | 0 | 533362 | CHAPMAN3 115.00 | 533323 | CLAYCTR3 115.00 |  |  | 1 | 12WP | [13 empty] | CATEGORYB | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | CHAPMAN JUNCTION 115KV | Build new four terminal ring bus with 2000 amp equipment | [12 empty] | 4877550 | 2011-01-01 | [38 empty] | 2012-10-01 | 2012-10-01
2009-AGP2 | AFS6 | [7 empty] | 2009AGP2AFS4MANUAL112WP |  | CHAPMAN JUNCTION 115KV | PL | WERE |  | NCENTRAL |  | 0 | 533362 | CHAPMAN3 115.00 | 533323 | CLAYCTR3 115.00 |  |  | 1 | 12WP | [13 empty] | CATEGORYB | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | CHAPMAN JUNCTION 115KV Capacitor | Install 14.4 MVAR capacitor at Chapman Junction 115 kV | [12 empty] | 850000 | 2011-01-01 | [38 empty] | 2012-10-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61V4155521SP |  | CHER CY2 69KV | REL | WFEC |  | AEP-CS |  |  | 520849 | CHER CY2 69.000 | [5 empty] | 21SP | [8 empty] | 0.91029 | 0.86456 | 0.96132 | 0.9 | 1.05 | CATEGORYB | SINGLE | FAIRVIEW - OKEENE 69KV CKT 1 | 0 | 521015 | OKEENE 2 69.000 | 520909 | FAIRVEW2 69.000 | 0 |  | 1 |  |  |  | WFEC | FAIRVIEW Capacitor 69KV | Install 18 Mvar capacitor at Fairview 69kV bus. | [52 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61V4155521SP |  | CHER CY2 69KV | REL | WFEC |  | AEP-CS |  |  | 520849 | CHER CY2 69.000 | [5 empty] | 21SP | [8 empty] | 0.91029 | 0.86456 | 0.96132 | 0.9 | 1.05 | CATEGORYB | SINGLE | FAIRVIEW - OKEENE 69KV CKT 1 | 0 | 521015 | OKEENE 2 69.000 | 520909 | FAIRVEW2 69.000 | 0 |  | 1 |  |  |  | WFEC | FAIRVIEW Capacitor 69KV | Install 18 Mvar capacitor at Fairview 69kV bus. | [52 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61V4165521SP |  | CHEROKEE JCT 69KV | REL | WFEC |  | AEP-IM |  |  | 520850 | CHEROKJ2 69.000 | [5 empty] | 21SP | [8 empty] | 0.90494 | 0.85796 | 0.95994 | 0.9 | 1.05 | CATEGORYB | SINGLE | FAIRVIEW - OKEENE 69KV CKT 1 | 0 | 521015 | OKEENE 2 69.000 | 520909 | FAIRVEW2 69.000 | 0 |  | 1 |  |  |  | WFEC | FAIRVIEW Capacitor 69KV | Install 18 Mvar capacitor at Fairview 69kV bus. | [52 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61V4165521SP |  | CHEROKEE JCT 69KV | REL | WFEC |  | AEP-IM |  |  | 520850 | CHEROKJ2 69.000 | [5 empty] | 21SP | [8 empty] | 0.90494 | 0.85796 | 0.95994 | 0.9 | 1.05 | CATEGORYB | SINGLE | FAIRVIEW - OKEENE 69KV CKT 1 | 0 | 521015 | OKEENE 2 69.000 | 520909 | FAIRVEW2 69.000 | 0 |  | 1 |  |  |  | WFEC | FAIRVIEW Capacitor 69KV | Install 18 Mvar capacitor at Fairview 69kV bus. | [52 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61V4175521SP |  | CHEROKEE SW 69KV | REL | WFEC |  | AEP-IM |  |  | 520851 | CHEROKS2 69.000 | [5 empty] | 21SP | [8 empty] | 0.9109 | 0.86856 | 0.96127 | 0.9 | 1.05 | CATEGORYB | SINGLE | FAIRVIEW - OKEENE 69KV CKT 1 | 0 | 521015 | OKEENE 2 69.000 | 520909 | FAIRVEW2 69.000 | 0 |  | 1 |  |  |  | WFEC | FAIRVIEW Capacitor 69KV | Install 18 Mvar capacitor at Fairview 69kV bus. | [52 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61V4175521SP |  | CHEROKEE SW 69KV | REL | WFEC |  | AEP-IM |  |  | 520851 | CHEROKS2 69.000 | [5 empty] | 21SP | [8 empty] | 0.9109 | 0.86856 | 0.96127 | 0.9 | 1.05 | CATEGORYB | SINGLE | FAIRVIEW - OKEENE 69KV CKT 1 | 0 | 521015 | OKEENE 2 69.000 | 520909 | FAIRVEW2 69.000 | 0 |  | 1 |  |  |  | WFEC | FAIRVIEW Capacitor 69KV | Install 18 Mvar capacitor at Fairview 69kV bus. | [52 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61V5775516SP |  | CIMARRON 69KV | REL | WFEC |  | AEP-IM |  |  | 520853 | KNGFSHSW2 69.000 | [5 empty] | 16SP | [8 empty] | 0.90954 | 0.88366 | 0.97238 | 0.9 | 1.05 | CATEGORYB | SINGLE | DOVER SW (DOVER) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 520882 | DOVERSW4 138.00 | 520881 | DOVERSW2 69.000 | 521166 | DVRTERT 13.800 | 1 |  |  |  | WFEC | East Kingfisher Capacitor 69 kV | Install 18 Mvar capacitor at East Kingfisher bus. | [52 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61V5775516SP |  | CIMARRON 69KV | REL | WFEC |  | AEP-IM |  |  | 520853 | KNGFSHSW2 69.000 | [5 empty] | 16SP | [8 empty] | 0.90954 | 0.88366 | 0.97238 | 0.9 | 1.05 | CATEGORYB | SINGLE | DOVER SW (DOVER) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 520882 | DOVERSW4 138.00 | 520881 | DOVERSW2 69.000 | 521166 | DVRTERT 13.800 | 1 |  |  |  | WFEC | East Kingfisher Capacitor 69 kV | Install 18 Mvar capacitor at East Kingfisher bus. | [52 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2725011SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 11SP | 43 | 43 | 0 |  | 71.7267 | 113.911 | [7 empty] | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 |  | 49 |  | WERE | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | Tear down / Rebuild 11.63-mile Timber Tap-Winfield 69 kV line, 954 ACSR | 72 | 72 | 72 | 72 | 11.63 | 18 | 6 |  | 0.0309 | 0.2101 | 0.05164 | Line switches limit to 72 MVA. $790k per mile | 8161986 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2725011SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 11SP | 43 | 43 | 0 |  | 71.7267 | 113.911 | [7 empty] | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 |  | 49 |  | WERE | RICHLAND - UDALL 69KV CKT 1 | Tear down / Rebuild 8.48-mile Richland-Udall 69 kV line using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 8.48 | 13 | 7 | N | 0.01789 | 0.12177 | 0.02589 | MVA limit is conductor $790k per mile | 6699200 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2725011SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 11SP | 43 | 43 | 0 |  | 71.7267 | 113.911 | [7 empty] | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 |  | 49 |  | WERE | RICHLAND - UDALL 69KV CKT 1 | Tear down / Rebuild 8.48-mile Richland-Udall 69 kV line using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 8.48 | 13 | 7 | N | 0.01789 | 0.12177 | 0.02589 | MVA limit is conductor $790k per mile | 6699200 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2725011SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 11SP | 43 | 43 | 0 |  | 71.7267 | 113.911 | [7 empty] | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 |  | 49 |  | WERE | RICHLAND - UDALL 69KV CKT 1 | Tear down / Rebuild 8.48-mile Richland-Udall 69 kV line using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 8.48 | 13 | 7 | N | 0.01789 | 0.12177 | 0.02589 | MVA limit is conductor $790k per mile | 6699200 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2725011SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 11SP | 43 | 43 | 0 |  | 71.7267 | 113.911 | [7 empty] | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 |  | 49 |  | WERE | RICHLAND - UDALL 69KV CKT 1 | Tear down / Rebuild 8.48-mile Richland-Udall 69 kV line using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 8.48 | 13 | 7 | N | 0.01789 | 0.12177 | 0.02589 | MVA limit is conductor $790k per mile | 6699200 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2725011SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 11SP | 43 | 43 | 0 |  | 71.7267 | 113.911 | [7 empty] | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 |  | 49 |  | WERE | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | Tear down / Rebuild 11.63-mile Timber Tap-Winfield 69 kV line, 954 ACSR | 72 | 72 | 72 | 72 | 11.63 | 18 | 6 |  | 0.0309 | 0.2101 | 0.05164 | Line switches limit to 72 MVA. $790k per mile | 8161986 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2725011SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 11SP | 43 | 43 | 0 |  | 71.7267 | 113.911 | [7 empty] | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 |  | 49 |  | WERE | RICHLAND - UDALL 69KV CKT 1 | Tear down / Rebuild 8.48-mile Richland-Udall 69 kV line using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 8.48 | 13 | 7 | N | 0.01789 | 0.12177 | 0.02589 | MVA limit is conductor $790k per mile | 6699200 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2725011SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 11SP | 43 | 43 | 0 |  | 71.7267 | 113.911 | [7 empty] | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 |  | 49 |  | WERE | RICHLAND - UDALL 69KV CKT 1 | Tear down / Rebuild 8.48-mile Richland-Udall 69 kV line using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 8.48 | 13 | 7 | N | 0.01789 | 0.12177 | 0.02589 | MVA limit is conductor $790k per mile | 6699200 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2725011SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 11SP | 43 | 43 | 0 |  | 71.7267 | 113.911 | [7 empty] | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 |  | 49 |  | WERE | RICHLAND - UDALL 69KV CKT 1 | Tear down / Rebuild 8.48-mile Richland-Udall 69 kV line using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 8.48 | 13 | 7 | N | 0.01789 | 0.12177 | 0.02589 | MVA limit is conductor $790k per mile | 6699200 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2725011SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 11SP | 43 | 43 | 0 |  | 71.7267 | 113.911 | [7 empty] | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 |  | 49 |  | WERE | RICHLAND - UDALL 69KV CKT 1 | Tear down / Rebuild 8.48-mile Richland-Udall 69 kV line using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 8.48 | 13 | 7 | N | 0.01789 | 0.12177 | 0.02589 | MVA limit is conductor $790k per mile | 6699200 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6NC |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS6NC1T115011SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 11SP | 43 | 43 | 0 | 69.9257 | 69.9257 | 105.9982 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-41B | 0 | 0 |  | 0 |  | 0 |  |  |  | 46 |  | WERE | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | Tear down / Rebuild 11.63-mile Timber Tap-Winfield 69 kV line, 954 ACSR | 72 | 72 | 72 | 72 | 11.63 | 18 | 6 |  | 0.0309 | 0.2101 | 0.05164 | Line switches limit to 72 MVA. $790k per mile | 8161986 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2009-AGP2 | AFS6NC |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS6NC1T115011SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 11SP | 43 | 43 | 0 | 69.9257 | 69.9257 | 105.9982 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-41B | 0 | 0 |  | 0 |  | 0 |  |  |  | 46 |  | WERE | RICHLAND - UDALL 69KV CKT 1 | Tear down / Rebuild 8.48-mile Richland-Udall 69 kV line using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 8.48 | 13 | 7 | N | 0.01789 | 0.12177 | 0.02589 | MVA limit is conductor $790k per mile | 6699200 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6NC |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS6NC1T115011SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 11SP | 43 | 43 | 0 | 69.9257 | 69.9257 | 105.9982 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-41B | 0 | 0 |  | 0 |  | 0 |  |  |  | 46 |  | WERE | TIMBER JUNCTION - UDALL 69KV CKT 1 | Tear down / Rebuild Udall-Timber Jct 69 kV using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 2.01 | 4 | 2 | N | 0.00424 | 0.02886 | 0.00614 | MVA limit is conductor $790k per mile | 1587900 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6NC |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS6NC1T115011SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 11SP | 43 | 43 | 0 | 69.9257 | 69.9257 | 105.9982 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-41B | 0 | 0 |  | 0 |  | 0 |  |  |  | 46 |  | WERE | RICHLAND - UDALL 69KV CKT 1 | Tear down / Rebuild 8.48-mile Richland-Udall 69 kV line using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 8.48 | 13 | 7 | N | 0.01789 | 0.12177 | 0.02589 | MVA limit is conductor $790k per mile | 6699200 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6NC |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS6NC1T115011SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 11SP | 43 | 43 | 0 | 69.9257 | 69.9257 | 105.9982 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-41B | 0 | 0 |  | 0 |  | 0 |  |  |  | 46 |  | WERE | TIMBER JUNCTION - UDALL 69KV CKT 1 | Tear down / Rebuild Udall-Timber Jct 69 kV using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 2.01 | 4 | 2 | N | 0.00424 | 0.02886 | 0.00614 | MVA limit is conductor $790k per mile | 1587900 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6NC |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS6NC1T115011SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 11SP | 43 | 43 | 0 | 69.9257 | 69.9257 | 105.9982 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-41B | 0 | 0 |  | 0 |  | 0 |  |  |  | 46 |  | WERE | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | Tear down / Rebuild 11.63-mile Timber Tap-Winfield 69 kV line, 954 ACSR | 72 | 72 | 72 | 72 | 11.63 | 18 | 6 |  | 0.0309 | 0.2101 | 0.05164 | Line switches limit to 72 MVA. $790k per mile | 8161986 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2009-AGP2 | AFS6NC |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS6NC1T115011SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 11SP | 43 | 43 | 0 | 69.9257 | 69.9257 | 105.9982 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-41B | 0 | 0 |  | 0 |  | 0 |  |  |  | 46 |  | WERE | RICHLAND - UDALL 69KV CKT 1 | Tear down / Rebuild 8.48-mile Richland-Udall 69 kV line using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 8.48 | 13 | 7 | N | 0.01789 | 0.12177 | 0.02589 | MVA limit is conductor $790k per mile | 6699200 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6NC |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS6NC1T115011SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 11SP | 43 | 43 | 0 | 69.9257 | 69.9257 | 105.9982 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-41B | 0 | 0 |  | 0 |  | 0 |  |  |  | 46 |  | WERE | TIMBER JUNCTION - UDALL 69KV CKT 1 | Tear down / Rebuild Udall-Timber Jct 69 kV using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 2.01 | 4 | 2 | N | 0.00424 | 0.02886 | 0.00614 | MVA limit is conductor $790k per mile | 1587900 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6NC |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS6NC1T115011SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 11SP | 43 | 43 | 0 | 69.9257 | 69.9257 | 105.9982 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-41B | 0 | 0 |  | 0 |  | 0 |  |  |  | 46 |  | WERE | RICHLAND - UDALL 69KV CKT 1 | Tear down / Rebuild 8.48-mile Richland-Udall 69 kV line using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 8.48 | 13 | 7 | N | 0.01789 | 0.12177 | 0.02589 | MVA limit is conductor $790k per mile | 6699200 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6NC |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS6NC1T115011SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 11SP | 43 | 43 | 0 | 69.9257 | 69.9257 | 105.9982 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-41B | 0 | 0 |  | 0 |  | 0 |  |  |  | 46 |  | WERE | TIMBER JUNCTION - UDALL 69KV CKT 1 | Tear down / Rebuild Udall-Timber Jct 69 kV using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 2.01 | 4 | 2 | N | 0.00424 | 0.02886 | 0.00614 | MVA limit is conductor $790k per mile | 1587900 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T15055511SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 11SP | 43 | 43 | 0 |  | 69.2235 | 102.8963 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-41B | 0 | 0 |  | 0 |  | 0 |  |  |  | 45 |  | WERE | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | Tear down / Rebuild 11.63-mile Timber Tap-Winfield 69 kV line, 954 ACSR | 72 | 72 | 72 | 72 | 11.63 | 18 | 6 |  | 0.0309 | 0.2101 | 0.05164 | Line switches limit to 72 MVA. $790k per mile | 8161986 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T15055511SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 11SP | 43 | 43 | 0 |  | 69.2235 | 102.8963 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-41B | 0 | 0 |  | 0 |  | 0 |  |  |  | 45 |  | WERE | RICHLAND - UDALL 69KV CKT 1 | Tear down / Rebuild 8.48-mile Richland-Udall 69 kV line using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 8.48 | 13 | 7 | N | 0.01789 | 0.12177 | 0.02589 | MVA limit is conductor $790k per mile | 6699200 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T15055511SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 11SP | 43 | 43 | 0 |  | 69.2235 | 102.8963 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-41B | 0 | 0 |  | 0 |  | 0 |  |  |  | 45 |  | WERE | TIMBER JUNCTION - UDALL 69KV CKT 1 | Tear down / Rebuild Udall-Timber Jct 69 kV using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 2.01 | 4 | 2 | N | 0.00424 | 0.02886 | 0.00614 | MVA limit is conductor $790k per mile | 1587900 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T15055511SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 11SP | 43 | 43 | 0 |  | 69.2235 | 102.8963 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-41B | 0 | 0 |  | 0 |  | 0 |  |  |  | 45 |  | WERE | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | Tear down / Rebuild 11.63-mile Timber Tap-Winfield 69 kV line, 954 ACSR | 72 | 72 | 72 | 72 | 11.63 | 18 | 6 |  | 0.0309 | 0.2101 | 0.05164 | Line switches limit to 72 MVA. $790k per mile | 8161986 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T15055511SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 11SP | 43 | 43 | 0 |  | 69.2235 | 102.8963 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-41B | 0 | 0 |  | 0 |  | 0 |  |  |  | 45 |  | WERE | RICHLAND - UDALL 69KV CKT 1 | Tear down / Rebuild 8.48-mile Richland-Udall 69 kV line using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 8.48 | 13 | 7 | N | 0.01789 | 0.12177 | 0.02589 | MVA limit is conductor $790k per mile | 6699200 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T15055511SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 11SP | 43 | 43 | 0 |  | 69.2235 | 102.8963 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-41B | 0 | 0 |  | 0 |  | 0 |  |  |  | 45 |  | WERE | TIMBER JUNCTION - UDALL 69KV CKT 1 | Tear down / Rebuild Udall-Timber Jct 69 kV using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 2.01 | 4 | 2 | N | 0.00424 | 0.02886 | 0.00614 | MVA limit is conductor $790k per mile | 1587900 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2985012SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 12SP | 43 | 43 | 0 |  | 74.3756 | 117.6575 | [7 empty] | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 |  | 51 |  | WERE | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | Tear down / Rebuild 11.63-mile Timber Tap-Winfield 69 kV line, 954 ACSR | 72 | 72 | 72 | 72 | 11.63 | 18 | 6 |  | 0.0309 | 0.2101 | 0.05164 | Line switches limit to 72 MVA. $790k per mile | 8161986 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2985012SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 12SP | 43 | 43 | 0 |  | 74.3756 | 117.6575 | [7 empty] | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 |  | 51 |  | WERE | TIMBER JUNCTION - UDALL 69KV CKT 1 | Tear down / Rebuild Udall-Timber Jct 69 kV using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 2.01 | 4 | 2 | N | 0.00424 | 0.02886 | 0.00614 | MVA limit is conductor $790k per mile | 1587900 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2985012SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 12SP | 43 | 43 | 0 |  | 74.3756 | 117.6575 | [7 empty] | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 |  | 51 |  | WERE | TIMBER JUNCTION - UDALL 69KV CKT 1 | Tear down / Rebuild Udall-Timber Jct 69 kV using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 2.01 | 4 | 2 | N | 0.00424 | 0.02886 | 0.00614 | MVA limit is conductor $790k per mile | 1587900 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2985012SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 12SP | 43 | 43 | 0 |  | 74.3756 | 117.6575 | [7 empty] | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 |  | 51 |  | WERE | TIMBER JUNCTION - UDALL 69KV CKT 1 | Tear down / Rebuild Udall-Timber Jct 69 kV using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 2.01 | 4 | 2 | N | 0.00424 | 0.02886 | 0.00614 | MVA limit is conductor $790k per mile | 1587900 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2985012SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 12SP | 43 | 43 | 0 |  | 74.3756 | 117.6575 | [7 empty] | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 |  | 51 |  | WERE | TIMBER JUNCTION - UDALL 69KV CKT 1 | Tear down / Rebuild Udall-Timber Jct 69 kV using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 2.01 | 4 | 2 | N | 0.00424 | 0.02886 | 0.00614 | MVA limit is conductor $790k per mile | 1587900 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2985012SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 12SP | 43 | 43 | 0 |  | 74.3756 | 117.6575 | [7 empty] | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 |  | 51 |  | WERE | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | Tear down / Rebuild 11.63-mile Timber Tap-Winfield 69 kV line, 954 ACSR | 72 | 72 | 72 | 72 | 11.63 | 18 | 6 |  | 0.0309 | 0.2101 | 0.05164 | Line switches limit to 72 MVA. $790k per mile | 8161986 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2985012SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 12SP | 43 | 43 | 0 |  | 74.3756 | 117.6575 | [7 empty] | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 |  | 51 |  | WERE | TIMBER JUNCTION - UDALL 69KV CKT 1 | Tear down / Rebuild Udall-Timber Jct 69 kV using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 2.01 | 4 | 2 | N | 0.00424 | 0.02886 | 0.00614 | MVA limit is conductor $790k per mile | 1587900 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2985012SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 12SP | 43 | 43 | 0 |  | 74.3756 | 117.6575 | [7 empty] | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 |  | 51 |  | WERE | TIMBER JUNCTION - UDALL 69KV CKT 1 | Tear down / Rebuild Udall-Timber Jct 69 kV using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 2.01 | 4 | 2 | N | 0.00424 | 0.02886 | 0.00614 | MVA limit is conductor $790k per mile | 1587900 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2985012SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 12SP | 43 | 43 | 0 |  | 74.3756 | 117.6575 | [7 empty] | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 |  | 51 |  | WERE | TIMBER JUNCTION - UDALL 69KV CKT 1 | Tear down / Rebuild Udall-Timber Jct 69 kV using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 2.01 | 4 | 2 | N | 0.00424 | 0.02886 | 0.00614 | MVA limit is conductor $790k per mile | 1587900 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2985012SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 12SP | 43 | 43 | 0 |  | 74.3756 | 117.6575 | [7 empty] | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 |  | 51 |  | WERE | TIMBER JUNCTION - UDALL 69KV CKT 1 | Tear down / Rebuild Udall-Timber Jct 69 kV using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 2.01 | 4 | 2 | N | 0.00424 | 0.02886 | 0.00614 | MVA limit is conductor $790k per mile | 1587900 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T13095012SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 12SP | 43 | 43 | 0 |  | 72.3762 | 109.0478 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-41B | 0 | 0 |  | 0 |  | 0 |  |  |  | 47 |  | WERE | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | Tear down / Rebuild 11.63-mile Timber Tap-Winfield 69 kV line, 954 ACSR | 72 | 72 | 72 | 72 | 11.63 | 18 | 6 |  | 0.0309 | 0.2101 | 0.05164 | Line switches limit to 72 MVA. $790k per mile | 8161986 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T13095012SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 12SP | 43 | 43 | 0 |  | 72.3762 | 109.0478 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-41B | 0 | 0 |  | 0 |  | 0 |  |  |  | 47 |  | WERE | RICHLAND - UDALL 69KV CKT 1 | Tear down / Rebuild 8.48-mile Richland-Udall 69 kV line using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 8.48 | 13 | 7 | N | 0.01789 | 0.12177 | 0.02589 | MVA limit is conductor $790k per mile | 6699200 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T13095012SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 12SP | 43 | 43 | 0 |  | 72.3762 | 109.0478 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-41B | 0 | 0 |  | 0 |  | 0 |  |  |  | 47 |  | WERE | TIMBER JUNCTION - UDALL 69KV CKT 1 | Tear down / Rebuild Udall-Timber Jct 69 kV using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 2.01 | 4 | 2 | N | 0.00424 | 0.02886 | 0.00614 | MVA limit is conductor $790k per mile | 1587900 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T13095012SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 12SP | 43 | 43 | 0 |  | 72.3762 | 109.0478 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-41B | 0 | 0 |  | 0 |  | 0 |  |  |  | 47 |  | WERE | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | Tear down / Rebuild 11.63-mile Timber Tap-Winfield 69 kV line, 954 ACSR | 72 | 72 | 72 | 72 | 11.63 | 18 | 6 |  | 0.0309 | 0.2101 | 0.05164 | Line switches limit to 72 MVA. $790k per mile | 8161986 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T13095012SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 12SP | 43 | 43 | 0 |  | 72.3762 | 109.0478 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-41B | 0 | 0 |  | 0 |  | 0 |  |  |  | 47 |  | WERE | RICHLAND - UDALL 69KV CKT 1 | Tear down / Rebuild 8.48-mile Richland-Udall 69 kV line using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 8.48 | 13 | 7 | N | 0.01789 | 0.12177 | 0.02589 | MVA limit is conductor $790k per mile | 6699200 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T13095012SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 12SP | 43 | 43 | 0 |  | 72.3762 | 109.0478 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-41B | 0 | 0 |  | 0 |  | 0 |  |  |  | 47 |  | WERE | TIMBER JUNCTION - UDALL 69KV CKT 1 | Tear down / Rebuild Udall-Timber Jct 69 kV using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 2.01 | 4 | 2 | N | 0.00424 | 0.02886 | 0.00614 | MVA limit is conductor $790k per mile | 1587900 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2615012SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 12SP | 43 | 43 | 0 |  | 63.7339 | 103.3666 | [7 empty] | CATEGORYB | SINGLE | OXFORD - SUMNER 4 138KV CKT 1 | 0 | 532982 | OXFORD 4 138.00 | 532984 | SUMNER 4 138.00 | 0 |  | 1 |  | 45 |  | WERE | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | Tear down / Rebuild 11.63-mile Timber Tap-Winfield 69 kV line, 954 ACSR | 72 | 72 | 72 | 72 | 11.63 | 18 | 6 |  | 0.0309 | 0.2101 | 0.05164 | Line switches limit to 72 MVA. $790k per mile | 8161986 | 2010-01-01 | 41061 | [37 empty] | 2011-06-01 | 2011-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2615012SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 12SP | 43 | 43 | 0 |  | 63.7339 | 103.3666 | [7 empty] | CATEGORYB | SINGLE | OXFORD - SUMNER 4 138KV CKT 1 | 0 | 532982 | OXFORD 4 138.00 | 532984 | SUMNER 4 138.00 | 0 |  | 1 |  | 45 |  | WERE | RICHLAND - UDALL 69KV CKT 1 | Tear down / Rebuild 8.48-mile Richland-Udall 69 kV line using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 8.48 | 13 | 7 | N | 0.01789 | 0.12177 | 0.02589 | MVA limit is conductor $790k per mile | 6699200 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2615012SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 12SP | 43 | 43 | 0 |  | 63.7339 | 103.3666 | [7 empty] | CATEGORYB | SINGLE | OXFORD - SUMNER 4 138KV CKT 1 | 0 | 532982 | OXFORD 4 138.00 | 532984 | SUMNER 4 138.00 | 0 |  | 1 |  | 45 |  | WERE | TIMBER JUNCTION - UDALL 69KV CKT 1 | Tear down / Rebuild Udall-Timber Jct 69 kV using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 2.01 | 4 | 2 | N | 0.00424 | 0.02886 | 0.00614 | MVA limit is conductor $790k per mile | 1587900 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2615012SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 12SP | 43 | 43 | 0 |  | 63.7339 | 103.3666 | [7 empty] | CATEGORYB | SINGLE | OXFORD - SUMNER 4 138KV CKT 1 | 0 | 532982 | OXFORD 4 138.00 | 532984 | SUMNER 4 138.00 | 0 |  | 1 |  | 45 |  | WERE | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | Tear down / Rebuild 11.63-mile Timber Tap-Winfield 69 kV line, 954 ACSR | 72 | 72 | 72 | 72 | 11.63 | 18 | 6 |  | 0.0309 | 0.2101 | 0.05164 | Line switches limit to 72 MVA. $790k per mile | 8161986 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2615012SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 12SP | 43 | 43 | 0 |  | 63.7339 | 103.3666 | [7 empty] | CATEGORYB | SINGLE | OXFORD - SUMNER 4 138KV CKT 1 | 0 | 532982 | OXFORD 4 138.00 | 532984 | SUMNER 4 138.00 | 0 |  | 1 |  | 45 |  | WERE | RICHLAND - UDALL 69KV CKT 1 | Tear down / Rebuild 8.48-mile Richland-Udall 69 kV line using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 8.48 | 13 | 7 | N | 0.01789 | 0.12177 | 0.02589 | MVA limit is conductor $790k per mile | 6699200 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2615012SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 12SP | 43 | 43 | 0 |  | 63.7339 | 103.3666 | [7 empty] | CATEGORYB | SINGLE | OXFORD - SUMNER 4 138KV CKT 1 | 0 | 532982 | OXFORD 4 138.00 | 532984 | SUMNER 4 138.00 | 0 |  | 1 |  | 45 |  | WERE | TIMBER JUNCTION - UDALL 69KV CKT 1 | Tear down / Rebuild Udall-Timber Jct 69 kV using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 2.01 | 4 | 2 | N | 0.00424 | 0.02886 | 0.00614 | MVA limit is conductor $790k per mile | 1587900 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T3405516SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 16SP | 43 | 43 | 0 |  | 77.6347 | 107.1487 | [7 empty] | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 |  | 47 |  | WERE | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | Tear down / Rebuild 11.63-mile Timber Tap-Winfield 69 kV line, 954 ACSR | 72 | 72 | 72 | 72 | 11.63 | 18 | 6 |  | 0.0309 | 0.2101 | 0.05164 | Line switches limit to 72 MVA. $790k per mile | 8161986 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T3405516SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 16SP | 43 | 43 | 0 |  | 77.6347 | 107.1487 | [7 empty] | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 |  | 47 |  | WERE | RICHLAND - UDALL 69KV CKT 1 | Tear down / Rebuild 8.48-mile Richland-Udall 69 kV line using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 8.48 | 13 | 7 | N | 0.01789 | 0.12177 | 0.02589 | MVA limit is conductor $790k per mile | 6699200 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T3405516SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 16SP | 43 | 43 | 0 |  | 77.6347 | 107.1487 | [7 empty] | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 |  | 47 |  | WERE | TIMBER JUNCTION - UDALL 69KV CKT 1 | Tear down / Rebuild Udall-Timber Jct 69 kV using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 2.01 | 4 | 2 | N | 0.00424 | 0.02886 | 0.00614 | MVA limit is conductor $790k per mile | 1587900 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T3405516SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 16SP | 43 | 43 | 0 |  | 77.6347 | 107.1487 | [7 empty] | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 |  | 47 |  | WERE | RICHLAND - UDALL 69KV CKT 1 | Tear down / Rebuild 8.48-mile Richland-Udall 69 kV line using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 8.48 | 13 | 7 | N | 0.01789 | 0.12177 | 0.02589 | MVA limit is conductor $790k per mile | 6699200 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T3405516SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 16SP | 43 | 43 | 0 |  | 77.6347 | 107.1487 | [7 empty] | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 |  | 47 |  | WERE | TIMBER JUNCTION - UDALL 69KV CKT 1 | Tear down / Rebuild Udall-Timber Jct 69 kV using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 2.01 | 4 | 2 | N | 0.00424 | 0.02886 | 0.00614 | MVA limit is conductor $790k per mile | 1587900 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T3405516SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 16SP | 43 | 43 | 0 |  | 77.6347 | 107.1487 | [7 empty] | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 |  | 47 |  | WERE | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | Tear down / Rebuild 11.63-mile Timber Tap-Winfield 69 kV line, 954 ACSR | 72 | 72 | 72 | 72 | 11.63 | 18 | 6 |  | 0.0309 | 0.2101 | 0.05164 | Line switches limit to 72 MVA. $790k per mile | 8161986 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T3405516SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 16SP | 43 | 43 | 0 |  | 77.6347 | 107.1487 | [7 empty] | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 |  | 47 |  | WERE | RICHLAND - UDALL 69KV CKT 1 | Tear down / Rebuild 8.48-mile Richland-Udall 69 kV line using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 8.48 | 13 | 7 | N | 0.01789 | 0.12177 | 0.02589 | MVA limit is conductor $790k per mile | 6699200 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T3405516SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 16SP | 43 | 43 | 0 |  | 77.6347 | 107.1487 | [7 empty] | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 |  | 47 |  | WERE | TIMBER JUNCTION - UDALL 69KV CKT 1 | Tear down / Rebuild Udall-Timber Jct 69 kV using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 2.01 | 4 | 2 | N | 0.00424 | 0.02886 | 0.00614 | MVA limit is conductor $790k per mile | 1587900 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T3405516SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 16SP | 43 | 43 | 0 |  | 77.6347 | 107.1487 | [7 empty] | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 |  | 47 |  | WERE | RICHLAND - UDALL 69KV CKT 1 | Tear down / Rebuild 8.48-mile Richland-Udall 69 kV line using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 8.48 | 13 | 7 | N | 0.01789 | 0.12177 | 0.02589 | MVA limit is conductor $790k per mile | 6699200 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T3405516SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 16SP | 43 | 43 | 0 |  | 77.6347 | 107.1487 | [7 empty] | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 |  | 47 |  | WERE | TIMBER JUNCTION - UDALL 69KV CKT 1 | Tear down / Rebuild Udall-Timber Jct 69 kV using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 2.01 | 4 | 2 | N | 0.00424 | 0.02886 | 0.00614 | MVA limit is conductor $790k per mile | 1587900 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T3305521SP | TO->FROM | CLASSEN - SW 5TAP 138KV CKT 1 | REL | OKGE | OKGE |  |  | 0 | 514921 | SW 5TAP4 138.00 | 514922 | CLASSEN4 138.00 | 0 |  | 1 | 21SP | 191 | 191 | 0 | 112.8 | 112.8148 | 114.5187 | [7 empty] | CATEGORYB | SINGLE | COUNCIL - MUSTANG 138KV CKT 1 | 0 | 514861 | MUSTANG4 138.00 | 514865 | COUNCIL4 138.00 | 0 |  | 1 |  | 219 |  | OKGE | CLASSEN - SW 5TAP 138KV CKT 1 | Replace 800A trap and CT at Classen | 268 | 287 | 287 | 287 |  | 18 | 8 | [5 empty] | 250000 | 2010-07-09 | [38 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T3305521SP | TO->FROM | CLASSEN - SW 5TAP 138KV CKT 1 | REL | OKGE | OKGE |  |  | 0 | 514921 | SW 5TAP4 138.00 | 514922 | CLASSEN4 138.00 | 0 |  | 1 | 21SP | 191 | 191 | 0 | 112.8 | 112.8148 | 114.5187 | [7 empty] | CATEGORYB | SINGLE | COUNCIL - MUSTANG 138KV CKT 1 | 0 | 514861 | MUSTANG4 138.00 | 514865 | COUNCIL4 138.00 | 0 |  | 1 |  | 219 |  | OKGE | CLASSEN - SW 5TAP 138KV CKT 1 | Replace 800A trap and CT at Classen | 268 | 287 | 287 | 287 |  | 18 | 8 | [5 empty] | 250000 | 2010-07-09 | [38 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T3305521SP | TO->FROM | CLASSEN - SW 5TAP 138KV CKT 1 | REL | OKGE | OKGE |  |  | 0 | 514921 | SW 5TAP4 138.00 | 514922 | CLASSEN4 138.00 | 0 |  | 1 | 21SP | 191 | 191 | 0 | 112.8 | 112.8148 | 114.5187 | [7 empty] | CATEGORYB | SINGLE | COUNCIL - MUSTANG 138KV CKT 1 | 0 | 514861 | MUSTANG4 138.00 | 514865 | COUNCIL4 138.00 | 0 |  | 1 |  | 219 |  | OKGE | CLASSEN - SW 5TAP 138KV CKT 1 | Replace 800A trap and CT at Classen | 268 | 287 | 287 | 287 |  | 18 | 8 | [5 empty] | 250000 | 2010-07-09 | [38 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T3305521SP | TO->FROM | CLASSEN - SW 5TAP 138KV CKT 1 | REL | OKGE | OKGE |  |  | 0 | 514921 | SW 5TAP4 138.00 | 514922 | CLASSEN4 138.00 | 0 |  | 1 | 21SP | 191 | 191 | 0 | 112.8 | 112.8148 | 114.5187 | [7 empty] | CATEGORYB | SINGLE | COUNCIL - MUSTANG 138KV CKT 1 | 0 | 514861 | MUSTANG4 138.00 | 514865 | COUNCIL4 138.00 | 0 |  | 1 |  | 219 |  | OKGE | CLASSEN - SW 5TAP 138KV CKT 1 | Replace 800A trap and CT at Classen | 268 | 287 | 287 | 287 |  | 18 | 8 | [5 empty] | 250000 | 2010-07-09 | [38 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T3315521SP | TO->FROM | CLASSEN - SW 5TAP 138KV CKT 1 | REL | OKGE | OKGE |  |  | 0 | 514921 | SW 5TAP4 138.00 | 514922 | CLASSEN4 138.00 | 0 |  | 1 | 21SP | 191 | 191 | 0 | 106.3 | 106.2778 | 107.9778 | [7 empty] | CATEGORYB | SINGLE | COUNCIL - WESTOAKS 138KV CKT 1 | 0 | 514865 | COUNCIL4 138.00 | 514866 | WESTOAK4 138.00 | 0 |  | 1 |  | 207 |  | OKGE | CLASSEN - SW 5TAP 138KV CKT 1 | Replace 800A trap and CT at Classen | 268 | 287 | 287 | 287 |  | 18 | 8 | [5 empty] | 250000 | 2010-07-09 | [38 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T3315521SP | TO->FROM | CLASSEN - SW 5TAP 138KV CKT 1 | REL | OKGE | OKGE |  |  | 0 | 514921 | SW 5TAP4 138.00 | 514922 | CLASSEN4 138.00 | 0 |  | 1 | 21SP | 191 | 191 | 0 | 106.3 | 106.2778 | 107.9778 | [7 empty] | CATEGORYB | SINGLE | COUNCIL - WESTOAKS 138KV CKT 1 | 0 | 514865 | COUNCIL4 138.00 | 514866 | WESTOAK4 138.00 | 0 |  | 1 |  | 207 |  | OKGE | CLASSEN - SW 5TAP 138KV CKT 1 | Replace 800A trap and CT at Classen | 268 | 287 | 287 | 287 |  | 18 | 8 | [5 empty] | 250000 | 2010-07-09 | [38 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T3315521SP | TO->FROM | CLASSEN - SW 5TAP 138KV CKT 1 | REL | OKGE | OKGE |  |  | 0 | 514921 | SW 5TAP4 138.00 | 514922 | CLASSEN4 138.00 | 0 |  | 1 | 21SP | 191 | 191 | 0 | 106.3 | 106.2778 | 107.9778 | [7 empty] | CATEGORYB | SINGLE | COUNCIL - WESTOAKS 138KV CKT 1 | 0 | 514865 | COUNCIL4 138.00 | 514866 | WESTOAK4 138.00 | 0 |  | 1 |  | 207 |  | OKGE | CLASSEN - SW 5TAP 138KV CKT 1 | Replace 800A trap and CT at Classen | 268 | 287 | 287 | 287 |  | 18 | 8 | [5 empty] | 250000 | 2010-07-09 | [38 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T3315521SP | TO->FROM | CLASSEN - SW 5TAP 138KV CKT 1 | REL | OKGE | OKGE |  |  | 0 | 514921 | SW 5TAP4 138.00 | 514922 | CLASSEN4 138.00 | 0 |  | 1 | 21SP | 191 | 191 | 0 | 106.3 | 106.2778 | 107.9778 | [7 empty] | CATEGORYB | SINGLE | COUNCIL - WESTOAKS 138KV CKT 1 | 0 | 514865 | COUNCIL4 138.00 | 514866 | WESTOAK4 138.00 | 0 |  | 1 |  | 207 |  | OKGE | CLASSEN - SW 5TAP 138KV CKT 1 | Replace 800A trap and CT at Classen | 268 | 287 | 287 | 287 |  | 18 | 8 | [5 empty] | 250000 | 2010-07-09 | [38 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 | [7 empty] | 2009AGP2AFS4MANUAL212WP |  | CLAY CENTER JUNCTION 115KV | PL | WERE |  | NCENTRAL |  | 0 | 533362 | CHAPMAN3 115.00 | 533323 | CLAYCTR3 115.00 |  |  | 1 | 12WP | [13 empty] | CATEGORYB | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | CLAY CENTER JUNCTION 115KV | Rebuild Clay Center Jct bus to a flat bus design with 4” IPS Bus and 2000 Amp equipment with 2 new 115 kV deadend structures, new metering equipment, and a new control building. | [12 empty] | 2837646 | 2011-01-01 | [38 empty] | 2012-10-01 | 2012-10-01
2009-AGP2 | AFS6 | [7 empty] | 2009AGP2AFS4MANUAL212WP |  | CLAY CENTER JUNCTION 115KV | PL | WERE |  | NCENTRAL |  | 0 | 533362 | CHAPMAN3 115.00 | 533323 | CLAYCTR3 115.00 |  |  | 1 | 12WP | [13 empty] | CATEGORYB | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | CLAY CENTER JUNCTION - CLAY CENTER SWITCHING STATION 115KV CKT 1 | Build 10 mile 115 kV line with Single 1192.5 kcmil ACSR (Bunting) | [12 empty] | 11340902 | 2011-01-01 | [38 empty] | 2012-10-01 | 2012-10-01
2009-AGP2 | AFS6 | [7 empty] | 2009AGP2AFS4MANUAL212WP |  | CLAY CENTER JUNCTION 115KV | PL | WERE |  | NCENTRAL |  | 0 | 533362 | CHAPMAN3 115.00 | 533323 | CLAYCTR3 115.00 |  |  | 1 | 12WP | [13 empty] | CATEGORYB | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | TC RILEY 115KV | Install a 2000 Amp bus system, GOAB switches, metering and communication systems. | [12 empty] | 850000 | 2011-01-01 | [38 empty] | 2012-10-01 | 2012-10-01
2009-AGP2 | AFS6 | [7 empty] | 2009AGP2AFS4MANUAL212WP |  | CLAY CENTER JUNCTION 115KV | PL | WERE |  | NCENTRAL |  | 0 | 533362 | CHAPMAN3 115.00 | 533323 | CLAYCTR3 115.00 |  |  | 1 | 12WP | [13 empty] | CATEGORYB | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | CLAY CENTER SWITCHING STATION - TC RILEY 115KV CKT 1 | Build 6.7 mile 115 kV line with Single 1192.5 kcmil ACSR (Bunting) | [12 empty] | 11340902 | 2011-01-01 | [38 empty] | 2012-10-01 | 2012-10-01
2009-AGP2 | AFS6 | CONT-0900 - JEC - East Manhattan 230kV |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61V6315021SP |  | CLAY CENTER JUNCTION 115KV | PL | WERE |  | NCENTRAL |  |  | 533323 | CLAYCTR3 115.00 | [5 empty] | 21SP | [8 empty] | 0.93995 | 0.9135 | 0.95607 | 0.93 | 1.05 | CATEGORYB | SINGLE | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 0 | 532852 | JEC 6 230.00 | 532861 | EMANHAT6 230.00 | 0 |  | 1 |  |  |  | WERE | CHAPMAN JUNCTION 115KV Capacitor | Install 14.4 MVAR capacitor at Chapman Junction 115 kV | [12 empty] | 850000 | 2011-01-01 | [38 empty] | 2012-10-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61V8495021SP |  | CLAY CENTER JUNCTION 115KV | PL | WERE |  | NCENTRAL |  |  | 533323 | CLAYCTR3 115.00 | [5 empty] | 21SP | [8 empty] | 0.94521 | 0.91749 | 0.95607 | 0.93 | 1.05 | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 |  |  |  | WERE | CHAPMAN JUNCTION 115KV Capacitor | Install 14.4 MVAR capacitor at Chapman Junction 115 kV | [12 empty] | 850000 | 2011-01-01 | [38 empty] | 2012-10-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61V9575021SP |  | CLAY CENTER JUNCTION 115KV | PL | WERE |  | NCENTRAL |  |  | 533323 | CLAYCTR3 115.00 | [5 empty] | 21SP | [8 empty] | 0.95579 | 0.92246 | 0.95607 | 0.93 | 1.05 | CATEGORYB | NONSINGLE | WR-DOUBLE16 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | CHAPMAN JUNCTION 115KV Capacitor | Install 14.4 MVAR capacitor at Chapman Junction 115 kV | [12 empty] | 850000 | 2011-01-01 | 41061 | [37 empty] | 2012-10-01 | 2012-10-01
2009-AGP2 | AFS6 | [7 empty] | 2009AGP2AFS4MANUAL212WP |  | CLAY CENTER SWITCHING STATION 115KV | PL | WERE |  | NCENTRAL |  | 0 | 533362 | CHAPMAN3 115.00 | 533323 | CLAYCTR3 115.00 |  |  | 1 | 12WP | [13 empty] | CATEGORYB | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | CLAY CENTER SWITCHING STATION 115KV | Build new four terminal ring bus with 2000 amp equipment | [12 empty] | 4877550 | 2011-01-01 | [38 empty] | 2012-10-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T10245511SP | TO->FROM | CLEO CORNER - GLASS MOUNTAIN 138KV CKT 1 | PL | OKGE | OKGE | ENID | ENID | 0 | 514788 | GLASMTN4 138.00 | 514778 | CLEOCOR4 138.00 | 0 |  | 1 | 11SP | 133 | 153 | 0 |  | 68.5253 | 101.5022 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  | 156 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T10245511SP | TO->FROM | CLEO CORNER - GLASS MOUNTAIN 138KV CKT 1 | PL | OKGE | OKGE | ENID | ENID | 0 | 514788 | GLASMTN4 138.00 | 514778 | CLEOCOR4 138.00 | 0 |  | 1 | 11SP | 133 | 153 | 0 |  | 68.5253 | 101.5022 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  | 156 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1865511SP | TO->FROM | CLEO CORNER - GLASS MOUNTAIN 138KV CKT 1 | PL | OKGE | OKGE | ENID | ENID | 0 | 514788 | GLASMTN4 138.00 | 514778 | CLEOCOR4 138.00 | 0 |  | 1 | 11SP | 133 | 153 | 0 |  | 68.509 | 101.497 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WWRDEHV7 345.00 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 156 |  |  | Priority Projects | [15 empty] | 41061 | [37 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1865511SP | TO->FROM | CLEO CORNER - GLASS MOUNTAIN 138KV CKT 1 | PL | OKGE | OKGE | ENID | ENID | 0 | 514788 | GLASMTN4 138.00 | 514778 | CLEOCOR4 138.00 | 0 |  | 1 | 11SP | 133 | 153 | 0 |  | 68.509 | 101.497 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WWRDEHV7 345.00 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 156 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1755511SP | TO->FROM | CLEO CORNER - GLASS MOUNTAIN 138KV CKT 1 | PL | OKGE | OKGE | ENID | ENID | 0 | 514788 | GLASMTN4 138.00 | 514778 | CLEOCOR4 138.00 | 0 |  | 1 | 11SP | 133 | 153 | 0 |  | 68.3583 | 101.1302 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 155 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1755511SP | TO->FROM | CLEO CORNER - GLASS MOUNTAIN 138KV CKT 1 | PL | OKGE | OKGE | ENID | ENID | 0 | 514788 | GLASMTN4 138.00 | 514778 | CLEOCOR4 138.00 | 0 |  | 1 | 11SP | 133 | 153 | 0 |  | 68.3583 | 101.1302 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 155 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2007-AG3 | AFS7 | [7 empty] | 2007AG3AFS71T2833413SP |  | CLIFTON - GREENLEAF 115KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539656 | CLIFTON3 115.00 | 539665 | GRNLEAF3 115.00 | 0 |  | 1 | 13SP | 83.9 | 89.6 |  | 53.4776 | 105.4507 | [9 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | CLIFTON - GREENLEAF 115KV CKT 1 | Rebuild 14.4 miles | 240 | 240 | 240 | 240 | 14.4 | 24 | 24 |  | 0.00922 | 0.072 | 0.0121 | 250k per mile | 3600000 | 2008-01-01 | [38 empty] | 2011-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T10535511SP | FROM->TO | COLBY2 (COLBY T3) 69/34.5/13.8KV TRANSFORMER CKT 3 | REL | MIDW | MIDW | REG E-IL | REG E-IL | 1 | 530644 | COLBY 2 69.000 | 530646 | CLBY34 1 34.500 | 530649 | CLBYT3 1 13.800 | 3 | 11SP | 13.33 | 13.33 | 0 | 143.1 | 143.1474 | 143.1469 | [7 empty] | CATEGORYB | SINGLE | COLBY (COLBY T2) 115/34.5/12.47KV TRANSFORMER CKT 2 | 1 | 530555 | COLBY 3 115.00 | 530646 | CLBY34 1 34.500 | 530647 | CLBYT2 1 12.470 | 2 |  | 20 |  | MIDW | COLBY 2 69.000 (COLBY T3) 69/34.5/13.8KV TRANSFORMER CKT 3 | Replace the Colby 69/34.5 kV transformer with a larger unit | [52 empty] | 2011-06-01 | 2013-01-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T6615011WP | FROM->TO | COLBY2 (COLBY T3) 69/34.5/13.8KV TRANSFORMER CKT 3 | REL | MIDW | MIDW | REG E-IL | REG E-IL | 1 | 530644 | COLBY 2 69.000 | 530646 | CLBY34 1 34.500 | 530649 | CLBYT3 1 13.800 | 3 | 11WP | 13.33 | 13.33 | 0 | 110.4 | 110.3897 | 110.401 | [7 empty] | CATEGORYB | SINGLE | COLBY (COLBY T2) 115/34.5/12.47KV TRANSFORMER CKT 2 | 1 | 530555 | COLBY 3 115.00 | 530646 | CLBY34 1 34.500 | 530647 | CLBYT2 1 12.470 | 2 |  | 15 |  | MIDW | COLBY 2 69.000 (COLBY T3) 69/34.5/13.8KV TRANSFORMER CKT 3 | Replace the Colby 69/34.5 kV transformer with a larger unit | [52 empty] | 2011-06-01 | 2013-01-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T9065012SP | FROM->TO | COLBY2 (COLBY T3) 69/34.5/13.8KV TRANSFORMER CKT 3 | REL | MIDW | MIDW | REG E-IL | REG E-IL | 1 | 530644 | COLBY 2 69.000 | 530646 | CLBY34 1 34.500 | 530649 | CLBYT3 1 13.800 | 3 | 12SP | 13.33 | 13.33 | 0 | 143.9 | 143.9354 | 144.0959 | [7 empty] | CATEGORYB | SINGLE | COLBY (COLBY T2) 115/34.5/12.47KV TRANSFORMER CKT 2 | 1 | 530555 | COLBY 3 115.00 | 530646 | CLBY34 1 34.500 | 530647 | CLBYT2 1 12.470 | 2 |  | 20 |  | MIDW | COLBY 2 69.000 (COLBY T3) 69/34.5/13.8KV TRANSFORMER CKT 3 | Replace the Colby 69/34.5 kV transformer with a larger unit | [52 empty] | 2011-06-01 | 2013-01-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T4785512WP | FROM->TO | COLBY2 (COLBY T3) 69/34.5/13.8KV TRANSFORMER CKT 3 | REL | MIDW | MIDW | REG E-IL | REG E-IL | 1 | 530644 | COLBY 2 69.000 | 530646 | CLBY34 1 34.500 | 530649 | CLBYT3 1 13.800 | 3 | 12WP | 13.33 | 13.33 | 0 | 111.1 | 111.0719 | 111.0466 | [7 empty] | CATEGORYB | SINGLE | COLBY (COLBY T2) 115/34.5/12.47KV TRANSFORMER CKT 2 | 1 | 530555 | COLBY 3 115.00 | 530646 | CLBY34 1 34.500 | 530647 | CLBYT2 1 12.470 | 2 |  | 15 |  | MIDW | COLBY 2 69.000 (COLBY T3) 69/34.5/13.8KV TRANSFORMER CKT 3 | Replace the Colby 69/34.5 kV transformer with a larger unit | [52 empty] | 2011-06-01 | 2013-01-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T10475016SP | FROM->TO | COLBY2 (COLBY T3) 69/34.5/13.8KV TRANSFORMER CKT 3 | REL | MIDW | MIDW | REG E-IL | REG E-IL | 1 | 530644 | COLBY 2 69.000 | 530646 | CLBY34 1 34.500 | 530649 | CLBYT3 1 13.800 | 3 | 16SP | 13.33 | 13.33 | 0 | 146.2 | 146.212 | 146.2361 | [7 empty] | CATEGORYB | SINGLE | COLBY (COLBY T2) 115/34.5/12.47KV TRANSFORMER CKT 2 | 1 | 530555 | COLBY 3 115.00 | 530646 | CLBY34 1 34.500 | 530647 | CLBYT2 1 12.470 | 2 |  | 20 |  | MIDW | COLBY 2 69.000 (COLBY T3) 69/34.5/13.8KV TRANSFORMER CKT 3 | Replace the Colby 69/34.5 kV transformer with a larger unit | [52 empty] | 2011-06-01 | 2013-01-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T6125016WP | FROM->TO | COLBY2 (COLBY T3) 69/34.5/13.8KV TRANSFORMER CKT 3 | REL | MIDW | MIDW | REG E-IL | REG E-IL | 1 | 530644 | COLBY 2 69.000 | 530646 | CLBY34 1 34.500 | 530649 | CLBYT3 1 13.800 | 3 | 16WP | 13.33 | 13.33 | 0 | 112.6 | 112.5508 | 112.5569 | [7 empty] | CATEGORYB | SINGLE | COLBY (COLBY T2) 115/34.5/12.47KV TRANSFORMER CKT 2 | 1 | 530555 | COLBY 3 115.00 | 530646 | CLBY34 1 34.500 | 530647 | CLBYT2 1 12.470 | 2 |  | 16 |  | MIDW | COLBY 2 69.000 (COLBY T3) 69/34.5/13.8KV TRANSFORMER CKT 3 | Replace the Colby 69/34.5 kV transformer with a larger unit | [52 empty] | 2011-06-01 | 2013-01-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T20105021SP | FROM->TO | COLBY2 (COLBY T3) 69/34.5/13.8KV TRANSFORMER CKT 3 | REL | MIDW | MIDW | REG E-IL | REG E-IL | 1 | 530644 | COLBY 2 69.000 | 530646 | CLBY34 1 34.500 | 530649 | CLBYT3 1 13.800 | 3 | 21SP | 13.33 | 13.33 | 0 | 147.4 | 147.4451 | 147.1919 | [7 empty] | CATEGORYB | SINGLE | COLBY (COLBY T2) 115/34.5/12.47KV TRANSFORMER CKT 2 | 1 | 530555 | COLBY 3 115.00 | 530646 | CLBY34 1 34.500 | 530647 | CLBYT2 1 12.470 | 2 |  | 20 |  | MIDW | COLBY 2 69.000 (COLBY T3) 69/34.5/13.8KV TRANSFORMER CKT 3 | Replace the Colby 69/34.5 kV transformer with a larger unit | [52 empty] | 2011-06-01 | 2013-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T3625511SP | FROM->TO | CRESWELL - OAK 69KV CKT 1 | S | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 | 11SP | 90 | 90 | 0 |  | 84.2601 | 110.3904 | [7 empty] | CATEGORYB | SINGLE | CRESWELL - PARIS 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533548 | PARIS 2 69.000 | 0 |  | 1 |  | 100 |  | WERE | CRESWELL - OAK 69KV CKT 1 | Replace jumpers and bus, and reset CTs and relaying. Rebuild substations. | 107 | 107 | 107 | 107 | 0 | 6 | 2 | N |  |  |  | Conductor limit is 107 MVA. | 1500000 | 2010-01-01 | [38 empty] | 2011-06-01 | 2013-06-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T3755512SP | FROM->TO | CRESWELL - OAK 69KV CKT 1 | S | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 | 12SP | 90 | 90 | 0 |  | 84.0071 | 109.1765 | [7 empty] | CATEGORYB | SINGLE | CRESWELL - PARIS 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533548 | PARIS 2 69.000 | 0 |  | 1 |  | 99 |  | WERE | CRESWELL - OAK 69KV CKT 1 | Replace jumpers and bus, and reset CTs and relaying. Rebuild substations. | 107 | 107 | 107 | 107 | 0 | 6 | 2 | N |  |  |  | Conductor limit is 107 MVA. | 1500000 | 2010-01-01 | [38 empty] | 2011-06-01 | 2013-06-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2545016SP | FROM->TO | CRESWELL - OAK 69KV CKT 1 | S | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 | 16SP | 90 | 90 | 0 |  | 90.5381 | 108.2075 | [7 empty] | CATEGORYB | SINGLE | CRESWELL - PARIS 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533548 | PARIS 2 69.000 | 0 |  | 1 |  | 98 |  | WERE | CRESWELL - OAK 69KV CKT 1 | Replace jumpers and bus, and reset CTs and relaying. Rebuild substations. | 107 | 107 | 107 | 107 | 0 | 6 | 2 | N |  |  |  | Conductor limit is 107 MVA. | 1500000 | 2010-01-01 | [38 empty] | 2011-06-01 | 2013-06-01 | 2012-10-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T5525021SP | FROM->TO | CRESWELL - OAK 69KV CKT 1 | S | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 | 21SP | 90 | 90 | 0 | 99.4 | 99.3836 | 106.1486 | [7 empty] | CATEGORYB | SINGLE | CRESWELL - PARIS 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533548 | PARIS 2 69.000 | 0 |  | 1 |  | 96 |  | WERE | CRESWELL - OAK 69KV CKT 1 | Replace jumpers and bus, and reset CTs and relaying. Rebuild substations. | 107 | 107 | 107 | 107 | 0 | 6 | 2 | N |  |  |  | Conductor limit is 107 MVA. | 1500000 | 2010-01-01 | [38 empty] | 2011-06-01 | 2013-06-01 | 2012-10-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T11345512SP | FROM->TO | DEAF SMITH COUNTY INTERCHANGE (GE M101353) 230/115/13.2KV TRANSFORMER CKT 1 | EXP | SPS | SPS | SPS-CLHF | SPS-CLHF | 1 | 524623 | DEAFSMITH 6230.00 | 524622 | DEAFSMITH 3115.00 | 524620 | DEFSMTH_TR1113.200 | 1 | 12SP | 149 | 171 | 0 | 99.8 | 99.8196 | 102.3953 | [7 empty] | CATEGORYB | SINGLE | DEAF SMITH COUNTY INTERCHANGE (ELCO 13458-1) 230/115/13.8KV TRANSFORMER CKT 2 | 1 | 524622 | DEAFSMITH 3115.00 | 524623 | DEAFSMITH 6230.00 | 524621 | DEFSMTH_TR2113.800 | 2 |  | 176 |  | SPS | DEAF SMITH COUNTY INTERCHANGE (GE M101353) 230/115/13.2KV TRANSFORMER CKT 1 | Upgrade transformer--230/115 Kv |  | 252 | [50 empty] | 2012-06-01 | 2013-06-01 | 2012-10-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T45521SP | FROM->TO | DIANA - PERDUE 138KV CKT 1 | REL | AEPW | AEPW | NWLANTEC | MTPLNTEC | 0 | 508831 | DIANA 4 138.00 | 508351 | PERDUE 4 138.00 | 0 |  | 1 | 21SP | 246 | 287 | 0 | 99.6 | 99.6273 | 106.0283 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  | 305 |  | AEPW | DIANA - PERDUE 138KV CKT 1 | Rebuild 21.85 miles of 2-397 ACSR with 1590 ACSR. Replace Breakers 9310 & 10080, wavetrap, & five switches @ Perdue. Replace switch 12798 and wavetrap @ Diana. | 368 | 478 | 434 | 478 |  | 30 | 12 |  | 0.00757 | 0.080814 | 0.02522 | Limit will be 2-397.5 ACSR for the summer and wavetraps at both ends for the winter. | 23000000 | 2009-12-09 | [38 empty] | 2020-06-01 | 2020-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T10635516SP | FROM->TO | DIANA (DIANA 3) 345/138/13.8KV TRANSFORMER CKT 3 | S | AEPW | AEPW | NWLA-ETX | NWLANTEC | 2 | 508832 | DIANA 7 345.00 | 508831 | DIANA 4 138.00 | 508845 | DIANA-N1 13.800 | 3 | 16SP | 309 | 330 | 0 | 99.4 | 99.3929 | 102.5323 | [7 empty] | CATEGORYB | SINGLE | DIANA (DIANA 2) 345/138/13.8KV TRANSFORMER CKT 2 | 1 | 508831 | DIANA 4 138.00 | 508832 | DIANA 7 345.00 | 508843 | DIANA-M1 13.800 | 2 |  | 339 |  | AEPW | DIANA (DIANA 3) 345/138/13.8KV TRANSFORMER CKT 3 | Replace auto with new 450 MVA. | 450 | 495 | 450 | 495 |  | 20 | 6 |  |  |  |  | New limit will be auto. | 5500000 | 2009-07-16 | [38 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61V5785516SP |  | DOVER SW 69KV | REL | WFEC |  | AEP-IM |  |  | 520881 | DOVERSW2 69.000 | [5 empty] | 16SP | [8 empty] | 0.9119 | 0.88402 | 0.98354 | 0.9 | 1.05 | CATEGORYB | SINGLE | DOVER SW (DOVER) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 520882 | DOVERSW4 138.00 | 520881 | DOVERSW2 69.000 | 521166 | DVRTERT 13.800 | 1 |  |  |  | WFEC | East Kingfisher Capacitor 69 kV | Install 18 Mvar capacitor at East Kingfisher bus. | [52 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61V5765516SP |  | DOVER TAP 69KV | REL | OKGE |  | ENID |  |  | 514772 | DOVERTP2 69.000 | [5 empty] | 16SP | [8 empty] | 0.91328 | 0.8852 | 0.98251 | 0.9 | 1.05 | CATEGORYB | SINGLE | DOVER SW (DOVER) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 520882 | DOVERSW4 138.00 | 520881 | DOVERSW2 69.000 | 521166 | DVRTERT 13.800 | 1 |  |  |  | WFEC | East Kingfisher Capacitor 69 kV | Install 18 Mvar capacitor at East Kingfisher bus. | [52 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61V5765516SP |  | DOVER TAP 69KV | REL | OKGE |  | ENID |  |  | 514772 | DOVERTP2 69.000 | [5 empty] | 16SP | [8 empty] | 0.91328 | 0.8852 | 0.98251 | 0.9 | 1.05 | CATEGORYB | SINGLE | DOVER SW (DOVER) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 520882 | DOVERSW4 138.00 | 520881 | DOVERSW2 69.000 | 521166 | DVRTERT 13.800 | 1 |  |  |  | WFEC | East Kingfisher Capacitor 69 kV | Install 18 Mvar capacitor at East Kingfisher bus. | [52 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61V4185521SP |  | EAGLE CHIEF 69KV | REL | WFEC |  | AEP-IM |  |  | 520890 | EAGLCHF2 69.000 | [5 empty] | 21SP | [7 empty] | 0.88644 | 0.88644 | 0.822 | 0.95581 | 0.9 | 1.05 | CATEGORYB | SINGLE | FAIRVIEW - OKEENE 69KV CKT 1 | 0 | 521015 | OKEENE 2 69.000 | 520909 | FAIRVEW2 69.000 | 0 |  | 1 |  |  |  | WFEC | FAIRVIEW Capacitor 69KV | Install 18 Mvar capacitor at Fairview 69kV bus. | [52 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61V5795516SP |  | EAST KINGFISHER 69KV | REL | WFEC |  | AEP-IM |  |  | 520891 | EKNGFSH2 69.000 | [5 empty] | 16SP | [8 empty] | 0.90377 | 0.8777 | 0.96701 | 0.9 | 1.05 | CATEGORYB | SINGLE | DOVER SW (DOVER) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 520882 | DOVERSW4 138.00 | 520881 | DOVERSW2 69.000 | 521166 | DVRTERT 13.800 | 1 |  |  |  | WFEC | East Kingfisher Capacitor 69 kV | Install 18 Mvar capacitor at East Kingfisher bus. | [52 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 | CONT-0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2305012SP | TO->FROM | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | EXP | WERE | WERE | NEAST | NCENTRAL | 0 | 532852 | JEC 6 230.00 | 532861 | EMANHAT6 230.00 | 0 |  | 1 | 12SP | 446 | 446 | 0 | 101 | 101.0305 | 102.192 | [7 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  | 456 |  | WERE | Line - E. Manhattan - JEC 230 kV | Uprate JEC- E. Manhattan 230 kV line to 100 deg C operation by raising structures. | 446 | 490 |  |  |  | 12 |  | N | 0.00414 | 0.03894 | 0.08101 | [41 empty] | 2012-06-01 | 2012-12-01 | 2012-10-01
2009-AGP2 | AFS6 | CONT-0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2305012SP | TO->FROM | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | EXP | WERE | WERE | NEAST | NCENTRAL | 0 | 532852 | JEC 6 230.00 | 532861 | EMANHAT6 230.00 | 0 |  | 1 | 12SP | 446 | 446 | 0 | 101 | 101.0305 | 102.192 | [7 empty] | CATEGORYB | SINGLE | HOYT - JEFFERY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  | 456 |  | WERE | Line - E. Manhattan - JEC 230 kV | Uprate JEC- E. Manhattan 230 kV line to 100 deg C operation by raising structures. | 446 | 490 |  |  |  | 12 |  | N | 0.00414 | 0.03894 | 0.08101 | [41 empty] | 2012-06-01 | 2012-12-01 | 2012-10-01
2009-AGP2 | AFS6 | CONT-0402 - JEC - Summit 345kV | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2405012SP | TO->FROM | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | EXP | WERE | WERE | NEAST | NCENTRAL | 0 | 532852 | JEC 6 230.00 | 532861 | EMANHAT6 230.00 | 0 |  | 1 | 12SP | 446 | 446 | 0 | 99.5 | 99.5042 | 100.7762 | [7 empty] | CATEGORYB | SINGLE | JEFFERY ENERGY CENTER - SUMMIT 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532773 | SUMMIT 7 345.00 | 0 |  | 1 |  | 450 | TOD 400 | WERE | Line - E. Manhattan - JEC 230 kV | Uprate JEC- E. Manhattan 230 kV line to 100 deg C operation by raising structures. | 446 | 490 |  |  |  | 12 |  | N | 0.00414 | 0.03894 | 0.08101 | [41 empty] | 2012-06-01 | 2012-12-01 | 2012-10-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2365012SP | TO->FROM | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | EXP | WERE | WERE | NEAST | NCENTRAL | 0 | 532852 | JEC 6 230.00 | 532861 | EMANHAT6 230.00 | 0 |  | 1 | 12SP | 446 | 446 | 0 | 99.7 | 99.7334 | 100.5049 | [7 empty] | CATEGORYB | SINGLE | JEFFERY ENERGY CENTER - MORRIS COUNTY 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532770 | MORRIS 7 345.00 | 0 |  | 1 |  | 449 | TOD 400 | WERE | Line - E. Manhattan - JEC 230 kV | Uprate JEC- E. Manhattan 230 kV line to 100 deg C operation by raising structures. | 446 | 490 |  |  |  | 12 |  | N | 0.00414 | 0.03894 | 0.08101 | [41 empty] | 2012-06-01 | 2012-12-01 | 2012-10-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T2965511SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | EXP | WERE | WERE | NCENTRAL | NCENTRAL | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 11SP | 280 | 308 | 350 | 101.3 | 101.2771 | 101.6646 | [7 empty] | CATEGORYB | SINGLE | JEFFERY ENERGY CENTER - MORRIS COUNTY 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532770 | MORRIS 7 345.00 | 0 |  | 1 |  | 314 | Build SW Manhattan 230-115 kV substation; Convert SW Manhattan-McDowell Creek line to 230 kV operation; Convert McDowell-E Manhattan line to 230 kV operation; Build new SW Manhattan-E Manhattan 115 kV ilne | WERE | EAST MANHATTAN - NW MANHATTAN 230/115KV | Tap the Concordia - East Manhattan 230kV line and add a new substation"NW Manhattan"; Add a 230kV/115kV transformer and tap the KSU - Wildcat 115kV line into NW Manhattan | 358 | 358 | 358 | 358 |  | 12 |  | No | 0.00346 | 0.02317 | 0.04637 |  |  | 2008-07-30 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T3725521SP | FROM->TO | EAST PLANT INTERCHANGE - MANHATTAN SUB 115KV CKT 1 | REL | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524162 | EAST_PLANT 3115.00 | 524224 | MANHATTAN 3115.00 | 0 |  | 1 | 21SP | 160 | 160 | 0 | 111.5 | 111.4855 | 112.8404 | [7 empty] | CATEGORYB | SINGLE | EAST PLANT INTERCHANGE - PIERCE STREET TAP 115KV CKT 1 | 0 | 524162 | EAST_PLANT 3115.00 | 524185 | PIERCE_TP 3115.00 | 0 |  | 1 |  | 181 |  | SPS | OSAGE - RANDALL 115KV CKT 1 | Osage station & line reterminations with a new 2 mile 115 kV line from Randall Co | [52 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T25945521SP | FROM->TO | EAST PLANT INTERCHANGE - MANHATTAN SUB 115KV CKT 1 | REL | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524162 | EAST_PLANT 3115.00 | 524224 | MANHATTAN 3115.00 | 0 |  | 1 | 21SP | 160 | 160 | 0 | 106.9 | 106.9268 | 108.285 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-V43 | 0 | 0 |  | 0 |  | 0 |  |  |  | 174 |  | SPS | OSAGE - RANDALL 115KV CKT 1 | Osage station & line reterminations with a new 2 mile 115 kV line from Randall Co | [52 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T3765521SP | FROM->TO | EAST PLANT INTERCHANGE - MANHATTAN SUB 115KV CKT 1 | REL | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524162 | EAST_PLANT 3115.00 | 524224 | MANHATTAN 3115.00 | 0 |  | 1 | 21SP | 160 | 160 | 0 | 100.7 | 100.678 | 102.0221 | [7 empty] | CATEGORYB | SINGLE | OSAGE SWITCHING STATION - PIERCE STREET TAP 115KV CKT 1 | 0 | 524185 | PIERCE_TP 3115.00 | 524345 | OSAGE 3115.00 | 0 |  | 1 |  | 164 |  | SPS | OSAGE - RANDALL 115KV CKT 1 | Osage station & line reterminations with a new 2 mile 115 kV line from Randall Co | [52 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T3745521SP | FROM->TO | EAST PLANT INTERCHANGE - PIERCE STREET TAP 115KV CKT 1 | REL | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524162 | EAST_PLANT 3115.00 | 524185 | PIERCE_TP 3115.00 | 0 |  | 1 | 21SP | 160 | 160 | 0 | 113 | 112.98 | 114.3264 | [7 empty] | CATEGORYB | SINGLE | EAST PLANT INTERCHANGE - MANHATTAN SUB 115KV CKT 1 | 0 | 524162 | EAST_PLANT 3115.00 | 524224 | MANHATTAN 3115.00 | 0 |  | 1 |  | 183 |  | SPS | OSAGE - RANDALL 115KV CKT 1 | Osage station & line reterminations with a new 2 mile 115 kV line from Randall Co | [52 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T25905521SP | FROM->TO | EAST PLANT INTERCHANGE - PIERCE STREET TAP 115KV CKT 1 | REL | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524162 | EAST_PLANT 3115.00 | 524185 | PIERCE_TP 3115.00 | 0 |  | 1 | 21SP | 160 | 160 | 0 | 110 | 110.0208 | 111.3537 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-V04 | 0 | 0 |  | 0 |  | 0 |  |  |  | 179 |  | SPS | OSAGE - RANDALL 115KV CKT 1 | Osage station & line reterminations with a new 2 mile 115 kV line from Randall Co | [52 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T25825521SP | FROM->TO | EAST PLANT INTERCHANGE - PIERCE STREET TAP 115KV CKT 1 | REL | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524162 | EAST_PLANT 3115.00 | 524185 | PIERCE_TP 3115.00 | 0 |  | 1 | 21SP | 160 | 160 | 0 | 103.3 | 103.2505 | 104.405 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-K19 | 0 | 0 |  | 0 |  | 0 |  |  |  | 168 |  | SPS | OSAGE - RANDALL 115KV CKT 1 | Osage station & line reterminations with a new 2 mile 115 kV line from Randall Co | [52 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T965512SP | FROM->TO | EASTON REC - KNOX LEE 138KV CKT 1 | REL | AEPW | AEPW | RKHLNTEC | LONG-MAR | 0 | 509092 | EASTON 4 138.00 | 508548 | KNOXLEE4 138.00 | 0 |  | 1 | 12SP | 455 | 478 | 0 | 101.7 | 101.6524 | 101.7378 | [7 empty] | CATEGORYB | SINGLE | PIRKEY - WHITNEY 138KV CKT 1 | 0 | 508562 | PIRKEY 4 138.00 | 508575 | WHITNEY4 138.00 | 0 |  | 1 |  | 487 |  | AEPW | EASTON REC - KNOX LEE 138KV CKT 1 | Replace 3 2000 A switches at Knox Lee | 455 | 526 | 478 | 526 |  | 12 | 3 | [5 empty] | 200000 | 2009-11-04 | [38 empty] | 2012-06-01 | 2012-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1315516SP | FROM->TO | EASTON REC - KNOX LEE 138KV CKT 1 | REL | AEPW | AEPW | RKHLNTEC | LONG-MAR | 0 | 509092 | EASTON 4 138.00 | 508548 | KNOXLEE4 138.00 | 0 |  | 1 | 16SP | 455 | 478 | 0 | 112 | 111.9677 | 112.8376 | [7 empty] | CATEGORYB | SINGLE | PIRKEY - WHITNEY 138KV CKT 1 | 0 | 508562 | PIRKEY 4 138.00 | 508575 | WHITNEY4 138.00 | 0 |  | 1 |  | 540 |  | AEPW | EASTON REC - KNOX LEE 138KV CKT 1 | Replace 3 2000 A switches at Knox Lee | 455 | 526 | 478 | 526 |  | 12 | 3 | [5 empty] | 200000 | 2009-11-04 | [38 empty] | 2012-06-01 | 2012-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T925516WP | FROM->TO | EASTON REC - KNOX LEE 138KV CKT 1 | REL | AEPW | AEPW | RKHLNTEC | LONG-MAR | 0 | 509092 | EASTON 4 138.00 | 508548 | KNOXLEE4 138.00 | 0 |  | 1 | 16WP | 478 | 478 | 0 | 101 | 101.0473 | 101.0056 | [7 empty] | CATEGORYB | SINGLE | PIRKEY - WHITNEY 138KV CKT 1 | 0 | 508562 | PIRKEY 4 138.00 | 508575 | WHITNEY4 138.00 | 0 |  | 1 |  | 483 |  | AEPW | EASTON REC - KNOX LEE 138KV CKT 1 | Replace 3 2000 A switches at Knox Lee | 455 | 526 | 478 | 526 |  | 12 | 3 | [5 empty] | 200000 | 2009-11-04 | [38 empty] | 2012-06-01 | 2012-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T975512SP | TO->FROM | EASTON REC - PIRKEY 138KV CKT 1 | REL | AEPW | AEPW | LONG-MAR | RKHLNTEC | 0 | 508562 | PIRKEY 4 138.00 | 509092 | EASTON 4 138.00 | 0 |  | 1 | 12SP | 460 | 478 | 0 | 103.1 | 103.1282 | 103.2135 | [7 empty] | CATEGORYB | SINGLE | PIRKEY - WHITNEY 138KV CKT 1 | 0 | 508562 | PIRKEY 4 138.00 | 508575 | WHITNEY4 138.00 | 0 |  | 1 |  | 494 |  | AEPW | EASTON REC - PIRKEY 138KV CKT 1 | Replace Switch at Easton, and Breaker and Switch at Pirkey | 461 | 526 | 478 | 526 |  | 12 | 2 |  |  |  |  | New limits will be line conductor summer normal and wave trap at Pirkey all other | 500000 | 2009-11-30 | [38 empty] | 2012-06-01 | 2012-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1325516SP | TO->FROM | EASTON REC - PIRKEY 138KV CKT 1 | REL | AEPW | AEPW | LONG-MAR | RKHLNTEC | 0 | 508562 | PIRKEY 4 138.00 | 509092 | EASTON 4 138.00 | 0 |  | 1 | 16SP | 460 | 478 | 0 | 113.5 | 113.4877 | 114.3576 | [7 empty] | CATEGORYB | SINGLE | PIRKEY - WHITNEY 138KV CKT 1 | 0 | 508562 | PIRKEY 4 138.00 | 508575 | WHITNEY4 138.00 | 0 |  | 1 |  | 547 |  | AEPW | EASTON REC - PIRKEY 138KV CKT 1 | Replace Switch at Easton, and Breaker and Switch at Pirkey | 461 | 526 | 478 | 526 |  | 12 | 2 |  |  |  |  | New limits will be line conductor summer normal and wave trap at Pirkey all other | 500000 | 2009-11-30 | [38 empty] | 2012-06-01 | 2012-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T935516WP | TO->FROM | EASTON REC - PIRKEY 138KV CKT 1 | REL | AEPW | AEPW | LONG-MAR | RKHLNTEC | 0 | 508562 | PIRKEY 4 138.00 | 509092 | EASTON 4 138.00 | 0 |  | 1 | 16WP | 478 | 478 | 0 | 102.5 | 102.5324 | 102.4906 | [7 empty] | CATEGORYB | SINGLE | PIRKEY - WHITNEY 138KV CKT 1 | 0 | 508562 | PIRKEY 4 138.00 | 508575 | WHITNEY4 138.00 | 0 |  | 1 |  | 490 |  | AEPW | EASTON REC - PIRKEY 138KV CKT 1 | Replace Switch at Easton, and Breaker and Switch at Pirkey | 461 | 526 | 478 | 526 |  | 12 | 2 |  |  |  |  | New limits will be line conductor summer normal and wave trap at Pirkey all other | 500000 | 2009-11-30 | [38 empty] | 2012-06-01 | 2012-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T12715012SP | FROM->TO | EL PASO - FARBER 138KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 | 12SP | 160 | 168 | 0 |  | 82.1883 | 100.61 | [7 empty] | CATEGORYB | NONSINGLE | OGE3TERM7 | 0 | 0 |  | 0 |  | 0 |  |  |  | 170 |  | WERE | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | Tear down / Rebuild 11.63-mile Timber Tap-Winfield 69 kV line, 954 ACSR | 72 | 72 | 72 | 72 | 11.63 | 18 | 6 |  | 0.0309 | 0.2101 | 0.05164 | Line switches limit to 72 MVA. $790k per mile | 8161986 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T12715012SP | FROM->TO | EL PASO - FARBER 138KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 | 12SP | 160 | 168 | 0 |  | 82.1883 | 100.61 | [7 empty] | CATEGORYB | NONSINGLE | OGE3TERM7 | 0 | 0 |  | 0 |  | 0 |  |  |  | 170 |  | WERE | RICHLAND - UDALL 69KV CKT 1 | Tear down / Rebuild 8.48-mile Richland-Udall 69 kV line using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 8.48 | 13 | 7 | N | 0.01789 | 0.12177 | 0.02589 | MVA limit is conductor $790k per mile | 6699200 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T12715012SP | FROM->TO | EL PASO - FARBER 138KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 | 12SP | 160 | 168 | 0 |  | 82.1883 | 100.61 | [7 empty] | CATEGORYB | NONSINGLE | OGE3TERM7 | 0 | 0 |  | 0 |  | 0 |  |  |  | 170 |  | WERE | TIMBER JUNCTION - UDALL 69KV CKT 1 | Tear down / Rebuild Udall-Timber Jct 69 kV using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 2.01 | 4 | 2 | N | 0.00424 | 0.02886 | 0.00614 | MVA limit is conductor $790k per mile | 1587900 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T12715012SP | FROM->TO | EL PASO - FARBER 138KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 | 12SP | 160 | 168 | 0 |  | 82.1883 | 100.61 | [7 empty] | CATEGORYB | NONSINGLE | OGE3TERM7 | 0 | 0 |  | 0 |  | 0 |  |  |  | 170 |  | WERE | BELL - PECK 69KV CKT 1 | Tear down / Rebuild 8.23 mile Bell-Peck 69 kV line with 1192 ACSR and replace CT | 134 | 147 | 134 | 147 | 8.23 | 18 | 5 | N |  |  |  | $790k per mile and $200k for CT | 6701700 | 2010-01-01 | [38 empty] | 2012-06-01 | 2012-12-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T1235012SP | FROM->TO | EL PASO - FARBER 138KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 | 12SP | 160 | 168 | 0 |  | 82.1861 | 100.6078 | [7 empty] | CATEGORYB | SINGLE | KILDARE4 - NEWKIRK4 138KV CKT 1 | 0 | 514759 | NEWKIRK4 138.00 | 514760 | KILDARE4 138.00 | 0 |  | 1 |  | 170 |  | WERE | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | Tear down / Rebuild 11.63-mile Timber Tap-Winfield 69 kV line, 954 ACSR | 72 | 72 | 72 | 72 | 11.63 | 18 | 6 |  | 0.0309 | 0.2101 | 0.05164 | Line switches limit to 72 MVA. $790k per mile | 8161986 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T1235012SP | FROM->TO | EL PASO - FARBER 138KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 | 12SP | 160 | 168 | 0 |  | 82.1861 | 100.6078 | [7 empty] | CATEGORYB | SINGLE | KILDARE4 - NEWKIRK4 138KV CKT 1 | 0 | 514759 | NEWKIRK4 138.00 | 514760 | KILDARE4 138.00 | 0 |  | 1 |  | 170 |  | WERE | RICHLAND - UDALL 69KV CKT 1 | Tear down / Rebuild 8.48-mile Richland-Udall 69 kV line using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 8.48 | 13 | 7 | N | 0.01789 | 0.12177 | 0.02589 | MVA limit is conductor $790k per mile | 6699200 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T1235012SP | FROM->TO | EL PASO - FARBER 138KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 | 12SP | 160 | 168 | 0 |  | 82.1861 | 100.6078 | [7 empty] | CATEGORYB | SINGLE | KILDARE4 - NEWKIRK4 138KV CKT 1 | 0 | 514759 | NEWKIRK4 138.00 | 514760 | KILDARE4 138.00 | 0 |  | 1 |  | 170 |  | WERE | TIMBER JUNCTION - UDALL 69KV CKT 1 | Tear down / Rebuild Udall-Timber Jct 69 kV using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 2.01 | 4 | 2 | N | 0.00424 | 0.02886 | 0.00614 | MVA limit is conductor $790k per mile | 1587900 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T1235012SP | FROM->TO | EL PASO - FARBER 138KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 | 12SP | 160 | 168 | 0 |  | 82.1861 | 100.6078 | [7 empty] | CATEGORYB | SINGLE | KILDARE4 - NEWKIRK4 138KV CKT 1 | 0 | 514759 | NEWKIRK4 138.00 | 514760 | KILDARE4 138.00 | 0 |  | 1 |  | 170 |  | WERE | BELL - PECK 69KV CKT 1 | Tear down / Rebuild 8.23 mile Bell-Peck 69 kV line with 1192 ACSR and replace CT | 134 | 147 | 134 | 147 | 8.23 | 18 | 5 | N |  |  |  | $790k per mile and $200k for CT | 6701700 | 2010-01-01 | [38 empty] | 2012-06-01 | 2012-12-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T10285511SP | TO->FROM | EL RENO - ROMAN NOSE 138KV CKT 1 | PL | OKGE | OKGE |  |  | 0 | 514823 | ROMNOSE4 138.00 | 514819 | EL-RENO4 138.00 | 0 |  | 1 | 11SP | 133 | 153 | 0 |  | 50.6942 | 101.5809 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  | 156 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T10285511SP | TO->FROM | EL RENO - ROMAN NOSE 138KV CKT 1 | PL | OKGE | OKGE |  |  | 0 | 514823 | ROMNOSE4 138.00 | 514819 | EL-RENO4 138.00 | 0 |  | 1 | 11SP | 133 | 153 | 0 |  | 50.6942 | 101.5809 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  | 156 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1905511SP | TO->FROM | EL RENO - ROMAN NOSE 138KV CKT 1 | PL | OKGE | OKGE |  |  | 0 | 514823 | ROMNOSE4 138.00 | 514819 | EL-RENO4 138.00 | 0 |  | 1 | 11SP | 133 | 153 | 0 |  | 50.6299 | 101.529 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WWRDEHV7 345.00 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 156 |  |  | Priority Projects | [15 empty] | 6/1/2013 | 6/1/2013 | 41061 | 41061 | [34 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1905511SP | TO->FROM | EL RENO - ROMAN NOSE 138KV CKT 1 | PL | OKGE | OKGE |  |  | 0 | 514823 | ROMNOSE4 138.00 | 514819 | EL-RENO4 138.00 | 0 |  | 1 | 11SP | 133 | 153 | 0 |  | 50.6299 | 101.529 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WWRDEHV7 345.00 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 156 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1795511SP | TO->FROM | EL RENO - ROMAN NOSE 138KV CKT 1 | PL | OKGE | OKGE |  |  | 0 | 514823 | ROMNOSE4 138.00 | 514819 | EL-RENO4 138.00 | 0 |  | 1 | 11SP | 133 | 153 | 0 |  | 50.2733 | 100.9666 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 155 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1795511SP | TO->FROM | EL RENO - ROMAN NOSE 138KV CKT 1 | PL | OKGE | OKGE |  |  | 0 | 514823 | ROMNOSE4 138.00 | 514819 | EL-RENO4 138.00 | 0 |  | 1 | 11SP | 133 | 153 | 0 |  | 50.2733 | 100.9666 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 155 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T10145511SP | FROM->TO | EL RENO - SERVICE PL EL RENO 69KV CKT 1 | PL | OKGE | OKGE |  |  | 0 | 514818 | ELRENO 2 69.000 | 514817 | SVCELRN2 69.000 | 0 |  | 1 | 11SP | 48 | 48 | 0 |  | 92.7823 | 100.3047 | [7 empty] | CATEGORYB | SINGLE | MUSTANG (MUSTANG6) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 514860 | MSTANG 2 69.000 | 514861 | MUSTANG4 138.00 | 515740 | MUSTANG1 13.200 | 1 |  | 49 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T10145511SP | FROM->TO | EL RENO - SERVICE PL EL RENO 69KV CKT 1 | PL | OKGE | OKGE |  |  | 0 | 514818 | ELRENO 2 69.000 | 514817 | SVCELRN2 69.000 | 0 |  | 1 | 11SP | 48 | 48 | 0 |  | 92.7823 | 100.3047 | [7 empty] | CATEGORYB | SINGLE | MUSTANG (MUSTANG6) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 514860 | MSTANG 2 69.000 | 514861 | MUSTANG4 138.00 | 515740 | MUSTANG1 13.200 | 1 |  | 49 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1855511SP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | PL | WFEC | AEPW | WESTERN | WESTERN | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 11SP | 144 | 179 | 179 |  | 38.0143 | 111.9228 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WWRDEHV7 345.00 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 201 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T10235511SP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | PL | WFEC | AEPW | WESTERN | WESTERN | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 11SP | 144 | 179 | 179 |  | 38.0118 | 111.9052 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  | 201 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1745511SP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | PL | WFEC | AEPW | WESTERN | WESTERN | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 11SP | 144 | 179 | 179 |  | 37.9011 | 111.6665 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 200 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T35511SP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | PL | WFEC | AEPW | WESTERN | WESTERN | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 11SP | 144 | 179 | 179 |  | 27.3324 | 103.9743 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  | 187 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T2115512SP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | PL | WFEC | AEPW | WESTERN | WESTERN | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 12SP | 144 | 179 | 179 |  | 36.6658 | 114.047 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WWRDEHV7 345.00 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 205 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T11105512SP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | PL | WFEC | AEPW | WESTERN | WESTERN | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 12SP | 144 | 179 | 179 |  | 36.666 | 114.0318 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  | 205 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1985512SP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | PL | WFEC | AEPW | WESTERN | WESTERN | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 12SP | 144 | 179 | 179 |  | 36.5372 | 113.7836 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 204 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T55512SP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | PL | WFEC | AEPW | WESTERN | WESTERN | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 12SP | 144 | 179 | 179 |  | 25.1604 | 107.5439 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  | 193 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61V4195521SP |  | FAIRVIEW 69KV | REL | WFEC |  | AEP-IM |  |  | 520909 | FAIRVEW2 69.000 | [5 empty] | 21SP | [7 empty] | 0.8641 | 0.8641 | 0.79077 | 0.9675 | 0.9 | 1.05 | CATEGORYB | SINGLE | FAIRVIEW - OKEENE 69KV CKT 1 | 0 | 521015 | OKEENE 2 69.000 | 520909 | FAIRVEW2 69.000 | 0 |  | 1 |  |  |  | WFEC | FAIRVIEW Capacitor 69KV | Install 18 Mvar capacitor at Fairview 69kV bus. | [52 empty] | 2017-06-01 | 2017-06-01
2007-AG3 | AFS7 | [7 empty] | 2007AG3AFS71T923309WP | FROM->TO | FLATRDG3 138.00 - HARPER 138KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 09WP | 105.2 | 105.2 |  | 36.146 | 108.5317 | [9 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | FLATRDG3 138.00 - MEDICINE LODGE 138KV CKT 1 | Rebuild 8.05 mile line | 286 | 286 |  |  | 8.05 | [6 empty] | 250k per mile | 2012500 | 2008-01-01 | [38 empty] | 2009-12-01 | 2013-06-01
2007-AG3 | AFS7 | [7 empty] | 2007AG3AFS71T923309WP | FROM->TO | FLATRDG3 138.00 - HARPER 138KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 09WP | 105.2 | 105.2 |  | 36.146 | 108.5317 | [9 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 |  |  | 24.15 | 24 | 24 |  |  |  |  | 250k per mile | 6037500 | 2008-01-01 | [38 empty] | 2009-12-01 | 2013-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T12935011SP | TO->FROM | FLETCHER - HOLCOMB 115KV CKT 1 | REL | SUNC | SUNC | SEPC | WHEATLAN | 0 | 531448 | HOLCOMB3 115.00 | 531420 | FLETCHR3 115.00 | 0 |  | 1 | 11SP | 165 | 198 | 198 | 106.9 | 106.8944 | 106.5393 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SUNC-14 | 0 | 0 |  | 0 |  | 0 |  |  |  | 211 |  | SUNC | FLETCHER - HOLCOMB 115KV CKT 1 | Rebuild 11.1 miles of the 18.3 mile Fletcher - Holcomb 115 kV line with 954 ACSR Cardinal | 214 | 246 |  |  | 11.1 | 24 |  |  | 0.0146 | 0.07617 | 0.02379 |  | 4000000 | 2009-11-11 | [38 empty] | 2010-10-01 | 2013-06-01 | 2013-02-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T12885012SP | TO->FROM | FLETCHER - HOLCOMB 115KV CKT 1 | REL | SUNC | SUNC | SEPC | WHEATLAN | 0 | 531448 | HOLCOMB3 115.00 | 531420 | FLETCHR3 115.00 | 0 |  | 1 | 12SP | 165 | 198 | 198 | 111 | 111.0028 | 108.8794 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SUNC-14 | 0 | 0 |  | 0 |  | 0 |  |  |  | 216 |  | SUNC | FLETCHER - HOLCOMB 115KV CKT 1 | Rebuild 11.1 miles of the 18.3 mile Fletcher - Holcomb 115 kV line with 954 ACSR Cardinal | 214 | 246 |  |  | 11.1 | 24 |  |  | 0.0146 | 0.07617 | 0.02379 |  | 4000000 | 2009-11-11 | [38 empty] | 2010-10-01 | 2013-06-01 | 2013-02-01
2009-AGP2 | AFS6UP |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS6UP1T4275021SP | FROM->TO | FORT JUNCTION SWITCHING STATION - WEST JUNCTION CITY JUNCTION (EAST) 115KV CKT 1 | REL | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533328 | FT JCT 3 115.00 | 533343 | WJCCTYE3 115.00 | 0 |  | 1 | 21SP | 92 | 92 | 0 |  | 101.5358 | 105.4801 | [7 empty] | CATEGORYB | SINGLE | FORT JUNCTION SWITCHING STATION - JUNCTION CITY 115KV CKT 1 | 0 | 533328 | FT JCT 3 115.00 | 533330 | JCTCTY 3 115.00 | 0 |  | 1 |  | 98 |  | WERE | Line - Fort Junction - West Junction City 115 kV | Build new 8.76 mile Fort Junction - West Junction City 115 kV line that follows the path of the JEC - Summit 345 kV line. Remove old double circuit and West Junction City Junction (East) - West Junction City 115 kV line. | [52 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6UP |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS6UP1T4285021SP | FROM->TO | FORT JUNCTION SWITCHING STATION - WEST JUNCTION CITY JUNCTION (EAST) 115KV CKT 2 | REL | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533328 | FT JCT 3 115.00 | 533343 | WJCCTYE3 115.00 | 0 |  | 2 | 21SP | 92 | 92 | 0 |  | 101.5358 | 105.4801 | [7 empty] | CATEGORYB | SINGLE | FORT JUNCTION SWITCHING STATION - JUNCTION CITY 115KV CKT 1 | 0 | 533328 | FT JCT 3 115.00 | 533330 | JCTCTY 3 115.00 | 0 |  | 1 |  | 98 |  | WERE | Line - Fort Junction - West Junction City 115 kV | Build new 8.76 mile Fort Junction - West Junction City 115 kV line that follows the path of the JEC - Summit 345 kV line. Remove old double circuit and West Junction City Junction (East) - West Junction City 115 kV line. | [52 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T10545510WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | PL | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 10WP | 171 | 185 | 0 |  | 38.4388 | 102.08 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  | 189 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T10545510WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | PL | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 10WP | 171 | 185 | 0 |  | 38.4388 | 102.08 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  | 189 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1155510WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | PL | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 10WP | 171 | 185 | 0 |  | 38.4344 | 102.0704 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WWRDEHV7 345.00 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 189 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1155510WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | PL | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 10WP | 171 | 185 | 0 |  | 38.4344 | 102.0704 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WWRDEHV7 345.00 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 189 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T10255511SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | PL | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 11SP | 133 | 153 | 0 |  | 42.8448 | 116.0967 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  | 178 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T10255511SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | PL | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 11SP | 133 | 153 | 0 |  | 42.8448 | 116.0967 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  | 178 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1875511SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | PL | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 11SP | 133 | 153 | 0 |  | 42.8365 | 116.0809 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WWRDEHV7 345.00 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 178 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1875511SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | PL | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 11SP | 133 | 153 | 0 |  | 42.8365 | 116.0809 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WWRDEHV7 345.00 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 178 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1765511SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | PL | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 11SP | 133 | 153 | 0 |  | 41.2135 | 113.3779 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 174 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1765511SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | PL | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 11SP | 133 | 153 | 0 |  | 41.2135 | 113.3779 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 174 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T5875511WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | PL | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 11WP | 171 | 185 | 0 |  | 38.4123 | 101.6684 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  | 189 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T5875511WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | PL | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 11WP | 171 | 185 | 0 |  | 38.4123 | 101.6684 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  | 189 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T775511WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | PL | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 11WP | 171 | 185 | 0 |  | 38.4076 | 101.6574 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WWRDEHV7 345.00 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 189 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T775511WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | PL | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 11WP | 171 | 185 | 0 |  | 38.4076 | 101.6574 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WWRDEHV7 345.00 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 189 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T11125512SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | PL | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 12SP | 133 | 153 | 0 |  | 42.3215 | 117.4315 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  | 180 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T11125512SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | PL | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 12SP | 133 | 153 | 0 |  | 42.3215 | 117.4315 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  | 180 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T2135512SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | PL | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 12SP | 133 | 153 | 0 |  | 42.3146 | 117.4138 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WWRDEHV7 345.00 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 180 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T2135512SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | PL | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 12SP | 133 | 153 | 0 |  | 42.3146 | 117.4138 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WWRDEHV7 345.00 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 180 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T2005512SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | PL | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 12SP | 133 | 153 | 0 |  | 40.6441 | 114.7287 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 176 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T2005512SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | PL | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 12SP | 133 | 153 | 0 |  | 40.6441 | 114.7287 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 176 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T1285011SP | FROM->TO | FRANKLIN SW (FRANKLIN) 138/69/13.8KV TRANSFORMER CKT 1 | EXP | WFEC | WFEC | AEP-IM-I | AEP-IM-I | 1 | 520917 | FRNKLNS4 138.00 | 520916 | FRNKLNS2 69.000 | 521169 | FRNKTERT 13.800 | 1 | 11SP | 70 | 70 | 70 | 101 | 101.0297 | 102.0383 | [7 empty] | CATEGORYB | SINGLE | CANADIAN SW - GOLDSBY 138KV CKT 1 | 0 | 520842 | CANADNS4 138.00 | 520924 | GOLDSBY4 138.00 | 0 |  | 1 |  | 72 |  | WFEC | Multi - Franklin SW - Acme - Norman - OU SW Conversion 138 kV | Convert 5 mile Acme - Franklin from 69 kV to 138 kV. | [52 empty] | 2011-06-01 | 2012-10-01 | 2011-10-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T1395012SP | FROM->TO | FRANKLIN SW (FRANKLIN) 138/69/13.8KV TRANSFORMER CKT 1 | EXP | WFEC | WFEC | AEP-IM-I | AEP-IM-I | 1 | 520917 | FRNKLNS4 138.00 | 520916 | FRNKLNS2 69.000 | 521169 | FRNKTERT 13.800 | 1 | 12SP | 70 | 70 | 70 | 102.2 | 102.2013 | 102.6147 | [7 empty] | CATEGORYB | SINGLE | CANADIAN SW - GOLDSBY 138KV CKT 1 | 0 | 520842 | CANADNS4 138.00 | 520924 | GOLDSBY4 138.00 | 0 |  | 1 |  | 72 |  | WFEC | Multi - Franklin SW - Acme - Norman - OU SW Conversion 138 kV | Convert 5 mile Acme - Franklin from 69 kV to 138 kV. | [52 empty] | 2011-06-01 | 2012-10-01 | 2011-10-01
2006-AG1 | 2006-AG1 | [7 empty] | 2006-AG1WFEC5209205209195211822 |  | FT SUPPLY 138/69KV TRANSFORMER CKT 1 | U | WFEC | WFEC |  |  | 1 | 520920 | FTSUPLY4 138 | 520919 | FTSUPLY269.0 | 521182 |  | 2 | 16SP |  | 70 | [12 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | WFEC | FT SUPPLY 138/69KV TRANSFORMER CKT 1 | Install 2nd 70 MVA auto at Ft Supply | 70 | 70 |  |  |  | 12 | 18 |  |  |  |  | Use RS from Ft Supply Auto | 2000000 | [39 empty] | 2006-12-01 | 2008-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1105510WP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | PL | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 10WP | 124 | 124 | 0 |  | 91.4516 | 125.4491 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 156 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T10555510WP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | PL | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 10WP | 124 | 124 | 0 |  | 91.6883 | 125.4052 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  | 156 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1165510WP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | PL | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 10WP | 124 | 124 | 0 |  | 91.6665 | 125.3991 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WWRDEHV7 345.00 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 156 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T10265511SP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | PL | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 11SP | 124 | 124 | 0 |  | 89.1052 | 129.9208 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  | 162 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1885511SP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | PL | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 11SP | 124 | 124 | 0 |  | 89.0853 | 129.9147 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WWRDEHV7 345.00 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 162 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1775511SP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | PL | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 11SP | 124 | 124 | 0 |  | 88.8902 | 129.4391 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 161 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T5885511WP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | PL | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 11WP | 124 | 124 | 0 |  | 94.0103 | 126.8963 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  | 158 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T785511WP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | PL | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 11WP | 124 | 124 | 0 |  | 93.9931 | 126.8869 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WWRDEHV7 345.00 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 158 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T725511WP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | PL | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 11WP | 124 | 124 | 0 |  | 93.7862 | 126.3912 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 157 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T11135512SP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | PL | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 12SP | 124 | 124 | 0 |  | 91.867 | 127.8223 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  | 159 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T2145512SP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | PL | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 12SP | 124 | 124 | 0 |  | 91.8529 | 127.814 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WWRDEHV7 345.00 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 159 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T2015512SP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | PL | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 12SP | 124 | 124 | 0 |  | 91.6445 | 127.3533 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 158 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T4575512WP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | PL | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 12WP | 124 | 124 | 0 |  | 91.2712 | 132.5952 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  | 165 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T805512WP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | PL | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 12WP | 124 | 124 | 0 |  | 91.2537 | 132.5575 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WWRDEHV7 345.00 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 165 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T685512WP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | PL | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 12WP | 124 | 124 | 0 |  | 91.0472 | 132.0627 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 164 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1505511SP | TO->FROM | GRAY TAP - PENSACOLA 69KV CKT 1 | REL | GRDA | GRDA | GRDA-NEO | GRDA | 0 | 512628 | PENSA 2 69.000 | 512665 | GRAY TP2 69.000 | 0 |  | 1 | 11SP | 37 | 47 | 0 | 131.1 | 131.1283 | 133.7143 | [7 empty] | CATEGORYB | SINGLE | KANSAS - KANSAS TAP 161KV CKT 1 | 0 | 512714 | KANSATP5 161.00 | 512716 | KANSAS 5 161.00 | 0 |  | 1 |  | 63 |  | GRDA | GRAY TAP - PENSACOLA 69KV CKT 1 | Rebuild 4.4 mile line to 795 ACSR | [52 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T9995511SP | TO->FROM | GRAY TAP - PENSACOLA 69KV CKT 1 | REL | GRDA | GRDA | GRDA-NEO | GRDA | 0 | 512628 | PENSA 2 69.000 | 512665 | GRAY TP2 69.000 | 0 |  | 1 | 11SP | 37 | 47 | 0 | 131.1 | 131.1282 | 133.7141 | [7 empty] | CATEGORYB | SINGLE | KANSAS (KANAUTO1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 512715 | KANSAS 2 69.000 | 512716 | KANSAS 5 161.00 | 512736 | KANSAS1 13.800 | 1 |  | 63 |  | GRDA | GRAY TAP - PENSACOLA 69KV CKT 1 | Rebuild 4.4 mile line to 795 ACSR | [52 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T55511SP | TO->FROM | GRAY TAP - PENSACOLA 69KV CKT 1 | REL | GRDA | GRDA | GRDA-NEO | GRDA | 0 | 512628 | PENSA 2 69.000 | 512665 | GRAY TP2 69.000 | 0 |  | 1 | 11SP | 37 | 47 | 0 | 129.3 | 129.2623 | 132.4441 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  | 63 |  | GRDA | GRAY TAP - PENSACOLA 69KV CKT 1 | Rebuild 4.4 mile line to 795 ACSR | [52 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T14495511SP | TO->FROM | GRAY TAP - PENSACOLA 69KV CKT 1 | REL | GRDA | GRDA | GRDA-NEO | GRDA | 0 | 512628 | PENSA 2 69.000 | 512665 | GRAY TP2 69.000 | 0 |  | 1 | 11SP | 37 | 47 | 0 | 129.2 | 129.2158 | 132.0022 | [7 empty] | CATEGORYB | NONSINGLE | GRDA-OPGD-05 | 0 | 0 |  | 0 |  | 0 |  |  |  | 63 |  | GRDA | GRAY TAP - PENSACOLA 69KV CKT 1 | Rebuild 4.4 mile line to 795 ACSR | [52 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1695512SP | TO->FROM | GRAY TAP - PENSACOLA 69KV CKT 1 | REL | GRDA | GRDA | GRDA-NEO | GRDA | 0 | 512628 | PENSA 2 69.000 | 512665 | GRAY TP2 69.000 | 0 |  | 1 | 12SP | 37 | 47 | 0 | 135.4 | 135.4379 | 140.2563 | [7 empty] | CATEGORYB | SINGLE | KANSAS - KANSAS TAP 161KV CKT 1 | 0 | 512714 | KANSATP5 161.00 | 512716 | KANSAS 5 161.00 | 0 |  | 1 |  | 66 |  | GRDA | GRAY TAP - PENSACOLA 69KV CKT 1 | Rebuild 4.4 mile line to 795 ACSR | [52 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T10855512SP | TO->FROM | GRAY TAP - PENSACOLA 69KV CKT 1 | REL | GRDA | GRDA | GRDA-NEO | GRDA | 0 | 512628 | PENSA 2 69.000 | 512665 | GRAY TP2 69.000 | 0 |  | 1 | 12SP | 37 | 47 | 0 | 135.4 | 135.4378 | 140.2561 | [7 empty] | CATEGORYB | SINGLE | KANSAS (KANAUTO1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 512715 | KANSAS 2 69.000 | 512716 | KANSAS 5 161.00 | 512736 | KANSAS1 13.800 | 1 |  | 66 |  | GRDA | GRAY TAP - PENSACOLA 69KV CKT 1 | Rebuild 4.4 mile line to 795 ACSR | [52 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T65512SP | TO->FROM | GRAY TAP - PENSACOLA 69KV CKT 1 | REL | GRDA | GRDA | GRDA-NEO | GRDA | 0 | 512628 | PENSA 2 69.000 | 512665 | GRAY TP2 69.000 | 0 |  | 1 | 12SP | 37 | 47 | 0 | 132.1 | 132.0959 | 137.9803 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  | 65 |  | GRDA | GRAY TAP - PENSACOLA 69KV CKT 1 | Rebuild 4.4 mile line to 795 ACSR | [52 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T15155512SP | TO->FROM | GRAY TAP - PENSACOLA 69KV CKT 1 | REL | GRDA | GRDA | GRDA-NEO | GRDA | 0 | 512628 | PENSA 2 69.000 | 512665 | GRAY TP2 69.000 | 0 |  | 1 | 12SP | 37 | 47 | 0 | 128.1 | 128.0914 | 133.2751 | [7 empty] | CATEGORYB | NONSINGLE | GRDA-OPGD-05 | 0 | 0 |  | 0 |  | 0 |  |  |  | 63 |  | GRDA | GRAY TAP - PENSACOLA 69KV CKT 1 | Rebuild 4.4 mile line to 795 ACSR | [52 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T2215516SP | TO->FROM | GRAY TAP - PENSACOLA 69KV CKT 1 | REL | GRDA | GRDA | GRDA-NEO | GRDA | 0 | 512628 | PENSA 2 69.000 | 512665 | GRAY TP2 69.000 | 0 |  | 1 | 16SP | 37 | 47 | 0 | 137.9 | 137.9347 | 140.5588 | [7 empty] | CATEGORYB | SINGLE | KANSAS - KANSAS TAP 161KV CKT 1 | 0 | 512714 | KANSATP5 161.00 | 512716 | KANSAS 5 161.00 | 0 |  | 1 |  | 67 |  | GRDA | GRAY TAP - PENSACOLA 69KV CKT 1 | Rebuild 4.4 mile line to 795 ACSR | [52 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T10985516SP | TO->FROM | GRAY TAP - PENSACOLA 69KV CKT 1 | REL | GRDA | GRDA | GRDA-NEO | GRDA | 0 | 512628 | PENSA 2 69.000 | 512665 | GRAY TP2 69.000 | 0 |  | 1 | 16SP | 37 | 47 | 0 | 137.9 | 137.9346 | 140.5587 | [7 empty] | CATEGORYB | SINGLE | KANSAS (KANAUTO1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 512715 | KANSAS 2 69.000 | 512716 | KANSAS 5 161.00 | 512736 | KANSAS1 13.800 | 1 |  | 67 |  | GRDA | GRAY TAP - PENSACOLA 69KV CKT 1 | Rebuild 4.4 mile line to 795 ACSR | [52 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T25016SP | TO->FROM | GRAY TAP - PENSACOLA 69KV CKT 1 | REL | GRDA | GRDA | GRDA-NEO | GRDA | 0 | 512628 | PENSA 2 69.000 | 512665 | GRAY TP2 69.000 | 0 |  | 1 | 16SP | 37 | 47 | 0 | 132.7 | 132.7066 | 140.3897 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  | 66 |  | GRDA | GRAY TAP - PENSACOLA 69KV CKT 1 | Rebuild 4.4 mile line to 795 ACSR | [52 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T15695516SP | TO->FROM | GRAY TAP - PENSACOLA 69KV CKT 1 | REL | GRDA | GRDA | GRDA-NEO | GRDA | 0 | 512628 | PENSA 2 69.000 | 512665 | GRAY TP2 69.000 | 0 |  | 1 | 16SP | 37 | 47 | 0 | 135 | 135.0459 | 138.0748 | [7 empty] | CATEGORYB | NONSINGLE | GRDA-OPGD-05 | 0 | 0 |  | 0 |  | 0 |  |  |  | 65 |  | GRDA | GRAY TAP - PENSACOLA 69KV CKT 1 | Rebuild 4.4 mile line to 795 ACSR | [52 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T55021SP | TO->FROM | GRAY TAP - PENSACOLA 69KV CKT 1 | REL | GRDA | GRDA | GRDA-NEO | GRDA | 0 | 512628 | PENSA 2 69.000 | 512665 | GRAY TP2 69.000 | 0 |  | 1 | 21SP | 37 | 47 | 0 | 147.7 | 147.7337 | 152.7819 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  | 72 |  | GRDA | GRAY TAP - PENSACOLA 69KV CKT 1 | Rebuild 4.4 mile line to 795 ACSR | [52 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T26005021SP | TO->FROM | GRAY TAP - PENSACOLA 69KV CKT 1 | REL | GRDA | GRDA | GRDA-NEO | GRDA | 0 | 512628 | PENSA 2 69.000 | 512665 | GRAY TP2 69.000 | 0 |  | 1 | 21SP | 37 | 47 | 0 | 142.7 | 142.7088 | 147.4237 | [7 empty] | CATEGORYB | NONSINGLE | GRDA-OPGD-05 | 0 | 0 |  | 0 |  | 0 |  |  |  | 70 |  | GRDA | GRAY TAP - PENSACOLA 69KV CKT 1 | Rebuild 4.4 mile line to 795 ACSR | [52 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T19605021SP | TO->FROM | GRAY TAP - PENSACOLA 69KV CKT 1 | REL | GRDA | GRDA | GRDA-NEO | GRDA | 0 | 512628 | PENSA 2 69.000 | 512665 | GRAY TP2 69.000 | 0 |  | 1 | 21SP | 37 | 47 | 0 | 142.8 | 142.7966 | 146.8669 | [7 empty] | CATEGORYB | SINGLE | KANSAS (KANAUTO1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 512715 | KANSAS 2 69.000 | 512716 | KANSAS 5 161.00 | 512736 | KANSAS1 13.800 | 1 |  | 70 |  | GRDA | GRAY TAP - PENSACOLA 69KV CKT 1 | Rebuild 4.4 mile line to 795 ACSR | [52 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T3395021SP | TO->FROM | GRAY TAP - PENSACOLA 69KV CKT 1 | REL | GRDA | GRDA | GRDA-NEO | GRDA | 0 | 512628 | PENSA 2 69.000 | 512665 | GRAY TP2 69.000 | 0 |  | 1 | 21SP | 37 | 47 | 0 | 142.8 | 142.7965 | 146.8668 | [7 empty] | CATEGORYB | SINGLE | KANSAS - KANSAS TAP 161KV CKT 1 | 0 | 512714 | KANSATP5 161.00 | 512716 | KANSAS 5 161.00 | 0 |  | 1 |  | 70 |  | GRDA | GRAY TAP - PENSACOLA 69KV CKT 1 | Rebuild 4.4 mile line to 795 ACSR | [52 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T65021SP | FROM->TO | GRAY TAP - ZENA TAP 69KV CKT 1 | REL | GRDA | GRDA | GRDA | GRDA | 0 | 512665 | GRAY TP2 69.000 | 512667 | ZENA TP2 69.000 | 0 |  | 1 | 21SP | 37 | 47 | 0 | 130 | 130.0226 | 135.0636 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  | 64 |  | GRDA | GRAY TAP - ZENA TAP 69KV CKT 1 | Rebuild 8.1 mile line to 795 ACSR | [52 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T26015021SP | FROM->TO | GRAY TAP - ZENA TAP 69KV CKT 1 | REL | GRDA | GRDA | GRDA | GRDA | 0 | 512665 | GRAY TP2 69.000 | 512667 | ZENA TP2 69.000 | 0 |  | 1 | 21SP | 37 | 47 | 0 | 128.6 | 128.5908 | 133.2871 | [7 empty] | CATEGORYB | NONSINGLE | GRDA-OPGD-05 | 0 | 0 |  | 0 |  | 0 |  |  |  | 63 |  | GRDA | GRAY TAP - ZENA TAP 69KV CKT 1 | Rebuild 8.1 mile line to 795 ACSR | [52 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T19615021SP | FROM->TO | GRAY TAP - ZENA TAP 69KV CKT 1 | REL | GRDA | GRDA | GRDA | GRDA | 0 | 512665 | GRAY TP2 69.000 | 512667 | ZENA TP2 69.000 | 0 |  | 1 | 21SP | 37 | 47 | 0 | 128.4 | 128.4417 | 132.5154 | [7 empty] | CATEGORYB | SINGLE | KANSAS (KANAUTO1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 512715 | KANSAS 2 69.000 | 512716 | KANSAS 5 161.00 | 512736 | KANSAS1 13.800 | 1 |  | 63 |  | GRDA | GRAY TAP - ZENA TAP 69KV CKT 1 | Rebuild 8.1 mile line to 795 ACSR | [52 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T3405021SP | FROM->TO | GRAY TAP - ZENA TAP 69KV CKT 1 | REL | GRDA | GRDA | GRDA | GRDA | 0 | 512665 | GRAY TP2 69.000 | 512667 | ZENA TP2 69.000 | 0 |  | 1 | 21SP | 37 | 47 | 0 | 128.4 | 128.4416 | 132.5152 | [7 empty] | CATEGORYB | SINGLE | KANSAS - KANSAS TAP 161KV CKT 1 | 0 | 512714 | KANSATP5 161.00 | 512716 | KANSAS 5 161.00 | 0 |  | 1 |  | 63 |  | GRDA | GRAY TAP - ZENA TAP 69KV CKT 1 | Rebuild 8.1 mile line to 795 ACSR | [52 empty] | 2013-06-01 | 2013-06-01
2008-AGP1 | AFS6 | [7 empty] | 2008AGP1AFS61T3481414SP | FROM->TO | GREENLEAF - KNOB HILL 115KV CKT 1 | U | SUNC | WERE |  | NCENTRAL | 0 | 539665 | GRNLEAF3 115.00 | 533332 | KNOB HL3 115.00 | 0 |  | 1 | 14SP | 92 | 92 | 92 | 97.6559 | 100.8753 | [9 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  |  | Rebuild Clifton to Knob Hill | MKEC | GREENLEAF - KNOB HILL 115KV CKT 1 MKEC | Rebuild 11.8 of 20.9 miles | 239 | 239 | 239 | 239 | 11.8 | 24 | 24 |  |  |  |  | $250k per mile | 3525000 | 2010-02-22 | [38 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T11425512SP | TO->FROM | HAYS PLANT - SOUTH HAYS 115KV CKT 1 | S | MIDW | MIDW | REG E-IL | REG E-IL | 0 | 530553 | S HAYS 3 115.00 | 530562 | HAYS 3 115.00 | 0 |  | 1 | 12SP | 80 | 88 | 0 |  | 90.965 | 102.5058 | [7 empty] | CATEGORYB | SINGLE | KNOLL 230 (KNOLL T1) 230/115/11.49KV TRANSFORMER CKT 1 | 1 | 530558 | KNOLL 6 230.00 | 530561 | KNOLL 3 115.00 | 530629 | KNLL1 1 11.490 | 1 |  | 91 |  | MIDW | HAYS PLANT - SOUTH HAYS 115KV CKT 1 | Replace Wavetrap |  | 99 | [10 empty] | 35000 | 2010-01-01 | [38 empty] | 2012-06-01 | 2012-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T4795512WP | TO->FROM | HAYS PLANT - SOUTH HAYS 115KV CKT 1 | S | MIDW | MIDW | REG E-IL | REG E-IL | 0 | 530553 | S HAYS 3 115.00 | 530562 | HAYS 3 115.00 | 0 |  | 1 | 12WP | 80 | 88 | 0 | 97.7 | 97.6687 | 102.1632 | [7 empty] | CATEGORYB | SINGLE | KNOLL 230 (KNOLL T1) 230/115/11.49KV TRANSFORMER CKT 1 | 1 | 530558 | KNOLL 6 230.00 | 530561 | KNOLL 3 115.00 | 530629 | KNLL1 1 11.490 | 1 |  | 90 |  | MIDW | HAYS PLANT - SOUTH HAYS 115KV CKT 1 | Replace Wavetrap |  | 99 | [10 empty] | 35000 | 2010-01-01 | [38 empty] | 2012-06-01 | 2012-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T11445516SP | TO->FROM | HAYS PLANT - SOUTH HAYS 115KV CKT 1 | S | MIDW | MIDW | REG E-IL | REG E-IL | 0 | 530553 | S HAYS 3 115.00 | 530562 | HAYS 3 115.00 | 0 |  | 1 | 16SP | 80 | 88 | 0 |  | 90.1008 | 103.3703 | [7 empty] | CATEGORYB | SINGLE | KNOLL 230 (KNOLL T1) 230/115/11.49KV TRANSFORMER CKT 1 | 1 | 530558 | KNOLL 6 230.00 | 530561 | KNOLL 3 115.00 | 530629 | KNLL1 1 11.490 | 1 |  | 91 |  | MIDW | HAYS PLANT - SOUTH HAYS 115KV CKT 1 | Replace Wavetrap |  | 99 | [10 empty] | 35000 | 2010-01-01 | [38 empty] | 2012-06-01 | 2012-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T7345516WP | TO->FROM | HAYS PLANT - SOUTH HAYS 115KV CKT 1 | S | MIDW | MIDW | REG E-IL | REG E-IL | 0 | 530553 | S HAYS 3 115.00 | 530562 | HAYS 3 115.00 | 0 |  | 1 | 16WP | 80 | 88 | 0 |  | 92.8261 | 100.1082 | [7 empty] | CATEGORYB | SINGLE | KNOLL 230 (KNOLL T1) 230/115/11.49KV TRANSFORMER CKT 1 | 1 | 530558 | KNOLL 6 230.00 | 530561 | KNOLL 3 115.00 | 530629 | KNLL1 1 11.490 | 1 |  | 89 |  | MIDW | HAYS PLANT - SOUTH HAYS 115KV CKT 1 | Replace Wavetrap |  | 99 | [10 empty] | 35000 | 2010-01-01 | [38 empty] | 2012-06-01 | 2012-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61V4205521SP |  | HAZELTON 69KV | REL | WFEC |  | AEP-IM |  |  | 520937 | HAZELTN2 69.000 | [5 empty] | 21SP | [7 empty] | 0.89724 | 0.89724 | 0.85219 | 0.94831 | 0.9 | 1.05 | CATEGORYB | SINGLE | FAIRVIEW - OKEENE 69KV CKT 1 | 0 | 521015 | OKEENE 2 69.000 | 520909 | FAIRVEW2 69.000 | 0 |  | 1 |  |  |  | WFEC | FAIRVIEW Capacitor 69KV | Install 18 Mvar capacitor at Fairview 69kV bus. | [52 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61V4215521SP |  | HAZELTON JCT 69KV | REL | WFEC |  | AEP-IM |  |  | 520938 | HAZLTNJ2 69.000 | [5 empty] | 21SP | [8 empty] | 0.91216 | 0.86799 | 0.96233 | 0.9 | 1.05 | CATEGORYB | SINGLE | FAIRVIEW - OKEENE 69KV CKT 1 | 0 | 521015 | OKEENE 2 69.000 | 520909 | FAIRVEW2 69.000 | 0 |  | 1 |  |  |  | WFEC | FAIRVIEW Capacitor 69KV | Install 18 Mvar capacitor at Fairview 69kV bus. | [52 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61V5805516SP |  | HENESSEY 69KV | REL | WFEC |  | AEP-IM |  |  | 520940 | HENESEY2 69.000 | [5 empty] | 16SP | [8 empty] | 0.91084 | 0.88292 | 0.98256 | 0.9 | 1.05 | CATEGORYB | SINGLE | DOVER SW (DOVER) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 520882 | DOVERSW4 138.00 | 520881 | DOVERSW2 69.000 | 521166 | DVRTERT 13.800 | 1 |  |  |  | WFEC | East Kingfisher Capacitor 69 kV | Install 18 Mvar capacitor at East Kingfisher bus. | [52 empty] | 2013-06-01 | 2013-06-01
2005-AG2 | 2005-AG2 | [7 empty] | 2005-AG2AEPW5211575109111 |  | HUGO POWER PLANT - VALLIANT 138KV CKT 1 | U | WFEC | AEPW |  |  | 0 | 55948 | HUGO PP4 138 | 54044 | VALIANT4 138 | 0 |  | 1 | 10SP |  | 315 | [12 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | AEPW | HUGO POWER PLANT - VALLIANT 345 KV AEPW | Vallient 345 KV line terminal | [5 empty] | 24 |  | Y |  |  |  |  | 2500000 | [39 empty] | 2012-07-01 | 2012-07-01
2005-AG2 | 2005-AG2 | [7 empty] | 2005-AG2WFEC5211575109111 |  | HUGO POWER PLANT - VALLIANT 138KV CKT 1 | U | WFEC | AEPW |  |  | 0 | 55948 | HUGO PP4 138 | 54044 | VALIANT4 138 | 0 |  | 1 | 10SP |  | 315 | [12 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | WFEC | HUGO POWER PLANT - VALLIANT 345 KV WFEC | New 19 miles 345 KV | 500 | 500 |  |  | 19 | 24 |  | Y |  |  |  | The 345kv line would go: From Hugo Power Station (55948) to a new 500 MVA 138/345kv autotransformer at the Hugo plant site to PSO Valiant (54037) USE data from GEN-2004-018 | 16000000 | [39 empty] | 2012-07-01 | 2012-07-01
2005-AG2 | 2005-AG2 | [7 empty] | 2005-AG2WFEC5211575209485211891 |  | HUGO POWER PLANT 345/138KV TRANSFORMER CKT 1 | U | WFEC | AEPW |  |  | 0 | 55948 | HUGO PP4 138 | 54044 | VALIANT4 138 | 0 |  | 1 | 10SP |  | 315 | [12 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | WFEC | HUGO POWER PLANT 345/138KV TRANSFORMER CKT 1 | New 345/138 kv Auto | 500 | 500 |  |  | 19 | 24 |  | Y |  |  |  | The 345kv line would go: From Hugo Power Station (55948) to a new 500 MVA 138/345kv autotransformer at the Hugo plant site to PSO Valiant (54037) USE data from GEN-2004-018 | 16000000 | [39 empty] | 2012-07-01 | 2012-07-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T26025021SP | TO->FROM | JAY - ZENA TAP 69KV CKT 1 | REL | GRDA | GRDA | GRDA | GRDA-NEO | 0 | 512667 | ZENA TP2 69.000 | 512720 | JAY GR 2 69.000 | 0 |  | 1 | 21SP | 37 | 47 | 0 | 117 | 117.0392 | 121.7182 | [7 empty] | CATEGORYB | NONSINGLE | GRDA-OPGD-05 | 0 | 0 |  | 0 |  | 0 |  |  |  | 58 |  | GRDA | JAY - ZENA TAP 69KV CKT 1 | Rebuild 6.5 mile line to 795 ACSR | [52 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T19625021SP | TO->FROM | JAY - ZENA TAP 69KV CKT 1 | REL | GRDA | GRDA | GRDA | GRDA-NEO | 0 | 512667 | ZENA TP2 69.000 | 512720 | JAY GR 2 69.000 | 0 |  | 1 | 21SP | 37 | 47 | 0 | 116.6 | 116.5644 | 120.644 | [7 empty] | CATEGORYB | SINGLE | KANSAS (KANAUTO1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 512715 | KANSAS 2 69.000 | 512716 | KANSAS 5 161.00 | 512736 | KANSAS1 13.800 | 1 |  | 57 |  | GRDA | JAY - ZENA TAP 69KV CKT 1 | Rebuild 6.5 mile line to 795 ACSR | [52 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T3415021SP | TO->FROM | JAY - ZENA TAP 69KV CKT 1 | REL | GRDA | GRDA | GRDA | GRDA-NEO | 0 | 512667 | ZENA TP2 69.000 | 512720 | JAY GR 2 69.000 | 0 |  | 1 | 21SP | 37 | 47 | 0 | 116.6 | 116.5643 | 120.6438 | [7 empty] | CATEGORYB | SINGLE | KANSAS - KANSAS TAP 161KV CKT 1 | 0 | 512714 | KANSATP5 161.00 | 512716 | KANSAS 5 161.00 | 0 |  | 1 |  | 57 |  | GRDA | JAY - ZENA TAP 69KV CKT 1 | Rebuild 6.5 mile line to 795 ACSR | [52 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T75021SP | TO->FROM | JAY - ZENA TAP 69KV CKT 1 | REL | GRDA | GRDA | GRDA | GRDA-NEO | 0 | 512667 | ZENA TP2 69.000 | 512720 | JAY GR 2 69.000 | 0 |  | 1 | 21SP | 37 | 47 | 0 | 115.5 | 115.5309 | 120.5691 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  | 57 |  | GRDA | JAY - ZENA TAP 69KV CKT 1 | Rebuild 6.5 mile line to 795 ACSR | [52 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1065521SP | FROM->TO | JONESBORO - JONESBORO 161KV CKT 1 | REL | EES | SWPA |  | EMINTH | 0 | 338170 | 5JONES 161.00 | 505418 | JONESBO5 161.00 | 0 |  | 1 | 21SP | 309 | 309 | 0 | 111.5 | 111.4682 | 111.9445 | [7 empty] | CATEGORYB | SINGLE | KENNETT - NEW MADRID 161KV CKT 1 | 0 | 505400 | N MADRD5 161.00 | 505410 | KENNETT5 161.00 | 0 |  | 1 |  | 346 |  | SWPA | JONESBORO - JONESBORO 161KV CKT 1 SWPA | Replace Jumpers and 1200 Amp Terminal Equipment | [52 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1105521SP | FROM->TO | JONESBORO - JONESBORO 161KV CKT 1 | REL | EES | SWPA |  | EMINTH | 0 | 338170 | 5JONES 161.00 | 505418 | JONESBO5 161.00 | 0 |  | 1 | 21SP | 309 | 309 | 0 | 107.2 | 107.235 | 108.0433 | [7 empty] | CATEGORYB | SINGLE | KENNETT - PARAGOULD 161KV CKT 1 | 0 | 505410 | KENNETT5 161.00 | 505412 | PARAGLD5 161.00 | 0 |  | 1 |  | 334 |  | SWPA | JONESBORO - JONESBORO 161KV CKT 1 SWPA | Replace Jumpers and 1200 Amp Terminal Equipment | [52 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61V5815516SP |  | KINGFISHER 69KV | REL | WFEC |  | AEP-IM |  |  | 520964 | KNGFSHR2 69.000 | [5 empty] | 16SP | [8 empty] | 0.9208 | 0.8974 | 0.97312 | 0.9 | 1.05 | CATEGORYB | SINGLE | DOVER SW (DOVER) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 520882 | DOVERSW4 138.00 | 520881 | DOVERSW2 69.000 | 521166 | DVRTERT 13.800 | 1 |  |  |  | WFEC | East Kingfisher Capacitor 69 kV | Install 18 Mvar capacitor at East Kingfisher bus. | [52 empty] | 2013-06-01 | 2013-06-01
2006-AG1 | 2006-AG1 | [7 empty] | 2006-AG1OKGE5147955147945157321 |  | KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1 | U | OKGE |  |  |  | 1 | 514795 | KNOBHIL4 138 | 514794 | KNOBHIL269.0 | 515732 | KNOBHIL113.2 | 1 | 16SP |  | 67 | [12 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1 | Replace bus tie with 100MVA transformer | 123 | 134 | 123 | 134 |  | 15 | 12 | [5 empty] | 1750000 | [39 empty] | 2006-06-01 | 2008-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61V5825516SP |  | LACEY 69KV | REL | WFEC |  | AEP-IM |  |  | 520967 | LACEY 2 69.000 | [5 empty] | 16SP | [8 empty] | 0.90044 | 0.87217 | 0.97298 | 0.9 | 1.05 | CATEGORYB | SINGLE | DOVER SW (DOVER) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 520882 | DOVERSW4 138.00 | 520881 | DOVERSW2 69.000 | 521166 | DVRTERT 13.800 | 1 |  |  |  | WFEC | East Kingfisher Capacitor 69 kV | Install 18 Mvar capacitor at East Kingfisher bus. | [52 empty] | 2013-06-01 | 2013-06-01
NA | [8 empty] | NAKACP5429815429651 |  | LACYGNE - WEST GARDNER 345KV CKT 1 | U | KACP | KACP |  |  | 0 | 542981 | LACYGNE7 | 542965 | W.GRDNR7 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | KACP | LACYGNE - WEST GARDNER 345KV CKT 1 | KCPL Sponsored Project to Reconductor Line to be In-Service by 6/1/2006 | [52 empty] | 2006-06-01 | 2006-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T4735021SP | TO->FROM | LEA COUNTY REC -MHOON - LEA COUNTY REC-LOVINGTON INTERCHANGE 69KV CKT 1 | REL | SPS | SPS | SPS-LEA | SPS-LEA | 0 | 528618 | LE-LOVINTON269.000 | 528667 | LE-MHOON 269.000 | 0 |  | 1 | 21SP | 41 | 54 | 0 | 111.8 | 111.7528 | 111.8025 | [7 empty] | CATEGORYB | SINGLE | LEA COUNTY REC-SAN ANDRES INTERCHANGE - LEA COUNTY REC-TEXACO 115KV CKT 1 | 0 | 528341 | LE-SANANDRS3115.00 | 528792 | LE-TEXACO 3115.00 | 0 |  | 1 |  | 61 |  | SPS | CUNNINGHAM - SAN ANRESS 115KV CKT2 | Build redundandant 115 kV line from Cunningham to LE-San Andress. IDEV: 16S_Build_Redundant_Line_to_LE-San Andress.idv | [52 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T26455021SP | TO->FROM | LEA COUNTY REC -MHOON - LEA COUNTY REC-LOVINGTON INTERCHANGE 69KV CKT 1 | REL | SPS | SPS | SPS-LEA | SPS-LEA | 0 | 528618 | LE-LOVINTON269.000 | 528667 | LE-MHOON 269.000 | 0 |  | 1 | 21SP | 41 | 54 | 0 | 111.7 | 111.7312 | 111.7925 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-V98 | 0 | 0 |  | 0 |  | 0 |  |  |  | 61 |  | SPS | CUNNINGHAM - SAN ANRESS 115KV CKT2 | Build redundandant 115 kV line from Cunningham to LE-San Andress. IDEV: 16S_Build_Redundant_Line_to_LE-San Andress.idv | [52 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T4705021SP | TO->FROM | LEA COUNTY REC -MHOON - LEA COUNTY REC-LOVINGTON INTERCHANGE 69KV CKT 1 | REL | SPS | SPS | SPS-LEA | SPS-LEA | 0 | 528618 | LE-LOVINTON269.000 | 528667 | LE-MHOON 269.000 | 0 |  | 1 | 21SP | 41 | 54 | 0 | 111.7 | 111.7457 | 111.7693 | [7 empty] | CATEGORYB | SINGLE | LEA COUNTY REC-SAN ANDRES INTERCHANGE 115/69KV TRANSFORMER CKT 1 | 0 | 528341 | LE-SANANDRS3115.00 | 528622 | LE-SANANDRS269.000 | 0 |  | 1 |  | 61 |  | SPS | CUNNINGHAM - SAN ANRESS 115KV CKT2 | Build redundandant 115 kV line from Cunningham to LE-San Andress. IDEV: 16S_Build_Redundant_Line_to_LE-San Andress.idv | [52 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T2425512SP | FROM->TO | LUBBOCK POWER & LIGHT-HOLLY PLANT 230/69KV TRANSFORMER CKT 1 | REL | SPS | SPS | SPS-MUNI | SPS-MUNI | 0 | 522870 | LP-HOLLY 6230.00 | 522866 | LP-HOLLY 269.000 | 0 |  | 1 | 12SP | 100 | 140 | 0 |  | 85.6886 | 105.0533 | [7 empty] | CATEGORYB | SINGLE | LUBBOCK POWER & LIGHT-SOUTHEAST 230/69KV TRANSFORMER CKT 1 | 0 | 522857 | LP-SOUTHEST269.000 | 522861 | LP-SOUTHEST6230.00 | 0 |  | 1 |  | 148 |  | LPL | LUBBOCK POWER & LIGHT-HOLLY PLANT 230/69KV TRANSFORMER CKT 1 | interim redispatch | [52 empty] | 2012-06-01 | 2016-06-01 | 2015-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T2435512SP | FROM->TO | LUBBOCK POWER & LIGHT-HOLLY PLANT 230/69KV TRANSFORMER CKT 1 | REL | SPS | SPS | SPS-MUNI | SPS-MUNI | 0 | 522870 | LP-HOLLY 6230.00 | 522866 | LP-HOLLY 269.000 | 0 |  | 1 | 12SP | 100 | 140 | 0 |  | 85.8231 | 105.053 | [7 empty] | CATEGORYB | SINGLE | LUBBOCK POWER & LIGHT-SOUTHEAST - LUBBOCK SOUTH INTERCHANGE 230KV CKT 1 | 0 | 522861 | LP-SOUTHEST6230.00 | 526269 | LUBBCK_STH 6230.00 | 0 |  | 1 |  | 148 |  | LPL | LUBBOCK POWER & LIGHT-HOLLY PLANT 230/69KV TRANSFORMER CKT 1 | interim redispatch | [52 empty] | 2012-06-01 | 2016-06-01 | 2015-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T115512SP | FROM->TO | LUBBOCK POWER & LIGHT-HOLLY PLANT 230/69KV TRANSFORMER CKT 1 | REL | SPS | SPS | SPS-MUNI | SPS-MUNI | 0 | 522870 | LP-HOLLY 6230.00 | 522866 | LP-HOLLY 269.000 | 0 |  | 1 | 12SP | 100 | 140 | 0 |  | 83.6929 | 100.7143 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  | 142 |  | LPL | LUBBOCK POWER & LIGHT-HOLLY PLANT 230/69KV TRANSFORMER CKT 1 | interim redispatch | [52 empty] | 2012-06-01 | 2016-06-01 | 2015-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T1685016SP | FROM->TO | LUBBOCK POWER & LIGHT-HOLLY PLANT 230/69KV TRANSFORMER CKT 1 | REL | SPS | SPS | SPS-MUNI | SPS-MUNI | 0 | 522870 | LP-HOLLY 6230.00 | 522866 | LP-HOLLY 269.000 | 0 |  | 1 | 16SP | 100 | 140 | 0 |  | 70.9702 | 105.9108 | [7 empty] | CATEGORYB | SINGLE | LUBBOCK POWER & LIGHT-SOUTHEAST - LUBBOCK SOUTH INTERCHANGE 230KV CKT 1 | 0 | 522861 | LP-SOUTHEST6230.00 | 526269 | LUBBCK_STH 6230.00 | 0 |  | 1 |  | 149 |  | LPL | LUBBOCK POWER & LIGHT-HOLLY PLANT 230/69KV TRANSFORMER CKT 1 | interim redispatch | [52 empty] | 2012-06-01 | 2016-06-01 | 2015-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T1665016SP | FROM->TO | LUBBOCK POWER & LIGHT-HOLLY PLANT 230/69KV TRANSFORMER CKT 1 | REL | SPS | SPS | SPS-MUNI | SPS-MUNI | 0 | 522870 | LP-HOLLY 6230.00 | 522866 | LP-HOLLY 269.000 | 0 |  | 1 | 16SP | 100 | 140 | 0 |  | 70.9697 | 105.9107 | [7 empty] | CATEGORYB | SINGLE | LUBBOCK POWER & LIGHT-SOUTHEAST 230/69KV TRANSFORMER CKT 1 | 0 | 522857 | LP-SOUTHEST269.000 | 522861 | LP-SOUTHEST6230.00 | 0 |  | 1 |  | 149 |  | LPL | LUBBOCK POWER & LIGHT-HOLLY PLANT 230/69KV TRANSFORMER CKT 1 | interim redispatch | [52 empty] | 2012-06-01 | 2016-06-01 | 2015-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T1775016SP | FROM->TO | LUBBOCK POWER & LIGHT-HOLLY PLANT 230/69KV TRANSFORMER CKT 1 | REL | SPS | SPS | SPS-MUNI | SPS-MUNI | 0 | 522870 | LP-HOLLY 6230.00 | 522866 | LP-HOLLY 269.000 | 0 |  | 1 | 16SP | 100 | 140 | 0 |  | 67.7561 | 102.0171 | [7 empty] | CATEGORYB | SINGLE | LUBBOCK EAST INTERCHANGE - LUBBOCK POWER & LIGHT-WADSWORTH 230KV CKT 1 | 0 | 522888 | LP-WADSWRTH6230.00 | 526299 | LUBBCK_EST 6230.00 | 0 |  | 1 |  | 143 |  | LPL | LUBBOCK POWER & LIGHT-HOLLY PLANT 230/69KV TRANSFORMER CKT 1 | interim redispatch | [52 empty] | 2012-06-01 | 2016-06-01 | 2015-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T75016SP | FROM->TO | LUBBOCK POWER & LIGHT-HOLLY PLANT 230/69KV TRANSFORMER CKT 1 | REL | SPS | SPS | SPS-MUNI | SPS-MUNI | 0 | 522870 | LP-HOLLY 6230.00 | 522866 | LP-HOLLY 269.000 | 0 |  | 1 | 16SP | 100 | 140 | 0 |  | 69.0473 | 101.1096 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  | 142 |  | LPL | LUBBOCK POWER & LIGHT-HOLLY PLANT 230/69KV TRANSFORMER CKT 1 | interim redispatch | [52 empty] | 2012-06-01 | 2016-06-01 | 2015-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T2455512SP | FROM->TO | LUBBOCK POWER & LIGHT-SOUTHEAST 230/69KV TRANSFORMER CKT 1 | REL | SPS | SPS | SPS-MUNI | SPS-MUNI | 0 | 522861 | LP-SOUTHEST6230.00 | 522857 | LP-SOUTHEST269.000 | 0 |  | 1 | 12SP | 100 | 140 | 0 |  | 85.4558 | 103.6051 | [7 empty] | CATEGORYB | SINGLE | Jones Station Bus#2 - LUBBOCK POWER & LIGHT-HOLLY PLANT 230KV CKT 1 | 0 | 522870 | LP-HOLLY 6230.00 | 526338 | JONES_BUS2 6230.00 | 0 |  | 1 |  | 146 |  | LPL | LUBBOCK POWER & LIGHT-SOUTHEAST 230/69KV TRANSFORMER CKT 1 | interim redispatch | [52 empty] | 2012-06-01 | 2016-06-01 | 2015-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T105512SP | FROM->TO | LUBBOCK POWER & LIGHT-SOUTHEAST 230/69KV TRANSFORMER CKT 1 | REL | SPS | SPS | SPS-MUNI | SPS-MUNI | 0 | 522861 | LP-SOUTHEST6230.00 | 522857 | LP-SOUTHEST269.000 | 0 |  | 1 | 12SP | 100 | 140 | 0 |  | 86.0517 | 101.5215 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  | 143 |  | LPL | LUBBOCK POWER & LIGHT-SOUTHEAST 230/69KV TRANSFORMER CKT 1 | interim redispatch | [52 empty] | 2012-06-01 | 2016-06-01 | 2015-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T1725016SP | FROM->TO | LUBBOCK POWER & LIGHT-SOUTHEAST 230/69KV TRANSFORMER CKT 1 | REL | SPS | SPS | SPS-MUNI | SPS-MUNI | 0 | 522861 | LP-SOUTHEST6230.00 | 522857 | LP-SOUTHEST269.000 | 0 |  | 1 | 16SP | 100 | 140 | 0 |  | 72.0794 | 104.2564 | [7 empty] | CATEGORYB | SINGLE | Jones Station Bus#2 - LUBBOCK POWER & LIGHT-HOLLY PLANT 230KV CKT 1 | 0 | 522870 | LP-HOLLY 6230.00 | 526338 | JONES_BUS2 6230.00 | 0 |  | 1 |  | 146 |  | LPL | LUBBOCK POWER & LIGHT-SOUTHEAST 230/69KV TRANSFORMER CKT 1 | interim redispatch | [52 empty] | 2012-06-01 | 2016-06-01 | 2015-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T1705016SP | FROM->TO | LUBBOCK POWER & LIGHT-SOUTHEAST 230/69KV TRANSFORMER CKT 1 | REL | SPS | SPS | SPS-MUNI | SPS-MUNI | 0 | 522861 | LP-SOUTHEST6230.00 | 522857 | LP-SOUTHEST269.000 | 0 |  | 1 | 16SP | 100 | 140 | 0 |  | 72.0794 | 104.2562 | [7 empty] | CATEGORYB | SINGLE | LUBBOCK POWER & LIGHT-HOLLY PLANT 230/69KV TRANSFORMER CKT 1 | 0 | 522866 | LP-HOLLY 269.000 | 522870 | LP-HOLLY 6230.00 | 0 |  | 1 |  | 146 |  | LPL | LUBBOCK POWER & LIGHT-SOUTHEAST 230/69KV TRANSFORMER CKT 1 | interim redispatch | [52 empty] | 2012-06-01 | 2016-06-01 | 2015-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T65016SP | FROM->TO | LUBBOCK POWER & LIGHT-SOUTHEAST 230/69KV TRANSFORMER CKT 1 | REL | SPS | SPS | SPS-MUNI | SPS-MUNI | 0 | 522861 | LP-SOUTHEST6230.00 | 522857 | LP-SOUTHEST269.000 | 0 |  | 1 | 16SP | 100 | 140 | 0 |  | 73.2951 | 103.7571 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  | 146 |  | LPL | LUBBOCK POWER & LIGHT-SOUTHEAST 230/69KV TRANSFORMER CKT 1 | interim redispatch | [52 empty] | 2012-06-01 | 2016-06-01 | 2015-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T1765016SP | FROM->TO | LUBBOCK POWER & LIGHT-SOUTHEAST 230/69KV TRANSFORMER CKT 1 | REL | SPS | SPS | SPS-MUNI | SPS-MUNI | 0 | 522861 | LP-SOUTHEST6230.00 | 522857 | LP-SOUTHEST269.000 | 0 |  | 1 | 16SP | 100 | 140 | 0 |  | 70.7188 | 102.9686 | [7 empty] | CATEGORYB | SINGLE | LUBBOCK EAST INTERCHANGE - LUBBOCK POWER & LIGHT-WADSWORTH 230KV CKT 1 | 0 | 522888 | LP-WADSWRTH6230.00 | 526299 | LUBBCK_EST 6230.00 | 0 |  | 1 |  | 145 |  | LPL | LUBBOCK POWER & LIGHT-SOUTHEAST 230/69KV TRANSFORMER CKT 1 | interim redispatch | [52 empty] | 2012-06-01 | 2016-06-01 | 2015-10-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T2575516SP | FROM->TO | MANHATTAN TAP - OSAGE SWITCHING STATION 115KV CKT 1 | REL | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524354 | MANHATN_TP 3115.00 | 524345 | OSAGE 3115.00 | 0 |  | 1 | 16SP | 160 | 160 | 0 | 101.3 | 101.3228 | 101.9498 | [7 empty] | CATEGORYB | SINGLE | EAST PLANT INTERCHANGE - PIERCE STREET TAP 115KV CKT 1 | 0 | 524162 | EAST_PLANT 3115.00 | 524185 | PIERCE_TP 3115.00 | 0 |  | 1 |  | 164 |  | SPS | OSAGE - RANDALL 115KV CKT 1 | Osage station & line reterminations with a new 2 mile 115 kV line from Randall Co | [52 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T1875016SP | FROM->TO | MANHATTAN TAP - OSAGE SWITCHING STATION 115KV CKT 1 | REL | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524354 | MANHATN_TP 3115.00 | 524345 | OSAGE 3115.00 | 0 |  | 1 | 16SP | 160 | 160 | 0 | 101.4 | 101.3991 | 101.7539 | [7 empty] | CATEGORYB | SINGLE | OSAGE SWITCHING STATION - RANDALL COUNTY INTERCHANGE 115KV CKT 1 | 0 | 524345 | OSAGE 3115.00 | 524364 | RANDALL 3115.00 | 0 |  | 1 |  | 163 |  | SPS | OSAGE - RANDALL 115KV CKT 1 | Osage station & line reterminations with a new 2 mile 115 kV line from Randall Co | [52 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T3735521SP | FROM->TO | MANHATTAN TAP - OSAGE SWITCHING STATION 115KV CKT 1 | REL | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524354 | MANHATN_TP 3115.00 | 524345 | OSAGE 3115.00 | 0 |  | 1 | 21SP | 160 | 160 | 0 | 124.5 | 124.485 | 125.447 | [7 empty] | CATEGORYB | SINGLE | EAST PLANT INTERCHANGE - PIERCE STREET TAP 115KV CKT 1 | 0 | 524162 | EAST_PLANT 3115.00 | 524185 | PIERCE_TP 3115.00 | 0 |  | 1 |  | 201 |  | SPS | OSAGE - RANDALL 115KV CKT 1 | Osage station & line reterminations with a new 2 mile 115 kV line from Randall Co | [52 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T4025021SP | FROM->TO | MANHATTAN TAP - OSAGE SWITCHING STATION 115KV CKT 1 | REL | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524354 | MANHATN_TP 3115.00 | 524345 | OSAGE 3115.00 | 0 |  | 1 | 21SP | 160 | 160 | 0 | 117.9 | 117.9179 | 118.0944 | [7 empty] | CATEGORYB | SINGLE | OSAGE SWITCHING STATION - RANDALL COUNTY INTERCHANGE 115KV CKT 1 | 0 | 524345 | OSAGE 3115.00 | 524364 | RANDALL 3115.00 | 0 |  | 1 |  | 189 |  | SPS | OSAGE - RANDALL 115KV CKT 1 | Osage station & line reterminations with a new 2 mile 115 kV line from Randall Co | [52 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T25955521SP | FROM->TO | MANHATTAN TAP - OSAGE SWITCHING STATION 115KV CKT 1 | REL | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524354 | MANHATN_TP 3115.00 | 524345 | OSAGE 3115.00 | 0 |  | 1 | 21SP | 160 | 160 | 0 | 116.6 | 116.6454 | 117.6224 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-V43 | 0 | 0 |  | 0 |  | 0 |  |  |  | 189 |  | SPS | OSAGE - RANDALL 115KV CKT 1 | Osage station & line reterminations with a new 2 mile 115 kV line from Randall Co | [52 empty] | 2017-06-01 | 2017-06-01
GEN-2006-010 | Turk | [7 empty] | GEN-2006-010AEPW5041225074561 |  | MCNAB REC - TURK 115KV CKT 1 | U | AEPW | AEPW | SARK | SARKAECC | 0 | 504122 | MCNAB 3 115.00 | 507456 | HEMPSTD3 115.00 | 0 |  | 1 |  | 150 | 174 |  | 47.9 | [10 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | AEPW | MCNAB REC - TURK 115KV CKT 1 | Build a new two mile, 138 kV, 1590 ACSR line section (operated at 115 kV) from Turk Substation to the existing Okay- Hope 115 kV line to form a Turk - Hope 115 kV line. | [11 empty] | 1520000 | 1520000 | [39 empty] | 2012-07-01 | 2012-07-01
2007-AG3 | AFS7 | [7 empty] | 2007AG3AFS71T853309WP | FROM->TO | MEDICINE LODGE - PRATT 115KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539673 | MED-LDG3 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 | 09WP | 79.7 | 79.7 |  | 38.6663 | 122.4019 | [9 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | MEDICINE LODGE - PRATT 115KV CKT 1 | Rebuild 26 mile line | [5 empty] | 24 | 24 |  |  |  |  | 250k per mile | 6500000 | 2008-01-01 | [38 empty] | 2009-12-01 | 2013-06-01
2007-AG3 | AFS7 | [7 empty] | 2007AG3AFS72T21409WP | FROM->TO | MEDICINE LODGE (MED-LDG4) 138/115/2.72KV TRANSFORMER CKT 1 | U | MKEC |  |  |  | 2 | 539674 | MED-LDG4 138.00 | 539673 | MED-LDG3 115.00 | 539917 | MEDLGT-T 2.7200 | 1 | 09WP | 56 | 56 |  | 123.6618 | 148.887 | [9 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | MEDICINE LODGE 138/115KV TRANSFORMER CKT 1 Displacement | Upgrade transformer |  | 250 |  |  |  | 18 | 18 |  | 0 | 0.06 |  | 22.5k per MVA at 250 MVA | 5625000 | 2008-01-01 | [38 empty] | 2009-12-01 | 2013-06-01
2009-AGP2 | AFS6UP |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T3215512SP | TO->FROM | MUND - PENTAGON 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533261 | PENTAGN3 115.00 | 533282 | MUND 3 115.00 | 0 |  | 1 | 12SP | 179 | 179 | 0 |  | 104.1653 | 103.1479 | [7 empty] | CATEGORYB | SINGLE | 87TH 7 345.00 - CRAIG 345KV CKT 1 | 0 | 532775 | 87TH 7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  | 185 |  | KCPL | Line - Iatan - Nashua 345 kV | Tap Nashua 345kV bus in Hawthorn-St. Joseph 345kV line, add Iatan-Nashua 345kV line and Nashua 345/161kv transformer | [52 empty] | 2012-06-01 | 2015-06-01
2009-AGP2 | AFS6UP |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1245512WP | TO->FROM | MUND - PENTAGON 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533261 | PENTAGN3 115.00 | 533282 | MUND 3 115.00 | 0 |  | 1 | 12WP | 179 | 179 | 0 |  | 101.8201 | 104.5399 | [7 empty] | CATEGORYB | SINGLE | 87TH 7 345.00 - CRAIG 345KV CKT 1 | 0 | 532775 | 87TH 7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  | 188 |  | KCPL | Line - Iatan - Nashua 345 kV | Tap Nashua 345kV bus in Hawthorn-St. Joseph 345kV line, add Iatan-Nashua 345kV line and Nashua 345/161kv transformer | [52 empty] | 2012-06-01 | 2015-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1765511WP | TO->FROM | NELIGH - PETERSBURG 115KV CKT 1 | CP | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640318 | PETRSBG7 115.00 | 640293 | NELIGH 7 115.00 | 0 |  | 1 | 11WP | 113 | 113 | 124 |  | 69.4127 | 104.1827 | [7 empty] | CATEGORYB | SINGLE | ALBION - PETERSBURG 115KV CKT 1 | 0 | 640054 | ALBION 7 115.00 | 640318 | PETRSBG7 115.00 | 0 |  | 1 |  | 118 |  | NPPD | PETERSBURG - MADISON 115KV CKT 1 | Build new 35 mile 115 kV line from Petersburg to Madison | 288 | 288 |  |  |  | 48 | 48 |  | 0.02568 | 0.18086 | 0.0285 |  | 28000000 | 2010-04-01 | [38 empty] | 2011-12-01 | 2015-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T4245512SP | TO->FROM | NELIGH - PETERSBURG 115KV CKT 1 | CP | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640318 | PETRSBG7 115.00 | 640293 | NELIGH 7 115.00 | 0 |  | 1 | 12SP | 113 | 113 | 124 |  | 69.0329 | 103.5992 | [7 empty] | CATEGORYB | SINGLE | ALBION - PETERSBURG 115KV CKT 1 | 0 | 640054 | ALBION 7 115.00 | 640318 | PETRSBG7 115.00 | 0 |  | 1 |  | 118 |  | NPPD | PETERSBURG - MADISON 115KV CKT 1 | Build new 35 mile 115 kV line from Petersburg to Madison | 288 | 288 |  |  |  | 48 | 48 |  | 0.02568 | 0.18086 | 0.0285 |  | 28000000 | 2010-04-01 | [38 empty] | 2011-12-01 | 2015-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1805512WP | TO->FROM | NELIGH - PETERSBURG 115KV CKT 1 | CP | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640318 | PETRSBG7 115.00 | 640293 | NELIGH 7 115.00 | 0 |  | 1 | 12WP | 113 | 113 | 124 |  | 69.1502 | 103.9344 | [7 empty] | CATEGORYB | SINGLE | ALBION - PETERSBURG 115KV CKT 1 | 0 | 640054 | ALBION 7 115.00 | 640318 | PETRSBG7 115.00 | 0 |  | 1 |  | 118 |  | NPPD | PETERSBURG - MADISON 115KV CKT 1 | Build new 35 mile 115 kV line from Petersburg to Madison | 288 | 288 |  |  |  | 48 | 48 |  | 0.02568 | 0.18086 | 0.0285 |  | 28000000 | 2010-04-01 | [38 empty] | 2011-12-01 | 2015-06-01
NA | [8 empty] | NAOKGE5148805153751 |  | NORTHWEST - WOODWARD 345KV CKT 1 | U | OKGE | OKGE | ENID | ENID | 0 | 514880 |  | 515407 |  |  |  | 1 |  | 2021 | 2325 | [12 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 kV | [12 empty] | 221000000 | [39 empty] | 2010-01-01 | 2010-01-01
NA | [8 empty] | NAOKGE5148805153751 |  | NORTHWEST - WOODWARD 345KV CKT 1 | U | OKGE | OKGE | ENID | ENID | 0 | 515407 |  | 515375 |  |  |  | 1 |  | 2021 | 2325 | [12 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | NORTHWEST - WOODWARD 345KV CKT 1 | Build 120 miles of 345 kV | [12 empty] | 221000000 | [39 empty] | 2010-01-01 | 2010-01-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T10165511SP | FROM->TO | NORTHWEST (NORTWST2) 345/138/13.8KV TRANSFORMER CKT 1 | CP | OKGE | OKGE |  |  | 2 | 514880 | NORTWST7 345.00 | 514879 | NORTWST4 138.00 | 515742 | NORTWS21 13.800 | 1 | 11SP | 493 | 493 | 0 | 96 | 95.9829 | 100.7242 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST (NORTWST3) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514879 | NORTWST4 138.00 | 514880 | NORTWST7 345.00 | 515743 | NORTWS31 13.800 | 1 |  | 497 |  | OKGE | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 Accelerated | Add 3rd 345/138KV Auto and convert the 345kV and 138kV to a breaker and a half configuration. | [5 empty] | 36 | 24 | [5 empty] | 13500000 | 2008-07-29 | [38 empty] | 2011-06-01 | 2014-06-01 | 2014-02-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T10165511SP | FROM->TO | NORTHWEST (NORTWST2) 345/138/13.8KV TRANSFORMER CKT 1 | CP | OKGE | OKGE |  |  | 2 | 514880 | NORTWST7 345.00 | 514879 | NORTWST4 138.00 | 515742 | NORTWS21 13.800 | 1 | 11SP | 493 | 493 | 0 | 96 | 95.9829 | 100.7242 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST (NORTWST3) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514879 | NORTWST4 138.00 | 514880 | NORTWST7 345.00 | 515743 | NORTWS31 13.800 | 1 |  | 497 |  | OKGE | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 Accelerated | Add 3rd 345/138KV Auto and convert the 345kV and 138kV to a breaker and a half configuration. | [5 empty] | 36 | 24 | [5 empty] | 13500000 | 2008-07-29 | [38 empty] | 2011-06-01 | 2014-06-01 | 2014-02-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T11095516SP | FROM->TO | NORTHWEST (NORTWST2) 345/138/13.8KV TRANSFORMER CKT 1 | CP | OKGE | OKGE |  |  | 2 | 514880 | NORTWST7 345.00 | 514879 | NORTWST4 138.00 | 515742 | NORTWS21 13.800 | 1 | 16SP | 493 | 493 | 0 |  | 94.8121 | 102.122 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST (NORTWST3) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514879 | NORTWST4 138.00 | 514880 | NORTWST7 345.00 | 515743 | NORTWS31 13.800 | 1 |  | 504 |  | OKGE | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 Accelerated | Add 3rd 345/138KV Auto and convert the 345kV and 138kV to a breaker and a half configuration. | [5 empty] | 36 | 24 | [5 empty] | 13500000 | 2008-07-29 | [38 empty] | 2011-06-01 | 2014-06-01 | 2014-02-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T11095516SP | FROM->TO | NORTHWEST (NORTWST2) 345/138/13.8KV TRANSFORMER CKT 1 | CP | OKGE | OKGE |  |  | 2 | 514880 | NORTWST7 345.00 | 514879 | NORTWST4 138.00 | 515742 | NORTWS21 13.800 | 1 | 16SP | 493 | 493 | 0 |  | 94.8121 | 102.122 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST (NORTWST3) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514879 | NORTWST4 138.00 | 514880 | NORTWST7 345.00 | 515743 | NORTWS31 13.800 | 1 |  | 504 |  | OKGE | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 Accelerated | Add 3rd 345/138KV Auto and convert the 345kV and 138kV to a breaker and a half configuration. | [5 empty] | 36 | 24 | [5 empty] | 13500000 | 2008-07-29 | [38 empty] | 2011-06-01 | 2014-06-01 | 2014-02-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T19075521SP | FROM->TO | NORTHWEST (NORTWST2) 345/138/13.8KV TRANSFORMER CKT 1 | S | OKGE | OKGE |  |  | 2 | 514880 | NORTWST7 345.00 | 514879 | NORTWST4 138.00 | 515742 | NORTWS21 13.800 | 1 | 21SP | 493 | 493 | 0 | 102.7 | 102.7355 | 105.764 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST (NORTWST3) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514879 | NORTWST4 138.00 | 514880 | NORTWST7 345.00 | 515743 | NORTWS31 13.800 | 1 |  | 522 |  | OKGE | NORTHWEST 345/138/13.8KV TRANSFORMER CKT 1 | Install third 345/138 kV Bus Tie in Northwest Sub | [5 empty] | 36 | [6 empty] | 15000000 | 2010-07-09 | [38 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T19075521SP | FROM->TO | NORTHWEST (NORTWST2) 345/138/13.8KV TRANSFORMER CKT 1 | S | OKGE | OKGE |  |  | 2 | 514880 | NORTWST7 345.00 | 514879 | NORTWST4 138.00 | 515742 | NORTWS21 13.800 | 1 | 21SP | 493 | 493 | 0 | 102.7 | 102.7355 | 105.764 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST (NORTWST3) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514879 | NORTWST4 138.00 | 514880 | NORTWST7 345.00 | 515743 | NORTWS31 13.800 | 1 |  | 522 |  | OKGE | NORTHWEST 345/138/13.8KV TRANSFORMER CKT 1 | Install third 345/138 kV Bus Tie in Northwest Sub | [5 empty] | 36 | [6 empty] | 15000000 | 2010-07-09 | [38 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T6605021SP | FROM->TO | OGALLALA 230/115KV TRANSFORMER CKT 1 | REL | NPPD | NPPD | NPPD_686 | BEPC_1628 | 0 | 640302 | OGALALA4 230.00 | 659132 | OGALALA7 115.00 | 0 |  | 1 | 21SP | 187 | 187 | 233.8 | 106.1 | 106.1048 | 105.7273 | [7 empty] | CATEGORYB | SINGLE | KEYSTONE - OGALLALLA 115KV CKT 1 | 0 | 640253 | KEYSTON7 115.00 | 659132 | OGALALA7 115.00 | 0 |  | 1 |  | 198 | MORE STUDY NEEDED. NPPD IS CONDUCTING A JOINT STUDY WITH TSGT TO ASSESS THE LOADING ISSUES ASSOCIATED WITH THE OGALLALA TRANSFORMER AND THE NETS REGION. | NPPD | OGALLALA 230/115KV TRANSFORMER CKT 1 | Replace 187MVA Ogallala transformer with 336MVA Ogallala transformer |  | 336 | [50 empty] | 2017-06-01 | 2017-06-01
GEN-2006-010 | Turk | [7 empty] | GEN-2006-010AEPW5074545074281 |  | OKAY - TURK 138KV CKT 1 | U | AEPW | AEPW | SARK | SARK | 0 | 507454 | HEMPSTD4 138.00 | 507428 | OKAY 4 138.00 | 0 |  | 1 |  | 368 | 512 |  | 175.2 | [10 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | AEPW | OKAY - TURK 138KV CKT 1 | Build two mile, 138 kV, 1590ACSR line section from Turk Sub to existing Okay-Hope 115 kV line and rebuild twelve miles of 115 kV line to Okay Sub to 138 kV, 1590 ACSR , to form a Turk-Okay 138 kV line | [11 empty] | 9190000 | 9190000 | [39 empty] | 2012-07-01 | 2012-07-01
GEN-2006-010 | Turk | [7 empty] | GEN-2006-010AEPW5074285074275074421 |  | OKAY 138/69KV TRANSFORMER CKT 1 | U | AEPW | AEPW | SARK | SARK | 1 | 507428 | OKAY 4 138.00 | 507427 | OKAY 2 69.000 | 507442 |  | 1 |  | 150 | 174 |  | 57.8 | [10 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | AEPW | OKAY 138/69KV TRANSFORMER CKT 1 | Replace three single-phase 115-69 kV autotransformers with one 90 MVA, three-phase 138-69 kV autotransformer and convert high side of station to 138 kV | [11 empty] | 3400000 | 3400000 | [39 empty] | 2012-07-01 | 2012-07-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T4935021SP | TO->FROM | OMHUFFYT - OMPA-PONCA CITY 69KV CKT 1 | REL | OMPA | OMPA | DOE | DOE | 0 | 529251 | OMRIGGS 69.000 | 529242 | OMHUFFYT 69.000 | 0 |  | 1 | 21SP | 95 | 95 | 0 | 111.3 | 111.3375 | 106.2525 | [7 empty] | CATEGORYB | SINGLE | OMNWESTT - OMPA-PONCA CITY 69KV CKT 1 | 0 | 529243 | OMNWESTT 69.000 | 529251 | OMRIGGS 69.000 | 0 |  | 1 |  | 101 |  | OMPA | OMHUFFYT - OMPA-PONCA CITY 69KV CKT 1 | Breaker CT | 143 | 143 |  |  |  | 9 | [5 empty] | Upgrades must be made in off peak months | 2000 | 2010-09-21 | [38 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T4905021SP | FROM->TO | OMKAWS - OMPECANT 69KV CKT 1 | REL | OMPA | OMPA | DOE | DOE | 0 | 529246 | OMKAWS 69.000 | 529248 | OMPECANT 69.000 | 0 |  | 1 | 21SP | 92 | 92 | 0 | 107.6 | 107.5913 | 101.9646 | [7 empty] | CATEGORYB | SINGLE | OMHUFFYT - OMPA-PONCA CITY 69KV CKT 1 | 0 | 529242 | OMHUFFYT 69.000 | 529251 | OMRIGGS 69.000 | 0 |  | 1 |  | 94 |  | OMPA | OMKAWS - OMPECANT 69KV CKT 1 | Breaker CT | 143 | 143 |  |  |  | 9 | [5 empty] | Upgrades must be made in off peak months | 2000 | 2010-09-21 | [38 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T4895021SP | TO->FROM | OMNWESTT - OMPA-PONCA CITY 69KV CKT 1 | REL | OMPA | OMPA | DOE | DOE | 0 | 529251 | OMRIGGS 69.000 | 529243 | OMNWESTT 69.000 | 0 |  | 1 | 21SP | 92 | 92 | 0 | 114.9 | 114.9467 | 109.5911 | [7 empty] | CATEGORYB | SINGLE | OMHUFFYT - OMPA-PONCA CITY 69KV CKT 1 | 0 | 529242 | OMHUFFYT 69.000 | 529251 | OMRIGGS 69.000 | 0 |  | 1 |  | 101 |  | OMPA | OMNWESTT - OMPA-PONCA CITY 69KV CKT 1 | Breaker CT | 143 | 143 |  |  |  | 9 | [5 empty] | Upgrades must be made in off peak months | 2000 | 2010-09-21 | [38 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61V4245521SP |  | OMPA-FAIRVIEW 69KV | REL | OMPA |  | DOE |  |  | 529343 | OMFAIRV2 69.000 | [5 empty] | 21SP | [7 empty] | 0.86147 | 0.86147 | 0.7869 | 0.96435 | 0.9 | 1.05 | CATEGORYB | SINGLE | FAIRVIEW - OKEENE 69KV CKT 1 | 0 | 521015 | OKEENE 2 69.000 | 520909 | FAIRVEW2 69.000 | 0 |  | 1 |  |  |  | WFEC | FAIRVIEW Capacitor 69KV | Install 18 Mvar capacitor at Fairview 69kV bus. | [52 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T1805016SP | FROM->TO | OSAGE SWITCHING STATION - SOUTH GEORGIA INTERCHANGE 115KV CKT 1 | REL | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524345 | OSAGE 3115.00 | 524322 | GEORGIA 3115.00 | 0 |  | 1 | 16SP | 160 | 160 | 0 | 101.1 | 101.1141 | 101.4663 | [7 empty] | CATEGORYB | SINGLE | CHERRY SUB - NORTHWEST INTERCHANGE 115KV CKT 1 | 0 | 524009 | CHERRY 3115.00 | 524106 | NORTHWEST 3115.00 | 0 |  | 1 |  | 163 |  | SPS | OSAGE - RANDALL 115KV CKT 1 | Osage station & line reterminations with a new 2 mile 115 kV line from Randall Co | [52 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T14915016SP | FROM->TO | OSAGE SWITCHING STATION - SOUTH GEORGIA INTERCHANGE 115KV CKT 1 | REL | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524345 | OSAGE 3115.00 | 524322 | GEORGIA 3115.00 | 0 |  | 1 | 16SP | 160 | 160 | 0 | 100.9 | 100.9361 | 101.2888 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-V28 | 0 | 0 |  | 0 |  | 0 |  |  |  | 163 |  | SPS | OSAGE - RANDALL 115KV CKT 1 | Osage station & line reterminations with a new 2 mile 115 kV line from Randall Co | [52 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T3815021SP | FROM->TO | OSAGE SWITCHING STATION - SOUTH GEORGIA INTERCHANGE 115KV CKT 1 | REL | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524345 | OSAGE 3115.00 | 524322 | GEORGIA 3115.00 | 0 |  | 1 | 21SP | 160 | 160 | 0 | 121.8 | 121.7862 | 122.1188 | [7 empty] | CATEGORYB | SINGLE | CHERRY SUB - NORTHWEST INTERCHANGE 115KV CKT 1 | 0 | 524009 | CHERRY 3115.00 | 524106 | NORTHWEST 3115.00 | 0 |  | 1 |  | 196 |  | SPS | OSAGE - RANDALL 115KV CKT 1 | Osage station & line reterminations with a new 2 mile 115 kV line from Randall Co | [52 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T26405021SP | FROM->TO | OSAGE SWITCHING STATION - SOUTH GEORGIA INTERCHANGE 115KV CKT 1 | REL | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524345 | OSAGE 3115.00 | 524322 | GEORGIA 3115.00 | 0 |  | 1 | 21SP | 160 | 160 | 0 | 121 | 120.9615 | 121.288 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-V28 | 0 | 0 |  | 0 |  | 0 |  |  |  | 195 |  | SPS | OSAGE - RANDALL 115KV CKT 1 | Osage station & line reterminations with a new 2 mile 115 kV line from Randall Co | [52 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T4095021SP | FROM->TO | OSAGE SWITCHING STATION - SOUTH GEORGIA INTERCHANGE 115KV CKT 1 | REL | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524345 | OSAGE 3115.00 | 524322 | GEORGIA 3115.00 | 0 |  | 1 | 21SP | 160 | 160 | 0 | 111.9 | 111.946 | 112.0658 | [7 empty] | CATEGORYB | SINGLE | AMARILLO SOUTH INTERCHANGE 230/115KV TRANSFORMER CKT 1 | 0 | 524414 | AMA_SOUTH 3115.00 | 524415 | AMA_SOUTH 6230.00 | 0 |  | 1 |  | 180 |  | SPS | OSAGE - RANDALL 115KV CKT 1 | Osage station & line reterminations with a new 2 mile 115 kV line from Randall Co | [52 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T8645511SP | FROM->TO | PARAGOULD (PRG X2) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA | SWPA | EMINTH | EMINTH | 2 | 505412 | PARAGLD5 161.00 | 505414 | PARAGLD2 69.000 | 505413 | PRG X2 1 13.800 | 1 | 11SP | 42 | 42 | 0 |  | 93.8898 | 103.0323 | [7 empty] | CATEGORYB | SINGLE | PARAGOULD (PRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505412 | PARAGLD5 161.00 | 505414 | PARAGLD2 69.000 | 505411 | PRG X1 1 13.800 | 1 |  | 44 | Xfmr 1 will be replaced by 11SP. Load is expected to shift from Paragould to Center Hill, which will have an additional xfmr. That may negate the need of replacing xfmr #2. | SWPA | XFR - Paragould 161/69 kV Auto 1 & 2 | Replace Paragould auto transformers 1 and 2 with 70 MVA units. | 70 | 70 |  |  |  | 24 | 24 | [5 empty] | 3150000 | [39 empty] | 2011-06-01 | 2013-06-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T8655511SP | FROM->TO | PARAGOULD (PRG X3) 161/69/13.8KV TRANSFORMER CKT 1 | REL | SWPA | SWPA | EMINTH | EMINTH | 2 | 505412 | PARAGLD5 161.00 | 505414 | PARAGLD2 69.000 | 505415 | PRG X3 1 13.800 | 1 | 11SP | 42 | 42 | 0 |  | 93.7431 | 102.8714 | [7 empty] | CATEGORYB | SINGLE | PARAGOULD (PRG X1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 505412 | PARAGLD5 161.00 | 505414 | PARAGLD2 69.000 | 505411 | PRG X1 1 13.800 | 1 |  | 44 | Xfmr 1 will be replaced by 11SP. Load is expected to shift from Paragould to Center Hill, which will have an additional xfmr. That may negate the need of replacing xfmr #2. | SWPA | XFR - Paragould 161/69 kV Auto 1 & 2 | Replace Paragould auto transformers 1 and 2 with 70 MVA units. | 70 | 70 |  |  |  | 24 | 24 | [5 empty] | 3150000 | [39 empty] | 2011-06-01 | 2013-06-01 | 2012-10-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1345516SP | FROM->TO | PIRKEY - WHITNEY 138KV CKT 1 | REL | AEPW | AEPW | LONG-MAR | LONG-MAR | 0 | 508562 | PIRKEY 4 138.00 | 508575 | WHITNEY4 138.00 | 0 |  | 1 | 16SP | 430 | 473 | 0 | 100.7 | 100.6831 | 101.5534 | [7 empty] | CATEGORYB | SINGLE | EASTON REC - PIRKEY 138KV CKT 1 | 0 | 508562 | PIRKEY 4 138.00 | 509092 | EASTON 4 138.00 | 0 |  | 1 |  | 481 |  | AEPW | PIRKEY - WHITNEY 138KV CKT 1 | Reset CT, Replace Breaker and Switch | [52 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1265516SP | FROM->TO | PIRKEY - WHITNEY 138KV CKT 1 | REL | AEPW | AEPW | LONG-MAR | LONG-MAR | 0 | 508562 | PIRKEY 4 138.00 | 508575 | WHITNEY4 138.00 | 0 |  | 1 | 16SP | 430 | 473 | 0 | 99.9 | 99.943 | 100.8125 | [7 empty] | CATEGORYB | SINGLE | EASTON REC - KNOX LEE 138KV CKT 1 | 0 | 508548 | KNOXLEE4 138.00 | 509092 | EASTON 4 138.00 | 0 |  | 1 |  | 477 |  | AEPW | PIRKEY - WHITNEY 138KV CKT 1 | Reset CT, Replace Breaker and Switch | [52 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61V5835516SP |  | REEDING 69KV | REL | WFEC |  | AEP-IM |  |  | 521037 | REEDING2 69.000 | [5 empty] | 16SP | [7 empty] | 0.88214 | 0.88214 | 0.85536 | 0.94693 | 0.9 | 1.05 | CATEGORYB | SINGLE | DOVER SW (DOVER) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 520882 | DOVERSW4 138.00 | 520881 | DOVERSW2 69.000 | 521166 | DVRTERT 13.800 | 1 |  |  |  | WFEC | East Kingfisher Capacitor 69 kV | Install 18 Mvar capacitor at East Kingfisher bus. | [52 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2405011SP | FROM->TO | RICHLAND - UDALL 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533550 | RICHLAN2 69.000 | 533559 | UDALL 2 69.000 | 0 |  | 1 | 11SP | 43 | 43 | 0 |  | 77.6312 | 109.1103 | [7 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  | 47 |  | WERE | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | Tear down / Rebuild 11.63-mile Timber Tap-Winfield 69 kV line, 954 ACSR | 72 | 72 | 72 | 72 | 11.63 | 18 | 6 |  | 0.0309 | 0.2101 | 0.05164 | Line switches limit to 72 MVA. $790k per mile | 8161986 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2405011SP | FROM->TO | RICHLAND - UDALL 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533550 | RICHLAN2 69.000 | 533559 | UDALL 2 69.000 | 0 |  | 1 | 11SP | 43 | 43 | 0 |  | 77.6312 | 109.1103 | [7 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  | 47 |  | WERE | RICHLAND - UDALL 69KV CKT 1 | Tear down / Rebuild 8.48-mile Richland-Udall 69 kV line using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 8.48 | 13 | 7 | N | 0.01789 | 0.12177 | 0.02589 | MVA limit is conductor $790k per mile | 6699200 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2405011SP | FROM->TO | RICHLAND - UDALL 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533550 | RICHLAN2 69.000 | 533559 | UDALL 2 69.000 | 0 |  | 1 | 11SP | 43 | 43 | 0 |  | 77.6312 | 109.1103 | [7 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  | 47 |  | WERE | TIMBER JUNCTION - UDALL 69KV CKT 1 | Tear down / Rebuild Udall-Timber Jct 69 kV using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 2.01 | 4 | 2 | N | 0.00424 | 0.02886 | 0.00614 | MVA limit is conductor $790k per mile | 1587900 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2405011SP | FROM->TO | RICHLAND - UDALL 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533550 | RICHLAN2 69.000 | 533559 | UDALL 2 69.000 | 0 |  | 1 | 11SP | 43 | 43 | 0 |  | 77.6312 | 109.1103 | [7 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  | 47 |  | WERE | BELL - PECK 69KV CKT 1 | Tear down / Rebuild 8.23 mile Bell-Peck 69 kV line with 1192 ACSR and replace CT | 134 | 147 | 134 | 147 | 8.23 | 18 | 5 | N |  |  |  | $790k per mile and $200k for CT | 6701700 | 2010-01-01 | [38 empty] | 2012-06-01 | 2012-12-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2695012SP | FROM->TO | RICHLAND - UDALL 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533550 | RICHLAN2 69.000 | 533559 | UDALL 2 69.000 | 0 |  | 1 | 12SP | 43 | 43 | 0 |  | 87.3122 | 116.9425 | [7 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  | 51 |  | WERE | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | Tear down / Rebuild 11.63-mile Timber Tap-Winfield 69 kV line, 954 ACSR | 72 | 72 | 72 | 72 | 11.63 | 18 | 6 |  | 0.0309 | 0.2101 | 0.05164 | Line switches limit to 72 MVA. $790k per mile | 8161986 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2695012SP | FROM->TO | RICHLAND - UDALL 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533550 | RICHLAN2 69.000 | 533559 | UDALL 2 69.000 | 0 |  | 1 | 12SP | 43 | 43 | 0 |  | 87.3122 | 116.9425 | [7 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  | 51 |  | WERE | RICHLAND - UDALL 69KV CKT 1 | Tear down / Rebuild 8.48-mile Richland-Udall 69 kV line using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 8.48 | 13 | 7 | N | 0.01789 | 0.12177 | 0.02589 | MVA limit is conductor $790k per mile | 6699200 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2695012SP | FROM->TO | RICHLAND - UDALL 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533550 | RICHLAN2 69.000 | 533559 | UDALL 2 69.000 | 0 |  | 1 | 12SP | 43 | 43 | 0 |  | 87.3122 | 116.9425 | [7 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  | 51 |  | WERE | TIMBER JUNCTION - UDALL 69KV CKT 1 | Tear down / Rebuild Udall-Timber Jct 69 kV using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 2.01 | 4 | 2 | N | 0.00424 | 0.02886 | 0.00614 | MVA limit is conductor $790k per mile | 1587900 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2695012SP | FROM->TO | RICHLAND - UDALL 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533550 | RICHLAN2 69.000 | 533559 | UDALL 2 69.000 | 0 |  | 1 | 12SP | 43 | 43 | 0 |  | 87.3122 | 116.9425 | [7 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  | 51 |  | WERE | BELL - PECK 69KV CKT 1 | Tear down / Rebuild 8.23 mile Bell-Peck 69 kV line with 1192 ACSR and replace CT | 134 | 147 | 134 | 147 | 8.23 | 18 | 5 | N |  |  |  | $790k per mile and $200k for CT | 6701700 | 2010-01-01 | [38 empty] | 2012-06-01 | 2012-12-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T3265516SP | FROM->TO | RICHLAND - UDALL 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533550 | RICHLAN2 69.000 | 533559 | UDALL 2 69.000 | 0 |  | 1 | 16SP | 43 | 43 | 0 |  | 84.6553 | 109.5849 | [7 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  | 48 |  | WERE | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | Tear down / Rebuild 11.63-mile Timber Tap-Winfield 69 kV line, 954 ACSR | 72 | 72 | 72 | 72 | 11.63 | 18 | 6 |  | 0.0309 | 0.2101 | 0.05164 | Line switches limit to 72 MVA. $790k per mile | 8161986 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T3265516SP | FROM->TO | RICHLAND - UDALL 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533550 | RICHLAN2 69.000 | 533559 | UDALL 2 69.000 | 0 |  | 1 | 16SP | 43 | 43 | 0 |  | 84.6553 | 109.5849 | [7 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  | 48 |  | WERE | RICHLAND - UDALL 69KV CKT 1 | Tear down / Rebuild 8.48-mile Richland-Udall 69 kV line using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 8.48 | 13 | 7 | N | 0.01789 | 0.12177 | 0.02589 | MVA limit is conductor $790k per mile | 6699200 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T3265516SP | FROM->TO | RICHLAND - UDALL 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533550 | RICHLAN2 69.000 | 533559 | UDALL 2 69.000 | 0 |  | 1 | 16SP | 43 | 43 | 0 |  | 84.6553 | 109.5849 | [7 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  | 48 |  | WERE | TIMBER JUNCTION - UDALL 69KV CKT 1 | Tear down / Rebuild Udall-Timber Jct 69 kV using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 2.01 | 4 | 2 | N | 0.00424 | 0.02886 | 0.00614 | MVA limit is conductor $790k per mile | 1587900 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T3265516SP | FROM->TO | RICHLAND - UDALL 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533550 | RICHLAN2 69.000 | 533559 | UDALL 2 69.000 | 0 |  | 1 | 16SP | 43 | 43 | 0 |  | 84.6553 | 109.5849 | [7 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  | 48 |  | WERE | BELL - PECK 69KV CKT 1 | Tear down / Rebuild 8.23 mile Bell-Peck 69 kV line with 1192 ACSR and replace CT | 134 | 147 | 134 | 147 | 8.23 | 18 | 5 | N |  |  |  | $790k per mile and $200k for CT | 6701700 | 2010-01-01 | [38 empty] | 2012-06-01 | 2012-12-01 | 2012-10-01
2009-AGP2 | AFS6NC |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS6NC1T25521SP | FROM->TO | RICHLAND - UDALL 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533550 | RICHLAN2 69.000 | 533559 | UDALL 2 69.000 | 0 |  | 1 | 21SP | 43 | 43 | 0 | 96.9556 | 96.9556 | 110.9347 | [7 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  | 48 |  | WERE | RICHLAND - UDALL 69KV CKT 1 | Tear down / Rebuild 8.48-mile Richland-Udall 69 kV line using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 8.48 | 13 | 7 | N | 0.01789 | 0.12177 | 0.02589 | MVA limit is conductor $790k per mile | 6699200 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6NC |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS6NC1T25521SP | FROM->TO | RICHLAND - UDALL 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533550 | RICHLAN2 69.000 | 533559 | UDALL 2 69.000 | 0 |  | 1 | 21SP | 43 | 43 | 0 | 96.9556 | 96.9556 | 110.9347 | [7 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  | 48 |  | WERE | TIMBER JUNCTION - UDALL 69KV CKT 1 | Tear down / Rebuild Udall-Timber Jct 69 kV using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 2.01 | 4 | 2 | N | 0.00424 | 0.02886 | 0.00614 | MVA limit is conductor $790k per mile | 1587900 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6NC |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS6NC1T25521SP | FROM->TO | RICHLAND - UDALL 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533550 | RICHLAN2 69.000 | 533559 | UDALL 2 69.000 | 0 |  | 1 | 21SP | 43 | 43 | 0 | 96.9556 | 96.9556 | 110.9347 | [7 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  | 48 |  | WERE | TIMBER JUNCTION - UDALL 69KV CKT 1 | Tear down / Rebuild Udall-Timber Jct 69 kV using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 2.01 | 4 | 2 | N | 0.00424 | 0.02886 | 0.00614 | MVA limit is conductor $790k per mile | 1587900 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6NC |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS6NC1T25521SP | FROM->TO | RICHLAND - UDALL 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533550 | RICHLAN2 69.000 | 533559 | UDALL 2 69.000 | 0 |  | 1 | 21SP | 43 | 43 | 0 | 96.9556 | 96.9556 | 110.9347 | [7 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  | 48 |  | WERE | BELL - PECK 69KV CKT 1 | Tear down / Rebuild 8.23 mile Bell-Peck 69 kV line with 1192 ACSR and replace CT | 134 | 147 | 134 | 147 | 8.23 | 18 | 5 | N |  |  |  | $790k per mile and $200k for CT | 6701700 | 2010-01-01 | [38 empty] | 2012-06-01 | 2012-12-01 | 2012-10-01
2009-AGP2 | AFS6NC |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS6NC1T25521SP | FROM->TO | RICHLAND - UDALL 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533550 | RICHLAN2 69.000 | 533559 | UDALL 2 69.000 | 0 |  | 1 | 21SP | 43 | 43 | 0 | 96.9556 | 96.9556 | 110.9347 | [7 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  | 48 |  | WERE | BELL - PECK 69KV CKT 1 | Tear down / Rebuild 8.23 mile Bell-Peck 69 kV line with 1192 ACSR and replace CT | 134 | 147 | 134 | 147 | 8.23 | 18 | 5 | N |  |  |  | $790k per mile and $200k for CT | 6701700 | 2010-01-01 | [38 empty] | 2012-06-01 | 2012-12-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T5375021SP | FROM->TO | RICHLAND - UDALL 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533550 | RICHLAN2 69.000 | 533559 | UDALL 2 69.000 | 0 |  | 1 | 21SP | 43 | 43 | 0 |  | 86.6768 | 103.8313 | [7 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  | 45 |  | WERE | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | Tear down / Rebuild 11.63-mile Timber Tap-Winfield 69 kV line, 954 ACSR | 72 | 72 | 72 | 72 | 11.63 | 18 | 6 |  | 0.0309 | 0.2101 | 0.05164 | Line switches limit to 72 MVA. $790k per mile | 8161986 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T5375021SP | FROM->TO | RICHLAND - UDALL 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533550 | RICHLAN2 69.000 | 533559 | UDALL 2 69.000 | 0 |  | 1 | 21SP | 43 | 43 | 0 |  | 86.6768 | 103.8313 | [7 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  | 45 |  | WERE | RICHLAND - UDALL 69KV CKT 1 | Tear down / Rebuild 8.48-mile Richland-Udall 69 kV line using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 8.48 | 13 | 7 | N | 0.01789 | 0.12177 | 0.02589 | MVA limit is conductor $790k per mile | 6699200 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T5375021SP | FROM->TO | RICHLAND - UDALL 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533550 | RICHLAN2 69.000 | 533559 | UDALL 2 69.000 | 0 |  | 1 | 21SP | 43 | 43 | 0 |  | 86.6768 | 103.8313 | [7 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  | 45 |  | WERE | TIMBER JUNCTION - UDALL 69KV CKT 1 | Tear down / Rebuild Udall-Timber Jct 69 kV using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 2.01 | 4 | 2 | N | 0.00424 | 0.02886 | 0.00614 | MVA limit is conductor $790k per mile | 1587900 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T5375021SP | FROM->TO | RICHLAND - UDALL 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533550 | RICHLAN2 69.000 | 533559 | UDALL 2 69.000 | 0 |  | 1 | 21SP | 43 | 43 | 0 |  | 86.6768 | 103.8313 | [7 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  | 45 |  | WERE | BELL - PECK 69KV CKT 1 | Tear down / Rebuild 8.23 mile Bell-Peck 69 kV line with 1192 ACSR and replace CT | 134 | 147 | 134 | 147 | 8.23 | 18 | 5 | N |  |  |  | $790k per mile and $200k for CT | 6701700 | 2010-01-01 | [38 empty] | 2012-06-01 | 2012-12-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61V2105511SP |  | RINGWOOD 69KV | PL | WFEC |  | AEP-IM |  |  | 521040 | RNGWOOD2 69.000 | [5 empty] | 11SP | [8 empty] | 0.93855 | 0.88948 | 0.94402 | 0.9 | 1.05 | CATEGORYB | SINGLE | TATONGA7 345.00 - WWRDEHV7 345.00 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61V6595511SP |  | RINGWOOD 69KV | PL | WFEC |  | AEP-IM |  |  | 521040 | RNGWOOD2 69.000 | [5 empty] | 11SP | [8 empty] | 0.93882 | 0.88975 | 0.94402 | 0.9 | 1.05 | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515376 | WWRDEHV4 138.00 | 515375 | WWRDEHV7 345.00 | 515795 | WWDEHV31 13.800 | 1 |  |  |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61V2055511SP |  | RINGWOOD 69KV | PL | WFEC |  | AEP-IM |  |  | 521040 | RNGWOOD2 69.000 | [5 empty] | 11SP | [8 empty] | 0.93953 | 0.89158 | 0.94402 | 0.9 | 1.05 | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 515407 | TATONGA7 345.00 | 514880 | NORTWST7 345.00 | 0 |  | 1 |  |  |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61V2045512SP |  | RINGWOOD 69KV | PL | WFEC |  | AEP-IM |  |  | 521040 | RNGWOOD2 69.000 | [5 empty] | 12SP | [8 empty] | 0.93793 | 0.88747 | 0.93872 | 0.9 | 1.05 | CATEGORYB | SINGLE | TATONGA7 345.00 - WWRDEHV7 345.00 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61V5845512SP |  | RINGWOOD 69KV | PL | WFEC |  | AEP-IM |  |  | 521040 | RNGWOOD2 69.000 | [5 empty] | 12SP | [8 empty] | 0.93822 | 0.88772 | 0.93872 | 0.9 | 1.05 | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515376 | WWRDEHV4 138.00 | 515375 | WWRDEHV7 345.00 | 515795 | WWDEHV31 13.800 | 1 |  |  |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61V1955512SP |  | RINGWOOD 69KV | PL | WFEC |  | AEP-IM |  |  | 521040 | RNGWOOD2 69.000 | [5 empty] | 12SP | [8 empty] | 0.939 | 0.88933 | 0.93872 | 0.9 | 1.05 | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 515407 | TATONGA7 345.00 | 514880 | NORTWST7 345.00 | 0 |  | 1 |  |  |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61V4225521SP |  | RINGWOOD JCT 69KV | REL | WFEC |  | AEP-IM |  |  | 521039 | RNGWODJ2 69.000 | [5 empty] | 21SP | [7 empty] | 0.87811 | 0.87811 | 0.81026 | 0.96021 | 0.9 | 1.05 | CATEGORYB | SINGLE | FAIRVIEW - OKEENE 69KV CKT 1 | 0 | 521015 | OKEENE 2 69.000 | 520909 | FAIRVEW2 69.000 | 0 |  | 1 |  |  |  | WFEC | FAIRVIEW Capacitor 69KV | Install 18 Mvar capacitor at Fairview 69kV bus. | [52 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T10295511SP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | PL | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 11SP | 133 | 153 | 0 |  | 57.604 | 109.0472 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  | 167 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T10295511SP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | PL | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 11SP | 133 | 153 | 0 |  | 57.604 | 109.0472 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  | 167 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1915511SP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | PL | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 11SP | 133 | 153 | 0 |  | 57.5604 | 109.0099 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WWRDEHV7 345.00 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 167 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1915511SP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | PL | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 11SP | 133 | 153 | 0 |  | 57.5604 | 109.0099 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WWRDEHV7 345.00 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 167 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1805511SP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | PL | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 11SP | 133 | 153 | 0 |  | 57.307 | 108.5195 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 167 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1805511SP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | PL | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 11SP | 133 | 153 | 0 |  | 57.307 | 108.5195 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 167 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T11155512SP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | PL | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 12SP | 133 | 153 | 0 |  | 59.5842 | 106.7445 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  | 164 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T11155512SP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | PL | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 12SP | 133 | 153 | 0 |  | 59.5842 | 106.7445 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  | 164 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T2165512SP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | PL | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 12SP | 133 | 153 | 0 |  | 59.544 | 106.706 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WWRDEHV7 345.00 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 164 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T2165512SP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | PL | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 12SP | 133 | 153 | 0 |  | 59.544 | 106.706 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WWRDEHV7 345.00 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 164 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T2035512SP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | PL | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 12SP | 133 | 153 | 0 |  | 59.2821 | 106.2063 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 163 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T2035512SP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | PL | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 12SP | 133 | 153 | 0 |  | 59.2821 | 106.2063 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 163 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T9055011SP | FROM->TO | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 1 | CP | WERE | WERE | SCENTRAL | SCENTRAL | 2 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532826 | ROSEH1 1 13.800 | 1 | 11SP | 400 | 440 | 500 | 103.8 | 103.8082 | 109.1713 | [7 empty] | CATEGORYB | SINGLE | ROSE HILL (ROSEHL3X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532827 | ROSEH3 1 13.800 | 1 |  | 481 | Add third 345-138 kV transformer at Rose Hill | WERE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 | Add third 345-138 kV transformer at Rose Hill | 400 | 440 | 400 | 440 | 0 | 24 | 2 | Y |  |  |  | Like existing Rose Hill 345-138 units | 8100000 | 2009-01-01 | [38 empty] | 2011-06-01 | 2013-06-15 | 2012-04-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T6735011WP | FROM->TO | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 1 | CP | WERE | WERE | SCENTRAL | SCENTRAL | 2 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532826 | ROSEH1 1 13.800 | 1 | 11WP | 400 | 440 | 500 | 97 | 96.9633 | 100.8433 | [7 empty] | CATEGORYB | SINGLE | ROSE HILL (ROSEHL3X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532827 | ROSEH3 1 13.800 | 1 |  | 444 | Add third 345-138 kV transformer at Rose Hill | WERE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 | Add third 345-138 kV transformer at Rose Hill | 400 | 440 | 400 | 440 | 0 | 24 | 2 | Y |  |  |  | Like existing Rose Hill 345-138 units | 8100000 | 2009-01-01 | [38 empty] | 2011-06-01 | 2013-06-15 | 2012-04-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T9035011SP | FROM->TO | ROSE HILL (ROSEHL3X) 345/138/13.8KV TRANSFORMER CKT 1 | CP | WERE | WERE | SCENTRAL | SCENTRAL | 2 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532827 | ROSEH3 1 13.800 | 1 | 11SP | 400 | 440 | 500 | 103.9 | 103.8537 | 109.2192 | [7 empty] | CATEGORYB | SINGLE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532826 | ROSEH1 1 13.800 | 1 |  | 481 | Add third 345-138 kV transformer at Rose Hill | WERE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 | Add third 345-138 kV transformer at Rose Hill | 400 | 440 | 400 | 440 | 0 | 24 | 2 | Y |  |  |  | Like existing Rose Hill 345-138 units | 8100000 | 2009-01-01 | [38 empty] | 2011-06-01 | 2013-06-15 | 2012-04-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T6715011WP | FROM->TO | ROSE HILL (ROSEHL3X) 345/138/13.8KV TRANSFORMER CKT 1 | CP | WERE | WERE | SCENTRAL | SCENTRAL | 2 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532827 | ROSEH3 1 13.800 | 1 | 11WP | 400 | 440 | 500 | 97 | 97.0062 | 100.8882 | [7 empty] | CATEGORYB | SINGLE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532826 | ROSEH1 1 13.800 | 1 |  | 444 | Add third 345-138 kV transformer at Rose Hill | WERE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 3 | Add third 345-138 kV transformer at Rose Hill | 400 | 440 | 400 | 440 | 0 | 24 | 2 | Y |  |  |  | Like existing Rose Hill 345-138 units | 8100000 | 2009-01-01 | [38 empty] | 2011-06-01 | 2013-06-15 | 2012-04-01
GEN-2006-010 | Turk | [7 empty] | GEN-2006-010AEPW5074545080781 |  | SE TEXARKANA - TURK 138KV CKT 1 | U | AEPW | AEPW | SARK | TEXARK | 0 | 507454 | HEMPSTD4 138.00 | 508078 | SETEXAR4 138.00 | 0 |  | 1 |  | 368 | 512 |  | 125.3 | [10 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | AEPW | SE TEXARKANA - TURK 138KV CKT 1 | Build new Turk-SE Texarkana 138 kV line and add SE Texarkana 138 kV terminal. | [11 empty] | 26850000 | 26850000 | [39 empty] | 2012-07-01 | 2012-07-01
2009-AGP2 | AFS6 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2835012SP | FROM->TO | SEVENTEENTH (17TH 4X) 138/69/11.295KV TRANSFORMER CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 1 | 533064 | 17TH 4 138.00 | 533840 | 17TH 2 69.000 | 533112 | 17TH 4 1 11.295 | 1 | 12SP | 150 | 165 | 187.5 | 100.2 | 100.1819 | 101.3877 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  | 168 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 | CONT-0602 - Chisholm #1 138-69kV XFMR | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T9325012SP | FROM->TO | SEVENTEENTH (17TH 4X) 138/69/11.295KV TRANSFORMER CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 1 | 533064 | 17TH 4 138.00 | 533840 | 17TH 2 69.000 | 533112 | 17TH 4 1 11.295 | 1 | 12SP | 150 | 165 | 187.5 | 99.9 | 99.9331 | 101.3629 | [7 empty] | CATEGORYB | SINGLE | CHISHOLM (CHISLM1X) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 533035 | CHISHLM4 138.00 | 533786 | CHISHLM2 69.000 | 533103 | CHISOLM1 13.200 | 1 |  | 168 |  |  | Priority Projects | [53 empty] | 2010-10-01 | 2015-01-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T2905512SP | FROM->TO | SEWARD - SEWRDMW3 115KV CKT 1 | CP | SUNC | MIDW |  | REG E-IL | 0 | 539692 | SEWARD 3 115.00 | 530679 | SEWRDMW3 115.00 | 0 |  | 1 | 12SP | 60 | 60 | 0 | 101.2 | 101.2484 | 103.6219 | [7 empty] | CATEGORYB | SINGLE | HEIZER 6 230.00 - MULLERGREN 230KV CKT 1 | 0 | 530680 | HEIZER 6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 |  | 63 |  | MKEC | HEIZER - MULLERGREN 115 KV CKT 1 MKEC | Construct approximately one mile of 115-kV transmission line from the Great Bend (Mullergren) generation station to Heizer Substation with 795 ACSR conductor | 165 | 178 | 165 | 178 | 1 | [7 empty] | 1000000 | 2010-03-05 | [38 empty] | 2011-06-01 | 2012-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T2905512SP | FROM->TO | SEWARD - SEWRDMW3 115KV CKT 1 | CP | SUNC | MIDW |  | REG E-IL | 0 | 539692 | SEWARD 3 115.00 | 530679 | SEWRDMW3 115.00 | 0 |  | 1 | 12SP | 60 | 60 | 0 | 101.2 | 101.2484 | 103.6219 | [7 empty] | CATEGORYB | SINGLE | HEIZER 6 230.00 - MULLERGREN 230KV CKT 1 | 0 | 530680 | HEIZER 6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 |  | 63 |  | MKEC | HEIZER - MULLERGREN 115 KV CKT 1 MKEC | Construct approximately one mile of 115-kV transmission line from the Great Bend (Mullergren) generation station to Heizer Substation with 795 ACSR conductor | 165 | 178 | 165 | 178 | 1 | [7 empty] | 1000000 | 2010-03-05 | [38 empty] | 2011-06-01 | 2012-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T2905512SP | FROM->TO | SEWARD - SEWRDMW3 115KV CKT 1 | CP | SUNC | MIDW |  | REG E-IL | 0 | 539692 | SEWARD 3 115.00 | 530679 | SEWRDMW3 115.00 | 0 |  | 1 | 12SP | 60 | 60 | 0 | 101.2 | 101.2484 | 103.6219 | [7 empty] | CATEGORYB | SINGLE | HEIZER 6 230.00 - MULLERGREN 230KV CKT 1 | 0 | 530680 | HEIZER 6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 |  | 63 |  | MIDW | HEIZER - MULLERGREN 115 KV CKT 1 MIDW | Install 115 kV bay at Heizer and update relaying equipment | 165 | 178 | 165 | 178 | 0.03 | 9 | 3 | New | 2.6627e-05 | 0.00017045 | 2.2765e-05 |  | 400000 | 2009-07-01 | [38 empty] | 2011-06-01 | 2011-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T11435512SP | FROM->TO | SEWARD - SEWRDMW3 115KV CKT 1 | CP | SUNC | MIDW |  | REG E-IL | 0 | 539692 | SEWARD 3 115.00 | 530679 | SEWRDMW3 115.00 | 0 |  | 1 | 12SP | 60 | 60 | 0 | 101.3 | 101.2532 | 103.5478 | [7 empty] | CATEGORYB | SINGLE | HEIZER 6 230.00 (HEIZER T1) 230/115/12.5KV TRANSFORMER CKT 1 | 1 | 530601 | HEIZER 3 115.00 | 530680 | HEIZER 6 230.00 | 530626 | HZRT1 1 12.500 | 1 |  | 63 |  | MKEC | HEIZER - MULLERGREN 115 KV CKT 1 MKEC | Construct approximately one mile of 115-kV transmission line from the Great Bend (Mullergren) generation station to Heizer Substation with 795 ACSR conductor | 165 | 178 | 165 | 178 | 1 | [7 empty] | 1000000 | 2010-03-05 | [38 empty] | 2011-06-01 | 2012-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T11435512SP | FROM->TO | SEWARD - SEWRDMW3 115KV CKT 1 | CP | SUNC | MIDW |  | REG E-IL | 0 | 539692 | SEWARD 3 115.00 | 530679 | SEWRDMW3 115.00 | 0 |  | 1 | 12SP | 60 | 60 | 0 | 101.3 | 101.2532 | 103.5478 | [7 empty] | CATEGORYB | SINGLE | HEIZER 6 230.00 (HEIZER T1) 230/115/12.5KV TRANSFORMER CKT 1 | 1 | 530601 | HEIZER 3 115.00 | 530680 | HEIZER 6 230.00 | 530626 | HZRT1 1 12.500 | 1 |  | 63 |  | MKEC | HEIZER - MULLERGREN 115 KV CKT 1 MKEC | Construct approximately one mile of 115-kV transmission line from the Great Bend (Mullergren) generation station to Heizer Substation with 795 ACSR conductor | 165 | 178 | 165 | 178 | 1 | [7 empty] | 1000000 | 2010-03-05 | [38 empty] | 2011-06-01 | 2012-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T11435512SP | FROM->TO | SEWARD - SEWRDMW3 115KV CKT 1 | CP | SUNC | MIDW |  | REG E-IL | 0 | 539692 | SEWARD 3 115.00 | 530679 | SEWRDMW3 115.00 | 0 |  | 1 | 12SP | 60 | 60 | 0 | 101.3 | 101.2532 | 103.5478 | [7 empty] | CATEGORYB | SINGLE | HEIZER 6 230.00 (HEIZER T1) 230/115/12.5KV TRANSFORMER CKT 1 | 1 | 530601 | HEIZER 3 115.00 | 530680 | HEIZER 6 230.00 | 530626 | HZRT1 1 12.500 | 1 |  | 63 |  | MIDW | HEIZER - MULLERGREN 115 KV CKT 1 MIDW | Install 115 kV bay at Heizer and update relaying equipment | 165 | 178 | 165 | 178 | 0.03 | 9 | 3 | New | 2.6627e-05 | 0.00017045 | 2.2765e-05 |  | 400000 | 2009-07-01 | [38 empty] | 2011-06-01 | 2011-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T4855521SP | FROM->TO | SEWARD - SEWRDMW3 115KV CKT 1 | CP | SUNC | MIDW |  | REG E-IL | 0 | 539692 | SEWARD 3 115.00 | 530679 | SEWRDMW3 115.00 | 0 |  | 1 | 21SP | 60 | 60 | 0 | 110.3 | 110.2719 | 101.7765 | [7 empty] | CATEGORYB | SINGLE | HEIZER 6 230.00 - MULLERGREN 230KV CKT 1 | 0 | 530680 | HEIZER 6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 |  | 62 |  | MKEC | HEIZER - MULLERGREN 115 KV CKT 1 MKEC | Construct approximately one mile of 115-kV transmission line from the Great Bend (Mullergren) generation station to Heizer Substation with 795 ACSR conductor | 165 | 178 | 165 | 178 | 1 | [7 empty] | 1000000 | 2010-03-05 | [38 empty] | 2011-06-01 | 2012-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T4855521SP | FROM->TO | SEWARD - SEWRDMW3 115KV CKT 1 | CP | SUNC | MIDW |  | REG E-IL | 0 | 539692 | SEWARD 3 115.00 | 530679 | SEWRDMW3 115.00 | 0 |  | 1 | 21SP | 60 | 60 | 0 | 110.3 | 110.2719 | 101.7765 | [7 empty] | CATEGORYB | SINGLE | HEIZER 6 230.00 - MULLERGREN 230KV CKT 1 | 0 | 530680 | HEIZER 6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 |  | 62 |  | MKEC | HEIZER - MULLERGREN 115 KV CKT 1 MKEC | Construct approximately one mile of 115-kV transmission line from the Great Bend (Mullergren) generation station to Heizer Substation with 795 ACSR conductor | 165 | 178 | 165 | 178 | 1 | [7 empty] | 1000000 | 2010-03-05 | [38 empty] | 2011-06-01 | 2012-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T4855521SP | FROM->TO | SEWARD - SEWRDMW3 115KV CKT 1 | CP | SUNC | MIDW |  | REG E-IL | 0 | 539692 | SEWARD 3 115.00 | 530679 | SEWRDMW3 115.00 | 0 |  | 1 | 21SP | 60 | 60 | 0 | 110.3 | 110.2719 | 101.7765 | [7 empty] | CATEGORYB | SINGLE | HEIZER 6 230.00 - MULLERGREN 230KV CKT 1 | 0 | 530680 | HEIZER 6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 |  | 62 |  | MIDW | HEIZER - MULLERGREN 115 KV CKT 1 MIDW | Install 115 kV bay at Heizer and update relaying equipment | 165 | 178 | 165 | 178 | 0.03 | 9 | 3 | New | 2.6627e-05 | 0.00017045 | 2.2765e-05 |  | 400000 | 2009-07-01 | [38 empty] | 2011-06-01 | 2011-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T19565521SP | FROM->TO | SEWARD - SEWRDMW3 115KV CKT 1 | CP | SUNC | MIDW |  | REG E-IL | 0 | 539692 | SEWARD 3 115.00 | 530679 | SEWRDMW3 115.00 | 0 |  | 1 | 21SP | 60 | 60 | 0 | 110.2 | 110.2461 | 101.6647 | [7 empty] | CATEGORYB | SINGLE | HEIZER 6 230.00 (HEIZER T1) 230/115/12.5KV TRANSFORMER CKT 1 | 1 | 530601 | HEIZER 3 115.00 | 530680 | HEIZER 6 230.00 | 530626 | HZRT1 1 12.500 | 1 |  | 61 |  | MKEC | HEIZER - MULLERGREN 115 KV CKT 1 MKEC | Construct approximately one mile of 115-kV transmission line from the Great Bend (Mullergren) generation station to Heizer Substation with 795 ACSR conductor | 165 | 178 | 165 | 178 | 1 | [7 empty] | 1000000 | 2010-03-05 | [38 empty] | 2011-06-01 | 2012-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T19565521SP | FROM->TO | SEWARD - SEWRDMW3 115KV CKT 1 | CP | SUNC | MIDW |  | REG E-IL | 0 | 539692 | SEWARD 3 115.00 | 530679 | SEWRDMW3 115.00 | 0 |  | 1 | 21SP | 60 | 60 | 0 | 110.2 | 110.2461 | 101.6647 | [7 empty] | CATEGORYB | SINGLE | HEIZER 6 230.00 (HEIZER T1) 230/115/12.5KV TRANSFORMER CKT 1 | 1 | 530601 | HEIZER 3 115.00 | 530680 | HEIZER 6 230.00 | 530626 | HZRT1 1 12.500 | 1 |  | 61 |  | MKEC | HEIZER - MULLERGREN 115 KV CKT 1 MKEC | Construct approximately one mile of 115-kV transmission line from the Great Bend (Mullergren) generation station to Heizer Substation with 795 ACSR conductor | 165 | 178 | 165 | 178 | 1 | [7 empty] | 1000000 | 2010-03-05 | [38 empty] | 2011-06-01 | 2012-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T19565521SP | FROM->TO | SEWARD - SEWRDMW3 115KV CKT 1 | CP | SUNC | MIDW |  | REG E-IL | 0 | 539692 | SEWARD 3 115.00 | 530679 | SEWRDMW3 115.00 | 0 |  | 1 | 21SP | 60 | 60 | 0 | 110.2 | 110.2461 | 101.6647 | [7 empty] | CATEGORYB | SINGLE | HEIZER 6 230.00 (HEIZER T1) 230/115/12.5KV TRANSFORMER CKT 1 | 1 | 530601 | HEIZER 3 115.00 | 530680 | HEIZER 6 230.00 | 530626 | HZRT1 1 12.500 | 1 |  | 61 |  | MIDW | HEIZER - MULLERGREN 115 KV CKT 1 MIDW | Install 115 kV bay at Heizer and update relaying equipment | 165 | 178 | 165 | 178 | 0.03 | 9 | 3 | New | 2.6627e-05 | 0.00017045 | 2.2765e-05 |  | 400000 | 2009-07-01 | [38 empty] | 2011-06-01 | 2011-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T2635511SP | FROM->TO | SEWRDMW3 (SEWARD T1) 115/69/12.5KV TRANSFORMER CKT 1 | CP | MIDW | MIDW | REG E-IL | REG E-IL | 1 | 530679 | SEWRDMW3 115.00 | 530565 | SEWARD 2 69.000 | 530631 | SWRD1 1 12.500 | 1 | 11SP | 40 | 44.8 | 0 | 129.3 | 129.2947 | 123.9412 | [7 empty] | CATEGORYB | SINGLE | HEIZER 6 230.00 - MULLERGREN 230KV CKT 1 | 0 | 530680 | HEIZER 6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 |  | 56 |  | MIDW | HEIZER - MULLERGREN 115 KV CKT 1 MIDW | Install 115 kV bay at Heizer and update relaying equipment | 165 | 178 | 165 | 178 | 0.03 | 9 | 3 | New | 2.6627e-05 | 0.00017045 | 2.2765e-05 |  | 400000 | 2009-07-01 | [38 empty] | 2011-06-01 | 2011-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T2635511SP | FROM->TO | SEWRDMW3 (SEWARD T1) 115/69/12.5KV TRANSFORMER CKT 1 | CP | MIDW | MIDW | REG E-IL | REG E-IL | 1 | 530679 | SEWRDMW3 115.00 | 530565 | SEWARD 2 69.000 | 530631 | SWRD1 1 12.500 | 1 | 11SP | 40 | 44.8 | 0 | 129.3 | 129.2947 | 123.9412 | [7 empty] | CATEGORYB | SINGLE | HEIZER 6 230.00 - MULLERGREN 230KV CKT 1 | 0 | 530680 | HEIZER 6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 |  | 56 |  | MKEC | HEIZER - MULLERGREN 115 KV CKT 1 MKEC | Construct approximately one mile of 115-kV transmission line from the Great Bend (Mullergren) generation station to Heizer Substation with 795 ACSR conductor | 165 | 178 | 165 | 178 | 1 | [7 empty] | 1000000 | 2010-03-05 | [38 empty] | 2011-06-01 | 2012-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T10565511SP | FROM->TO | SEWRDMW3 (SEWARD T1) 115/69/12.5KV TRANSFORMER CKT 1 | CP | MIDW | MIDW | REG E-IL | REG E-IL | 1 | 530679 | SEWRDMW3 115.00 | 530565 | SEWARD 2 69.000 | 530631 | SWRD1 1 12.500 | 1 | 11SP | 40 | 44.8 | 0 | 129.2 | 129.1863 | 123.885 | [7 empty] | CATEGORYB | SINGLE | HEIZER 6 230.00 (HEIZER T1) 230/115/12.5KV TRANSFORMER CKT 1 | 1 | 530601 | HEIZER 3 115.00 | 530680 | HEIZER 6 230.00 | 530626 | HZRT1 1 12.500 | 1 |  | 56 |  | MIDW | HEIZER - MULLERGREN 115 KV CKT 1 MIDW | Install 115 kV bay at Heizer and update relaying equipment | 165 | 178 | 165 | 178 | 0.03 | 9 | 3 | New | 2.6627e-05 | 0.00017045 | 2.2765e-05 |  | 400000 | 2009-07-01 | [38 empty] | 2011-06-01 | 2011-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T10565511SP | FROM->TO | SEWRDMW3 (SEWARD T1) 115/69/12.5KV TRANSFORMER CKT 1 | CP | MIDW | MIDW | REG E-IL | REG E-IL | 1 | 530679 | SEWRDMW3 115.00 | 530565 | SEWARD 2 69.000 | 530631 | SWRD1 1 12.500 | 1 | 11SP | 40 | 44.8 | 0 | 129.2 | 129.1863 | 123.885 | [7 empty] | CATEGORYB | SINGLE | HEIZER 6 230.00 (HEIZER T1) 230/115/12.5KV TRANSFORMER CKT 1 | 1 | 530601 | HEIZER 3 115.00 | 530680 | HEIZER 6 230.00 | 530626 | HZRT1 1 12.500 | 1 |  | 56 |  | MKEC | HEIZER - MULLERGREN 115 KV CKT 1 MKEC | Construct approximately one mile of 115-kV transmission line from the Great Bend (Mullergren) generation station to Heizer Substation with 795 ACSR conductor | 165 | 178 | 165 | 178 | 1 | [7 empty] | 1000000 | 2010-03-05 | [38 empty] | 2011-06-01 | 2012-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T2925512SP | FROM->TO | SEWRDMW3 (SEWARD T1) 115/69/12.5KV TRANSFORMER CKT 1 | CP | MIDW | MIDW | REG E-IL | REG E-IL | 1 | 530679 | SEWRDMW3 115.00 | 530565 | SEWARD 2 69.000 | 530631 | SWRD1 1 12.500 | 1 | 12SP | 40 | 44.8 | 0 | 129.7 | 129.679 | 132.7184 | [7 empty] | CATEGORYB | SINGLE | HEIZER 6 230.00 - MULLERGREN 230KV CKT 1 | 0 | 530680 | HEIZER 6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 |  | 60 |  | MIDW | HEIZER - MULLERGREN 115 KV CKT 1 MIDW | Install 115 kV bay at Heizer and update relaying equipment | 165 | 178 | 165 | 178 | 0.03 | 9 | 3 | New | 2.6627e-05 | 0.00017045 | 2.2765e-05 |  | 400000 | 2009-07-01 | [38 empty] | 2011-06-01 | 2011-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T2925512SP | FROM->TO | SEWRDMW3 (SEWARD T1) 115/69/12.5KV TRANSFORMER CKT 1 | CP | MIDW | MIDW | REG E-IL | REG E-IL | 1 | 530679 | SEWRDMW3 115.00 | 530565 | SEWARD 2 69.000 | 530631 | SWRD1 1 12.500 | 1 | 12SP | 40 | 44.8 | 0 | 129.7 | 129.679 | 132.7184 | [7 empty] | CATEGORYB | SINGLE | HEIZER 6 230.00 - MULLERGREN 230KV CKT 1 | 0 | 530680 | HEIZER 6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 |  | 60 |  | MKEC | HEIZER - MULLERGREN 115 KV CKT 1 MKEC | Construct approximately one mile of 115-kV transmission line from the Great Bend (Mullergren) generation station to Heizer Substation with 795 ACSR conductor | 165 | 178 | 165 | 178 | 1 | [7 empty] | 1000000 | 2010-03-05 | [38 empty] | 2011-06-01 | 2012-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T11455512SP | FROM->TO | SEWRDMW3 (SEWARD T1) 115/69/12.5KV TRANSFORMER CKT 1 | CP | MIDW | MIDW | REG E-IL | REG E-IL | 1 | 530679 | SEWRDMW3 115.00 | 530565 | SEWARD 2 69.000 | 530631 | SWRD1 1 12.500 | 1 | 12SP | 40 | 44.8 | 0 | 129.7 | 129.7387 | 132.6349 | [7 empty] | CATEGORYB | SINGLE | HEIZER 6 230.00 (HEIZER T1) 230/115/12.5KV TRANSFORMER CKT 1 | 1 | 530601 | HEIZER 3 115.00 | 530680 | HEIZER 6 230.00 | 530626 | HZRT1 1 12.500 | 1 |  | 60 |  | MIDW | HEIZER - MULLERGREN 115 KV CKT 1 MIDW | Install 115 kV bay at Heizer and update relaying equipment | 165 | 178 | 165 | 178 | 0.03 | 9 | 3 | New | 2.6627e-05 | 0.00017045 | 2.2765e-05 |  | 400000 | 2009-07-01 | [38 empty] | 2011-06-01 | 2011-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T11455512SP | FROM->TO | SEWRDMW3 (SEWARD T1) 115/69/12.5KV TRANSFORMER CKT 1 | CP | MIDW | MIDW | REG E-IL | REG E-IL | 1 | 530679 | SEWRDMW3 115.00 | 530565 | SEWARD 2 69.000 | 530631 | SWRD1 1 12.500 | 1 | 12SP | 40 | 44.8 | 0 | 129.7 | 129.7387 | 132.6349 | [7 empty] | CATEGORYB | SINGLE | HEIZER 6 230.00 (HEIZER T1) 230/115/12.5KV TRANSFORMER CKT 1 | 1 | 530601 | HEIZER 3 115.00 | 530680 | HEIZER 6 230.00 | 530626 | HZRT1 1 12.500 | 1 |  | 60 |  | MKEC | HEIZER - MULLERGREN 115 KV CKT 1 MKEC | Construct approximately one mile of 115-kV transmission line from the Great Bend (Mullergren) generation station to Heizer Substation with 795 ACSR conductor | 165 | 178 | 165 | 178 | 1 | [7 empty] | 1000000 | 2010-03-05 | [38 empty] | 2011-06-01 | 2012-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T2945516SP | FROM->TO | SEWRDMW3 (SEWARD T1) 115/69/12.5KV TRANSFORMER CKT 1 | CP | MIDW | MIDW | REG E-IL | REG E-IL | 1 | 530679 | SEWRDMW3 115.00 | 530565 | SEWARD 2 69.000 | 530631 | SWRD1 1 12.500 | 1 | 16SP | 40 | 44.8 | 0 | 138.9 | 138.892 | 128.4291 | [7 empty] | CATEGORYB | SINGLE | HEIZER 6 230.00 - MULLERGREN 230KV CKT 1 | 0 | 530680 | HEIZER 6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 |  | 58 |  | MIDW | HEIZER - MULLERGREN 115 KV CKT 1 MIDW | Install 115 kV bay at Heizer and update relaying equipment | 165 | 178 | 165 | 178 | 0.03 | 9 | 3 | New | 2.6627e-05 | 0.00017045 | 2.2765e-05 |  | 400000 | 2009-07-01 | [38 empty] | 2011-06-01 | 2011-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T2945516SP | FROM->TO | SEWRDMW3 (SEWARD T1) 115/69/12.5KV TRANSFORMER CKT 1 | CP | MIDW | MIDW | REG E-IL | REG E-IL | 1 | 530679 | SEWRDMW3 115.00 | 530565 | SEWARD 2 69.000 | 530631 | SWRD1 1 12.500 | 1 | 16SP | 40 | 44.8 | 0 | 138.9 | 138.892 | 128.4291 | [7 empty] | CATEGORYB | SINGLE | HEIZER 6 230.00 - MULLERGREN 230KV CKT 1 | 0 | 530680 | HEIZER 6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 |  | 58 |  | MKEC | HEIZER - MULLERGREN 115 KV CKT 1 MKEC | Construct approximately one mile of 115-kV transmission line from the Great Bend (Mullergren) generation station to Heizer Substation with 795 ACSR conductor | 165 | 178 | 165 | 178 | 1 | [7 empty] | 1000000 | 2010-03-05 | [38 empty] | 2011-06-01 | 2012-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T11475516SP | FROM->TO | SEWRDMW3 (SEWARD T1) 115/69/12.5KV TRANSFORMER CKT 1 | CP | MIDW | MIDW | REG E-IL | REG E-IL | 1 | 530679 | SEWRDMW3 115.00 | 530565 | SEWARD 2 69.000 | 530631 | SWRD1 1 12.500 | 1 | 16SP | 40 | 44.8 | 0 | 138.8 | 138.8193 | 128.3121 | [7 empty] | CATEGORYB | SINGLE | HEIZER 6 230.00 (HEIZER T1) 230/115/12.5KV TRANSFORMER CKT 1 | 1 | 530601 | HEIZER 3 115.00 | 530680 | HEIZER 6 230.00 | 530626 | HZRT1 1 12.500 | 1 |  | 58 |  | MIDW | HEIZER - MULLERGREN 115 KV CKT 1 MIDW | Install 115 kV bay at Heizer and update relaying equipment | 165 | 178 | 165 | 178 | 0.03 | 9 | 3 | New | 2.6627e-05 | 0.00017045 | 2.2765e-05 |  | 400000 | 2009-07-01 | [38 empty] | 2011-06-01 | 2011-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T11475516SP | FROM->TO | SEWRDMW3 (SEWARD T1) 115/69/12.5KV TRANSFORMER CKT 1 | CP | MIDW | MIDW | REG E-IL | REG E-IL | 1 | 530679 | SEWRDMW3 115.00 | 530565 | SEWARD 2 69.000 | 530631 | SWRD1 1 12.500 | 1 | 16SP | 40 | 44.8 | 0 | 138.8 | 138.8193 | 128.3121 | [7 empty] | CATEGORYB | SINGLE | HEIZER 6 230.00 (HEIZER T1) 230/115/12.5KV TRANSFORMER CKT 1 | 1 | 530601 | HEIZER 3 115.00 | 530680 | HEIZER 6 230.00 | 530626 | HZRT1 1 12.500 | 1 |  | 58 |  | MKEC | HEIZER - MULLERGREN 115 KV CKT 1 MKEC | Construct approximately one mile of 115-kV transmission line from the Great Bend (Mullergren) generation station to Heizer Substation with 795 ACSR conductor | 165 | 178 | 165 | 178 | 1 | [7 empty] | 1000000 | 2010-03-05 | [38 empty] | 2011-06-01 | 2012-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T4875521SP | FROM->TO | SEWRDMW3 (SEWARD T1) 115/69/12.5KV TRANSFORMER CKT 1 | CP | MIDW | MIDW | REG E-IL | REG E-IL | 1 | 530679 | SEWRDMW3 115.00 | 530565 | SEWARD 2 69.000 | 530631 | SWRD1 1 12.500 | 1 | 21SP | 40 | 44.8 | 0 | 142.8 | 142.7838 | 132.8229 | [7 empty] | CATEGORYB | SINGLE | HEIZER 6 230.00 - MULLERGREN 230KV CKT 1 | 0 | 530680 | HEIZER 6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 |  | 60 |  | MIDW | HEIZER - MULLERGREN 115 KV CKT 1 MIDW | Install 115 kV bay at Heizer and update relaying equipment | 165 | 178 | 165 | 178 | 0.03 | 9 | 3 | New | 2.6627e-05 | 0.00017045 | 2.2765e-05 |  | 400000 | 2009-07-01 | [38 empty] | 2011-06-01 | 2011-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T4875521SP | FROM->TO | SEWRDMW3 (SEWARD T1) 115/69/12.5KV TRANSFORMER CKT 1 | CP | MIDW | MIDW | REG E-IL | REG E-IL | 1 | 530679 | SEWRDMW3 115.00 | 530565 | SEWARD 2 69.000 | 530631 | SWRD1 1 12.500 | 1 | 21SP | 40 | 44.8 | 0 | 142.8 | 142.7838 | 132.8229 | [7 empty] | CATEGORYB | SINGLE | HEIZER 6 230.00 - MULLERGREN 230KV CKT 1 | 0 | 530680 | HEIZER 6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 |  | 60 |  | MKEC | HEIZER - MULLERGREN 115 KV CKT 1 MKEC | Construct approximately one mile of 115-kV transmission line from the Great Bend (Mullergren) generation station to Heizer Substation with 795 ACSR conductor | 165 | 178 | 165 | 178 | 1 | [7 empty] | 1000000 | 2010-03-05 | [38 empty] | 2011-06-01 | 2012-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T19585521SP | FROM->TO | SEWRDMW3 (SEWARD T1) 115/69/12.5KV TRANSFORMER CKT 1 | CP | MIDW | MIDW | REG E-IL | REG E-IL | 1 | 530679 | SEWRDMW3 115.00 | 530565 | SEWARD 2 69.000 | 530631 | SWRD1 1 12.500 | 1 | 21SP | 40 | 44.8 | 0 | 142.8 | 142.7598 | 132.677 | [7 empty] | CATEGORYB | SINGLE | HEIZER 6 230.00 (HEIZER T1) 230/115/12.5KV TRANSFORMER CKT 1 | 1 | 530601 | HEIZER 3 115.00 | 530680 | HEIZER 6 230.00 | 530626 | HZRT1 1 12.500 | 1 |  | 60 |  | MIDW | HEIZER - MULLERGREN 115 KV CKT 1 MIDW | Install 115 kV bay at Heizer and update relaying equipment | 165 | 178 | 165 | 178 | 0.03 | 9 | 3 | New | 2.6627e-05 | 0.00017045 | 2.2765e-05 |  | 400000 | 2009-07-01 | [38 empty] | 2011-06-01 | 2011-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T19585521SP | FROM->TO | SEWRDMW3 (SEWARD T1) 115/69/12.5KV TRANSFORMER CKT 1 | CP | MIDW | MIDW | REG E-IL | REG E-IL | 1 | 530679 | SEWRDMW3 115.00 | 530565 | SEWARD 2 69.000 | 530631 | SWRD1 1 12.500 | 1 | 21SP | 40 | 44.8 | 0 | 142.8 | 142.7598 | 132.677 | [7 empty] | CATEGORYB | SINGLE | HEIZER 6 230.00 (HEIZER T1) 230/115/12.5KV TRANSFORMER CKT 1 | 1 | 530601 | HEIZER 3 115.00 | 530680 | HEIZER 6 230.00 | 530626 | HZRT1 1 12.500 | 1 |  | 60 |  | MKEC | HEIZER - MULLERGREN 115 KV CKT 1 MKEC | Construct approximately one mile of 115-kV transmission line from the Great Bend (Mullergren) generation station to Heizer Substation with 795 ACSR conductor | 165 | 178 | 165 | 178 | 1 | [7 empty] | 1000000 | 2010-03-05 | [38 empty] | 2011-06-01 | 2012-06-01
2005-AG2 | 2005-AG2 | [7 empty] | 2005-AG2EMDE5474695474671 |  | SUB 110 - ORONOGO JCT. - SUB 167 - RIVERTON 161KV CKT 1 | U | EMDE | EMDE |  |  | 0 | 547469 | RIV167 5 161 | 547467 | ORO110 5 161 | 0 |  | 1 | 15SP |  | 214 | [12 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | EMDE | SUB 110 - ORONOGO JCT. - SUB 167 - RIVERTON 161KV CKT 1 | Reconductor Oronogo 59467 to Riverton 59469 with Bundled 556 ACSR | 299 | 335 | 299 | 335 | 11.84 | 24 | 12 |  | 0.00379 | 0.02451 | 0.02427 |  | 5400000 | [39 empty] | 2011-06-01 | 2011-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T6735021SP | FROM->TO | SUB 907 - SUB 919 69KV CKT 1 | EXP | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 647907 | S907 8 69.000 | 647919 | S919 8 69.000 | 0 |  | 1 | 21SP | 65 | 65 | 65 | 101.9 | 101.916 | 100.0659 | [7 empty] | CATEGORYB | SINGLE | SUB 1250 - SUB 919 69KV CKT 1 | 0 | 647919 | S919 8 69.000 | 647950 | S950 8 69.000 | 0 |  | 1 |  | 66 |  | OPPD | SUB 907 - SUB 919 69KV CKT 1 | Increase line clearances to allow the use of a higher conductor rating. | 76 | 76 |  |  |  | 12 | 12 | [5 empty] | 272000 | 2009-01-01 | [38 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T22285021SP | FROM->TO | SUB 907 - SUB 919 69KV CKT 1 | EXP | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 647907 | S907 8 69.000 | 647919 | S919 8 69.000 | 0 |  | 1 | 21SP | 65 | 65 | 65 | 101.9 | 101.905 | 100.0546 | [7 empty] | CATEGORYB | SINGLE | SUB 1250 (S1250 T1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 646250 | S1250 5 161.00 | 647950 | S950 8 69.000 | 648250 | S1250T19 13.800 | 1 |  | 66 |  | OPPD | SUB 907 - SUB 919 69KV CKT 1 | Increase line clearances to allow the use of a higher conductor rating. | 76 | 76 |  |  |  | 12 | 12 | [5 empty] | 272000 | 2009-01-01 | [38 empty] | 2017-06-01 | 2017-06-01
GEN-2006-010 | Turk | [7 empty] | GEN-2006-010AEPW5074545080801 |  | SUGAR HILL - TURK 138KV CKT 1 | U | AEPW | AEPW | SARK | TEXARK | 0 | 507454 | HEMPSTD4 138.00 | 508080 | SUGARHL4 138.00 | 0 |  | 1 |  | 368 | 512 |  | 159.6 | [10 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | AEPW | SUGAR HILL - TURK 138KV CKT 1 | Build new Turk-Sugar Hill 138 kV line and add Sugar Hill 138 kV terminal. | [11 empty] | 19700000 | 19700000 | [39 empty] | 2012-07-01 | 2012-07-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1035510WP | FROM->TO | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 2 | 521065 | TALOGA 4 138.00 | 521064 | TALOGA 2 69.000 | 521178 | TLGTERT 13.800 | 1 | 10WP | 56 | 56 | 56 |  | 66.4834 | 112.4182 | [7 empty] | CATEGORYB | SINGLE | DEWEY - SOUTHARD 138KV CKT 1 | 0 | 514787 | DEWEY 4 138.00 | 514822 | SOUTHRD4 138.00 | 0 |  | 1 |  | 63 | Upgrade Taloga Auto to 112MVA | WFEC | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | Auto XFMR 56 to 112MVA | 112 | 112 | 112 | 112 | [8 empty] | 1000000 | [39 empty] | 2010-10-01 | 2013-06-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T10585510WP | FROM->TO | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 2 | 521065 | TALOGA 4 138.00 | 521064 | TALOGA 2 69.000 | 521178 | TLGTERT 13.800 | 1 | 10WP | 56 | 56 | 56 |  | 64.4157 | 109.3787 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  | 62 | Upgrade Taloga Auto to 112MVA | WFEC | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | Auto XFMR 56 to 112MVA | 112 | 112 | 112 | 112 | [8 empty] | 1000000 | [39 empty] | 2010-10-01 | 2013-06-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1195510WP | FROM->TO | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 2 | 521065 | TALOGA 4 138.00 | 521064 | TALOGA 2 69.000 | 521178 | TLGTERT 13.800 | 1 | 10WP | 56 | 56 | 56 |  | 64.405 | 109.3739 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WWRDEHV7 345.00 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 62 | Upgrade Taloga Auto to 112MVA | WFEC | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | Auto XFMR 56 to 112MVA | 112 | 112 | 112 | 112 | [8 empty] | 1000000 | [39 empty] | 2010-10-01 | 2013-06-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1615511SP | FROM->TO | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 2 | 521065 | TALOGA 4 138.00 | 521064 | TALOGA 2 69.000 | 521178 | TLGTERT 13.800 | 1 | 11SP | 56 | 56 | 56 |  | 71.5182 | 121.8384 | [7 empty] | CATEGORYB | SINGLE | DEWEY - SOUTHARD 138KV CKT 1 | 0 | 514787 | DEWEY 4 138.00 | 514822 | SOUTHRD4 138.00 | 0 |  | 1 |  | 69 | Upgrade Taloga Auto to 112MVA | WFEC | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | Auto XFMR 56 to 112MVA | 112 | 112 | 112 | 112 | [8 empty] | 1000000 | [39 empty] | 2010-10-01 | 2013-06-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T10315511SP | FROM->TO | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 2 | 521065 | TALOGA 4 138.00 | 521064 | TALOGA 2 69.000 | 521178 | TLGTERT 13.800 | 1 | 11SP | 56 | 56 | 56 |  | 65.1786 | 116.7569 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  | 66 | Upgrade Taloga Auto to 112MVA | WFEC | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | Auto XFMR 56 to 112MVA | 112 | 112 | 112 | 112 | [8 empty] | 1000000 | [39 empty] | 2010-10-01 | 2013-06-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1935511SP | FROM->TO | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 2 | 521065 | TALOGA 4 138.00 | 521064 | TALOGA 2 69.000 | 521178 | TLGTERT 13.800 | 1 | 11SP | 56 | 56 | 56 |  | 65.1649 | 116.748 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WWRDEHV7 345.00 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 66 | Upgrade Taloga Auto to 112MVA | WFEC | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | Auto XFMR 56 to 112MVA | 112 | 112 | 112 | 112 | [8 empty] | 1000000 | [39 empty] | 2010-10-01 | 2013-06-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T655511WP | FROM->TO | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 2 | 521065 | TALOGA 4 138.00 | 521064 | TALOGA 2 69.000 | 521178 | TLGTERT 13.800 | 1 | 11WP | 56 | 56 | 56 |  | 66.4968 | 114.0032 | [7 empty] | CATEGORYB | SINGLE | DEWEY - SOUTHARD 138KV CKT 1 | 0 | 514787 | DEWEY 4 138.00 | 514822 | SOUTHRD4 138.00 | 0 |  | 1 |  | 64 | Upgrade Taloga Auto to 112MVA | WFEC | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | Auto XFMR 56 to 112MVA | 112 | 112 | 112 | 112 | [8 empty] | 1000000 | [39 empty] | 2010-10-01 | 2013-06-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T755511WP | FROM->TO | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 2 | 521065 | TALOGA 4 138.00 | 521064 | TALOGA 2 69.000 | 521178 | TLGTERT 13.800 | 1 | 11WP | 56 | 56 | 56 |  | 65.09 | 111.2893 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 63 | Upgrade Taloga Auto to 112MVA | WFEC | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | Auto XFMR 56 to 112MVA | 112 | 112 | 112 | 112 | [8 empty] | 1000000 | [39 empty] | 2010-10-01 | 2013-06-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T815511WP | FROM->TO | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 2 | 521065 | TALOGA 4 138.00 | 521064 | TALOGA 2 69.000 | 521178 | TLGTERT 13.800 | 1 | 11WP | 56 | 56 | 56 |  | 65.0204 | 111.1501 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WWRDEHV7 345.00 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 63 | Upgrade Taloga Auto to 112MVA | WFEC | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | Auto XFMR 56 to 112MVA | 112 | 112 | 112 | 112 | [8 empty] | 1000000 | [39 empty] | 2010-10-01 | 2013-06-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1865512SP | FROM->TO | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 1 | 521065 | TALOGA 4 138.00 | 521064 | TALOGA 2 69.000 | 521178 | TLGTERT 13.800 | 1 | 12SP | 56 | 56 | 56 |  | 74.4299 | 123.077 | [7 empty] | CATEGORYB | SINGLE | DEWEY - SOUTHARD 138KV CKT 1 | 0 | 514787 | DEWEY 4 138.00 | 514822 | SOUTHRD4 138.00 | 0 |  | 1 |  | 69 | Upgrade Taloga Auto to 112MVA | WFEC | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | Auto XFMR 56 to 112MVA | 112 | 112 | 112 | 112 | [8 empty] | 1000000 | [39 empty] | 2010-10-01 | 2013-06-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T2195512SP | FROM->TO | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 2 | 521065 | TALOGA 4 138.00 | 521064 | TALOGA 2 69.000 | 521178 | TLGTERT 13.800 | 1 | 12SP | 56 | 56 | 56 |  | 69.2678 | 119.1869 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WWRDEHV7 345.00 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 67 | Upgrade Taloga Auto to 112MVA | WFEC | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | Auto XFMR 56 to 112MVA | 112 | 112 | 112 | 112 | [8 empty] | 1000000 | [39 empty] | 2010-10-01 | 2013-06-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T11185512SP | FROM->TO | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 2 | 521065 | TALOGA 4 138.00 | 521064 | TALOGA 2 69.000 | 521178 | TLGTERT 13.800 | 1 | 12SP | 56 | 56 | 56 |  | 69.2871 | 119.1848 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  | 67 | Upgrade Taloga Auto to 112MVA | WFEC | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | Auto XFMR 56 to 112MVA | 112 | 112 | 112 | 112 | [8 empty] | 1000000 | [39 empty] | 2010-10-01 | 2013-06-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T765512WP | FROM->TO | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 2 | 521065 | TALOGA 4 138.00 | 521064 | TALOGA 2 69.000 | 521178 | TLGTERT 13.800 | 1 | 12WP | 56 | 56 | 56 |  | 67.1695 | 121.4788 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 69 | Upgrade Taloga Auto to 112MVA | WFEC | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | Auto XFMR 56 to 112MVA | 112 | 112 | 112 | 112 | [8 empty] | 1000000 | [39 empty] | 2010-10-01 | 2013-06-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T885512WP | FROM->TO | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 2 | 521065 | TALOGA 4 138.00 | 521064 | TALOGA 2 69.000 | 521178 | TLGTERT 13.800 | 1 | 12WP | 56 | 56 | 56 |  | 67.1018 | 121.3875 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WWRDEHV7 345.00 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 68 | Upgrade Taloga Auto to 112MVA | WFEC | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | Auto XFMR 56 to 112MVA | 112 | 112 | 112 | 112 | [8 empty] | 1000000 | [39 empty] | 2010-10-01 | 2013-06-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T4655512WP | FROM->TO | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 2 | 521065 | TALOGA 4 138.00 | 521064 | TALOGA 2 69.000 | 521178 | TLGTERT 13.800 | 1 | 12WP | 56 | 56 | 56 |  | 67.119 | 121.3282 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  | 68 | Upgrade Taloga Auto to 112MVA | WFEC | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | Auto XFMR 56 to 112MVA | 112 | 112 | 112 | 112 | [8 empty] | 1000000 | [39 empty] | 2010-10-01 | 2013-06-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T2335516SP | FROM->TO | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 1 | 521065 | TALOGA 4 138.00 | 521064 | TALOGA 2 69.000 | 521178 | TLGTERT 13.800 | 1 | 16SP | 56 | 56 | 56 |  | 64.8945 | 104.2163 | [7 empty] | CATEGORYB | SINGLE | DEWEY - SOUTHARD 138KV CKT 1 | 0 | 514787 | DEWEY 4 138.00 | 514822 | SOUTHRD4 138.00 | 0 |  | 1 |  | 59 | Upgrade Taloga Auto to 112MVA | WFEC | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | Auto XFMR 56 to 112MVA | 112 | 112 | 112 | 112 | [8 empty] | 1000000 | [39 empty] | 2010-10-01 | 2013-06-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T3275521SP | FROM->TO | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-OP | 1 | 521065 | TALOGA 4 138.00 | 521064 | TALOGA 2 69.000 | 521178 | TLGTERT 13.800 | 1 | 21SP | 56 | 56 | 56 |  | 60.9125 | 101.0797 | [7 empty] | CATEGORYB | SINGLE | DEWEY - SOUTHARD 138KV CKT 1 | 0 | 514787 | DEWEY 4 138.00 | 514822 | SOUTHRD4 138.00 | 0 |  | 1 |  | 57 | Upgrade Taloga Auto to 112MVA | WFEC | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | Auto XFMR 56 to 112MVA | 112 | 112 | 112 | 112 | [8 empty] | 1000000 | [39 empty] | 2010-10-01 | 2013-06-01 | 2012-10-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1355516SP | TO->FROM | TEXAS EASTMAN - WHITNEY 138KV CKT 1 | CP | AEPW | AEPW | LONG-MAR | LONG-MAR | 0 | 508575 | WHITNEY4 138.00 | 508582 | EASTEX 4 138.00 | 0 |  | 1 | 16SP | 235 | 272 | 0 | 124.5 | 124.4675 | 126.5871 | [7 empty] | CATEGORYB | SINGLE | EASTON REC - PIRKEY 138KV CKT 1 | 0 | 508562 | PIRKEY 4 138.00 | 509092 | EASTON 4 138.00 | 0 |  | 1 |  | 345 |  | AEPW | TEXAS EASTMAN - WHITNEY 138KV CKT 1 | Rebuild 2.49 miles with 1590 ACSR. Replace wavetrap & jumpers @ Whitney. Replace metering CT @ Texas Eastman | 320 | 380 | 379 | 429 | 2.49 | 18 | 6 |  | 0.00117 | 0.01147 | 0.00404 | New limits will be jumpers | 2800000 | 2008-07-30 | [38 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T1275516SP | TO->FROM | TEXAS EASTMAN - WHITNEY 138KV CKT 1 | CP | AEPW | AEPW | LONG-MAR | LONG-MAR | 0 | 508575 | WHITNEY4 138.00 | 508582 | EASTEX 4 138.00 | 0 |  | 1 | 16SP | 235 | 272 | 0 | 123 | 122.9529 | 125.0701 | [7 empty] | CATEGORYB | SINGLE | EASTON REC - KNOX LEE 138KV CKT 1 | 0 | 508548 | KNOXLEE4 138.00 | 509092 | EASTON 4 138.00 | 0 |  | 1 |  | 341 |  | AEPW | TEXAS EASTMAN - WHITNEY 138KV CKT 1 | Rebuild 2.49 miles with 1590 ACSR. Replace wavetrap & jumpers @ Whitney. Replace metering CT @ Texas Eastman | 320 | 380 | 379 | 429 | 2.49 | 18 | 6 |  | 0.00117 | 0.01147 | 0.00404 | New limits will be jumpers | 2800000 | 2008-07-30 | [38 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T945516WP | TO->FROM | TEXAS EASTMAN - WHITNEY 138KV CKT 1 | CP | AEPW | AEPW | LONG-MAR | LONG-MAR | 0 | 508575 | WHITNEY4 138.00 | 508582 | EASTEX 4 138.00 | 0 |  | 1 | 16WP | 277 | 307 | 0 | 106.7 | 106.7079 | 106.5929 | [7 empty] | CATEGORYB | SINGLE | EASTON REC - PIRKEY 138KV CKT 1 | 0 | 508562 | PIRKEY 4 138.00 | 509092 | EASTON 4 138.00 | 0 |  | 1 |  | 328 |  | AEPW | TEXAS EASTMAN - WHITNEY 138KV CKT 1 | Rebuild 2.49 miles with 1590 ACSR. Replace wavetrap & jumpers @ Whitney. Replace metering CT @ Texas Eastman | 320 | 380 | 379 | 429 | 2.49 | 18 | 6 |  | 0.00117 | 0.01147 | 0.00404 | New limits will be jumpers | 2800000 | 2008-07-30 | [38 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T895516WP | TO->FROM | TEXAS EASTMAN - WHITNEY 138KV CKT 1 | CP | AEPW | AEPW | LONG-MAR | LONG-MAR | 0 | 508575 | WHITNEY4 138.00 | 508582 | EASTEX 4 138.00 | 0 |  | 1 | 16WP | 277 | 307 | 0 | 105.4 | 105.4492 | 105.3342 | [7 empty] | CATEGORYB | SINGLE | EASTON REC - KNOX LEE 138KV CKT 1 | 0 | 508548 | KNOXLEE4 138.00 | 509092 | EASTON 4 138.00 | 0 |  | 1 |  | 324 |  | AEPW | TEXAS EASTMAN - WHITNEY 138KV CKT 1 | Rebuild 2.49 miles with 1590 ACSR. Replace wavetrap & jumpers @ Whitney. Replace metering CT @ Texas Eastman | 320 | 380 | 379 | 429 | 2.49 | 18 | 6 |  | 0.00117 | 0.01147 | 0.00404 | New limits will be jumpers | 2800000 | 2008-07-30 | [38 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T2075521SP | TO->FROM | TEXAS EASTMAN - WHITNEY 138KV CKT 1 | CP | AEPW | AEPW | LONG-MAR | LONG-MAR | 0 | 508575 | WHITNEY4 138.00 | 508582 | EASTEX 4 138.00 | 0 |  | 1 | 21SP | 235 | 272 | 0 |  | 74.3068 | 103.9507 | [7 empty] | CATEGORYB | SINGLE | EASTON REC - PIRKEY 138KV CKT 1 | 0 | 508562 | PIRKEY 4 138.00 | 509092 | EASTON 4 138.00 | 0 |  | 1 |  | 283 |  | AEPW | TEXAS EASTMAN - WHITNEY 138KV CKT 1 | Rebuild 2.49 miles with 1590 ACSR. Replace wavetrap & jumpers @ Whitney. Replace metering CT @ Texas Eastman | 320 | 380 | 379 | 429 | 2.49 | 18 | 6 |  | 0.00117 | 0.01147 | 0.00404 | New limits will be jumpers | 2800000 | 2008-07-30 | [38 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T2005521SP | TO->FROM | TEXAS EASTMAN - WHITNEY 138KV CKT 1 | CP | AEPW | AEPW | LONG-MAR | LONG-MAR | 0 | 508575 | WHITNEY4 138.00 | 508582 | EASTEX 4 138.00 | 0 |  | 1 | 21SP | 235 | 272 | 0 |  | 72.729 | 102.3239 | [7 empty] | CATEGORYB | SINGLE | EASTON REC - KNOX LEE 138KV CKT 1 | 0 | 508548 | KNOXLEE4 138.00 | 509092 | EASTON 4 138.00 | 0 |  | 1 |  | 279 |  | AEPW | TEXAS EASTMAN - WHITNEY 138KV CKT 1 | Rebuild 2.49 miles with 1590 ACSR. Replace wavetrap & jumpers @ Whitney. Replace metering CT @ Texas Eastman | 320 | 380 | 379 | 429 | 2.49 | 18 | 6 |  | 0.00117 | 0.01147 | 0.00404 | New limits will be jumpers | 2800000 | 2008-07-30 | [38 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2415011SP | TO->FROM | TIMBER JUNCTION - UDALL 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533559 | UDALL 2 69.000 | 533558 | TIMBJCT2 69.000 | 0 |  | 1 | 11SP | 43 | 43 | 0 |  | 73.1132 | 104.5989 | [7 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  | 45 |  | WERE | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | Tear down / Rebuild 11.63-mile Timber Tap-Winfield 69 kV line, 954 ACSR | 72 | 72 | 72 | 72 | 11.63 | 18 | 6 |  | 0.0309 | 0.2101 | 0.05164 | Line switches limit to 72 MVA. $790k per mile | 8161986 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2415011SP | TO->FROM | TIMBER JUNCTION - UDALL 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533559 | UDALL 2 69.000 | 533558 | TIMBJCT2 69.000 | 0 |  | 1 | 11SP | 43 | 43 | 0 |  | 73.1132 | 104.5989 | [7 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  | 45 |  | WERE | RICHLAND - UDALL 69KV CKT 1 | Tear down / Rebuild 8.48-mile Richland-Udall 69 kV line using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 8.48 | 13 | 7 | N | 0.01789 | 0.12177 | 0.02589 | MVA limit is conductor $790k per mile | 6699200 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2415011SP | TO->FROM | TIMBER JUNCTION - UDALL 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533559 | UDALL 2 69.000 | 533558 | TIMBJCT2 69.000 | 0 |  | 1 | 11SP | 43 | 43 | 0 |  | 73.1132 | 104.5989 | [7 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  | 45 |  | WERE | TIMBER JUNCTION - UDALL 69KV CKT 1 | Tear down / Rebuild Udall-Timber Jct 69 kV using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 2.01 | 4 | 2 | N | 0.00424 | 0.02886 | 0.00614 | MVA limit is conductor $790k per mile | 1587900 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2415011SP | TO->FROM | TIMBER JUNCTION - UDALL 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533559 | UDALL 2 69.000 | 533558 | TIMBJCT2 69.000 | 0 |  | 1 | 11SP | 43 | 43 | 0 |  | 73.1132 | 104.5989 | [7 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  | 45 |  | WERE | BELL - PECK 69KV CKT 1 | Tear down / Rebuild 8.23 mile Bell-Peck 69 kV line with 1192 ACSR and replace CT | 134 | 147 | 134 | 147 | 8.23 | 18 | 5 | N |  |  |  | $790k per mile and $200k for CT | 6701700 | 2010-01-01 | [38 empty] | 2012-06-01 | 2012-12-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2705012SP | TO->FROM | TIMBER JUNCTION - UDALL 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533559 | UDALL 2 69.000 | 533558 | TIMBJCT2 69.000 | 0 |  | 1 | 12SP | 43 | 43 | 0 |  | 82.8227 | 112.4559 | [7 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  | 49 |  | WERE | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | Tear down / Rebuild 11.63-mile Timber Tap-Winfield 69 kV line, 954 ACSR | 72 | 72 | 72 | 72 | 11.63 | 18 | 6 |  | 0.0309 | 0.2101 | 0.05164 | Line switches limit to 72 MVA. $790k per mile | 8161986 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2705012SP | TO->FROM | TIMBER JUNCTION - UDALL 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533559 | UDALL 2 69.000 | 533558 | TIMBJCT2 69.000 | 0 |  | 1 | 12SP | 43 | 43 | 0 |  | 82.8227 | 112.4559 | [7 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  | 49 |  | WERE | RICHLAND - UDALL 69KV CKT 1 | Tear down / Rebuild 8.48-mile Richland-Udall 69 kV line using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 8.48 | 13 | 7 | N | 0.01789 | 0.12177 | 0.02589 | MVA limit is conductor $790k per mile | 6699200 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2705012SP | TO->FROM | TIMBER JUNCTION - UDALL 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533559 | UDALL 2 69.000 | 533558 | TIMBJCT2 69.000 | 0 |  | 1 | 12SP | 43 | 43 | 0 |  | 82.8227 | 112.4559 | [7 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  | 49 |  | WERE | TIMBER JUNCTION - UDALL 69KV CKT 1 | Tear down / Rebuild Udall-Timber Jct 69 kV using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 2.01 | 4 | 2 | N | 0.00424 | 0.02886 | 0.00614 | MVA limit is conductor $790k per mile | 1587900 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T2705012SP | TO->FROM | TIMBER JUNCTION - UDALL 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533559 | UDALL 2 69.000 | 533558 | TIMBJCT2 69.000 | 0 |  | 1 | 12SP | 43 | 43 | 0 |  | 82.8227 | 112.4559 | [7 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  | 49 |  | WERE | BELL - PECK 69KV CKT 1 | Tear down / Rebuild 8.23 mile Bell-Peck 69 kV line with 1192 ACSR and replace CT | 134 | 147 | 134 | 147 | 8.23 | 18 | 5 | N |  |  |  | $790k per mile and $200k for CT | 6701700 | 2010-01-01 | [38 empty] | 2012-06-01 | 2012-12-01 | 2012-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T3275516SP | TO->FROM | TIMBER JUNCTION - UDALL 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533559 | UDALL 2 69.000 | 533558 | TIMBJCT2 69.000 | 0 |  | 1 | 16SP | 43 | 43 | 0 |  | 79.7959 | 102.8378 | [7 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  | 45 |  | WERE | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | Tear down / Rebuild 11.63-mile Timber Tap-Winfield 69 kV line, 954 ACSR | 72 | 72 | 72 | 72 | 11.63 | 18 | 6 |  | 0.0309 | 0.2101 | 0.05164 | Line switches limit to 72 MVA. $790k per mile | 8161986 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T3275516SP | TO->FROM | TIMBER JUNCTION - UDALL 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533559 | UDALL 2 69.000 | 533558 | TIMBJCT2 69.000 | 0 |  | 1 | 16SP | 43 | 43 | 0 |  | 79.7959 | 102.8378 | [7 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  | 45 |  | WERE | RICHLAND - UDALL 69KV CKT 1 | Tear down / Rebuild 8.48-mile Richland-Udall 69 kV line using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 8.48 | 13 | 7 | N | 0.01789 | 0.12177 | 0.02589 | MVA limit is conductor $790k per mile | 6699200 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T3275516SP | TO->FROM | TIMBER JUNCTION - UDALL 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533559 | UDALL 2 69.000 | 533558 | TIMBJCT2 69.000 | 0 |  | 1 | 16SP | 43 | 43 | 0 |  | 79.7959 | 102.8378 | [7 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  | 45 |  | WERE | TIMBER JUNCTION - UDALL 69KV CKT 1 | Tear down / Rebuild Udall-Timber Jct 69 kV using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 2.01 | 4 | 2 | N | 0.00424 | 0.02886 | 0.00614 | MVA limit is conductor $790k per mile | 1587900 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T3275516SP | TO->FROM | TIMBER JUNCTION - UDALL 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533559 | UDALL 2 69.000 | 533558 | TIMBJCT2 69.000 | 0 |  | 1 | 16SP | 43 | 43 | 0 |  | 79.7959 | 102.8378 | [7 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  | 45 |  | WERE | BELL - PECK 69KV CKT 1 | Tear down / Rebuild 8.23 mile Bell-Peck 69 kV line with 1192 ACSR and replace CT | 134 | 147 | 134 | 147 | 8.23 | 18 | 5 | N |  |  |  | $790k per mile and $200k for CT | 6701700 | 2010-01-01 | [38 empty] | 2012-06-01 | 2012-12-01 | 2012-10-01
2009-AGP2 | AFS6NC |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS6NC1T35521SP | TO->FROM | TIMBER JUNCTION - UDALL 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533559 | UDALL 2 69.000 | 533558 | TIMBJCT2 69.000 | 0 |  | 1 | 21SP | 43 | 43 | 0 | 91.6404 | 91.6404 | 103.9712 | [7 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  | 45 |  | WERE | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | Tear down / Rebuild 11.63-mile Timber Tap-Winfield 69 kV line, 954 ACSR | 72 | 72 | 72 | 72 | 11.63 | 18 | 6 |  | 0.0309 | 0.2101 | 0.05164 | Line switches limit to 72 MVA. $790k per mile | 8161986 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-06-01
2009-AGP2 | AFS6NC |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS6NC1T35521SP | TO->FROM | TIMBER JUNCTION - UDALL 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533559 | UDALL 2 69.000 | 533558 | TIMBJCT2 69.000 | 0 |  | 1 | 21SP | 43 | 43 | 0 | 91.6404 | 91.6404 | 103.9712 | [7 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  | 45 |  | WERE | RICHLAND - UDALL 69KV CKT 1 | Tear down / Rebuild 8.48-mile Richland-Udall 69 kV line using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 8.48 | 13 | 7 | N | 0.01789 | 0.12177 | 0.02589 | MVA limit is conductor $790k per mile | 6699200 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6NC |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS6NC1T35521SP | TO->FROM | TIMBER JUNCTION - UDALL 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533559 | UDALL 2 69.000 | 533558 | TIMBJCT2 69.000 | 0 |  | 1 | 21SP | 43 | 43 | 0 | 91.6404 | 91.6404 | 103.9712 | [7 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  | 45 |  | WERE | TIMBER JUNCTION - UDALL 69KV CKT 1 | Tear down / Rebuild Udall-Timber Jct 69 kV using 954 kcmil ACSR | 116 | 128 | 116 | 128 | 2.01 | 4 | 2 | N | 0.00424 | 0.02886 | 0.00614 | MVA limit is conductor $790k per mile | 1587900 | 2010-01-01 | [38 empty] | 2011-06-01 | 2011-12-01 | 2011-10-01
2009-AGP2 | AFS6NC |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS6NC1T35521SP | TO->FROM | TIMBER JUNCTION - UDALL 69KV CKT 1 | PL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533559 | UDALL 2 69.000 | 533558 | TIMBJCT2 69.000 | 0 |  | 1 | 21SP | 43 | 43 | 0 | 91.6404 | 91.6404 | 103.9712 | [7 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 |  | 45 |  | WERE | BELL - PECK 69KV CKT 1 | Tear down / Rebuild 8.23 mile Bell-Peck 69 kV line with 1192 ACSR and replace CT | 134 | 147 | 134 | 147 | 8.23 | 18 | 5 | N |  |  |  | $790k per mile and $200k for CT | 6701700 | 2010-01-01 | [38 empty] | 2012-06-01 | 2012-12-01 | 2012-10-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T27475521SP | FROM->TO | TRUMANN - TRUMANN WEST AECC 161KV CKT 1 | S | EES | EES | EAINTH |  | 0 | 338169 | 5TRUMAN 161.00 | 338707 | 5TRUM-W# 161.00 | 0 |  | 1 | 21SP | 148 | 148 | 0 | 135.8 | 135.7604 | 135.9084 | [7 empty] | CATEGORYB | NONSINGLE | HERGETT TO N | 0 | 0 |  | 0 |  | 0 |  |  |  | 202 |  | EES | TRUMANN - TRUMANN WEST AECC 161KV CKT 1 | [53 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T15205521SP | FROM->TO | TRUMANN - TRUMANN WEST AECC 161KV CKT 1 | S | EES | EES | EAINTH |  | 0 | 338169 | 5TRUMAN 161.00 | 338707 | 5TRUM-W# 161.00 | 0 |  | 1 | 21SP | 148 | 148 | 0 | 134.9 | 134.9083 | 135.0083 | [7 empty] | CATEGORYB | SINGLE | NEWPORT - NEWPORT INDUSTRIAL 161KV CKT 1 | 0 | 338151 | 5NEWPO 161.00 | 338173 | 5NEW-IN 161.00 | 0 |  | 1 |  | 200 |  | EES | TRUMANN - TRUMANN WEST AECC 161KV CKT 1 | [53 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS61T15695521SP | FROM->TO | TRUMANN - TRUMANN WEST AECC 161KV CKT 1 | S | EES | EES | EAINTH |  | 0 | 338169 | 5TRUMAN 161.00 | 338707 | 5TRUM-W# 161.00 | 0 |  | 1 | 21SP | 148 | 148 | 0 | 132.1 | 132.1182 | 132.171 | [7 empty] | CATEGORYB | SINGLE | NEWPORT AB - NEWPORT INDUSTRIAL 161KV CKT 1 | 0 | 338172 | 5NEW-AB 161.00 | 338173 | 5NEW-IN 161.00 | 0 |  | 1 |  | 196 |  | EES | TRUMANN - TRUMANN WEST AECC 161KV CKT 1 | [53 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T4325021SP | FROM->TO | TUCO INTERCHANGE 230/115KV TRANSFORMER CKT 1 | REL | SPS | SPS | SPS-CNPL | SPS-CNPL | 0 | 525830 | TUCO_INT 6230.00 | 525828 | TUCO_INT 3115.00 | 0 |  | 1 | 21SP | 252 | 252 | 0 | 103.2 | 103.216 | 102.2691 | [7 empty] | CATEGORYB | SINGLE | TUCO INTERCHANGE 230/115KV TRANSFORMER CKT 2 | 0 | 525828 | TUCO_INT 3115.00 | 525830 | TUCO_INT 6230.00 | 0 |  | 2 |  | 258 |  | SPS | SWISHER 230/115KV TRANSFORMER CKT 1 | Upgrade existing Swisher 230/115 kV transformer to 252 MVA | [52 empty] | 2017-06-01 | 2017-06-01
2009-AGP2 | AFS6 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS61T4305021SP | FROM->TO | TUCO INTERCHANGE 230/115KV TRANSFORMER CKT 2 | REL | SPS | SPS | SPS-CNPL | SPS-CNPL | 0 | 525830 | TUCO_INT 6230.00 | 525828 | TUCO_INT 3115.00 | 0 |  | 2 | 21SP | 250 | 250 | 0 | 101.5 | 101.4702 | 100.5305 | [7 empty] | CATEGORYB | SINGLE | TUCO INTERCHANGE 230/115KV TRANSFORMER CKT 1 | 0 | 525828 | TUCO_INT 3115.00 | 525830 | TUCO_INT 6230.00 | 0 |  | 1 |  | 252 |  | SPS | SWISHER 230/115KV TRANSFORMER CKT 1 | Upgrade existing Swisher 230/115 kV transformer to 252 MVA | [52 empty] | 2017-06-01 | 2017-06-01
GEN-2006-010 | Turk | [7 empty] | GEN-2006-010AEPW5074545074565074581 |  | TURK (HEMP 1) 138/115/13.8KV TRANSFORMER CKT 1 | U | AEPW |  | SARK |  | 1 | 507454 | HEMPSTD4 138.00 | 507456 | HEMPSTD3 115.00 | 507458 | HEMP1 1 13.800 | 1 |  | 175 | 234 |  | 109.4 | [10 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | AEPW | TURK (HEMP 1) 138/115/13.8KV TRANSFORMER CKT 1 | Build Turk 138-115 kV station and relocate autotransformer (and spare) from Patterson to this new Turk station | [11 empty] | 9110000 | 9110000 | [39 empty] | 2012-07-01 | 2012-07-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61V5755516SP |  | TURKEY CREEK 69KV | REL | OKGE |  | ENID |  |  | 514735 | TURCRK 2 69.000 | [5 empty] | 16SP | [8 empty] | 0.91382 | 0.88563 | 0.98189 | 0.9 | 1.05 | CATEGORYB | SINGLE | DOVER SW (DOVER) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 520882 | DOVERSW4 138.00 | 520881 | DOVERSW2 69.000 | 521166 | DVRTERT 13.800 | 1 |  |  |  | WFEC | East Kingfisher Capacitor 69 kV | Install 18 Mvar capacitor at East Kingfisher bus. | [52 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61V5755516SP |  | TURKEY CREEK 69KV | REL | OKGE |  | ENID |  |  | 514735 | TURCRK 2 69.000 | [5 empty] | 16SP | [8 empty] | 0.91382 | 0.88563 | 0.98189 | 0.9 | 1.05 | CATEGORYB | SINGLE | DOVER SW (DOVER) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 520882 | DOVERSW4 138.00 | 520881 | DOVERSW2 69.000 | 521166 | DVRTERT 13.800 | 1 |  |  |  | WFEC | East Kingfisher Capacitor 69 kV | Install 18 Mvar capacitor at East Kingfisher bus. | [52 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS6 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS61V4235521SP |  | WAKITA 69KV | REL | WFEC |  | AEP-IM |  |  | 521085 | WAKITA 2 69.000 | [5 empty] | 21SP | [8 empty] | 0.92702 | 0.88657 | 0.97046 | 0.9 | 1.05 | CATEGORYB | SINGLE | FAIRVIEW - OKEENE 69KV CKT 1 | 0 | 521015 | OKEENE 2 69.000 | 520909 | FAIRVEW2 69.000 | 0 |  | 1 |  |  |  | WFEC | FAIRVIEW Capacitor 69KV | Install 18 Mvar capacitor at Fairview 69kV bus. | [52 empty] | 2017-06-01 | 2017-06-01
NA | [8 empty] | NAOKGE5153765147961 |  | WOODWARD - IODINE 138KV CKT 1 | U | OKGE | OKGE | ENID | ENID | 0 | 515376 |  | 514796 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | WOODWARD - IODINE 138KV CKT 1 | Tap Iodine to Woodward 138 kV line | [12 empty] | 221000000 | [39 empty] | 2010-01-01 | 2010-01-01
NA | [8 empty] | NAOKGE5153765147851 |  | WOODWARD - WOODWARD EHV 138KV CKT 1 | U | OKGE | OKGE | ENID | ENID | 0 | 515376 |  | 514785 |  |  |  | 1 |  | 537 | 616 | [12 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | WOODWARD - WOODWARD EHV 138KV CKT 1 | Build .5 miles of 138 kV and install terminal equipment | [12 empty] | 221000000 | [39 empty] | 2010-01-01 | 2010-01-01
NA | [8 empty] | NAOKGE5153765147852 |  | WOODWARD - WOODWARD EHV 138KV CKT 2 | U | OKGE | OKGE | ENID | ENID | 0 | 515376 |  | 514785 |  |  |  | 2 |  | 537 | 616 | [12 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | WOODWARD - WOODWARD EHV 138KV CKT 2 | Build .5 miles of 138 kV and install terminal equipment | [12 empty] | 221000000 | [39 empty] | 2010-01-01 | 2010-01-01
NA | [8 empty] | NAOKGE5153755153765157951 |  | WOODWARD 345/138KV TRANSFORMER CKT 1 | U | OKGE | OKGE | ENID | ENID | 1 | 515375 |  | 515376 |  | 515795 |  | 1 |  | 0 | 0 | [12 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | WOODWARD 345/138KV TRANSFORMER CKT 1 | Install 345/138 kV XF | [12 empty] | 221000000 | [39 empty] | 2010-01-01 | 2010-01-01
Formulas:
EOC = [DUN]

## tblAllFacilityLog-Thermals<100%
STUDYDES | STUDYDES2 | EVENTTYPE | AssessmentSOLUTIONTYPE | AssessmenFDNS-TERMINATION | SOLUTIONTYPE | FDNS-TERMINATION | GROUP | SCENARIO | FGName | DIRECTION | FacilityName | FacilityUpgradeCode | ModelArea1 | ModelArea2 | FZONENAME | TZONENAME | MONTFLAG | MONTFB | MONTFNAME | MONTTB1 | MONTTNAME1 | MONTTB2 | MONTTNAME2 | MONTCKT | Case | RATEA | RATEB | RATEC | Assessment Loading | BaseCaseLoading | TransferCaseLoading | NameOfBusWithMonitoredVoltage | Assessment Voltage | BaseCaseVoltage | TransferCaseVoltage | VINIT | VMIN | VMAX | CATEGORY | CONTTYPE | CONTNAME | CONTXFMRFLAG | CONTFB | CONTFNAME | CONTTB1 | CONTTNAME1 | CONTTB2 | CONTTNAME2 | CONTCKT | TransmissionProviderSystemImpactStudyNotesComments | RequiredRateB | TransmissionOwnerComments | OwnerDesignation | UpgradeName | UpgradeComponentWithinFacility | NewSummerA | NewSummerB | NewOtherA | NewOtherB | DistToConstruct | TotalLead | ConstructionLeadOnly | NewOrConstructWhileEnergized | NewR | NewX | NewB | CommentsRegardingUpgradeRequirements | NewCost | EffDate | NetPlantDate | ReusableEx_GrossValue | ReusableEx_NetValue | Reusable_EndofDepr | SalvageValue | NewCostWhileExpediting | EffDateExpedited | StartDeprExpedited | EndDeprExpedited | NetPlantDateExpedited | ReusableEx_GrossExpedited | ReusableEx_NetExpedited | Reusable_EndofDeprExpedited | SalvageValueExpedited | Generation 1 Owner & Unit (Name) | Generation 1 Redispatch Cost ($) | Generation 1 Redispatch Date (M/D/Y) | Generation 2 Owner & Unit (Name) | Generation 2 Redispatch Cost ($) | Generation 2 Redispatch Date (M/D/Y) | Generation 3 Owner & Unit (Name) | Generation 3 Redispatch Cost ($) | Generation 3 Redispatch Date (M/D/Y) | ActualCompletion | ActualNewCost | ActualNetPlantDate | ActualReusableEx_GrossValue | ActualReusableEx_NetValue | ActualReusable_EndofDepr | ActualSalvageValue | Actual_NewCostWhileExpediting | Actual_StartDeprExp | Actual_EndDeprExp | Actual_NetPlantDateExpedited | ActualReusableEx_GrossExpedited | ActualReusableEx_NetExpedited | ActualReusable_EndofDeprExpedited | Actual_SalvageValueExpedited | DUN | EOC | EarliestDate
2009-AGP2 | AFS5 | INVALID | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T2865021SP | FROM->TO | 36TH & LEWIS - 52ND & DELAWARE TAP 138KV CKT 1 | E | AEPW | AEPW | TULSA | TULSA | 0 | 509800 | 36LEWIS4 138.00 | 509776 | 52DELTP4 138.00 | 0 |  | 1 | 21SP | 265 | 309 | 0 | 101.4 | 101.4386 | 99.1972 | [7 empty] | CATEGORYB | SINGLE | ORU EAST TAP - RIVERSIDE STATION 138KV CKT 1 | 0 | 509783 | R.S.S.-4 138.00 | 509849 | ORU ETP4 138.00 | 0 |  | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T10515512SP | TO->FROM | 4FISHERTP - KEYSTONE DAM 138KV CKT 1 | E | SWPA | AECI | EMINTH | KAMO-OK | 0 | 505610 | KEYSTON4 138.00 | 300131 | 4FISHERTP 138.00 | 0 |  | 1 | 12SP | 174 | 174 | 0 | 96 | 95.9657 | 97.4 | [7 empty] | CATEGORYB | SINGLE | SILVER CITY - WEKIWA 138KV CKT 1 | 0 | 509757 | WEKIWA-4 138.00 | 300140 | 4SILVCTY 138.00 | 0 |  | 1
2009-AGP2 | AFS5 | INVALID | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T2435011SP | FROM->TO | 59TH ST - GILL ENERGY CENTER SOUTH 138KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533029 | 59TH ST4 138.00 | 533046 | GILL S 4 138.00 | 0 |  | 1 | 11SP | 191 | 210 | 0 | 96 | 96.031 | 97.4364 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER NORTH - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533040 | EVANS N4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T3085016SP | FROM->TO | 7SPORTSMAN 345/161KV TRANSFORMER CKT 1 | E | AECI | AECI | KAMO-OK | KAMO-OK | 0 | 300741 | 5SPORTSMAN 161.00 | 300740 | 7SPORTSMAN 345.00 | 0 |  | 1 | 16SP | 500 | 500 | 0 |  | 94.5995 | 95.4 | [7 empty] | CATEGORYB | SINGLE | 7SPORTSMAN 345/161KV TRANSFORMER CKT 2 | 0 | 300740 | 7SPORTSMAN 345.00 | 300741 | 5SPORTSMAN 161.00 | 0 |  | 2
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T6975021SP | FROM->TO | 7SPORTSMAN 345/161KV TRANSFORMER CKT 1 | E | AECI | AECI | KAMO-OK | KAMO-OK | 0 | 300741 | 5SPORTSMAN 161.00 | 300740 | 7SPORTSMAN 345.00 | 0 |  | 1 | 21SP | 500 | 500 | 0 | 95.4 | 95.3978 | 95.8 | [7 empty] | CATEGORYB | SINGLE | 7SPORTSMAN 345/161KV TRANSFORMER CKT 2 | 0 | 300740 | 7SPORTSMAN 345.00 | 300741 | 5SPORTSMAN 161.00 | 0 |  | 2
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T3075016SP | FROM->TO | 7SPORTSMAN 345/161KV TRANSFORMER CKT 2 | E | AECI | AECI | KAMO-OK | KAMO-OK | 0 | 300741 | 5SPORTSMAN 161.00 | 300740 | 7SPORTSMAN 345.00 | 0 |  | 2 | 16SP | 500 | 500 | 0 |  | 94.5995 | 95.4 | [7 empty] | CATEGORYB | SINGLE | 7SPORTSMAN 345/161KV TRANSFORMER CKT 1 | 0 | 300740 | 7SPORTSMAN 345.00 | 300741 | 5SPORTSMAN 161.00 | 0 |  | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T6965021SP | FROM->TO | 7SPORTSMAN 345/161KV TRANSFORMER CKT 2 | E | AECI | AECI | KAMO-OK | KAMO-OK | 0 | 300741 | 5SPORTSMAN 161.00 | 300740 | 7SPORTSMAN 345.00 | 0 |  | 2 | 21SP | 500 | 500 | 0 | 95.4 | 95.3978 | 95.8 | [7 empty] | CATEGORYB | SINGLE | 7SPORTSMAN 345/161KV TRANSFORMER CKT 1 | 0 | 300740 | 7SPORTSMAN 345.00 | 300741 | 5SPORTSMAN 161.00 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T2035516SP | FROM->TO | AFTON - FAIRLAND EDE TAP 69KV CKT 1 | E | GRDA | GRDA | GRDA | GRDA | 0 | 512633 | AFTON 2 69.000 | 512708 | FAIRTAP2 69.000 | 0 |  | 1 | 16SP | 72 | 72 | 0 |  | 94.8032 | 99.2 | [7 empty] | CATEGORYB | SINGLE | AFTON - MIAMI 161KV CKT 1 | 0 | 512631 | MIAMI 5 161.00 | 512632 | AFTON 5 161.00 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T4305512SP | TO->FROM | ALBION - PETERSBURG 115KV CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640318 | PETRSBG7 115.00 | 640054 | ALBION 7 115.00 | 0 |  | 1 | 12SP | 113 | 113 | 124 |  | 82.0809 | 96.9 | [7 empty] | CATEGORYB | SINGLE | LOUP CITY - NORTH LOUP 115KV CKT 1 | 0 | 640259 | LOUPCTY7 115.00 | 640284 | N.LOUP 7 115.00 | 0 |  | 1 | [58 empty] | 2011-12-01 | 2015-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T935010WP | FROM->TO | ALLEN - LEHIGH TAP 69KV CKT 1 | E | WERE | WERE | SEAST | SEAST | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 10WP | 32 | 32 | 0 |  | 88.3228 | 96.3 | [7 empty] | CATEGORYB | SINGLE | ORCHARD - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533643 | ORCHARD2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T10285510WP | FROM->TO | ALPINE AECC - AMITY SS 115KV CKT 1 | E | EES | EES | EAISTH-A | EAISTH | 0 | 338850 | 3ALPINE# 115.00 | 337674 | 3AMITY* 115.00 | 0 |  | 1 | 10WP | 98 | 98 | 0 | 95.6 | 95.5737 | 95.7 | [7 empty] | CATEGORYB | SINGLE | ELDORADO EHV - LONGWOOD 345KV CKT 1 | 0 | 508809 | LONGWD 7 345.00 | 337562 | 7ELDEHV 345.00 | 0 |  | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T10305510WP | TO->FROM | ALPINE AECC - BISMARK 115KV CKT 1 | E | EES | EES | EAISTH | EAISTH-A | 0 | 337678 | 3BISMRK 115.00 | 338850 | 3ALPINE# 115.00 | 0 |  | 1 | 10WP | 98 | 98 | 0 | 99.3 | 99.2569 | 99.4 | [7 empty] | CATEGORYB | SINGLE | ELDORADO EHV - LONGWOOD 345KV CKT 1 | 0 | 508809 | LONGWD 7 345.00 | 337562 | 7ELDEHV 345.00 | 0 |  | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T3995021SP | FROM->TO | AMARILLO SOUTH INTERCHANGE - FARMERS SUB 115KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524414 | AMA_SOUTH 3115.00 | 524377 | FARMERS 3115.00 | 0 |  | 1 | 21SP | 159 | 160 | 0 | 97.5 | 97.453 | 97.5 | [7 empty] | CATEGORYB | SINGLE | OSAGE SWITCHING STATION - SOUTH GEORGIA INTERCHANGE 115KV CKT 1 | 0 | 524322 | GEORGIA 3115.00 | 524345 | OSAGE 3115.00 | 0 |  | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T3325521SP | FROM->TO | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 | E | OKGE | OKGE |  |  | 2 | 514908 | ARCADIA7 345.00 | 514907 | ARCADIA4 138.00 | 515703 | ARCADI21 13.800 | 1 | 21SP | 493 | 493 | 0 | 98.9 | 98.9311 | 96.2 | [7 empty] | CATEGORYB | SINGLE | ARCADIA - NORTHWEST 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 514908 | ARCADIA7 345.00 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T3325521SP | FROM->TO | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 | E | OKGE | OKGE |  |  | 2 | 514908 | ARCADIA7 345.00 | 514907 | ARCADIA4 138.00 | 515703 | ARCADI21 13.800 | 1 | 21SP | 493 | 493 | 0 | 98.9 | 98.9311 | 96.2 | [7 empty] | CATEGORYB | SINGLE | ARCADIA - NORTHWEST 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 514908 | ARCADIA7 345.00 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T10195511SP | FROM->TO | ARCADIA (ARCADIA3) 345/138/13.8KV TRANSFORMER CKT 1 | E | OKGE | OKGE |  |  | 2 | 514908 | ARCADIA7 345.00 | 514907 | ARCADIA4 138.00 | 515704 | ARCADI31 13.800 | 1 | 11SP | 493 | 493 | 0 | 97.3 | 97.3199 | 97.3 | [7 empty] | CATEGORYB | SINGLE | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514907 | ARCADIA4 138.00 | 514908 | ARCADIA7 345.00 | 515703 | ARCADI21 13.800 | 1 | [58 empty] | 2013-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T10195511SP | FROM->TO | ARCADIA (ARCADIA3) 345/138/13.8KV TRANSFORMER CKT 1 | E | OKGE | OKGE |  |  | 2 | 514908 | ARCADIA7 345.00 | 514907 | ARCADIA4 138.00 | 515704 | ARCADI31 13.800 | 1 | 11SP | 493 | 493 | 0 | 97.3 | 97.3199 | 97.3 | [7 empty] | CATEGORYB | SINGLE | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514907 | ARCADIA4 138.00 | 514908 | ARCADIA7 345.00 | 515703 | ARCADI21 13.800 | 1 | [58 empty] | 2013-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T11045512SP | FROM->TO | ARCADIA (ARCADIA3) 345/138/13.8KV TRANSFORMER CKT 1 | E | OKGE | OKGE |  |  | 2 | 514908 | ARCADIA7 345.00 | 514907 | ARCADIA4 138.00 | 515704 | ARCADI31 13.800 | 1 | 12SP | 493 | 493 | 0 | 96.7 | 96.6814 | 97.7 | [7 empty] | CATEGORYB | SINGLE | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514907 | ARCADIA4 138.00 | 514908 | ARCADIA7 345.00 | 515703 | ARCADI21 13.800 | 1 | [58 empty] | 2013-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T11045512SP | FROM->TO | ARCADIA (ARCADIA3) 345/138/13.8KV TRANSFORMER CKT 1 | E | OKGE | OKGE |  |  | 2 | 514908 | ARCADIA7 345.00 | 514907 | ARCADIA4 138.00 | 515704 | ARCADI31 13.800 | 1 | 12SP | 493 | 493 | 0 | 96.7 | 96.6814 | 97.7 | [7 empty] | CATEGORYB | SINGLE | ARCADIA (ARCADIA2) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514907 | ARCADIA4 138.00 | 514908 | ARCADIA7 345.00 | 515703 | ARCADI21 13.800 | 1 | [58 empty] | 2013-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T2525016SP | TO->FROM | ARKANSAS CITY - PARIS 69KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533548 | PARIS 2 69.000 | 533542 | ARKCITY2 69.000 | 0 |  | 1 | 16SP | 72 | 72 | 0 |  | 78.5801 | 98.4 | [7 empty] | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T3715511SP | FROM->TO | ATHENS SWITCHING STATION - OWL CREEK 69KV CKT 1 | E | WERE | WERE | SEAST | SEAST | 0 | 533623 | ATHENS 2 69.000 | 533642 | OWL CRK2 69.000 | 0 |  | 1 | 11SP | 41 | 41 | 0 | 102.6 | 102.5956 | 98.9 | [7 empty] | CATEGORYB | SINGLE | ORCHARD - UNITED NO. 7 ROSE 69KV CKT 1 | 0 | 533643 | ORCHARD2 69.000 | 533649 | UN7ROSE2 69.000 | 0 |  | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T15785512SP | TO->FROM | AUBURN ROAD - JEFFREY ENERGY CENTER 230KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532852 | JEC 6 230.00 | 532851 | AUBURN 6 230.00 | 0 |  | 1 | 12SP | 565 | 565 | 0 | 97.3 | 97.2715 | 96.9 | [7 empty] | CATEGORYB | NONSINGLE | WRTOD400 | 0 | 0 |  | 0 |  | 0
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T26035521SP | TO->FROM | AUBURN ROAD - JEFFREY ENERGY CENTER 230KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532852 | JEC 6 230.00 | 532851 | AUBURN 6 230.00 | 0 |  | 1 | 21SP | 565 | 565 | 0 | 96.2 | 96.1966 | 98 | [7 empty] | CATEGORYB | NONSINGLE | WRTOD400 | 0 | 0 |  | 0 |  | 0
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T745510WP | TO->FROM | BISMARK - HOT SPRINGS WEST BUS 115KV CKT 1 | E | EES | EES | EAISTH | EAISTH | 0 | 337685 | 3HSEHVW 115.00 | 337678 | 3BISMRK 115.00 | 0 |  | 1 | 10WP | 98 | 98 | 0 | 96.4 | 96.3929 | 97.9 | [7 empty] | CATEGORYB | SINGLE | LYDIA - VALLIANT 345KV CKT 1 | 0 | 508298 | LYDIA 7 345.00 | 510911 | VALIANT7 345.00 | 0 |  | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T1645016SP | TO->FROM | BLUEBELL - PRATTVILLE 138KV CKT 1 | E | AEPW | OKGE | TULSA | MUSKOGEE | 0 | 509758 | PRATTV-4 138.00 | 515242 | BLUEBEL4 138.00 | 0 |  | 1 | 16SP | 202 | 235 | 0 |  | 94.3048 | 95.6 | [7 empty] | CATEGORYB | SINGLE | BEELINE - EXPLORER GLENPOOL 138KV CKT 1 | 0 | 515247 | BEELINE4 138.00 | 515248 | EXPLGLN4 138.00 | 0 |  | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T14875511SP | FROM->TO | BROOKLINE (BRKLTX1) 345/161/13.2KV TRANSFORMER CKT 1 | E | SPRM | SPRM | SPRM | SPRM | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549988 | BRKLNE XF1 113.200 | 1 | 11SP | 400 | 400 | 0 | 97.7 | 97.7034 | 99.6 | [7 empty] | CATEGORYB | NONSINGLE | SPRM-OPGD-02 | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T5325512WP | FROM->TO | BROOKLINE (BRKLTX1) 345/161/13.2KV TRANSFORMER CKT 1 | E | SPRM | SPRM | SPRM | SPRM | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549988 | BRKLNE XF1 113.200 | 1 | 12WP | 400 | 400 | 0 |  | 93.8356 | 96.8 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE (BRKLTX2) 345/161/13.2KV TRANSFORMER CKT 2 | 1 | 549969 | BROOKLINE 5161.00 | 549984 | BROOKLINE 7345.00 | 549989 | BRKLNE XF2 113.200 | 2 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T21255521SP | FROM->TO | BROOKLINE (BRKLTX1) 345/161/13.2KV TRANSFORMER CKT 1 | E | SPRM | SPRM | SPRM | SPRM | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549988 | BRKLNE XF1 113.200 | 1 | 21SP | 400 | 400 | 0 |  | 93.2799 | 96.8 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE (BRKLTX2) 345/161/13.2KV TRANSFORMER CKT 2 | 1 | 549969 | BROOKLINE 5161.00 | 549984 | BROOKLINE 7345.00 | 549989 | BRKLNE XF2 113.200 | 2 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T25745521SP | FROM->TO | BROOKLINE (BRKLTX1) 345/161/13.2KV TRANSFORMER CKT 1 | E | SPRM | SPRM | SPRM | SPRM | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549988 | BRKLNE XF1 113.200 | 1 | 21SP | 400 | 400 | 0 |  | 91.8161 | 95.7 | [7 empty] | CATEGORYB | NONSINGLE | SPRM-OPGD-02 | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2011-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T14855511SP | FROM->TO | BROOKLINE (BRKLTX2) 345/161/13.2KV TRANSFORMER CKT 2 | E | SPRM | SPRM | SPRM | SPRM | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549989 | BRKLNE XF2 113.200 | 2 | 11SP | 400 | 400 | 0 | 97.4 | 97.4375 | 99.3 | [7 empty] | CATEGORYB | NONSINGLE | SPRM-OPGD-01 | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T5305512WP | FROM->TO | BROOKLINE (BRKLTX2) 345/161/13.2KV TRANSFORMER CKT 2 | E | SPRM | SPRM | SPRM | SPRM | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549989 | BRKLNE XF2 113.200 | 2 | 12WP | 400 | 400 | 0 |  | 93.5428 | 96.5 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE (BRKLTX1) 345/161/13.2KV TRANSFORMER CKT 1 | 1 | 549969 | BROOKLINE 5161.00 | 549984 | BROOKLINE 7345.00 | 549988 | BRKLNE XF1 113.200 | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T21235521SP | FROM->TO | BROOKLINE (BRKLTX2) 345/161/13.2KV TRANSFORMER CKT 2 | E | SPRM | SPRM | SPRM | SPRM | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549989 | BRKLNE XF2 113.200 | 2 | 21SP | 400 | 400 | 0 |  | 92.9916 | 96.5 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE (BRKLTX1) 345/161/13.2KV TRANSFORMER CKT 1 | 1 | 549969 | BROOKLINE 5161.00 | 549984 | BROOKLINE 7345.00 | 549988 | BRKLNE XF1 113.200 | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T21235521SP | FROM->TO | BROOKLINE (BRKLTX2) 345/161/13.2KV TRANSFORMER CKT 2 | E | SPRM | SPRM | SPRM | SPRM | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549989 | BRKLNE XF2 113.200 | 2 | 21SP | 400 | 400 | 0 |  | 92.9916 | 96.5 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE (BRKLTX1) 345/161/13.2KV TRANSFORMER CKT 1 | 1 | 549969 | BROOKLINE 5161.00 | 549984 | BROOKLINE 7345.00 | 549988 | BRKLNE XF1 113.200 | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T21235521SP | FROM->TO | BROOKLINE (BRKLTX2) 345/161/13.2KV TRANSFORMER CKT 2 | E | SPRM | SPRM | SPRM | SPRM | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549989 | BRKLNE XF2 113.200 | 2 | 21SP | 400 | 400 | 0 |  | 92.9916 | 96.5 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE (BRKLTX1) 345/161/13.2KV TRANSFORMER CKT 1 | 1 | 549969 | BROOKLINE 5161.00 | 549984 | BROOKLINE 7345.00 | 549988 | BRKLNE XF1 113.200 | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T25735521SP | FROM->TO | BROOKLINE (BRKLTX2) 345/161/13.2KV TRANSFORMER CKT 2 | E | SPRM | SPRM | SPRM | SPRM | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549989 | BRKLNE XF2 113.200 | 2 | 21SP | 400 | 400 | 0 |  | 91.5529 | 95.4 | [7 empty] | CATEGORYB | NONSINGLE | SPRM-OPGD-01 | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T25735521SP | FROM->TO | BROOKLINE (BRKLTX2) 345/161/13.2KV TRANSFORMER CKT 2 | E | SPRM | SPRM | SPRM | SPRM | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549989 | BRKLNE XF2 113.200 | 2 | 21SP | 400 | 400 | 0 |  | 91.5529 | 95.4 | [7 empty] | CATEGORYB | NONSINGLE | SPRM-OPGD-01 | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T25735521SP | FROM->TO | BROOKLINE (BRKLTX2) 345/161/13.2KV TRANSFORMER CKT 2 | E | SPRM | SPRM | SPRM | SPRM | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549989 | BRKLNE XF2 113.200 | 2 | 21SP | 400 | 400 | 0 |  | 91.5529 | 95.4 | [7 empty] | CATEGORYB | NONSINGLE | SPRM-OPGD-01 | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2011-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T1885012SP | TO->FROM | BUCKEYE TAP - CUNNINGHAM STATION 115KV CKT 1 | E | SPS | SPS | SPS-PECO | SPS-HOBB | 0 | 527864 | CUNNINHAM 3115.00 | 528348 | BUCKEYE_TP 3115.00 | 0 |  | 1 | 12SP | 141 | 141 | 0 | 98 | 97.9797 | 99 | [7 empty] | CATEGORYB | SINGLE | LEA COUNTY REC-LOVINGTON INTERCHANGE 115/69KV TRANSFORMER CKT 1 | 0 | 528334 | LE-LOVINTON3115.00 | 528618 | LE-LOVINTON269.000 | 0 |  | 1 | [58 empty] | 2013-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T985016WP | TO->FROM | BUCKEYE TAP - CUNNINGHAM STATION 115KV CKT 1 | E | SPS | SPS | SPS-PECO | SPS-HOBB | 0 | 527864 | CUNNINHAM 3115.00 | 528348 | BUCKEYE_TP 3115.00 | 0 |  | 1 | 16WP | 156 | 156 | 0 | 98.1 | 98.1434 | 98.7 | [7 empty] | CATEGORYB | SINGLE | LEA COUNTY REC-LOVINGTON INTERCHANGE 115/69KV TRANSFORMER CKT 1 | 0 | 528334 | LE-LOVINTON3115.00 | 528618 | LE-LOVINTON269.000 | 0 |  | 1 | [58 empty] | 2013-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T15255511SP | TO->FROM | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | E | WERE | WERE | SEAST | SEAST | 0 | 533653 | WOLFCRK2 69.000 | 533626 | BURLJCT2 69.000 | 0 |  | 1 | 11SP | 72 | 72 | 0 |  | 92.1192 | 96.1 | [7 empty] | CATEGORYB | NONSINGLE | AMRN_OUTS6 | 0 | 0 |  | 0 |  | 0
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T10935511SP | TO->FROM | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | E | WERE | WERE | SEAST | SEAST | 0 | 533653 | WOLFCRK2 69.000 | 533626 | BURLJCT2 69.000 | 0 |  | 1 | 11SP | 72 | 72 | 0 |  | 91.6142 | 95 | [7 empty] | CATEGORYB | SINGLE | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T6085511WP | TO->FROM | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | E | WERE | WERE | SEAST | SEAST | 0 | 533653 | WOLFCRK2 69.000 | 533626 | BURLJCT2 69.000 | 0 |  | 1 | 11WP | 72 | 72 | 0 |  | 86.2226 | 99.5 | [7 empty] | CATEGORYB | SINGLE | NEOSHO (NEOSHO1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 533021 | NEOSHO 4 138.00 | 532824 | N345 1 1 13.800 | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T6145511WP | TO->FROM | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | E | WERE | WERE | SEAST | SEAST | 0 | 533653 | WOLFCRK2 69.000 | 533626 | BURLJCT2 69.000 | 0 |  | 1 | 11WP | 72 | 72 | 0 |  | 81.807 | 95.7 | [7 empty] | CATEGORYB | SINGLE | MARMTNE5 (MARMTN1X) 161/69/13.2KV TRANSFORMER CKT 1 | 1 | 532934 | MARMTNE5 161.00 | 533639 | MARMATN2 69.000 | 532955 | MARMATN1 13.200 | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T15955512SP | TO->FROM | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | E | WERE | WERE | SEAST | SEAST | 0 | 533653 | WOLFCRK2 69.000 | 533626 | BURLJCT2 69.000 | 0 |  | 1 | 12SP | 72 | 72 | 0 | 95.9 | 95.9234 | 96.4 | [7 empty] | CATEGORYB | NONSINGLE | AMRN_OUTS6 | 0 | 0 |  | 0 |  | 0
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T18445512SP | TO->FROM | BURLINGTON JUNCTION - WOLF CREEK 69KV CKT 1 | E | WERE | WERE | SEAST | SEAST | 0 | 533653 | WOLFCRK2 69.000 | 533626 | BURLJCT2 69.000 | 0 |  | 1 | 12SP | 72 | 72 | 0 | 95.1 | 95.0902 | 96.3 | [7 empty] | CATEGORYB | GENOUT | GEN533662 14-CHANUTE GENERATION SUB | 0 | 0 |  | 0 |  | 0
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T8665010WP | TO->FROM | CALICO ROCK - MELBOURNE 161KV CKT 1 | E | EES | EES | EAINTH |  | 0 | 338131 | 5MELBRN 161.00 | 338130 | 5CALCR 161.00 | 0 |  | 1 | 10WP | 148 | 148 | 0 | 103.9 | 103.8801 | 99.8 | [7 empty] | CATEGORYB | NONSINGLE | HERGETT TO N | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2010-10-01
2009-AGP2 | AFS5 | INVALID | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T765011WP | FROM->TO | CALICO ROCK - NORFORK 161KV CKT 1 | E | EES | SWPA |  | EMINTH | 0 | 338130 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 11WP | 148 | 148 | 0 | 102.5 | 102.544 | 98.6841 | [7 empty] | CATEGORYB | SINGLE | GRDA1 - TONECE7 345.00 345KV CKT 1 | 0 | 512650 | GRDA1 7 345.00 | 512750 | TONECE7 345.00 | 0 |  | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 | INVALID | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T2475011SP | FROM->TO | CANAL (CANAL 4X) 138/69/9.461KV TRANSFORMER CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 1 | 533033 | CANAL 4 138.00 | 533784 | CANAL 2 69.000 | 533101 | CANAL 1 9.4610 | 1 | 11SP | 150 | 165 | 187.5 | 97.6 | 97.6238 | 98.8366 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER NORTH - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533040 | EVANS N4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1
2009-AGP2 | AFS5 | INVALID | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T2765012SP | FROM->TO | CANAL (CANAL 4X) 138/69/9.461KV TRANSFORMER CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 1 | 533033 | CANAL 4 138.00 | 533784 | CANAL 2 69.000 | 533101 | CANAL 1 9.4610 | 1 | 12SP | 150 | 165 | 187.5 | 98.1 | 98.1452 | 99.9219 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER NORTH - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533040 | EVANS N4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T835512WP | FROM->TO | CANTON - OKEENE 69KV CKT 1 | E | WFEC | WFEC | AEP-OP | AEP-IM | 0 | 520843 | CANTON-2 69.000 | 521015 | OKEENE 2 69.000 | 0 |  | 1 | 12WP | 48 | 48 | 48 |  | 52.6861 | 96.6 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WWRDEHV7 345.00 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T4605512WP | FROM->TO | CANTON - OKEENE 69KV CKT 1 | E | WFEC | WFEC | AEP-OP | AEP-IM | 0 | 520843 | CANTON-2 69.000 | 521015 | OKEENE 2 69.000 | 0 |  | 1 | 12WP | 48 | 48 | 48 |  | 52.6908 | 96.5 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T715512WP | FROM->TO | CANTON - OKEENE 69KV CKT 1 | E | WFEC | WFEC | AEP-OP | AEP-IM | 0 | 520843 | CANTON-2 69.000 | 521015 | OKEENE 2 69.000 | 0 |  | 1 | 12WP | 48 | 48 | 48 |  | 52.5765 | 96.1 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T10575510WP | TO->FROM | CANTON - TALOGA 69KV CKT 1 | E | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521064 | TALOGA 2 69.000 | 520843 | CANTON-2 69.000 | 0 |  | 1 | 10WP | 42 | 46 | 46 |  | 58.6222 | 99.9 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1125510WP | TO->FROM | CANTON - TALOGA 69KV CKT 1 | E | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521064 | TALOGA 2 69.000 | 520843 | CANTON-2 69.000 | 0 |  | 1 | 10WP | 42 | 46 | 46 |  | 58.4804 | 97.7 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1715511SP | TO->FROM | CANTON - TALOGA 69KV CKT 1 | E | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521064 | TALOGA 2 69.000 | 520843 | CANTON-2 69.000 | 0 |  | 1 | 11SP | 33 | 39 | 39 |  | 58.1364 | 98.2 | [7 empty] | CATEGORYB | SINGLE | ROMAN NOSE - SOUTHARD 138KV CKT 1 | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1685511SP | TO->FROM | CANTON - TALOGA 69KV CKT 1 | E | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521064 | TALOGA 2 69.000 | 520843 | CANTON-2 69.000 | 0 |  | 1 | 11SP | 33 | 39 | 39 |  | 55.1878 | 95.1 | [7 empty] | CATEGORYB | SINGLE | EL RENO - ROMAN NOSE 138KV CKT 1 | 0 | 514819 | EL-RENO4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T835511WP | TO->FROM | CANTON - TALOGA 69KV CKT 1 | E | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521064 | TALOGA 2 69.000 | 520843 | CANTON-2 69.000 | 0 |  | 1 | 11WP | 42 | 46 | 46 |  | 68.8374 | 98.7 | [7 empty] | CATEGORYB | SINGLE | CEDARDALE - MOORELAND 138KV CKT 1 | 0 | 520848 | CEDRDAL4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T865511WP | TO->FROM | CANTON - TALOGA 69KV CKT 1 | E | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521064 | TALOGA 2 69.000 | 520843 | CANTON-2 69.000 | 0 |  | 1 | 11WP | 42 | 46 | 46 |  | 67.5627 | 97.3 | [7 empty] | CATEGORYB | SINGLE | CEDARDALE - OKEENE 138KV CKT 1 | 0 | 520848 | CEDRDAL4 138.00 | 521016 | OKEENE 4 138.00 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1925512SP | TO->FROM | CANTON - TALOGA 69KV CKT 1 | E | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521064 | TALOGA 2 69.000 | 520843 | CANTON-2 69.000 | 0 |  | 1 | 12SP | 33 | 39 | 39 |  | 57.2169 | 97.5 | [7 empty] | CATEGORYB | SINGLE | EL RENO - ROMAN NOSE 138KV CKT 1 | 0 | 514819 | EL-RENO4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T4025521SP | FROM->TO | CANYON EAST SUB - CANYON WEST SUB 115KV CKT 1 | E | SPS | SPS | SPS-CLHF | SPS-CLHF | 0 | 524523 | CANYON_EAST3115.00 | 524516 | CANYON_WEST3115.00 | 0 |  | 1 | 21SP | 96 | 96 | 0 | 97.2 | 97.1582 | 98 | [7 empty] | CATEGORYB | SINGLE | DEAF SMITH COUNTY INTERCHANGE - HEREFORD INTERCHANGE 115KV CKT 1 | 0 | 524606 | HEREFORD 3115.00 | 524622 | DEAFSMITH 3115.00 | 0 |  | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T2635516SP | TO->FROM | CANYON EAST SUB - OSAGE SWITCHING STATION 115KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524345 | OSAGE 3115.00 | 524523 | CANYON_EAST3115.00 | 0 |  | 1 | 16SP | 96 | 96 | 0 | 95.1 | 95.1185 | 95.9 | [7 empty] | CATEGORYB | SINGLE | DEAF SMITH COUNTY INTERCHANGE - HEREFORD INTERCHANGE 115KV CKT 1 | 0 | 524606 | HEREFORD 3115.00 | 524622 | DEAFSMITH 3115.00 | 0 |  | 1 | [58 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T30175521SP | TO->FROM | CANYON EAST SUB - OSAGE SWITCHING STATION 115KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524345 | OSAGE 3115.00 | 524523 | CANYON_EAST3115.00 | 0 |  | 1 | 21SP | 96 | 96 | 0 | 97.8 | 97.799 | 99.1 | [7 empty] | CATEGORYB | GENOUT | GEN525562 1-TOLK GEN #2 24 KV | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T30145521SP | TO->FROM | CANYON EAST SUB - OSAGE SWITCHING STATION 115KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524345 | OSAGE 3115.00 | 524523 | CANYON_EAST3115.00 | 0 |  | 1 | 21SP | 96 | 96 | 0 | 95.1 | -999 | 96.4 | [7 empty] | CATEGORYB | GENOUT | GEN525561 1-TOLK GEN #1 24 KV | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T25845521SP | TO->FROM | CAPROCK REC-PHILLIPS - CAPROCK REC-TATE 138KV CKT 1 | E | SPS | SPS | SPS-CAPR | SPS-CAPR | 0 | 522992 | CR-GARNDALE4138.00 | 522979 | CR-E_MIDLND4138.00 | 0 |  | 1 | 21SP | 208 | 271 | 0 | 98.7 | 98.6762 | 98.7 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-K48 | 0 | 0 |  | 0 |  | 0
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T4415521SP | FROM->TO | CARLISLE INTERCHANGE 230/115KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 0 | 526161 | CARLISLE 6230.00 | 526160 | CARLISLE 3115.00 | 0 |  | 1 | 21SP | 168 | 168 | 0 | 96.3 | 96.2868 | 95.9 | [7 empty] | CATEGORYB | SINGLE | WOLFFORTH INTERCHANGE 230/115KV TRANSFORMER CKT 1 | 0 | 526524 | WOLFFORTH 3115.00 | 526525 | WOLFFORTH 6230.00 | 0 |  | 1 | [58 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T13055012SP | TO->FROM | CENTENNIAL - COWSKIN 138KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533038 | COWSKIN4 138.00 | 533034 | CENTENN4 138.00 | 0 |  | 1 | 12SP | 232 | 232 | 0 | 99.1 | 99.1112 | 99.8 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T4525521SP | FROM->TO | CHAVES COUNTY INTERCHANGE - SAMSON SUB 115KV CKT 1 | E | SPS | SPS | SPS-PECO | SPS-PECO | 0 | 527482 | CHAVES_CNTY3115.00 | 527546 | SAMSON 3115.00 | 0 |  | 1 | 21SP | 120 | 154 | 0 | 96.7 | 96.7336 | 96.8 | [7 empty] | CATEGORYB | SINGLE | CHAVES COUNTY INTERCHANGE - URTON SUB 115KV CKT 1 | 0 | 527482 | CHAVES_CNTY3115.00 | 527501 | URTON 3115.00 | 0 |  | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T4515521SP | FROM->TO | CHAVES COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 2 | E | SPS | SPS | SPS-PECO | SPS-PECO | 0 | 527483 | CHAVES_CNTY6230.00 | 527482 | CHAVES_CNTY3115.00 | 0 |  | 2 | 21SP | 149 | 171 | 0 | 98.6 | 98.5639 | 98.6 | [7 empty] | CATEGORYB | SINGLE | CHAVES COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 1 | 0 | 527482 | CHAVES_CNTY3115.00 | 527483 | CHAVES_CNTY6230.00 | 0 |  | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T25895521SP | TO->FROM | CHERRY SUB - NICHOLS STATION 115KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524043 | NICHOLS 3115.00 | 524009 | CHERRY 3115.00 | 0 |  | 1 | 21SP | 159 | 160 | 0 | 98.3 | 98.3272 | 99.3 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-V03 | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2017-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T3695521SP | TO->FROM | CHERRY SUB - NICHOLS STATION 115KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524043 | NICHOLS 3115.00 | 524009 | CHERRY 3115.00 | 0 |  | 1 | 21SP | 159 | 160 | 0 |  | 94.2561 | 95.2 | [7 empty] | CATEGORYB | SINGLE | EAST PLANT INTERCHANGE - WHITAKER SUB 115KV CKT 1 | 0 | 524058 | WHITAKER 3115.00 | 524162 | EAST_PLANT 3115.00 | 0 |  | 1 | [58 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T3895521SP | FROM->TO | CHERRY SUB - NORTHWEST INTERCHANGE 115KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524009 | CHERRY 3115.00 | 524106 | NORTHWEST 3115.00 | 0 |  | 1 | 21SP | 159 | 160 | 0 | 98.1 | 98.11 | 98.6 | [7 empty] | CATEGORYB | SINGLE | OSAGE SWITCHING STATION - SOUTH GEORGIA INTERCHANGE 115KV CKT 1 | 0 | 524322 | GEORGIA 3115.00 | 524345 | OSAGE 3115.00 | 0 |  | 1
2009-AGP2 | AFS5 | INVALID | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T2735012SP | TO->FROM | CHISHOLM - MAIZE 4 138.00 138KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533054 | MAIZE 4 138.00 | 533035 | CHISHLM4 138.00 | 0 |  | 1 | 12SP | 382 | 382 | 0 | 96.6 | 96.6141 | 95.3959 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER NORTH - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533040 | EVANS N4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1
2009-AGP2 | AFS5 | INVALID | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T2755012SP | FROM->TO | CHISHOLM - RIPLEY 69KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533786 | CHISHLM2 69.000 | 533832 | RIPLEYM2 69.000 | 0 |  | 1 | 12SP | 134 | 147 | 0 | 96 | 95.9617 | 96.9078 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER NORTH - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533040 | EVANS N4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T12725012SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 12SP | 43 | 43 | 0 |  | 65.8219 | 99 | [7 empty] | CATEGORYB | NONSINGLE | OGE3TERM7 | 0 | 0 |  | 0 |  | 0
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T1285012SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 12SP | 43 | 43 | 0 |  | 65.5727 | 97.6 | [7 empty] | CATEGORYB | SINGLE | KILDARE4 - WHITE EAGLE 138KV CKT 1 | 0 | 514760 | KILDARE4 138.00 | 514761 | WHEAGLE4 138.00 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T14945016SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 16SP | 43 | 43 | 0 |  | 75.705 | 99.5 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-41B | 0 | 0 |  | 0 |  | 0
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T26485021SP | TO->FROM | CITY OF WINFIELD - TIMBER JUNCTION 69KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533558 | TIMBJCT2 69.000 | 533561 | WINFLD 2 69.000 | 0 |  | 1 | 21SP | 43 | 43 | 0 |  | 84.2099 | 95.8 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-41B | 0 | 0 |  | 0 |  | 0
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T2365516SP | TO->FROM | CLASSEN - SW 5TAP 138KV CKT 1 | E | OKGE | OKGE |  |  | 0 | 514921 | SW 5TAP4 138.00 | 514922 | CLASSEN4 138.00 | 0 |  | 1 | 16SP | 191 | 191 | 0 | 101 | 100.9786 | 98.3 | [7 empty] | CATEGORYB | SINGLE | COUNCIL - MUSTANG 138KV CKT 1 | 0 | 514861 | MUSTANG4 138.00 | 514865 | COUNCIL4 138.00 | 0 |  | 1 | [58 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T2365516SP | TO->FROM | CLASSEN - SW 5TAP 138KV CKT 1 | E | OKGE | OKGE |  |  | 0 | 514921 | SW 5TAP4 138.00 | 514922 | CLASSEN4 138.00 | 0 |  | 1 | 16SP | 191 | 191 | 0 | 101 | 100.9786 | 98.3 | [7 empty] | CATEGORYB | SINGLE | COUNCIL - MUSTANG 138KV CKT 1 | 0 | 514861 | MUSTANG4 138.00 | 514865 | COUNCIL4 138.00 | 0 |  | 1 | [58 empty] | 2017-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T15865512SP | TO->FROM | CLAY - SPRINGFIELD 161KV CKT 1 | E | SWPA | SPRM | EMINTH | SPRM | 0 | 505492 | SPRGFLD5 161.00 | 549970 | CLAY 5161.00 | 0 |  | 1 | 12SP | 167 | 167 | 0 |  | 91.0253 | 96.3 | [7 empty] | CATEGORYB | NONSINGLE | AI03 | 0 | 0 |  | 0 |  | 0
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T11115512SP | TO->FROM | CLEO CORNER - GLASS MOUNTAIN 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514788 | GLASMTN4 138.00 | 514778 | CLEOCOR4 138.00 | 0 |  | 1 | 12SP | 133 | 153 | 0 |  | 70.7771 | 99.8 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T11115512SP | TO->FROM | CLEO CORNER - GLASS MOUNTAIN 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514788 | GLASMTN4 138.00 | 514778 | CLEOCOR4 138.00 | 0 |  | 1 | 12SP | 133 | 153 | 0 |  | 70.7771 | 99.8 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 | [20 empty] | 41061 | [37 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1995512SP | TO->FROM | CLEO CORNER - GLASS MOUNTAIN 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514788 | GLASMTN4 138.00 | 514778 | CLEOCOR4 138.00 | 0 |  | 1 | 12SP | 133 | 153 | 0 |  | 70.6038 | 99.5 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1995512SP | TO->FROM | CLEO CORNER - GLASS MOUNTAIN 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514788 | GLASMTN4 138.00 | 514778 | CLEOCOR4 138.00 | 0 |  | 1 | 12SP | 133 | 153 | 0 |  | 70.6038 | 99.5 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T14965016SP | TO->FROM | CRESWELL - PECKHMT4 138.00 138KV CKT 1 | E | OKGE | WERE | ENID | SCENTRAL | 0 | 515381 | PECKHMT4 138.00 | 532981 | CRESWLN4 138.00 | 0 |  | 1 | 16SP | 160 | 168 | 0 |  | 81.8458 | 96.5 | [7 empty] | CATEGORYB | NONSINGLE | WRTOD1104 | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T14965016SP | TO->FROM | CRESWELL - PECKHMT4 138.00 138KV CKT 1 | E | OKGE | WERE | ENID | SCENTRAL | 0 | 515381 | PECKHMT4 138.00 | 532981 | CRESWLN4 138.00 | 0 |  | 1 | 16SP | 160 | 168 | 0 |  | 81.8458 | 96.5 | [7 empty] | CATEGORYB | NONSINGLE | WRTOD1104 | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T26505021SP | TO->FROM | CRESWELL - PECKHMT4 138.00 138KV CKT 1 | E | OKGE | WERE | ENID | SCENTRAL | 0 | 515381 | PECKHMT4 138.00 | 532981 | CRESWLN4 138.00 | 0 |  | 1 | 21SP | 160 | 168 | 0 |  | -999 | 99.2 | [7 empty] | CATEGORYB | NONSINGLE | WRTOD1104 | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T26505021SP | TO->FROM | CRESWELL - PECKHMT4 138.00 138KV CKT 1 | E | OKGE | WERE | ENID | SCENTRAL | 0 | 515381 | PECKHMT4 138.00 | 532981 | CRESWLN4 138.00 | 0 |  | 1 | 21SP | 160 | 168 | 0 |  | -999 | 99.2 | [7 empty] | CATEGORYB | NONSINGLE | WRTOD1104 | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2011-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T5755021SP | TO->FROM | CROSSTOWN - GRAND AVENUE WEST 161KV CKT 1 | E | KACP | KACP | DWNTWN | DWNTWN | 0 | 542988 | GRAND W5 161.00 | 542990 | CROSTWN5 161.00 | 0 |  | 1 | 21SP | 259 | 259 | 0 | 98.8 | 98.7749 | 97.1 | [7 empty] | CATEGORYB | SINGLE | CROSSTOWN - NORTHEAST 161KV CKT 1 | 0 | 542985 | NEAST 5 161.00 | 542990 | CROSTWN5 161.00 | 0 |  | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T5805021SP | TO->FROM | CROSSTOWN - NORTHEAST 161KV CKT 1 | E | KACP | KACP | DWNTWN | DWNTWN | 0 | 542985 | NEAST 5 161.00 | 542990 | CROSTWN5 161.00 | 0 |  | 1 | 21SP | 259 | 259 | 0 | 98.8 | 98.7966 | 96.6 | [7 empty] | CATEGORYB | SINGLE | GRAND AVENUE REACTOR - NORTHEAST REACTOR 161KV CKT 1 | 0 | 543636 | GRANDREA 161.00 | 543637 | NEASTREA 161.00 | 0 |  | 1 | [58 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T5765021SP | TO->FROM | CROSSTOWN - NORTHEAST 161KV CKT 1 | E | KACP | KACP | DWNTWN | DWNTWN | 0 | 542985 | NEAST 5 161.00 | 542990 | CROSTWN5 161.00 | 0 |  | 1 | 21SP | 259 | 259 | 0 | 98.6 | 98.6178 | 96.4 | [7 empty] | CATEGORYB | SINGLE | NORTHEAST - NORTHEAST REACTOR 161KV CKT 1 | 0 | 542985 | NEAST 5 161.00 | 543637 | NEASTREA 161.00 | 0 |  | 1 | [58 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T14905511SP | TO->FROM | CUDAHY - JUDSON LARGE 115KV CKT 1 | E | SUNC | SUNC |  |  | 0 | 539671 | FTDODGE3 115.00 | 539659 | CUDAHY 3 115.00 | 0 |  | 1 | 11SP | 120.7 | 129.5 | 0 | 96.5 | 96.5033 | 97.7 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SUNC-14 | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2011-06-01
2009-AGP2 | AFS5 | INVALID | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T3045512SP | TO->FROM | CUDAHY - JUDSON LARGE 115KV CKT 1 | E | SUNC | SUNC |  |  | 0 | 539671 | FTDODGE3 115.00 | 539659 | CUDAHY 3 115.00 | 0 |  | 1 | 12SP | 120.7 | 129.5 | 0 | 95.9 | 95.866 | 99.9025 | [7 empty] | CATEGORYB | SINGLE | HOLCOMB - PLYMELL 115KV CKT 1 | 0 | 531393 | PLYMELL3 115.00 | 531448 | HOLCOMB3 115.00 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T15565512SP | TO->FROM | CUDAHY - JUDSON LARGE 115KV CKT 1 | E | SUNC | SUNC |  |  | 0 | 539671 | FTDODGE3 115.00 | 539659 | CUDAHY 3 115.00 | 0 |  | 1 | 12SP | 120.7 | 129.5 | 0 |  | 92.0865 | 96 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SUNC-14 | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2011-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T4495521SP | TO->FROM | DENVER CITY INTERCHANGE N. - MUSTANG STATION N. 115KV CKT 1 | E | SPS | SPS | SPS-YOGS | SPS-YOGS | 0 | 527146 | MUSTANG_N 3115.00 | 527130 | DENVER_N 3115.00 | 0 |  | 1 | 21SP | 239 | 280 | 0 | 96.6 | 96.5786 | 96.6 | [7 empty] | CATEGORYB | SINGLE | DENVER CITY INTERCHANGE S. - MUSTANG STATION S. 115KV CKT 1 | 0 | 527136 | DENVER_S 3115.00 | 527148 | MUSTANG_S 3115.00 | 0 |  | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T4485521SP | TO->FROM | DENVER CITY INTERCHANGE S. - MUSTANG STATION S. 115KV CKT 1 | E | SPS | SPS | SPS-YOGS | SPS-YOGS | 0 | 527148 | MUSTANG_S 3115.00 | 527136 | DENVER_S 3115.00 | 0 |  | 1 | 21SP | 243 | 280 | 0 | 95.5 | 95.4965 | 95.5 | [7 empty] | CATEGORYB | SINGLE | DENVER CITY INTERCHANGE N. - MUSTANG STATION N. 115KV CKT 1 | 0 | 527130 | DENVER_N 3115.00 | 527146 | MUSTANG_N 3115.00 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T2495521SP | FROM->TO | DIANA - PERDUE 138KV CKT 1 | E | AEPW | AEPW | NWLANTEC | MTPLNTEC | 0 | 508831 | DIANA 4 138.00 | 508351 | PERDUE 4 138.00 | 0 |  | 1 | 21SP | 246 | 287 | 0 |  | 93.3759 | 98.8 | [7 empty] | CATEGORYB | SINGLE | ANTIOCH (RAYBURN) - NEW YORK (RAYBURN) 138KV CKT 1 | 0 | 509244 | ANTIOCH4 138.00 | 509255 | NEWYORK4 138.00 | 0 |  | 1 | [20 empty] | 41061 | [37 empty] | 2017-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1815521SP | FROM->TO | DIANA - PERDUE 138KV CKT 1 | E | AEPW | AEPW | NWLANTEC | MTPLNTEC | 0 | 508831 | DIANA 4 138.00 | 508351 | PERDUE 4 138.00 | 0 |  | 1 | 21SP | 246 | 287 | 0 |  | 93.0283 | 98.6 | [7 empty] | CATEGORYB | SINGLE | CHAPEL HILL REC - WELSH REC 138KV CKT 1 | 0 | 508337 | CHAPELH4 138.00 | 508355 | WELSHRE4 138.00 | 0 |  | 1 | [58 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T10615516SP | FROM->TO | DIANA (DIANA 3) 345/138/13.8KV TRANSFORMER CKT 3 | E | AEPW | AEPW | NWLA-ETX | NWLANTEC | 2 | 508832 | DIANA 7 345.00 | 508831 | DIANA 4 138.00 | 508845 | DIANA-N1 13.800 | 3 | 16SP | 309 | 330 | 0 | 96.3 | 96.2826 | 99.3 | [7 empty] | CATEGORYB | SINGLE | DIANA (DIANA 1) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 508831 | DIANA 4 138.00 | 508832 | DIANA 7 345.00 | 508844 | DIANA-S1 13.800 | 1 | [58 empty] | 2013-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T18235521SP | FROM->TO | DIANA (DIANA 3) 345/138/13.8KV TRANSFORMER CKT 3 | E | AEPW | AEPW | NWLA-ETX | NWLANTEC | 2 | 508832 | DIANA 7 345.00 | 508831 | DIANA 4 138.00 | 508845 | DIANA-N1 13.800 | 3 | 21SP | 309 | 330 | 0 |  | 90.8913 | 97.2 | [7 empty] | CATEGORYB | SINGLE | DIANA (DIANA 2) 345/138/13.8KV TRANSFORMER CKT 2 | 1 | 508831 | DIANA 4 138.00 | 508832 | DIANA 7 345.00 | 508843 | DIANA-M1 13.800 | 2 | [20 empty] | 41061 | [37 empty] | 2013-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T1315012SP | FROM->TO | DMNCRKT4 - WHITE EAGLE 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 515412 | DMNCRKT4 138.00 | 514761 | WHEAGLE4 138.00 | 0 |  | 1 | 12SP | 287 | 287 | 0 |  | 91.0952 | 95.5 | [7 empty] | CATEGORYB | SINGLE | SOONER - SOONER PUMP TAP 138KV CKT 1 | 0 | 514798 | SNRPMPT4 138.00 | 514802 | SOONER 4 138.00 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T1315012SP | FROM->TO | DMNCRKT4 - WHITE EAGLE 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 515412 | DMNCRKT4 138.00 | 514761 | WHEAGLE4 138.00 | 0 |  | 1 | 12SP | 287 | 287 | 0 |  | 91.0952 | 95.5 | [7 empty] | CATEGORYB | SINGLE | SOONER - SOONER PUMP TAP 138KV CKT 1 | 0 | 514798 | SNRPMPT4 138.00 | 514802 | SOONER 4 138.00 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T1225012SP | FROM->TO | DMNCRKT4 - WHITE EAGLE 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 515412 | DMNCRKT4 138.00 | 514761 | WHEAGLE4 138.00 | 0 |  | 1 | 12SP | 287 | 287 | 0 |  | 91.0634 | 95.4 | [7 empty] | CATEGORYB | SINGLE | OSAGE - SOONER PUMP TAP 138KV CKT 1 | 0 | 514743 | OSAGE 4 138.00 | 514798 | SNRPMPT4 138.00 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T1225012SP | FROM->TO | DMNCRKT4 - WHITE EAGLE 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 515412 | DMNCRKT4 138.00 | 514761 | WHEAGLE4 138.00 | 0 |  | 1 | 12SP | 287 | 287 | 0 |  | 91.0634 | 95.4 | [7 empty] | CATEGORYB | SINGLE | OSAGE - SOONER PUMP TAP 138KV CKT 1 | 0 | 514743 | OSAGE 4 138.00 | 514798 | SNRPMPT4 138.00 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T11175512SP | TO->FROM | DOVER SW - OKEENE 138KV CKT 1 | E | WFEC | WFEC | AEP-IM | AEP-IM | 0 | 521016 | OKEENE 4 138.00 | 520882 | DOVERSW4 138.00 | 0 |  | 1 | 12SP | 106 | 130 | 130 |  | 61.7256 | 96.2 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T2055512SP | TO->FROM | DOVER SW - OKEENE 138KV CKT 1 | E | WFEC | WFEC | AEP-IM | AEP-IM | 0 | 521016 | OKEENE 4 138.00 | 520882 | DOVERSW4 138.00 | 0 |  | 1 | 12SP | 106 | 130 | 130 |  | 61.5669 | 96 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T855512WP | TO->FROM | DOVER SW - OKEENE 138KV CKT 1 | E | WFEC | WFEC | AEP-IM | AEP-IM | 0 | 521016 | OKEENE 4 138.00 | 520882 | DOVERSW4 138.00 | 0 |  | 1 | 12WP | 137 | 143 | 143 |  | 62.3003 | 96.8 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WWRDEHV7 345.00 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T4625512WP | TO->FROM | DOVER SW - OKEENE 138KV CKT 1 | E | WFEC | WFEC | AEP-IM | AEP-IM | 0 | 521016 | OKEENE 4 138.00 | 520882 | DOVERSW4 138.00 | 0 |  | 1 | 12WP | 137 | 143 | 143 |  | 62.3137 | 96.7 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T735512WP | TO->FROM | DOVER SW - OKEENE 138KV CKT 1 | E | WFEC | WFEC | AEP-IM | AEP-IM | 0 | 521016 | OKEENE 4 138.00 | 520882 | DOVERSW4 138.00 | 0 |  | 1 | 12WP | 137 | 143 | 143 |  | 62.1621 | 96.3 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T2515012SP | TO->FROM | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | E | WERE | WERE | NEAST | NCENTRAL | 0 | 532852 | JEC 6 230.00 | 532861 | EMANHAT6 230.00 | 0 |  | 1 | 12SP | 446 | 446 | 0 | 98.9 | 98.927 | 99.9 | [7 empty] | CATEGORYB | SINGLE | AUBURN ROAD - JEFFREY ENERGY CENTER 230KV CKT 1 | 0 | 532851 | AUBURN 6 230.00 | 532852 | JEC 6 230.00 | 0 |  | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T5225021SP | TO->FROM | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | E | WERE | WERE | NEAST | NCENTRAL | 0 | 532852 | JEC 6 230.00 | 532861 | EMANHAT6 230.00 | 0 |  | 1 | 21SP | 446 | 490 | 0 | 95.6 | 95.5916 | 95.3 | [7 empty] | CATEGORYB | SINGLE | JEFFERY ENERGY CENTER - MORRIS COUNTY 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532770 | MORRIS 7 345.00 | 0 |  | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T10905511SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | E | WERE | WERE | NCENTRAL | NCENTRAL | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 11SP | 280 | 308 | 350 | 96.6 | 96.5824 | 97.7 | [7 empty] | CATEGORYB | SINGLE | MCDOWELL CREEK (MCDWL 1X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T10725511SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | E | WERE | WERE | NCENTRAL | NCENTRAL | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 11SP | 280 | 308 | 350 | 95.5 | 95.5259 | 96.2 | [7 empty] | CATEGORYB | SINGLE | MORRIS COUNTY (MORRIS1X) 345/230/14.4KV TRANSFORMER CKT 1 | 1 | 532770 | MORRIS 7 345.00 | 532863 | MORRIS 6 230.00 | 532809 | MORRIS 1 14.400 | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T3635521SP | FROM->TO | EAST PLANT INTERCHANGE - MANHATTAN SUB 115KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524162 | EAST_PLANT 3115.00 | 524224 | MANHATTAN 3115.00 | 0 |  | 1 | 21SP | 160 | 160 | 0 | 95.4 | 95.3778 | 96.6 | [7 empty] | CATEGORYB | SINGLE | Harrington Station Mid Bus - RANDALL COUNTY INTERCHANGE 230KV CKT 1 | 0 | 523978 | HARRNG_MID 6230.00 | 524365 | RANDALL 6230.00 | 0 |  | 1 | [58 empty] | 2017-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T3645521SP | FROM->TO | EAST PLANT INTERCHANGE - PIERCE STREET TAP 115KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524162 | EAST_PLANT 3115.00 | 524185 | PIERCE_TP 3115.00 | 0 |  | 1 | 21SP | 160 | 160 | 0 |  | 94.2102 | 95.2 | [7 empty] | CATEGORYB | SINGLE | CHERRY SUB - NORTHWEST INTERCHANGE 115KV CKT 1 | 0 | 524009 | CHERRY 3115.00 | 524106 | NORTHWEST 3115.00 | 0 |  | 1 | [58 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T12945012SP | FROM->TO | EAST PLANT INTERCHANGE 230/115KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524163 | EAST_PLANT 6230.00 | 524162 | EAST_PLANT 3115.00 | 0 |  | 1 | 12SP | 218 | 251 | 0 | 95.9 | 95.8712 | 96.1 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-K19 | 0 | 0 |  | 0 |  | 0
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T25815521SP | FROM->TO | EAST PLANT INTERCHANGE 230/115KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524163 | EAST_PLANT 6230.00 | 524162 | EAST_PLANT 3115.00 | 0 |  | 1 | 21SP | 218 | 251 | 0 | 98 | 98.0467 | 98.5 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-K19 | 0 | 0 |  | 0 |  | 0
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T3615521SP | FROM->TO | EAST PLANT INTERCHANGE 230/115KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524163 | EAST_PLANT 6230.00 | 524162 | EAST_PLANT 3115.00 | 0 |  | 1 | 21SP | 218 | 251 | 0 | 95.8 | 95.8294 | 96.3 | [7 empty] | CATEGORYB | SINGLE | Harrington Station Mid Bus - RANDALL COUNTY INTERCHANGE 230KV CKT 1 | 0 | 523978 | HARRNG_MID 6230.00 | 524365 | RANDALL 6230.00 | 0 |  | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1165516SP | FROM->TO | EASTON REC - KNOX LEE 138KV CKT 1 | E | AEPW | AEPW | RKHLNTEC | LONG-MAR | 0 | 509092 | EASTON 4 138.00 | 508548 | KNOXLEE4 138.00 | 0 |  | 1 | 16SP | 455 | 478 | 0 | 96.2 | 96.1697 | 96.8 | [7 empty] | CATEGORYB | SINGLE | DIANA - PERDUE 138KV CKT 1 | 0 | 508351 | PERDUE 4 138.00 | 508831 | DIANA 4 138.00 | 0 |  | 1 | [58 empty] | 2012-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1455516SP | FROM->TO | EASTON REC - KNOX LEE 138KV CKT 1 | E | AEPW | AEPW | RKHLNTEC | LONG-MAR | 0 | 509092 | EASTON 4 138.00 | 508548 | KNOXLEE4 138.00 | 0 |  | 1 | 16SP | 455 | 478 | 0 | 95.6 | 95.6308 | 96.6 | [7 empty] | CATEGORYB | SINGLE | TEXAS EASTMAN - WHITNEY 138KV CKT 1 | 0 | 508575 | WHITNEY4 138.00 | 508582 | EASTEX 4 138.00 | 0 |  | 1 | [58 empty] | 2012-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T2045521SP | FROM->TO | EASTON REC - KNOX LEE 138KV CKT 1 | E | AEPW | AEPW | RKHLNTEC | LONG-MAR | 0 | 509092 | EASTON 4 138.00 | 508548 | KNOXLEE4 138.00 | 0 |  | 1 | 21SP | 455 | 478 | 0 |  | 83.5564 | 98.3 | [7 empty] | CATEGORYB | SINGLE | PIRKEY - WHITNEY 138KV CKT 1 | 0 | 508562 | PIRKEY 4 138.00 | 508575 | WHITNEY4 138.00 | 0 |  | 1 | [58 empty] | 2012-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1175516SP | TO->FROM | EASTON REC - PIRKEY 138KV CKT 1 | E | AEPW | AEPW | LONG-MAR | RKHLNTEC | 0 | 508562 | PIRKEY 4 138.00 | 509092 | EASTON 4 138.00 | 0 |  | 1 | 16SP | 460 | 478 | 0 | 97.7 | 97.6509 | 98.3 | [7 empty] | CATEGORYB | SINGLE | DIANA - PERDUE 138KV CKT 1 | 0 | 508351 | PERDUE 4 138.00 | 508831 | DIANA 4 138.00 | 0 |  | 1 | [58 empty] | 2012-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1465516SP | TO->FROM | EASTON REC - PIRKEY 138KV CKT 1 | E | AEPW | AEPW | LONG-MAR | RKHLNTEC | 0 | 508562 | PIRKEY 4 138.00 | 509092 | EASTON 4 138.00 | 0 |  | 1 | 16SP | 460 | 478 | 0 | 97.2 | 97.1566 | 98.1 | [7 empty] | CATEGORYB | SINGLE | TEXAS EASTMAN - WHITNEY 138KV CKT 1 | 0 | 508575 | WHITNEY4 138.00 | 508582 | EASTEX 4 138.00 | 0 |  | 1 | [58 empty] | 2012-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1405516SP | TO->FROM | EASTON REC - PIRKEY 138KV CKT 1 | E | AEPW | AEPW | LONG-MAR | RKHLNTEC | 0 | 508562 | PIRKEY 4 138.00 | 509092 | EASTON 4 138.00 | 0 |  | 1 | 16SP | 460 | 478 | 0 |  | 94.4437 | 95 | [7 empty] | CATEGORYB | SINGLE | LEBROCK - TENASKA RUSK COUNTY 345KV CKT 1 | 0 | 508572 | LEBROCK7 345.00 | 508585 | TENRUSK7 345.00 | 0 |  | 1 | [58 empty] | 2012-06-01
2009-AGP2 | AFS5UP |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS5UP1T1235512WP | TO->FROM | EDWARDSVILLE - MUND 115KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 533282 | MUND 3 115.00 | 533238 | EDWARVL3 115.00 | 0 |  | 1 | 12WP | 179 | 179 | 0 |  | 95.5646 | 98.3 | [7 empty] | CATEGORYB | SINGLE | 87TH 7 345.00 - CRAIG 345KV CKT 1 | 0 | 532775 | 87TH 7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1
2009-AGP2 | AFS5UP |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS5UP1T1165511WP | FROM->TO | EDWARDSVILLE (EDWRDV4X) 161/115/12.47KV TRANSFORMER CKT 1 | E | WERE | WERE | NEAST | NEAST | 1 | 533238 | EDWARVL3 115.00 | 532912 | EDWRDVL5 161.00 | 532940 | EDWRDVL1 12.470 | 1 | 11WP | 168 | 184.8 | 210 |  | 95.386 | 97.6 | [7 empty] | CATEGORYB | SINGLE | 87TH 7 345.00 - CRAIG 345KV CKT 1 | 0 | 532775 | 87TH 7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1
2009-AGP2 | AFS5UP |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS5UP1T1165511WP | FROM->TO | EDWARDSVILLE (EDWRDV4X) 161/115/12.47KV TRANSFORMER CKT 1 | E | WERE | WERE | NEAST | NEAST | 1 | 533238 | EDWARVL3 115.00 | 532912 | EDWRDVL5 161.00 | 532940 | EDWRDVL1 12.470 | 1 | 11WP | 168 | 184.8 | 210 |  | 95.386 | 97.6 | [7 empty] | CATEGORYB | SINGLE | 87TH 7 345.00 - CRAIG 345KV CKT 1 | 0 | 532775 | 87TH 7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T14675511SP | FROM->TO | EL PASO - FARBER 138KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 | 11SP | 160 | 168 | 0 |  | 79.7306 | 97.9 | [7 empty] | CATEGORYB | NONSINGLE | OGE3TERM7 | 0 | 0 |  | 0 |  | 0
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T15775516SP | FROM->TO | EL PASO - FARBER 138KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 | 16SP | 160 | 168 | 0 |  | 85.4991 | 97.9 | [7 empty] | CATEGORYB | NONSINGLE | OGE3TERM7 | 0 | 0 |  | 0 |  | 0
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T26085021SP | FROM->TO | EL PASO - FARBER 138KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 | 21SP | 160 | 168 | 0 |  | 92.5217 | 99.8 | [7 empty] | CATEGORYB | NONSINGLE | OGE3TERM7 | 0 | 0 |  | 0 |  | 0
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T3255521SP | FROM->TO | EL PASO - FARBER 138KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 | 21SP | 160 | 168 | 0 |  | 89.3262 | 96.9 | [7 empty] | CATEGORYB | SINGLE | KILDARE4 - WHITE EAGLE 138KV CKT 1 | 0 | 514760 | KILDARE4 138.00 | 514761 | WHEAGLE4 138.00 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T11145512SP | TO->FROM | EL RENO - ROMAN NOSE 138KV CKT 1 | E | OKGE | OKGE |  |  | 0 | 514823 | ROMNOSE4 138.00 | 514819 | EL-RENO4 138.00 | 0 |  | 1 | 12SP | 133 | 153 | 0 |  | 51.513 | 98.2 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T11145512SP | TO->FROM | EL RENO - ROMAN NOSE 138KV CKT 1 | E | OKGE | OKGE |  |  | 0 | 514823 | ROMNOSE4 138.00 | 514819 | EL-RENO4 138.00 | 0 |  | 1 | 12SP | 133 | 153 | 0 |  | 51.513 | 98.2 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T2155512SP | TO->FROM | EL RENO - ROMAN NOSE 138KV CKT 1 | E | OKGE | OKGE |  |  | 0 | 514823 | ROMNOSE4 138.00 | 514819 | EL-RENO4 138.00 | 0 |  | 1 | 12SP | 133 | 153 | 0 |  | 51.4536 | 98.1 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WWRDEHV7 345.00 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T2155512SP | TO->FROM | EL RENO - ROMAN NOSE 138KV CKT 1 | E | OKGE | OKGE |  |  | 0 | 514823 | ROMNOSE4 138.00 | 514819 | EL-RENO4 138.00 | 0 |  | 1 | 12SP | 133 | 153 | 0 |  | 51.4536 | 98.1 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WWRDEHV7 345.00 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T2025512SP | TO->FROM | EL RENO - ROMAN NOSE 138KV CKT 1 | E | OKGE | OKGE |  |  | 0 | 514823 | ROMNOSE4 138.00 | 514819 | EL-RENO4 138.00 | 0 |  | 1 | 12SP | 133 | 153 | 0 |  | 51.1029 | 97.6 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T2025512SP | TO->FROM | EL RENO - ROMAN NOSE 138KV CKT 1 | E | OKGE | OKGE |  |  | 0 | 514823 | ROMNOSE4 138.00 | 514819 | EL-RENO4 138.00 | 0 |  | 1 | 12SP | 133 | 153 | 0 |  | 51.1029 | 97.6 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T2105511SP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | E | WFEC | AEPW | WESTERN | WESTERN | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 11SP | 144 | 179 | 179 |  | 32.264 | 96.3 | [7 empty] | CATEGORYB | SINGLE | MOREWOOD SW - MORWOOD 138KV CKT 1 | 0 | 521001 | MORWODS4 138.00 | 521002 | MORWOOD4 138.00 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T17175511SP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | E | WFEC | AEPW | WESTERN | WESTERN | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 11SP | 144 | 179 | 179 |  | 34.3373 | 95.4 | [7 empty] | CATEGORYB | GENOUT | GEN525562 1-TOLK GEN #2 24 KV | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T2365512SP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | E | WFEC | AEPW | WESTERN | WESTERN | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 12SP | 144 | 179 | 179 |  | 30.2526 | 99.7 | [7 empty] | CATEGORYB | SINGLE | MOREWOOD SW - MORWOOD 138KV CKT 1 | 0 | 521001 | MORWODS4 138.00 | 521002 | MORWOOD4 138.00 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T2245512SP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | E | WFEC | AEPW | WESTERN | WESTERN | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 12SP | 144 | 179 | 179 |  | 29.1912 | 98.7 | [7 empty] | CATEGORYB | SINGLE | BRANTLEY - DURHAM 138KV CKT 1 | 0 | 520832 | BRANTLEY4 138.00 | 520885 | DURHAM 4 138.00 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T4555512WP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | E | WFEC | AEPW | WESTERN | WESTERN | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 12WP | 188 | 210 | 210 |  | 30.648 | 97.7 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T665512WP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | E | WFEC | AEPW | WESTERN | WESTERN | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 12WP | 188 | 210 | 210 |  | 30.5506 | 97.4 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T75521SP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | E | WFEC | AEPW | WESTERN | WESTERN | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 21SP | 144 | 179 | 179 |  | 29.9704 | 97.3 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1245511SP | FROM->TO | ELK CITY (ELKCTY-4) 138/69/13.8KV TRANSFORMER CKT 1 | E | AEPW | AEPW | WESTERN | WESTERN | 1 | 511458 | ELKCTY-4 138.00 | 511459 | ELKCTY-2 69.000 | 511493 | ELKC4-1 13.800 | 1 | 11SP | 72 | 72 | 0 |  | 81.339 | 99 | [7 empty] | CATEGORYB | SINGLE | CLINTON AIR FORCE BASE TAP - ELK CITY 138KV CKT 1 | 0 | 511446 | CL-AFTP4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1265511SP | FROM->TO | ELK CITY (ELKCTY-4) 138/69/13.8KV TRANSFORMER CKT 1 | E | AEPW | AEPW | WESTERN | WESTERN | 1 | 511458 | ELKCTY-4 138.00 | 511459 | ELKCTY-2 69.000 | 511493 | ELKC4-1 13.800 | 1 | 11SP | 72 | 72 | 0 |  | 80.4845 | 98.1 | [7 empty] | CATEGORYB | SINGLE | CLINTON AIR FORCE BASE TAP - HOBART JUNCTION 138KV CKT 1 | 0 | 511446 | CL-AFTP4 138.00 | 511463 | HOB-JCT4 138.00 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T2125511SP | FROM->TO | ELK CITY (ELKCTY-4) 138/69/13.8KV TRANSFORMER CKT 1 | E | AEPW | AEPW | WESTERN | WESTERN | 1 | 511458 | ELKCTY-4 138.00 | 511459 | ELKCTY-2 69.000 | 511493 | ELKC4-1 13.800 | 1 | 11SP | 72 | 72 | 0 |  | 86.642 | 96 | [7 empty] | CATEGORYB | SINGLE | BLUCAN5 4 138.00 - PARADISE 138KV CKT 1 | 0 | 521024 | PARADSE4 138.00 | 521129 | BLUCAN5 4 138.00 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1435512SP | FROM->TO | ELK CITY (ELKCTY-4) 138/69/13.8KV TRANSFORMER CKT 1 | E | AEPW | AEPW | WESTERN | WESTERN | 1 | 511458 | ELKCTY-4 138.00 | 511459 | ELKCTY-2 69.000 | 511493 | ELKC4-1 13.800 | 1 | 12SP | 72 | 72 | 0 |  | 90.99 | 97.2 | [7 empty] | CATEGORYB | SINGLE | CLINTON AIR FORCE BASE TAP - ELK CITY 138KV CKT 1 | 0 | 511446 | CL-AFTP4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1455512SP | FROM->TO | ELK CITY (ELKCTY-4) 138/69/13.8KV TRANSFORMER CKT 1 | E | AEPW | AEPW | WESTERN | WESTERN | 1 | 511458 | ELKCTY-4 138.00 | 511459 | ELKCTY-2 69.000 | 511493 | ELKC4-1 13.800 | 1 | 12SP | 72 | 72 | 0 |  | 90.1013 | 96.4 | [7 empty] | CATEGORYB | SINGLE | CLINTON AIR FORCE BASE TAP - HOBART JUNCTION 138KV CKT 1 | 0 | 511446 | CL-AFTP4 138.00 | 511463 | HOB-JCT4 138.00 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T525512WP | FROM->TO | ELK CITY (ELKCTY-4) 138/69/13.8KV TRANSFORMER CKT 1 | E | AEPW | AEPW | WESTERN | WESTERN | 2 | 511458 | ELKCTY-4 138.00 | 511459 | ELKCTY-2 69.000 | 511493 | ELKC4-1 13.800 | 1 | 12WP | 72 | 72 | 0 |  | 86.532 | 96.4 | [7 empty] | CATEGORYB | SINGLE | CLINTON AIR FORCE BASE TAP - ELK CITY 138KV CKT 1 | 0 | 511446 | CL-AFTP4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T545512WP | FROM->TO | ELK CITY (ELKCTY-4) 138/69/13.8KV TRANSFORMER CKT 1 | E | AEPW | AEPW | WESTERN | WESTERN | 2 | 511458 | ELKCTY-4 138.00 | 511459 | ELKCTY-2 69.000 | 511493 | ELKC4-1 13.800 | 1 | 12WP | 72 | 72 | 0 |  | 85.9824 | 95.8 | [7 empty] | CATEGORYB | SINGLE | CLINTON AIR FORCE BASE TAP - HOBART JUNCTION 138KV CKT 1 | 0 | 511446 | CL-AFTP4 138.00 | 511463 | HOB-JCT4 138.00 | 0 |  | 1 | [20 empty] | 6/1/2013 | 6/1/2013 | 41061 | 41061
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1955516SP | FROM->TO | ELK CITY (ELKCTY-4) 138/69/13.8KV TRANSFORMER CKT 1 | E | AEPW | AEPW | WESTERN | WESTERN | 1 | 511458 | ELKCTY-4 138.00 | 511459 | ELKCTY-2 69.000 | 511493 | ELKC4-1 13.800 | 1 | 16SP | 72 | 72 | 0 |  | 86.099 | 99.5 | [7 empty] | CATEGORYB | SINGLE | CLINTON AIR FORCE BASE TAP - ELK CITY 138KV CKT 1 | 0 | 511446 | CL-AFTP4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1975516SP | FROM->TO | ELK CITY (ELKCTY-4) 138/69/13.8KV TRANSFORMER CKT 1 | E | AEPW | AEPW | WESTERN | WESTERN | 1 | 511458 | ELKCTY-4 138.00 | 511459 | ELKCTY-2 69.000 | 511493 | ELKC4-1 13.800 | 1 | 16SP | 72 | 72 | 0 |  | 85.1586 | 98.6 | [7 empty] | CATEGORYB | SINGLE | CLINTON AIR FORCE BASE TAP - HOBART JUNCTION 138KV CKT 1 | 0 | 511446 | CL-AFTP4 138.00 | 511463 | HOB-JCT4 138.00 | 0 |  | 1
2009-AGP2 | AFS5 | INVALID | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T2745012SP | FROM->TO | EVANS ENERGY CENTER NORTH - MAIZE 4 138.00 138KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533040 | EVANS N4 138.00 | 533054 | MAIZE 4 138.00 | 0 |  | 1 | 12SP | 382 | 382 | 0 | 100 | 99.9661 | 98.7467 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER NORTH - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533040 | EVANS N4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T2375011SP | FROM->TO | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 | 11SP | 382 | 413 | 0 | 99.2 | 99.2312 | 99.7 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T2685012SP | FROM->TO | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 | 12SP | 382 | 413 | 0 | 96.5 | 96.5007 | 96.9 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1895510WP | FROM->TO | FLATRDG3 - HARPER 138KV CKT 1 | E | SUNC | SUNC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 10WP | 105.2 | 105.2 | 0 |  | 93.8252 | 97.5 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1915510WP | FROM->TO | FLATRDG3 - HARPER 138KV CKT 1 | E | SUNC | SUNC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 10WP | 105.2 | 105.2 | 0 |  | 93.7022 | 97.4 | [7 empty] | CATEGORYB | SINGLE | PRATT - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1465511WP | FROM->TO | FLATRDG3 - HARPER 138KV CKT 1 | E | SUNC | SUNC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 11WP | 105.2 | 105.2 | 0 | 99.2 | 99.1908 | 98.9 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1485511WP | FROM->TO | FLATRDG3 - HARPER 138KV CKT 1 | E | SUNC | SUNC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 11WP | 105.2 | 105.2 | 0 | 99.1 | 99.0612 | 98.7 | [7 empty] | CATEGORYB | SINGLE | PRATT - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1565512WP | FROM->TO | FLATRDG3 - HARPER 138KV CKT 1 | E | SUNC | SUNC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 12WP | 105.2 | 105.2 | 0 |  | 94.0478 | 96 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1585512WP | FROM->TO | FLATRDG3 - HARPER 138KV CKT 1 | E | SUNC | SUNC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 12WP | 105.2 | 105.2 | 0 |  | 93.911 | 95.8 | [7 empty] | CATEGORYB | SINGLE | PRATT - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1
2009-AGP2 | AFS5UP | INVALID |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS5UP1T1155016WP | FROM->TO | FORT JUNCTION SWITCHING STATION - WEST JUNCTION CITY JUNCTION (EAST) 115KV CKT 1 | E | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533328 | FT JCT 3 115.00 | 533343 | WJCCTYE3 115.00 | 0 |  | 1 | 16WP | 92 | 92 | 0 |  | 86.6618 | 95.7299 | [7 empty] | CATEGORYB | SINGLE | FORT JUNCTION SWITCHING STATION - WEST JUNCTION CITY JUNCTION (EAST) 115KV CKT 2 | 0 | 533328 | FT JCT 3 115.00 | 533343 | WJCCTYE3 115.00 | 0 |  | 2
2009-AGP2 | AFS5 | INVALID |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T1255016WP | FROM->TO | FORT JUNCTION SWITCHING STATION - WEST JUNCTION CITY JUNCTION (EAST) 115KV CKT 1 | E | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533328 | FT JCT 3 115.00 | 533343 | WJCCTYE3 115.00 | 0 |  | 1 | 16WP | 92 | 92 | 0 |  | 86.5232 | 95.6145 | [7 empty] | CATEGORYB | SINGLE | FORT JUNCTION SWITCHING STATION - WEST JUNCTION CITY JUNCTION (EAST) 115KV CKT 2 | 0 | 533328 | FT JCT 3 115.00 | 533343 | WJCCTYE3 115.00 | 0 |  | 2
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T5425021SP | FROM->TO | FORT JUNCTION SWITCHING STATION - WEST JUNCTION CITY JUNCTION (EAST) 115KV CKT 1 | E | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533328 | FT JCT 3 115.00 | 533343 | WJCCTYE3 115.00 | 0 |  | 1 | 21SP | 92 | 92 | 0 |  | 94.4945 | 98.7 | [7 empty] | CATEGORYB | SINGLE | FORT JUNCTION SWITCHING STATION - JUNCTION CITY 115KV CKT 1 | 0 | 533328 | FT JCT 3 115.00 | 533330 | JCTCTY 3 115.00 | 0 |  | 1
2009-AGP2 | AFS5 | INVALID |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T5455021SP | FROM->TO | FORT JUNCTION SWITCHING STATION - WEST JUNCTION CITY JUNCTION (EAST) 115KV CKT 1 | E | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533328 | FT JCT 3 115.00 | 533343 | WJCCTYE3 115.00 | 0 |  | 1 | 21SP | 92 | 92 | 0 |  | 88.7727 | 95.0193 | [7 empty] | CATEGORYB | SINGLE | FORT JUNCTION SWITCHING STATION - WEST JUNCTION CITY JUNCTION (EAST) 115KV CKT 2 | 0 | 533328 | FT JCT 3 115.00 | 533343 | WJCCTYE3 115.00 | 0 |  | 2
2009-AGP2 | AFS5UP | INVALID |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS5UP1T1145016WP | FROM->TO | FORT JUNCTION SWITCHING STATION - WEST JUNCTION CITY JUNCTION (EAST) 115KV CKT 2 | E | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533328 | FT JCT 3 115.00 | 533343 | WJCCTYE3 115.00 | 0 |  | 2 | 16WP | 92 | 92 | 0 |  | 86.6618 | 95.7299 | [7 empty] | CATEGORYB | SINGLE | FORT JUNCTION SWITCHING STATION - WEST JUNCTION CITY JUNCTION (EAST) 115KV CKT 1 | 0 | 533328 | FT JCT 3 115.00 | 533343 | WJCCTYE3 115.00 | 0 |  | 1
2009-AGP2 | AFS5 | INVALID |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T1245016WP | FROM->TO | FORT JUNCTION SWITCHING STATION - WEST JUNCTION CITY JUNCTION (EAST) 115KV CKT 2 | E | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533328 | FT JCT 3 115.00 | 533343 | WJCCTYE3 115.00 | 0 |  | 2 | 16WP | 92 | 92 | 0 |  | 86.5232 | 95.6145 | [7 empty] | CATEGORYB | SINGLE | FORT JUNCTION SWITCHING STATION - WEST JUNCTION CITY JUNCTION (EAST) 115KV CKT 1 | 0 | 533328 | FT JCT 3 115.00 | 533343 | WJCCTYE3 115.00 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T5435021SP | FROM->TO | FORT JUNCTION SWITCHING STATION - WEST JUNCTION CITY JUNCTION (EAST) 115KV CKT 2 | E | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533328 | FT JCT 3 115.00 | 533343 | WJCCTYE3 115.00 | 0 |  | 2 | 21SP | 92 | 92 | 0 |  | 94.4945 | 98.7 | [7 empty] | CATEGORYB | SINGLE | FORT JUNCTION SWITCHING STATION - JUNCTION CITY 115KV CKT 1 | 0 | 533328 | FT JCT 3 115.00 | 533330 | JCTCTY 3 115.00 | 0 |  | 1
2009-AGP2 | AFS5 | INVALID |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T5445021SP | FROM->TO | FORT JUNCTION SWITCHING STATION - WEST JUNCTION CITY JUNCTION (EAST) 115KV CKT 2 | E | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533328 | FT JCT 3 115.00 | 533343 | WJCCTYE3 115.00 | 0 |  | 2 | 21SP | 92 | 92 | 0 |  | 88.7727 | 95.0193 | [7 empty] | CATEGORYB | SINGLE | FORT JUNCTION SWITCHING STATION - WEST JUNCTION CITY JUNCTION (EAST) 115KV CKT 1 | 0 | 533328 | FT JCT 3 115.00 | 533343 | WJCCTYE3 115.00 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T10565510WP | FROM->TO | FPL SWITCH - MOORELAND 138KV CKT 1 | E | OKGE | WFEC | ENID | AEP-OP | 0 | 515785 | WINDFRM4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 10WP | 287 | 287 | 0 |  | 57.8896 | 98.6 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1115510WP | FROM->TO | FPL SWITCH - MOORELAND 138KV CKT 1 | E | OKGE | WFEC | ENID | AEP-OP | 0 | 515785 | WINDFRM4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 10WP | 287 | 287 | 0 |  | 57.4392 | 97.6 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T5895511WP | FROM->TO | FPL SWITCH - MOORELAND 138KV CKT 1 | E | OKGE | WFEC | ENID | AEP-OP | 0 | 515785 | WINDFRM4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 11WP | 287 | 287 | 0 |  | 57.8641 | 98.3 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T735511WP | FROM->TO | FPL SWITCH - MOORELAND 138KV CKT 1 | E | OKGE | WFEC | ENID | AEP-OP | 0 | 515785 | WINDFRM4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 11WP | 287 | 287 | 0 |  | 57.4304 | 97.3 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T4595512WP | FROM->TO | FPL SWITCH - MOORELAND 138KV CKT 1 | E | OKGE | WFEC | ENID | AEP-OP | 0 | 515785 | WINDFRM4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 12WP | 287 | 287 | 0 |  | 57.9249 | 96.7 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T705512WP | FROM->TO | FPL SWITCH - MOORELAND 138KV CKT 1 | E | OKGE | WFEC | ENID | AEP-OP | 0 | 515785 | WINDFRM4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 12WP | 287 | 287 | 0 |  | 57.4839 | 95.7 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1095510WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 10WP | 171 | 185 | 0 |  | 37.1026 | 99.7 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1095510WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 10WP | 171 | 185 | 0 |  | 37.1026 | 99.7 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T715511WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 11WP | 171 | 185 | 0 |  | 37.094 | 99.2 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T715511WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 11WP | 171 | 185 | 0 |  | 37.094 | 99.2 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T4565512WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 12WP | 171 | 185 | 0 |  | 38.5577 | 99 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T4565512WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 12WP | 171 | 185 | 0 |  | 38.5577 | 99 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T675512WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 12WP | 171 | 185 | 0 |  | 37.2181 | 96.5 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T675512WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 12WP | 171 | 185 | 0 |  | 37.2181 | 96.5 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T5085516WP | TO->FROM | FRANKLIN - RAY BRASWELL SES 500KV CKT 1 | E | EES | EES | EMI-CLTN | AEC | 0 | 336839 | 8R.BRAS 500.00 | 336562 | 8FRKLIN 500.00 | 0 |  | 1 | 16WP | 1732 | 1732 | 0 | 95.7 | 95.7417 | 95.8 | [7 empty] | CATEGORYB | SINGLE | FRANKLIN - GRAND GULF 500KV CKT 1 | 0 | 336562 | 8FRKLIN 500.00 | 336820 | 8G.GULF 500.00 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1655511SP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | E | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 11SP | 124 | 124 | 0 |  | 76.0382 | 97.3 | [7 empty] | CATEGORYB | SINGLE | KNOBHILL - MOORELAND 138KV CKT 1 | 0 | 514795 | KNOBHIL4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1655511SP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | E | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 11SP | 124 | 124 | 0 |  | 76.0382 | 97.3 | [7 empty] | CATEGORYB | SINGLE | KNOBHILL - MOORELAND 138KV CKT 1 | 0 | 514795 | KNOBHIL4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T10115511SP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | E | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 11SP | 124 | 124 | 0 |  | 75.9939 | 97.2 | [7 empty] | CATEGORYB | SINGLE | KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 514794 | KNOBHIL2 69.000 | 514795 | KNOBHIL4 138.00 | 515732 | KNOBHIL1 13.200 | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T10115511SP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | E | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 11SP | 124 | 124 | 0 |  | 75.9939 | 97.2 | [7 empty] | CATEGORYB | SINGLE | KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 514794 | KNOBHIL2 69.000 | 514795 | KNOBHIL4 138.00 | 515732 | KNOBHIL1 13.200 | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T2005511SP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | E | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 11SP | 124 | 124 | 0 |  | 73.8406 | 95.5 | [7 empty] | CATEGORYB | SINGLE | CEDARDALE - MOORELAND 138KV CKT 1 | 0 | 520848 | CEDRDAL4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T2005511SP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | E | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 11SP | 124 | 124 | 0 |  | 73.8406 | 95.5 | [7 empty] | CATEGORYB | SINGLE | CEDARDALE - MOORELAND 138KV CKT 1 | 0 | 520848 | CEDRDAL4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1895512SP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | E | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 12SP | 124 | 124 | 0 |  | 78.253 | 96.4 | [7 empty] | CATEGORYB | SINGLE | KNOBHILL - MOORELAND 138KV CKT 1 | 0 | 514795 | KNOBHIL4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1895512SP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | E | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 12SP | 124 | 124 | 0 |  | 78.253 | 96.4 | [7 empty] | CATEGORYB | SINGLE | KNOBHILL - MOORELAND 138KV CKT 1 | 0 | 514795 | KNOBHIL4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T10975512SP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | E | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 12SP | 124 | 124 | 0 |  | 78.1955 | 96.3 | [7 empty] | CATEGORYB | SINGLE | KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 514794 | KNOBHIL2 69.000 | 514795 | KNOBHIL4 138.00 | 515732 | KNOBHIL1 13.200 | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T10975512SP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | E | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 12SP | 124 | 124 | 0 |  | 78.1955 | 96.3 | [7 empty] | CATEGORYB | SINGLE | KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 514794 | KNOBHIL2 69.000 | 514795 | KNOBHIL4 138.00 | 515732 | KNOBHIL1 13.200 | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T17135511SP | TO->FROM | GRAY TAP - PENSACOLA 69KV CKT 1 | E | GRDA | GRDA | GRDA-NEO | GRDA | 0 | 512628 | PENSA 2 69.000 | 512665 | GRAY TP2 69.000 | 0 |  | 1 | 11SP | 37 | 47 | 0 |  | 96.8492 | 97.9 | [7 empty] | CATEGORYB | GENOUT | GEN512628 1-PENSACOLA | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1415511SP | TO->FROM | GRAY TAP - PENSACOLA 69KV CKT 1 | E | GRDA | GRDA | GRDA-NEO | GRDA | 0 | 512628 | PENSA 2 69.000 | 512665 | GRAY TP2 69.000 | 0 |  | 1 | 11SP | 37 | 47 | 0 |  | 95.6284 | 97.8 | [7 empty] | CATEGORYB | SINGLE | SILOAM CITY - WEST SILOAM SPRINGS 161KV CKT 1 | 0 | 512642 | SILSPWW5 161.00 | 512643 | SILMCTY5 161.00 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1425511SP | TO->FROM | GRAY TAP - PENSACOLA 69KV CKT 1 | E | GRDA | GRDA | GRDA-NEO | GRDA | 0 | 512628 | PENSA 2 69.000 | 512665 | GRAY TP2 69.000 | 0 |  | 1 | 11SP | 37 | 47 | 0 | 95.3 | 95.2655 | 97.5 | [7 empty] | CATEGORYB | SINGLE | KANSAS TAP - WEST SILOAM SPRINGS 161KV CKT 1 | 0 | 512642 | SILSPWW5 161.00 | 512714 | KANSATP5 161.00 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1755512SP | TO->FROM | GRAY TAP - PENSACOLA 69KV CKT 1 | E | GRDA | GRDA | GRDA-NEO | GRDA | 0 | 512628 | PENSA 2 69.000 | 512665 | GRAY TP2 69.000 | 0 |  | 1 | 12SP | 37 | 47 | 0 | 95.4 | 95.3865 | 99.5 | [7 empty] | CATEGORYB | SINGLE | GROVE NEO - WHITEW2 69.000 69KV CKT 1 | 0 | 512718 | GROVNEO2 69.000 | 512743 | WHITEW2 69.000 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T14855012SP | TO->FROM | GRAY TAP - PENSACOLA 69KV CKT 1 | E | GRDA | GRDA | GRDA-NEO | GRDA | 0 | 512628 | PENSA 2 69.000 | 512665 | GRAY TP2 69.000 | 0 |  | 1 | 12SP | 37 | 47 | 0 | 97.5 | 97.4869 | 98.9 | [7 empty] | CATEGORYB | GENOUT | GEN512628 2-PENSACOLA | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1765512SP | TO->FROM | GRAY TAP - PENSACOLA 69KV CKT 1 | E | GRDA | GRDA | GRDA-NEO | GRDA | 0 | 512628 | PENSA 2 69.000 | 512665 | GRAY TP2 69.000 | 0 |  | 1 | 12SP | 37 | 47 | 0 |  | 94.1318 | 98.3 | [7 empty] | CATEGORYB | SINGLE | JAY - WHITEW2 69.000 69KV CKT 1 | 0 | 512720 | JAY GR 2 69.000 | 512743 | WHITEW2 69.000 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 | ISLAND-LOAD |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1655512SP | TO->FROM | GRAY TAP - PENSACOLA 69KV CKT 1 | E | GRDA | GRDA | GRDA-NEO | GRDA | 0 | 512628 | PENSA 2 69.000 | 512665 | GRAY TP2 69.000 | 0 |  | 1 | 12SP | 37 | 47 | 0 |  | 92.8036 | 97.4 | [7 empty] | CATEGORYB | SINGLE | GRAY - GRAY TAP 69KV CKT 1 | 0 | 512665 | GRAY TP2 69.000 | 512666 | GRAY 2 69.000 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T2275516SP | TO->FROM | GRAY TAP - PENSACOLA 69KV CKT 1 | E | GRDA | GRDA | GRDA-NEO | GRDA | 0 | 512628 | PENSA 2 69.000 | 512665 | GRAY TP2 69.000 | 0 |  | 1 | 16SP | 37 | 47 | 0 | 97.2 | 97.25 | 99.2 | [7 empty] | CATEGORYB | SINGLE | GROVE NEO - WHITEW2 69.000 69KV CKT 1 | 0 | 512718 | GROVNEO2 69.000 | 512743 | WHITEW2 69.000 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T1395016SP | TO->FROM | GRAY TAP - PENSACOLA 69KV CKT 1 | E | GRDA | GRDA | GRDA-NEO | GRDA | 0 | 512628 | PENSA 2 69.000 | 512665 | GRAY TP2 69.000 | 0 |  | 1 | 16SP | 37 | 47 | 0 |  | 93.3823 | 99 | [7 empty] | CATEGORYB | SINGLE | MAID - PENSACOLA 161KV CKT 1 | 0 | 512648 | MAID 5 161.00 | 512654 | PENSA 5 161.00 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 | ISLAND-LOAD |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T1435016SP | TO->FROM | GRAY TAP - PENSACOLA 69KV CKT 1 | E | GRDA | GRDA | GRDA-NEO | GRDA | 0 | 512628 | PENSA 2 69.000 | 512665 | GRAY TP2 69.000 | 0 |  | 1 | 16SP | 37 | 47 | 0 |  | 91.9456 | 98 | [7 empty] | CATEGORYB | SINGLE | GRAY - GRAY TAP 69KV CKT 1 | 0 | 512665 | GRAY TP2 69.000 | 512666 | GRAY 2 69.000 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T795016WP | TO->FROM | GRAY TAP - PENSACOLA 69KV CKT 1 | E | GRDA | GRDA | GRDA-NEO | GRDA | 0 | 512628 | PENSA 2 69.000 | 512665 | GRAY TP2 69.000 | 0 |  | 1 | 16WP | 46 | 50 | 0 |  | 88.1615 | 98.3 | [7 empty] | CATEGORYB | SINGLE | CLEORA TAP - PENSACOLA 69KV CKT 1 | 0 | 512628 | PENSA 2 69.000 | 512692 | CLEORTP2 69.000 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T15016WP | TO->FROM | GRAY TAP - PENSACOLA 69KV CKT 1 | E | GRDA | GRDA | GRDA-NEO | GRDA | 0 | 512628 | PENSA 2 69.000 | 512665 | GRAY TP2 69.000 | 0 |  | 1 | 16WP | 46 | 50 | 0 |  | 88.0088 | 97.7 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2011-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1125511SP | FROM->TO | GRAY TAP - ZENA TAP 69KV CKT 1 | E | GRDA | GRDA | GRDA | GRDA | 0 | 512665 | GRAY TP2 69.000 | 512667 | ZENA TP2 69.000 | 0 |  | 1 | 11SP | 37 | 47 | 0 | 96.2 | 96.1727 | 98.7 | [7 empty] | CATEGORYB | SINGLE | BIRD HOLLOW (LANGLEY) - PRYOR JUNCTION 138KV CKT 1 | 0 | 510398 | BIRDHOL4 138.00 | 510419 | PRY-JCT4 138.00 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T10035511SP | FROM->TO | GRAY TAP - ZENA TAP 69KV CKT 1 | E | GRDA | GRDA | GRDA | GRDA | 0 | 512665 | GRAY TP2 69.000 | 512667 | ZENA TP2 69.000 | 0 |  | 1 | 11SP | 37 | 47 | 0 | 95.8 | 95.7758 | 98 | [7 empty] | CATEGORYB | SINGLE | COWSKIN (COWAUTO1) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 512717 | COWSKIN 69.000 | 512719 | COWSKIN 138.00 | 512738 | COWSKIN 13.800 | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T995012SP | FROM->TO | GRAY TAP - ZENA TAP 69KV CKT 1 | E | GRDA | GRDA | GRDA | GRDA | 0 | 512665 | GRAY TP2 69.000 | 512667 | ZENA TP2 69.000 | 0 |  | 1 | 12SP | 37 | 47 | 0 | 95.8 | 95.8426 | 97.2 | [7 empty] | CATEGORYB | SINGLE | ADAIR - PENSACOLA 69KV CKT 1 | 0 | 512628 | PENSA 2 69.000 | 512695 | ADARNEO2 69.000 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T5905016WP | FROM->TO | GRAY TAP - ZENA TAP 69KV CKT 1 | E | GRDA | GRDA | GRDA | GRDA | 0 | 512665 | GRAY TP2 69.000 | 512667 | ZENA TP2 69.000 | 0 |  | 1 | 16WP | 46 | 50 | 0 |  | 90.9817 | 99.6 | [7 empty] | CATEGORYB | SINGLE | KANSAS (KANAUTO1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 512715 | KANSAS 2 69.000 | 512716 | KANSAS 5 161.00 | 512736 | KANSAS1 13.800 | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T31415021SP | FROM->TO | GRAY TAP - ZENA TAP 69KV CKT 1 | E | GRDA | GRDA | GRDA | GRDA | 0 | 512665 | GRAY TP2 69.000 | 512667 | ZENA TP2 69.000 | 0 |  | 1 | 21SP | 37 | 47 | 0 | 95.8 | 95.7922 | 99.7 | [7 empty] | CATEGORYB | GENOUT | GEN512689 1-GRDA1 GSU1 22 | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T19595021SP | FROM->TO | GRAY TAP - ZENA TAP 69KV CKT 1 | E | GRDA | GRDA | GRDA | GRDA | 0 | 512665 | GRAY TP2 69.000 | 512667 | ZENA TP2 69.000 | 0 |  | 1 | 21SP | 37 | 47 | 0 |  | 94.0695 | 98.1 | [7 empty] | CATEGORYB | SINGLE | CLAREMORE - SEQUOYAH 69KV CKT 1 | 0 | 512679 | CLARMR 2 69.000 | 301002 | 2SEQUOYA 69.000 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T3305021SP | FROM->TO | GRAY TAP - ZENA TAP 69KV CKT 1 | E | GRDA | GRDA | GRDA | GRDA | 0 | 512665 | GRAY TP2 69.000 | 512667 | ZENA TP2 69.000 | 0 |  | 1 | 21SP | 37 | 47 | 0 |  | 92.8753 | 97.9 | [7 empty] | CATEGORYB | SINGLE | MAID - PENSACOLA 161KV CKT 1 | 0 | 512648 | MAID 5 161.00 | 512654 | PENSA 5 161.00 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T15685521SP | TO->FROM | HARISBURG TAP - MARKED TREE 161KV CKT 1 | E | EES | EES | EAINTH | EAINTH | 0 | 338165 | 5MTREE 161.00 | 338167 | 5HRSBRG* 161.00 | 0 |  | 1 | 21SP | 223 | 223 | 0 | 99.3 | 99.2684 | 99.4 | [7 empty] | CATEGORYB | SINGLE | NEWPORT AB - NEWPORT INDUSTRIAL 161KV CKT 1 | 0 | 338172 | 5NEW-AB 161.00 | 338173 | 5NEW-IN 161.00 | 0 |  | 1 | [58 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T15595521SP | TO->FROM | HARISBURG TAP - MARKED TREE 161KV CKT 1 | E | EES | EES | EAINTH | EAINTH | 0 | 338165 | 5MTREE 161.00 | 338167 | 5HRSBRG* 161.00 | 0 |  | 1 | 21SP | 223 | 223 | 0 | 96.9 | 96.9364 | 97 | [7 empty] | CATEGORYB | SINGLE | CASH - NEWPORT AB 161KV CKT 1 | 0 | 338171 | 5CASH 161.00 | 338172 | 5NEW-AB 161.00 | 0 |  | 1 | [58 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T2525516SP | FROM->TO | Harrington Station East Bus - POTTER COUNTY INTERCHANGE 230KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 523979 | HARRNG_EST 6230.00 | 523959 | POTTER_CO 6230.00 | 0 |  | 1 | 16SP | 319 | 351 | 0 | 96.3 | 96.2933 | 97.2 | [7 empty] | CATEGORYB | SINGLE | CHERRY1 - HARRINGTON STATION 230KV CKT 2 | 0 | 523977 | HARRNG_WST 6230.00 | 524010 | CHERRY 6230.00 | 0 |  | 2
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T20115021SP | TO->FROM | HAYS PLANT - SOUTH HAYS 115KV CKT 1 | E | MIDW | MIDW | REG E-IL | REG E-IL | 0 | 530553 | S HAYS 3 115.00 | 530562 | HAYS 3 115.00 | 0 |  | 1 | 21SP | 80 | 88 | 0 |  | 90.056 | 99.7 | [7 empty] | CATEGORYB | SINGLE | KNOLL 230 (KNOLL T1) 230/115/11.49KV TRANSFORMER CKT 1 | 1 | 530558 | KNOLL 6 230.00 | 530561 | KNOLL 3 115.00 | 530629 | KNLL1 1 11.490 | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T15745521SP | TO->FROM | HERGETT - TRUMANN WEST AECC 161KV CKT 1 | E | EES | SWPA |  | EMINTH | 0 | 338707 | 5TRUM-W# 161.00 | 505420 | HERGETT5 161.00 | 0 |  | 1 | 21SP | 148 | 148 | 0 | 99.6 | 99.565 | 99.4 | [7 empty] | CATEGORYB | SINGLE | NEWPORT AB - NEWPORT INDUSTRIAL 161KV CKT 1 | 0 | 338172 | 5NEW-AB 161.00 | 338173 | 5NEW-IN 161.00 | 0 |  | 1 | [58 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T15655521SP | TO->FROM | HERGETT - TRUMANN WEST AECC 161KV CKT 1 | E | EES | SWPA |  | EMINTH | 0 | 338707 | 5TRUM-W# 161.00 | 505420 | HERGETT5 161.00 | 0 |  | 1 | 21SP | 148 | 148 | 0 | 96.4 | 96.4086 | 96.2 | [7 empty] | CATEGORYB | SINGLE | CASH - NEWPORT AB 161KV CKT 1 | 0 | 338171 | 5CASH 161.00 | 338172 | 5NEW-AB 161.00 | 0 |  | 1 | [58 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T2395011SP | TO->FROM | HOOVER NORTH - LAKERIDGE 138KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533053 | LAKERDG4 138.00 | 533049 | HOOVERN4 138.00 | 0 |  | 1 | 11SP | 382 | 382 | 0 | 95.9 | 95.9314 | 96.4 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T9265016WP | FROM->TO | HUMBOLDT (S975 T4) 161/69/13.8KV TRANSFORMER CKT 1 | E | OPPD | OPPD | NPPD_686 | OPPD_691 | 1 | 640234 | HUMBOLT5 161.00 | 647975 | S975 8 69.000 | 648275 | S975T4 9 13.800 | 1 | 16WP | 67.2 | 67.2 | 67.2 |  | 93.0172 | 97.6 | [7 empty] | CATEGORYB | NONSINGLE | S1263T1 AUTO | 0 | 0 |  | 0 |  | 0
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T6885016WP | FROM->TO | HUMBOLDT (S975 T4) 161/69/13.8KV TRANSFORMER CKT 1 | E | OPPD | OPPD | NPPD_686 | OPPD_691 | 1 | 640234 | HUMBOLT5 161.00 | 647975 | S975 8 69.000 | 648275 | S975T4 9 13.800 | 1 | 16WP | 67.2 | 67.2 | 67.2 |  | 91.9522 | 97.4 | [7 empty] | CATEGORYB | SINGLE | SUB 1263 BROCK (S1263 T1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 646263 | S1263 5 161.00 | 647111 | W BROCK8 69.000 | 648263 | S1263T19 13.800 | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T12755011SP | FROM->TO | IATAN (IATAN 11) 345/161/13.8KV TRANSFORMER CKT 11 | E | KACP | MIPU | KACP |  | 1 | 542982 | IATAN 7 345.00 | 541350 | IATAN5 161.00 | 541150 | IATAN 11 13.800 | 11 | 11SP | 650 | 715 | 715 | 100.5 | 100.5022 | 98.6 | [7 empty] | CATEGORYB | NONSINGLE | KCPL-OPGD#07 | 0 | 0 |  | 0 |  | 0
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T12685011SP | FROM->TO | IATAN (IATAN 11) 345/161/13.8KV TRANSFORMER CKT 11 | E | KACP | MIPU | KACP |  | 1 | 542982 | IATAN 7 345.00 | 541350 | IATAN5 161.00 | 541150 | IATAN 11 13.800 | 11 | 11SP | 650 | 715 | 715 | 99.8 | 99.7626 | 97.9 | [7 empty] | CATEGORYB | NONSINGLE | KCPL-OPGD#02 | 0 | 0 |  | 0 |  | 0
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T31145021SP | FROM->TO | INDEPENDENCE - LS POWER OSCEOLA UNIT 500KV CKT 1 | E | EES | EES | EAINTH | EAINTH | 0 | 338145 | 8ISES 500.00 | 338144 | 8ISXF 500.00 | 0 |  | 1 | 21SP | 850 | 850 | 850 | 95.7 | 95.6879 | 95 | [7 empty] | CATEGORYB | GENOUT | GEN338143 1-INDEPENDENCE UNIT #1 | 0 | 0 |  | 0 |  | 0
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T75511SP | TO->FROM | JAY - ZENA TAP 69KV CKT 1 | E | GRDA | GRDA | GRDA | GRDA-NEO | 0 | 512667 | ZENA TP2 69.000 | 512720 | JAY GR 2 69.000 | 0 |  | 1 | 11SP | 37 | 47 | 0 |  | 94.7508 | 97.9 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1565512SP | TO->FROM | JAY - ZENA TAP 69KV CKT 1 | E | GRDA | GRDA | GRDA | GRDA-NEO | 0 | 512667 | ZENA TP2 69.000 | 512720 | JAY GR 2 69.000 | 0 |  | 1 | 12SP | 37 | 47 | 0 |  | 91.4604 | 96.4 | [7 empty] | CATEGORYB | SINGLE | 412SUB - KERR 161KV CKT 1 | 0 | 512635 | KERR GR5 161.00 | 512637 | 412SUB 5 161.00 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1595512SP | TO->FROM | JAY - ZENA TAP 69KV CKT 1 | E | GRDA | GRDA | GRDA | GRDA-NEO | 0 | 512667 | ZENA TP2 69.000 | 512720 | JAY GR 2 69.000 | 0 |  | 1 | 12SP | 37 | 47 | 0 |  | 91.1757 | 96.1 | [7 empty] | CATEGORYB | SINGLE | 412SUB - KANSAS TAP 161KV CKT 1 | 0 | 512637 | 412SUB 5 161.00 | 512714 | KANSATP5 161.00 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1795512SP | TO->FROM | JAY - ZENA TAP 69KV CKT 1 | E | GRDA | GRDA | GRDA | GRDA-NEO | 0 | 512667 | ZENA TP2 69.000 | 512720 | JAY GR 2 69.000 | 0 |  | 1 | 12SP | 37 | 47 | 0 |  | 92.1787 | 95.7 | [7 empty] | CATEGORYB | SINGLE | COLCORD TAP - JAY 69KV CKT 1 | 0 | 512720 | JAY GR 2 69.000 | 512829 | COLCOTP2 69.000 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T1325016SP | TO->FROM | JAY - ZENA TAP 69KV CKT 1 | E | GRDA | GRDA | GRDA | GRDA-NEO | 0 | 512667 | ZENA TP2 69.000 | 512720 | JAY GR 2 69.000 | 0 |  | 1 | 16SP | 37 | 47 | 0 |  | 90.5549 | 97.4 | [7 empty] | CATEGORYB | SINGLE | 412SUB - KERR 161KV CKT 1 | 0 | 512635 | KERR GR5 161.00 | 512637 | 412SUB 5 161.00 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T1365016SP | TO->FROM | JAY - ZENA TAP 69KV CKT 1 | E | GRDA | GRDA | GRDA | GRDA-NEO | 0 | 512667 | ZENA TP2 69.000 | 512720 | JAY GR 2 69.000 | 0 |  | 1 | 16SP | 37 | 47 | 0 |  | 90.205 | 97 | [7 empty] | CATEGORYB | SINGLE | 412SUB - KANSAS TAP 161KV CKT 1 | 0 | 512637 | 412SUB 5 161.00 | 512714 | KANSATP5 161.00 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T4365521SP | FROM->TO | Jones Station Bus#2 - LUBBOCK SOUTH INTERCHANGE 230KV CKT 2 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 0 | 526338 | JONES_BUS2 6230.00 | 526269 | LUBBCK_STH 6230.00 | 0 |  | 2 | 21SP | 319 | 351 | 0 | 100 | 99.9685 | 99.6 | [7 empty] | CATEGORYB | SINGLE | JONES STATION - LUBBOCK SOUTH INTERCHANGE 230KV CKT 1 | 0 | 526269 | LUBBCK_STH 6230.00 | 526337 | JONES_BUS1 6230.00 | 0 |  | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T15705521SP | TO->FROM | JONESBORO - JONESBORO NORTH (AECC) 161KV CKT 1 | E | EES | EES | EAINTH-A |  | 0 | 338703 | 5JONE-N# 161.00 | 338170 | 5JONES 161.00 | 0 |  | 1 | 21SP | 246 | 246 | 0 | 98.8 | 98.8362 | 99.4 | [7 empty] | CATEGORYB | SINGLE | NEWPORT AB - NEWPORT INDUSTRIAL 161KV CKT 1 | 0 | 338172 | 5NEW-AB 161.00 | 338173 | 5NEW-IN 161.00 | 0 |  | 1 | [58 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T15615521SP | TO->FROM | JONESBORO - JONESBORO NORTH (AECC) 161KV CKT 1 | E | EES | EES | EAINTH-A |  | 0 | 338703 | 5JONE-N# 161.00 | 338170 | 5JONES 161.00 | 0 |  | 1 | 21SP | 246 | 246 | 0 | 96.3 | 96.2934 | 96.8 | [7 empty] | CATEGORYB | SINGLE | CASH - NEWPORT AB 161KV CKT 1 | 0 | 338171 | 5CASH 161.00 | 338172 | 5NEW-AB 161.00 | 0 |  | 1 | [58 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T27975521SP | TO->FROM | JONESBORO NORTH (AECC) - PARAGOULD SOUTH (AECC) 161KV CKT 1 | E | EES | EES | EAINTH-A | EAINTH-A | 0 | 338706 | 5PARA-S# 161.00 | 338703 | 5JONE-N# 161.00 | 0 |  | 1 | 21SP | 246 | 246 | 0 | 98.6 | 98.6484 | 99.1 | [7 empty] | CATEGORYB | NONSINGLE | A041 | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T15535521SP | TO->FROM | JONESBORO NORTH (AECC) - PARAGOULD SOUTH (AECC) 161KV CKT 1 | E | EES | EES | EAINTH-A | EAINTH-A | 0 | 338706 | 5PARA-S# 161.00 | 338703 | 5JONE-N# 161.00 | 0 |  | 1 | 21SP | 246 | 246 | 0 | 98.5 | 98.4964 | 98.9 | [7 empty] | CATEGORYB | SINGLE | CASH - JONESBORO 161KV CKT 1 | 0 | 338170 | 5JONES 161.00 | 338171 | 5CASH 161.00 | 0 |  | 1 | [58 empty] | 2017-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T10275511SP | TO->FROM | KNOBHILL - MOORELAND 138KV CKT 1 | E | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514795 | KNOBHIL4 138.00 | 0 |  | 1 | 11SP | 96 | 96 | 0 |  | 74.1273 | 95.5 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1785511SP | TO->FROM | KNOBHILL - MOORELAND 138KV CKT 1 | E | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514795 | KNOBHIL4 138.00 | 0 |  | 1 | 11SP | 96 | 96 | 0 |  | 74.0079 | 95.2 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1
2009-AGP2 | AFS5 | INVALID | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T2005016SP | FROM->TO | LEA COUNTY INTERCHANGE - LEA COUNTY REC-LOVINGTON INTERCHANGE 115KV CKT 1 | E | SPS | SPS | SPS-PECO | SPS-HOBB | 0 | 527848 | LEA_CNTY 3115.00 | 528334 | LE-LOVINTON3115.00 | 0 |  | 1 | 16SP | 159 | 175 | 0 | 98.6 | 98.6045 | 98.1876 | [7 empty] | CATEGORYB | SINGLE | BUCKEYE TAP - CUNNINGHAM STATION 115KV CKT 1 | 0 | 527864 | CUNNINHAM 3115.00 | 528348 | BUCKEYE_TP 3115.00 | 0 |  | 1 | [58 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T26435021SP | FROM->TO | LEA COUNTY INTERCHANGE - LEA COUNTY REC-LOVINGTON INTERCHANGE 115KV CKT 1 | E | SPS | SPS | SPS-PECO | SPS-HOBB | 0 | 527848 | LEA_CNTY 3115.00 | 528334 | LE-LOVINTON3115.00 | 0 |  | 1 | 21SP | 159 | 175 | 0 | 98.2 | 98.193 | 98.3 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-V98 | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T4715021SP | FROM->TO | LEA COUNTY INTERCHANGE - LEA COUNTY REC-LOVINGTON INTERCHANGE 115KV CKT 1 | E | SPS | SPS | SPS-PECO | SPS-HOBB | 0 | 527848 | LEA_CNTY 3115.00 | 528334 | LE-LOVINTON3115.00 | 0 |  | 1 | 21SP | 159 | 175 | 0 | 97.6 | 97.6131 | 97.7 | [7 empty] | CATEGORYB | SINGLE | LEA COUNTY REC-SAN ANDRES INTERCHANGE - LEA COUNTY REC-TEXACO 115KV CKT 1 | 0 | 528341 | LE-SANANDRS3115.00 | 528792 | LE-TEXACO 3115.00 | 0 |  | 1 | [58 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T4685021SP | FROM->TO | LEA COUNTY INTERCHANGE - LEA COUNTY REC-LOVINGTON INTERCHANGE 115KV CKT 1 | E | SPS | SPS | SPS-PECO | SPS-HOBB | 0 | 527848 | LEA_CNTY 3115.00 | 528334 | LE-LOVINTON3115.00 | 0 |  | 1 | 21SP | 159 | 175 | 0 | 97.6 | 97.6101 | 97.6 | [7 empty] | CATEGORYB | SINGLE | LEA COUNTY REC-SAN ANDRES INTERCHANGE 115/69KV TRANSFORMER CKT 1 | 0 | 528341 | LE-SANANDRS3115.00 | 528622 | LE-SANANDRS269.000 | 0 |  | 1 | [58 empty] | 2017-06-01
2009-AGP2 | AFS5 | INVALID | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T2815512SP | TO->FROM | LEA COUNTY REC -MHOON - LEA COUNTY REC-LOVINGTON INTERCHANGE 69KV CKT 1 | E | SPS | SPS | SPS-LEA | SPS-LEA | 0 | 528618 | LE-LOVINTON269.000 | 528667 | LE-MHOON 269.000 | 0 |  | 1 | 12SP | 41 | 54 | 0 | 99.1 | 99.0747 | 98.9974 | [7 empty] | CATEGORYB | SINGLE | BUCKEYE TAP - CUNNINGHAM STATION 115KV CKT 1 | 0 | 527864 | CUNNINHAM 3115.00 | 528348 | BUCKEYE_TP 3115.00 | 0 |  | 1 | [58 empty] | 2013-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1715510WP | TO->FROM | LEHIGH TAP - OWL CREEK 69KV CKT 1 | E | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 10WP | 32 | 32 | 0 |  | 78.8847 | 95 | [7 empty] | CATEGORYB | SINGLE | ALLEN - LEHIGH TAP 69KV CKT 1 | 0 | 533621 | ALLEN 2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T2795011SP | TO->FROM | LEHIGH TAP - OWL CREEK 69KV CKT 1 | E | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 11SP | 32 | 32 | 0 | 102.6 | 102.6205 | 98.4 | [7 empty] | CATEGORYB | SINGLE | MARMATON - UNITED NO. 1 ELSMORE 69KV CKT 1 | 0 | 533639 | MARMATN2 69.000 | 533647 | UN1ELSM2 69.000 | 0 |  | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T2825011SP | TO->FROM | LEHIGH TAP - OWL CREEK 69KV CKT 1 | E | WERE | WERE | SEAST | SEAST | 0 | 533642 | OWL CRK2 69.000 | 533638 | LEHIGTP2 69.000 | 0 |  | 1 | 11SP | 32 | 32 | 0 | 101.4 | 101.3504 | 97.2 | [7 empty] | CATEGORYB | SINGLE | UNITED NO. 1 ELSMORE - ZILA JUNCTION 69KV CKT 1 | 0 | 533647 | UN1ELSM2 69.000 | 533654 | ZILAJCT2 69.000 | 0 |  | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T31135021SP | FROM->TO | LS POWER OSCEOLA UNIT 500/161KV TRANSFORMER CKT 1 | E | EES | EES | EAINTH | EAINTH | 0 | 338144 | 8ISXF 500.00 | 338142 | 5ISES-1 161.00 | 0 |  | 1 | 21SP | 425 | 425 | 0 | 97 | 97.0066 | 96.3 | [7 empty] | CATEGORYB | GENOUT | GEN338143 1-INDEPENDENCE UNIT #1 | 0 | 0 |  | 0 |  | 0
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T31155021SP | FROM->TO | LS POWER OSCEOLA UNIT 500/161KV TRANSFORMER CKT 2 | E | EES | EES | EAINTH | EAINTH | 0 | 338144 | 8ISXF 500.00 | 338152 | 5ISES-2 161.00 | 0 |  | 2 | 21SP | 425 | 425 | 0 | 98.2 | 98.1687 | 97.5 | [7 empty] | CATEGORYB | GENOUT | GEN338143 1-INDEPENDENCE UNIT #1 | 0 | 0 |  | 0 |  | 0
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T2495512SP | FROM->TO | LUBBOCK POWER & LIGHT-HOLLY PLANT 230/69KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-MUNI | SPS-MUNI | 0 | 522870 | LP-HOLLY 6230.00 | 522866 | LP-HOLLY 269.000 | 0 |  | 1 | 12SP | 100 | 140 | 0 |  | 82.2976 | 99.8 | [7 empty] | CATEGORYB | SINGLE | LUBBOCK EAST INTERCHANGE - LUBBOCK POWER & LIGHT-WADSWORTH 230KV CKT 1 | 0 | 522888 | LP-WADSWRTH6230.00 | 526299 | LUBBCK_EST 6230.00 | 0 |  | 1 | [58 empty] | 2012-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T2485512SP | FROM->TO | LUBBOCK POWER & LIGHT-SOUTHEAST 230/69KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-MUNI | SPS-MUNI | 0 | 522861 | LP-SOUTHEST6230.00 | 522857 | LP-SOUTHEST269.000 | 0 |  | 1 | 12SP | 100 | 140 | 0 |  | 83.6668 | 99.6 | [7 empty] | CATEGORYB | SINGLE | LUBBOCK EAST INTERCHANGE - LUBBOCK POWER & LIGHT-WADSWORTH 230KV CKT 1 | 0 | 522888 | LP-WADSWRTH6230.00 | 526299 | LUBBCK_EST 6230.00 | 0 |  | 1 | [58 empty] | 2012-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T1695016SP | FROM->TO | LUBBOCK POWER & LIGHT-WADSWORTH 230/69KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-MUNI | SPS-MUNI | 0 | 522888 | LP-WADSWRTH6230.00 | 522879 | LP-WADSWRTH269.000 | 0 |  | 1 | 16SP | 100 | 140 | 0 |  | 67.291 | 96.8 | [7 empty] | CATEGORYB | SINGLE | LUBBOCK POWER & LIGHT-SOUTHEAST - LUBBOCK SOUTH INTERCHANGE 230KV CKT 1 | 0 | 522861 | LP-SOUTHEST6230.00 | 526269 | LUBBCK_STH 6230.00 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T85016SP | FROM->TO | LUBBOCK POWER & LIGHT-WADSWORTH 230/69KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-MUNI | SPS-MUNI | 0 | 522888 | LP-WADSWRTH6230.00 | 522879 | LP-WADSWRTH269.000 | 0 |  | 1 | 16SP | 100 | 140 | 0 |  | 65.7164 | 95.5 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T4975021SP | TO->FROM | LYONS - WHEATLAND 115KV CKT 1 | E | WERE | WERE | WEST | REG E-IL | 0 | 533439 | WHEATLD3 115.00 | 530620 | LYONS 3 115.00 | 0 |  | 1 | 21SP | 55 | 55 | 0 | 96.1 | 96.0904 | 96.1 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICE_CO 115KV CKT 1 | 0 | 530623 | RICE 3 115.00 | 533413 | CIRCLE 3 115.00 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T16035516SP | FROM->TO | MANHATTAN TAP - OSAGE SWITCHING STATION 115KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524354 | MANHATN_TP 3115.00 | 524345 | OSAGE 3115.00 | 0 |  | 1 | 16SP | 160 | 160 | 0 |  | 94.7535 | 95.4 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-V43 | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2016-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T9025511WP | FROM->TO | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | E | SUNC | SUNC |  |  | 0 | 539673 | MED-LDG3 115.00 | 539649 | SAWYER 3 115.00 | 0 |  | 1 | 11WP | 79.7 | 79.7 | 0 |  | 92.4965 | 96.7 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-34 | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T18475512SP | FROM->TO | MEDICINE LODGE (MED-LDG4) 138/115/2.72KV TRANSFORMER CKT 1 | E | SUNC | SUNC |  |  | 2 | 539674 | MED-LDG4 138.00 | 539673 | MED-LDG3 115.00 | 539917 | MEDLGT-T 2.7200 | 1 | 12SP | 56 | 62 | 62 |  | 89.5151 | 97 | [7 empty] | CATEGORYB | GENOUT | GEN539670 4-JUDSON LARGE GENERATOR | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T18375512SP | FROM->TO | MEDICINE LODGE (MED-LDG4) 138/115/2.72KV TRANSFORMER CKT 1 | E | SUNC | SUNC |  |  | 2 | 539674 | MED-LDG4 138.00 | 539673 | MED-LDG3 115.00 | 539917 | MEDLGT-T 2.7200 | 1 | 12SP | 56 | 62 | 62 |  | 87.2672 | 95.2 | [7 empty] | CATEGORYB | GENOUT | GEN531447 1-HOLCOMB GENERATOR | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2011-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T6605012SP | FROM->TO | MONETTE JUNCTION - PARAGOULD 161 161KV CKT 1 | E | EES | EES | EAINTH | EAINTH | 0 | 338186 | 5MONETE 161.00 | 338204 | 5PARAG 161.00 | 0 |  | 1 | 12SP | 148 | 148 | 0 | 100 | 100.0097 | 98.6 | [7 empty] | CATEGORYB | SINGLE | NEWPORT - NEWPORT INDUSTRIAL 161KV CKT 1 | 0 | 338151 | 5NEWPO 161.00 | 338173 | 5NEW-IN 161.00 | 0 |  | 1 | [58 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T13725012SP | FROM->TO | MONETTE JUNCTION - PARAGOULD 161 161KV CKT 1 | E | EES | EES | EAINTH | EAINTH | 0 | 338186 | 5MONETE 161.00 | 338204 | 5PARAG 161.00 | 0 |  | 1 | 12SP | 148 | 148 | 0 | 100 | 99.9917 | 98.5 | [7 empty] | CATEGORYB | NONSINGLE | HERGETT TO N | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T6795012SP | FROM->TO | MONETTE JUNCTION - PARAGOULD 161 161KV CKT 1 | E | EES | EES | EAINTH | EAINTH | 0 | 338186 | 5MONETE 161.00 | 338204 | 5PARAG 161.00 | 0 |  | 1 | 12SP | 148 | 148 | 0 | 98.9 | 98.9447 | 97.5 | [7 empty] | CATEGORYB | SINGLE | NEWPORT AB - NEWPORT INDUSTRIAL 161KV CKT 1 | 0 | 338172 | 5NEW-AB 161.00 | 338173 | 5NEW-IN 161.00 | 0 |  | 1 | [58 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T28205521SP | FROM->TO | MONETTE JUNCTION - PARAGOULD 161 161KV CKT 1 | E | EES | EES | EAINTH | EAINTH | 0 | 338186 | 5MONETE 161.00 | 338204 | 5PARAG 161.00 | 0 |  | 1 | 21SP | 148 | 148 | 0 | 100.8 | 100.8019 | 99.6 | [7 empty] | CATEGORYB | NONSINGLE | A195 | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T15475521SP | FROM->TO | MONETTE JUNCTION - PARAGOULD 161 161KV CKT 1 | E | EES | EES | EAINTH | EAINTH | 0 | 338186 | 5MONETE 161.00 | 338204 | 5PARAG 161.00 | 0 |  | 1 | 21SP | 148 | 148 | 0 | 100.6 | 100.6305 | 99.4 | [7 empty] | CATEGORYB | SINGLE | TRUMANN - TRUMANN WEST AECC 161KV CKT 1 | 0 | 338169 | 5TRUMAN 161.00 | 338707 | 5TRUM-W# 161.00 | 0 |  | 1 | [58 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T965021SP | FROM->TO | MONETTE JUNCTION - PARAGOULD 161 161KV CKT 1 | E | EES | EES | EAINTH | EAINTH | 0 | 338186 | 5MONETE 161.00 | 338204 | 5PARAG 161.00 | 0 |  | 1 | 21SP | 148 | 148 | 0 | 98.2 | 98.1578 | 97.4 | [7 empty] | CATEGORYB | SINGLE | KENNETT - NEW MADRID 161KV CKT 1 | 0 | 505400 | N MADRD5 161.00 | 505410 | KENNETT5 161.00 | 0 |  | 1 | [58 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T3055511SP | TO->FROM | NASHUA - SMITHVILLE 161KV CKT 1 | E | MIPU | MIPU |  |  | 0 | 541204 | SMTHVL 5 161.00 | 541203 | NASHUA 5 161.00 | 0 |  | 1 | 11SP | 224 | 224 | 224 | 99.8 | 99.8344 | 99.2 | [7 empty] | CATEGORYB | SINGLE | IATAN - STRANGER CREEK 345KV CKT 1 | 0 | 532772 | STRANGR7 345.00 | 542982 | IATAN 7 345.00 | 0 |  | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T8895511WP | TO->FROM | NASHUA - SMITHVILLE 161KV CKT 1 | E | MIPU | MIPU |  |  | 0 | 541204 | SMTHVL 5 161.00 | 541203 | NASHUA 5 161.00 | 0 |  | 1 | 11WP | 245 | 245 | 245 |  | 94.0421 | 95.8 | [7 empty] | CATEGORYB | NONSINGLE | KCPL-OPGD#07 | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2010-10-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T3315512SP | TO->FROM | NASHUA - SMITHVILLE 161KV CKT 1 | E | MIPU | MIPU |  |  | 0 | 541204 | SMTHVL 5 161.00 | 541203 | NASHUA 5 161.00 | 0 |  | 1 | 12SP | 224 | 224 | 224 | 99.1 | 99.1114 | 97.7 | [7 empty] | CATEGORYB | SINGLE | IATAN - STRANGER CREEK 345KV CKT 1 | 0 | 532772 | STRANGR7 345.00 | 542982 | IATAN 7 345.00 | 0 |  | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1725512WP | TO->FROM | NASHUA - SMITHVILLE 161KV CKT 1 | E | MIPU | MIPU |  |  | 0 | 541204 | SMTHVL 5 161.00 | 541203 | NASHUA 5 161.00 | 0 |  | 1 | 12WP | 245 | 245 | 245 |  | 92.2215 | 95 | [7 empty] | CATEGORYB | SINGLE | KCI - PLATTE CITY 161KV CKT 1 | 0 | 541212 | KCI 5 161.00 | 541221 | PLTCTY 5 161.00 | 0 |  | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T15905521SP | FROM->TO | NEWPORT - NEWPORT INDUSTRIAL 161KV CKT 1 | E | EES | EES | EAINTH | EAINTH | 0 | 338151 | 5NEWPO 161.00 | 338173 | 5NEW-IN 161.00 | 0 |  | 1 | 21SP | 335 | 335 | 0 | 97.9 | 97.8894 | 98.5 | [7 empty] | CATEGORYB | SINGLE | PARAGOULD 161 - PARAGOULD SOUTH (AECC) 161KV CKT 1 | 0 | 338204 | 5PARAG 161.00 | 338706 | 5PARA-S# 161.00 | 0 |  | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T15395521SP | FROM->TO | NEWPORT - NEWPORT INDUSTRIAL 161KV CKT 1 | E | EES | EES | EAINTH | EAINTH | 0 | 338151 | 5NEWPO 161.00 | 338173 | 5NEW-IN 161.00 | 0 |  | 1 | 21SP | 335 | 335 | 0 | 97.2 | 97.2139 | 97.7 | [7 empty] | CATEGORYB | SINGLE | HARISBURG TAP - MARKED TREE 161KV CKT 1 | 0 | 338165 | 5MTREE 161.00 | 338167 | 5HRSBRG* 161.00 | 0 |  | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T16165521SP | FROM->TO | NEWPORT - NEWPORT INDUSTRIAL 161KV CKT 1 | E | EES | EES | EAINTH | EAINTH | 0 | 338151 | 5NEWPO 161.00 | 338173 | 5NEW-IN 161.00 | 0 |  | 1 | 21SP | 335 | 335 | 0 | 96.7 | 96.6586 | 97.2 | [7 empty] | CATEGORYB | SINGLE | JONESBORO NORTH (AECC) - PARAGOULD SOUTH (AECC) 161KV CKT 1 | 0 | 338703 | 5JONE-N# 161.00 | 338706 | 5PARA-S# 161.00 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T11015512SP | FROM->TO | NORTHWEST (NORTWST2) 345/138/13.8KV TRANSFORMER CKT 1 | E | OKGE | OKGE |  |  | 2 | 514880 | NORTWST7 345.00 | 514879 | NORTWST4 138.00 | 515742 | NORTWS21 13.800 | 1 | 12SP | 493 | 493 | 0 |  | 94.7766 | 98.8 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST (NORTWST3) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514879 | NORTWST4 138.00 | 514880 | NORTWST7 345.00 | 515743 | NORTWS31 13.800 | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T11015512SP | FROM->TO | NORTHWEST (NORTWST2) 345/138/13.8KV TRANSFORMER CKT 1 | E | OKGE | OKGE |  |  | 2 | 514880 | NORTWST7 345.00 | 514879 | NORTWST4 138.00 | 515742 | NORTWS21 13.800 | 1 | 12SP | 493 | 493 | 0 |  | 94.7766 | 98.8 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST (NORTWST3) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514879 | NORTWST4 138.00 | 514880 | NORTWST7 345.00 | 515743 | NORTWS31 13.800 | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T19055521SP | FROM->TO | NORTHWEST (NORTWST3) 345/138/13.8KV TRANSFORMER CKT 1 | E | OKGE | OKGE |  |  | 2 | 514880 | NORTWST7 345.00 | 514879 | NORTWST4 138.00 | 515743 | NORTWS31 13.800 | 1 | 21SP | 493 | 493 | 0 |  | 94.1434 | 96.9 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST (NORTWST2) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514879 | NORTWST4 138.00 | 514880 | NORTWST7 345.00 | 515742 | NORTWS21 13.800 | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T19055521SP | FROM->TO | NORTHWEST (NORTWST3) 345/138/13.8KV TRANSFORMER CKT 1 | E | OKGE | OKGE |  |  | 2 | 514880 | NORTWST7 345.00 | 514879 | NORTWST4 138.00 | 515743 | NORTWS31 13.800 | 1 | 21SP | 493 | 493 | 0 |  | 94.1434 | 96.9 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST (NORTWST2) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514879 | NORTWST4 138.00 | 514880 | NORTWST7 345.00 | 515742 | NORTWS21 13.800 | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T3105011SP | FROM->TO | OGALLALA 230/115KV TRANSFORMER CKT 1 | E | NPPD | NPPD | NPPD_686 | BEPC_1628 | 0 | 640302 | OGALALA4 230.00 | 659132 | OGALALA7 115.00 | 0 |  | 1 | 11SP | 187 | 187 | 233.8 | 99.6 | 99.6125 | 99.5 | [7 empty] | CATEGORYB | SINGLE | KEYSTONE - OGALLALLA 115KV CKT 1 | 0 | 640253 | KEYSTON7 115.00 | 659132 | OGALALA7 115.00 | 0 |  | 1 | [58 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T10085011SP | FROM->TO | OGALLALA 230/115KV TRANSFORMER CKT 1 | E | NPPD | NPPD | NPPD_686 | BEPC_1628 | 0 | 640302 | OGALALA4 230.00 | 659132 | OGALALA7 115.00 | 0 |  | 1 | 11SP | 187 | 187 | 233.8 | 96.6 | 96.5744 | 96.4 | [7 empty] | CATEGORYB | SINGLE | KEYSTONE (KEYST T1) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 640252 | KEYSTON3 345.00 | 640253 | KEYSTON7 115.00 | 640254 | KEYSTON9 13.800 | 1 | [58 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T3325012SP | FROM->TO | OGALLALA 230/115KV TRANSFORMER CKT 1 | E | NPPD | NPPD | NPPD_686 | BEPC_1628 | 0 | 640302 | OGALALA4 230.00 | 659132 | OGALALA7 115.00 | 0 |  | 1 | 12SP | 187 | 187 | 233.8 | 99.3 | 99.329 | 99.8 | [7 empty] | CATEGORYB | SINGLE | KEYSTONE - OGALLALLA 115KV CKT 1 | 0 | 640253 | KEYSTON7 115.00 | 659132 | OGALALA7 115.00 | 0 |  | 1 | [58 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T10285012SP | FROM->TO | OGALLALA 230/115KV TRANSFORMER CKT 1 | E | NPPD | NPPD | NPPD_686 | BEPC_1628 | 0 | 640302 | OGALALA4 230.00 | 659132 | OGALALA7 115.00 | 0 |  | 1 | 12SP | 187 | 187 | 233.8 | 96.3 | 96.3066 | 96.8 | [7 empty] | CATEGORYB | SINGLE | KEYSTONE (KEYST T1) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 640252 | KEYSTON3 345.00 | 640253 | KEYSTON7 115.00 | 640254 | KEYSTON9 13.800 | 1 | [58 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T21995021SP | FROM->TO | OGALLALA 230/115KV TRANSFORMER CKT 1 | E | NPPD | NPPD | NPPD_686 | BEPC_1628 | 0 | 640302 | OGALALA4 230.00 | 659132 | OGALALA7 115.00 | 0 |  | 1 | 21SP | 187 | 187 | 233.8 | 96.3 | 96.2588 | 95.9 | [7 empty] | CATEGORYB | SINGLE | KEYSTONE (KEYST T1) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 640252 | KEYSTON3 345.00 | 640253 | KEYSTON7 115.00 | 640254 | KEYSTON9 13.800 | 1 | [58 empty] | 2017-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T965512WP | FROM->TO | OKEENE - WATONGA SW 69KV CKT 1 | E | WFEC | WFEC | AEP-IM | AEP-IM | 0 | 521015 | OKEENE 2 69.000 | 521090 | WATNGSW2 69.000 | 0 |  | 1 | 12WP | 48 | 48 | 48 |  | 68.1535 | 99 | [7 empty] | CATEGORYB | SINGLE | DOVER SW - OKEENE 138KV CKT 1 | 0 | 520882 | DOVERSW4 138.00 | 521016 | OKEENE 4 138.00 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T4635512WP | FROM->TO | OKEENE - WATONGA SW 69KV CKT 1 | E | WFEC | WFEC | AEP-IM | AEP-IM | 0 | 521015 | OKEENE 2 69.000 | 521090 | WATNGSW2 69.000 | 0 |  | 1 | 12WP | 48 | 48 | 48 |  | 64.7546 | 95.4 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T4925021SP | FROM->TO | OMHUFFYT - OMMORANT 69KV CKT 1 | E | OMPA | OMPA | DOE | DOE | 0 | 529242 | OMHUFFYT 69.000 | 529241 | OMMORANT 69.000 | 0 |  | 1 | 21SP | 95 | 95 | 0 | 101.4 | 101.3627 | 96.2 | [7 empty] | CATEGORYB | SINGLE | OMNWESTT - OMPA-PONCA CITY 69KV CKT 1 | 0 | 529243 | OMNWESTT 69.000 | 529251 | OMRIGGS 69.000 | 0 |  | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T4945021SP | TO->FROM | OMHUFFYT - OMPA-PONCA CITY 69KV CKT 1 | E | OMPA | OMPA | DOE | DOE | 0 | 529251 | OMRIGGS 69.000 | 529242 | OMHUFFYT 69.000 | 0 |  | 1 | 21SP | 95 | 95 | 0 | 101.9 | 101.9199 | 96.9 | [7 empty] | CATEGORYB | SINGLE | OMKAWS - OMPECANT 69KV CKT 1 | 0 | 529246 | OMKAWS 69.000 | 529248 | OMPECANT 69.000 | 0 |  | 1 | [58 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T4915021SP | TO->FROM | OMHUFFYT - OMPA-PONCA CITY 69KV CKT 1 | E | OMPA | OMPA | DOE | DOE | 0 | 529251 | OMRIGGS 69.000 | 529242 | OMHUFFYT 69.000 | 0 |  | 1 | 21SP | 95 | 95 | 0 | 100.7 | 100.7136 | 95.6 | [7 empty] | CATEGORYB | SINGLE | OMNEASTT - OMNWESTT 69KV CKT 1 | 0 | 529243 | OMNWESTT 69.000 | 529244 | OMNEASTT 69.000 | 0 |  | 1 | [58 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T4885021SP | TO->FROM | OMNEASTT - OMNWESTT 69KV CKT 1 | E | OMPA | OMPA | DOE | DOE | 0 | 529243 | OMNWESTT 69.000 | 529244 | OMNEASTT 69.000 | 0 |  | 1 | 21SP | 92 | 92 | 0 | 103.8 | 103.7811 | 98.4 | [7 empty] | CATEGORYB | SINGLE | OMHUFFYT - OMPA-PONCA CITY 69KV CKT 1 | 0 | 529242 | OMHUFFYT 69.000 | 529251 | OMRIGGS 69.000 | 0 |  | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T4875021SP | TO->FROM | OMNWESTT - OMPA-PONCA CITY 69KV CKT 1 | E | OMPA | OMPA | DOE | DOE | 0 | 529251 | OMRIGGS 69.000 | 529243 | OMNWESTT 69.000 | 0 |  | 1 | 21SP | 92 | 92 | 0 | 104.8 | 104.8088 | 99.5 | [7 empty] | CATEGORYB | SINGLE | OMHUFFYT - OMMORANT 69KV CKT 1 | 0 | 529241 | OMMORANT 69.000 | 529242 | OMHUFFYT 69.000 | 0 |  | 1 | [58 empty] | 2017-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T18805521SP | TO->FROM | OMPA-MANGUM - RUSSELL 69KV CKT 1 | E | WFEC | OMPA | AEP-KP | DOE | 0 | 521042 | RUSSELL2 69.000 | 529342 | OMMANGM2 69.000 | 0 |  | 1 | 21SP | 48 | 48 | 48 |  | 81.0502 | 95.5 | [7 empty] | CATEGORYB | SINGLE | ELK CITY (ELKCTY-4) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 511458 | ELKCTY-4 138.00 | 511459 | ELKCTY-2 69.000 | 511493 | ELKC4-1 13.800 | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T3755521SP | TO->FROM | OSAGE SWITCHING STATION - PIERCE STREET TAP 115KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524185 | PIERCE_TP 3115.00 | 524345 | OSAGE 3115.00 | 0 |  | 1 | 21SP | 160 | 160 | 0 | 95.3 | 95.301 | 96.6 | [7 empty] | CATEGORYB | SINGLE | EAST PLANT INTERCHANGE - MANHATTAN SUB 115KV CKT 1 | 0 | 524162 | EAST_PLANT 3115.00 | 524224 | MANHATTAN 3115.00 | 0 |  | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T4015021SP | TO->FROM | OSAGE SWITCHING STATION - RANDALL COUNTY INTERCHANGE 115KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524364 | RANDALL 3115.00 | 524345 | OSAGE 3115.00 | 0 |  | 1 | 21SP | 160 | 160 | 0 | 99.5 | 99.4974 | 99.5 | [7 empty] | CATEGORYB | SINGLE | MANHATTAN TAP - OSAGE SWITCHING STATION 115KV CKT 1 | 0 | 524345 | OSAGE 3115.00 | 524354 | MANHATN_TP 3115.00 | 0 |  | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T3785021SP | FROM->TO | OSAGE SWITCHING STATION - SOUTH GEORGIA INTERCHANGE 115KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524345 | OSAGE 3115.00 | 524322 | GEORGIA 3115.00 | 0 |  | 1 | 21SP | 160 | 160 | 0 | 99.1 | 99.1043 | 99.6 | [7 empty] | CATEGORYB | SINGLE | BUSHLAND INTERCHANGE - POTTER COUNTY INTERCHANGE 230KV CKT 1 | 0 | 523959 | POTTER_CO 6230.00 | 524267 | BUSHLAND 6230.00 | 0 |  | 1 | [58 empty] | 2013-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T4055021SP | FROM->TO | OSAGE SWITCHING STATION - SOUTH GEORGIA INTERCHANGE 115KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524345 | OSAGE 3115.00 | 524322 | GEORGIA 3115.00 | 0 |  | 1 | 21SP | 160 | 160 | 0 | 99.2 | 99.2299 | 99.4 | [7 empty] | CATEGORYB | SINGLE | CROUSE HINDS SUB - FARMERS SUB 115KV CKT 1 | 0 | 524377 | FARMERS 3115.00 | 524388 | CROUSE_HIND3115.00 | 0 |  | 1 | [58 empty] | 2013-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T4005021SP | FROM->TO | OSAGE SWITCHING STATION - SOUTH GEORGIA INTERCHANGE 115KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524345 | OSAGE 3115.00 | 524322 | GEORGIA 3115.00 | 0 |  | 1 | 21SP | 160 | 160 | 0 | 98.6 | 98.573 | 98.7 | [7 empty] | CATEGORYB | SINGLE | CROUSE HINDS SUB - SOUTH GEORGIA INTERCHANGE 115KV CKT 1 | 0 | 524322 | GEORGIA 3115.00 | 524388 | CROUSE_HIND3115.00 | 0 |  | 1 | [58 empty] | 2013-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T8675011SP | FROM->TO | OUSW4 (OW SW) 138/69/13.8KV TRANSFORMER CKT 1 | E | WFEC | WFEC | AEP-IM-I | AEP-IM-I | 1 | 521104 | OU SW 4 138.00 | 521018 | OU SW 2 69.000 | 521183 | OUSWTERT 13.800 | 1 | 11SP | 70 | 70 | 70 |  | 94.1461 | 95.2 | [7 empty] | CATEGORYB | SINGLE | FRANKLIN SW (FRANKLIN) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 520916 | FRNKLNS2 69.000 | 520917 | FRNKLNS4 138.00 | 521169 | FRNKTERT 13.800 | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T8895012SP | FROM->TO | OUSW4 (OW SW) 138/69/13.8KV TRANSFORMER CKT 1 | E | WFEC | WFEC | AEP-IM-I | AEP-IM-I | 1 | 521104 | OU SW 4 138.00 | 521018 | OU SW 2 69.000 | 521183 | OUSWTERT 13.800 | 1 | 12SP | 70 | 70 | 70 | 95.2 | 95.1526 | 95.5 | [7 empty] | CATEGORYB | SINGLE | FRANKLIN SW (FRANKLIN) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 520916 | FRNKLNS2 69.000 | 520917 | FRNKLNS4 138.00 | 521169 | FRNKTERT 13.800 | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T13905012SP | FROM->TO | PARKIN - TWIST 161KV CKT 1 | E | EES | EES | EAICEN | EAICEN | 0 | 338033 | 5PARKIN 161.00 | 338041 | 5TWIST 161.00 | 0 |  | 1 | 12SP | 112 | 112 | 0 | 99.5 | 99.4586 | 98.4 | [7 empty] | CATEGORYB | NONSINGLE | A043 | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2011-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T15795521SP | FROM->TO | PARKIN - TWIST 161KV CKT 1 | E | EES | EES | EAICEN | EAICEN | 0 | 338033 | 5PARKIN 161.00 | 338041 | 5TWIST 161.00 | 0 |  | 1 | 21SP | 112 | 112 | 0 | 99.6 | 99.5517 | 99.7 | [7 empty] | CATEGORYB | SINGLE | MONETTE JUNCTION - PARAGOULD 161 161KV CKT 1 | 0 | 338186 | 5MONETE 161.00 | 338204 | 5PARAG 161.00 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T28075521SP | FROM->TO | PARKIN - TWIST 161KV CKT 1 | E | EES | EES | EAICEN | EAICEN | 0 | 338033 | 5PARKIN 161.00 | 338041 | 5TWIST 161.00 | 0 |  | 1 | 21SP | 112 | 112 | 0 | 99.2 | 99.2301 | 99.5 | [7 empty] | CATEGORYB | NONSINGLE | A068 | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2011-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T705012SP | FROM->TO | PECAN CREEK - RIVERSIDE STATION 345KV CKT 1 | E | OKGE | AEPW | MUSKOGEE | TULSA | 0 | 515235 | PECANCK7 345.00 | 509782 | R.S.S.-7 345.00 | 0 |  | 1 | 12SP | 1052 | 1052 | 0 | 105.2 | 105.2173 | 97.3 | [7 empty] | CATEGORYB | SINGLE | CLARKSVILLE - MUSKOGEE 345KV CKT 1 | 0 | 509745 | CLARKSV7 345.00 | 515224 | MUSKOGE7 345.00 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T15595512SP | FROM->TO | PLANT X STATION (WH ALM20171) 230/115/13.2KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 1 | 525481 | PLANT_X 6230.00 | 525480 | PLANT_X 3115.00 | 525479 | PLANTX_TR1 113.200 | 1 | 12SP | 239 | 239 | 0 |  | 91.0575 | 98.8 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-K37 | 0 | 0 |  | 0 |  | 0
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T4145511SP | FROM->TO | PLATTE CITY - SMITHVILLE 161KV CKT 1 | E | MIPU | MIPU |  |  | 0 | 541221 | PLTCTY 5 161.00 | 541204 | SMTHVL 5 161.00 | 0 |  | 1 | 11SP | 233 | 265 | 265 | 98.7 | 98.7396 | 98.8 | [7 empty] | CATEGORYB | SINGLE | FERRELVIEW - KCI 161KV CKT 1 | 0 | 541212 | KCI 5 161.00 | 541213 | FRLVW 5 161.00 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T4095512SP | FROM->TO | PLATTE CITY - SMITHVILLE 161KV CKT 1 | E | MIPU | MIPU |  |  | 0 | 541221 | PLTCTY 5 161.00 | 541204 | SMTHVL 5 161.00 | 0 |  | 1 | 12SP | 233 | 265 | 265 | 100.2 | 100.219 | 99.6 | [7 empty] | CATEGORYB | SINGLE | FERRELVIEW - KCI 161KV CKT 1 | 0 | 541212 | KCI 5 161.00 | 541213 | FRLVW 5 161.00 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T15205512SP | FROM->TO | PLATTE CITY - SMITHVILLE 161KV CKT 1 | E | MIPU | MIPU |  |  | 0 | 541221 | PLTCTY 5 161.00 | 541204 | SMTHVL 5 161.00 | 0 |  | 1 | 12SP | 233 | 265 | 265 | 99.9 | 99.8552 | 98.1 | [7 empty] | CATEGORYB | NONSINGLE | KCPL-OPGD#01 | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2011-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T11765011SP | FROM->TO | PLEASANT HILL 500/161KV TRANSFORMER CKT 1 | E | EES | EES | EAICEN | EAICEN | 0 | 337922 | 8P HILL 500.00 | 337923 | 5P HILL 161.00 | 0 |  | 1 | 11SP | 600 | 600 | 0 | 97.2 | 97.1758 | 96.3 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE (ANO) 500/161/22.0KV TRANSFORMER CKT 1 | 1 | 337909 | 8ANO 50 500.00 | 337912 | 5ANO 161.00 | 337913 | 1ANOACCD 22.000 | 1 | [58 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T11895012SP | FROM->TO | PLEASANT HILL 500/161KV TRANSFORMER CKT 1 | E | EES | EES | EAICEN | EAICEN | 0 | 337922 | 8P HILL 500.00 | 337923 | 5P HILL 161.00 | 0 |  | 1 | 12SP | 600 | 600 | 0 | 98.1 | 98.0822 | 97.3 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE (ANO) 500/161/22.0KV TRANSFORMER CKT 1 | 1 | 337909 | 8ANO 50 500.00 | 337912 | 5ANO 161.00 | 337913 | 1ANOACCD 22.000 | 1 | [58 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T13645016SP | FROM->TO | PLEASANT HILL 500/161KV TRANSFORMER CKT 1 | E | EES | EES | EAICEN | EAICEN | 0 | 337922 | 8P HILL 500.00 | 337923 | 5P HILL 161.00 | 0 |  | 1 | 16SP | 600 | 600 | 0 | 98.5 | 98.5108 | 97.8 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE (ANO) 500/161/22.0KV TRANSFORMER CKT 1 | 1 | 337909 | 8ANO 50 500.00 | 337912 | 5ANO 161.00 | 337913 | 1ANOACCD 22.000 | 1 | [58 empty] | 2017-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T9035511WP | TO->FROM | PRATT - SAWYER 3 115.00 115KV CKT 1 | E | SUNC | SUNC |  |  | 0 | 539649 | SAWYER 3 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 | 11WP | 79.7 | 79.7 | 0 |  | 92.1684 | 96.4 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-34 | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T13075011SP | FROM->TO | RICHLAND - UDALL 69KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533550 | RICHLAN2 69.000 | 533559 | UDALL 2 69.000 | 0 |  | 1 | 11SP | 43 | 43 | 0 |  | 70.423 | 99.7 | [7 empty] | CATEGORYB | NONSINGLE | WRTOD1104 | 0 | 0 |  | 0 |  | 0
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T26515021SP | FROM->TO | RICHLAND - UDALL 69KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533550 | RICHLAN2 69.000 | 533559 | UDALL 2 69.000 | 0 |  | 1 | 21SP | 43 | 43 | 0 |  | -999 | 98.4 | [7 empty] | CATEGORYB | NONSINGLE | WRTOD1104 | 0 | 0 |  | 0 |  | 0
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T4585512WP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | E | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 12WP | 171 | 185 | 0 |  | 55.0115 | 97.5 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T4585512WP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | E | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 12WP | 171 | 185 | 0 |  | 55.0115 | 97.5 | [7 empty] | CATEGORYB | SINGLE | WWRDEHV7 345.00 (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T815512WP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | E | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 12WP | 171 | 185 | 0 |  | 54.9776 | 97.4 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WWRDEHV7 345.00 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T815512WP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | E | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 12WP | 171 | 185 | 0 |  | 54.9776 | 97.4 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WWRDEHV7 345.00 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T695512WP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | E | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 12WP | 171 | 185 | 0 |  | 54.7828 | 97 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T695512WP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | E | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 12WP | 171 | 185 | 0 |  | 54.7828 | 97 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 | [58 empty] | 2011-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T1615012SP | FROM->TO | ROOSEVELT COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CLHF | SPS-CLHF | 0 | 524909 | ROSEVELT_N 6230.00 | 524908 | ROOSEVELT 3115.00 | 0 |  | 1 | 12SP | 252 | 289.8 | 0 |  | 94.8997 | 97.1 | [7 empty] | CATEGORYB | SINGLE | OASIS INTERCHANGE - Roosevelt County Interchange SWITCH #4K33 230KV CKT 1 | 0 | 524875 | OASIS 6230.00 | 524915 | SW_4K33 6230.00 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1585510WP | FROM->TO | S1399 5 (FLTWTR TFMR) 161/34.5/13.8KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 1 | 648500 | FLTWTRX9 34.500 | 646399 | S1399 5 161.00 | 648501 | FLTWTRY9 13.800 | 1 | 10WP | 66 | 66 | 66 |  | 4.8e-08 | 98.6 | [7 empty] | CATEGORYB | SINGLE | KELLY - S1399 5 161KV CKT 1 | 0 | 532913 | KELLY 5 161.00 | 646399 | S1399 5 161.00 | 0 |  | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T14645510WP | FROM->TO | S1399 5 (FLTWTR TFMR) 161/34.5/13.8KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 1 | 648500 | FLTWTRX9 34.500 | 646399 | S1399 5 161.00 | 648501 | FLTWTRY9 13.800 | 1 | 10WP | 66 | 66 | 66 |  | 4.8e-08 | 98.4 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-02A | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T10925511SP | FROM->TO | S1399 5 (FLTWTR TFMR) 161/34.5/13.8KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 1 | 648500 | FLTWTRX9 34.500 | 646399 | S1399 5 161.00 | 648501 | FLTWTRY9 13.800 | 1 | 11SP | 66 | 66 | 66 |  | 0 | 96.5 | [7 empty] | CATEGORYB | SINGLE | KELLY (KELLY 1X) 161/115/13.8KV TRANSFORMER CKT 1 | 1 | 532913 | KELLY 5 161.00 | 533217 | KELLY 3 115.00 | 532942 | KELLY 1 13.800 | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T15015511SP | FROM->TO | S1399 5 (FLTWTR TFMR) 161/34.5/13.8KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 1 | 648500 | FLTWTRX9 34.500 | 646399 | S1399 5 161.00 | 648501 | FLTWTRY9 13.800 | 1 | 11SP | 66 | 66 | 66 |  | 0 | 95.7 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-02A | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T3355511SP | FROM->TO | S1399 5 (FLTWTR TFMR) 161/34.5/13.8KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 1 | 648500 | FLTWTRX9 34.500 | 646399 | S1399 5 161.00 | 648501 | FLTWTRY9 13.800 | 1 | 11SP | 66 | 66 | 66 |  | 0 | 95.5 | [7 empty] | CATEGORYB | SINGLE | KELLY - S1399 5 161KV CKT 1 | 0 | 532913 | KELLY 5 161.00 | 646399 | S1399 5 161.00 | 0 |  | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1255511WP | FROM->TO | S1399 5 (FLTWTR TFMR) 161/34.5/13.8KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 1 | 648500 | FLTWTRX9 34.500 | 646399 | S1399 5 161.00 | 648501 | FLTWTRY9 13.800 | 1 | 11WP | 66 | 66 | 66 |  | 2e-09 | 99.9 | [7 empty] | CATEGORYB | SINGLE | KELLY - S1399 5 161KV CKT 1 | 0 | 532913 | KELLY 5 161.00 | 646399 | S1399 5 161.00 | 0 |  | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T9015511WP | FROM->TO | S1399 5 (FLTWTR TFMR) 161/34.5/13.8KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 1 | 648500 | FLTWTRX9 34.500 | 646399 | S1399 5 161.00 | 648501 | FLTWTRY9 13.800 | 1 | 11WP | 66 | 66 | 66 |  | 1.3e-08 | 99.7 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-02A | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T1095011WP | FROM->TO | S1399 5 (FLTWTR TFMR) 161/34.5/13.8KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 1 | 648500 | FLTWTRX9 34.500 | 646399 | S1399 5 161.00 | 648501 | FLTWTRY9 13.800 | 1 | 11WP | 66 | 66 | 66 |  | 1.1e-08 | 98.8 | [7 empty] | CATEGORYB | SINGLE | KELLY - SOUTH SENECA 115KV CKT 1 | 0 | 533217 | KELLY 3 115.00 | 533337 | SENECA 3 115.00 | 0 |  | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T5145012WP | FROM->TO | S1399 5 (FLTWTR TFMR) 161/34.5/13.8KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 1 | 648500 | FLTWTRX9 34.500 | 646399 | S1399 5 161.00 | 648501 | FLTWTRY9 13.800 | 1 | 12WP | 66 | 66 | 66 |  | 9e-09 | 99.3 | [7 empty] | CATEGORYB | SINGLE | KELLY (KELLY 1X) 161/115/13.8KV TRANSFORMER CKT 1 | 1 | 532913 | KELLY 5 161.00 | 533217 | KELLY 3 115.00 | 532942 | KELLY 1 13.800 | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T7355512WP | FROM->TO | S1399 5 (FLTWTR TFMR) 161/34.5/13.8KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 1 | 648500 | FLTWTRX9 34.500 | 646399 | S1399 5 161.00 | 648501 | FLTWTRY9 13.800 | 1 | 12WP | 66 | 66 | 66 |  | 1.4e-08 | 98.2 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-02A | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T10525516WP | FROM->TO | S1399 5 (FLTWTR TFMR) 161/34.5/13.8KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 1 | 648500 | FLTWTRX9 34.500 | 646399 | S1399 5 161.00 | 648501 | FLTWTRY9 13.800 | 1 | 16WP | 66 | 66 | 66 |  | 4e-09 | 98.1 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-02A | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T7415516WP | FROM->TO | S1399 5 (FLTWTR TFMR) 161/34.5/13.8KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 1 | 648500 | FLTWTRX9 34.500 | 646399 | S1399 5 161.00 | 648501 | FLTWTRY9 13.800 | 1 | 16WP | 66 | 66 | 66 |  | 3e-09 | 97.9 | [7 empty] | CATEGORYB | SINGLE | KELLY (KELLY 1X) 161/115/13.8KV TRANSFORMER CKT 1 | 1 | 532913 | KELLY 5 161.00 | 533217 | KELLY 3 115.00 | 532942 | KELLY 1 13.800 | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1515516WP | FROM->TO | S1399 5 (FLTWTR TFMR) 161/34.5/13.8KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 1 | 648500 | FLTWTRX9 34.500 | 646399 | S1399 5 161.00 | 648501 | FLTWTRY9 13.800 | 1 | 16WP | 66 | 66 | 66 |  | 3e-09 | 97.6 | [7 empty] | CATEGORYB | SINGLE | KELLY - S1399 5 161KV CKT 1 | 0 | 532913 | KELLY 5 161.00 | 646399 | S1399 5 161.00 | 0 |  | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T20345021SP | FROM->TO | S1399 5 (FLTWTR TFMR) 161/34.5/13.8KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 1 | 648500 | FLTWTRX9 34.500 | 646399 | S1399 5 161.00 | 648501 | FLTWTRY9 13.800 | 1 | 21SP | 66 | 66 | 66 |  | 6e-09 | 96.8 | [7 empty] | CATEGORYB | SINGLE | KELLY (KELLY 1X) 161/115/13.8KV TRANSFORMER CKT 1 | 1 | 532913 | KELLY 5 161.00 | 533217 | KELLY 3 115.00 | 532942 | KELLY 1 13.800 | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T5345521SP | FROM->TO | S1399 5 (FLTWTR TFMR) 161/34.5/13.8KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 1 | 648500 | FLTWTRX9 34.500 | 646399 | S1399 5 161.00 | 648501 | FLTWTRY9 13.800 | 1 | 21SP | 66 | 66 | 66 |  | 5e-09 | 96.1 | [7 empty] | CATEGORYB | SINGLE | KELLY - S1399 5 161KV CKT 1 | 0 | 532913 | KELLY 5 161.00 | 646399 | S1399 5 161.00 | 0 |  | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T26005521SP | FROM->TO | S1399 5 (FLTWTR TFMR) 161/34.5/13.8KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 1 | 648500 | FLTWTRX9 34.500 | 646399 | S1399 5 161.00 | 648501 | FLTWTRY9 13.800 | 1 | 21SP | 66 | 66 | 66 |  | 8e-09 | 95.9 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-02A | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2010-10-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T13065012SP | FROM->TO | SEVENTEENTH (17TH 4X) 138/69/11.295KV TRANSFORMER CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 1 | 533064 | 17TH 4 138.00 | 533840 | 17TH 2 69.000 | 533112 | 17TH 4 1 11.295 | 1 | 12SP | 150 | 165 | 187.5 | 96 | 95.9715 | 97.2 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T3005012SP | FROM->TO | SEVENTEENTH (17TH 4X) 138/69/11.295KV TRANSFORMER CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 1 | 533064 | 17TH 4 138.00 | 533840 | 17TH 2 69.000 | 533112 | 17TH 4 1 11.295 | 1 | 12SP | 150 | 165 | 187.5 |  | 94.6125 | 96 | [7 empty] | CATEGORYB | SINGLE | CHISHOLM - RIPLEY 69KV CKT 1 | 0 | 533786 | CHISHLM2 69.000 | 533832 | RIPLEYM2 69.000 | 0 |  | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T10545511SP | FROM->TO | SEWARD - SEWRDMW3 115KV CKT 1 | E | SUNC | MIDW |  | REG E-IL | 0 | 539692 | SEWARD 3 115.00 | 530679 | SEWRDMW3 115.00 | 0 |  | 1 | 11SP | 60 | 60 | 0 | 100.5 | 100.5013 | 96 | [7 empty] | CATEGORYB | SINGLE | HEIZER 6 230.00 (HEIZER T1) 230/115/12.5KV TRANSFORMER CKT 1 | 1 | 530601 | HEIZER 3 115.00 | 530680 | HEIZER 6 230.00 | 530626 | HZRT1 1 12.500 | 1 | [58 empty] | 2012-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T10545511SP | FROM->TO | SEWARD - SEWRDMW3 115KV CKT 1 | E | SUNC | MIDW |  | REG E-IL | 0 | 539692 | SEWARD 3 115.00 | 530679 | SEWRDMW3 115.00 | 0 |  | 1 | 11SP | 60 | 60 | 0 | 100.5 | 100.5013 | 96 | [7 empty] | CATEGORYB | SINGLE | HEIZER 6 230.00 (HEIZER T1) 230/115/12.5KV TRANSFORMER CKT 1 | 1 | 530601 | HEIZER 3 115.00 | 530680 | HEIZER 6 230.00 | 530626 | HZRT1 1 12.500 | 1 | [58 empty] | 2012-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T10545511SP | FROM->TO | SEWARD - SEWRDMW3 115KV CKT 1 | E | SUNC | MIDW |  | REG E-IL | 0 | 539692 | SEWARD 3 115.00 | 530679 | SEWRDMW3 115.00 | 0 |  | 1 | 11SP | 60 | 60 | 0 | 100.5 | 100.5013 | 96 | [7 empty] | CATEGORYB | SINGLE | HEIZER 6 230.00 (HEIZER T1) 230/115/12.5KV TRANSFORMER CKT 1 | 1 | 530601 | HEIZER 3 115.00 | 530680 | HEIZER 6 230.00 | 530626 | HZRT1 1 12.500 | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T2925516SP | FROM->TO | SEWARD - SEWRDMW3 115KV CKT 1 | E | SUNC | MIDW |  | REG E-IL | 0 | 539692 | SEWARD 3 115.00 | 530679 | SEWRDMW3 115.00 | 0 |  | 1 | 16SP | 60 | 60 | 0 | 106.1 | 106.0862 | 97.5 | [7 empty] | CATEGORYB | SINGLE | HEIZER 6 230.00 - MULLERGREN 230KV CKT 1 | 0 | 530680 | HEIZER 6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | [58 empty] | 2012-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T2925516SP | FROM->TO | SEWARD - SEWRDMW3 115KV CKT 1 | E | SUNC | MIDW |  | REG E-IL | 0 | 539692 | SEWARD 3 115.00 | 530679 | SEWRDMW3 115.00 | 0 |  | 1 | 16SP | 60 | 60 | 0 | 106.1 | 106.0862 | 97.5 | [7 empty] | CATEGORYB | SINGLE | HEIZER 6 230.00 - MULLERGREN 230KV CKT 1 | 0 | 530680 | HEIZER 6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | [58 empty] | 2012-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T2925516SP | FROM->TO | SEWARD - SEWRDMW3 115KV CKT 1 | E | SUNC | MIDW |  | REG E-IL | 0 | 539692 | SEWARD 3 115.00 | 530679 | SEWRDMW3 115.00 | 0 |  | 1 | 16SP | 60 | 60 | 0 | 106.1 | 106.0862 | 97.5 | [7 empty] | CATEGORYB | SINGLE | HEIZER 6 230.00 - MULLERGREN 230KV CKT 1 | 0 | 530680 | HEIZER 6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T11455516SP | FROM->TO | SEWARD - SEWRDMW3 115KV CKT 1 | E | SUNC | MIDW |  | REG E-IL | 0 | 539692 | SEWARD 3 115.00 | 530679 | SEWRDMW3 115.00 | 0 |  | 1 | 16SP | 60 | 60 | 0 | 106 | 106.0204 | 97.4 | [7 empty] | CATEGORYB | SINGLE | HEIZER 6 230.00 (HEIZER T1) 230/115/12.5KV TRANSFORMER CKT 1 | 1 | 530601 | HEIZER 3 115.00 | 530680 | HEIZER 6 230.00 | 530626 | HZRT1 1 12.500 | 1 | [58 empty] | 2012-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T11455516SP | FROM->TO | SEWARD - SEWRDMW3 115KV CKT 1 | E | SUNC | MIDW |  | REG E-IL | 0 | 539692 | SEWARD 3 115.00 | 530679 | SEWRDMW3 115.00 | 0 |  | 1 | 16SP | 60 | 60 | 0 | 106 | 106.0204 | 97.4 | [7 empty] | CATEGORYB | SINGLE | HEIZER 6 230.00 (HEIZER T1) 230/115/12.5KV TRANSFORMER CKT 1 | 1 | 530601 | HEIZER 3 115.00 | 530680 | HEIZER 6 230.00 | 530626 | HZRT1 1 12.500 | 1 | [58 empty] | 2012-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T11455516SP | FROM->TO | SEWARD - SEWRDMW3 115KV CKT 1 | E | SUNC | MIDW |  | REG E-IL | 0 | 539692 | SEWARD 3 115.00 | 530679 | SEWRDMW3 115.00 | 0 |  | 1 | 16SP | 60 | 60 | 0 | 106 | 106.0204 | 97.4 | [7 empty] | CATEGORYB | SINGLE | HEIZER 6 230.00 (HEIZER T1) 230/115/12.5KV TRANSFORMER CKT 1 | 1 | 530601 | HEIZER 3 115.00 | 530680 | HEIZER 6 230.00 | 530626 | HZRT1 1 12.500 | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T25365521SP | FROM->TO | SOUTHWEST SHREVEPORT - SPRINGRIDGE PAN-HARR REC 138KV CKT 1 | E | AEPW | AEPW | SHREVEPO | SHRVNTEC | 0 | 507759 | SW SHV 4 138.00 | 507757 | SPRIDGE4 138.00 | 0 |  | 1 | 21SP | 131 | 151 | 0 |  | 87.575 | 98.2 | [7 empty] | CATEGORYB | NONSINGLE | SPP-AEPW-30 | 0 | 0 |  | 0 |  | 0
2009-AGP2 | AFS5 | INVALID |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1555521SP | FROM->TO | SOUTHWEST SHREVEPORT - SPRINGRIDGE PAN-HARR REC 138KV CKT 1 | E | AEPW | AEPW | SHREVEPO | SHRVNTEC | 0 | 507759 | SW SHV 4 138.00 | 507757 | SPRIDGE4 138.00 | 0 |  | 1 | 21SP | 131 | 151 | 0 |  | 85.815 | 96.4206 | [7 empty] | CATEGORYB | SINGLE | STONEWALL - WESTERN ELECTRIC T 138KV CKT 1 | 0 | 507768 | WESTELT4 138.00 | 509052 | STONWAL4 138.00 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T15510WP | TO->FROM | SOUTHWESTERN STATION - WASHITA 138KV CKT 1 | E | WFEC | AEPW | AEP-CS | WESTERN | 0 | 521089 | WASHITA4 138.00 | 511477 | S.W.S.-4 138.00 | 0 |  | 1 | 10WP | 196 | 260 | 0 |  | 71.1415 | 95.8 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T45511SP | TO->FROM | SOUTHWESTERN STATION - WASHITA 138KV CKT 1 | E | WFEC | AEPW | AEP-CS | WESTERN | 0 | 521089 | WASHITA4 138.00 | 511477 | S.W.S.-4 138.00 | 0 |  | 1 | 11SP | 196 | 260 | 0 |  | 67.7218 | 96.5 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T14695016SP | FROM->TO | SUB 1206 (S1206 T2) 161/69/13.8KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 1 | 646206 | S1206 5 161.00 | 647006 | S906 N 8 69.000 | 648306 | S1206T29 13.800 | 1 | 16SP | 201.6 | 201.6 | 201.6 | 98.6 | 98.5994 | 98.2 | [7 empty] | CATEGORYB | NONSINGLE | S1206T1 BSCL | 0 | 0 |  | 0 |  | 0
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T12815011SP | FROM->TO | SUB 1211 - SUB 1220 161KV CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 646211 | S1211 5 161.00 | 646220 | S1220 5 161.00 | 0 |  | 1 | 11SP | 262 | 262 | 262 | 98.4 | 53.5069 | 98.7 | [7 empty] | CATEGORYB | GENOUT | NC1_GEN-NEBRASKA CITY 1 | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2011-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T12755012SP | FROM->TO | SUB 1211 - SUB 1220 161KV CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 646211 | S1211 5 161.00 | 646220 | S1220 5 161.00 | 0 |  | 1 | 12SP | 262 | 262 | 262 | 99 | 54.1165 | 98.4 | [7 empty] | CATEGORYB | GENOUT | NC1_GEN-NEBRASKA CITY 1 | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2011-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T12785012SP | FROM->TO | SUB 1211 - SUB 1250 161KV CKT 2 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 646211 | S1211 5 161.00 | 646250 | S1250 5 161.00 | 0 |  | 2 | 12SP | 221 | 221 | 221 | 97.2 | 19.3272 | 98 | [7 empty] | CATEGORYB | GENOUT | NC2_GEN-NEBRASKA CITY 2 | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T14775016SP | FROM->TO | SUB 1211 - SUB 1250 161KV CKT 2 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 646211 | S1211 5 161.00 | 646250 | S1250 5 161.00 | 0 |  | 2 | 16SP | 221 | 221 | 221 | 97 | 18.5847 | 97.1 | [7 empty] | CATEGORYB | GENOUT | NC2_GEN-NEBRASKA CITY 2 | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2017-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T21715521SP | FROM->TO | SUB 906 SOUTH - SUB 924 69KV CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 647906 | S906 S 8 69.000 | 647924 | S924 8 69.000 | 0 |  | 1 | 21SP | 95 | 95 | 95 |  | 75.9579 | 99.4 | [7 empty] | CATEGORYB | SINGLE | SUB 1201 (S1201 T1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 646201 | S1201 5 161.00 | 647901 | S901 8 69.000 | 648201 | S1201T19 13.800 | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T6445521SP | FROM->TO | SUB 906 SOUTH - SUB 924 69KV CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 647906 | S906 S 8 69.000 | 647924 | S924 8 69.000 | 0 |  | 1 | 21SP | 95 | 95 | 95 |  | 89.973 | 96.7 | [7 empty] | CATEGORYB | SINGLE | SUB 901 - SUB 912 69KV CKT 1 | 0 | 647901 | S901 8 69.000 | 647912 | S912 8 69.000 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T6455521SP | FROM->TO | SUB 906 SOUTH - SUB 924 69KV CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 647906 | S906 S 8 69.000 | 647924 | S924 8 69.000 | 0 |  | 1 | 21SP | 95 | 95 | 95 |  | 82.234 | 95.9 | [7 empty] | CATEGORYB | SINGLE | SUB 910 - SUB 923 69KV CKT 1 | 0 | 647910 | S910 8 69.000 | 647923 | S923 8 69.000 | 0 |  | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T21725521SP | TO->FROM | SUB 912 - SUB 924 69KV CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 647924 | S924 8 69.000 | 647912 | S912 8 69.000 | 0 |  | 1 | 21SP | 72 | 72 | 112 |  | 66.3723 | 96.3 | [7 empty] | CATEGORYB | SINGLE | SUB 1201 (S1201 T1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 646201 | S1201 5 161.00 | 647901 | S901 8 69.000 | 648201 | S1201T19 13.800 | 1
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T10095511SP | FROM->TO | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | E | WFEC | WFEC | AEP-OP | AEP-OP | 2 | 521065 | TALOGA 4 138.00 | 521064 | TALOGA 2 69.000 | 521178 | TLGTERT 13.800 | 1 | 11SP | 56 | 56 | 56 |  | 62.4907 | 99.9 | [7 empty] | CATEGORYB | SINGLE | WOODWARD (WOODWRD2) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 514782 | WODWRD 2 69.000 | 514785 | WOODWRD4 138.00 | 515771 | WOODWR21 13.200 | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T10405511SP | FROM->TO | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | E | WFEC | WFEC | AEP-OP | AEP-OP | 2 | 521065 | TALOGA 4 138.00 | 521064 | TALOGA 2 69.000 | 521178 | TLGTERT 13.800 | 1 | 11SP | 56 | 56 | 56 |  | 63.1197 | 98.7 | [7 empty] | CATEGORYB | SINGLE | OKEENE (OKEENE) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 521015 | OKEENE 2 69.000 | 521016 | OKEENE 4 138.00 | 521173 | OKENTERT 13.800 | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T9875511SP | FROM->TO | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | E | WFEC | WFEC | AEP-OP | AEP-OP | 1 | 521065 | TALOGA 4 138.00 | 521064 | TALOGA 2 69.000 | 521178 | TLGTERT 13.800 | 1 | 11SP | 56 | 56 | 56 |  | 61.4906 | 98.1 | [7 empty] | CATEGORYB | SINGLE | ELK CITY (ELKCTY-4) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 511458 | ELKCTY-4 138.00 | 511459 | ELKCTY-2 69.000 | 511493 | ELKC4-1 13.800 | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T11285512SP | FROM->TO | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | E | WFEC | WFEC | AEP-OP | AEP-OP | 1 | 521065 | TALOGA 4 138.00 | 521064 | TALOGA 2 69.000 | 521178 | TLGTERT 13.800 | 1 | 12SP | 56 | 56 | 56 |  | 66.4848 | 99.1 | [7 empty] | CATEGORYB | SINGLE | OKEENE (OKEENE) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 521015 | OKEENE 2 69.000 | 521016 | OKEENE 4 138.00 | 521173 | OKENTERT 13.800 | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T2375512SP | FROM->TO | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | E | WFEC | WFEC | AEP-OP | AEP-OP | 2 | 521065 | TALOGA 4 138.00 | 521064 | TALOGA 2 69.000 | 521178 | TLGTERT 13.800 | 1 | 12SP | 56 | 56 | 56 |  | 62.136 | 95.8 | [7 empty] | CATEGORYB | SINGLE | TALOGA - VICI 69KV CKT 1 | 0 | 521064 | TALOGA 2 69.000 | 521082 | VICI 2 69.000 | 0 |  | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T4465512WP | FROM->TO | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | E | WFEC | WFEC | AEP-OP | AEP-OP | 2 | 521065 | TALOGA 4 138.00 | 521064 | TALOGA 2 69.000 | 521178 | TLGTERT 13.800 | 1 | 12WP | 56 | 56 | 56 |  | -999 | 99.2 | [7 empty] | CATEGORYB | SINGLE | ELK CITY (ELKCTY-4) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 511458 | ELKCTY-4 138.00 | 511459 | ELKCTY-2 69.000 | 511493 | ELKC4-1 13.800 | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T4535512WP | FROM->TO | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | E | WFEC | WFEC | AEP-OP | AEP-OP | 2 | 521065 | TALOGA 4 138.00 | 521064 | TALOGA 2 69.000 | 521178 | TLGTERT 13.800 | 1 | 12WP | 56 | 56 | 56 |  | 56.7722 | 95.2 | [7 empty] | CATEGORYB | SINGLE | WOODWARD (WOODWRD2) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 514782 | WODWRD 2 69.000 | 514785 | WOODWRD4 138.00 | 515771 | WOODWR21 13.200 | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T2355516SP | FROM->TO | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | E | WFEC | WFEC | AEP-OP | AEP-OP | 1 | 521065 | TALOGA 4 138.00 | 521064 | TALOGA 2 69.000 | 521178 | TLGTERT 13.800 | 1 | 16SP | 56 | 56 | 56 |  | 57.7471 | 97.4 | [7 empty] | CATEGORYB | SINGLE | ROMAN NOSE - SOUTHARD 138KV CKT 1 | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T2455516SP | FROM->TO | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | E | WFEC | WFEC | AEP-OP | AEP-OP | 1 | 521065 | TALOGA 4 138.00 | 521064 | TALOGA 2 69.000 | 521178 | TLGTERT 13.800 | 1 | 16SP | 56 | 56 | 56 |  | 64.1196 | 96.9 | [7 empty] | CATEGORYB | SINGLE | CEDARDALE - MOORELAND 138KV CKT 1 | 0 | 520848 | CEDRDAL4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T2485516SP | FROM->TO | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | E | WFEC | WFEC | AEP-OP | AEP-OP | 1 | 521065 | TALOGA 4 138.00 | 521064 | TALOGA 2 69.000 | 521178 | TLGTERT 13.800 | 1 | 16SP | 56 | 56 | 56 |  | 63.3584 | 96 | [7 empty] | CATEGORYB | SINGLE | CEDARDALE - OKEENE 138KV CKT 1 | 0 | 520848 | CEDRDAL4 138.00 | 521016 | OKEENE 4 138.00 | 0 |  | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1185516WP | FROM->TO | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | E | WFEC | WFEC | AEP-OP | AEP-OP | 1 | 521065 | TALOGA 4 138.00 | 521064 | TALOGA 2 69.000 | 521178 | TLGTERT 13.800 | 1 | 16WP | 56 | 56 | 56 |  | 61.1536 | 99.7 | [7 empty] | CATEGORYB | SINGLE | DEWEY - SOUTHARD 138KV CKT 1 | 0 | 514787 | DEWEY 4 138.00 | 514822 | SOUTHRD4 138.00 | 0 |  | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T1195516WP | FROM->TO | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | E | WFEC | WFEC | AEP-OP | AEP-OP | 2 | 521065 | TALOGA 4 138.00 | 521064 | TALOGA 2 69.000 | 521178 | TLGTERT 13.800 | 1 | 16WP | 56 | 56 | 56 |  | 56.9262 | 95.7 | [7 empty] | CATEGORYB | SINGLE | ROMAN NOSE - SOUTHARD 138KV CKT 1 | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | [58 empty] | 2010-10-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T495512WP | TO->FROM | TEXAS EASTMAN - WHITNEY 138KV CKT 1 | E | AEPW | AEPW | LONG-MAR | LONG-MAR | 0 | 508575 | WHITNEY4 138.00 | 508582 | EASTEX 4 138.00 | 0 |  | 1 | 12WP | 277 | 307 | 0 | 97 | 96.9521 | 96.9 | [7 empty] | CATEGORYB | SINGLE | EASTON REC - PIRKEY 138KV CKT 1 | 0 | 508562 | PIRKEY 4 138.00 | 509092 | EASTON 4 138.00 | 0 |  | 1 | [58 empty] | 2013-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T485512WP | TO->FROM | TEXAS EASTMAN - WHITNEY 138KV CKT 1 | E | AEPW | AEPW | LONG-MAR | LONG-MAR | 0 | 508575 | WHITNEY4 138.00 | 508582 | EASTEX 4 138.00 | 0 |  | 1 | 12WP | 277 | 307 | 0 | 95.8 | 95.7541 | 95.7 | [7 empty] | CATEGORYB | SINGLE | EASTON REC - KNOX LEE 138KV CKT 1 | 0 | 508548 | KNOXLEE4 138.00 | 509092 | EASTON 4 138.00 | 0 |  | 1 | [58 empty] | 2013-06-01
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T13085011SP | TO->FROM | TIMBER JUNCTION - UDALL 69KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533559 | UDALL 2 69.000 | 533558 | TIMBJCT2 69.000 | 0 |  | 1 | 11SP | 43 | 43 | 0 |  | 65.8974 | 95.1 | [7 empty] | CATEGORYB | NONSINGLE | WRTOD1104 | 0 | 0 |  | 0 |  | 0
2009-AGP2 | AFS5 |  |  |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T16105516SP | TO->FROM | TIMBER JUNCTION - UDALL 69KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533559 | UDALL 2 69.000 | 533558 | TIMBJCT2 69.000 | 0 |  | 1 | 16SP | 43 | 43 | 0 |  | 76.0184 | 97.9 | [7 empty] | CATEGORYB | NONSINGLE | WRTOD1104 | 0 | 0 |  | 0 |  | 0
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T13645011SP | FROM->TO | TRUMANN - TRUMANN WEST AECC 161KV CKT 1 | E | EES | EES | EAINTH |  | 0 | 338169 | 5TRUMAN 161.00 | 338707 | 5TRUM-W# 161.00 | 0 |  | 1 | 11SP | 148 | 148 | 0 | 97 | 97.0265 | 95.8 | [7 empty] | CATEGORYB | NONSINGLE | HERGETT TO N | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T6305011SP | FROM->TO | TRUMANN - TRUMANN WEST AECC 161KV CKT 1 | E | EES | EES | EAINTH |  | 0 | 338169 | 5TRUMAN 161.00 | 338707 | 5TRUM-W# 161.00 | 0 |  | 1 | 11SP | 148 | 148 | 0 | 96.9 | 96.8822 | 95.5 | [7 empty] | CATEGORYB | SINGLE | NEWPORT - NEWPORT INDUSTRIAL 161KV CKT 1 | 0 | 338151 | 5NEWPO 161.00 | 338173 | 5NEW-IN 161.00 | 0 |  | 1 | [58 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T6595012SP | FROM->TO | TRUMANN - TRUMANN WEST AECC 161KV CKT 1 | E | EES | EES | EAINTH |  | 0 | 338169 | 5TRUMAN 161.00 | 338707 | 5TRUM-W# 161.00 | 0 |  | 1 | 12SP | 148 | 148 | 0 | 100.9 | 100.8536 | 99.8 | [7 empty] | CATEGORYB | SINGLE | NEWPORT - NEWPORT INDUSTRIAL 161KV CKT 1 | 0 | 338151 | 5NEWPO 161.00 | 338173 | 5NEW-IN 161.00 | 0 |  | 1 | [58 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T6785012SP | FROM->TO | TRUMANN - TRUMANN WEST AECC 161KV CKT 1 | E | EES | EES | EAINTH |  | 0 | 338169 | 5TRUMAN 161.00 | 338707 | 5TRUM-W# 161.00 | 0 |  | 1 | 12SP | 148 | 148 | 0 | 99 | 99.0475 | 98 | [7 empty] | CATEGORYB | SINGLE | NEWPORT AB - NEWPORT INDUSTRIAL 161KV CKT 1 | 0 | 338172 | 5NEW-AB 161.00 | 338173 | 5NEW-IN 161.00 | 0 |  | 1 | [58 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T6735012SP | FROM->TO | TRUMANN - TRUMANN WEST AECC 161KV CKT 1 | E | EES | EES | EAINTH |  | 0 | 338169 | 5TRUMAN 161.00 | 338707 | 5TRUM-W# 161.00 | 0 |  | 1 | 12SP | 148 | 148 | 0 | 96.6 | 96.6253 | 95.6 | [7 empty] | CATEGORYB | SINGLE | CASH - NEWPORT AB 161KV CKT 1 | 0 | 338171 | 5CASH 161.00 | 338172 | 5NEW-AB 161.00 | 0 |  | 1 | [58 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T4085016WP | FROM->TO | TRUMANN - TRUMANN WEST AECC 161KV CKT 1 | E | EES | EES | EAINTH |  | 0 | 338169 | 5TRUMAN 161.00 | 338707 | 5TRUM-W# 161.00 | 0 |  | 1 | 16WP | 148 | 148 | 0 | 99.4 | 99.3785 | 98.4 | [7 empty] | CATEGORYB | SINGLE | NEWPORT - NEWPORT INDUSTRIAL 161KV CKT 1 | 0 | 338151 | 5NEWPO 161.00 | 338173 | 5NEW-IN 161.00 | 0 |  | 1 | [58 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T11295516WP | FROM->TO | TRUMANN - TRUMANN WEST AECC 161KV CKT 1 | E | EES | EES | EAINTH |  | 0 | 338169 | 5TRUMAN 161.00 | 338707 | 5TRUM-W# 161.00 | 0 |  | 1 | 16WP | 148 | 148 | 0 | 99.2 | 99.1547 | 98 | [7 empty] | CATEGORYB | NONSINGLE | HERGETT TO N | 0 | 0 |  | 0 |  | 0 | [60 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 0 | 2009AGP2AFS51T4255016WP | FROM->TO | TRUMANN - TRUMANN WEST AECC 161KV CKT 1 | E | EES | EES | EAINTH |  | 0 | 338169 | 5TRUMAN 161.00 | 338707 | 5TRUM-W# 161.00 | 0 |  | 1 | 16WP | 148 | 148 | 0 | 97.7 | 97.6601 | 96.7 | [7 empty] | CATEGORYB | SINGLE | NEWPORT AB - NEWPORT INDUSTRIAL 161KV CKT 1 | 0 | 338172 | 5NEW-AB 161.00 | 338173 | 5NEW-IN 161.00 | 0 |  | 1 | [58 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T15785521SP | FROM->TO | TRUMANN - TRUMANN WEST AECC 161KV CKT 1 | E | EES | EES | EAINTH |  | 0 | 338169 | 5TRUMAN 161.00 | 338707 | 5TRUM-W# 161.00 | 0 |  | 1 | 21SP | 148 | 148 | 0 | 98.2 | 98.23 | 97.6 | [7 empty] | CATEGORYB | SINGLE | DELL 161 - MANILLA AECC 161KV CKT 1 | 0 | 338185 | 5DELL 161.00 | 338806 | 5MNILA# 161.00 | 0 |  | 1 | [58 empty] | 2017-06-01
2009-AGP2 | AFS5 |  | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T15815521SP | FROM->TO | TRUMANN - TRUMANN WEST AECC 161KV CKT 1 | E | EES | EES | EAINTH |  | 0 | 338169 | 5TRUMAN 161.00 | 338707 | 5TRUM-W# 161.00 | 0 |  | 1 | 21SP | 148 | 148 | 0 | 97.7 | 97.7308 | 97.1 | [7 empty] | CATEGORYB | SINGLE | MANILLA AECC - MONETTE JUNCTION 161KV CKT 1 | 0 | 338186 | 5MONETE 161.00 | 338806 | 5MNILA# 161.00 | 0 |  | 1 | [58 empty] | 2017-06-01
2009-AGP2 | AFS5 | INVALID | FDNS |  | FDNS |  | 5 | 5 | 2009AGP2AFS51T6695510WP | FROM->TO | WELLS 500/230KV TRANSFORMER CKT 1 | E | EES | CELE |  | CLE_CENTRAL | 0 | 335368 | 8WELLS 500.00 | 500950 | WELSRCT6 230.00 | 0 |  | 1 | 10WP | 594 | 653 | 0 | 97.6 | 97.591 | 97.6669 | [7 empty] | CATEGORYB | SINGLE | RICHARD - WELLS 500KV CKT 1 | 0 | 335367 | 8RICHARD 500.00 | 335368 | 8WELLS 500.00 | 0 |  | 1 | [58 empty] | 2010-10-01