## tblAllFacilityLog
STUDYDES | STUDYDES2 | EVENTTYPE | AssessmentSOLUTIONTYPE | AssessmenFDNS-TERMINATION | SOLUTIONTYPE | FDNS-TERMINATION | GROUP | SCENARIO | FGName | DIRECTION | FacilityName | FacilityUpgradeCode | ModelArea1 | ModelArea2 | FZONENAME | TZONENAME | MONTFLAG | MONTFB | MONTFNAME | MONTTB1 | MONTTNAME1 | MONTTB2 | MONTTNAME2 | MONTCKT | Case | RATEA | RATEB | RATEC | Assessment Loading | BaseCaseLoading | TransferCaseLoading | NameOfBusWithMonitoredVoltage | Assessment Voltage | BaseCaseVoltage | TransferCaseVoltage | VINIT | VMIN | VMAX | CATEGORY | CONTTYPE | CONTNAME | CONTXFMRFLAG | CONTFB | CONTFNAME | CONTTB1 | CONTTNAME1 | CONTTB2 | CONTTNAME2 | CONTCKT | TransmissionProviderCommentsNotes | RequiredRateB | TransmissionOwnerComments | OwnerDesignation | UpgradeName | UpgradeComponentWithinFacility | NewSummerA | NewSummerB | NewOtherA | NewOtherB | DistToConstruct | TotalLead | ConstructionLeadOnly | NewOrConstructWhileEnergized | NewR | NewX | NewB | CommentsRegardingUpgradeRequirements | NewCost | EffDate | NetPlantDate | ReusableEx_GrossValue | ReusableEx_NetValue | Reusable_EndofDepr | SalvageValue | NewCostWhileExpediting | EffDateExpedited | StartDeprExpedited | EndDeprExpedited | NetPlantDateExpedited | ReusableEx_GrossExpedited | ReusableEx_NetExpedited | Reusable_EndofDeprExpedited | SalvageValueExpedited | Generation 1 Owner & Unit (Name) | Generation 1 Redispatch Cost ($) | Generation 1 Redispatch Date (M/D/Y) | Generation 2 Owner & Unit (Name) | Generation 2 Redispatch Cost ($) | Generation 2 Redispatch Date (M/D/Y) | Generation 3 Owner & Unit (Name) | Generation 3 Redispatch Cost ($) | Generation 3 Redispatch Date (M/D/Y) | ActualCompletion | ActualNewCost | ActualNetPlantDate | ActualReusableEx_GrossValue | ActualReusableEx_NetValue | ActualReusable_EndofDepr | ActualSalvageValue | Actual_NewCostWhileExpediting | Actual_StartDeprExp | Actual_EndDeprExp | Actual_NetPlantDateExpedited | ActualReusableEx_GrossExpedited | ActualReusableEx_NetExpedited | ActualReusable_EndofDeprExpedited | Actual_SalvageValueExpedited | SPPReliabilityDate | DUN | EOC | EarliestDate
GEN | [10 empty] | ALBION - PETERSBURG 115KV CKT 1 | U | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640318 | PETRSBG7 115.00 | 640054 | ALBION 7 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | NPPD | ALBION - PETERSBURG 115KV CKT 1 | Replace Breaker Switch 1106-D and jumpers at Albion. Replace main bus at Petersburg. Upgrade and replace transmission structures on 115 kV lineto facilitate 100 degrees Centigrade line operation. | [53 empty] | 2013-01-01 | 2013-01-01
2007-AG3 | [10 empty] | ALEXANDER - PRATT 115KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | MKEC | ALEXANDER - PRATT 115KV CKT 1 | Rebuild line | [53 empty] | 2009-12-01 | 2014-01-01
2007-AG3 | [10 empty] | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | MKEC | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | Rebuild line | [53 empty] | 2009-12-01 | 2014-01-01
2009-AGP1 | [10 empty] | ALTUS SW - NAVAJO 69KV CKT 1 | U | WFEC | WFEC | AEP-KP | AEP-KP | 0 | 521009 | NAVAJO 2 69.000 | 520805 | ALTUSSW2 69.000 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | WFEC | ALTUS SW - NAVAJO 69KV CKT 1 | Upgrade Terminal Equipment at Altus SW, 300-600A, new rating conductor 53/65MVA | [53 empty] | 2013-06-01 | 2013-06-01
2006-AG1 | [10 empty] | ALUMAX TAP - BANN 138KV CKT 1 | U | AEPW | AEPW |  |  | 0 | 508049 | ALUMXT 4 138 | 508054 | BANN 4 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | AEPW | ALUMAX TAP - BANN 138KV CKT 1 | Replace six (6) 138 kV switches, five at Bann & one at Alumax Tap. Rebuild 0.67 miles of 1024 ACAR with 2156 ACSR. Replace wavetrap & jumpers @ Bann. Replace breaker 3300 @ Bann. | [53 empty] | 2008-06-01 | 2008-06-01
GEN-2006-010 | [10 empty] | ASHDOWN REC (MILLWOOD) - OKAY 138KV CKT 1 | U | AEPW | AEPW | SARK | SARKAECC | 0 | 507428 | OKAY 4 138.00 | 507402 | ASHDWNR4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | AEPW | ASHDOWN REC (MILLWOOD) - OKAY 138KV CKT 1 | Recunductor and convert line to 138 kV and replace switches at Ashdown REC | [53 empty] | 2012-07-01 | 2012-07-01
GEN-2006-010 | [10 empty] | ASHDOWN REC (MILLWOOD) - PATTERSON 138KV CKT 1 | U | AEPW | AEPW | SARKAECC | SARK | 0 | 507402 | ASHDWNR4 138.00 | 507431 | PATTERS4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | AEPW | ASHDOWN REC (MILLWOOD) - PATTERSON 138KV CKT 1 | Reconductor Line & Convert Line to 138 kV and convert Patterson station to breaker-and-a half cofiguration | [53 empty] | 2012-07-01 | 2012-07-01
2011-AG2 | AFS9 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3375513SP | TO->FROM | AUBURN ROAD - JEFFREY ENERGY CENTER 230KV CKT 1 | PL | WERE | WERE | NEAST | NEAST | 0 | 532852 | JEC 6 230.00 | 532851 | AUBURN 6 230.00 | 0 |  | 1 | 13SP | 565 | 565 | 0 | 104.8 | 104.7887 | 106.4613 | [7 empty] | CATEGORYB | SINGLE | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  | WERE | GOODYEAR JUNCTION - MCVICAR3 115kV | Build 3.25 miles of 115kV from Goodyear to MacVicar. 223 MVA Rate A. 245 MVA Rate B. | [53 empty] | 2013-06-01 | 2013-12-01
2011-AG2 | AFS9 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3375513SP | TO->FROM | AUBURN ROAD - JEFFREY ENERGY CENTER 230KV CKT 1 | PL | WERE | WERE | NEAST | NEAST | 0 | 532852 | JEC 6 230.00 | 532851 | AUBURN 6 230.00 | 0 |  | 1 | 13SP | 565 | 565 | 0 | 104.8 | 104.7887 | 106.4613 | [7 empty] | CATEGORYB | SINGLE | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  | WERE | MCVICAR3 - 17TH & FAIRLAWN 115kV | Build 3.6 miles of 115kV from MacVicar to 17th & Fairlawn. 223 MVA Rate A. 245 MVA Rate B. | [53 empty] | 2013-06-01 | 2014-12-01
2011-AG2 | AFS9 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2555517SP | TO->FROM | AUBURN ROAD - JEFFREY ENERGY CENTER 230KV CKT 1 | PL | WERE | WERE | NEAST | NEAST | 0 | 532852 | JEC 6 230.00 | 532851 | AUBURN 6 230.00 | 0 |  | 1 | 17SP | 565 | 565 | 0 | 103.7 | 103.6711 | 109.5377 | [7 empty] | CATEGORYB | SINGLE | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  | WERE | GOODYEAR JUNCTION - MCVICAR3 115kV | Build 3.25 miles of 115kV from Goodyear to MacVicar. 223 MVA Rate A. 245 MVA Rate B. | [53 empty] | 2013-06-01 | 2013-12-01
2011-AG2 | AFS9 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2555517SP | TO->FROM | AUBURN ROAD - JEFFREY ENERGY CENTER 230KV CKT 1 | PL | WERE | WERE | NEAST | NEAST | 0 | 532852 | JEC 6 230.00 | 532851 | AUBURN 6 230.00 | 0 |  | 1 | 17SP | 565 | 565 | 0 | 103.7 | 103.6711 | 109.5377 | [7 empty] | CATEGORYB | SINGLE | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  | WERE | MCVICAR3 - 17TH & FAIRLAWN 115kV | Build 3.6 miles of 115kV from MacVicar to 17th & Fairlawn. 223 MVA Rate A. 245 MVA Rate B. | [53 empty] | 2013-06-01 | 2014-12-01
2011-AG2 | AFS9 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3715522SP | TO->FROM | AUBURN ROAD - JEFFREY ENERGY CENTER 230KV CKT 1 | PL | WERE | WERE | NEAST | NEAST | 0 | 532852 | JEC 6 230.00 | 532851 | AUBURN 6 230.00 | 0 |  | 1 | 22SP | 565 | 565 | 0 | 102.6401 | 102.6401 | 108.3648 | [7 empty] | CATEGORYB | SINGLE | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  | WERE | GOODYEAR JUNCTION - MCVICAR3 115kV | Build 3.25 miles of 115kV from Goodyear to MacVicar. 223 MVA Rate A. 245 MVA Rate B. | [53 empty] | 2013-06-01 | 2013-12-01
2011-AG2 | AFS9 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3715522SP | TO->FROM | AUBURN ROAD - JEFFREY ENERGY CENTER 230KV CKT 1 | PL | WERE | WERE | NEAST | NEAST | 0 | 532852 | JEC 6 230.00 | 532851 | AUBURN 6 230.00 | 0 |  | 1 | 22SP | 565 | 565 | 0 | 102.6401 | 102.6401 | 108.3648 | [7 empty] | CATEGORYB | SINGLE | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  | WERE | MCVICAR3 - 17TH & FAIRLAWN 115kV | Build 3.6 miles of 115kV from MacVicar to 17th & Fairlawn. 223 MVA Rate A. 245 MVA Rate B. | [53 empty] | 2013-06-01 | 2014-12-01
GEN-2006-010 | [10 empty] | BANN - RED SPRINGS REC 138KV CKT 1 | U | AEPW | AEPW | TEXARK | TXARNTEC | 0 | 508054 | BANN 4 138.00 | 508075 | REDSPRG4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | AEPW | BANN - RED SPRINGS REC 138KV CKT 1 | Replace 138 kV breakers 3300 & 3310 | [53 empty] | 2012-07-01 | 2012-07-01
2011-AG2 | AFS9 | SPP_FG-5218 - BEAEURMONBRK | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4185513SP | FROM->TO | BEAVER - EUREKA SPRINGS 161KV CKT 1 | S | SWPA | AEPW | EMINTH | FAYETTEVILLE | 0 | 505480 | BEAVER 5 161.00 | 506932 | EUREKA 5 161.00 | 0 |  | 1 | 13SP | 236 | 247 | 0 | 97.8 | 97.766 | 103.6209 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE - SUB 383 - MONETT 345KV CKT 1 | 0 | 547481 | MON383 7 345.00 | 549984 | BROOKLINE 7345.00 | 0 |  | 1 |  |  |  | AEPW | BEAVER - EUREKA SPRINGS 161KV CKT 1 AEPW | Rebuild 1.25 miles of 795 ACSR with 1590 ACSR. Replace wavetrap & jumpers @ Eureka Springs | 318 | 438 | 422 | 502 | 1.25 | 18 | 6 |  | 0.00032 | 0.003398 | 0.00196 | Ratings are for AEP equipment only. New limit is the switch @ Eureka Springs. | 2635665.74 | 2012-06-19 | [39 empty] | 2013-06-01 | 2016-06-01
2011-AG2 | STUDYDES2 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T15045513SP | FROM->TO | BEAVER - EUREKA SPRINGS 161KV CKT 1 | S | SWPA | AEPW | EMINTH | FAYETTEVILLE | 0 | 505480 | BEAVER 5 161.00 | 506932 | EUREKA 5 161.00 | 0 |  | 1 | 13SP | 236 | 247 | 0 | 97.7503 | 97.7503 | 103.6049 | [7 empty] | CATEGORYB | NONSINGLE | AI12 | 0 | 0 |  | 0 |  | 0 | [5 empty] | AEPW | BEAVER - EUREKA SPRINGS 161KV CKT 1 AEPW | Rebuild 1.25 miles of 795 ACSR with 1590 ACSR. Replace wavetrap & jumpers @ Eureka Springs | 318 | 438 | 422 | 502 | 1.25 | 18 | 6 |  | 0.00032 | 0.003398 | 0.00196 | Ratings are for AEP equipment only. New limit is the switch @ Eureka Springs. | 2635665.74 | 2012-06-19 | [39 empty] | 2013-06-01 | 2016-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4605513SP | FROM->TO | BEAVER - EUREKA SPRINGS 161KV CKT 1 | S | SWPA | AEPW | EMINTH | FAYETTEVILLE | 0 | 505480 | BEAVER 5 161.00 | 506932 | EUREKA 5 161.00 | 0 |  | 1 | 13SP | 236 | 247 | 0 | 97.4 | 97.3589 | 103.5715 | [7 empty] | CATEGORYB | SINGLE | 7JASPER 345.00 - BLACKBERRY 345KV CKT 1 | 0 | 300739 | 7BLACKBERRY 345.00 | 300949 | 7JASPER 345.00 | 0 |  | 1 |  |  |  | AEPW | BEAVER - EUREKA SPRINGS 161KV CKT 1 AEPW | Rebuild 1.25 miles of 795 ACSR with 1590 ACSR. Replace wavetrap & jumpers @ Eureka Springs | 318 | 438 | 422 | 502 | 1.25 | 18 | 6 |  | 0.00032 | 0.003398 | 0.00196 | Ratings are for AEP equipment only. New limit is the switch @ Eureka Springs. | 2635665.74 | 2012-06-19 | [39 empty] | 2013-06-01 | 2016-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T775513SP | FROM->TO | BEAVER - EUREKA SPRINGS 161KV CKT 1 | S | SWPA | AEPW | EMINTH | FAYETTEVILLE | 0 | 505480 | BEAVER 5 161.00 | 506932 | EUREKA 5 161.00 | 0 |  | 1 | 13SP | 236 | 247 | 0 | 97.6944 | 97.6944 | 103.5458 | [7 empty] | CATEGORYB | SINGLE | FLINT CREEK - SUB 383 - MONETT 345KV CKT 1 | 0 | 506935 | FLINTCR7 345.00 | 547481 | MON383 7 345.00 | 0 |  | 1 |  |  |  | AEPW | BEAVER - EUREKA SPRINGS 161KV CKT 1 AEPW | Rebuild 1.25 miles of 795 ACSR with 1590 ACSR. Replace wavetrap & jumpers @ Eureka Springs | 318 | 438 | 422 | 502 | 1.25 | 18 | 6 |  | 0.00032 | 0.003398 | 0.00196 | Ratings are for AEP equipment only. New limit is the switch @ Eureka Springs. | 2635665.74 | 2012-06-19 | [39 empty] | 2013-06-01 | 2016-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1315522SP | FROM->TO | BEAVER - EUREKA SPRINGS 161KV CKT 1 | S | SWPA | AEPW | EMINTH | FAYETTEVILLE | 0 | 505480 | BEAVER 5 161.00 | 506932 | EUREKA 5 161.00 | 0 |  | 1 | 22SP | 236 | 247 | 0 | 93.4264 | 93.4264 | 103.7409 | [7 empty] | CATEGORYB | SINGLE | EROGERS7 345.00 - OSBOURNE 345KV CKT 1 | 0 | 506979 | SHIPERD7 345.00 | 506982 | EROGERS7 345.00 | 0 |  | 1 |  |  |  | AEPW | BEAVER - EUREKA SPRINGS 161KV CKT 1 AEPW | Rebuild 1.25 miles of 795 ACSR with 1590 ACSR. Replace wavetrap & jumpers @ Eureka Springs | 318 | 438 | 422 | 502 | 1.25 | 18 | 6 |  | 0.00032 | 0.003398 | 0.00196 | Ratings are for AEP equipment only. New limit is the switch @ Eureka Springs. | 2635665.74 | 2012-06-19 | [39 empty] | 2013-06-01 | 2016-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T20015522SP | FROM->TO | BEAVER - EUREKA SPRINGS 161KV CKT 1 | S | SWPA | AEPW | EMINTH | FAYETTEVILLE | 0 | 505480 | BEAVER 5 161.00 | 506932 | EUREKA 5 161.00 | 0 |  | 1 | 22SP | 236 | 247 | 0 | 92.8987 | 92.8987 | 103.2871 | [7 empty] | CATEGORYB | SINGLE | EROGERS7 345.00 - OSAGE CREEK 345KV CKT 1 | 0 | 506982 | EROGERS7 345.00 | 338683 | 7OSAGECK 345.00 | 0 |  | 1 |  |  |  | AEPW | BEAVER - EUREKA SPRINGS 161KV CKT 1 AEPW | Rebuild 1.25 miles of 795 ACSR with 1590 ACSR. Replace wavetrap & jumpers @ Eureka Springs | 318 | 438 | 422 | 502 | 1.25 | 18 | 6 |  | 0.00032 | 0.003398 | 0.00196 | Ratings are for AEP equipment only. New limit is the switch @ Eureka Springs. | 2635665.74 | 2012-06-19 | [39 empty] | 2013-06-01 | 2016-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T16025522SP | FROM->TO | BEAVER - EUREKA SPRINGS 161KV CKT 1 | S | SWPA | AEPW | EMINTH | FAYETTEVILLE | 0 | 505480 | BEAVER 5 161.00 | 506932 | EUREKA 5 161.00 | 0 |  | 1 | 22SP | 236 | 247 | 0 | 92.8493 | 92.8493 | 103.2761 | [7 empty] | CATEGORYB | SINGLE | OSAGE CREEK 345/161KV TRANSFORMER CKT 2 | 0 | 338682 | 5OSAGE # 161.00 | 338683 | 7OSAGECK 345.00 | 0 |  | 2 |  |  |  | AEPW | BEAVER - EUREKA SPRINGS 161KV CKT 1 AEPW | Rebuild 1.25 miles of 795 ACSR with 1590 ACSR. Replace wavetrap & jumpers @ Eureka Springs | 318 | 438 | 422 | 502 | 1.25 | 18 | 6 |  | 0.00032 | 0.003398 | 0.00196 | Ratings are for AEP equipment only. New limit is the switch @ Eureka Springs. | 2635665.74 | 2012-06-19 | [39 empty] | 2013-06-01 | 2016-06-01
2005-AG2 | [10 empty] | BEELINE - EXPLORER GLENPOOL 138KV CKT 1 | U | OKGE | OKGE |  |  | 0 | 515248 | EXPLGLN4 138 | 515247 | BEELINE4 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | OKGE | BEELINE - EXPLORER GLENPOOL 138KV CKT 1 | Reconductor .92miles of line with Drake ACCC/TW. | [53 empty] | 2009-06-01 | 2009-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4065514SP | FROM->TO | BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 | REL | GMO | GMO |  |  | 0 | 541211 | BLSPS 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 | 17SP | 224 | 224 | 224 |  | 94.5986 | 103.4388 | [7 empty] | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEYPL 161.00 161KV CKT 1 | 0 | 541235 | DUNCAN 5 161.00 | 541250 | SIBLEYPL 161.00 | 0 |  | 1 |  |  |  | MIPU | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #1 | Upgrade Prairie Lee wavetrap to at least 1200 A. | 233 | 259 |  |  |  | 18 | 6 | [5 empty] | 20537 | 2012-10-01 | [39 empty] | 2014-06-01 | 2015-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4065514SP | FROM->TO | BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 | S | GMO | GMO |  |  | 0 | 541211 | BLSPS 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 | 17SP | 224 | 224 | 224 |  | 94.5986 | 103.4388 | [7 empty] | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEYPL 161.00 161KV CKT 1 | 0 | 541235 | DUNCAN 5 161.00 | 541250 | SIBLEYPL 161.00 | 0 |  | 1 |  |  |  | MIPU | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #2 Accelerate | Reconductor 3.21 miles from Blue Springs South to Prairie Lee 161 kV to 954 ACSS. Upgrade substation equipment to 2000 Amps. | 558 | 558 |  |  |  | 24 | 24 | [5 empty] | 2983951.993 | 2011-11-09 | [38 empty] | 2018-06-01 | 2014-06-01 | 2016-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4065514SP | FROM->TO | BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 | S | GMO | GMO |  |  | 0 | 541211 | BLSPS 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 | 17SP | 224 | 224 | 224 |  | 94.5986 | 103.4388 | [7 empty] | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEYPL 161.00 161KV CKT 1 | 0 | 541235 | DUNCAN 5 161.00 | 541250 | SIBLEYPL 161.00 | 0 |  | 1 |  |  |  | MIPU | BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #1 Accelerate | Upgrade wave trap. | 228 | 259 |  |  |  | 18 | 6 | [5 empty] | 19775 | 2012-09-13 | [38 empty] | 2018-06-01 | 2014-06-01 | 2015-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3985514SP | FROM->TO | BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 | REL | GMO | GMO |  |  | 0 | 541211 | BLSPS 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 | 17SP | 224 | 224 | 224 |  | 88.5584 | 102.8899 | [7 empty] | CATEGORYB | SINGLE | PLEASANT HILL - SIBLEY 345KV CKT 1 | 0 | 541200 | PHILL 7 345.00 | 541201 | SIBLEY 7 345.00 | 0 |  | 1 |  |  |  | MIPU | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #1 | Upgrade Prairie Lee wavetrap to at least 1200 A. | 233 | 259 |  |  |  | 18 | 6 | [5 empty] | 20537 | 2012-10-01 | [39 empty] | 2014-06-01 | 2015-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3985514SP | FROM->TO | BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 | S | GMO | GMO |  |  | 0 | 541211 | BLSPS 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 | 17SP | 224 | 224 | 224 |  | 88.5584 | 102.8899 | [7 empty] | CATEGORYB | SINGLE | PLEASANT HILL - SIBLEY 345KV CKT 1 | 0 | 541200 | PHILL 7 345.00 | 541201 | SIBLEY 7 345.00 | 0 |  | 1 |  |  |  | MIPU | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #2 Accelerate | Reconductor 3.21 miles from Blue Springs South to Prairie Lee 161 kV to 954 ACSS. Upgrade substation equipment to 2000 Amps. | 558 | 558 |  |  |  | 24 | 24 | [5 empty] | 2983951.993 | 2011-11-09 | [38 empty] | 2018-06-01 | 2014-06-01 | 2016-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3985514SP | FROM->TO | BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 | S | GMO | GMO |  |  | 0 | 541211 | BLSPS 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 | 17SP | 224 | 224 | 224 |  | 88.5584 | 102.8899 | [7 empty] | CATEGORYB | SINGLE | PLEASANT HILL - SIBLEY 345KV CKT 1 | 0 | 541200 | PHILL 7 345.00 | 541201 | SIBLEY 7 345.00 | 0 |  | 1 |  |  |  | MIPU | BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #1 Accelerate | Upgrade wave trap. | 228 | 259 |  |  |  | 18 | 6 | [5 empty] | 19775 | 2012-09-13 | [38 empty] | 2018-06-01 | 2014-06-01 | 2015-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3395517SP | FROM->TO | BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 | REL | GMO | GMO |  |  | 0 | 541211 | BLSPS 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 | 17SP | 224 | 224 | 224 | 90.654 | 90.654 | 100.8494 | [7 empty] | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEYPL 161.00 161KV CKT 1 | 0 | 541235 | DUNCAN 5 161.00 | 541250 | SIBLEYPL 161.00 | 0 |  | 1 |  |  |  | MIPU | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #1 | Upgrade Prairie Lee wavetrap to at least 1200 A. | 233 | 259 |  |  |  | 18 | 6 | [5 empty] | 20537 | 2012-10-01 | [39 empty] | 2014-06-01 | 2015-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3395517SP | FROM->TO | BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 | S | GMO | GMO |  |  | 0 | 541211 | BLSPS 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 | 17SP | 224 | 224 | 224 | 90.654 | 90.654 | 100.8494 | [7 empty] | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEYPL 161.00 161KV CKT 1 | 0 | 541235 | DUNCAN 5 161.00 | 541250 | SIBLEYPL 161.00 | 0 |  | 1 |  |  |  | MIPU | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #2 Accelerate | Reconductor 3.21 miles from Blue Springs South to Prairie Lee 161 kV to 954 ACSS. Upgrade substation equipment to 2000 Amps. | 558 | 558 |  |  |  | 24 | 24 | [5 empty] | 2983951.993 | 2011-11-09 | [38 empty] | 2018-06-01 | 2014-06-01 | 2016-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3395517SP | FROM->TO | BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 | S | GMO | GMO |  |  | 0 | 541211 | BLSPS 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 | 17SP | 224 | 224 | 224 | 90.654 | 90.654 | 100.8494 | [7 empty] | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEYPL 161.00 161KV CKT 1 | 0 | 541235 | DUNCAN 5 161.00 | 541250 | SIBLEYPL 161.00 | 0 |  | 1 |  |  |  | MIPU | BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #1 Accelerate | Upgrade wave trap. | 228 | 259 |  |  |  | 18 | 6 | [5 empty] | 19775 | 2012-09-13 | [38 empty] | 2018-06-01 | 2014-06-01 | 2015-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4505522SP | FROM->TO | BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 | REL | GMO | GMO |  |  | 0 | 541211 | BLSPS 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 | 22SP | 224 | 224 | 224 | 94.7172 | 94.7172 | 104.42 | [7 empty] | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEYPL 161.00 161KV CKT 1 | 0 | 541235 | DUNCAN 5 161.00 | 541250 | SIBLEYPL 161.00 | 0 |  | 1 |  |  |  | MIPU | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #1 | Upgrade Prairie Lee wavetrap to at least 1200 A. | 233 | 259 |  |  |  | 18 | 6 | [5 empty] | 20537 | 2012-10-01 | [39 empty] | 2014-06-01 | 2015-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4505522SP | FROM->TO | BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 | S | GMO | GMO |  |  | 0 | 541211 | BLSPS 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 | 22SP | 224 | 224 | 224 | 94.7172 | 94.7172 | 104.42 | [7 empty] | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEYPL 161.00 161KV CKT 1 | 0 | 541235 | DUNCAN 5 161.00 | 541250 | SIBLEYPL 161.00 | 0 |  | 1 |  |  |  | MIPU | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #2 Accelerate | Reconductor 3.21 miles from Blue Springs South to Prairie Lee 161 kV to 954 ACSS. Upgrade substation equipment to 2000 Amps. | 558 | 558 |  |  |  | 24 | 24 | [5 empty] | 2983951.993 | 2011-11-09 | [38 empty] | 2018-06-01 | 2014-06-01 | 2016-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4505522SP | FROM->TO | BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 | S | GMO | GMO |  |  | 0 | 541211 | BLSPS 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 | 22SP | 224 | 224 | 224 | 94.7172 | 94.7172 | 104.42 | [7 empty] | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEYPL 161.00 161KV CKT 1 | 0 | 541235 | DUNCAN 5 161.00 | 541250 | SIBLEYPL 161.00 | 0 |  | 1 |  |  |  | MIPU | BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #1 Accelerate | Upgrade wave trap. | 228 | 259 |  |  |  | 18 | 6 | [5 empty] | 19775 | 2012-09-13 | [38 empty] | 2018-06-01 | 2014-06-01 | 2015-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4075514SP | TO->FROM | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 | REL | GMO | GMO |  |  | 0 | 541206 | PRALEE 5 161.00 | 541211 | BLSPS 5 161.00 | 0 |  | 1 | 17SP | 224 | 224 | 224 |  | 104.4844 | 113.3545 | [7 empty] | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEYPL 161.00 161KV CKT 1 | 0 | 541235 | DUNCAN 5 161.00 | 541250 | SIBLEYPL 161.00 | 0 |  | 1 |  |  |  | MIPU | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #1 | Upgrade Prairie Lee wavetrap to at least 1200 A. | 233 | 259 |  |  |  | 18 | 6 | [5 empty] | 20537 | 2012-10-01 | [39 empty] | 2014-06-01 | 2015-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4075514SP | TO->FROM | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 | S | GMO | GMO |  |  | 0 | 541206 | PRALEE 5 161.00 | 541211 | BLSPS 5 161.00 | 0 |  | 1 | 17SP | 224 | 224 | 224 |  | 104.4844 | 113.3545 | [7 empty] | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEYPL 161.00 161KV CKT 1 | 0 | 541235 | DUNCAN 5 161.00 | 541250 | SIBLEYPL 161.00 | 0 |  | 1 |  |  |  | MIPU | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #2 Accelerate | Reconductor 3.21 miles from Blue Springs South to Prairie Lee 161 kV to 954 ACSS. Upgrade substation equipment to 2000 Amps. | 558 | 558 |  |  |  | 24 | 24 | [5 empty] | 2983951.993 | 2011-11-09 | [38 empty] | 2018-06-01 | 2014-06-01 | 2016-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4075514SP | TO->FROM | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 | S | GMO | GMO |  |  | 0 | 541206 | PRALEE 5 161.00 | 541211 | BLSPS 5 161.00 | 0 |  | 1 | 17SP | 224 | 224 | 224 |  | 104.4844 | 113.3545 | [7 empty] | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEYPL 161.00 161KV CKT 1 | 0 | 541235 | DUNCAN 5 161.00 | 541250 | SIBLEYPL 161.00 | 0 |  | 1 |  |  |  | MIPU | BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #1 Accelerate | Upgrade wave trap. | 228 | 259 |  |  |  | 18 | 6 | [5 empty] | 19775 | 2012-09-13 | [38 empty] | 2018-06-01 | 2014-06-01 | 2015-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3995514SP | TO->FROM | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 | REL | GMO | GMO |  |  | 0 | 541206 | PRALEE 5 161.00 | 541211 | BLSPS 5 161.00 | 0 |  | 1 | 17SP | 224 | 224 | 224 |  | 97.5299 | 111.9501 | [7 empty] | CATEGORYB | SINGLE | PLEASANT HILL - SIBLEY 345KV CKT 1 | 0 | 541200 | PHILL 7 345.00 | 541201 | SIBLEY 7 345.00 | 0 |  | 1 |  |  |  | MIPU | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #1 | Upgrade Prairie Lee wavetrap to at least 1200 A. | 233 | 259 |  |  |  | 18 | 6 | [5 empty] | 20537 | 2012-10-01 | [39 empty] | 2014-06-01 | 2015-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3995514SP | TO->FROM | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 | S | GMO | GMO |  |  | 0 | 541206 | PRALEE 5 161.00 | 541211 | BLSPS 5 161.00 | 0 |  | 1 | 17SP | 224 | 224 | 224 |  | 97.5299 | 111.9501 | [7 empty] | CATEGORYB | SINGLE | PLEASANT HILL - SIBLEY 345KV CKT 1 | 0 | 541200 | PHILL 7 345.00 | 541201 | SIBLEY 7 345.00 | 0 |  | 1 |  |  |  | MIPU | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #2 Accelerate | Reconductor 3.21 miles from Blue Springs South to Prairie Lee 161 kV to 954 ACSS. Upgrade substation equipment to 2000 Amps. | 558 | 558 |  |  |  | 24 | 24 | [5 empty] | 2983951.993 | 2011-11-09 | [38 empty] | 2018-06-01 | 2014-06-01 | 2016-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3995514SP | TO->FROM | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 | S | GMO | GMO |  |  | 0 | 541206 | PRALEE 5 161.00 | 541211 | BLSPS 5 161.00 | 0 |  | 1 | 17SP | 224 | 224 | 224 |  | 97.5299 | 111.9501 | [7 empty] | CATEGORYB | SINGLE | PLEASANT HILL - SIBLEY 345KV CKT 1 | 0 | 541200 | PHILL 7 345.00 | 541201 | SIBLEY 7 345.00 | 0 |  | 1 |  |  |  | MIPU | BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #1 Accelerate | Upgrade wave trap. | 228 | 259 |  |  |  | 18 | 6 | [5 empty] | 19775 | 2012-09-13 | [38 empty] | 2018-06-01 | 2014-06-01 | 2015-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3405517SP | TO->FROM | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 | REL | GMO | GMO |  |  | 0 | 541206 | PRALEE 5 161.00 | 541211 | BLSPS 5 161.00 | 0 |  | 1 | 17SP | 224 | 224 | 224 | 100.4876 | 100.4876 | 110.6888 | [7 empty] | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEYPL 161.00 161KV CKT 1 | 0 | 541235 | DUNCAN 5 161.00 | 541250 | SIBLEYPL 161.00 | 0 |  | 1 |  |  |  | MIPU | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #1 | Upgrade Prairie Lee wavetrap to at least 1200 A. | 233 | 259 |  |  |  | 18 | 6 | [5 empty] | 20537 | 2012-10-01 | [39 empty] | 2014-06-01 | 2015-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3405517SP | TO->FROM | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 | S | GMO | GMO |  |  | 0 | 541206 | PRALEE 5 161.00 | 541211 | BLSPS 5 161.00 | 0 |  | 1 | 17SP | 224 | 224 | 224 | 100.4876 | 100.4876 | 110.6888 | [7 empty] | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEYPL 161.00 161KV CKT 1 | 0 | 541235 | DUNCAN 5 161.00 | 541250 | SIBLEYPL 161.00 | 0 |  | 1 |  |  |  | MIPU | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #2 Accelerate | Reconductor 3.21 miles from Blue Springs South to Prairie Lee 161 kV to 954 ACSS. Upgrade substation equipment to 2000 Amps. | 558 | 558 |  |  |  | 24 | 24 | [5 empty] | 2983951.993 | 2011-11-09 | [38 empty] | 2018-06-01 | 2014-06-01 | 2016-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3405517SP | TO->FROM | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 | S | GMO | GMO |  |  | 0 | 541206 | PRALEE 5 161.00 | 541211 | BLSPS 5 161.00 | 0 |  | 1 | 17SP | 224 | 224 | 224 | 100.4876 | 100.4876 | 110.6888 | [7 empty] | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEYPL 161.00 161KV CKT 1 | 0 | 541235 | DUNCAN 5 161.00 | 541250 | SIBLEYPL 161.00 | 0 |  | 1 |  |  |  | MIPU | BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #1 Accelerate | Upgrade wave trap. | 228 | 259 |  |  |  | 18 | 6 | [5 empty] | 19775 | 2012-09-13 | [38 empty] | 2018-06-01 | 2014-06-01 | 2015-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T15085514SP | TO->FROM | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 | REL | GMO | GMO |  |  | 0 | 541206 | PRALEE 5 161.00 | 541211 | BLSPS 5 161.00 | 0 |  | 1 | 17SP | 224 | 224 | 224 |  | 94.4227 | 106.9989 | [7 empty] | CATEGORYB | SINGLE | CLINTON - MONTROSE 161KV CKT 1 | 0 | 542995 | MONTROS5 161.00 | 300071 | 5CLINTN 161.00 | 0 |  | 1 |  |  |  | MIPU | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #1 | Upgrade Prairie Lee wavetrap to at least 1200 A. | 233 | 259 |  |  |  | 18 | 6 | [5 empty] | 20537 | 2012-10-01 | [39 empty] | 2014-06-01 | 2015-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T15085514SP | TO->FROM | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 | S | GMO | GMO |  |  | 0 | 541206 | PRALEE 5 161.00 | 541211 | BLSPS 5 161.00 | 0 |  | 1 | 17SP | 224 | 224 | 224 |  | 94.4227 | 106.9989 | [7 empty] | CATEGORYB | SINGLE | CLINTON - MONTROSE 161KV CKT 1 | 0 | 542995 | MONTROS5 161.00 | 300071 | 5CLINTN 161.00 | 0 |  | 1 |  |  |  | MIPU | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #2 Accelerate | Reconductor 3.21 miles from Blue Springs South to Prairie Lee 161 kV to 954 ACSS. Upgrade substation equipment to 2000 Amps. | 558 | 558 |  |  |  | 24 | 24 | [5 empty] | 2983951.993 | 2011-11-09 | [38 empty] | 2018-06-01 | 2014-06-01 | 2016-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T15085514SP | TO->FROM | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 | S | GMO | GMO |  |  | 0 | 541206 | PRALEE 5 161.00 | 541211 | BLSPS 5 161.00 | 0 |  | 1 | 17SP | 224 | 224 | 224 |  | 94.4227 | 106.9989 | [7 empty] | CATEGORYB | SINGLE | CLINTON - MONTROSE 161KV CKT 1 | 0 | 542995 | MONTROS5 161.00 | 300071 | 5CLINTN 161.00 | 0 |  | 1 |  |  |  | MIPU | BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #1 Accelerate | Upgrade wave trap. | 228 | 259 |  |  |  | 18 | 6 | [5 empty] | 19775 | 2012-09-13 | [38 empty] | 2018-06-01 | 2014-06-01 | 2015-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T15475517SP | TO->FROM | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 | S | GMO | GMO |  |  | 0 | 541206 | PRALEE 5 161.00 | 541211 | BLSPS 5 161.00 | 0 |  | 1 | 17SP | 224 | 224 | 224 | 87.8234 | 87.8234 | 102.6102 | [7 empty] | CATEGORYB | SINGLE | CLINTON - MONTROSE 161KV CKT 1 | 0 | 542995 | MONTROS5 161.00 | 300071 | 5CLINTN 161.00 | 0 |  | 1 |  |  |  | MIPU | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #2 Accelerate | Reconductor 3.21 miles from Blue Springs South to Prairie Lee 161 kV to 954 ACSS. Upgrade substation equipment to 2000 Amps. | 558 | 558 |  |  |  | 24 | 24 | [5 empty] | 2983951.993 | 2011-11-09 | [38 empty] | 2018-06-01 | 2014-06-01 | 2016-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T15475517SP | TO->FROM | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 | REL | GMO | GMO |  |  | 0 | 541206 | PRALEE 5 161.00 | 541211 | BLSPS 5 161.00 | 0 |  | 1 | 17SP | 224 | 224 | 224 | 87.8234 | 87.8234 | 102.6102 | [7 empty] | CATEGORYB | SINGLE | CLINTON - MONTROSE 161KV CKT 1 | 0 | 542995 | MONTROS5 161.00 | 300071 | 5CLINTN 161.00 | 0 |  | 1 |  |  |  | MIPU | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #1 | Upgrade Prairie Lee wavetrap to at least 1200 A. | 233 | 259 |  |  |  | 18 | 6 | [5 empty] | 20537 | 2012-10-01 | [39 empty] | 2014-06-01 | 2015-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T15475517SP | TO->FROM | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 | S | GMO | GMO |  |  | 0 | 541206 | PRALEE 5 161.00 | 541211 | BLSPS 5 161.00 | 0 |  | 1 | 17SP | 224 | 224 | 224 | 87.8234 | 87.8234 | 102.6102 | [7 empty] | CATEGORYB | SINGLE | CLINTON - MONTROSE 161KV CKT 1 | 0 | 542995 | MONTROS5 161.00 | 300071 | 5CLINTN 161.00 | 0 |  | 1 |  |  |  | MIPU | BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #1 Accelerate | Upgrade wave trap. | 228 | 259 |  |  |  | 18 | 6 | [5 empty] | 19775 | 2012-09-13 | [38 empty] | 2018-06-01 | 2014-06-01 | 2015-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4515522SP | TO->FROM | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 | REL | GMO | GMO |  |  | 0 | 541206 | PRALEE 5 161.00 | 541211 | BLSPS 5 161.00 | 0 |  | 1 | 22SP | 224 | 224 | 224 | 105.5037 | 105.5037 | 115.2455 | [7 empty] | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEYPL 161.00 161KV CKT 1 | 0 | 541235 | DUNCAN 5 161.00 | 541250 | SIBLEYPL 161.00 | 0 |  | 1 |  |  |  | MIPU | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #1 | Upgrade Prairie Lee wavetrap to at least 1200 A. | 233 | 259 |  |  |  | 18 | 6 | [5 empty] | 20537 | 2012-10-01 | [39 empty] | 2014-06-01 | 2015-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4515522SP | TO->FROM | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 | S | GMO | GMO |  |  | 0 | 541206 | PRALEE 5 161.00 | 541211 | BLSPS 5 161.00 | 0 |  | 1 | 22SP | 224 | 224 | 224 | 105.5037 | 105.5037 | 115.2455 | [7 empty] | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEYPL 161.00 161KV CKT 1 | 0 | 541235 | DUNCAN 5 161.00 | 541250 | SIBLEYPL 161.00 | 0 |  | 1 |  |  |  | MIPU | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #2 Accelerate | Reconductor 3.21 miles from Blue Springs South to Prairie Lee 161 kV to 954 ACSS. Upgrade substation equipment to 2000 Amps. | 558 | 558 |  |  |  | 24 | 24 | [5 empty] | 2983951.993 | 2011-11-09 | [38 empty] | 2018-06-01 | 2014-06-01 | 2016-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4515522SP | TO->FROM | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 | S | GMO | GMO |  |  | 0 | 541206 | PRALEE 5 161.00 | 541211 | BLSPS 5 161.00 | 0 |  | 1 | 22SP | 224 | 224 | 224 | 105.5037 | 105.5037 | 115.2455 | [7 empty] | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEYPL 161.00 161KV CKT 1 | 0 | 541235 | DUNCAN 5 161.00 | 541250 | SIBLEYPL 161.00 | 0 |  | 1 |  |  |  | MIPU | BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #1 Accelerate | Upgrade wave trap. | 228 | 259 |  |  |  | 18 | 6 | [5 empty] | 19775 | 2012-09-13 | [38 empty] | 2018-06-01 | 2014-06-01 | 2015-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T22865522SP | TO->FROM | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 | REL | GMO | GMO |  |  | 0 | 541206 | PRALEE 5 161.00 | 541211 | BLSPS 5 161.00 | 0 |  | 1 | 22SP | 224 | 224 | 224 | 88.5677 | 88.5677 | 103.4277 | [7 empty] | CATEGORYB | SINGLE | CLINTON - MONTROSE 161KV CKT 1 | 0 | 542995 | MONTROS5 161.00 | 300071 | 5CLINTN 161.00 | 0 |  | 1 |  |  |  | MIPU | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #1 | Upgrade Prairie Lee wavetrap to at least 1200 A. | 233 | 259 |  |  |  | 18 | 6 | [5 empty] | 20537 | 2012-10-01 | [39 empty] | 2014-06-01 | 2015-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T22865522SP | TO->FROM | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 | S | GMO | GMO |  |  | 0 | 541206 | PRALEE 5 161.00 | 541211 | BLSPS 5 161.00 | 0 |  | 1 | 22SP | 224 | 224 | 224 | 88.5677 | 88.5677 | 103.4277 | [7 empty] | CATEGORYB | SINGLE | CLINTON - MONTROSE 161KV CKT 1 | 0 | 542995 | MONTROS5 161.00 | 300071 | 5CLINTN 161.00 | 0 |  | 1 |  |  |  | MIPU | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #2 Accelerate | Reconductor 3.21 miles from Blue Springs South to Prairie Lee 161 kV to 954 ACSS. Upgrade substation equipment to 2000 Amps. | 558 | 558 |  |  |  | 24 | 24 | [5 empty] | 2983951.993 | 2011-11-09 | [38 empty] | 2018-06-01 | 2014-06-01 | 2016-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T22865522SP | TO->FROM | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 | S | GMO | GMO |  |  | 0 | 541206 | PRALEE 5 161.00 | 541211 | BLSPS 5 161.00 | 0 |  | 1 | 22SP | 224 | 224 | 224 | 88.5677 | 88.5677 | 103.4277 | [7 empty] | CATEGORYB | SINGLE | CLINTON - MONTROSE 161KV CKT 1 | 0 | 542995 | MONTROS5 161.00 | 300071 | 5CLINTN 161.00 | 0 |  | 1 |  |  |  | MIPU | BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #1 Accelerate | Upgrade wave trap. | 228 | 259 |  |  |  | 18 | 6 | [5 empty] | 19775 | 2012-09-13 | [38 empty] | 2018-06-01 | 2014-06-01 | 2015-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4395522SP | TO->FROM | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 | REL | GMO | GMO |  |  | 0 | 541206 | PRALEE 5 161.00 | 541211 | BLSPS 5 161.00 | 0 |  | 1 | 22SP | 224 | 224 | 224 | 92.1607 | 92.1607 | 101.4851 | [7 empty] | CATEGORYB | SINGLE | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | 0 | 541205 | BLSPE 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  | MIPU | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #1 | Upgrade Prairie Lee wavetrap to at least 1200 A. | 233 | 259 |  |  |  | 18 | 6 | [5 empty] | 20537 | 2012-10-01 | [39 empty] | 2014-06-01 | 2015-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4395522SP | TO->FROM | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 | S | GMO | GMO |  |  | 0 | 541206 | PRALEE 5 161.00 | 541211 | BLSPS 5 161.00 | 0 |  | 1 | 22SP | 224 | 224 | 224 | 92.1607 | 92.1607 | 101.4851 | [7 empty] | CATEGORYB | SINGLE | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | 0 | 541205 | BLSPE 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  | MIPU | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #2 Accelerate | Reconductor 3.21 miles from Blue Springs South to Prairie Lee 161 kV to 954 ACSS. Upgrade substation equipment to 2000 Amps. | 558 | 558 |  |  |  | 24 | 24 | [5 empty] | 2983951.993 | 2011-11-09 | [38 empty] | 2018-06-01 | 2014-06-01 | 2016-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4395522SP | TO->FROM | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 | S | GMO | GMO |  |  | 0 | 541206 | PRALEE 5 161.00 | 541211 | BLSPS 5 161.00 | 0 |  | 1 | 22SP | 224 | 224 | 224 | 92.1607 | 92.1607 | 101.4851 | [7 empty] | CATEGORYB | SINGLE | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | 0 | 541205 | BLSPE 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 |  |  |  | MIPU | BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #1 Accelerate | Upgrade wave trap. | 228 | 259 |  |  |  | 18 | 6 | [5 empty] | 19775 | 2012-09-13 | [38 empty] | 2018-06-01 | 2014-06-01 | 2015-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2225513WP | FROM->TO | BROKEN BOW - LOUP CITY 115KV CKT 1 | REL | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640089 | BROKENB7 115.00 | 640259 | LOUPCTY7 115.00 | 0 |  | 1 | 13WP | 120 | 120 | 127 | 78.7527 | 78.7527 | 101.4284 | [7 empty] | CATEGORYB | SINGLE | GRAND ISLAND - SWEETWATER 345KV CKT 1 | 0 | 640374 | SWEET W3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 |  |  |  | NPPD | Cherry Co - Gentleman 345 kV Ckt1 | Build new 345 kV Transmission Line from GGS 345 kV Substation to a new Cherry County 345 kV Substation (76 miles). | [5 empty] | 72 | 72 | Y | [45 empty] | 2013-10-01 | 2018-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2225513WP | FROM->TO | BROKEN BOW - LOUP CITY 115KV CKT 1 | REL | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640089 | BROKENB7 115.00 | 640259 | LOUPCTY7 115.00 | 0 |  | 1 | 13WP | 120 | 120 | 127 | 78.7527 | 78.7527 | 101.4284 | [7 empty] | CATEGORYB | SINGLE | GRAND ISLAND - SWEETWATER 345KV CKT 1 | 0 | 640374 | SWEET W3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 |  |  |  | NPPD | Cherry Co - Holt Co 345 kV Ckt1 | Build new 345 kV Transmission Line from new Cherry County 345 kV Substation to new 345 kV Holt County Substation. (Estimated 146 miles). | [5 empty] | 72 | [47 empty] | 2013-10-01 | 2018-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2225513WP | FROM->TO | BROKEN BOW - LOUP CITY 115KV CKT 1 | REL | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640089 | BROKENB7 115.00 | 640259 | LOUPCTY7 115.00 | 0 |  | 1 | 13WP | 120 | 120 | 127 | 78.7527 | 78.7527 | 101.4284 | [7 empty] | CATEGORYB | SINGLE | GRAND ISLAND - SWEETWATER 345KV CKT 1 | 0 | 640374 | SWEET W3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 |  |  |  | NPPD | Cherry Co 345 kV Terminal Upgrades | Build new Cherry County 345 kV Substation. | [5 empty] | 72 | [47 empty] | 2013-10-01 | 2018-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1755517WP | FROM->TO | BROKEN BOW - LOUP CITY 115KV CKT 1 | REL | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640089 | BROKENB7 115.00 | 640259 | LOUPCTY7 115.00 | 0 |  | 1 | 17WP | 120 | 120 | 127 | 75.9638 | 75.9638 | 102.9128 | [7 empty] | CATEGORYB | SINGLE | GRAND ISLAND - SWEETWATER 345KV CKT 1 | 0 | 640374 | SWEET W3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 |  |  |  | NPPD | Cherry Co - Gentleman 345 kV Ckt1 | Build new 345 kV Transmission Line from GGS 345 kV Substation to a new Cherry County 345 kV Substation (76 miles). | [5 empty] | 72 | 72 | Y | [45 empty] | 2013-10-01 | 2018-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1755517WP | FROM->TO | BROKEN BOW - LOUP CITY 115KV CKT 1 | REL | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640089 | BROKENB7 115.00 | 640259 | LOUPCTY7 115.00 | 0 |  | 1 | 17WP | 120 | 120 | 127 | 75.9638 | 75.9638 | 102.9128 | [7 empty] | CATEGORYB | SINGLE | GRAND ISLAND - SWEETWATER 345KV CKT 1 | 0 | 640374 | SWEET W3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 |  |  |  | NPPD | Cherry Co - Holt Co 345 kV Ckt1 | Build new 345 kV Transmission Line from new Cherry County 345 kV Substation to new 345 kV Holt County Substation. (Estimated 146 miles). | [5 empty] | 72 | [47 empty] | 2013-10-01 | 2018-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1755517WP | FROM->TO | BROKEN BOW - LOUP CITY 115KV CKT 1 | REL | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640089 | BROKENB7 115.00 | 640259 | LOUPCTY7 115.00 | 0 |  | 1 | 17WP | 120 | 120 | 127 | 75.9638 | 75.9638 | 102.9128 | [7 empty] | CATEGORYB | SINGLE | GRAND ISLAND - SWEETWATER 345KV CKT 1 | 0 | 640374 | SWEET W3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 |  |  |  | NPPD | Cherry Co 345 kV Terminal Upgrades | Build new Cherry County 345 kV Substation. | [5 empty] | 72 | [47 empty] | 2013-10-01 | 2018-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1665517WP | FROM->TO | BROKEN BOW - LOUP CITY 115KV CKT 1 | REL | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640089 | BROKENB7 115.00 | 640259 | LOUPCTY7 115.00 | 0 |  | 1 | 17WP | 120 | 120 | 127 | 75.2409 | 75.2409 | 100.6508 | [7 empty] | CATEGORYB | SINGLE | CROOKED CREEK - RIVERDALE 230KV CKT 1 | 0 | 640093 | C.CREEK4 230.00 | 640330 | RIVERDL4 230.00 | 0 |  | 1 |  |  |  | NPPD | Cherry Co - Gentleman 345 kV Ckt1 | Build new 345 kV Transmission Line from GGS 345 kV Substation to a new Cherry County 345 kV Substation (76 miles). | [5 empty] | 72 | 72 | Y | [45 empty] | 2013-10-01 | 2018-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1665517WP | FROM->TO | BROKEN BOW - LOUP CITY 115KV CKT 1 | REL | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640089 | BROKENB7 115.00 | 640259 | LOUPCTY7 115.00 | 0 |  | 1 | 17WP | 120 | 120 | 127 | 75.2409 | 75.2409 | 100.6508 | [7 empty] | CATEGORYB | SINGLE | CROOKED CREEK - RIVERDALE 230KV CKT 1 | 0 | 640093 | C.CREEK4 230.00 | 640330 | RIVERDL4 230.00 | 0 |  | 1 |  |  |  | NPPD | Cherry Co - Holt Co 345 kV Ckt1 | Build new 345 kV Transmission Line from new Cherry County 345 kV Substation to new 345 kV Holt County Substation. (Estimated 146 miles). | [5 empty] | 72 | [47 empty] | 2013-10-01 | 2018-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1665517WP | FROM->TO | BROKEN BOW - LOUP CITY 115KV CKT 1 | REL | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640089 | BROKENB7 115.00 | 640259 | LOUPCTY7 115.00 | 0 |  | 1 | 17WP | 120 | 120 | 127 | 75.2409 | 75.2409 | 100.6508 | [7 empty] | CATEGORYB | SINGLE | CROOKED CREEK - RIVERDALE 230KV CKT 1 | 0 | 640093 | C.CREEK4 230.00 | 640330 | RIVERDL4 230.00 | 0 |  | 1 |  |  |  | NPPD | Cherry Co 345 kV Terminal Upgrades | Build new Cherry County 345 kV Substation. | [5 empty] | 72 | [47 empty] | 2013-10-01 | 2018-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T11295513SP | FROM->TO | BROOKLINE (BRKLTX1) 345/161/13.2KV TRANSFORMER CKT 1 | REL | SPRM | SPRM | SPRM > 69KV | SPRM > 69KV | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549988 | BRKLNE XF1 113.200 | 1 | 13SP | 400 | 400 | 0 | 103.1117 | 103.1117 | 105.5143 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE (BRKLTX2) 345/161/13.2KV TRANSFORMER CKT 2 | 1 | 549969 | BROOKLINE 5161.00 | 549984 | BROOKLINE 7345.00 | 549989 | BRKLNE XF2 113.200 | 2 |  |  |  | AEPW | Multi - Centerton - Osage Creek 345 kV | Install new 345/161 kV transformer at Kings River (Previous name Osage Creek); Install 9 miles of 345 kV line from Shipe Road to East Rogers; Install 32 miles of 345 kV line from East Rogers to Kings River (previous Osage Creek). | [53 empty] | 2013-06-01 | 2016-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T11295513SP | FROM->TO | BROOKLINE (BRKLTX1) 345/161/13.2KV TRANSFORMER CKT 1 | REL | SPRM | SPRM | SPRM > 69KV | SPRM > 69KV | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549988 | BRKLNE XF1 113.200 | 1 | 13SP | 400 | 400 | 0 | 103.1117 | 103.1117 | 105.5143 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE (BRKLTX2) 345/161/13.2KV TRANSFORMER CKT 2 | 1 | 549969 | BROOKLINE 5161.00 | 549984 | BROOKLINE 7345.00 | 549989 | BRKLNE XF2 113.200 | 2 |  |  |  | AEPW | Multi - Flint Creek – Centerton 345 kV and Centerton- East Centerton 161 kV | Install 9 miles of 161 kV from new Shipe Road Substation to East Centerton Substation; Install 345/161 kV transformer at Shipe Road; Install 18 miles of new 345 kV, 2-954 ACSR line. | [53 empty] | 2016-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T23575522SP | FROM->TO | BROOKLINE (BRKLTX1) 345/161/13.2KV TRANSFORMER CKT 1 | REL | SPRM | SPRM | SPRM > 69KV | SPRM > 69KV | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549988 | BRKLNE XF1 113.200 | 1 | 22SP | 400 | 400 | 0 | 100.8 | 100.7776 | 104.6933 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE (BRKLTX2) 345/161/13.2KV TRANSFORMER CKT 2 | 1 | 549969 | BROOKLINE 5161.00 | 549984 | BROOKLINE 7345.00 | 549989 | BRKLNE XF2 113.200 | 2 |  |  |  | SPRM | Brookline – Compton Ridge 345 kV SPRM | Build approx. 30 mile 345 kV line | [5 empty] | 60 | 60 | [46 empty] | 2020-06-01 | 2020-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T23575522SP | FROM->TO | BROOKLINE (BRKLTX1) 345/161/13.2KV TRANSFORMER CKT 1 | REL | SPRM | SPRM | SPRM > 69KV | SPRM > 69KV | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549988 | BRKLNE XF1 113.200 | 1 | 22SP | 400 | 400 | 0 | 100.8 | 100.7776 | 104.6933 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE (BRKLTX2) 345/161/13.2KV TRANSFORMER CKT 2 | 1 | 549969 | BROOKLINE 5161.00 | 549984 | BROOKLINE 7345.00 | 549989 | BRKLNE XF2 113.200 | 2 |  |  |  | EMDE | Brookline – Compton Ridge 345 kV EMDE | Build approx. 50% of 30 mile 345 kV line | [53 empty] | 2020-06-01 | 2020-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T23575522SP | FROM->TO | BROOKLINE (BRKLTX1) 345/161/13.2KV TRANSFORMER CKT 1 | REL | SPRM | SPRM | SPRM > 69KV | SPRM > 69KV | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549988 | BRKLNE XF1 113.200 | 1 | 22SP | 400 | 400 | 0 | 100.8 | 100.7776 | 104.6933 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE (BRKLTX2) 345/161/13.2KV TRANSFORMER CKT 2 | 1 | 549969 | BROOKLINE 5161.00 | 549984 | BROOKLINE 7345.00 | 549989 | BRKLNE XF2 113.200 | 2 |  |  |  | EMDE | Compton Ridge 345/161 kV Transformer | Install 500 MVA, 345/161 kV transformer and Cut EDE Reeds Spring? Branson line at 50% and route in & out of Compton Ridge | [53 empty] | 2020-06-01 | 2020-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T11275513SP | FROM->TO | BROOKLINE (BRKLTX2) 345/161/13.2KV TRANSFORMER CKT 2 | REL | SPRM | SPRM | SPRM > 69KV | SPRM > 69KV | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549989 | BRKLNE XF2 113.200 | 2 | 13SP | 400 | 400 | 0 | 102.8 | 102.8007 | 105.194 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE (BRKLTX1) 345/161/13.2KV TRANSFORMER CKT 1 | 1 | 549969 | BROOKLINE 5161.00 | 549984 | BROOKLINE 7345.00 | 549988 | BRKLNE XF1 113.200 | 1 |  |  |  | AEPW | Multi - Centerton - Osage Creek 345 kV | Install new 345/161 kV transformer at Kings River (Previous name Osage Creek); Install 9 miles of 345 kV line from Shipe Road to East Rogers; Install 32 miles of 345 kV line from East Rogers to Kings River (previous Osage Creek). | [53 empty] | 2013-06-01 | 2016-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T11275513SP | FROM->TO | BROOKLINE (BRKLTX2) 345/161/13.2KV TRANSFORMER CKT 2 | REL | SPRM | SPRM | SPRM > 69KV | SPRM > 69KV | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549989 | BRKLNE XF2 113.200 | 2 | 13SP | 400 | 400 | 0 | 102.8 | 102.8007 | 105.194 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE (BRKLTX1) 345/161/13.2KV TRANSFORMER CKT 1 | 1 | 549969 | BROOKLINE 5161.00 | 549984 | BROOKLINE 7345.00 | 549988 | BRKLNE XF1 113.200 | 1 |  |  |  | AEPW | Multi - Flint Creek – Centerton 345 kV and Centerton- East Centerton 161 kV | Install 9 miles of 161 kV from new Shipe Road Substation to East Centerton Substation; Install 345/161 kV transformer at Shipe Road; Install 18 miles of new 345 kV, 2-954 ACSR line. | [53 empty] | 2016-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T23555522SP | FROM->TO | BROOKLINE (BRKLTX2) 345/161/13.2KV TRANSFORMER CKT 2 | REL | SPRM | SPRM | SPRM > 69KV | SPRM > 69KV | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549989 | BRKLNE XF2 113.200 | 2 | 22SP | 400 | 400 | 0 | 100.4801 | 100.4801 | 104.3765 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE (BRKLTX1) 345/161/13.2KV TRANSFORMER CKT 1 | 1 | 549969 | BROOKLINE 5161.00 | 549984 | BROOKLINE 7345.00 | 549988 | BRKLNE XF1 113.200 | 1 |  |  |  | SPRM | Brookline – Compton Ridge 345 kV SPRM | Build approx. 30 mile 345 kV line | [5 empty] | 60 | 60 | [46 empty] | 2020-06-01 | 2020-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T23555522SP | FROM->TO | BROOKLINE (BRKLTX2) 345/161/13.2KV TRANSFORMER CKT 2 | REL | SPRM | SPRM | SPRM > 69KV | SPRM > 69KV | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549989 | BRKLNE XF2 113.200 | 2 | 22SP | 400 | 400 | 0 | 100.4801 | 100.4801 | 104.3765 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE (BRKLTX1) 345/161/13.2KV TRANSFORMER CKT 1 | 1 | 549969 | BROOKLINE 5161.00 | 549984 | BROOKLINE 7345.00 | 549988 | BRKLNE XF1 113.200 | 1 |  |  |  | EMDE | Brookline – Compton Ridge 345 kV EMDE | Build approx. 50% of 30 mile 345 kV line | [53 empty] | 2020-06-01 | 2020-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T23555522SP | FROM->TO | BROOKLINE (BRKLTX2) 345/161/13.2KV TRANSFORMER CKT 2 | REL | SPRM | SPRM | SPRM > 69KV | SPRM > 69KV | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549989 | BRKLNE XF2 113.200 | 2 | 22SP | 400 | 400 | 0 | 100.4801 | 100.4801 | 104.3765 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE (BRKLTX1) 345/161/13.2KV TRANSFORMER CKT 1 | 1 | 549969 | BROOKLINE 5161.00 | 549984 | BROOKLINE 7345.00 | 549988 | BRKLNE XF1 113.200 | 1 |  |  |  | EMDE | Compton Ridge 345/161 kV Transformer | Install 500 MVA, 345/161 kV transformer and Cut EDE Reeds Spring? Branson line at 50% and route in & out of Compton Ridge | [53 empty] | 2020-06-01 | 2020-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T9495513WP | FROM->TO | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | EXP | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | 13WP | 329 | 360 | 0 | 115.2 | 115.2251 | 117.3009 | [7 empty] | CATEGORYB | GENOUT | GEN525562 1-TOLK GEN #2 24 KV | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T9495513WP | FROM->TO | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | EXP | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | 13WP | 329 | 360 | 0 | 115.2 | 115.2251 | 117.3009 | [7 empty] | CATEGORYB | GENOUT | GEN525562 1-TOLK GEN #2 24 KV | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T9495513WP | FROM->TO | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | EXP | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | 13WP | 329 | 360 | 0 | 115.2 | 115.2251 | 117.3009 | [7 empty] | CATEGORYB | GENOUT | GEN525562 1-TOLK GEN #2 24 KV | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T9495513WP | FROM->TO | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | EXP | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | 13WP | 329 | 360 | 0 | 115.2 | 115.2251 | 117.3009 | [7 empty] | CATEGORYB | GENOUT | GEN525562 1-TOLK GEN #2 24 KV | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T9465513WP | FROM->TO | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | EXP | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | 13WP | 329 | 360 | 0 | 110.7 | 110.8475 | 113.5177 | [7 empty] | CATEGORYB | GENOUT | GEN525561 1-TOLK GEN #1 24 KV | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T9465513WP | FROM->TO | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | EXP | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | 13WP | 329 | 360 | 0 | 110.7 | 110.8475 | 113.5177 | [7 empty] | CATEGORYB | GENOUT | GEN525561 1-TOLK GEN #1 24 KV | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T9465513WP | FROM->TO | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | EXP | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | 13WP | 329 | 360 | 0 | 110.7 | 110.8475 | 113.5177 | [7 empty] | CATEGORYB | GENOUT | GEN525561 1-TOLK GEN #1 24 KV | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T9465513WP | FROM->TO | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | EXP | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | 13WP | 329 | 360 | 0 | 110.7 | 110.8475 | 113.5177 | [7 empty] | CATEGORYB | GENOUT | GEN525561 1-TOLK GEN #1 24 KV | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T895513WP | FROM->TO | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | EXP | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | 13WP | 329 | 360 | 0 | 105.7043 | 105.7043 | 108.8001 | [7 empty] | CATEGORYB | SINGLE | PLANT X STATION - POTTER COUNTY INTERCHANGE 230KV CKT 1 | 0 | 523959 | POTTER_CO 6230.00 | 525481 | PLANT_X 6230.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T895513WP | FROM->TO | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | EXP | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | 13WP | 329 | 360 | 0 | 105.7043 | 105.7043 | 108.8001 | [7 empty] | CATEGORYB | SINGLE | PLANT X STATION - POTTER COUNTY INTERCHANGE 230KV CKT 1 | 0 | 523959 | POTTER_CO 6230.00 | 525481 | PLANT_X 6230.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T895513WP | FROM->TO | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | EXP | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | 13WP | 329 | 360 | 0 | 105.7043 | 105.7043 | 108.8001 | [7 empty] | CATEGORYB | SINGLE | PLANT X STATION - POTTER COUNTY INTERCHANGE 230KV CKT 1 | 0 | 523959 | POTTER_CO 6230.00 | 525481 | PLANT_X 6230.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T895513WP | FROM->TO | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | EXP | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | 13WP | 329 | 360 | 0 | 105.7043 | 105.7043 | 108.8001 | [7 empty] | CATEGORYB | SINGLE | PLANT X STATION - POTTER COUNTY INTERCHANGE 230KV CKT 1 | 0 | 523959 | POTTER_CO 6230.00 | 525481 | PLANT_X 6230.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2085513WP | FROM->TO | CANADAY - ELM CREEK 115KV CKT 1 | REL | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640103 | CANADAY7 115.00 | 640161 | ELMCRK_7 115.00 | 0 |  | 1 | 13WP | 80 | 80 | 88 | 92.6784 | 92.6784 | 103.6264 | [7 empty] | CATEGORYB | SINGLE | CROOKED CREEK - RIVERDALE 230KV CKT 1 | 0 | 640093 | C.CREEK4 230.00 | 640330 | RIVERDL4 230.00 | 0 |  | 1 |  |  |  | NPPD | Cherry Co - Gentleman 345 kV Ckt1 | Build new 345 kV Transmission Line from GGS 345 kV Substation to a new Cherry County 345 kV Substation (76 miles). | [5 empty] | 72 | 72 | Y | [45 empty] | 2013-10-01 | 2018-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2085513WP | FROM->TO | CANADAY - ELM CREEK 115KV CKT 1 | REL | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640103 | CANADAY7 115.00 | 640161 | ELMCRK_7 115.00 | 0 |  | 1 | 13WP | 80 | 80 | 88 | 92.6784 | 92.6784 | 103.6264 | [7 empty] | CATEGORYB | SINGLE | CROOKED CREEK - RIVERDALE 230KV CKT 1 | 0 | 640093 | C.CREEK4 230.00 | 640330 | RIVERDL4 230.00 | 0 |  | 1 |  |  |  | NPPD | Cherry Co - Holt Co 345 kV Ckt1 | Build new 345 kV Transmission Line from new Cherry County 345 kV Substation to new 345 kV Holt County Substation. (Estimated 146 miles). | [5 empty] | 72 | [47 empty] | 2013-10-01 | 2018-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2085513WP | FROM->TO | CANADAY - ELM CREEK 115KV CKT 1 | REL | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640103 | CANADAY7 115.00 | 640161 | ELMCRK_7 115.00 | 0 |  | 1 | 13WP | 80 | 80 | 88 | 92.6784 | 92.6784 | 103.6264 | [7 empty] | CATEGORYB | SINGLE | CROOKED CREEK - RIVERDALE 230KV CKT 1 | 0 | 640093 | C.CREEK4 230.00 | 640330 | RIVERDL4 230.00 | 0 |  | 1 |  |  |  | NPPD | Cherry Co 345 kV Terminal Upgrades | Build new Cherry County 345 kV Substation. | [5 empty] | 72 | [47 empty] | 2013-10-01 | 2018-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1675517WP | FROM->TO | CANADAY - ELM CREEK 115KV CKT 1 | REL | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640103 | CANADAY7 115.00 | 640161 | ELMCRK_7 115.00 | 0 |  | 1 | 17WP | 80 | 80 | 88 | 92.8097 | 92.8097 | 106.5212 | [7 empty] | CATEGORYB | SINGLE | CROOKED CREEK - RIVERDALE 230KV CKT 1 | 0 | 640093 | C.CREEK4 230.00 | 640330 | RIVERDL4 230.00 | 0 |  | 1 |  |  |  | NPPD | Cherry Co - Gentleman 345 kV Ckt1 | Build new 345 kV Transmission Line from GGS 345 kV Substation to a new Cherry County 345 kV Substation (76 miles). | [5 empty] | 72 | 72 | Y | [45 empty] | 2013-10-01 | 2018-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1675517WP | FROM->TO | CANADAY - ELM CREEK 115KV CKT 1 | REL | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640103 | CANADAY7 115.00 | 640161 | ELMCRK_7 115.00 | 0 |  | 1 | 17WP | 80 | 80 | 88 | 92.8097 | 92.8097 | 106.5212 | [7 empty] | CATEGORYB | SINGLE | CROOKED CREEK - RIVERDALE 230KV CKT 1 | 0 | 640093 | C.CREEK4 230.00 | 640330 | RIVERDL4 230.00 | 0 |  | 1 |  |  |  | NPPD | Cherry Co - Holt Co 345 kV Ckt1 | Build new 345 kV Transmission Line from new Cherry County 345 kV Substation to new 345 kV Holt County Substation. (Estimated 146 miles). | [5 empty] | 72 | [47 empty] | 2013-10-01 | 2018-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1675517WP | FROM->TO | CANADAY - ELM CREEK 115KV CKT 1 | REL | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640103 | CANADAY7 115.00 | 640161 | ELMCRK_7 115.00 | 0 |  | 1 | 17WP | 80 | 80 | 88 | 92.8097 | 92.8097 | 106.5212 | [7 empty] | CATEGORYB | SINGLE | CROOKED CREEK - RIVERDALE 230KV CKT 1 | 0 | 640093 | C.CREEK4 230.00 | 640330 | RIVERDL4 230.00 | 0 |  | 1 |  |  |  | NPPD | Cherry Co 345 kV Terminal Upgrades | Build new Cherry County 345 kV Substation. | [5 empty] | 72 | [47 empty] | 2013-10-01 | 2018-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1825513SP | FROM->TO | CANTON - OKEENE 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-IM | 0 | 520843 | CANTON-2 69.000 | 521015 | OKEENE 2 69.000 | 0 |  | 1 | 13SP | 48 | 48 | 48 | 107.7 | 107.6529 | 111.8917 | [7 empty] | CATEGORYB | SINGLE | CEDARDALE - MOORELAND 138KV CKT 1 | 0 | 520848 | CEDRDAL4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 |  |  |  | WFEC | CANTON - OKEENE 69KV CKT 1 | Reset CT | 53 | 65 |  |  |  | 12 | 12 | [5 empty] | 150000 | 2012-12-05 | [39 empty] | 2013-06-01 | 2015-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1835513SP | FROM->TO | CANTON - OKEENE 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-IM | 0 | 520843 | CANTON-2 69.000 | 521015 | OKEENE 2 69.000 | 0 |  | 1 | 13SP | 48 | 48 | 48 | 105.9 | 105.941 | 111.2429 | [7 empty] | CATEGORYB | SINGLE | CEDARDALE - OKEENE 138KV CKT 1 | 0 | 520848 | CEDRDAL4 138.00 | 521016 | OKEENE 4 138.00 | 0 |  | 1 |  |  |  | WFEC | CANTON - OKEENE 69KV CKT 1 | Reset CT | 53 | 65 |  |  |  | 12 | 12 | [5 empty] | 150000 | 2012-12-05 | [39 empty] | 2013-06-01 | 2015-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T9195513SP | FROM->TO | CANTON - OKEENE 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-IM | 0 | 520843 | CANTON-2 69.000 | 521015 | OKEENE 2 69.000 | 0 |  | 1 | 13SP | 48 | 48 | 48 | 97.4198 | 97.4198 | 103.0451 | [7 empty] | CATEGORYB | SINGLE | WOODWARD DISTRICT EHV (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  |  |  | WFEC | CANTON - OKEENE 69KV CKT 1 | Reset CT | 53 | 65 |  |  |  | 12 | 12 | [5 empty] | 150000 | 2012-12-05 | [39 empty] | 2013-06-01 | 2015-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T765513WP | FROM->TO | CANTON - OKEENE 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-IM | 0 | 520843 | CANTON-2 69.000 | 521015 | OKEENE 2 69.000 | 0 |  | 1 | 13WP | 48 | 48 | 48 | 107.3 | 107.2746 | 111.7303 | [7 empty] | CATEGORYB | SINGLE | CEDARDALE - MOORELAND 138KV CKT 1 | 0 | 520848 | CEDRDAL4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 |  |  |  | WFEC | CANTON - OKEENE 69KV CKT 1 | Reset CT | 53 | 65 |  |  |  | 12 | 12 | [5 empty] | 150000 | 2012-12-05 | [39 empty] | 2013-06-01 | 2015-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T775513WP | FROM->TO | CANTON - OKEENE 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-IM | 0 | 520843 | CANTON-2 69.000 | 521015 | OKEENE 2 69.000 | 0 |  | 1 | 13WP | 48 | 48 | 48 | 105.8839 | 105.8839 | 110.3325 | [7 empty] | CATEGORYB | SINGLE | CEDARDALE - OKEENE 138KV CKT 1 | 0 | 520848 | CEDRDAL4 138.00 | 521016 | OKEENE 4 138.00 | 0 |  | 1 |  |  |  | WFEC | CANTON - OKEENE 69KV CKT 1 | Reset CT | 53 | 65 |  |  |  | 12 | 12 | [5 empty] | 150000 | 2012-12-05 | [39 empty] | 2013-06-01 | 2015-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T5505513WP | FROM->TO | CANTON - OKEENE 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-IM | 0 | 520843 | CANTON-2 69.000 | 521015 | OKEENE 2 69.000 | 0 |  | 1 | 13WP | 48 | 48 | 48 | 103.6 | 103.596 | 109.4701 | [7 empty] | CATEGORYB | SINGLE | WOODWARD DISTRICT EHV (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  |  |  | WFEC | CANTON - OKEENE 69KV CKT 1 | Reset CT | 53 | 65 |  |  |  | 12 | 12 | [5 empty] | 150000 | 2012-12-05 | [39 empty] | 2013-06-01 | 2015-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1985517SP | FROM->TO | CANTON - OKEENE 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-IM | 0 | 520843 | CANTON-2 69.000 | 521015 | OKEENE 2 69.000 | 0 |  | 1 | 17SP | 48 | 48 | 48 | 87.7915 | 87.7915 | 102.0344 | [7 empty] | CATEGORYB | SINGLE | CEDARDALE - MOORELAND 138KV CKT 1 | 0 | 520848 | CEDRDAL4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 |  |  |  | WFEC | CANTON - OKEENE 69KV CKT 1 | Reset CT | 53 | 65 |  |  |  | 12 | 12 | [5 empty] | 150000 | 2012-12-05 | [39 empty] | 2013-06-01 | 2015-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1995517SP | FROM->TO | CANTON - OKEENE 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-IM | 0 | 520843 | CANTON-2 69.000 | 521015 | OKEENE 2 69.000 | 0 |  | 1 | 17SP | 48 | 48 | 48 | 86.2698 | 86.2698 | 100.4938 | [7 empty] | CATEGORYB | SINGLE | CEDARDALE - OKEENE 138KV CKT 1 | 0 | 520848 | CEDRDAL4 138.00 | 521016 | OKEENE 4 138.00 | 0 |  | 1 |  |  |  | WFEC | CANTON - OKEENE 69KV CKT 1 | Reset CT | 53 | 65 |  |  |  | 12 | 12 | [5 empty] | 150000 | 2012-12-05 | [39 empty] | 2013-06-01 | 2015-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T855517WP | FROM->TO | CANTON - OKEENE 69KV CKT 1 | S | WFEC | WFEC | AEP-OP | AEP-IM | 0 | 520843 | CANTON-2 69.000 | 521015 | OKEENE 2 69.000 | 0 |  | 1 | 17WP | 48 | 48 | 48 | 84.9456 | 84.9456 | 100.0903 | [7 empty] | CATEGORYB | SINGLE | CEDARDALE - MOORELAND 138KV CKT 1 | 0 | 520848 | CEDRDAL4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 |  |  |  | WFEC | CANTON - OKEENE 69KV CKT 1 | Reset CT | 53 | 65 |  |  |  | 12 | 12 | [5 empty] | 150000 | 2012-12-05 | [39 empty] | 2013-06-01 | 2015-06-01
2009-AGP2 | [10 empty] | CANTON - TALOGA 69KV CKT 1 | U | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521064 | TALOGA 2 69.000 | 520843 | CANTON-2 69.000 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | WFEC | CANTON - TALOGA 69KV CKT 1 | UPGRADE CANTON TO TALOGA TO 336.4 | 106 | 132 |  |  | 9.7 | 24 | 24 |  | 0.04013 | 0.16101 | 0.00252 | [42 empty] | 2011-06-01 | 2013-06-01
2009-AGP1 | [10 empty] | CHERRY6 230.00 - Harrington Station East Bus 230KV CKT 1 | U | SPS | SPS | SPS-AMA |  | 0 | 523977 |  | 524010 |  | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | SPS | CHERRY6 230.00 - Harrington Station East Bus 230KV CKT 1 | Replace wavetrap at Harrington East | [53 empty] | 2015-06-01 | 2015-06-01
GI | [10 empty] | CIRCLE - RICE_CO 230KV CKT 1 | U | WERE | MIDW |  |  | 0 | 560012 | RICECO 230.00 | 532871 | CIRCLE 6 230.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | MIDW | CIRCLE - RICE_CO 230KV CKT 1 | Convert from 115kV to 230kV operation | [53 empty] | 2012-10-01 | 2012-11-15
2011-AG2 | AFS9-ADD |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS7CCP1T725517SP | FROM->TO | CLARKCO - CLARKCO 345KV CKT 1 | EXP | SUNC | SUNC |  | SPS-MUNI | 0 | 560688 | CLARKCO 7 | 539800 | CLARKCO 7 | 0 |  | 1 | 17SP | 100 | 100 | 100 |  | 999 | 999 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-ADD |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS7CCP1T725517SP | FROM->TO | CLARKCO - CLARKCO 345KV CKT 1 | EXP | SUNC | SUNC |  | SPS-MUNI | 0 | 560688 | CLARKCO 7 | 539800 | CLARKCO 7 | 0 |  | 1 | 17SP | 100 | 100 | 100 |  | 999 | 999 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-ADD |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS7CCP1T725517SP | FROM->TO | CLARKCO - CLARKCO 345KV CKT 1 | EXP | SUNC | SUNC |  | SPS-MUNI | 0 | 560688 | CLARKCO 7 | 539800 | CLARKCO 7 | 0 |  | 1 | 17SP | 100 | 100 | 100 |  | 999 | 999 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-ADD |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS7CCP1T725517SP | FROM->TO | CLARKCO - CLARKCO 345KV CKT 1 | EXP | SUNC | SUNC |  | SPS-MUNI | 0 | 560688 | CLARKCO 7 | 539800 | CLARKCO 7 | 0 |  | 1 | 17SP | 100 | 100 | 100 |  | 999 | 999 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-ADD |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS7CCP1T725517SP | FROM->TO | CLARKCO - CLARKCO 345KV CKT 1 | EXP | SUNC | SUNC |  | SPS-MUNI | 0 | 560688 | CLARKCO 7 | 539800 | CLARKCO 7 | 0 |  | 1 | 17SP | 100 | 100 | 100 |  | 999 | 999 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-ADD |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS7CCP1T725517SP | FROM->TO | CLARKCO - CLARKCO 345KV CKT 1 | EXP | SUNC | SUNC |  | SPS-MUNI | 0 | 560688 | CLARKCO 7 | 539800 | CLARKCO 7 | 0 |  | 1 | 17SP | 100 | 100 | 100 |  | 999 | 999 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-ADD |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS7CCP1T725517SP | FROM->TO | CLARKCO - CLARKCO 345KV CKT 1 | EXP | SUNC | SUNC |  | SPS-MUNI | 0 | 560688 | CLARKCO 7 | 539800 | CLARKCO 7 | 0 |  | 1 | 17SP | 100 | 100 | 100 |  | 999 | 999 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-ADD |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS7CCP1T725517SP | FROM->TO | CLARKCO - CLARKCO 345KV CKT 1 | EXP | SUNC | SUNC |  | SPS-MUNI | 0 | 560688 | CLARKCO 7 | 539800 | CLARKCO 7 | 0 |  | 1 | 17SP | 100 | 100 | 100 |  | 999 | 999 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-ADD |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS7CCP1T725517SP | FROM->TO | CLARKCO - CLARKCO 345KV CKT 1 | EXP | SUNC | SUNC |  | SPS-MUNI | 0 | 560688 | CLARKCO 7 | 539800 | CLARKCO 7 | 0 |  | 1 | 17SP | 100 | 100 | 100 |  | 999 | 999 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-ADD |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS7CCP1T725517SP | FROM->TO | CLARKCO - CLARKCO 345KV CKT 1 | EXP | SUNC | SUNC |  | SPS-MUNI | 0 | 560688 | CLARKCO 7 | 539800 | CLARKCO 7 | 0 |  | 1 | 17SP | 100 | 100 | 100 |  | 999 | 999 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-ADD |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS7CCP1T725517SP | FROM->TO | CLARKCO - CLARKCO 345KV CKT 1 | EXP | SUNC | SUNC |  | SPS-MUNI | 0 | 560688 | CLARKCO 7 | 539800 | CLARKCO 7 | 0 |  | 1 | 17SP | 100 | 100 | 100 |  | 999 | 999 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T14995513SP | TO->FROM | CLAY - SPRINGFIELD 161KV CKT 1 | S | SWPA | SPRM | EMINTH | SPRM > 69KV | 0 | 505492 | SPRGFLD5 161.00 | 549970 | CLAY 5161.00 | 0 |  | 1 | 13SP | 167 | 167 | 0 | 94.685 | 94.685 | 101.1367 | [7 empty] | CATEGORYB | NONSINGLE | AI03 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SWPA | CLAY - SPRINGFIELD 161KV CKT 1 SWPA #1 | Replace 600 amp disconnect switches at Springfield. | 189 | 189 | 234 | 234 | 0 | 12 | 6 | [5 empty] | 50000 | 2012-09-18 | [39 empty] | 2013-06-01 | 2015-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1625513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 114.3537 | 114.3537 | 122.5137 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 | Replace Wave Trap at Harper Substation |  | 110 |  |  |  | 18 | 18 | [5 empty] | 385244 | 2012-11-12 | [39 empty] | 2013-06-01 | 2014-12-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1625513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | S | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 114.3537 | 114.3537 | 122.5137 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | MKEC | CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | Rebuild MKEC portion of the 5.6 mile Clearwater-Milan Tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 5.6 | 24 | 24 | [5 empty] | 2501569 | 2011-12-07 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1625513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | S | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 114.3537 | 114.3537 | 122.5137 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | WERE | CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | Rebuild Westar portion of the Clearwater-Milan tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 6.1 | 24 | 24 | [5 empty] | 7951703 | 2011-11-15 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1625513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | S | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 114.3537 | 114.3537 | 122.5137 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | Reconductor 22.1 mile Harper to Milan Tap 138 kV line. | 261 | 314 |  |  | 22.1 | 36 | 36 | [5 empty] | 9613332 | 2011-12-02 | [38 empty] | 2020-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1625513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 114.3537 | 114.3537 | 122.5137 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1625513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 114.3537 | 114.3537 | 122.5137 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1625513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 114.3537 | 114.3537 | 122.5137 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1625513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 114.3537 | 114.3537 | 122.5137 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1625513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 114.3537 | 114.3537 | 122.5137 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1625513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 114.3537 | 114.3537 | 122.5137 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1625513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 114.3537 | 114.3537 | 122.5137 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1625513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 114.3537 | 114.3537 | 122.5137 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1625513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 114.3537 | 114.3537 | 122.5137 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1625513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 114.3537 | 114.3537 | 122.5137 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1625513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 114.3537 | 114.3537 | 122.5137 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1605513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 113.2 | 113.2053 | 121.4173 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 | Replace Wave Trap at Harper Substation |  | 110 |  |  |  | 18 | 18 | [5 empty] | 385244 | 2012-11-12 | [39 empty] | 2013-06-01 | 2014-12-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1605513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | S | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 113.2 | 113.2053 | 121.4173 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | MKEC | CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | Rebuild MKEC portion of the 5.6 mile Clearwater-Milan Tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 5.6 | 24 | 24 | [5 empty] | 2501569 | 2011-12-07 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1605513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | S | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 113.2 | 113.2053 | 121.4173 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | WERE | CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | Rebuild Westar portion of the Clearwater-Milan tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 6.1 | 24 | 24 | [5 empty] | 7951703 | 2011-11-15 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1605513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | S | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 113.2 | 113.2053 | 121.4173 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | Reconductor 22.1 mile Harper to Milan Tap 138 kV line. | 261 | 314 |  |  | 22.1 | 36 | 36 | [5 empty] | 9613332 | 2011-12-02 | [38 empty] | 2020-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1605513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 113.2 | 113.2053 | 121.4173 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1605513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 113.2 | 113.2053 | 121.4173 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1605513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 113.2 | 113.2053 | 121.4173 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1605513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 113.2 | 113.2053 | 121.4173 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1605513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 113.2 | 113.2053 | 121.4173 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1605513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 113.2 | 113.2053 | 121.4173 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1605513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 113.2 | 113.2053 | 121.4173 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1605513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 113.2 | 113.2053 | 121.4173 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1605513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 113.2 | 113.2053 | 121.4173 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1605513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 113.2 | 113.2053 | 121.4173 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1605513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 113.2 | 113.2053 | 121.4173 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1645513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 111.9 | 111.8996 | 118.9165 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 | Replace Wave Trap at Harper Substation |  | 110 |  |  |  | 18 | 18 | [5 empty] | 385244 | 2012-11-12 | [39 empty] | 2013-06-01 | 2014-12-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1645513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | S | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 111.9 | 111.8996 | 118.9165 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | MKEC | CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | Rebuild MKEC portion of the 5.6 mile Clearwater-Milan Tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 5.6 | 24 | 24 | [5 empty] | 2501569 | 2011-12-07 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1645513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | S | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 111.9 | 111.8996 | 118.9165 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | WERE | CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | Rebuild Westar portion of the Clearwater-Milan tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 6.1 | 24 | 24 | [5 empty] | 7951703 | 2011-11-15 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1645513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | S | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 111.9 | 111.8996 | 118.9165 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | Reconductor 22.1 mile Harper to Milan Tap 138 kV line. | 261 | 314 |  |  | 22.1 | 36 | 36 | [5 empty] | 9613332 | 2011-12-02 | [38 empty] | 2020-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1645513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 111.9 | 111.8996 | 118.9165 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1645513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 111.9 | 111.8996 | 118.9165 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1645513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 111.9 | 111.8996 | 118.9165 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1645513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 111.9 | 111.8996 | 118.9165 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1645513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 111.9 | 111.8996 | 118.9165 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1645513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 111.9 | 111.8996 | 118.9165 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1645513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 111.9 | 111.8996 | 118.9165 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1645513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 111.9 | 111.8996 | 118.9165 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1645513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 111.9 | 111.8996 | 118.9165 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1645513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 111.9 | 111.8996 | 118.9165 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1645513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 111.9 | 111.8996 | 118.9165 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2105514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 79.7549 | 111.3418 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 | Replace Wave Trap at Harper Substation |  | 110 |  |  |  | 18 | 18 | [5 empty] | 385244 | 2012-11-12 | [39 empty] | 2013-06-01 | 2014-12-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2105514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | S | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 79.7549 | 111.3418 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 |  |  |  | MKEC | CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | Rebuild MKEC portion of the 5.6 mile Clearwater-Milan Tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 5.6 | 24 | 24 | [5 empty] | 2501569 | 2011-12-07 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2105514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | S | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 79.7549 | 111.3418 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 |  |  |  | WERE | CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | Rebuild Westar portion of the Clearwater-Milan tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 6.1 | 24 | 24 | [5 empty] | 7951703 | 2011-11-15 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2105514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | S | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 79.7549 | 111.3418 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | Reconductor 22.1 mile Harper to Milan Tap 138 kV line. | 261 | 314 |  |  | 22.1 | 36 | 36 | [5 empty] | 9613332 | 2011-12-02 | [38 empty] | 2020-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2105514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 79.7549 | 111.3418 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2105514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 79.7549 | 111.3418 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2105514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 79.7549 | 111.3418 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2105514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 79.7549 | 111.3418 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2105514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 79.7549 | 111.3418 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2105514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 79.7549 | 111.3418 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2105514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 79.7549 | 111.3418 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2105514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 79.7549 | 111.3418 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2105514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 79.7549 | 111.3418 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2105514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 79.7549 | 111.3418 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2105514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 79.7549 | 111.3418 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3725514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 86.0773 | 107.9805 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 | Replace Wave Trap at Harper Substation |  | 110 |  |  |  | 18 | 18 | [5 empty] | 385244 | 2012-11-12 | [39 empty] | 2013-06-01 | 2014-12-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3725514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | S | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 86.0773 | 107.9805 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | MKEC | CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | Rebuild MKEC portion of the 5.6 mile Clearwater-Milan Tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 5.6 | 24 | 24 | [5 empty] | 2501569 | 2011-12-07 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3725514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | S | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 86.0773 | 107.9805 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | WERE | CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | Rebuild Westar portion of the Clearwater-Milan tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 6.1 | 24 | 24 | [5 empty] | 7951703 | 2011-11-15 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3725514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | S | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 86.0773 | 107.9805 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | Reconductor 22.1 mile Harper to Milan Tap 138 kV line. | 261 | 314 |  |  | 22.1 | 36 | 36 | [5 empty] | 9613332 | 2011-12-02 | [38 empty] | 2020-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3725514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 86.0773 | 107.9805 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3725514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 86.0773 | 107.9805 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3725514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 86.0773 | 107.9805 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3725514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 86.0773 | 107.9805 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3725514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 86.0773 | 107.9805 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3725514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 86.0773 | 107.9805 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3725514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 86.0773 | 107.9805 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3725514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 86.0773 | 107.9805 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3725514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 86.0773 | 107.9805 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3725514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 86.0773 | 107.9805 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3725514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 86.0773 | 107.9805 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3695514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 84.7064 | 106.5448 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 | Replace Wave Trap at Harper Substation |  | 110 |  |  |  | 18 | 18 | [5 empty] | 385244 | 2012-11-12 | [39 empty] | 2013-06-01 | 2014-12-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3695514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | S | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 84.7064 | 106.5448 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | MKEC | CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | Rebuild MKEC portion of the 5.6 mile Clearwater-Milan Tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 5.6 | 24 | 24 | [5 empty] | 2501569 | 2011-12-07 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3695514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | S | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 84.7064 | 106.5448 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | WERE | CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | Rebuild Westar portion of the Clearwater-Milan tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 6.1 | 24 | 24 | [5 empty] | 7951703 | 2011-11-15 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3695514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | S | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 84.7064 | 106.5448 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | Reconductor 22.1 mile Harper to Milan Tap 138 kV line. | 261 | 314 |  |  | 22.1 | 36 | 36 | [5 empty] | 9613332 | 2011-12-02 | [38 empty] | 2020-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3695514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 84.7064 | 106.5448 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3695514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 84.7064 | 106.5448 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3695514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 84.7064 | 106.5448 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3695514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 84.7064 | 106.5448 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3695514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 84.7064 | 106.5448 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3695514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 84.7064 | 106.5448 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3695514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 84.7064 | 106.5448 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3695514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 84.7064 | 106.5448 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3695514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 84.7064 | 106.5448 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3695514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 84.7064 | 106.5448 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3695514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 |  | 84.7064 | 106.5448 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2007-AG3 | [10 empty] | CLIFTON - GREENLEAF 115KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539656 | CLIFTON3 115.00 | 539665 | GRNLEAF3 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | MKEC | CLIFTON - GREENLEAF 115KV CKT 1 | Rebuild 14.4 miles | [53 empty] | 2011-06-01 | 2013-06-01
2007-AG3 | [10 empty] | DEARING 138KV | U | WERE |  | SEAST |  |  | 533002 | DEARING4 138.00 | [20 empty] | BASECASE | BASE CASE | [11 empty] | WERE | DEARING 138KV Capacitor | Dearing 138 kV 20 MVAR Capacitor Addition | [53 empty] | 2012-06-01 | 2012-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1285513WP | FROM->TO | EDWARDSVILLE (EDWRDV4X) 161/115/12.47KV TRANSFORMER CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 1 | 533238 | EDWARVL3 115.00 | 532912 | EDWRDVL5 161.00 | 532940 | EDWRDVL1 12.470 | 1 | 13WP | 168 | 184.8 | 210 | 91.2827 | 91.2827 | 101.5028 | [7 empty] | CATEGORYB | SINGLE | 87th STREET - CRAIG 345KV CKT 1 | 0 | 532775 | 87TH 7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  |  |  | KACP | IATAN - NASHUA 345KV CKT 1 | Tap Nashua 345kV bus in Hawthorn - St. Joseph 345 kV line. Build new 345 kV line from Iatan to Nashua,Add Nashua 345/161 kV | [53 empty] | 2013-06-01 | 2015-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1855517SP | FROM->TO | EL PASO - FARBER 138KV CKT 1 | CP | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 | 17SP | 160 | 168 | 0 | 98.2036 | 98.2036 | 100.2475 | [7 empty] | CATEGORYB | SINGLE | KILDARE4 - WHITE EAGLE 138KV CKT 1 | 0 | 514760 | KILDARE4 138.00 | 514761 | WHEAGLE4 138.00 | 0 |  | 1 |  |  |  | WERE | EL PASO - FARBER 138KV CKT 1 | Tear down / Rebuild 3.1 miles with dual 477 ACSR | 286 | 286 | 286 | 286 | 3.1 |  |  |  | 0.001395 | 0.01178 | 0.00372 |  | 4790473 | 2011-11-16 | [39 empty] | 2014-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T9165513SP | TO->FROM | EL RENO - ROMAN NOSE 138KV CKT 1 | EXP | OKGE | OKGE |  |  | 0 | 514823 | ROMNOSE4 138.00 | 514819 | EL-RENO4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 | 99.3 | 99.2634 | 103.1458 | [7 empty] | CATEGORYB | SINGLE | WOODWARD DISTRICT EHV (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T9165513SP | TO->FROM | EL RENO - ROMAN NOSE 138KV CKT 1 | EXP | OKGE | OKGE |  |  | 0 | 514823 | ROMNOSE4 138.00 | 514819 | EL-RENO4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 | 99.3 | 99.2634 | 103.1458 | [7 empty] | CATEGORYB | SINGLE | WOODWARD DISTRICT EHV (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T9165513SP | TO->FROM | EL RENO - ROMAN NOSE 138KV CKT 1 | EXP | OKGE | OKGE |  |  | 0 | 514823 | ROMNOSE4 138.00 | 514819 | EL-RENO4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 | 99.3 | 99.2634 | 103.1458 | [7 empty] | CATEGORYB | SINGLE | WOODWARD DISTRICT EHV (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T9165513SP | TO->FROM | EL RENO - ROMAN NOSE 138KV CKT 1 | EXP | OKGE | OKGE |  |  | 0 | 514823 | ROMNOSE4 138.00 | 514819 | EL-RENO4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 | 99.3 | 99.2634 | 103.1458 | [7 empty] | CATEGORYB | SINGLE | WOODWARD DISTRICT EHV (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1775513SP | TO->FROM | EL RENO - ROMAN NOSE 138KV CKT 1 | EXP | OKGE | OKGE |  |  | 0 | 514823 | ROMNOSE4 138.00 | 514819 | EL-RENO4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 | 99.2 | 99.227 | 103.1089 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WOODWARD DISTRICT EHV 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1775513SP | TO->FROM | EL RENO - ROMAN NOSE 138KV CKT 1 | EXP | OKGE | OKGE |  |  | 0 | 514823 | ROMNOSE4 138.00 | 514819 | EL-RENO4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 | 99.2 | 99.227 | 103.1089 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WOODWARD DISTRICT EHV 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1775513SP | TO->FROM | EL RENO - ROMAN NOSE 138KV CKT 1 | EXP | OKGE | OKGE |  |  | 0 | 514823 | ROMNOSE4 138.00 | 514819 | EL-RENO4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 | 99.2 | 99.227 | 103.1089 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WOODWARD DISTRICT EHV 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1775513SP | TO->FROM | EL RENO - ROMAN NOSE 138KV CKT 1 | EXP | OKGE | OKGE |  |  | 0 | 514823 | ROMNOSE4 138.00 | 514819 | EL-RENO4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 | 99.2 | 99.227 | 103.1089 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WOODWARD DISTRICT EHV 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-ADD |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS9ADD1T1985513SP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 13SP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-ADD |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS9ADD1T1985513SP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 13SP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-ADD |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS9ADD1T1985513SP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 13SP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-ADD |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS9ADD1T1985513SP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 13SP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-ADD |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS9ADD1T1985513WP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 13WP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-ADD |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS9ADD1T1985513WP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 13WP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-ADD |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS9ADD1T1985513WP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 13WP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-ADD |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS9ADD1T1985513WP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 13WP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2005-AG2 | [10 empty] | EXPLORER GLENPOOL - RIVERSIDE STATION 138KV CKT 1 AEPW | U | AEPW | OKGE |  |  | 0 | 509783 | R.S.S.-4 138 | 515248 | EXPLGLN4 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | AEPW | EXPLORER GLENPOOL - RIVERSIDE STATION 138KV CKT 1 AEPW | Reconductor 1.82 miles with ACCC. Replace wave trap jumpers at Riverside. | [53 empty] | 2009-06-01 | 2009-06-01
2005-AG2 | [10 empty] | EXPLORER GLENPOOL - RIVERSIDE STATION 138KV CKT 1 OKGE | U | AEPW | OKGE |  |  | 0 | 509783 | R.S.S.-4 138 | 515248 | EXPLGLN4 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | OKGE | EXPLORER GLENPOOL - RIVERSIDE STATION 138KV CKT 1 OKGE | Reconductor 1.82 miles line with Drake ACCC/TW. | [53 empty] | 2009-06-01 | 2009-06-01
2007-AG3 | [10 empty] | FLATRDG3 138.00 - MEDICINE LODGE 138KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539674 | MED-LDG4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | MKEC | FLATRDG3 138.00 - MEDICINE LODGE 138KV CKT 1 | Rebuild 8.05 mile line | [53 empty] | 2009-12-01 | 2013-06-01
2007-AG3 | [10 empty] | FLATRDG3 138.00 - HARPER 138KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 |  |  | 24.15 | 24 | 24 | [46 empty] | 2009-12-01 | 2013-06-15
2011-AG2 | AFS9-ADD |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS9ADD1T2005513SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-ADD |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS9ADD1T2005513SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-ADD |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS9ADD1T2005513SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-ADD |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS9ADD1T2005513SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T9145513SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 | 117.5 | 117.4994 | 118.2708 | [7 empty] | CATEGORYB | SINGLE | WOODWARD DISTRICT EHV (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T9145513SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 | 117.5 | 117.4994 | 118.2708 | [7 empty] | CATEGORYB | SINGLE | WOODWARD DISTRICT EHV (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T9145513SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 | 117.5 | 117.4994 | 118.2708 | [7 empty] | CATEGORYB | SINGLE | WOODWARD DISTRICT EHV (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T9145513SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 | 117.5 | 117.4994 | 118.2708 | [7 empty] | CATEGORYB | SINGLE | WOODWARD DISTRICT EHV (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1755513SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 | 117.5 | 117.4796 | 118.2507 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WOODWARD DISTRICT EHV 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1755513SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 | 117.5 | 117.4796 | 118.2507 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WOODWARD DISTRICT EHV 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1755513SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 | 117.5 | 117.4796 | 118.2507 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WOODWARD DISTRICT EHV 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1755513SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 | 117.5 | 117.4796 | 118.2507 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WOODWARD DISTRICT EHV 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-ADD |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS9ADD1T2005513WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 13WP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-ADD |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS9ADD1T2005513WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 13WP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-ADD |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS9ADD1T2005513WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 13WP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-ADD |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS9ADD1T2005513WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 13WP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
GEN | [10 empty] | FT RANDAL - MADISONCO 230.00 230KV CKT 1 | U | NPPD | WAPA | NPPD_686 | WAPA_1604 | 0 | 560006 | MADISONCO 230.00 | 652509 | FTRANDL4 230.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | NPPD | FT RANDAL - MADISONCO 230.00 230KV CKT 1 | Raise structures and line clearances as necessary to re-rate the transmission line to 320MVA | [53 empty] | 2013-10-01 | 2014-11-01
2006-AG1 | [10 empty] | FT SUPPLY 138/69KV TRANSFORMER CKT 1 | U | WFEC | WFEC |  |  | 1 | 520920 | FTSUPLY4 138 | 520919 | FTSUPLY269.0 | 521182 |  | 2 | [15 empty] | BASECASE | BASE CASE | [11 empty] | WFEC | FT SUPPLY 138/69KV TRANSFORMER CKT 1 | Install 2nd 70 MVA auto at Ft Supply | [53 empty] | 2006-12-01 | 2008-06-01
2009-AGP1 | [10 empty] | APACHE CO 138.00 - PARADISE 138KV CKT 1 | U | WFEC | WFEC | AEP-OP-I | AEP-KP | 0 | 521129 | APACHE CO 138.00 | 521024 | PARADSE4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | WFEC | APACHE CO 138.00 - PARADISE 138KV CKT 1 | Upgrade Paradise to APACHE CO to 1113 | [53 empty] | 2010-06-01 | 2013-06-01
2011-AG2 | AFS9-ADD |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS9ADD1T2015513SP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | EXP | WFEC | OKGE | ENID |  | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 13SP | 152 | 152 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-ADD |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS9ADD1T2015513SP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | EXP | WFEC | OKGE | ENID |  | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 13SP | 152 | 152 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-ADD |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS9ADD1T2015513SP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | EXP | WFEC | OKGE | ENID |  | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 13SP | 152 | 152 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-ADD |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS9ADD1T2015513SP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | EXP | WFEC | OKGE | ENID |  | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 13SP | 152 | 152 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T9155513SP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | EXP | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 13SP | 152 | 152 | 0 | 100 | 100.0282 | 102.5753 | [7 empty] | CATEGORYB | SINGLE | WOODWARD DISTRICT EHV (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T9155513SP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | EXP | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 13SP | 152 | 152 | 0 | 100 | 100.0282 | 102.5753 | [7 empty] | CATEGORYB | SINGLE | WOODWARD DISTRICT EHV (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T9155513SP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | EXP | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 13SP | 152 | 152 | 0 | 100 | 100.0282 | 102.5753 | [7 empty] | CATEGORYB | SINGLE | WOODWARD DISTRICT EHV (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T9155513SP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | EXP | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 13SP | 152 | 152 | 0 | 100 | 100.0282 | 102.5753 | [7 empty] | CATEGORYB | SINGLE | WOODWARD DISTRICT EHV (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1765513SP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | EXP | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 13SP | 152 | 152 | 0 | 100 | 100.0194 | 102.5667 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WOODWARD DISTRICT EHV 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1765513SP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | EXP | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 13SP | 152 | 152 | 0 | 100 | 100.0194 | 102.5667 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WOODWARD DISTRICT EHV 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1765513SP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | EXP | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 13SP | 152 | 152 | 0 | 100 | 100.0194 | 102.5667 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WOODWARD DISTRICT EHV 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1765513SP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | EXP | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 13SP | 152 | 152 | 0 | 100 | 100.0194 | 102.5667 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WOODWARD DISTRICT EHV 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-ADD |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS9ADD1T685513WP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | EXP | WFEC | OKGE | ENID |  | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 13WP | 152 | 152 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-ADD |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS9ADD1T685513WP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | EXP | WFEC | OKGE | ENID |  | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 13WP | 152 | 152 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-ADD |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS9ADD1T685513WP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | EXP | WFEC | OKGE | ENID |  | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 13WP | 152 | 152 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-ADD |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS9ADD1T685513WP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | EXP | WFEC | OKGE | ENID |  | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 13WP | 152 | 152 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T5465513WP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | EXP | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 13WP | 152 | 152 | 0 | 105.5661 | 105.5661 | 108.3139 | [7 empty] | CATEGORYB | SINGLE | WOODWARD DISTRICT EHV (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T5465513WP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | EXP | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 13WP | 152 | 152 | 0 | 105.5661 | 105.5661 | 108.3139 | [7 empty] | CATEGORYB | SINGLE | WOODWARD DISTRICT EHV (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T5465513WP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | EXP | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 13WP | 152 | 152 | 0 | 105.5661 | 105.5661 | 108.3139 | [7 empty] | CATEGORYB | SINGLE | WOODWARD DISTRICT EHV (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T5465513WP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | EXP | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 13WP | 152 | 152 | 0 | 105.5661 | 105.5661 | 108.3139 | [7 empty] | CATEGORYB | SINGLE | WOODWARD DISTRICT EHV (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T695513WP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | EXP | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 13WP | 152 | 152 | 0 | 105.6 | 105.5617 | 108.2733 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WOODWARD DISTRICT EHV 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T695513WP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | EXP | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 13WP | 152 | 152 | 0 | 105.6 | 105.5617 | 108.2733 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WOODWARD DISTRICT EHV 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T695513WP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | EXP | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 13WP | 152 | 152 | 0 | 105.6 | 105.5617 | 108.2733 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WOODWARD DISTRICT EHV 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T695513WP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | EXP | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 13WP | 152 | 152 | 0 | 105.6 | 105.5617 | 108.2733 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WOODWARD DISTRICT EHV 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
GEN | [10 empty] | GRACMNT4 138.00 - WASHITA 138KV CKT 2 OKGE | U | WFEC | OKGE | AEP-CS | ARDMORE | 0 | 521089 | WASHITA4 138.00 | 515802 | GRACMNT4 138.00 | 0 |  | 2 | [15 empty] | BASECASE | BASE CASE | [11 empty] | OKGE | GRACMNT4 138.00 - WASHITA 138KV CKT 2 OKGE | Build 138kV Terminal. | [53 empty] | 2012-01-01 | 2012-01-01
GEN | [10 empty] | GRACMNT4 138.00 - WASHITA 138KV CKT 2 WFEC | U | WFEC | OKGE | AEP-CS | ARDMORE | 0 | 521089 | WASHITA4 138.00 | 515802 | GRACMNT4 138.00 | 0 |  | 2 | [15 empty] | BASECASE | BASE CASE | [11 empty] | WFEC | GRACMNT4 138.00 - WASHITA 138KV CKT 2 WFEC | Build approximately 6 miles of 138kV. | [53 empty] | 2012-01-01 | 2012-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2045513WP | TO->FROM | GRAND ISLAND - SWEETWATER 345KV CKT 1 | REL | NPPD | NPPD | NPPD_686 | WAPA_1606 | 0 | 640374 | SWEET W3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 | 13WP | 717 | 717 | 789 | 96.3 | 96.2683 | 102.7404 | [7 empty] | CATEGORYB | SINGLE | AXTELL - SWEETWATER 345KV CKT 1 | 0 | 640065 | AXTELL 3 345.00 | 640374 | SWEET W3 345.00 | 0 |  | 1 |  |  |  | NPPD | Cherry Co - Gentleman 345 kV Ckt1 | Build new 345 kV Transmission Line from GGS 345 kV Substation to a new Cherry County 345 kV Substation (76 miles). | [5 empty] | 72 | 72 | Y | [45 empty] | 2013-10-01 | 2018-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2045513WP | TO->FROM | GRAND ISLAND - SWEETWATER 345KV CKT 1 | REL | NPPD | NPPD | NPPD_686 | WAPA_1606 | 0 | 640374 | SWEET W3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 | 13WP | 717 | 717 | 789 | 96.3 | 96.2683 | 102.7404 | [7 empty] | CATEGORYB | SINGLE | AXTELL - SWEETWATER 345KV CKT 1 | 0 | 640065 | AXTELL 3 345.00 | 640374 | SWEET W3 345.00 | 0 |  | 1 |  |  |  | NPPD | Cherry Co - Holt Co 345 kV Ckt1 | Build new 345 kV Transmission Line from new Cherry County 345 kV Substation to new 345 kV Holt County Substation. (Estimated 146 miles). | [5 empty] | 72 | [47 empty] | 2013-10-01 | 2018-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2045513WP | TO->FROM | GRAND ISLAND - SWEETWATER 345KV CKT 1 | REL | NPPD | NPPD | NPPD_686 | WAPA_1606 | 0 | 640374 | SWEET W3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 | 13WP | 717 | 717 | 789 | 96.3 | 96.2683 | 102.7404 | [7 empty] | CATEGORYB | SINGLE | AXTELL - SWEETWATER 345KV CKT 1 | 0 | 640065 | AXTELL 3 345.00 | 640374 | SWEET W3 345.00 | 0 |  | 1 |  |  |  | NPPD | Cherry Co 345 kV Terminal Upgrades | Build new Cherry County 345 kV Substation. | [5 empty] | 72 | [47 empty] | 2013-10-01 | 2018-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1635517WP | TO->FROM | GRAND ISLAND - SWEETWATER 345KV CKT 1 | REL | NPPD | NPPD | NPPD_686 | WAPA_1606 | 0 | 640374 | SWEET W3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 | 17WP | 717 | 717 | 789 | 96.3561 | 96.3561 | 107.3334 | [7 empty] | CATEGORYB | SINGLE | AXTELL - SWEETWATER 345KV CKT 1 | 0 | 640065 | AXTELL 3 345.00 | 640374 | SWEET W3 345.00 | 0 |  | 1 |  |  |  | NPPD | Cherry Co - Gentleman 345 kV Ckt1 | Build new 345 kV Transmission Line from GGS 345 kV Substation to a new Cherry County 345 kV Substation (76 miles). | [5 empty] | 72 | 72 | Y | [45 empty] | 2013-10-01 | 2018-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1635517WP | TO->FROM | GRAND ISLAND - SWEETWATER 345KV CKT 1 | REL | NPPD | NPPD | NPPD_686 | WAPA_1606 | 0 | 640374 | SWEET W3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 | 17WP | 717 | 717 | 789 | 96.3561 | 96.3561 | 107.3334 | [7 empty] | CATEGORYB | SINGLE | AXTELL - SWEETWATER 345KV CKT 1 | 0 | 640065 | AXTELL 3 345.00 | 640374 | SWEET W3 345.00 | 0 |  | 1 |  |  |  | NPPD | Cherry Co - Holt Co 345 kV Ckt1 | Build new 345 kV Transmission Line from new Cherry County 345 kV Substation to new 345 kV Holt County Substation. (Estimated 146 miles). | [5 empty] | 72 | [47 empty] | 2013-10-01 | 2018-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1635517WP | TO->FROM | GRAND ISLAND - SWEETWATER 345KV CKT 1 | REL | NPPD | NPPD | NPPD_686 | WAPA_1606 | 0 | 640374 | SWEET W3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 | 17WP | 717 | 717 | 789 | 96.3561 | 96.3561 | 107.3334 | [7 empty] | CATEGORYB | SINGLE | AXTELL - SWEETWATER 345KV CKT 1 | 0 | 640065 | AXTELL 3 345.00 | 640374 | SWEET W3 345.00 | 0 |  | 1 |  |  |  | NPPD | Cherry Co 345 kV Terminal Upgrades | Build new Cherry County 345 kV Substation. | [5 empty] | 72 | [47 empty] | 2013-10-01 | 2018-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1625517WP | TO->FROM | GRAND ISLAND - SWEETWATER 345KV CKT 1 | REL | NPPD | NPPD | NPPD_686 | WAPA_1606 | 0 | 640374 | SWEET W3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 | 17WP | 717 | 717 | 789 | 85.9336 | 85.9336 | 101.552 | [7 empty] | CATEGORYB | SINGLE | AXTELL - PAULINE 345KV CKT 1 | 0 | 640065 | AXTELL 3 345.00 | 640312 | PAULINE3 345.00 | 0 |  | 1 |  |  |  | NPPD | Cherry Co - Gentleman 345 kV Ckt1 | Build new 345 kV Transmission Line from GGS 345 kV Substation to a new Cherry County 345 kV Substation (76 miles). | [5 empty] | 72 | 72 | Y | [45 empty] | 2013-10-01 | 2018-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1625517WP | TO->FROM | GRAND ISLAND - SWEETWATER 345KV CKT 1 | REL | NPPD | NPPD | NPPD_686 | WAPA_1606 | 0 | 640374 | SWEET W3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 | 17WP | 717 | 717 | 789 | 85.9336 | 85.9336 | 101.552 | [7 empty] | CATEGORYB | SINGLE | AXTELL - PAULINE 345KV CKT 1 | 0 | 640065 | AXTELL 3 345.00 | 640312 | PAULINE3 345.00 | 0 |  | 1 |  |  |  | NPPD | Cherry Co - Holt Co 345 kV Ckt1 | Build new 345 kV Transmission Line from new Cherry County 345 kV Substation to new 345 kV Holt County Substation. (Estimated 146 miles). | [5 empty] | 72 | [47 empty] | 2013-10-01 | 2018-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1625517WP | TO->FROM | GRAND ISLAND - SWEETWATER 345KV CKT 1 | REL | NPPD | NPPD | NPPD_686 | WAPA_1606 | 0 | 640374 | SWEET W3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 | 17WP | 717 | 717 | 789 | 85.9336 | 85.9336 | 101.552 | [7 empty] | CATEGORYB | SINGLE | AXTELL - PAULINE 345KV CKT 1 | 0 | 640065 | AXTELL 3 345.00 | 640312 | PAULINE3 345.00 | 0 |  | 1 |  |  |  | NPPD | Cherry Co 345 kV Terminal Upgrades | Build new Cherry County 345 kV Substation. | [5 empty] | 72 | [47 empty] | 2013-10-01 | 2018-01-01
2008-AGP1 | [10 empty] | GREENLEAF - KNOB HILL 115KV CKT 1 | U | SUNC | WERE |  | NCENTRAL | 0 | 539665 | GRNLEAF3 115.00 | 533332 | KNOB HL3 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | MKEC | GREENLEAF - KNOB HILL 115KV CKT 1 MKEC | Rebuild 43.5% Ownership of 20.9 miles | [53 empty] | 2013-06-01 | 2013-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3935513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 111.5988 | 111.5988 | 121.088 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 | Replace Wave Trap at Harper Substation |  | 110 |  |  |  | 18 | 18 | [5 empty] | 385244 | 2012-11-12 | [39 empty] | 2013-06-01 | 2014-12-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3935513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 111.5988 | 111.5988 | 121.088 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | MKEC | CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | Rebuild MKEC portion of the 5.6 mile Clearwater-Milan Tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 5.6 | 24 | 24 | [5 empty] | 2501569 | 2011-12-07 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3935513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 111.5988 | 111.5988 | 121.088 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | WERE | CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | Rebuild Westar portion of the Clearwater-Milan tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 6.1 | 24 | 24 | [5 empty] | 7951703 | 2011-11-15 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3935513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 111.5988 | 111.5988 | 121.088 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | Reconductor 22.1 mile Harper to Milan Tap 138 kV line. | 261 | 314 |  |  | 22.1 | 36 | 36 | [5 empty] | 9613332 | 2011-12-02 | [38 empty] | 2020-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3935513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 111.5988 | 111.5988 | 121.088 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3935513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 111.5988 | 111.5988 | 121.088 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3935513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 111.5988 | 111.5988 | 121.088 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3935513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 111.5988 | 111.5988 | 121.088 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3935513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 111.5988 | 111.5988 | 121.088 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3935513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 111.5988 | 111.5988 | 121.088 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3935513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 111.5988 | 111.5988 | 121.088 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3935513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 111.5988 | 111.5988 | 121.088 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3935513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 111.5988 | 111.5988 | 121.088 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3935513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 111.5988 | 111.5988 | 121.088 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3935513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 111.5988 | 111.5988 | 121.088 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3915513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 110.1 | 110.0633 | 119.5495 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 | Replace Wave Trap at Harper Substation |  | 110 |  |  |  | 18 | 18 | [5 empty] | 385244 | 2012-11-12 | [39 empty] | 2013-06-01 | 2014-12-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3915513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 110.1 | 110.0633 | 119.5495 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | MKEC | CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | Rebuild MKEC portion of the 5.6 mile Clearwater-Milan Tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 5.6 | 24 | 24 | [5 empty] | 2501569 | 2011-12-07 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3915513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 110.1 | 110.0633 | 119.5495 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | WERE | CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | Rebuild Westar portion of the Clearwater-Milan tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 6.1 | 24 | 24 | [5 empty] | 7951703 | 2011-11-15 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3915513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 110.1 | 110.0633 | 119.5495 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | Reconductor 22.1 mile Harper to Milan Tap 138 kV line. | 261 | 314 |  |  | 22.1 | 36 | 36 | [5 empty] | 9613332 | 2011-12-02 | [38 empty] | 2020-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3915513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 110.1 | 110.0633 | 119.5495 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3915513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 110.1 | 110.0633 | 119.5495 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3915513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 110.1 | 110.0633 | 119.5495 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3915513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 110.1 | 110.0633 | 119.5495 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3915513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 110.1 | 110.0633 | 119.5495 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3915513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 110.1 | 110.0633 | 119.5495 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3915513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 110.1 | 110.0633 | 119.5495 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3915513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 110.1 | 110.0633 | 119.5495 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3915513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 110.1 | 110.0633 | 119.5495 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3915513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 110.1 | 110.0633 | 119.5495 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3915513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 110.1 | 110.0633 | 119.5495 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3945513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 108.5 | 108.469 | 118.0558 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 | Replace Wave Trap at Harper Substation |  | 110 |  |  |  | 18 | 18 | [5 empty] | 385244 | 2012-11-12 | [39 empty] | 2013-06-01 | 2014-12-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3945513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 108.5 | 108.469 | 118.0558 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | MKEC | CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | Rebuild MKEC portion of the 5.6 mile Clearwater-Milan Tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 5.6 | 24 | 24 | [5 empty] | 2501569 | 2011-12-07 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3945513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 108.5 | 108.469 | 118.0558 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | WERE | CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | Rebuild Westar portion of the Clearwater-Milan tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 6.1 | 24 | 24 | [5 empty] | 7951703 | 2011-11-15 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3945513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 108.5 | 108.469 | 118.0558 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | Reconductor 22.1 mile Harper to Milan Tap 138 kV line. | 261 | 314 |  |  | 22.1 | 36 | 36 | [5 empty] | 9613332 | 2011-12-02 | [38 empty] | 2020-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3945513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 108.5 | 108.469 | 118.0558 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3945513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 108.5 | 108.469 | 118.0558 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3945513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 108.5 | 108.469 | 118.0558 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3945513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 108.5 | 108.469 | 118.0558 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3945513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 108.5 | 108.469 | 118.0558 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3945513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 108.5 | 108.469 | 118.0558 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3945513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 108.5 | 108.469 | 118.0558 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3945513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 108.5 | 108.469 | 118.0558 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3945513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 108.5 | 108.469 | 118.0558 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3945513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 108.5 | 108.469 | 118.0558 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3945513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 108.5 | 108.469 | 118.0558 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1635513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 139.9859 | 139.9859 | 149.3381 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 | Replace Wave Trap at Harper Substation |  | 110 |  |  |  | 18 | 18 | [5 empty] | 385244 | 2012-11-12 | [39 empty] | 2013-06-01 | 2014-12-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1635513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 139.9859 | 139.9859 | 149.3381 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | MKEC | CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | Rebuild MKEC portion of the 5.6 mile Clearwater-Milan Tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 5.6 | 24 | 24 | [5 empty] | 2501569 | 2011-12-07 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1635513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 139.9859 | 139.9859 | 149.3381 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | WERE | CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | Rebuild Westar portion of the Clearwater-Milan tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 6.1 | 24 | 24 | [5 empty] | 7951703 | 2011-11-15 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1635513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 139.9859 | 139.9859 | 149.3381 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | Reconductor 22.1 mile Harper to Milan Tap 138 kV line. | 261 | 314 |  |  | 22.1 | 36 | 36 | [5 empty] | 9613332 | 2011-12-02 | [38 empty] | 2020-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1635513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 139.9859 | 139.9859 | 149.3381 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1635513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 139.9859 | 139.9859 | 149.3381 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1635513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 139.9859 | 139.9859 | 149.3381 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1635513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 139.9859 | 139.9859 | 149.3381 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1635513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 139.9859 | 139.9859 | 149.3381 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1635513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 139.9859 | 139.9859 | 149.3381 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1635513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 139.9859 | 139.9859 | 149.3381 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1635513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 139.9859 | 139.9859 | 149.3381 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1635513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 139.9859 | 139.9859 | 149.3381 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1635513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 139.9859 | 139.9859 | 149.3381 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1635513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 139.9859 | 139.9859 | 149.3381 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1615513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 138.6733 | 138.6733 | 148.0889 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 | Replace Wave Trap at Harper Substation |  | 110 |  |  |  | 18 | 18 | [5 empty] | 385244 | 2012-11-12 | [39 empty] | 2013-06-01 | 2014-12-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1615513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 138.6733 | 138.6733 | 148.0889 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | MKEC | CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | Rebuild MKEC portion of the 5.6 mile Clearwater-Milan Tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 5.6 | 24 | 24 | [5 empty] | 2501569 | 2011-12-07 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1615513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 138.6733 | 138.6733 | 148.0889 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | WERE | CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | Rebuild Westar portion of the Clearwater-Milan tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 6.1 | 24 | 24 | [5 empty] | 7951703 | 2011-11-15 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1615513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 138.6733 | 138.6733 | 148.0889 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | Reconductor 22.1 mile Harper to Milan Tap 138 kV line. | 261 | 314 |  |  | 22.1 | 36 | 36 | [5 empty] | 9613332 | 2011-12-02 | [38 empty] | 2020-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1615513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 138.6733 | 138.6733 | 148.0889 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1615513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 138.6733 | 138.6733 | 148.0889 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1615513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 138.6733 | 138.6733 | 148.0889 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1615513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 138.6733 | 138.6733 | 148.0889 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1615513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 138.6733 | 138.6733 | 148.0889 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1615513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 138.6733 | 138.6733 | 148.0889 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1615513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 138.6733 | 138.6733 | 148.0889 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1615513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 138.6733 | 138.6733 | 148.0889 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1615513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 138.6733 | 138.6733 | 148.0889 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1615513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 138.6733 | 138.6733 | 148.0889 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1615513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 138.6733 | 138.6733 | 148.0889 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1655513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 137.3 | 137.3229 | 145.4958 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 | Replace Wave Trap at Harper Substation |  | 110 |  |  |  | 18 | 18 | [5 empty] | 385244 | 2012-11-12 | [39 empty] | 2013-06-01 | 2014-12-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1655513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 137.3 | 137.3229 | 145.4958 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | MKEC | CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | Rebuild MKEC portion of the 5.6 mile Clearwater-Milan Tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 5.6 | 24 | 24 | [5 empty] | 2501569 | 2011-12-07 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1655513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 137.3 | 137.3229 | 145.4958 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | WERE | CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | Rebuild Westar portion of the Clearwater-Milan tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 6.1 | 24 | 24 | [5 empty] | 7951703 | 2011-11-15 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1655513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 137.3 | 137.3229 | 145.4958 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | Reconductor 22.1 mile Harper to Milan Tap 138 kV line. | 261 | 314 |  |  | 22.1 | 36 | 36 | [5 empty] | 9613332 | 2011-12-02 | [38 empty] | 2020-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1655513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 137.3 | 137.3229 | 145.4958 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1655513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 137.3 | 137.3229 | 145.4958 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1655513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 137.3 | 137.3229 | 145.4958 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1655513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 137.3 | 137.3229 | 145.4958 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1655513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 137.3 | 137.3229 | 145.4958 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1655513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 137.3 | 137.3229 | 145.4958 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1655513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 137.3 | 137.3229 | 145.4958 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1655513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 137.3 | 137.3229 | 145.4958 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1655513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 137.3 | 137.3229 | 145.4958 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1655513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 137.3 | 137.3229 | 145.4958 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1655513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 137.3 | 137.3229 | 145.4958 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8575513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 110.8076 | 110.8076 | 121.695 | [7 empty] | CATEGORYB | NONSINGLE | MIDW-CATB05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 | Replace Wave Trap at Harper Substation |  | 110 |  |  |  | 18 | 18 | [5 empty] | 385244 | 2012-11-12 | [39 empty] | 2013-06-01 | 2014-12-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8575513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 110.8076 | 110.8076 | 121.695 | [7 empty] | CATEGORYB | NONSINGLE | MIDW-CATB05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | Rebuild MKEC portion of the 5.6 mile Clearwater-Milan Tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 5.6 | 24 | 24 | [5 empty] | 2501569 | 2011-12-07 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8575513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 110.8076 | 110.8076 | 121.695 | [7 empty] | CATEGORYB | NONSINGLE | MIDW-CATB05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | Rebuild Westar portion of the Clearwater-Milan tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 6.1 | 24 | 24 | [5 empty] | 7951703 | 2011-11-15 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8575513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 110.8076 | 110.8076 | 121.695 | [7 empty] | CATEGORYB | NONSINGLE | MIDW-CATB05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | Reconductor 22.1 mile Harper to Milan Tap 138 kV line. | 261 | 314 |  |  | 22.1 | 36 | 36 | [5 empty] | 9613332 | 2011-12-02 | [38 empty] | 2020-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8575513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 110.8076 | 110.8076 | 121.695 | [7 empty] | CATEGORYB | NONSINGLE | MIDW-CATB05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8575513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 110.8076 | 110.8076 | 121.695 | [7 empty] | CATEGORYB | NONSINGLE | MIDW-CATB05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8575513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 110.8076 | 110.8076 | 121.695 | [7 empty] | CATEGORYB | NONSINGLE | MIDW-CATB05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8575513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 110.8076 | 110.8076 | 121.695 | [7 empty] | CATEGORYB | NONSINGLE | MIDW-CATB05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8575513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 110.8076 | 110.8076 | 121.695 | [7 empty] | CATEGORYB | NONSINGLE | MIDW-CATB05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8575513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 110.8076 | 110.8076 | 121.695 | [7 empty] | CATEGORYB | NONSINGLE | MIDW-CATB05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8575513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 110.8076 | 110.8076 | 121.695 | [7 empty] | CATEGORYB | NONSINGLE | MIDW-CATB05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8575513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 110.8076 | 110.8076 | 121.695 | [7 empty] | CATEGORYB | NONSINGLE | MIDW-CATB05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8575513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 110.8076 | 110.8076 | 121.695 | [7 empty] | CATEGORYB | NONSINGLE | MIDW-CATB05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8575513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 110.8076 | 110.8076 | 121.695 | [7 empty] | CATEGORYB | NONSINGLE | MIDW-CATB05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8575513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 110.8076 | 110.8076 | 121.695 | [7 empty] | CATEGORYB | NONSINGLE | MIDW-CATB05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T35513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 106.9 | 106.8641 | 116.252 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 | Replace Wave Trap at Harper Substation |  | 110 |  |  |  | 18 | 18 | [5 empty] | 385244 | 2012-11-12 | [39 empty] | 2013-06-01 | 2014-12-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T35513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 106.9 | 106.8641 | 116.252 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | Rebuild MKEC portion of the 5.6 mile Clearwater-Milan Tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 5.6 | 24 | 24 | [5 empty] | 2501569 | 2011-12-07 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T35513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 106.9 | 106.8641 | 116.252 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | Rebuild Westar portion of the Clearwater-Milan tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 6.1 | 24 | 24 | [5 empty] | 7951703 | 2011-11-15 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T35513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 106.9 | 106.8641 | 116.252 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | Reconductor 22.1 mile Harper to Milan Tap 138 kV line. | 261 | 314 |  |  | 22.1 | 36 | 36 | [5 empty] | 9613332 | 2011-12-02 | [38 empty] | 2020-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T35513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 106.9 | 106.8641 | 116.252 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T35513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 106.9 | 106.8641 | 116.252 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T35513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 106.9 | 106.8641 | 116.252 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T35513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 106.9 | 106.8641 | 116.252 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T35513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 106.9 | 106.8641 | 116.252 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T35513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 106.9 | 106.8641 | 116.252 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T35513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 106.9 | 106.8641 | 116.252 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T35513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 106.9 | 106.8641 | 116.252 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T35513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 106.9 | 106.8641 | 116.252 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T35513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 106.9 | 106.8641 | 116.252 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T35513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 106.9 | 106.8641 | 116.252 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 | CONT-LaCygne West Gardner 345kv | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1835513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 102.8 | 102.8494 | 112.2478 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 | Replace Wave Trap at Harper Substation |  | 110 |  |  |  | 18 | 18 | [5 empty] | 385244 | 2012-11-12 | [39 empty] | 2013-06-01 | 2014-12-01
2011-AG2 | AFS9 | CONT-LaCygne West Gardner 345kv | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1835513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 102.8 | 102.8494 | 112.2478 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 |  |  |  | MKEC | CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | Rebuild MKEC portion of the 5.6 mile Clearwater-Milan Tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 5.6 | 24 | 24 | [5 empty] | 2501569 | 2011-12-07 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 | CONT-LaCygne West Gardner 345kv | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1835513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 102.8 | 102.8494 | 112.2478 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 |  |  |  | WERE | CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | Rebuild Westar portion of the Clearwater-Milan tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 6.1 | 24 | 24 | [5 empty] | 7951703 | 2011-11-15 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 | CONT-LaCygne West Gardner 345kv | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1835513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 102.8 | 102.8494 | 112.2478 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | Reconductor 22.1 mile Harper to Milan Tap 138 kV line. | 261 | 314 |  |  | 22.1 | 36 | 36 | [5 empty] | 9613332 | 2011-12-02 | [38 empty] | 2020-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 | CONT-LaCygne West Gardner 345kv | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1835513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 102.8 | 102.8494 | 112.2478 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 | CONT-LaCygne West Gardner 345kv | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1835513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 102.8 | 102.8494 | 112.2478 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 | CONT-LaCygne West Gardner 345kv | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1835513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 102.8 | 102.8494 | 112.2478 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 | CONT-LaCygne West Gardner 345kv | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1835513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 102.8 | 102.8494 | 112.2478 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 | CONT-LaCygne West Gardner 345kv | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1835513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 102.8 | 102.8494 | 112.2478 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 | CONT-LaCygne West Gardner 345kv | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1835513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 102.8 | 102.8494 | 112.2478 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 | CONT-LaCygne West Gardner 345kv | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1835513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 102.8 | 102.8494 | 112.2478 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 | CONT-LaCygne West Gardner 345kv | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1835513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 102.8 | 102.8494 | 112.2478 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 | CONT-LaCygne West Gardner 345kv | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1835513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 102.8 | 102.8494 | 112.2478 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 | CONT-LaCygne West Gardner 345kv | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1835513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 102.8 | 102.8494 | 112.2478 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 | CONT-LaCygne West Gardner 345kv | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1835513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 102.8 | 102.8494 | 112.2478 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8645513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 96.1976 | 96.1976 | 102.7413 | [7 empty] | CATEGORYB | NONSINGLE | SPP-MKEC-06 | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 | Replace Wave Trap at Harper Substation |  | 110 |  |  |  | 18 | 18 | [5 empty] | 385244 | 2012-11-12 | [39 empty] | 2013-06-01 | 2014-12-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8645513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 96.1976 | 96.1976 | 102.7413 | [7 empty] | CATEGORYB | NONSINGLE | SPP-MKEC-06 | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | Rebuild MKEC portion of the 5.6 mile Clearwater-Milan Tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 5.6 | 24 | 24 | [5 empty] | 2501569 | 2011-12-07 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8645513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 96.1976 | 96.1976 | 102.7413 | [7 empty] | CATEGORYB | NONSINGLE | SPP-MKEC-06 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | Rebuild Westar portion of the Clearwater-Milan tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 6.1 | 24 | 24 | [5 empty] | 7951703 | 2011-11-15 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8645513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 96.1976 | 96.1976 | 102.7413 | [7 empty] | CATEGORYB | NONSINGLE | SPP-MKEC-06 | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | Reconductor 22.1 mile Harper to Milan Tap 138 kV line. | 261 | 314 |  |  | 22.1 | 36 | 36 | [5 empty] | 9613332 | 2011-12-02 | [38 empty] | 2020-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8645513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 96.1976 | 96.1976 | 102.7413 | [7 empty] | CATEGORYB | NONSINGLE | SPP-MKEC-06 | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8645513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 96.1976 | 96.1976 | 102.7413 | [7 empty] | CATEGORYB | NONSINGLE | SPP-MKEC-06 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8645513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 96.1976 | 96.1976 | 102.7413 | [7 empty] | CATEGORYB | NONSINGLE | SPP-MKEC-06 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8645513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 96.1976 | 96.1976 | 102.7413 | [7 empty] | CATEGORYB | NONSINGLE | SPP-MKEC-06 | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8645513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 96.1976 | 96.1976 | 102.7413 | [7 empty] | CATEGORYB | NONSINGLE | SPP-MKEC-06 | 0 | 0 |  | 0 |  | 0 | [5 empty] | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8645513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 96.1976 | 96.1976 | 102.7413 | [7 empty] | CATEGORYB | NONSINGLE | SPP-MKEC-06 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8645513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 96.1976 | 96.1976 | 102.7413 | [7 empty] | CATEGORYB | NONSINGLE | SPP-MKEC-06 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8645513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 96.1976 | 96.1976 | 102.7413 | [7 empty] | CATEGORYB | NONSINGLE | SPP-MKEC-06 | 0 | 0 |  | 0 |  | 0 | [5 empty] | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8645513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 96.1976 | 96.1976 | 102.7413 | [7 empty] | CATEGORYB | NONSINGLE | SPP-MKEC-06 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8645513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 96.1976 | 96.1976 | 102.7413 | [7 empty] | CATEGORYB | NONSINGLE | SPP-MKEC-06 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8645513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 96.1976 | 96.1976 | 102.7413 | [7 empty] | CATEGORYB | NONSINGLE | SPP-MKEC-06 | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2135514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 105.9724 | 142.0768 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 | Replace Wave Trap at Harper Substation |  | 110 |  |  |  | 18 | 18 | [5 empty] | 385244 | 2012-11-12 | [39 empty] | 2013-06-01 | 2014-12-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2135514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 105.9724 | 142.0768 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 |  |  |  | MKEC | CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | Rebuild MKEC portion of the 5.6 mile Clearwater-Milan Tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 5.6 | 24 | 24 | [5 empty] | 2501569 | 2011-12-07 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2135514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 105.9724 | 142.0768 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 |  |  |  | WERE | CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | Rebuild Westar portion of the Clearwater-Milan tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 6.1 | 24 | 24 | [5 empty] | 7951703 | 2011-11-15 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2135514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 105.9724 | 142.0768 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | Reconductor 22.1 mile Harper to Milan Tap 138 kV line. | 261 | 314 |  |  | 22.1 | 36 | 36 | [5 empty] | 9613332 | 2011-12-02 | [38 empty] | 2020-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2135514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 105.9724 | 142.0768 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2135514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 105.9724 | 142.0768 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2135514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 105.9724 | 142.0768 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2135514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 105.9724 | 142.0768 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2135514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 105.9724 | 142.0768 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2135514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 105.9724 | 142.0768 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2135514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 105.9724 | 142.0768 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2135514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 105.9724 | 142.0768 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2135514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 105.9724 | 142.0768 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2135514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 105.9724 | 142.0768 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2135514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 105.9724 | 142.0768 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3735514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 113.428 | 138.5269 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 | Replace Wave Trap at Harper Substation |  | 110 |  |  |  | 18 | 18 | [5 empty] | 385244 | 2012-11-12 | [39 empty] | 2013-06-01 | 2014-12-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3735514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 113.428 | 138.5269 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | MKEC | CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | Rebuild MKEC portion of the 5.6 mile Clearwater-Milan Tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 5.6 | 24 | 24 | [5 empty] | 2501569 | 2011-12-07 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3735514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 113.428 | 138.5269 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | WERE | CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | Rebuild Westar portion of the Clearwater-Milan tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 6.1 | 24 | 24 | [5 empty] | 7951703 | 2011-11-15 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3735514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 113.428 | 138.5269 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | Reconductor 22.1 mile Harper to Milan Tap 138 kV line. | 261 | 314 |  |  | 22.1 | 36 | 36 | [5 empty] | 9613332 | 2011-12-02 | [38 empty] | 2020-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3735514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 113.428 | 138.5269 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3735514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 113.428 | 138.5269 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3735514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 113.428 | 138.5269 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3735514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 113.428 | 138.5269 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3735514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 113.428 | 138.5269 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3735514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 113.428 | 138.5269 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3735514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 113.428 | 138.5269 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3735514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 113.428 | 138.5269 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3735514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 113.428 | 138.5269 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3735514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 113.428 | 138.5269 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3735514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 113.428 | 138.5269 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3705514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 111.862 | 136.8866 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 | Replace Wave Trap at Harper Substation |  | 110 |  |  |  | 18 | 18 | [5 empty] | 385244 | 2012-11-12 | [39 empty] | 2013-06-01 | 2014-12-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3705514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 111.862 | 136.8866 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | MKEC | CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | Rebuild MKEC portion of the 5.6 mile Clearwater-Milan Tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 5.6 | 24 | 24 | [5 empty] | 2501569 | 2011-12-07 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3705514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 111.862 | 136.8866 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | WERE | CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | Rebuild Westar portion of the Clearwater-Milan tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 6.1 | 24 | 24 | [5 empty] | 7951703 | 2011-11-15 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3705514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 111.862 | 136.8866 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | Reconductor 22.1 mile Harper to Milan Tap 138 kV line. | 261 | 314 |  |  | 22.1 | 36 | 36 | [5 empty] | 9613332 | 2011-12-02 | [38 empty] | 2020-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3705514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 111.862 | 136.8866 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3705514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 111.862 | 136.8866 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3705514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 111.862 | 136.8866 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3705514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 111.862 | 136.8866 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3705514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 111.862 | 136.8866 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3705514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 111.862 | 136.8866 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3705514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 111.862 | 136.8866 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3705514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 111.862 | 136.8866 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3705514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 111.862 | 136.8866 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3705514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 111.862 | 136.8866 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3705514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 111.862 | 136.8866 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3335514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 87.0685 | 112.0689 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 | Replace Wave Trap at Harper Substation |  | 110 |  |  |  | 18 | 18 | [5 empty] | 385244 | 2012-11-12 | [39 empty] | 2013-06-01 | 2014-12-01
2011-AG2 | AFS9-14SP | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3335514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 87.0685 | 112.0689 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | MKEC | CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | Rebuild MKEC portion of the 5.6 mile Clearwater-Milan Tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 5.6 | 24 | 24 | [5 empty] | 2501569 | 2011-12-07 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9-14SP | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3335514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 87.0685 | 112.0689 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | WERE | CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | Rebuild Westar portion of the Clearwater-Milan tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 6.1 | 24 | 24 | [5 empty] | 7951703 | 2011-11-15 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9-14SP | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3335514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 87.0685 | 112.0689 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | Reconductor 22.1 mile Harper to Milan Tap 138 kV line. | 261 | 314 |  |  | 22.1 | 36 | 36 | [5 empty] | 9613332 | 2011-12-02 | [38 empty] | 2020-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9-14SP | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3335514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 87.0685 | 112.0689 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3335514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 87.0685 | 112.0689 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-14SP | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3335514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 87.0685 | 112.0689 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-14SP | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3335514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 87.0685 | 112.0689 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3335514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 87.0685 | 112.0689 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3335514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 87.0685 | 112.0689 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3335514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 87.0685 | 112.0689 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3335514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 87.0685 | 112.0689 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3335514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 87.0685 | 112.0689 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3335514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 87.0685 | 112.0689 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3335514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 87.0685 | 112.0689 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19715514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 85.2516 | 110.3136 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 | Replace Wave Trap at Harper Substation |  | 110 |  |  |  | 18 | 18 | [5 empty] | 385244 | 2012-11-12 | [39 empty] | 2013-06-01 | 2014-12-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19715514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 85.2516 | 110.3136 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | Rebuild MKEC portion of the 5.6 mile Clearwater-Milan Tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 5.6 | 24 | 24 | [5 empty] | 2501569 | 2011-12-07 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19715514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 85.2516 | 110.3136 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | Rebuild Westar portion of the Clearwater-Milan tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 6.1 | 24 | 24 | [5 empty] | 7951703 | 2011-11-15 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19715514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 85.2516 | 110.3136 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | Reconductor 22.1 mile Harper to Milan Tap 138 kV line. | 261 | 314 |  |  | 22.1 | 36 | 36 | [5 empty] | 9613332 | 2011-12-02 | [38 empty] | 2020-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19715514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 85.2516 | 110.3136 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19715514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 85.2516 | 110.3136 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19715514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 85.2516 | 110.3136 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19715514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 85.2516 | 110.3136 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19715514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 85.2516 | 110.3136 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19715514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 85.2516 | 110.3136 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19715514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 85.2516 | 110.3136 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19715514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 85.2516 | 110.3136 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19715514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 85.2516 | 110.3136 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19715514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 85.2516 | 110.3136 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19715514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 85.2516 | 110.3136 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19625514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 83.9278 | 109.1725 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WEPL-01 | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 | Replace Wave Trap at Harper Substation |  | 110 |  |  |  | 18 | 18 | [5 empty] | 385244 | 2012-11-12 | [39 empty] | 2013-06-01 | 2014-12-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19625514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 83.9278 | 109.1725 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WEPL-01 | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | Rebuild MKEC portion of the 5.6 mile Clearwater-Milan Tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 5.6 | 24 | 24 | [5 empty] | 2501569 | 2011-12-07 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19625514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 83.9278 | 109.1725 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WEPL-01 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | Rebuild Westar portion of the Clearwater-Milan tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 6.1 | 24 | 24 | [5 empty] | 7951703 | 2011-11-15 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19625514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 83.9278 | 109.1725 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WEPL-01 | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | Reconductor 22.1 mile Harper to Milan Tap 138 kV line. | 261 | 314 |  |  | 22.1 | 36 | 36 | [5 empty] | 9613332 | 2011-12-02 | [38 empty] | 2020-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19625514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 83.9278 | 109.1725 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WEPL-01 | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19625514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 83.9278 | 109.1725 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WEPL-01 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19625514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 83.9278 | 109.1725 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WEPL-01 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19625514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 83.9278 | 109.1725 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WEPL-01 | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19625514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 83.9278 | 109.1725 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WEPL-01 | 0 | 0 |  | 0 |  | 0 | [5 empty] | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19625514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 83.9278 | 109.1725 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WEPL-01 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19625514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 83.9278 | 109.1725 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WEPL-01 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19625514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 83.9278 | 109.1725 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WEPL-01 | 0 | 0 |  | 0 |  | 0 | [5 empty] | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19625514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 83.9278 | 109.1725 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WEPL-01 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19625514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 83.9278 | 109.1725 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WEPL-01 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19625514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 83.9278 | 109.1725 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WEPL-01 | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2745517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 74.8341 | 74.8341 | 106.5454 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 | Replace Wave Trap at Harper Substation |  | 110 |  |  |  | 18 | 18 | [5 empty] | 385244 | 2012-11-12 | [39 empty] | 2013-06-01 | 2014-12-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2745517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 74.8341 | 74.8341 | 106.5454 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | MKEC | CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | Rebuild MKEC portion of the 5.6 mile Clearwater-Milan Tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 5.6 | 24 | 24 | [5 empty] | 2501569 | 2011-12-07 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2745517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 74.8341 | 74.8341 | 106.5454 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | WERE | CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | Rebuild Westar portion of the Clearwater-Milan tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 6.1 | 24 | 24 | [5 empty] | 7951703 | 2011-11-15 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2745517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 74.8341 | 74.8341 | 106.5454 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | Reconductor 22.1 mile Harper to Milan Tap 138 kV line. | 261 | 314 |  |  | 22.1 | 36 | 36 | [5 empty] | 9613332 | 2011-12-02 | [38 empty] | 2020-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2745517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 74.8341 | 74.8341 | 106.5454 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2745517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 74.8341 | 74.8341 | 106.5454 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2745517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 74.8341 | 74.8341 | 106.5454 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2745517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 74.8341 | 74.8341 | 106.5454 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2745517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 74.8341 | 74.8341 | 106.5454 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2745517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 74.8341 | 74.8341 | 106.5454 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2745517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 74.8341 | 74.8341 | 106.5454 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2745517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 74.8341 | 74.8341 | 106.5454 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2745517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 74.8341 | 74.8341 | 106.5454 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2745517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 74.8341 | 74.8341 | 106.5454 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2745517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 74.8341 | 74.8341 | 106.5454 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2885517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 82.5354 | 82.5354 | 105.8438 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 | Replace Wave Trap at Harper Substation |  | 110 |  |  |  | 18 | 18 | [5 empty] | 385244 | 2012-11-12 | [39 empty] | 2013-06-01 | 2014-12-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2885517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 82.5354 | 82.5354 | 105.8438 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 |  |  |  | MKEC | CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | Rebuild MKEC portion of the 5.6 mile Clearwater-Milan Tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 5.6 | 24 | 24 | [5 empty] | 2501569 | 2011-12-07 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2885517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 82.5354 | 82.5354 | 105.8438 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 |  |  |  | WERE | CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | Rebuild Westar portion of the Clearwater-Milan tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 6.1 | 24 | 24 | [5 empty] | 7951703 | 2011-11-15 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2885517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 82.5354 | 82.5354 | 105.8438 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | Reconductor 22.1 mile Harper to Milan Tap 138 kV line. | 261 | 314 |  |  | 22.1 | 36 | 36 | [5 empty] | 9613332 | 2011-12-02 | [38 empty] | 2020-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2885517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 82.5354 | 82.5354 | 105.8438 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2885517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 82.5354 | 82.5354 | 105.8438 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2885517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 82.5354 | 82.5354 | 105.8438 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2885517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 82.5354 | 82.5354 | 105.8438 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2885517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 82.5354 | 82.5354 | 105.8438 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2885517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 82.5354 | 82.5354 | 105.8438 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2885517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 82.5354 | 82.5354 | 105.8438 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2885517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 82.5354 | 82.5354 | 105.8438 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2885517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 82.5354 | 82.5354 | 105.8438 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2885517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 82.5354 | 82.5354 | 105.8438 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2885517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 82.5354 | 82.5354 | 105.8438 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T135514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 79.9342 | 105.085 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 | Replace Wave Trap at Harper Substation |  | 110 |  |  |  | 18 | 18 | [5 empty] | 385244 | 2012-11-12 | [39 empty] | 2013-06-01 | 2014-12-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T135514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 79.9342 | 105.085 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | Rebuild MKEC portion of the 5.6 mile Clearwater-Milan Tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 5.6 | 24 | 24 | [5 empty] | 2501569 | 2011-12-07 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T135514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 79.9342 | 105.085 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | Rebuild Westar portion of the Clearwater-Milan tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 6.1 | 24 | 24 | [5 empty] | 7951703 | 2011-11-15 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T135514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 79.9342 | 105.085 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | Reconductor 22.1 mile Harper to Milan Tap 138 kV line. | 261 | 314 |  |  | 22.1 | 36 | 36 | [5 empty] | 9613332 | 2011-12-02 | [38 empty] | 2020-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T135514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 79.9342 | 105.085 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T135514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 79.9342 | 105.085 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T135514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 79.9342 | 105.085 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T135514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 79.9342 | 105.085 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T135514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 79.9342 | 105.085 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T135514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 79.9342 | 105.085 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T135514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 79.9342 | 105.085 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T135514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 79.9342 | 105.085 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T135514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 79.9342 | 105.085 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T135514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 79.9342 | 105.085 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T135514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 79.9342 | 105.085 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2935517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 80.1333 | 80.1333 | 103.5311 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 | Replace Wave Trap at Harper Substation |  | 110 |  |  |  | 18 | 18 | [5 empty] | 385244 | 2012-11-12 | [39 empty] | 2013-06-01 | 2014-12-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2935517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 80.1333 | 80.1333 | 103.5311 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | MKEC | CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | Rebuild MKEC portion of the 5.6 mile Clearwater-Milan Tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 5.6 | 24 | 24 | [5 empty] | 2501569 | 2011-12-07 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2935517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 80.1333 | 80.1333 | 103.5311 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | WERE | CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | Rebuild Westar portion of the Clearwater-Milan tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 6.1 | 24 | 24 | [5 empty] | 7951703 | 2011-11-15 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2935517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 80.1333 | 80.1333 | 103.5311 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | Reconductor 22.1 mile Harper to Milan Tap 138 kV line. | 261 | 314 |  |  | 22.1 | 36 | 36 | [5 empty] | 9613332 | 2011-12-02 | [38 empty] | 2020-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2935517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 80.1333 | 80.1333 | 103.5311 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2935517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 80.1333 | 80.1333 | 103.5311 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2935517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 80.1333 | 80.1333 | 103.5311 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2935517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 80.1333 | 80.1333 | 103.5311 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2935517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 80.1333 | 80.1333 | 103.5311 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2935517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 80.1333 | 80.1333 | 103.5311 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2935517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 80.1333 | 80.1333 | 103.5311 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2935517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 80.1333 | 80.1333 | 103.5311 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2935517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 80.1333 | 80.1333 | 103.5311 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2935517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 80.1333 | 80.1333 | 103.5311 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2935517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 80.1333 | 80.1333 | 103.5311 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP | CONT-LaCygne West Gardner 345kv |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4155514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 76.0104 | 101.2299 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 | Replace Wave Trap at Harper Substation |  | 110 |  |  |  | 18 | 18 | [5 empty] | 385244 | 2012-11-12 | [39 empty] | 2013-06-01 | 2014-12-01
2011-AG2 | AFS9-14SP | CONT-LaCygne West Gardner 345kv |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4155514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 76.0104 | 101.2299 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 |  |  |  | MKEC | CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | Rebuild MKEC portion of the 5.6 mile Clearwater-Milan Tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 5.6 | 24 | 24 | [5 empty] | 2501569 | 2011-12-07 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9-14SP | CONT-LaCygne West Gardner 345kv |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4155514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 76.0104 | 101.2299 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 |  |  |  | WERE | CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | Rebuild Westar portion of the Clearwater-Milan tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 6.1 | 24 | 24 | [5 empty] | 7951703 | 2011-11-15 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9-14SP | CONT-LaCygne West Gardner 345kv |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4155514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 76.0104 | 101.2299 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | Reconductor 22.1 mile Harper to Milan Tap 138 kV line. | 261 | 314 |  |  | 22.1 | 36 | 36 | [5 empty] | 9613332 | 2011-12-02 | [38 empty] | 2020-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9-14SP | CONT-LaCygne West Gardner 345kv |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4155514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 76.0104 | 101.2299 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP | CONT-LaCygne West Gardner 345kv |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4155514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 76.0104 | 101.2299 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-14SP | CONT-LaCygne West Gardner 345kv |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4155514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 76.0104 | 101.2299 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-14SP | CONT-LaCygne West Gardner 345kv |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4155514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 76.0104 | 101.2299 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP | CONT-LaCygne West Gardner 345kv |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4155514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 76.0104 | 101.2299 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP | CONT-LaCygne West Gardner 345kv |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4155514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 76.0104 | 101.2299 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP | CONT-LaCygne West Gardner 345kv |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4155514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 76.0104 | 101.2299 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP | CONT-LaCygne West Gardner 345kv |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4155514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 76.0104 | 101.2299 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP | CONT-LaCygne West Gardner 345kv |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4155514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 76.0104 | 101.2299 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP | CONT-LaCygne West Gardner 345kv |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4155514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 76.0104 | 101.2299 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP | CONT-LaCygne West Gardner 345kv |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4155514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 76.0104 | 101.2299 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T20555517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 77.2768 | 77.2768 | 100.7258 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 | Replace Wave Trap at Harper Substation |  | 110 |  |  |  | 18 | 18 | [5 empty] | 385244 | 2012-11-12 | [39 empty] | 2013-06-01 | 2014-12-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T20555517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 77.2768 | 77.2768 | 100.7258 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | Rebuild MKEC portion of the 5.6 mile Clearwater-Milan Tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 5.6 | 24 | 24 | [5 empty] | 2501569 | 2011-12-07 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T20555517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 77.2768 | 77.2768 | 100.7258 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | Rebuild Westar portion of the Clearwater-Milan tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 6.1 | 24 | 24 | [5 empty] | 7951703 | 2011-11-15 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T20555517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 77.2768 | 77.2768 | 100.7258 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | Reconductor 22.1 mile Harper to Milan Tap 138 kV line. | 261 | 314 |  |  | 22.1 | 36 | 36 | [5 empty] | 9613332 | 2011-12-02 | [38 empty] | 2020-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T20555517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 77.2768 | 77.2768 | 100.7258 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T20555517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 77.2768 | 77.2768 | 100.7258 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T20555517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 77.2768 | 77.2768 | 100.7258 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T20555517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 77.2768 | 77.2768 | 100.7258 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T20555517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 77.2768 | 77.2768 | 100.7258 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T20555517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 77.2768 | 77.2768 | 100.7258 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T20555517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 77.2768 | 77.2768 | 100.7258 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T20555517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 77.2768 | 77.2768 | 100.7258 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T20555517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 77.2768 | 77.2768 | 100.7258 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T20555517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 77.2768 | 77.2768 | 100.7258 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T20555517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 77.2768 | 77.2768 | 100.7258 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1175517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 88.7398 | 88.7398 | 120.4692 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 | Replace Wave Trap at Harper Substation |  | 110 |  |  |  | 18 | 18 | [5 empty] | 385244 | 2012-11-12 | [39 empty] | 2013-06-01 | 2014-12-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1175517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 88.7398 | 88.7398 | 120.4692 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | MKEC | CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | Rebuild MKEC portion of the 5.6 mile Clearwater-Milan Tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 5.6 | 24 | 24 | [5 empty] | 2501569 | 2011-12-07 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1175517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 88.7398 | 88.7398 | 120.4692 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | WERE | CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | Rebuild Westar portion of the Clearwater-Milan tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 6.1 | 24 | 24 | [5 empty] | 7951703 | 2011-11-15 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1175517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 88.7398 | 88.7398 | 120.4692 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | Reconductor 22.1 mile Harper to Milan Tap 138 kV line. | 261 | 314 |  |  | 22.1 | 36 | 36 | [5 empty] | 9613332 | 2011-12-02 | [38 empty] | 2020-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1175517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 88.7398 | 88.7398 | 120.4692 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1175517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 88.7398 | 88.7398 | 120.4692 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1175517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 88.7398 | 88.7398 | 120.4692 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1175517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 88.7398 | 88.7398 | 120.4692 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1175517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 88.7398 | 88.7398 | 120.4692 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1175517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 88.7398 | 88.7398 | 120.4692 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1175517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 88.7398 | 88.7398 | 120.4692 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1175517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 88.7398 | 88.7398 | 120.4692 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1175517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 88.7398 | 88.7398 | 120.4692 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1175517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 88.7398 | 88.7398 | 120.4692 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1175517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 88.7398 | 88.7398 | 120.4692 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T835517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 86.9094 | 86.9094 | 113.9501 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 | Replace Wave Trap at Harper Substation |  | 110 |  |  |  | 18 | 18 | [5 empty] | 385244 | 2012-11-12 | [39 empty] | 2013-06-01 | 2014-12-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T835517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 86.9094 | 86.9094 | 113.9501 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | MKEC | CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | Rebuild MKEC portion of the 5.6 mile Clearwater-Milan Tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 5.6 | 24 | 24 | [5 empty] | 2501569 | 2011-12-07 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T835517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 86.9094 | 86.9094 | 113.9501 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | WERE | CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | Rebuild Westar portion of the Clearwater-Milan tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 6.1 | 24 | 24 | [5 empty] | 7951703 | 2011-11-15 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T835517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 86.9094 | 86.9094 | 113.9501 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | Reconductor 22.1 mile Harper to Milan Tap 138 kV line. | 261 | 314 |  |  | 22.1 | 36 | 36 | [5 empty] | 9613332 | 2011-12-02 | [38 empty] | 2020-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T835517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 86.9094 | 86.9094 | 113.9501 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T835517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 86.9094 | 86.9094 | 113.9501 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T835517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 86.9094 | 86.9094 | 113.9501 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T835517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 86.9094 | 86.9094 | 113.9501 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T835517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 86.9094 | 86.9094 | 113.9501 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T835517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 86.9094 | 86.9094 | 113.9501 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T835517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 86.9094 | 86.9094 | 113.9501 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T835517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 86.9094 | 86.9094 | 113.9501 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T835517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 86.9094 | 86.9094 | 113.9501 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T835517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 86.9094 | 86.9094 | 113.9501 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T835517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 86.9094 | 86.9094 | 113.9501 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1285517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 84.844 | 84.844 | 108.395 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 | Replace Wave Trap at Harper Substation |  | 110 |  |  |  | 18 | 18 | [5 empty] | 385244 | 2012-11-12 | [39 empty] | 2013-06-01 | 2014-12-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1285517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 84.844 | 84.844 | 108.395 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | MKEC | CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | Rebuild MKEC portion of the 5.6 mile Clearwater-Milan Tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 5.6 | 24 | 24 | [5 empty] | 2501569 | 2011-12-07 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1285517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 84.844 | 84.844 | 108.395 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | WERE | CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | Rebuild Westar portion of the Clearwater-Milan tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 6.1 | 24 | 24 | [5 empty] | 7951703 | 2011-11-15 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1285517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 84.844 | 84.844 | 108.395 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | Reconductor 22.1 mile Harper to Milan Tap 138 kV line. | 261 | 314 |  |  | 22.1 | 36 | 36 | [5 empty] | 9613332 | 2011-12-02 | [38 empty] | 2020-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1285517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 84.844 | 84.844 | 108.395 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1285517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 84.844 | 84.844 | 108.395 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1285517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 84.844 | 84.844 | 108.395 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1285517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 84.844 | 84.844 | 108.395 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1285517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 84.844 | 84.844 | 108.395 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1285517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 84.844 | 84.844 | 108.395 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1285517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 84.844 | 84.844 | 108.395 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1285517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 84.844 | 84.844 | 108.395 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1285517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 84.844 | 84.844 | 108.395 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1285517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 84.844 | 84.844 | 108.395 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1285517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 84.844 | 84.844 | 108.395 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10945517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 83.0126 | 83.0126 | 106.5748 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 | Replace Wave Trap at Harper Substation |  | 110 |  |  |  | 18 | 18 | [5 empty] | 385244 | 2012-11-12 | [39 empty] | 2013-06-01 | 2014-12-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10945517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 83.0126 | 83.0126 | 106.5748 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | Rebuild MKEC portion of the 5.6 mile Clearwater-Milan Tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 5.6 | 24 | 24 | [5 empty] | 2501569 | 2011-12-07 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10945517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 83.0126 | 83.0126 | 106.5748 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | Rebuild Westar portion of the Clearwater-Milan tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 6.1 | 24 | 24 | [5 empty] | 7951703 | 2011-11-15 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10945517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 83.0126 | 83.0126 | 106.5748 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | Reconductor 22.1 mile Harper to Milan Tap 138 kV line. | 261 | 314 |  |  | 22.1 | 36 | 36 | [5 empty] | 9613332 | 2011-12-02 | [38 empty] | 2020-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10945517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 83.0126 | 83.0126 | 106.5748 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10945517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 83.0126 | 83.0126 | 106.5748 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10945517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 83.0126 | 83.0126 | 106.5748 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10945517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 83.0126 | 83.0126 | 106.5748 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10945517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 83.0126 | 83.0126 | 106.5748 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10945517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 83.0126 | 83.0126 | 106.5748 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10945517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 83.0126 | 83.0126 | 106.5748 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10945517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 83.0126 | 83.0126 | 106.5748 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10945517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 83.0126 | 83.0126 | 106.5748 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10945517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 83.0126 | 83.0126 | 106.5748 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10945517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 83.0126 | 83.0126 | 106.5748 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10935517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 81.3969 | 81.3969 | 104.9911 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-30 | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 | Replace Wave Trap at Harper Substation |  | 110 |  |  |  | 18 | 18 | [5 empty] | 385244 | 2012-11-12 | [39 empty] | 2013-06-01 | 2014-12-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10935517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 81.3969 | 81.3969 | 104.9911 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-30 | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | Rebuild MKEC portion of the 5.6 mile Clearwater-Milan Tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 5.6 | 24 | 24 | [5 empty] | 2501569 | 2011-12-07 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10935517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 81.3969 | 81.3969 | 104.9911 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-30 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | Rebuild Westar portion of the Clearwater-Milan tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 6.1 | 24 | 24 | [5 empty] | 7951703 | 2011-11-15 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10935517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 81.3969 | 81.3969 | 104.9911 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-30 | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | Reconductor 22.1 mile Harper to Milan Tap 138 kV line. | 261 | 314 |  |  | 22.1 | 36 | 36 | [5 empty] | 9613332 | 2011-12-02 | [38 empty] | 2020-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10935517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 81.3969 | 81.3969 | 104.9911 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-30 | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10935517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 81.3969 | 81.3969 | 104.9911 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-30 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10935517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 81.3969 | 81.3969 | 104.9911 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-30 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10935517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 81.3969 | 81.3969 | 104.9911 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-30 | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10935517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 81.3969 | 81.3969 | 104.9911 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-30 | 0 | 0 |  | 0 |  | 0 | [5 empty] | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10935517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 81.3969 | 81.3969 | 104.9911 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-30 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10935517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 81.3969 | 81.3969 | 104.9911 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-30 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10935517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 81.3969 | 81.3969 | 104.9911 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-30 | 0 | 0 |  | 0 |  | 0 | [5 empty] | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10935517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 81.3969 | 81.3969 | 104.9911 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-30 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10935517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 81.3969 | 81.3969 | 104.9911 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-30 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10935517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 81.3969 | 81.3969 | 104.9911 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-30 | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10925517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 80.9374 | 80.9374 | 104.5937 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-28 | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 | Replace Wave Trap at Harper Substation |  | 110 |  |  |  | 18 | 18 | [5 empty] | 385244 | 2012-11-12 | [39 empty] | 2013-06-01 | 2014-12-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10925517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 80.9374 | 80.9374 | 104.5937 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-28 | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | Rebuild MKEC portion of the 5.6 mile Clearwater-Milan Tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 5.6 | 24 | 24 | [5 empty] | 2501569 | 2011-12-07 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10925517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 80.9374 | 80.9374 | 104.5937 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-28 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | Rebuild Westar portion of the Clearwater-Milan tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 6.1 | 24 | 24 | [5 empty] | 7951703 | 2011-11-15 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10925517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 80.9374 | 80.9374 | 104.5937 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-28 | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | Reconductor 22.1 mile Harper to Milan Tap 138 kV line. | 261 | 314 |  |  | 22.1 | 36 | 36 | [5 empty] | 9613332 | 2011-12-02 | [38 empty] | 2020-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10925517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 80.9374 | 80.9374 | 104.5937 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-28 | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10925517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 80.9374 | 80.9374 | 104.5937 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-28 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10925517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 80.9374 | 80.9374 | 104.5937 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-28 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10925517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 80.9374 | 80.9374 | 104.5937 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-28 | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10925517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 80.9374 | 80.9374 | 104.5937 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-28 | 0 | 0 |  | 0 |  | 0 | [5 empty] | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10925517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 80.9374 | 80.9374 | 104.5937 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-28 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10925517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 80.9374 | 80.9374 | 104.5937 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-28 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10925517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 80.9374 | 80.9374 | 104.5937 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-28 | 0 | 0 |  | 0 |  | 0 | [5 empty] | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10925517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 80.9374 | 80.9374 | 104.5937 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-28 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10925517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 80.9374 | 80.9374 | 104.5937 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-28 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10925517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 80.9374 | 80.9374 | 104.5937 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-28 | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 | CONT-0301 - Rose Hill - Wolf Creek 345kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1135517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 80.2836 | 80.2836 | 103.4399 | [7 empty] | CATEGORYB | SINGLE | ROSE HILL - WOLF CREEK 345KV CKT 1 | 0 | 532794 | ROSEHIL7 345.00 | 532797 | WOLFCRK7 345.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 | Replace Wave Trap at Harper Substation |  | 110 |  |  |  | 18 | 18 | [5 empty] | 385244 | 2012-11-12 | [39 empty] | 2013-06-01 | 2014-12-01
2011-AG2 | AFS9 | CONT-0301 - Rose Hill - Wolf Creek 345kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1135517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 80.2836 | 80.2836 | 103.4399 | [7 empty] | CATEGORYB | SINGLE | ROSE HILL - WOLF CREEK 345KV CKT 1 | 0 | 532794 | ROSEHIL7 345.00 | 532797 | WOLFCRK7 345.00 | 0 |  | 1 |  |  |  | MKEC | CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | Rebuild MKEC portion of the 5.6 mile Clearwater-Milan Tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 5.6 | 24 | 24 | [5 empty] | 2501569 | 2011-12-07 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 | CONT-0301 - Rose Hill - Wolf Creek 345kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1135517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 80.2836 | 80.2836 | 103.4399 | [7 empty] | CATEGORYB | SINGLE | ROSE HILL - WOLF CREEK 345KV CKT 1 | 0 | 532794 | ROSEHIL7 345.00 | 532797 | WOLFCRK7 345.00 | 0 |  | 1 |  |  |  | WERE | CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | Rebuild Westar portion of the Clearwater-Milan tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 6.1 | 24 | 24 | [5 empty] | 7951703 | 2011-11-15 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 | CONT-0301 - Rose Hill - Wolf Creek 345kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1135517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 80.2836 | 80.2836 | 103.4399 | [7 empty] | CATEGORYB | SINGLE | ROSE HILL - WOLF CREEK 345KV CKT 1 | 0 | 532794 | ROSEHIL7 345.00 | 532797 | WOLFCRK7 345.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | Reconductor 22.1 mile Harper to Milan Tap 138 kV line. | 261 | 314 |  |  | 22.1 | 36 | 36 | [5 empty] | 9613332 | 2011-12-02 | [38 empty] | 2020-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 | CONT-0301 - Rose Hill - Wolf Creek 345kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1135517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 80.2836 | 80.2836 | 103.4399 | [7 empty] | CATEGORYB | SINGLE | ROSE HILL - WOLF CREEK 345KV CKT 1 | 0 | 532794 | ROSEHIL7 345.00 | 532797 | WOLFCRK7 345.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 | CONT-0301 - Rose Hill - Wolf Creek 345kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1135517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 80.2836 | 80.2836 | 103.4399 | [7 empty] | CATEGORYB | SINGLE | ROSE HILL - WOLF CREEK 345KV CKT 1 | 0 | 532794 | ROSEHIL7 345.00 | 532797 | WOLFCRK7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 | CONT-0301 - Rose Hill - Wolf Creek 345kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1135517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 80.2836 | 80.2836 | 103.4399 | [7 empty] | CATEGORYB | SINGLE | ROSE HILL - WOLF CREEK 345KV CKT 1 | 0 | 532794 | ROSEHIL7 345.00 | 532797 | WOLFCRK7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 | CONT-0301 - Rose Hill - Wolf Creek 345kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1135517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 80.2836 | 80.2836 | 103.4399 | [7 empty] | CATEGORYB | SINGLE | ROSE HILL - WOLF CREEK 345KV CKT 1 | 0 | 532794 | ROSEHIL7 345.00 | 532797 | WOLFCRK7 345.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 | CONT-0301 - Rose Hill - Wolf Creek 345kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1135517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 80.2836 | 80.2836 | 103.4399 | [7 empty] | CATEGORYB | SINGLE | ROSE HILL - WOLF CREEK 345KV CKT 1 | 0 | 532794 | ROSEHIL7 345.00 | 532797 | WOLFCRK7 345.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 | CONT-0301 - Rose Hill - Wolf Creek 345kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1135517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 80.2836 | 80.2836 | 103.4399 | [7 empty] | CATEGORYB | SINGLE | ROSE HILL - WOLF CREEK 345KV CKT 1 | 0 | 532794 | ROSEHIL7 345.00 | 532797 | WOLFCRK7 345.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 | CONT-0301 - Rose Hill - Wolf Creek 345kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1135517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 80.2836 | 80.2836 | 103.4399 | [7 empty] | CATEGORYB | SINGLE | ROSE HILL - WOLF CREEK 345KV CKT 1 | 0 | 532794 | ROSEHIL7 345.00 | 532797 | WOLFCRK7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 | CONT-0301 - Rose Hill - Wolf Creek 345kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1135517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 80.2836 | 80.2836 | 103.4399 | [7 empty] | CATEGORYB | SINGLE | ROSE HILL - WOLF CREEK 345KV CKT 1 | 0 | 532794 | ROSEHIL7 345.00 | 532797 | WOLFCRK7 345.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 | CONT-0301 - Rose Hill - Wolf Creek 345kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1135517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 80.2836 | 80.2836 | 103.4399 | [7 empty] | CATEGORYB | SINGLE | ROSE HILL - WOLF CREEK 345KV CKT 1 | 0 | 532794 | ROSEHIL7 345.00 | 532797 | WOLFCRK7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 | CONT-0301 - Rose Hill - Wolf Creek 345kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1135517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 80.2836 | 80.2836 | 103.4399 | [7 empty] | CATEGORYB | SINGLE | ROSE HILL - WOLF CREEK 345KV CKT 1 | 0 | 532794 | ROSEHIL7 345.00 | 532797 | WOLFCRK7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 | CONT-0301 - Rose Hill - Wolf Creek 345kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1135517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 80.2836 | 80.2836 | 103.4399 | [7 empty] | CATEGORYB | SINGLE | ROSE HILL - WOLF CREEK 345KV CKT 1 | 0 | 532794 | ROSEHIL7 345.00 | 532797 | WOLFCRK7 345.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4045522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 79.3455 | 79.3455 | 103.7423 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 | Replace Wave Trap at Harper Substation |  | 110 |  |  |  | 18 | 18 | [5 empty] | 385244 | 2012-11-12 | [39 empty] | 2013-06-01 | 2014-12-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4045522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 79.3455 | 79.3455 | 103.7423 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 |  |  |  | MKEC | CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | Rebuild MKEC portion of the 5.6 mile Clearwater-Milan Tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 5.6 | 24 | 24 | [5 empty] | 2501569 | 2011-12-07 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4045522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 79.3455 | 79.3455 | 103.7423 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 |  |  |  | WERE | CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | Rebuild Westar portion of the Clearwater-Milan tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 6.1 | 24 | 24 | [5 empty] | 7951703 | 2011-11-15 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4045522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 79.3455 | 79.3455 | 103.7423 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | Reconductor 22.1 mile Harper to Milan Tap 138 kV line. | 261 | 314 |  |  | 22.1 | 36 | 36 | [5 empty] | 9613332 | 2011-12-02 | [38 empty] | 2020-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4045522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 79.3455 | 79.3455 | 103.7423 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4045522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 79.3455 | 79.3455 | 103.7423 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4045522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 79.3455 | 79.3455 | 103.7423 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4045522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 79.3455 | 79.3455 | 103.7423 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4045522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 79.3455 | 79.3455 | 103.7423 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4045522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 79.3455 | 79.3455 | 103.7423 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4045522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 79.3455 | 79.3455 | 103.7423 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4045522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 79.3455 | 79.3455 | 103.7423 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4045522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 79.3455 | 79.3455 | 103.7423 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4045522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 79.3455 | 79.3455 | 103.7423 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4045522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 79.3455 | 79.3455 | 103.7423 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4115522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 76.8407 | 76.8407 | 101.3204 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 | Replace Wave Trap at Harper Substation |  | 110 |  |  |  | 18 | 18 | [5 empty] | 385244 | 2012-11-12 | [39 empty] | 2013-06-01 | 2014-12-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4115522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 76.8407 | 76.8407 | 101.3204 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | MKEC | CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | Rebuild MKEC portion of the 5.6 mile Clearwater-Milan Tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 5.6 | 24 | 24 | [5 empty] | 2501569 | 2011-12-07 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4115522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 76.8407 | 76.8407 | 101.3204 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | WERE | CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | Rebuild Westar portion of the Clearwater-Milan tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 6.1 | 24 | 24 | [5 empty] | 7951703 | 2011-11-15 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4115522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 76.8407 | 76.8407 | 101.3204 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | Reconductor 22.1 mile Harper to Milan Tap 138 kV line. | 261 | 314 |  |  | 22.1 | 36 | 36 | [5 empty] | 9613332 | 2011-12-02 | [38 empty] | 2020-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4115522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 76.8407 | 76.8407 | 101.3204 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4115522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 76.8407 | 76.8407 | 101.3204 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4115522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 76.8407 | 76.8407 | 101.3204 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4115522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 76.8407 | 76.8407 | 101.3204 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4115522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 76.8407 | 76.8407 | 101.3204 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4115522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 76.8407 | 76.8407 | 101.3204 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4115522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 76.8407 | 76.8407 | 101.3204 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4115522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 76.8407 | 76.8407 | 101.3204 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4115522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 76.8407 | 76.8407 | 101.3204 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4115522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 76.8407 | 76.8407 | 101.3204 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4115522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 76.8407 | 76.8407 | 101.3204 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3925522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 69.8745 | 69.8745 | 101.0146 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 | Replace Wave Trap at Harper Substation |  | 110 |  |  |  | 18 | 18 | [5 empty] | 385244 | 2012-11-12 | [39 empty] | 2013-06-01 | 2014-12-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3925522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 69.8745 | 69.8745 | 101.0146 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | MKEC | CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | Rebuild MKEC portion of the 5.6 mile Clearwater-Milan Tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 5.6 | 24 | 24 | [5 empty] | 2501569 | 2011-12-07 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3925522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 69.8745 | 69.8745 | 101.0146 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | WERE | CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | Rebuild Westar portion of the Clearwater-Milan tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 261 | 314 |  |  | 6.1 | 24 | 24 | [5 empty] | 7951703 | 2011-11-15 | [38 empty] | 2022-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3925522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 69.8745 | 69.8745 | 101.0146 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | Reconductor 22.1 mile Harper to Milan Tap 138 kV line. | 261 | 314 |  |  | 22.1 | 36 | 36 | [5 empty] | 9613332 | 2011-12-02 | [38 empty] | 2020-03-01 | 2013-06-01 | 2017-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3925522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 69.8745 | 69.8745 | 101.0146 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3925522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 69.8745 | 69.8745 | 101.0146 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3925522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 69.8745 | 69.8745 | 101.0146 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3925522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 69.8745 | 69.8745 | 101.0146 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3925522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 69.8745 | 69.8745 | 101.0146 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3925522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 69.8745 | 69.8745 | 101.0146 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3925522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 69.8745 | 69.8745 | 101.0146 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3925522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 69.8745 | 69.8745 | 101.0146 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3925522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 69.8745 | 69.8745 | 101.0146 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3925522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 69.8745 | 69.8745 | 101.0146 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3925522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 69.8745 | 69.8745 | 101.0146 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2535514SP | TO->FROM | HAYS PLANT - SOUTH HAYS 115KV CKT 1 | EXP | MIDW | MIDW | REG E-IL | REG E-IL | 0 | 530553 | S HAYS 3 115.00 | 530562 | HAYS 3 115.00 | 0 |  | 1 | 17SP | 80 | 99 | 0 |  | 89.3229 | 120.7598 | [7 empty] | CATEGORYB | SINGLE | KNOLL 230 - POSTROCK6 230.00 230KV CKT 1 | 0 | 530558 | KNOLL 6 230.00 | 530584 | POSTROCK6 230.00 | 0 |  | 1 |  |  |  | MIDW | HAYS PLANT - SOUTH HAYS 115KV CKT 1 #2 | Tear down and rebuild of exisiting South Hays - Hays Plant 115 kV line. Tentative plans include rebuilding on existing right-of-way with the possibility of re-routing a portion of the line to new right-of-way as necessary. | 164 | 199 | 164 | 199 |  | 24 | 24 | [46 empty] | 2014-06-01 | 2016-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2545514SP | FROM->TO | HAYS PLANT - VINE STREET 115KV CKT 1 | EXP | MIDW | MIDW | REG E-IL | REG E-IL | 0 | 530562 | HAYS 3 115.00 | 530591 | VINE 3 115.00 | 0 |  | 1 | 17SP | 80 | 88 | 0 |  | 67.4264 | 103.3909 | [7 empty] | CATEGORYB | SINGLE | KNOLL 230 - POSTROCK6 230.00 230KV CKT 1 | 0 | 530558 | KNOLL 6 230.00 | 530584 | POSTROCK6 230.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2545514SP | FROM->TO | HAYS PLANT - VINE STREET 115KV CKT 1 | EXP | MIDW | MIDW | REG E-IL | REG E-IL | 0 | 530562 | HAYS 3 115.00 | 530591 | VINE 3 115.00 | 0 |  | 1 | 17SP | 80 | 88 | 0 |  | 67.4264 | 103.3909 | [7 empty] | CATEGORYB | SINGLE | KNOLL 230 - POSTROCK6 230.00 230KV CKT 1 | 0 | 530558 | KNOLL 6 230.00 | 530584 | POSTROCK6 230.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2545514SP | FROM->TO | HAYS PLANT - VINE STREET 115KV CKT 1 | EXP | MIDW | MIDW | REG E-IL | REG E-IL | 0 | 530562 | HAYS 3 115.00 | 530591 | VINE 3 115.00 | 0 |  | 1 | 17SP | 80 | 88 | 0 |  | 67.4264 | 103.3909 | [7 empty] | CATEGORYB | SINGLE | KNOLL 230 - POSTROCK6 230.00 230KV CKT 1 | 0 | 530558 | KNOLL 6 230.00 | 530584 | POSTROCK6 230.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2545514SP | FROM->TO | HAYS PLANT - VINE STREET 115KV CKT 1 | EXP | MIDW | MIDW | REG E-IL | REG E-IL | 0 | 530562 | HAYS 3 115.00 | 530591 | VINE 3 115.00 | 0 |  | 1 | 17SP | 80 | 88 | 0 |  | 67.4264 | 103.3909 | [7 empty] | CATEGORYB | SINGLE | KNOLL 230 - POSTROCK6 230.00 230KV CKT 1 | 0 | 530558 | KNOLL 6 230.00 | 530584 | POSTROCK6 230.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2545514SP | FROM->TO | HAYS PLANT - VINE STREET 115KV CKT 1 | EXP | MIDW | MIDW | REG E-IL | REG E-IL | 0 | 530562 | HAYS 3 115.00 | 530591 | VINE 3 115.00 | 0 |  | 1 | 17SP | 80 | 88 | 0 |  | 67.4264 | 103.3909 | [7 empty] | CATEGORYB | SINGLE | KNOLL 230 - POSTROCK6 230.00 230KV CKT 1 | 0 | 530558 | KNOLL 6 230.00 | 530584 | POSTROCK6 230.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2545514SP | FROM->TO | HAYS PLANT - VINE STREET 115KV CKT 1 | EXP | MIDW | MIDW | REG E-IL | REG E-IL | 0 | 530562 | HAYS 3 115.00 | 530591 | VINE 3 115.00 | 0 |  | 1 | 17SP | 80 | 88 | 0 |  | 67.4264 | 103.3909 | [7 empty] | CATEGORYB | SINGLE | KNOLL 230 - POSTROCK6 230.00 230KV CKT 1 | 0 | 530558 | KNOLL 6 230.00 | 530584 | POSTROCK6 230.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2545514SP | FROM->TO | HAYS PLANT - VINE STREET 115KV CKT 1 | EXP | MIDW | MIDW | REG E-IL | REG E-IL | 0 | 530562 | HAYS 3 115.00 | 530591 | VINE 3 115.00 | 0 |  | 1 | 17SP | 80 | 88 | 0 |  | 67.4264 | 103.3909 | [7 empty] | CATEGORYB | SINGLE | KNOLL 230 - POSTROCK6 230.00 230KV CKT 1 | 0 | 530558 | KNOLL 6 230.00 | 530584 | POSTROCK6 230.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2545514SP | FROM->TO | HAYS PLANT - VINE STREET 115KV CKT 1 | EXP | MIDW | MIDW | REG E-IL | REG E-IL | 0 | 530562 | HAYS 3 115.00 | 530591 | VINE 3 115.00 | 0 |  | 1 | 17SP | 80 | 88 | 0 |  | 67.4264 | 103.3909 | [7 empty] | CATEGORYB | SINGLE | KNOLL 230 - POSTROCK6 230.00 230KV CKT 1 | 0 | 530558 | KNOLL 6 230.00 | 530584 | POSTROCK6 230.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2545514SP | FROM->TO | HAYS PLANT - VINE STREET 115KV CKT 1 | EXP | MIDW | MIDW | REG E-IL | REG E-IL | 0 | 530562 | HAYS 3 115.00 | 530591 | VINE 3 115.00 | 0 |  | 1 | 17SP | 80 | 88 | 0 |  | 67.4264 | 103.3909 | [7 empty] | CATEGORYB | SINGLE | KNOLL 230 - POSTROCK6 230.00 230KV CKT 1 | 0 | 530558 | KNOLL 6 230.00 | 530584 | POSTROCK6 230.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2545514SP | FROM->TO | HAYS PLANT - VINE STREET 115KV CKT 1 | EXP | MIDW | MIDW | REG E-IL | REG E-IL | 0 | 530562 | HAYS 3 115.00 | 530591 | VINE 3 115.00 | 0 |  | 1 | 17SP | 80 | 88 | 0 |  | 67.4264 | 103.3909 | [7 empty] | CATEGORYB | SINGLE | KNOLL 230 - POSTROCK6 230.00 230KV CKT 1 | 0 | 530558 | KNOLL 6 230.00 | 530584 | POSTROCK6 230.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2545514SP | FROM->TO | HAYS PLANT - VINE STREET 115KV CKT 1 | EXP | MIDW | MIDW | REG E-IL | REG E-IL | 0 | 530562 | HAYS 3 115.00 | 530591 | VINE 3 115.00 | 0 |  | 1 | 17SP | 80 | 88 | 0 |  | 67.4264 | 103.3909 | [7 empty] | CATEGORYB | SINGLE | KNOLL 230 - POSTROCK6 230.00 230KV CKT 1 | 0 | 530558 | KNOLL 6 230.00 | 530584 | POSTROCK6 230.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T21515522SP | FROM->TO | HITCHLAND INTERCHANGE (H TP80148301) 230/115/13.2KV TRANSFORMER CKT 1 | EXP | SPS | SPS | SPS-OKLA | SPS-OKLA | 1 | 523095 | HITCHLAND 6230.00 | 523093 | HITCHLAND 3115.00 | 523092 | HITCHLD_TR1113.200 | 1 | 22SP | 250 | 250 | 0 | 99.3378 | 99.3378 | 101.5409 | [7 empty] | CATEGORYB | SINGLE | MOORE COUNTY INTERCHANGE (ENRCO 136402) 230/115/13.2KV TRANSFORMER CKT 1 | 1 | 523308 | MOORE_E 3115.00 | 523309 | MOORE_CNTY 6230.00 | 523302 | MOORE_TR1 113.200 | 1 |  |  |  | SPS | HITCHLAND INTERCHANGE () 230/115/13.2KV TRANSFORMER CKT 2 | Install 2nd 230/115 kV, 150 MVA Autotransformer at Hitchland Interchange | [5 empty] | 24 | 24 | [5 empty] | 4220694 | 2011-09-12 | [39 empty] | 2018-06-01 | 2018-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2625517SP | TO->FROM | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | S | WERE | WERE | NEAST | NEAST | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 | 17SP | 1076 | 1076 | 0 | 94.8673 | 94.8673 | 100.6952 | [7 empty] | CATEGORYB | SINGLE | JEFFREY ENERGY CENTER - MORRIS COUNTY 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532770 | MORRIS 7 345.00 | 0 |  | 1 |  |  |  | WERE | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | Rebuild the JEC - Hoyt 345kV line as a single circuit with new conductor, poles, and shield wire. Substation work at JEC (Station 1) substation will include removal of 345kV carrier equipment and installation of new fiber optic relay panels. Substation | [5 empty] | 48 | 48 |  |  |  |  | Includes redispatch requirements | 49623119 | 2011-03-27 | [39 empty] | 2014-06-01 | 2018-06-01
2005-AG2 | [10 empty] | HUGO POWER PLANT - VALLIANT 138KV CKT 1 | U | WFEC | AEPW |  |  | 0 | 521157 | HUGO PP4 138 | 510911 | VALIANT4 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | AEPW | HUGO POWER PLANT - VALLIANT 345 KV AEPW | Vallient 345 KV line terminal | [53 empty] | 2012-07-01 | 2012-07-01
2005-AG2 | [10 empty] | HUGO POWER PLANT - VALLIANT 345KV CKT 1 AEPW | U | WFEC | AEPW |  |  | 0 | 521157 | HUGO PP4 138 | 510911 | VALIANT4 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | AEPW | HUGO POWER PLANT - VALLIANT 345KV CKT 1 AEPW | Vallient 345 KV line terminal | [53 empty] | 2012-07-01 | 2012-07-01
2005-AG2 | [10 empty] | HUGO POWER PLANT - VALLIANT 345KV CKT 1 WFEC | U | WFEC | AEPW |  |  | 0 | 521157 | HUGO PP4 138 | 510911 | VALIANT4 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | WFEC | HUGO POWER PLANT - VALLIANT 345KV CKT 1 WFEC | New 19 miles 345 KV | [53 empty] | 2012-07-01 | 2012-07-01
2005-AG2 | [10 empty] | HUGO POWER PLANT 345/138KV TRANSFORMER CKT 1 | U | WFEC | AEPW |  |  | 1 | 521157 | HUGO PP4 138 | 520948 | HUGO PP4 138.00 | 521189 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | WFEC | HUGO POWER PLANT 345/138KV TRANSFORMER CKT 1 | New 345/138 kv Auto | [53 empty] | 2012-07-01 | 2012-07-01
GEN | [10 empty] | KELLY - MADISONCO 230.00 230KV CKT 1 | U | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 560006 | MADISONCO 230.00 | 640133 | COLMBUS4 230.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | NPPD | KELLY - MADISONCO 230.00 230KV CKT 1 | Raise structures and line clearances as necessary to re-rate the transmission line to 320MVA | 320 | 320 |  |  |  | 24 | 24 | [5 empty] | 480000 | 2011-01-01 | [39 empty] | 2013-10-01 | 2014-11-01
2006-AG1 | [10 empty] | KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1 | U | OKGE |  |  |  | 1 | 514795 | KNOBHIL4 138 | 514794 | KNOBHIL269.0 | 515732 | KNOBHIL113.2 | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | OKGE | KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1 | Replace bus tie with 100MVA transformer | [53 empty] | 2006-06-01 | 2008-06-01
NA | [10 empty] | LACYGNE - WEST GARDNER 345KV CKT 1 | U | KACP | KACP |  |  | 0 | 542981 | LACYGNE7 | 542965 | W.GRDNR7 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | KACP | LACYGNE - WEST GARDNER 345KV CKT 1 | KCPL Sponsored Project to Reconductor Line to be In-Service by 6/1/2006 | [53 empty] | 2006-06-01 | 2006-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8945513SP | TO->FROM | LAKE CREEK - LONEWOLF 69KV CKT 1 | CP | WFEC | WFEC | AEP-CS | AEP-CS | 0 | 520982 | LONEWLF2 69.000 | 520978 | LKCREEK2 69.000 | 0 |  | 1 | 13SP | 48 | 48 | 48 | 78.9445 | 78.9445 | 106.2567 | [7 empty] | CATEGORYB | SINGLE | ELK CITY (ELKCTY-4) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 511458 | ELKCTY-4 138.00 | 511459 | ELKCTY-2 69.000 | 511493 | ELKC4-1 13.800 | 1 |  |  |  | WFEC | LAKE CREEK - LONEWOLF 69KV CKT 1 | Reset CT | 53 | 65 |  |  |  | 12 | 12 | [5 empty] | 350000 | 2010-01-01 | [39 empty] | 2013-06-01 | 2015-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T14105517SP | TO->FROM | LAKE CREEK - LONEWOLF 69KV CKT 1 | CP | WFEC | WFEC | AEP-CS | AEP-CS | 0 | 520982 | LONEWLF2 69.000 | 520978 | LKCREEK2 69.000 | 0 |  | 1 | 17SP | 48 | 48 | 48 | 79.1058 | 79.1058 | 107.4323 | [7 empty] | CATEGORYB | SINGLE | ELK CITY (ELKCTY-4) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 511458 | ELKCTY-4 138.00 | 511459 | ELKCTY-2 69.000 | 511493 | ELKC4-1 13.800 | 1 |  |  |  | WFEC | LAKE CREEK - LONEWOLF 69KV CKT 1 | Reset CT | 53 | 65 |  |  |  | 12 | 12 | [5 empty] | 350000 | 2010-01-01 | [39 empty] | 2013-06-01 | 2015-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T18195022SP | TO->FROM | LAKE CREEK - LONEWOLF 69KV CKT 1 | CP | WFEC | WFEC | AEP-CS | AEP-CS | 0 | 520982 | LONEWLF2 69.000 | 520978 | LKCREEK2 69.000 | 0 |  | 1 | 22SP | 48 | 48 | 48 | 87.5355 | 87.5355 | 109.6389 | [7 empty] | CATEGORYB | SINGLE | ELK CITY (ELKCTY-4) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 511458 | ELKCTY-4 138.00 | 511459 | ELKCTY-2 69.000 | 511493 | ELKC4-1 13.800 | 1 |  |  |  | WFEC | LAKE CREEK - LONEWOLF 69KV CKT 1 | Reset CT | 53 | 65 |  |  |  | 12 | 12 | [5 empty] | 350000 | 2010-01-01 | [39 empty] | 2013-06-01 | 2015-06-01
2011-AG2 | [10 empty] | LAKE CREEK - LONEWOLF 69KV CKT 1 | U | WFEC | WFEC | AEP-CS | AEP-CS | 0 | 520982 | LONEWLF2 69.000 | 520978 | LKCREEK2 69.000 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | WFEC | LAKE CREEK - LONEWOLF 69KV CKT 1 | Reset CT | 53 | 65 |  |  |  | 12 | 12 | [5 empty] | 350000 | 2010-01-01 | [39 empty] | 2013-06-01 | 2015-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4465513SP | FROM->TO | LAMAR 161/69KV TRANSFORMER CKT 1 | S | AECI | AECI | KAMO | KAMO | 0 | 300794 | 5LAMAR 161.00 | 300651 | 2LAMR 69.000 | 0 |  | 1 | 13SP | 84 | 84 | 0 | 111.3 | 111.3457 | 114.9471 | [7 empty] | CATEGORYB | SINGLE | 7JASPER 345.00 - MORGAN 345KV CKT 1 | 0 | 300045 | 7MORGAN 345.00 | 300949 | 7JASPER 345.00 | 0 |  | 1 |  |  |  | AECI | LAMAR 161/69KV TRANSFORMER CKT 1 | Replace with 112 MVA unit | [5 empty] | 24 | 24 | [5 empty] | 2500000 | 2012-07-26 | [39 empty] | 2013-06-01 | 2016-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3905517SP | FROM->TO | LAMAR 161/69KV TRANSFORMER CKT 1 | S | AECI | AECI | KAMO | KAMO | 0 | 300794 | 5LAMAR 161.00 | 300651 | 2LAMR 69.000 | 0 |  | 1 | 17SP | 84 | 84 | 0 | 113.2 | 113.2066 | 118.6915 | [7 empty] | CATEGORYB | SINGLE | 7JASPER 345.00 - MORGAN 345KV CKT 1 | 0 | 300045 | 7MORGAN 345.00 | 300949 | 7JASPER 345.00 | 0 |  | 1 |  |  |  | AECI | LAMAR 161/69KV TRANSFORMER CKT 1 | Replace with 112 MVA unit | [5 empty] | 24 | 24 | [5 empty] | 2500000 | 2012-07-26 | [39 empty] | 2013-06-01 | 2016-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T5295522SP | FROM->TO | LAMAR 161/69KV TRANSFORMER CKT 1 | S | AECI | AECI | KAMO | KAMO | 0 | 300794 | 5LAMAR 161.00 | 300651 | 2LAMR 69.000 | 0 |  | 1 | 22SP | 84 | 84 | 0 | 121.0587 | 121.0587 | 125.6801 | [7 empty] | CATEGORYB | SINGLE | 7JASPER 345.00 - MORGAN 345KV CKT 1 | 0 | 300045 | 7MORGAN 345.00 | 300949 | 7JASPER 345.00 | 0 |  | 1 |  |  |  | AECI | LAMAR 161/69KV TRANSFORMER CKT 1 | Replace with 112 MVA unit | [5 empty] | 24 | 24 | [5 empty] | 2500000 | 2012-07-26 | [39 empty] | 2013-06-01 | 2016-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T5365522SP | FROM->TO | LAMAR 161/69KV TRANSFORMER CKT 1 | S | AECI | AECI | KAMO | KAMO | 0 | 300794 | 5LAMAR 161.00 | 300651 | 2LAMR 69.000 | 0 |  | 1 | 22SP | 84 | 84 | 0 | 105.8 | 105.7666 | 104.7057 | [7 empty] | CATEGORYB | SINGLE | CLARK 161/69KV TRANSFORMER CKT 1 | 0 | 300070 | 5CLARK 161.00 | 300802 | 2CLARK 69.000 | 0 |  | 1 |  |  |  | AECI | LAMAR 161/69KV TRANSFORMER CKT 1 | Replace with 112 MVA unit | [5 empty] | 24 | 24 | [5 empty] | 2500000 | 2012-07-26 | [39 empty] | 2013-06-01 | 2016-06-01
GI | [10 empty] | LYONS - RICE_CO 115KV CKT 1 | U | MIDW | WERE |  |  | 0 | 530623 | RICE 3 115.00 | 530620 | LYONS 3 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | MIDW | LYONS - RICE_CO 115KV CKT 1 | Rebuild 11.7 mile line | [53 empty] | 2012-10-01 | 2013-04-01
GI | [10 empty] | LYONS - WHEATLAND 115KV CKT 1 #1 | U | WERE | WERE |  |  | 0 | 530620 | LYONS 3 115.00 | 533439 | WHEATLD3 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | WERE | LYONS - WHEATLAND 115KV CKT 1 #1 | Replace CTs | [53 empty] | 2012-10-01 | 2013-07-15
GI | [10 empty] | LYONS - WHEATLAND 115KV CKT 1 #2 | U | WERE | WERE |  |  | 0 | 530620 | LYONS 3 115.00 | 533439 | WHEATLD3 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | WERE | LYONS - WHEATLAND 115KV CKT 1 #2 | Rerate circuit to 1000 amps | [53 empty] | 2012-10-01 | 2013-07-15
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4415513SP | TO->FROM | MARYVILLE - MIDWAY 161KV CKT 1 | EXP | GMO | GMO |  |  | 0 | 541369 | MIDWAY_5 161.00 | 541251 | MARYVLE5 161.00 | 0 |  | 1 | 13SP | 152 | 171 | 171 | 98.8 | 98.7934 | 100.5994 | [7 empty] | CATEGORYB | SINGLE | FAIRPORT 345/161KV TRANSFORMER CKT 3 | 0 | 300039 | 7FAIRPT 345.00 | 300076 | 5FAIRPT 161.00 | 0 |  | 3 |  |  |  | MPU | MIDWAY - ST JOE 161KV CKT 1 Reactor | Install 6% series reactors on the Midway - St. Joseph 161KV line. Reactor will be installed at the St. Joseph bus. | [12 empty] | 440733 | 2014-06-01 | [39 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3855517SP | TO->FROM | MARYVILLE - MIDWAY 161KV CKT 1 | EXP | GMO | GMO |  |  | 0 | 541369 | MIDWAY_5 161.00 | 541251 | MARYVLE5 161.00 | 0 |  | 1 | 17SP | 152 | 171 | 171 | 96.7435 | 96.7435 | 101.2553 | [7 empty] | CATEGORYB | SINGLE | FAIRPORT 345/161KV TRANSFORMER CKT 3 | 0 | 300039 | 7FAIRPT 345.00 | 300076 | 5FAIRPT 161.00 | 0 |  | 3 |  |  |  | MPU | MIDWAY - ST JOE 161KV CKT 1 Reactor | Install 6% series reactors on the Midway - St. Joseph 161KV line. Reactor will be installed at the St. Joseph bus. | [12 empty] | 440733 | 2014-06-01 | [39 empty] | 2013-06-01 | 2014-06-01
GEN-2006-010 | [10 empty] | MCNAB REC - TURK 115KV CKT 1 | U | AEPW | AEPW | SARK | SARKAECC | 0 | 504122 | MCNAB 3 115.00 | 507456 | HEMPSTD3 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | AEPW | MCNAB REC - TURK 115KV CKT 1 | Build a new two mile, 138 kV, 1590 ACSR line section (operated at 115 kV) from Turk Substation to the existing Okay- Hope 115 kV line to form a Turk - Hope 115 kV line. | [53 empty] | 2012-07-01 | 2012-07-01
2007-AG3 | [10 empty] | MEDICINE LODGE - SAWYER 115KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539673 | MED-LDG3 115.00 | 539649 | SAWYER 3 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | MKEC | MEDICINE LODGE - SAWYER 115KV CKT 1 | Rebuild line | [53 empty] | 2009-12-01 | 2013-06-01
2007-AG3 | [10 empty] | MEDICINE LODGE (MED-LDG4) 138/115/2.72KV TRANSFORMER CKT 1 | U | MKEC |  |  |  | 2 | 539674 | MED-LDG4 138.00 | 539673 | MED-LDG3 115.00 | 539917 | MEDLGT-T 2.7200 | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | MKEC | MEDICINE LODGE 138/115KV TRANSFORMER CKT 1 Displacement | Upgrade transformer | [53 empty] | 2009-12-01 | 2013-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4425513SP | TO->FROM | MIDWAY - ST JOE 161KV CKT 1 | EXP | GMO | GMO |  |  | 0 | 541253 | ST JOE 5 161.00 | 541369 | MIDWAY_5 161.00 | 0 |  | 1 | 13SP | 152 | 171 | 171 | 109.0316 | 109.0316 | 110.8905 | [7 empty] | CATEGORYB | SINGLE | FAIRPORT 345/161KV TRANSFORMER CKT 3 | 0 | 300039 | 7FAIRPT 345.00 | 300076 | 5FAIRPT 161.00 | 0 |  | 3 |  |  |  | MPU | MIDWAY - ST JOE 161KV CKT 1 Reactor | Install 6% series reactors on the Midway - St. Joseph 161KV line. Reactor will be installed at the St. Joseph bus. | [12 empty] | 440733 | 2014-06-01 | [39 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T14555513SP | TO->FROM | MIDWAY - ST JOE 161KV CKT 1 | EXP | GMO | GMO |  |  | 0 | 541253 | ST JOE 5 161.00 | 541369 | MIDWAY_5 161.00 | 0 |  | 1 | 13SP | 152 | 171 | 171 | 106.3 | 106.3328 | 107.3185 | [7 empty] | CATEGORYB | NONSINGLE | LN-FAIRPORT | 0 | 0 |  | 0 |  | 0 | [5 empty] | MPU | MIDWAY - ST JOE 161KV CKT 1 Reactor | Install 6% series reactors on the Midway - St. Joseph 161KV line. Reactor will be installed at the St. Joseph bus. | [12 empty] | 440733 | 2014-06-01 | [39 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3865517SP | TO->FROM | MIDWAY - ST JOE 161KV CKT 1 | EXP | GMO | GMO |  |  | 0 | 541253 | ST JOE 5 161.00 | 541369 | MIDWAY_5 161.00 | 0 |  | 1 | 17SP | 152 | 171 | 171 | 107.6 | 107.6046 | 112.1758 | [7 empty] | CATEGORYB | SINGLE | FAIRPORT 345/161KV TRANSFORMER CKT 3 | 0 | 300039 | 7FAIRPT 345.00 | 300076 | 5FAIRPT 161.00 | 0 |  | 3 |  |  |  | MPU | MIDWAY - ST JOE 161KV CKT 1 Reactor | Install 6% series reactors on the Midway - St. Joseph 161KV line. Reactor will be installed at the St. Joseph bus. | [12 empty] | 440733 | 2014-06-01 | [39 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T20285517SP | TO->FROM | MIDWAY - ST JOE 161KV CKT 1 | EXP | GMO | GMO |  |  | 0 | 541253 | ST JOE 5 161.00 | 541369 | MIDWAY_5 161.00 | 0 |  | 1 | 17SP | 152 | 171 | 171 | 105.8 | 105.8396 | 109.7665 | [7 empty] | CATEGORYB | NONSINGLE | LN-FAIRPORT | 0 | 0 |  | 0 |  | 0 | [5 empty] | MPU | MIDWAY - ST JOE 161KV CKT 1 Reactor | Install 6% series reactors on the Midway - St. Joseph 161KV line. Reactor will be installed at the St. Joseph bus. | [12 empty] | 440733 | 2014-06-01 | [39 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19195514SP | TO->FROM | MIDWAY - ST JOE 161KV CKT 1 | EXP | GMO | GMO |  |  | 0 | 541253 | ST JOE 5 161.00 | 541369 | MIDWAY_5 161.00 | 0 |  | 1 | 17SP | 152 | 171 | 171 |  | 105.1888 | 105.5381 | [7 empty] | CATEGORYB | NONSINGLE | SPP-2006-001 | 0 | 0 |  | 0 |  | 0 | [5 empty] | MPU | MIDWAY - ST JOE 161KV CKT 1 Reactor | Install 6% series reactors on the Midway - St. Joseph 161KV line. Reactor will be installed at the St. Joseph bus. | [12 empty] | 440733 | 2014-06-01 | [39 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1255513WP | FROM->TO | MOUNDRIDGE (MOUND10X) 138/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE | WERE | WEST | SCENTRAL | 2 | 533429 | MOUNDRG3 115.00 | 533013 | MOUND 4 138.00 | 533096 | MOUNDRI1 13.800 | 1 | 13WP | 100 | 110 | 125 | 104.4546 | 104.4546 | 113.2983 | [7 empty] | CATEGORYB | SINGLE | RENO COUNTY - WICHITA 345KV CKT 1 | 0 | 532771 | RENO 7 345.00 | 532796 | WICHITA7 345.00 | 0 |  | 1 |  |  |  | WERE | MOUNDRIDGE 138/115KV TRANSFORMER CKT 2 | Install second 138/115 kV transformer at Moundridge. Operate both 138/115 kV transformers normally closed. | 100 | 110 |  |  |  | 24 | 24 | [46 empty] | 2013-10-01 | 2014-12-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3215513SP | TO->FROM | MULLERGREN - SPEARVILLE 230KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539695 | SPEARVL6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | 13SP | 330.3 | 355.3 | 0 | 87.7216 | 87.7216 | 100.1652 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3215513SP | TO->FROM | MULLERGREN - SPEARVILLE 230KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539695 | SPEARVL6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | 13SP | 330.3 | 355.3 | 0 | 87.7216 | 87.7216 | 100.1652 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3215513SP | TO->FROM | MULLERGREN - SPEARVILLE 230KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539695 | SPEARVL6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | 13SP | 330.3 | 355.3 | 0 | 87.7216 | 87.7216 | 100.1652 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3215513SP | TO->FROM | MULLERGREN - SPEARVILLE 230KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539695 | SPEARVL6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | 13SP | 330.3 | 355.3 | 0 | 87.7216 | 87.7216 | 100.1652 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3215513SP | TO->FROM | MULLERGREN - SPEARVILLE 230KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539695 | SPEARVL6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | 13SP | 330.3 | 355.3 | 0 | 87.7216 | 87.7216 | 100.1652 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3215513SP | TO->FROM | MULLERGREN - SPEARVILLE 230KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539695 | SPEARVL6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | 13SP | 330.3 | 355.3 | 0 | 87.7216 | 87.7216 | 100.1652 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3215513SP | TO->FROM | MULLERGREN - SPEARVILLE 230KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539695 | SPEARVL6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | 13SP | 330.3 | 355.3 | 0 | 87.7216 | 87.7216 | 100.1652 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3215513SP | TO->FROM | MULLERGREN - SPEARVILLE 230KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539695 | SPEARVL6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | 13SP | 330.3 | 355.3 | 0 | 87.7216 | 87.7216 | 100.1652 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3215513SP | TO->FROM | MULLERGREN - SPEARVILLE 230KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539695 | SPEARVL6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | 13SP | 330.3 | 355.3 | 0 | 87.7216 | 87.7216 | 100.1652 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3215513SP | TO->FROM | MULLERGREN - SPEARVILLE 230KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539695 | SPEARVL6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | 13SP | 330.3 | 355.3 | 0 | 87.7216 | 87.7216 | 100.1652 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3215513SP | TO->FROM | MULLERGREN - SPEARVILLE 230KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539695 | SPEARVL6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | 13SP | 330.3 | 355.3 | 0 | 87.7216 | 87.7216 | 100.1652 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2585514SP | TO->FROM | MULLERGREN - SPEARVILLE 230KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539695 | SPEARVL6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | 17SP | 330.3 | 355.3 | 0 |  | 96.6511 | 140.1461 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2585514SP | TO->FROM | MULLERGREN - SPEARVILLE 230KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539695 | SPEARVL6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | 17SP | 330.3 | 355.3 | 0 |  | 96.6511 | 140.1461 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2585514SP | TO->FROM | MULLERGREN - SPEARVILLE 230KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539695 | SPEARVL6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | 17SP | 330.3 | 355.3 | 0 |  | 96.6511 | 140.1461 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2585514SP | TO->FROM | MULLERGREN - SPEARVILLE 230KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539695 | SPEARVL6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | 17SP | 330.3 | 355.3 | 0 |  | 96.6511 | 140.1461 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2585514SP | TO->FROM | MULLERGREN - SPEARVILLE 230KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539695 | SPEARVL6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | 17SP | 330.3 | 355.3 | 0 |  | 96.6511 | 140.1461 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2585514SP | TO->FROM | MULLERGREN - SPEARVILLE 230KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539695 | SPEARVL6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | 17SP | 330.3 | 355.3 | 0 |  | 96.6511 | 140.1461 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2585514SP | TO->FROM | MULLERGREN - SPEARVILLE 230KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539695 | SPEARVL6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | 17SP | 330.3 | 355.3 | 0 |  | 96.6511 | 140.1461 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2585514SP | TO->FROM | MULLERGREN - SPEARVILLE 230KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539695 | SPEARVL6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | 17SP | 330.3 | 355.3 | 0 |  | 96.6511 | 140.1461 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2585514SP | TO->FROM | MULLERGREN - SPEARVILLE 230KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539695 | SPEARVL6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | 17SP | 330.3 | 355.3 | 0 |  | 96.6511 | 140.1461 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2585514SP | TO->FROM | MULLERGREN - SPEARVILLE 230KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539695 | SPEARVL6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | 17SP | 330.3 | 355.3 | 0 |  | 96.6511 | 140.1461 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2585514SP | TO->FROM | MULLERGREN - SPEARVILLE 230KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539695 | SPEARVL6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | 17SP | 330.3 | 355.3 | 0 |  | 96.6511 | 140.1461 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T14255514SP | TO->FROM | MULLERGREN - SPEARVILLE 230KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539695 | SPEARVL6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | 17SP | 330.3 | 355.3 | 0 |  | 73.8896 | 106.2791 | [7 empty] | CATEGORYB | SINGLE | POST ROCK (POSTROCK T1) 345/230/13.8KV TRANSFORMER CKT 1 | 1 | 530583 | POSTROCK7 345.00 | 530584 | POSTROCK6 230.00 | 530673 | POSTROCK1 13.800 | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T14255514SP | TO->FROM | MULLERGREN - SPEARVILLE 230KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539695 | SPEARVL6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | 17SP | 330.3 | 355.3 | 0 |  | 73.8896 | 106.2791 | [7 empty] | CATEGORYB | SINGLE | POST ROCK (POSTROCK T1) 345/230/13.8KV TRANSFORMER CKT 1 | 1 | 530583 | POSTROCK7 345.00 | 530584 | POSTROCK6 230.00 | 530673 | POSTROCK1 13.800 | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T14255514SP | TO->FROM | MULLERGREN - SPEARVILLE 230KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539695 | SPEARVL6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | 17SP | 330.3 | 355.3 | 0 |  | 73.8896 | 106.2791 | [7 empty] | CATEGORYB | SINGLE | POST ROCK (POSTROCK T1) 345/230/13.8KV TRANSFORMER CKT 1 | 1 | 530583 | POSTROCK7 345.00 | 530584 | POSTROCK6 230.00 | 530673 | POSTROCK1 13.800 | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T14255514SP | TO->FROM | MULLERGREN - SPEARVILLE 230KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539695 | SPEARVL6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | 17SP | 330.3 | 355.3 | 0 |  | 73.8896 | 106.2791 | [7 empty] | CATEGORYB | SINGLE | POST ROCK (POSTROCK T1) 345/230/13.8KV TRANSFORMER CKT 1 | 1 | 530583 | POSTROCK7 345.00 | 530584 | POSTROCK6 230.00 | 530673 | POSTROCK1 13.800 | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T14255514SP | TO->FROM | MULLERGREN - SPEARVILLE 230KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539695 | SPEARVL6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | 17SP | 330.3 | 355.3 | 0 |  | 73.8896 | 106.2791 | [7 empty] | CATEGORYB | SINGLE | POST ROCK (POSTROCK T1) 345/230/13.8KV TRANSFORMER CKT 1 | 1 | 530583 | POSTROCK7 345.00 | 530584 | POSTROCK6 230.00 | 530673 | POSTROCK1 13.800 | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T14255514SP | TO->FROM | MULLERGREN - SPEARVILLE 230KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539695 | SPEARVL6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | 17SP | 330.3 | 355.3 | 0 |  | 73.8896 | 106.2791 | [7 empty] | CATEGORYB | SINGLE | POST ROCK (POSTROCK T1) 345/230/13.8KV TRANSFORMER CKT 1 | 1 | 530583 | POSTROCK7 345.00 | 530584 | POSTROCK6 230.00 | 530673 | POSTROCK1 13.800 | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T14255514SP | TO->FROM | MULLERGREN - SPEARVILLE 230KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539695 | SPEARVL6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | 17SP | 330.3 | 355.3 | 0 |  | 73.8896 | 106.2791 | [7 empty] | CATEGORYB | SINGLE | POST ROCK (POSTROCK T1) 345/230/13.8KV TRANSFORMER CKT 1 | 1 | 530583 | POSTROCK7 345.00 | 530584 | POSTROCK6 230.00 | 530673 | POSTROCK1 13.800 | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T14255514SP | TO->FROM | MULLERGREN - SPEARVILLE 230KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539695 | SPEARVL6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | 17SP | 330.3 | 355.3 | 0 |  | 73.8896 | 106.2791 | [7 empty] | CATEGORYB | SINGLE | POST ROCK (POSTROCK T1) 345/230/13.8KV TRANSFORMER CKT 1 | 1 | 530583 | POSTROCK7 345.00 | 530584 | POSTROCK6 230.00 | 530673 | POSTROCK1 13.800 | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T14255514SP | TO->FROM | MULLERGREN - SPEARVILLE 230KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539695 | SPEARVL6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | 17SP | 330.3 | 355.3 | 0 |  | 73.8896 | 106.2791 | [7 empty] | CATEGORYB | SINGLE | POST ROCK (POSTROCK T1) 345/230/13.8KV TRANSFORMER CKT 1 | 1 | 530583 | POSTROCK7 345.00 | 530584 | POSTROCK6 230.00 | 530673 | POSTROCK1 13.800 | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T14255514SP | TO->FROM | MULLERGREN - SPEARVILLE 230KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539695 | SPEARVL6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | 17SP | 330.3 | 355.3 | 0 |  | 73.8896 | 106.2791 | [7 empty] | CATEGORYB | SINGLE | POST ROCK (POSTROCK T1) 345/230/13.8KV TRANSFORMER CKT 1 | 1 | 530583 | POSTROCK7 345.00 | 530584 | POSTROCK6 230.00 | 530673 | POSTROCK1 13.800 | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T14255514SP | TO->FROM | MULLERGREN - SPEARVILLE 230KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539695 | SPEARVL6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | 17SP | 330.3 | 355.3 | 0 |  | 73.8896 | 106.2791 | [7 empty] | CATEGORYB | SINGLE | POST ROCK (POSTROCK T1) 345/230/13.8KV TRANSFORMER CKT 1 | 1 | 530583 | POSTROCK7 345.00 | 530584 | POSTROCK6 230.00 | 530673 | POSTROCK1 13.800 | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1275513WP | TO->FROM | MUND - PENTAGON 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533261 | PENTAGN3 115.00 | 533282 | MUND 3 115.00 | 0 |  | 1 | 13WP | 173 | 206 | 0 | 93.722 | 93.722 | 101.9127 | [7 empty] | CATEGORYB | SINGLE | 87th STREET - CRAIG 345KV CKT 1 | 0 | 532775 | 87TH 7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  |  |  | KACP | IATAN - NASHUA 345KV CKT 1 | Tap Nashua 345kV bus in Hawthorn - St. Joseph 345 kV line. Build new 345 kV line from Iatan to Nashua,Add Nashua 345/161 kV | [53 empty] | 2013-06-01 | 2015-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3075514SP | TO->FROM | MUND - PENTAGON 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533261 | PENTAGN3 115.00 | 533282 | MUND 3 115.00 | 0 |  | 1 | 17SP | 173 | 206 | 0 |  | 91.7906 | 100.8246 | [7 empty] | CATEGORYB | SINGLE | 87th STREET - CRAIG 345KV CKT 1 | 0 | 532775 | 87TH 7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  |  |  | KACP | IATAN - NASHUA 345KV CKT 1 | Tap Nashua 345kV bus in Hawthorn - St. Joseph 345 kV line. Build new 345 kV line from Iatan to Nashua,Add Nashua 345/161 kV | [53 empty] | 2013-06-01 | 2015-06-01
GEN | [10 empty] | NELIGH - PETERSBURG 115KV CKT 1 | U | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640444 |  | 640293 | NELIGH 7 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | NPPD | NELIGH - PETERSBURG 115KV CKT 1 | Replace Breaker 1106, jumpers, and 115 kV Switch 1106-D2 at Neligh. Replace main bus at Petersburg. Upgrade and replace transmission structures on 115 kV lineto facilitate 100 degrees Centigrade line operation. | [53 empty] | 2013-01-01 | 2013-01-01
NA | [10 empty] | NORTHWEST - TATONGA 345KV CKT 1 | U | OKGE | OKGE | ENID | ENID | 0 | 515407 |  | 514880 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | OKGE | NORTHWEST - TATONGA 345KV CKT 1 | Build 345 kV line | [53 empty] | 2010-01-01 | 2010-01-01
GEN-2006-010 | [10 empty] | OKAY - TURK 138KV CKT 1 | U | AEPW | AEPW | SARK | SARK | 0 | 507454 | HEMPSTD4 138.00 | 507428 | OKAY 4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | AEPW | OKAY - TURK 138KV CKT 1 | Build two mile, 138 kV, 1590ACSR line section from Turk Sub to existing Okay-Hope 115 kV line and rebuild twelve miles of 115 kV line to Okay Sub to 138 kV, 1590 ACSR , to form a Turk-Okay 138 kV line | [53 empty] | 2012-07-01 | 2012-07-01
GEN-2006-010 | [10 empty] | OKAY 138/69KV TRANSFORMER CKT 1 | U | AEPW | AEPW | SARK | SARK | 1 | 507428 | OKAY 4 138.00 | 507427 | OKAY 2 69.000 | 507442 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | AEPW | OKAY 138/69KV TRANSFORMER CKT 1 | Replace three single-phase 115-69 kV autotransformers with one 90 MVA, three-phase 138-69 kV autotransformer and convert high side of station to 138 kV | [53 empty] | 2012-07-01 | 2012-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T9805513SP | FROM->TO | PLANT X STATION (WH ALM20171) 230/115/13.2KV TRANSFORMER CKT 1 | EXP | SPS | SPS | SPS-CNPL | SPS-CNPL | 2 | 525481 | PLANT_X 6230.00 | 525480 | PLANT_X 3115.00 | 525479 | PLANTX_TR1 113.200 | 1 | 13SP | 239 | 239 | 0 | 122.9341 | 122.9341 | 123.6156 | [7 empty] | CATEGORYB | SINGLE | LAMB COUNTY INTERCHANGE (WH ALM20172) 230/115/13.2KV TRANSFORMER CKT 1 | 1 | 525636 | LAMB_CNTY 3115.00 | 525637 | LAMB_CNTY 6230.00 | 525633 | LAMB_TR3 113.200 | 1 |  |  |  | SPS | NEWHART INTERCHANGE PROJECT | Tap the Potter Interchange - Plant X Station 230 kV line for new Newhart Substation and install 230/115 kV, 150/173 MVA transformer. New 15 mile Lampton Interchange - Hart Industrial Substation 115 kV line. New 19 mile Swisher County Interchange - Newhart | [53 empty] | 2013-06-01 | 2015-04-30
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T9805513SP | FROM->TO | PLANT X STATION (WH ALM20171) 230/115/13.2KV TRANSFORMER CKT 1 | EXP | SPS | SPS | SPS-CNPL | SPS-CNPL | 2 | 525481 | PLANT_X 6230.00 | 525480 | PLANT_X 3115.00 | 525479 | PLANTX_TR1 113.200 | 1 | 13SP | 239 | 239 | 0 | 122.9 | 122.9341 | 123.6156 | [7 empty] | CATEGORYB | SINGLE | LAMB COUNTY INTERCHANGE (WH ALM20172) 230/115/13.2KV TRANSFORMER CKT 1 | 1 | 525636 | LAMB_CNTY 3115.00 | 525637 | LAMB_CNTY 6230.00 | 525633 | LAMB_TR3 113.200 | 1 |  |  |  | SPS | NEWHART INTERCHANGE PROJECT | Tap the Potter Interchange - Plant X Station 230 kV line for new Newhart Substation and install 230/115 kV, 150/173 MVA transformer. New 15 mile Lampton Interchange - Hart Industrial Substation 115 kV line. New 19 mile Swisher County Interchange - Newhart | [53 empty] | 2013-06-01 | 2015-04-30
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T9805513SP | FROM->TO | PLANT X STATION (WH ALM20171) 230/115/13.2KV TRANSFORMER CKT 1 | EXP | SPS | SPS | SPS-CNPL | SPS-CNPL | 2 | 525481 | PLANT_X 6230.00 | 525480 | PLANT_X 3115.00 | 525479 | PLANTX_TR1 113.200 | 1 | 13SP | 239 | 239 | 0 | 122.9 | 122.9341 | 123.6156 | 526_SPS_22S_BAILEY CO- CURRY CO 115 kV_2011-05-18.idv | [6 empty] | CATEGORYB | SINGLE | LAMB COUNTY INTERCHANGE (WH ALM20172) 230/115/13.2KV TRANSFORMER CKT 1 | 1 | 525636 | LAMB_CNTY 3115.00 | 525637 | LAMB_CNTY 6230.00 | 525633 | LAMB_TR3 113.200 | 1 |  |  |  | SPS | BAILEY COUNTY INTERCHANGE - CURRY COUNTY INTERCHANGE 115KV CKT 1 | 40 miles 115 kV between Bailey and Curry. | [5 empty] | 30 | 30 | [46 empty] | 2013-06-01 | 2015-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T9805513SP | FROM->TO | PLANT X STATION (WH ALM20171) 230/115/13.2KV TRANSFORMER CKT 1 | EXP | SPS | SPS | SPS-CNPL | SPS-CNPL | 2 | 525481 | PLANT_X 6230.00 | 525480 | PLANT_X 3115.00 | 525479 | PLANTX_TR1 113.200 | 1 | 13SP | 239 | 239 | 0 | 122.9341 | 122.9341 | 123.6156 | 526_SPS_22S_BAILEY CO- CURRY CO 115 kV_2011-05-18.idv | [6 empty] | CATEGORYB | SINGLE | LAMB COUNTY INTERCHANGE (WH ALM20172) 230/115/13.2KV TRANSFORMER CKT 1 | 1 | 525636 | LAMB_CNTY 3115.00 | 525637 | LAMB_CNTY 6230.00 | 525633 | LAMB_TR3 113.200 | 1 |  |  |  | SPS | BAILEY COUNTY INTERCHANGE - CURRY COUNTY INTERCHANGE 115KV CKT 1 | 40 miles 115 kV between Bailey and Curry. | [5 empty] | 30 | 30 | [46 empty] | 2013-06-01 | 2015-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2685513SP | FROM->TO | PLANT X STATION (WH ALM20171) 230/115/13.2KV TRANSFORMER CKT 1 | EXP | SPS | SPS | SPS-CNPL | SPS-CNPL | 2 | 525481 | PLANT_X 6230.00 | 525480 | PLANT_X 3115.00 | 525479 | PLANTX_TR1 113.200 | 1 | 13SP | 239 | 239 | 0 | -999 | -999 | 123.5962 | [7 empty] | CATEGORYB | SINGLE | LAMB COUNTY INTERCHANGE - TOLK STATION WEST 230KV CKT 1 | 0 | 525531 | TOLK_WEST 6230.00 | 525637 | LAMB_CNTY 6230.00 | 0 |  | 1 |  |  |  | SPS | NEWHART INTERCHANGE PROJECT | Tap the Potter Interchange - Plant X Station 230 kV line for new Newhart Substation and install 230/115 kV, 150/173 MVA transformer. New 15 mile Lampton Interchange - Hart Industrial Substation 115 kV line. New 19 mile Swisher County Interchange - Newhart | [53 empty] | 2013-06-01 | 2015-04-30
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2685513SP | FROM->TO | PLANT X STATION (WH ALM20171) 230/115/13.2KV TRANSFORMER CKT 1 | EXP | SPS | SPS | SPS-CNPL | SPS-CNPL | 2 | 525481 | PLANT_X 6230.00 | 525480 | PLANT_X 3115.00 | 525479 | PLANTX_TR1 113.200 | 1 | 13SP | 239 | 239 | 0 | -999 | -999 | 123.5962 | 526_SPS_22S_BAILEY CO- CURRY CO 115 kV_2011-05-18.idv | [6 empty] | CATEGORYB | SINGLE | LAMB COUNTY INTERCHANGE - TOLK STATION WEST 230KV CKT 1 | 0 | 525531 | TOLK_WEST 6230.00 | 525637 | LAMB_CNTY 6230.00 | 0 |  | 1 |  |  |  | SPS | BAILEY COUNTY INTERCHANGE - CURRY COUNTY INTERCHANGE 115KV CKT 1 | 40 miles 115 kV between Bailey and Curry. | [5 empty] | 30 | 30 | [46 empty] | 2013-06-01 | 2015-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T14705513SP | FROM->TO | PLANT X STATION (WH ALM20171) 230/115/13.2KV TRANSFORMER CKT 1 | EXP | SPS | SPS | SPS-CNPL | SPS-CNPL | 2 | 525481 | PLANT_X 6230.00 | 525480 | PLANT_X 3115.00 | 525479 | PLANTX_TR1 113.200 | 1 | 13SP | 239 | 239 | 0 | 117.1053 | 117.1053 | 118.0937 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-T04 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | NEWHART INTERCHANGE PROJECT | Tap the Potter Interchange - Plant X Station 230 kV line for new Newhart Substation and install 230/115 kV, 150/173 MVA transformer. New 15 mile Lampton Interchange - Hart Industrial Substation 115 kV line. New 19 mile Swisher County Interchange - Newhart | [53 empty] | 2013-06-01 | 2015-04-30
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T14705513SP | FROM->TO | PLANT X STATION (WH ALM20171) 230/115/13.2KV TRANSFORMER CKT 1 | EXP | SPS | SPS | SPS-CNPL | SPS-CNPL | 2 | 525481 | PLANT_X 6230.00 | 525480 | PLANT_X 3115.00 | 525479 | PLANTX_TR1 113.200 | 1 | 13SP | 239 | 239 | 0 | 117.1 | 117.1053 | 118.0937 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-T04 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | NEWHART INTERCHANGE PROJECT | Tap the Potter Interchange - Plant X Station 230 kV line for new Newhart Substation and install 230/115 kV, 150/173 MVA transformer. New 15 mile Lampton Interchange - Hart Industrial Substation 115 kV line. New 19 mile Swisher County Interchange - Newhart | [53 empty] | 2013-06-01 | 2015-04-30
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T14705513SP | FROM->TO | PLANT X STATION (WH ALM20171) 230/115/13.2KV TRANSFORMER CKT 1 | EXP | SPS | SPS | SPS-CNPL | SPS-CNPL | 2 | 525481 | PLANT_X 6230.00 | 525480 | PLANT_X 3115.00 | 525479 | PLANTX_TR1 113.200 | 1 | 13SP | 239 | 239 | 0 | 117.1053 | 117.1053 | 118.0937 | 526_SPS_22S_BAILEY CO- CURRY CO 115 kV_2011-05-18.idv | [6 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-T04 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | BAILEY COUNTY INTERCHANGE - CURRY COUNTY INTERCHANGE 115KV CKT 1 | 40 miles 115 kV between Bailey and Curry. | [5 empty] | 30 | 30 | [46 empty] | 2013-06-01 | 2015-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T14705513SP | FROM->TO | PLANT X STATION (WH ALM20171) 230/115/13.2KV TRANSFORMER CKT 1 | EXP | SPS | SPS | SPS-CNPL | SPS-CNPL | 2 | 525481 | PLANT_X 6230.00 | 525480 | PLANT_X 3115.00 | 525479 | PLANTX_TR1 113.200 | 1 | 13SP | 239 | 239 | 0 | 117.1 | 117.1053 | 118.0937 | 526_SPS_22S_BAILEY CO- CURRY CO 115 kV_2011-05-18.idv | [6 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-T04 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | BAILEY COUNTY INTERCHANGE - CURRY COUNTY INTERCHANGE 115KV CKT 1 | 40 miles 115 kV between Bailey and Curry. | [5 empty] | 30 | 30 | [46 empty] | 2013-06-01 | 2015-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T14725513SP | FROM->TO | PLANT X STATION (WH ALM20171) 230/115/13.2KV TRANSFORMER CKT 1 | EXP | SPS | SPS | SPS-CNPL | SPS-CNPL | 2 | 525481 | PLANT_X 6230.00 | 525480 | PLANT_X 3115.00 | 525479 | PLANTX_TR1 113.200 | 1 | 13SP | 239 | 239 | 0 | 101.9 | 101.8711 | 102.5517 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-T66 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | NEWHART INTERCHANGE PROJECT | Tap the Potter Interchange - Plant X Station 230 kV line for new Newhart Substation and install 230/115 kV, 150/173 MVA transformer. New 15 mile Lampton Interchange - Hart Industrial Substation 115 kV line. New 19 mile Swisher County Interchange - Newhart | [53 empty] | 2013-06-01 | 2015-04-30
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T14725513SP | FROM->TO | PLANT X STATION (WH ALM20171) 230/115/13.2KV TRANSFORMER CKT 1 | EXP | SPS | SPS | SPS-CNPL | SPS-CNPL | 2 | 525481 | PLANT_X 6230.00 | 525480 | PLANT_X 3115.00 | 525479 | PLANTX_TR1 113.200 | 1 | 13SP | 239 | 239 | 0 | 101.8711 | 101.8711 | 102.5517 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-T66 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | NEWHART INTERCHANGE PROJECT | Tap the Potter Interchange - Plant X Station 230 kV line for new Newhart Substation and install 230/115 kV, 150/173 MVA transformer. New 15 mile Lampton Interchange - Hart Industrial Substation 115 kV line. New 19 mile Swisher County Interchange - Newhart | [53 empty] | 2013-06-01 | 2015-04-30
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T14725513SP | FROM->TO | PLANT X STATION (WH ALM20171) 230/115/13.2KV TRANSFORMER CKT 1 | EXP | SPS | SPS | SPS-CNPL | SPS-CNPL | 2 | 525481 | PLANT_X 6230.00 | 525480 | PLANT_X 3115.00 | 525479 | PLANTX_TR1 113.200 | 1 | 13SP | 239 | 239 | 0 | 101.9 | 101.8711 | 102.5517 | 526_SPS_22S_BAILEY CO- CURRY CO 115 kV_2011-05-18.idv | [6 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-T66 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | BAILEY COUNTY INTERCHANGE - CURRY COUNTY INTERCHANGE 115KV CKT 1 | 40 miles 115 kV between Bailey and Curry. | [5 empty] | 30 | 30 | [46 empty] | 2013-06-01 | 2015-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T14725513SP | FROM->TO | PLANT X STATION (WH ALM20171) 230/115/13.2KV TRANSFORMER CKT 1 | EXP | SPS | SPS | SPS-CNPL | SPS-CNPL | 2 | 525481 | PLANT_X 6230.00 | 525480 | PLANT_X 3115.00 | 525479 | PLANTX_TR1 113.200 | 1 | 13SP | 239 | 239 | 0 | 101.8711 | 101.8711 | 102.5517 | 526_SPS_22S_BAILEY CO- CURRY CO 115 kV_2011-05-18.idv | [6 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-T66 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | BAILEY COUNTY INTERCHANGE - CURRY COUNTY INTERCHANGE 115KV CKT 1 | 40 miles 115 kV between Bailey and Curry. | [5 empty] | 30 | 30 | [46 empty] | 2013-06-01 | 2015-06-01
2011-AG2 | AFS9 | SPP_FG-5219 - STIREDSTIPEC | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4015513SP | TO->FROM | REDEL - STILWELL 161KV CKT 1 | EXP | KCPL | KCPL | JOCO | JOCO | 0 | 542969 | STILWEL5 161.00 | 543053 | REDEL 5 161.00 | 0 |  | 1 | 13SP | 293 | 334 | 0 | 98.7536 | 98.7536 | 100.9016 | [7 empty] | CATEGORYB | SINGLE | PECULIAR - STILWELL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 |  |  |  | KACP | IATAN - NASHUA 345KV CKT 1 | Tap Nashua 345kV bus in Hawthorn - St. Joseph 345 kV line. Build new 345 kV line from Iatan to Nashua,Add Nashua 345/161 kV | [53 empty] | 2013-06-01 | 2015-06-01
GI | [10 empty] | RICE_CO 230/115KV TRANSFORMER CKT 1 | U | MIDW | MIDW |  |  | 0 | 560012 | RICECO 230.00 | 530623 | RICE 3 115.00 |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | MIDW | RICE_CO 230/115KV TRANSFORMER CKT 1 | Add 230/115kV Transformer | [53 empty] | 2012-10-01 | 2012-11-15
2011-AG2 | AFS9-ADD |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS9ADD1T2035513SP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | EXP | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-ADD |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS9ADD1T2035513SP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | EXP | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-ADD |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS9ADD1T2035513SP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | EXP | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-ADD |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS9ADD1T2035513SP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | EXP | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T9175513SP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | EXP | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 | 102.5729 | 102.5729 | 106.4646 | [7 empty] | CATEGORYB | SINGLE | WOODWARD DISTRICT EHV (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T9175513SP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | EXP | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 | 102.5729 | 102.5729 | 106.4646 | [7 empty] | CATEGORYB | SINGLE | WOODWARD DISTRICT EHV (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T9175513SP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | EXP | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 | 102.5729 | 102.5729 | 106.4646 | [7 empty] | CATEGORYB | SINGLE | WOODWARD DISTRICT EHV (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T9175513SP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | EXP | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 | 102.5729 | 102.5729 | 106.4646 | [7 empty] | CATEGORYB | SINGLE | WOODWARD DISTRICT EHV (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1785513SP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | EXP | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 | 102.5 | 102.5407 | 106.4318 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WOODWARD DISTRICT EHV 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1785513SP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | EXP | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 | 102.5 | 102.5407 | 106.4318 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WOODWARD DISTRICT EHV 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1785513SP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | EXP | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 | 102.5 | 102.5407 | 106.4318 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WOODWARD DISTRICT EHV 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1785513SP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | EXP | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 | 102.5 | 102.5407 | 106.4318 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WOODWARD DISTRICT EHV 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-ADD |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS9ADD1T2035513WP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | EXP | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 13WP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-ADD |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS9ADD1T2035513WP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | EXP | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 13WP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-ADD |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS9ADD1T2035513WP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | EXP | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 13WP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-ADD |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS9ADD1T2035513WP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | EXP | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 13WP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T5485513WP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | EXP | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 13WP | 171 | 185 | 0 | 97.4 | 97.3667 | 100.671 | [7 empty] | CATEGORYB | SINGLE | WOODWARD DISTRICT EHV (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T5485513WP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | EXP | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 13WP | 171 | 185 | 0 | 97.4 | 97.3667 | 100.671 | [7 empty] | CATEGORYB | SINGLE | WOODWARD DISTRICT EHV (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T5485513WP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | EXP | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 13WP | 171 | 185 | 0 | 97.4 | 97.3667 | 100.671 | [7 empty] | CATEGORYB | SINGLE | WOODWARD DISTRICT EHV (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T5485513WP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | EXP | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 13WP | 171 | 185 | 0 | 97.4 | 97.3667 | 100.671 | [7 empty] | CATEGORYB | SINGLE | WOODWARD DISTRICT EHV (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T715513WP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | EXP | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 13WP | 171 | 185 | 0 | 97.3423 | 97.3423 | 100.6291 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WOODWARD DISTRICT EHV 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T715513WP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | EXP | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 13WP | 171 | 185 | 0 | 97.3423 | 97.3423 | 100.6291 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WOODWARD DISTRICT EHV 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T715513WP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | EXP | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 13WP | 171 | 185 | 0 | 97.3423 | 97.3423 | 100.6291 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WOODWARD DISTRICT EHV 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T715513WP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | EXP | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 13WP | 171 | 185 | 0 | 97.3423 | 97.3423 | 100.6291 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WOODWARD DISTRICT EHV 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
GEN-2006-010 | [10 empty] | SE TEXARKANA - TURK 138KV CKT 1 | U | AEPW | AEPW | SARK | TEXARK | 0 | 507454 | HEMPSTD4 138.00 | 508078 | SETEXAR4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | AEPW | SE TEXARKANA - TURK 138KV CKT 1 | Build new Turk-SE Texarkana 138 kV line and add SE Texarkana 138 kV terminal. | [53 empty] | 2012-07-01 | 2012-07-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2085514SP | FROM->TO | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | EXP | MIDW | WERE | REG E-IL | WEST | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 17SP | 319 | 319 | 0 |  | 82.5798 | 113.926 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2085514SP | FROM->TO | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | EXP | MIDW | WERE | REG E-IL | WEST | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 17SP | 319 | 319 | 0 |  | 82.5798 | 113.926 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2085514SP | FROM->TO | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | EXP | MIDW | WERE | REG E-IL | WEST | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 17SP | 319 | 319 | 0 |  | 82.5798 | 113.926 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2085514SP | FROM->TO | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | EXP | MIDW | WERE | REG E-IL | WEST | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 17SP | 319 | 319 | 0 |  | 82.5798 | 113.926 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2085514SP | FROM->TO | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | EXP | MIDW | WERE | REG E-IL | WEST | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 17SP | 319 | 319 | 0 |  | 82.5798 | 113.926 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2085514SP | FROM->TO | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | EXP | MIDW | WERE | REG E-IL | WEST | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 17SP | 319 | 319 | 0 |  | 82.5798 | 113.926 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2085514SP | FROM->TO | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | EXP | MIDW | WERE | REG E-IL | WEST | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 17SP | 319 | 319 | 0 |  | 82.5798 | 113.926 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2085514SP | FROM->TO | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | EXP | MIDW | WERE | REG E-IL | WEST | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 17SP | 319 | 319 | 0 |  | 82.5798 | 113.926 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2085514SP | FROM->TO | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | EXP | MIDW | WERE | REG E-IL | WEST | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 17SP | 319 | 319 | 0 |  | 82.5798 | 113.926 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2085514SP | FROM->TO | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | EXP | MIDW | WERE | REG E-IL | WEST | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 17SP | 319 | 319 | 0 |  | 82.5798 | 113.926 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2085514SP | FROM->TO | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | EXP | MIDW | WERE | REG E-IL | WEST | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 17SP | 319 | 319 | 0 |  | 82.5798 | 113.926 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2635514SP | FROM->TO | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | EXP | MIDW | WERE | REG E-IL | WEST | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 17SP | 319 | 319 | 0 |  | 76.0763 | 104.1957 | [7 empty] | CATEGORYB | SINGLE | AXTELL - POST ROCK 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 640065 | AXTELL 3 345.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2635514SP | FROM->TO | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | EXP | MIDW | WERE | REG E-IL | WEST | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 17SP | 319 | 319 | 0 |  | 76.0763 | 104.1957 | [7 empty] | CATEGORYB | SINGLE | AXTELL - POST ROCK 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 640065 | AXTELL 3 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2635514SP | FROM->TO | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | EXP | MIDW | WERE | REG E-IL | WEST | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 17SP | 319 | 319 | 0 |  | 76.0763 | 104.1957 | [7 empty] | CATEGORYB | SINGLE | AXTELL - POST ROCK 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 640065 | AXTELL 3 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2635514SP | FROM->TO | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | EXP | MIDW | WERE | REG E-IL | WEST | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 17SP | 319 | 319 | 0 |  | 76.0763 | 104.1957 | [7 empty] | CATEGORYB | SINGLE | AXTELL - POST ROCK 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 640065 | AXTELL 3 345.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2635514SP | FROM->TO | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | EXP | MIDW | WERE | REG E-IL | WEST | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 17SP | 319 | 319 | 0 |  | 76.0763 | 104.1957 | [7 empty] | CATEGORYB | SINGLE | AXTELL - POST ROCK 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 640065 | AXTELL 3 345.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2635514SP | FROM->TO | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | EXP | MIDW | WERE | REG E-IL | WEST | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 17SP | 319 | 319 | 0 |  | 76.0763 | 104.1957 | [7 empty] | CATEGORYB | SINGLE | AXTELL - POST ROCK 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 640065 | AXTELL 3 345.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2635514SP | FROM->TO | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | EXP | MIDW | WERE | REG E-IL | WEST | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 17SP | 319 | 319 | 0 |  | 76.0763 | 104.1957 | [7 empty] | CATEGORYB | SINGLE | AXTELL - POST ROCK 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 640065 | AXTELL 3 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2635514SP | FROM->TO | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | EXP | MIDW | WERE | REG E-IL | WEST | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 17SP | 319 | 319 | 0 |  | 76.0763 | 104.1957 | [7 empty] | CATEGORYB | SINGLE | AXTELL - POST ROCK 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 640065 | AXTELL 3 345.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2635514SP | FROM->TO | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | EXP | MIDW | WERE | REG E-IL | WEST | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 17SP | 319 | 319 | 0 |  | 76.0763 | 104.1957 | [7 empty] | CATEGORYB | SINGLE | AXTELL - POST ROCK 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 640065 | AXTELL 3 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2635514SP | FROM->TO | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | EXP | MIDW | WERE | REG E-IL | WEST | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 17SP | 319 | 319 | 0 |  | 76.0763 | 104.1957 | [7 empty] | CATEGORYB | SINGLE | AXTELL - POST ROCK 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 640065 | AXTELL 3 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2635514SP | FROM->TO | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | EXP | MIDW | WERE | REG E-IL | WEST | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 17SP | 319 | 319 | 0 |  | 76.0763 | 104.1957 | [7 empty] | CATEGORYB | SINGLE | AXTELL - POST ROCK 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 640065 | AXTELL 3 345.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2605514SP | FROM->TO | SPEARVILLE (SPEARVL) 345/230/13.8KV TRANSFORMER CKT 1 | EXP | SUNC | SUNC | SEPC | GREAT PL | 2 | 531469 | SPERVIL7 345.00 | 539695 | SPEARVL6 230.00 | 531468 | SPERTER1 13.800 | 1 | 17SP | 336 | 336 | 336 |  | 56.862 | 101.4444 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2605514SP | FROM->TO | SPEARVILLE (SPEARVL) 345/230/13.8KV TRANSFORMER CKT 1 | EXP | SUNC | SUNC | SEPC | GREAT PL | 2 | 531469 | SPERVIL7 345.00 | 539695 | SPEARVL6 230.00 | 531468 | SPERTER1 13.800 | 1 | 17SP | 336 | 336 | 336 |  | 56.862 | 101.4444 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2605514SP | FROM->TO | SPEARVILLE (SPEARVL) 345/230/13.8KV TRANSFORMER CKT 1 | EXP | SUNC | SUNC | SEPC | GREAT PL | 2 | 531469 | SPERVIL7 345.00 | 539695 | SPEARVL6 230.00 | 531468 | SPERTER1 13.800 | 1 | 17SP | 336 | 336 | 336 |  | 56.862 | 101.4444 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2605514SP | FROM->TO | SPEARVILLE (SPEARVL) 345/230/13.8KV TRANSFORMER CKT 1 | EXP | SUNC | SUNC | SEPC | GREAT PL | 2 | 531469 | SPERVIL7 345.00 | 539695 | SPEARVL6 230.00 | 531468 | SPERTER1 13.800 | 1 | 17SP | 336 | 336 | 336 |  | 56.862 | 101.4444 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2605514SP | FROM->TO | SPEARVILLE (SPEARVL) 345/230/13.8KV TRANSFORMER CKT 1 | EXP | SUNC | SUNC | SEPC | GREAT PL | 2 | 531469 | SPERVIL7 345.00 | 539695 | SPEARVL6 230.00 | 531468 | SPERTER1 13.800 | 1 | 17SP | 336 | 336 | 336 |  | 56.862 | 101.4444 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2605514SP | FROM->TO | SPEARVILLE (SPEARVL) 345/230/13.8KV TRANSFORMER CKT 1 | EXP | SUNC | SUNC | SEPC | GREAT PL | 2 | 531469 | SPERVIL7 345.00 | 539695 | SPEARVL6 230.00 | 531468 | SPERTER1 13.800 | 1 | 17SP | 336 | 336 | 336 |  | 56.862 | 101.4444 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2605514SP | FROM->TO | SPEARVILLE (SPEARVL) 345/230/13.8KV TRANSFORMER CKT 1 | EXP | SUNC | SUNC | SEPC | GREAT PL | 2 | 531469 | SPERVIL7 345.00 | 539695 | SPEARVL6 230.00 | 531468 | SPERTER1 13.800 | 1 | 17SP | 336 | 336 | 336 |  | 56.862 | 101.4444 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2605514SP | FROM->TO | SPEARVILLE (SPEARVL) 345/230/13.8KV TRANSFORMER CKT 1 | EXP | SUNC | SUNC | SEPC | GREAT PL | 2 | 531469 | SPERVIL7 345.00 | 539695 | SPEARVL6 230.00 | 531468 | SPERTER1 13.800 | 1 | 17SP | 336 | 336 | 336 |  | 56.862 | 101.4444 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2605514SP | FROM->TO | SPEARVILLE (SPEARVL) 345/230/13.8KV TRANSFORMER CKT 1 | EXP | SUNC | SUNC | SEPC | GREAT PL | 2 | 531469 | SPERVIL7 345.00 | 539695 | SPEARVL6 230.00 | 531468 | SPERTER1 13.800 | 1 | 17SP | 336 | 336 | 336 |  | 56.862 | 101.4444 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2605514SP | FROM->TO | SPEARVILLE (SPEARVL) 345/230/13.8KV TRANSFORMER CKT 1 | EXP | SUNC | SUNC | SEPC | GREAT PL | 2 | 531469 | SPERVIL7 345.00 | 539695 | SPEARVL6 230.00 | 531468 | SPERTER1 13.800 | 1 | 17SP | 336 | 336 | 336 |  | 56.862 | 101.4444 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2605514SP | FROM->TO | SPEARVILLE (SPEARVL) 345/230/13.8KV TRANSFORMER CKT 1 | EXP | SUNC | SUNC | SEPC | GREAT PL | 2 | 531469 | SPERVIL7 345.00 | 539695 | SPEARVL6 230.00 | 531468 | SPERTER1 13.800 | 1 | 17SP | 336 | 336 | 336 |  | 56.862 | 101.4444 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T295513WP | FROM->TO | SPS North-South Stability Limit | EXP | SPS |  |  |  | SPSNORTH_STH | 0 |  | 0 |  | 0 |  |  | 13WP | 800 | 800 | 800 | 114.3919 | 114.3919 | 118.0638 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T295513WP | FROM->TO | SPS North-South Stability Limit | EXP | SPS |  |  |  | SPSNORTH_STH | 0 |  | 0 |  | 0 |  |  | 13WP | 800 | 800 | 800 | 114.3919 | 114.3919 | 118.0638 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T295513WP | FROM->TO | SPS North-South Stability Limit | EXP | SPS |  |  |  | SPSNORTH_STH | 0 |  | 0 |  | 0 |  |  | 13WP | 800 | 800 | 800 | 114.3919 | 114.3919 | 118.0638 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T295513WP | FROM->TO | SPS North-South Stability Limit | EXP | SPS |  |  |  | SPSNORTH_STH | 0 |  | 0 |  | 0 |  |  | 13WP | 800 | 800 | 800 | 114.3919 | 114.3919 | 118.0638 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP | INVALID |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3605514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 83.9219 | 109.318 | [7 empty] | CATEGORYB | SINGLE | FLATRDG3 - HARPER 138KV CKT 1 | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP | INVALID |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3605514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 83.9219 | 109.318 | [7 empty] | CATEGORYB | SINGLE | FLATRDG3 - HARPER 138KV CKT 1 | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-14SP | INVALID |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3605514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 83.9219 | 109.318 | [7 empty] | CATEGORYB | SINGLE | FLATRDG3 - HARPER 138KV CKT 1 | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-14SP | INVALID |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3605514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 83.9219 | 109.318 | [7 empty] | CATEGORYB | SINGLE | FLATRDG3 - HARPER 138KV CKT 1 | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP | INVALID |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3605514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 83.9219 | 109.318 | [7 empty] | CATEGORYB | SINGLE | FLATRDG3 - HARPER 138KV CKT 1 | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP | INVALID |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3605514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 83.9219 | 109.318 | [7 empty] | CATEGORYB | SINGLE | FLATRDG3 - HARPER 138KV CKT 1 | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP | INVALID |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3605514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 83.9219 | 109.318 | [7 empty] | CATEGORYB | SINGLE | FLATRDG3 - HARPER 138KV CKT 1 | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP | INVALID |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3605514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 83.9219 | 109.318 | [7 empty] | CATEGORYB | SINGLE | FLATRDG3 - HARPER 138KV CKT 1 | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP | INVALID |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3605514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 83.9219 | 109.318 | [7 empty] | CATEGORYB | SINGLE | FLATRDG3 - HARPER 138KV CKT 1 | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP | INVALID |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3605514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 83.9219 | 109.318 | [7 empty] | CATEGORYB | SINGLE | FLATRDG3 - HARPER 138KV CKT 1 | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP | INVALID |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3605514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 83.9219 | 109.318 | [7 empty] | CATEGORYB | SINGLE | FLATRDG3 - HARPER 138KV CKT 1 | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP | CONT-1213 - Circle - Hutchinson |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3445514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 86.659 | 102.4034 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | 0 | 533413 | CIRCLE 3 115.00 | 533419 | HEC 3 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP | CONT-1213 - Circle - Hutchinson |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3445514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 86.659 | 102.4034 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | 0 | 533413 | CIRCLE 3 115.00 | 533419 | HEC 3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-14SP | CONT-1213 - Circle - Hutchinson |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3445514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 86.659 | 102.4034 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | 0 | 533413 | CIRCLE 3 115.00 | 533419 | HEC 3 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-14SP | CONT-1213 - Circle - Hutchinson |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3445514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 86.659 | 102.4034 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | 0 | 533413 | CIRCLE 3 115.00 | 533419 | HEC 3 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP | CONT-1213 - Circle - Hutchinson |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3445514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 86.659 | 102.4034 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | 0 | 533413 | CIRCLE 3 115.00 | 533419 | HEC 3 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP | CONT-1213 - Circle - Hutchinson |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3445514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 86.659 | 102.4034 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | 0 | 533413 | CIRCLE 3 115.00 | 533419 | HEC 3 115.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP | CONT-1213 - Circle - Hutchinson |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3445514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 86.659 | 102.4034 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | 0 | 533413 | CIRCLE 3 115.00 | 533419 | HEC 3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP | CONT-1213 - Circle - Hutchinson |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3445514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 86.659 | 102.4034 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | 0 | 533413 | CIRCLE 3 115.00 | 533419 | HEC 3 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP | CONT-1213 - Circle - Hutchinson |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3445514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 86.659 | 102.4034 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | 0 | 533413 | CIRCLE 3 115.00 | 533419 | HEC 3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP | CONT-1213 - Circle - Hutchinson |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3445514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 86.659 | 102.4034 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | 0 | 533413 | CIRCLE 3 115.00 | 533419 | HEC 3 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP | CONT-1213 - Circle - Hutchinson |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3445514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 86.659 | 102.4034 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | 0 | 533413 | CIRCLE 3 115.00 | 533419 | HEC 3 115.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19645514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 75.9711 | 101.0185 | [7 empty] | CATEGORYB | NONSINGLE | SPP-MKEC-05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19645514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 75.9711 | 101.0185 | [7 empty] | CATEGORYB | NONSINGLE | SPP-MKEC-05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19645514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 75.9711 | 101.0185 | [7 empty] | CATEGORYB | NONSINGLE | SPP-MKEC-05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19645514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 75.9711 | 101.0185 | [7 empty] | CATEGORYB | NONSINGLE | SPP-MKEC-05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19645514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 75.9711 | 101.0185 | [7 empty] | CATEGORYB | NONSINGLE | SPP-MKEC-05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19645514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 75.9711 | 101.0185 | [7 empty] | CATEGORYB | NONSINGLE | SPP-MKEC-05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19645514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 75.9711 | 101.0185 | [7 empty] | CATEGORYB | NONSINGLE | SPP-MKEC-05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19645514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 75.9711 | 101.0185 | [7 empty] | CATEGORYB | NONSINGLE | SPP-MKEC-05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19645514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 75.9711 | 101.0185 | [7 empty] | CATEGORYB | NONSINGLE | SPP-MKEC-05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19645514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 75.9711 | 101.0185 | [7 empty] | CATEGORYB | NONSINGLE | SPP-MKEC-05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19645514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 75.9711 | 101.0185 | [7 empty] | CATEGORYB | NONSINGLE | SPP-MKEC-05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19725514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 75.9291 | 100.9606 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-34 | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19725514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 75.9291 | 100.9606 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-34 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19725514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 75.9291 | 100.9606 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-34 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2014-07-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19725514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 75.9291 | 100.9606 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-34 | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19725514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 75.9291 | 100.9606 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-34 | 0 | 0 |  | 0 |  | 0 | [5 empty] | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19725514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 75.9291 | 100.9606 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-34 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19725514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 75.9291 | 100.9606 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-34 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19725514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 75.9291 | 100.9606 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-34 | 0 | 0 |  | 0 |  | 0 | [5 empty] | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2013-06-01 | 2015-01-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19725514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 75.9291 | 100.9606 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-34 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19725514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 75.9291 | 100.9606 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-34 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGEs Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2013-06-01 | 2014-06-01
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19725514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | EXP | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 75.9291 | 100.9606 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-34 | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2013-06-01 | 2015-01-01
2005-AG2 | [10 empty] | SUB 110 - ORONOGO JCT. - SUB 167 - RIVERTON 161KV CKT 1 | U | EMDE | EMDE |  |  | 0 | 547469 | RIV167 5 161 | 547467 | ORO110 5 161 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | EMDE | SUB 110 - ORONOGO JCT. - SUB 167 - RIVERTON 161KV CKT 1 | Reconductor Oronogo 59467 to Riverton 59469 with Bundled 556 ACSR | [53 empty] | 2011-06-01 | 2011-06-01
GEN-2006-010 | [10 empty] | SUGAR HILL - TURK 138KV CKT 1 | U | AEPW | AEPW | SARK | TEXARK | 0 | 507454 | HEMPSTD4 138.00 | 508080 | SUGARHL4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | AEPW | SUGAR HILL - TURK 138KV CKT 1 | Build new Turk-Sugar Hill 138 kV line and add Sugar Hill 138 kV terminal. | [53 empty] | 2012-07-01 | 2012-07-01
2009-AGP2 | [10 empty] | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | U | WFEC | WFEC | AEP-OP | AEP-OP | 2 | 521065 | TALOGA 4 138.00 | 521064 | TALOGA 2 69.000 | 521178 | TLGTERT 13.800 | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | WFEC | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | Auto XFMR 56 to 112MVA | 112 | 112 | 112 | 112 |  | 24 | 24 | [46 empty] | 2010-10-01 | 2013-06-01
NA | [10 empty] | TATONGA - WOODWARD 345KV CKT 1 | U | OKGE | OKGE | ENID | ENID | 0 | 515407 |  | 515375 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | OKGE | TATONGA - WOODWARD 345KV CKT 1 | Build 345 kV line | [53 empty] | 2010-01-01 | 2010-01-01
GEN-2006-010 | [10 empty] | TURK (HEMP 1) 138/115/13.8KV TRANSFORMER CKT 1 | U | AEPW |  | SARK |  | 1 | 507454 | HEMPSTD4 138.00 | 507456 | HEMPSTD3 115.00 | 507458 | HEMP1 1 13.800 | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | AEPW | TURK (HEMP 1) 138/115/13.8KV TRANSFORMER CKT 1 | Build Turk 138-115 kV station and relocate autotransformer (and spare) from Patterson to this new Turk station | [53 empty] | 2012-07-01 | 2012-07-01
NA | [10 empty] | WOODWARD - IODINE 138KV CKT 1 | U | OKGE | OKGE | ENID | ENID | 0 | 515376 |  | 514796 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | OKGE | WOODWARD - IODINE 138KV CKT 1 | Tap Iodine to Woodward 138 kV line | [53 empty] | 2010-01-01 | 2010-01-01
NA | [10 empty] | WOODWARD - WOODWARD EHV 138KV CKT 1 | U | OKGE | OKGE | ENID | ENID | 0 | 515376 |  | 514785 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | OKGE | WOODWARD - WOODWARD EHV 138KV CKT 1 | Build .5 miles of 138 kV and install terminal equipment | [53 empty] | 2010-01-01 | 2010-01-01
NA | [10 empty] | WOODWARD - WOODWARD EHV 138KV CKT 2 | U | OKGE | OKGE | ENID | ENID | 0 | 515376 |  | 514785 |  |  |  | 2 | [15 empty] | BASECASE | BASE CASE | [11 empty] | OKGE | WOODWARD - WOODWARD EHV 138KV CKT 2 | Build .5 miles of 138 kV and install terminal equipment | [53 empty] | 2010-01-01 | 2010-01-01
NA | [10 empty] | WOODWARD 345/138KV TRANSFORMER CKT 1 | U | OKGE | OKGE | ENID | ENID | 1 | 515375 |  | 515376 |  | 515795 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | OKGE | WOODWARD 345/138KV TRANSFORMER CKT 1 | Install 345/138 kV XF | [53 empty] | 2010-01-01 | 2010-01-01

## tblAllFacilityLog < 100%
STUDYDES | STUDYDES2 | EVENTTYPE | AssessmentSOLUTIONTYPE | AssessmenFDNS-TERMINATION | SOLUTIONTYPE | FDNS-TERMINATION | GROUP | SCENARIO | FGName | DIRECTION | FacilityName | FacilityUpgradeCode | ModelArea1 | ModelArea2 | FZONENAME | TZONENAME | MONTFLAG | MONTFB | MONTFNAME | MONTTB1 | MONTTNAME1 | MONTTB2 | MONTTNAME2 | MONTCKT | Case | RATEA | RATEB | RATEC | Assessment Loading | BaseCaseLoading | TransferCaseLoading | NameOfBusWithMonitoredVoltage | Assessment Voltage | BaseCaseVoltage | TransferCaseVoltage | VINIT | VMIN | VMAX | CATEGORY | CONTTYPE | CONTNAME | CONTXFMRFLAG | CONTFB | CONTFNAME | CONTTB1 | CONTTNAME1 | CONTTB2 | CONTTNAME2 | CONTCKT | TransmissionProviderCommentsNotes | RequiredRateB | TransmissionOwnerComments | OwnerDesignation | UpgradeName | UpgradeComponentWithinFacility | NewSummerA | NewSummerB | NewOtherA | NewOtherB | DistToConstruct | TotalLead | ConstructionLeadOnly | NewOrConstructWhileEnergized | NewR | NewX | NewB | CommentsRegardingUpgradeRequirements | NewCost | EffDate | NetPlantDate | ReusableEx_GrossValue | ReusableEx_NetValue | Reusable_EndofDepr | SalvageValue | NewCostWhileExpediting | EffDateExpedited | StartDeprExpedited | EndDeprExpedited | NetPlantDateExpedited | ReusableEx_GrossExpedited | ReusableEx_NetExpedited | Reusable_EndofDeprExpedited | SalvageValueExpedited | Generation 1 Owner & Unit (Name) | Generation 1 Redispatch Cost ($) | Generation 1 Redispatch Date (M/D/Y) | Generation 2 Owner & Unit (Name) | Generation 2 Redispatch Cost ($) | Generation 2 Redispatch Date (M/D/Y) | Generation 3 Owner & Unit (Name) | Generation 3 Redispatch Cost ($) | Generation 3 Redispatch Date (M/D/Y) | ActualCompletion | ActualNewCost | ActualNetPlantDate | ActualReusableEx_GrossValue | ActualReusableEx_NetValue | ActualReusable_EndofDepr | ActualSalvageValue | Actual_NewCostWhileExpediting | Actual_StartDeprExp | Actual_EndDeprExp | Actual_NetPlantDateExpedited | ActualReusableEx_GrossExpedited | ActualReusableEx_NetExpedited | ActualReusable_EndofDeprExpedited | Actual_SalvageValueExpedited | SPPReliabilityDate | DUN | EOC | EarliestDate
2011-AG2 | AFS9 | INVALID | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T1005017WP | FROM->TO | 59TH ST - GILL ENERGY CENTER SOUTH 138KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533029 | 59TH ST4 138.00 | 533046 | GILL S 4 138.00 | 0 |  | 1 | 17WP | 191 | 210 | 0 | 103.0321 | 103.0321 | 98.5924 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER NORTH - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533040 | EVANS N4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T16105512SP | FROM->TO | 5OVERTON 161.00 - HUNTSDALE 161KV CKT 1 | E | AMMO | AECI | AMRNMO | CENTRAL | 0 | 345409 | 5OVERTON 161.00 | 300500 | 5HUNTSDL 161.00 | 0 |  | 1 | 12SP | 223 | 223 | 203 | 95.3 | 95.2788 | 95.3 | [7 empty] | CATEGORYB | NONSINGLE | AM1_A_OG | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T16105512SP | FROM->TO | 5OVERTON 161.00 - HUNTSDALE 161KV CKT 1 | E | AMMO | AECI | AMRNMO | CENTRAL | 0 | 345409 | 5OVERTON 161.00 | 300500 | 5HUNTSDL 161.00 | 0 |  | 1 | 12SP | 223 | 223 | 203 | 95.2788 | 95.2788 | 95.3 | [7 empty] | CATEGORYB | NONSINGLE | AM1_A_OG | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-14WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T12605514WP | FROM->TO | 5OVERTON 161.00 - HUNTSDALE 161KV CKT 1 | E | AMMO | AECI | AMRNMO | CENTRAL | 0 | 345409 | 5OVERTON 161.00 | 300500 | 5HUNTSDL 161.00 | 0 |  | 1 | 17WP | 223 | 223 | 203 |  | 91.9184 | 97.9 | [7 empty] | CATEGORYB | NONSINGLE | AM1_A_OG | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T29645522SP | FROM->TO | 5OVERTON 161.00 - HUNTSDALE 161KV CKT 1 | E | AMMO | AECI | AMRNMO | CENTRAL | 0 | 345409 | 5OVERTON 161.00 | 300500 | 5HUNTSDL 161.00 | 0 |  | 1 | 22SP | 223 | 223 | 203 | 86.7856 | 86.7856 | 95.6 | [7 empty] | CATEGORYB | NONSINGLE | AM1_A_OG | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T20065514SP | TO->FROM | 5PERCHE 161.00 - HUNTSDALE 161KV CKT 1 | E | AECI | CWLD | CENTRAL | CMWL | 0 | 300500 | 5HUNTSDL 161.00 | 343004 | 5PERCHE 161.00 | 0 |  | 1 | 17SP | 223 | 223 | 223 |  | 90.8003 | 97.5 | [7 empty] | CATEGORYB | NONSINGLE | AM1_A_OG | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-16WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10435516WP | TO->FROM | 5PERCHE 161.00 - HUNTSDALE 161KV CKT 1 | E | AECI | CWLD | CENTRAL | CMWL | 0 | 300500 | 5HUNTSDL 161.00 | 343004 | 5PERCHE 161.00 | 0 |  | 1 | 17WP | 223 | 223 | 223 |  | 90.7341 | 97 | [7 empty] | CATEGORYB | NONSINGLE | AM1_A_OG | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T28655522SP | TO->FROM | 7JASPER 345.00 - BLACKBERRY 345KV CKT 1 | E | AECI | AECI | KAMO | KAMO | 0 | 300739 | 7BLACKBERRY 345.00 | 300949 | 7JASPER 345.00 | 0 |  | 1 | 22SP | 870 | 870 | 0 | 87.6303 | 87.6303 | 97.7 | [7 empty] | CATEGORYB | NONSINGLE | GRDA-OPGD-05 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 | INVALID | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2335522SP | TO->FROM | 7JASPER 345.00 - BLACKBERRY 345KV CKT 1 | E | AECI | AECI | KAMO | KAMO | 0 | 300739 | 7BLACKBERRY 345.00 | 300949 | 7JASPER 345.00 | 0 |  | 1 | 22SP | 870 | 870 | 0 | 87.4071 | 87.4071 | 97.4161 | [7 empty] | CATEGORYB | SINGLE | GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 | 0 | 512650 | GRDA1 7 345.00 | 512750 | TONECE7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3945512WP | FROM->TO | 7OVERTON 345.00 () 345/161/13.8KV TRANSFORMER CKT 1 | E | AMMO | AMMO | AMRNMO | AMRNMO | 1 | 345408 | 7OVERTON 345.00 | 345409 | 5OVERTON 161.00 | 345410 | 1OVERTERT 13.800 | 1 | 12WP | 300 | 300 | 0 | 95.1914 | 95.1914 | 98.9 | [7 empty] | CATEGORYB | SINGLE | THOMAS HILL 345/161KV TRANSFORMER CKT 1 | 0 | 300049 | 7THOMHL 345.00 | 300120 | 5THMHIL 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3945512WP | FROM->TO | 7OVERTON 345.00 () 345/161/13.8KV TRANSFORMER CKT 1 | E | AMMO | AMMO | AMRNMO | AMRNMO | 1 | 345408 | 7OVERTON 345.00 | 345409 | 5OVERTON 161.00 | 345410 | 1OVERTERT 13.800 | 1 | 12WP | 300 | 300 | 0 | 95.2 | 95.1914 | 98.9 | [7 empty] | CATEGORYB | SINGLE | THOMAS HILL 345/161KV TRANSFORMER CKT 1 | 0 | 300049 | 7THOMHL 345.00 | 300120 | 5THMHIL 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T7425512WP | FROM->TO | 7OVERTON 345.00 () 345/161/13.8KV TRANSFORMER CKT 1 | E | AMMO | AMMO | AMRNMO | AMRNMO | 1 | 345408 | 7OVERTON 345.00 | 345409 | 5OVERTON 161.00 | 345410 | 1OVERTERT 13.800 | 1 | 12WP | 300 | 300 | 0 | 92.0972 | 92.0972 | 95.8 | [7 empty] | CATEGORYB | NONSINGLE | KCPL-MSL#02 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-16SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T9235516SP | FROM->TO | 7OVERTON 345.00 () 345/161/13.8KV TRANSFORMER CKT 1 | E | AMMO | AMMO | AMRNMO | AMRNMO | 1 | 345408 | 7OVERTON 345.00 | 345409 | 5OVERTON 161.00 | 345410 | 1OVERTERT 13.800 | 1 | 17SP | 300 | 300 | 0 |  | 88.5791 | 96.6 | [7 empty] | CATEGORYB | SINGLE | 7MCCREDIE 345.00 - 7MONTGMRY 345.00 345KV CKT 1 | 0 | 345088 | 7MCCREDIE 345.00 | 345230 | 7MONTGMRY 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T5545517WP | FROM->TO | 7OVERTON 345.00 () 345/161/13.8KV TRANSFORMER CKT 1 | E | AMMO | AMMO | AMRNMO | AMRNMO | 1 | 345408 | 7OVERTON 345.00 | 345409 | 5OVERTON 161.00 | 345410 | 1OVERTERT 13.800 | 1 | 17WP | 300 | 300 | 0 | 89.9245 | 89.9245 | 99.7 | [7 empty] | CATEGORYB | SINGLE | 7MCCREDIE 345.00 - 7MONTGMRY 345.00 345KV CKT 1 | 0 | 345088 | 7MCCREDIE 345.00 | 345230 | 7MONTGMRY 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T7955512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 98.9011 | 98.9011 | 99 | [7 empty] | CATEGORYB | GENOUT | GEN336153 1-WATERFORD UNIT#3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3085512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 97.186 | 97.186 | 97.1 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2805512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 96.7635 | 96.7635 | 96.8 | [7 empty] | CATEGORYB | SINGLE | WATERFORD - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WGLEN 500.00 | 336150 | 8WATERFO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8025512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 96.5 | 96.4971 | 96.6 | [7 empty] | CATEGORYB | GENOUT | GEN336251 1-NINEMILE POINT UNIT#4 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3425512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 96.3743 | 96.3743 | 96.4 | [7 empty] | CATEGORYB | SINGLE | BOGALUSA - FRANKLIN 500KV CKT 1 | 0 | 336130 | 8BOGALUS 500.00 | 336562 | 8FRKLIN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3485512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 96.2661 | 96.2661 | 96.3 | [7 empty] | CATEGORYB | SINGLE | WATERFORD 500/230KV TRANSFORMER CKT 1 | 0 | 336150 | 8WATERFO 500.00 | 336154 | 6WATFRD 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2755512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 96.2 | 96.2125 | 96.2 | [7 empty] | CATEGORYB | SINGLE | COLY - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WGLEN 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2875512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 96.2248 | 96.2248 | 96.2 | [7 empty] | CATEGORYB | SINGLE | JAGUAR - POINT ESSO TAP 230KV CKT 1 | 0 | 335641 | 6TP.ESSO 230.00 | 335770 | 6JAGUAR 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3305512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 96.1559 | 96.1559 | 96.2 | [7 empty] | CATEGORYB | SINGLE | BOGALUSA 500/230KV TRANSFORMER CKT 1 | 0 | 336130 | 8BOGALUS 500.00 | 336131 | 6ADMSCRK 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2955512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 96 | 95.9663 | 96 | [7 empty] | CATEGORYB | SINGLE | ENJAY - FANCY POINT 230KV CKT 1 | 0 | 335772 | 6ENJAY 230.00 | 335825 | 6FANCY 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T7845512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 95.9357 | 95.9357 | 96 | [7 empty] | CATEGORYB | GENOUT | GEN335831 1-RIVERBEND UNIT#1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2365512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 95.8 | 95.8439 | 95.8 | [7 empty] | CATEGORYB | SINGLE | 8CAJUN2 - WEBRE 500KV CKT 1 | 0 | 303005 | 8CAJUN2 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2915512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 95.8 | 95.8299 | 95.8 | [7 empty] | CATEGORYB | SINGLE | ENJAY - JAGUAR 230KV CKT 1 | 0 | 335770 | 6JAGUAR 230.00 | 335772 | 6ENJAY 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4145512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 95.6865 | 95.6865 | 95.7 | [7 empty] | CATEGORYB | SINGLE | BARKERS 6 230.00 - BOGALUSA 230KV CKT 1 | 0 | 500025 | BARKERS 6 230.00 | 336136 | 6BOGALUS 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T305512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 95.5681 | 95.5681 | 95.6 | [7 empty] | CATEGORYB | SINGLE | BAYOU SALE - TECHE 138KV CKT 1 | 0 | 500050 | BSALES 4 138.00 | 500820 | TECHE 4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T325512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 95.5555 | 95.5555 | 95.6 | [7 empty] | CATEGORYB | SINGLE | BAYOU SALE - WAXLAKE 138KV CKT 1 | 0 | 500050 | BSALES 4 138.00 | 500890 | WAXLAKE4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2595512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 95.5 | 95.4566 | 95.5 | [7 empty] | CATEGORYB | SINGLE | NELSON - RICHARD 500KV CKT 1 | 0 | 335192 | 8NELSON 500.00 | 335367 | 8RICHARD 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2615512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 95.5 | 95.5431 | 95.5 | [7 empty] | CATEGORYB | SINGLE | WEBRE - WELLS 500KV CKT 1 | 0 | 335368 | 8WELLS 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T285512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 95.516 | 95.516 | 95.5 | [7 empty] | CATEGORYB | SINGLE | BARKERS 6 230.00 - RAMSAY 230KV CKT 1 | 0 | 500025 | BARKERS 6 230.00 | 500750 | RAMSAY 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T7395512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 95.5 | 95.4756 | 95.5 | [7 empty] | CATEGORYB | NONSINGLE | CELE-WELLOP2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T7695512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 95.5 | 95.4505 | 95.5 | [7 empty] | CATEGORYB | NONSINGLE | SERCW-21 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T7785512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 95.5 | 95.4963 | 95.5 | [7 empty] | CATEGORYB | GENOUT | GEN303008 1-1BC2 U3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T345512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 95.3516 | 95.3516 | 95.4 | [7 empty] | CATEGORYB | SINGLE | EL PASO TAP - WAXLAKE 138KV CKT 1 | 0 | 500290 | ELPTAP 4 138.00 | 500890 | WAXLAKE4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T7735512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 95.4 | 95.4034 | 95.4 | [7 empty] | CATEGORYB | GENOUT | GEN303006 1-1BC2 U1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T1065012WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 95.3 | 95.3243 | 95.3 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T5205012WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 95.3 | 95.2696 | 95.3 | [7 empty] | CATEGORYB | GENOUT | GEN336153 1-WATERFORD UNIT#3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T4255013SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13SP | 615 | 615 | 0 | 95.2515 | 95.2515 | 95 | [7 empty] | CATEGORYB | SINGLE | ELDORADO EHV - STERLINGTON 500KV CKT 1 | 0 | 337420 | 8STERL 500.00 | 337561 | 8ELDEHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4725513SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13SP | 615 | 615 | 0 | 95.0777 | 95.0777 | 95 | [7 empty] | CATEGORYB | SINGLE | 8CAJUN2 - WEBRE 500KV CKT 1 | 0 | 303005 | 8CAJUN2 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T5185513SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13SP | 615 | 615 | 0 | 95.0614 | 95.0614 | 95 | [7 empty] | CATEGORYB | SINGLE | DYNEGY - PECAN GROVE 230KV CKT 1 | 0 | 335074 | 6DYNEGY 230.00 | 335077 | 6PGROVE 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T5315513SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13SP | 615 | 615 | 0 | 95.2 | 95.15 | 95 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T6705013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 99.3875 | 99.3875 | 99.5 | [7 empty] | CATEGORYB | GENOUT | GEN336153 1-WATERFORD UNIT#3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3315513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 97.343 | 97.343 | 97.2 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T9145513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 96.8 | 96.7986 | 96.9 | [7 empty] | CATEGORYB | GENOUT | GEN336251 1-NINEMILE POINT UNIT#4 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2915513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 96.3 | 96.3493 | 96.4 | [7 empty] | CATEGORYB | SINGLE | WATERFORD - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WGLEN 500.00 | 336150 | 8WATERFO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T1665013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 96.2583 | 96.2583 | 96.2 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T6805013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 95.9 | 95.9523 | 96.1 | [7 empty] | CATEGORYB | GENOUT | GEN336251 1-NINEMILE POINT UNIT#4 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T1265013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 95.9 | 95.9208 | 96 | [7 empty] | CATEGORYB | SINGLE | WATERFORD - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WGLEN 500.00 | 336150 | 8WATERFO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8925513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 95.9 | 95.8744 | 95.9 | [7 empty] | CATEGORYB | GENOUT | GEN335831 1-RIVERBEND UNIT#1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2855513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 95.8191 | 95.8191 | 95.7 | [7 empty] | CATEGORYB | SINGLE | COLY - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WGLEN 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3635513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 95.649 | 95.649 | 95.7 | [7 empty] | CATEGORYB | SINGLE | BOGALUSA - FRANKLIN 500KV CKT 1 | 0 | 336130 | 8BOGALUS 500.00 | 336562 | 8FRKLIN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3715513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 95.7 | 95.7383 | 95.6 | [7 empty] | CATEGORYB | SINGLE | WATERFORD 500/230KV TRANSFORMER CKT 1 | 0 | 336150 | 8WATERFO 500.00 | 336154 | 6WATFRD 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8825513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 95.6 | 95.6392 | 95.5 | [7 empty] | CATEGORYB | GENOUT | GEN303008 1-1BC2 U3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3005513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 95.4 | 95.4059 | 95.4 | [7 empty] | CATEGORYB | SINGLE | JAGUAR - POINT ESSO TAP 230KV CKT 1 | 0 | 335641 | 6TP.ESSO 230.00 | 335770 | 6JAGUAR 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8815513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 95.5347 | 95.5347 | 95.4 | [7 empty] | CATEGORYB | GENOUT | GEN303006 1-1BC2 U1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T2015013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 95.2 | 95.2132 | 95.3 | [7 empty] | CATEGORYB | SINGLE | BOGALUSA - FRANKLIN 500KV CKT 1 | 0 | 336130 | 8BOGALUS 500.00 | 336562 | 8FRKLIN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T2085013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 95.3 | 95.3097 | 95.3 | [7 empty] | CATEGORYB | SINGLE | WATERFORD 500/230KV TRANSFORMER CKT 1 | 0 | 336150 | 8WATERFO 500.00 | 336154 | 6WATFRD 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3525513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 95.3764 | 95.3764 | 95.3 | [7 empty] | CATEGORYB | SINGLE | BOGALUSA 500/230KV TRANSFORMER CKT 1 | 0 | 336130 | 8BOGALUS 500.00 | 336131 | 6ADMSCRK 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3155513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 95.1939 | 95.1939 | 95.2 | [7 empty] | CATEGORYB | SINGLE | ENJAY - FANCY POINT 230KV CKT 1 | 0 | 335772 | 6ENJAY 230.00 | 335825 | 6FANCY 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T6615013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 95.2124 | 95.2124 | 95.2 | [7 empty] | CATEGORYB | GENOUT | GEN335831 1-RIVERBEND UNIT#1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T1895013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 94.9824 | 94.9824 | 95 | [7 empty] | CATEGORYB | SINGLE | BOGALUSA 500/230KV TRANSFORMER CKT 1 | 0 | 336130 | 8BOGALUS 500.00 | 336131 | 6ADMSCRK 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2325513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 95.0819 | 95.0819 | 95 | [7 empty] | CATEGORYB | SINGLE | 8CAJUN2 - WEBRE 500KV CKT 1 | 0 | 303005 | 8CAJUN2 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3095513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 95 | 95.033 | 95 | [7 empty] | CATEGORYB | SINGLE | ENJAY - JAGUAR 230KV CKT 1 | 0 | 335770 | 6JAGUAR 230.00 | 335772 | 6ENJAY 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T13355514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 98.9584 | 99.1 | [7 empty] | CATEGORYB | GENOUT | GEN336153 1-WATERFORD UNIT#3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-16WP | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T11145516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 98.9594 | 99.1 | [7 empty] | CATEGORYB | GENOUT | GEN336153 1-WATERFORD UNIT#3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T11965517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 98.8988 | 98.8988 | 99 | [7 empty] | CATEGORYB | GENOUT | GEN336153 1-WATERFORD UNIT#3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-14WP | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T5725514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 97.3703 | 97.2 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16WP | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4075516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 97.3714 | 97.2 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2011AG2AFS91T8485014WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 97.1599 | 97.1 | [7 empty] | CATEGORYB | GENOUT | GEN336153 1-WATERFORD UNIT#3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-16WP | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2011AG2AFS91T8455016WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 97.1662 | 97.1 | [7 empty] | CATEGORYB | GENOUT | GEN336153 1-WATERFORD UNIT#3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4415517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 97.2757 | 97.2757 | 97.1 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T8645017WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 97.1645 | 97.1645 | 97.1 | [7 empty] | CATEGORYB | GENOUT | GEN336153 1-WATERFORD UNIT#3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-14WP | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T5095514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 96.3953 | 96.4 | [7 empty] | CATEGORYB | SINGLE | WATERFORD - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WGLEN 500.00 | 336150 | 8WATERFO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16WP | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3445516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 96.4083 | 96.4 | [7 empty] | CATEGORYB | SINGLE | WATERFORD - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WGLEN 500.00 | 336150 | 8WATERFO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3765517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.138 | 96.138 | 96.4 | [7 empty] | CATEGORYB | SINGLE | WATERFORD - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WGLEN 500.00 | 336150 | 8WATERFO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2011AG2AFS91T2515014WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 96.195 | 96 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16WP | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2011AG2AFS91T2485016WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 96.1929 | 96 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T6195514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 95.9713 | 95.9 | [7 empty] | CATEGORYB | SINGLE | BOGALUSA - FRANKLIN 500KV CKT 1 | 0 | 336130 | 8BOGALUS 500.00 | 336562 | 8FRKLIN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16WP | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4545516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 95.9731 | 95.9 | [7 empty] | CATEGORYB | SINGLE | BOGALUSA - FRANKLIN 500KV CKT 1 | 0 | 336130 | 8BOGALUS 500.00 | 336562 | 8FRKLIN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T2785017WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.1911 | 96.1911 | 95.9 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4885517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95.9171 | 95.9171 | 95.9 | [7 empty] | CATEGORYB | SINGLE | BOGALUSA - FRANKLIN 500KV CKT 1 | 0 | 336130 | 8BOGALUS 500.00 | 336562 | 8FRKLIN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP | SWINGBUS |  |  | FNSL | FDNS-Blown up | 5 | 5 | 2011AG2AFS92T155514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 95.8899 | 95.8 | [7 empty] | CATEGORYB | GENOUT | GEN335831 1-RIVERBEND UNIT#1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-16WP | SWINGBUS |  |  | FNSL | FDNS-Blown up | 5 | 5 | 2011AG2AFS92T85516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 95.8872 | 95.8 | [7 empty] | CATEGORYB | GENOUT | GEN335831 1-RIVERBEND UNIT#1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FNSL | FDNS-Blown up | FNSL | FDNS-Blown up | 5 | 5 | 2011AG2AFS92T115517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95.9 | 95.8693 | 95.8 | [7 empty] | CATEGORYB | GENOUT | GEN335831 1-RIVERBEND UNIT#1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-14WP | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T5055514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 95.853 | 95.7 | [7 empty] | CATEGORYB | SINGLE | COLY - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WGLEN 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T6265514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 95.5636 | 95.7 | [7 empty] | CATEGORYB | SINGLE | WATERFORD 500/230KV TRANSFORMER CKT 1 | 0 | 336150 | 8WATERFO 500.00 | 336154 | 6WATFRD 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16WP | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3405516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 95.8546 | 95.7 | [7 empty] | CATEGORYB | SINGLE | COLY - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WGLEN 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16WP | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4615516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 95.5657 | 95.7 | [7 empty] | CATEGORYB | SINGLE | WATERFORD 500/230KV TRANSFORMER CKT 1 | 0 | 336150 | 8WATERFO 500.00 | 336154 | 6WATFRD 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3725517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95.7859 | 95.7859 | 95.7 | [7 empty] | CATEGORYB | SINGLE | COLY - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WGLEN 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4955517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95.5 | 95.488 | 95.7 | [7 empty] | CATEGORYB | SINGLE | WATERFORD 500/230KV TRANSFORMER CKT 1 | 0 | 336150 | 8WATERFO 500.00 | 336154 | 6WATFRD 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T12835514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 95.674 | 95.6 | [7 empty] | CATEGORYB | GENOUT | GEN303008 1-1BC2 U3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-14WP | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T5205514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 95.6807 | 95.6 | [7 empty] | CATEGORYB | SINGLE | JAGUAR - POINT ESSO TAP 230KV CKT 1 | 0 | 335641 | 6TP.ESSO 230.00 | 335770 | 6JAGUAR 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T6065514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 95.6799 | 95.6 | [7 empty] | CATEGORYB | SINGLE | BOGALUSA 500/230KV TRANSFORMER CKT 1 | 0 | 336130 | 8BOGALUS 500.00 | 336131 | 6ADMSCRK 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16WP | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10665516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 95.6687 | 95.6 | [7 empty] | CATEGORYB | GENOUT | GEN303008 1-1BC2 U3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-16WP | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3555516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 95.6823 | 95.6 | [7 empty] | CATEGORYB | SINGLE | JAGUAR - POINT ESSO TAP 230KV CKT 1 | 0 | 335641 | 6TP.ESSO 230.00 | 335770 | 6JAGUAR 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16WP | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4415516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 95.6816 | 95.6 | [7 empty] | CATEGORYB | SINGLE | BOGALUSA 500/230KV TRANSFORMER CKT 1 | 0 | 336130 | 8BOGALUS 500.00 | 336131 | 6ADMSCRK 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3875517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95.6 | 95.6249 | 95.6 | [7 empty] | CATEGORYB | SINGLE | JAGUAR - POINT ESSO TAP 230KV CKT 1 | 0 | 335641 | 6TP.ESSO 230.00 | 335770 | 6JAGUAR 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4755517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95.621 | 95.621 | 95.6 | [7 empty] | CATEGORYB | SINGLE | BOGALUSA 500/230KV TRANSFORMER CKT 1 | 0 | 336130 | 8BOGALUS 500.00 | 336131 | 6ADMSCRK 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T12725514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 95.5856 | 95.5 | [7 empty] | CATEGORYB | GENOUT | GEN303006 1-1BC2 U1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-14WP | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T5495514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 95.5816 | 95.5 | [7 empty] | CATEGORYB | SINGLE | ENJAY - FANCY POINT 230KV CKT 1 | 0 | 335772 | 6ENJAY 230.00 | 335825 | 6FANCY 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16WP | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10555516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 95.5801 | 95.5 | [7 empty] | CATEGORYB | GENOUT | GEN303006 1-1BC2 U1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-16WP | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3845516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 95.5831 | 95.5 | [7 empty] | CATEGORYB | SINGLE | ENJAY - FANCY POINT 230KV CKT 1 | 0 | 335772 | 6ENJAY 230.00 | 335825 | 6FANCY 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T11435517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95.6 | 95.6438 | 95.5 | [7 empty] | CATEGORYB | GENOUT | GEN303008 1-1BC2 U3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4185517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95.5 | 95.4743 | 95.5 | [7 empty] | CATEGORYB | SINGLE | ENJAY - FANCY POINT 230KV CKT 1 | 0 | 335772 | 6ENJAY 230.00 | 335825 | 6FANCY 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T11305517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95.6 | 95.5578 | 95.4 | [7 empty] | CATEGORYB | GENOUT | GEN303006 1-1BC2 U1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-14WP | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T13505514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 95.3716 | 95.3 | [7 empty] | CATEGORYB | GENOUT | GEN336251 1-NINEMILE POINT UNIT#4 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-14WP | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T13605514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 95.387 | 95.3 | [7 empty] | CATEGORYB | GENOUT | GEN336252 1-NINEMILE POINT UNIT#5 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-14WP | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3385514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 95.37 | 95.3 | [7 empty] | CATEGORYB | SINGLE | 8CAJUN2 - WEBRE 500KV CKT 1 | 0 | 303005 | 8CAJUN2 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T5415514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 95.382 | 95.3 | [7 empty] | CATEGORYB | SINGLE | ENJAY - JAGUAR 230KV CKT 1 | 0 | 335770 | 6JAGUAR 230.00 | 335772 | 6ENJAY 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16WP | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T11285516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 95.3637 | 95.3 | [7 empty] | CATEGORYB | GENOUT | GEN336251 1-NINEMILE POINT UNIT#4 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-16WP | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T11375516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 95.3792 | 95.3 | [7 empty] | CATEGORYB | GENOUT | GEN336252 1-NINEMILE POINT UNIT#5 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-16WP | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1735516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 95.3713 | 95.3 | [7 empty] | CATEGORYB | SINGLE | 8CAJUN2 - WEBRE 500KV CKT 1 | 0 | 303005 | 8CAJUN2 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16WP | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3765516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 95.3837 | 95.3 | [7 empty] | CATEGORYB | SINGLE | ENJAY - JAGUAR 230KV CKT 1 | 0 | 335770 | 6JAGUAR 230.00 | 335772 | 6ENJAY 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T12115517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95.4 | 95.3798 | 95.3 | [7 empty] | CATEGORYB | GENOUT | GEN336251 1-NINEMILE POINT UNIT#4 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T12215517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95.4 | 95.3951 | 95.3 | [7 empty] | CATEGORYB | GENOUT | GEN336252 1-NINEMILE POINT UNIT#5 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4105517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95.3 | 95.3201 | 95.3 | [7 empty] | CATEGORYB | SINGLE | ENJAY - JAGUAR 230KV CKT 1 | 0 | 335770 | 6JAGUAR 230.00 | 335772 | 6ENJAY 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1885517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95.3 | 95.3253 | 95.2 | [7 empty] | CATEGORYB | SINGLE | 8CAJUN2 - WEBRE 500KV CKT 1 | 0 | 303005 | 8CAJUN2 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T6475514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 95.1293 | 95.1 | [7 empty] | CATEGORYB | SINGLE | ELDORADO EHV - MOUNT OLIVE 500KV CKT 1 | 0 | 337368 | 8MTOLIV 500.00 | 337561 | 8ELDEHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16WP | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4825516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 95.1323 | 95.1 | [7 empty] | CATEGORYB | SINGLE | ELDORADO EHV - MOUNT OLIVE 500KV CKT 1 | 0 | 337368 | 8MTOLIV 500.00 | 337561 | 8ELDEHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T5175517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95.1 | 95.053 | 95.1 | [7 empty] | CATEGORYB | SINGLE | ELDORADO EHV - MOUNT OLIVE 500KV CKT 1 | 0 | 337368 | 8MTOLIV 500.00 | 337561 | 8ELDEHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2011AG2AFS91T2015014WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 95.1384 | 95 | [7 empty] | CATEGORYB | SINGLE | WATERFORD - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WGLEN 500.00 | 336150 | 8WATERFO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T7315514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 95.1066 | 95 | [7 empty] | CATEGORYB | SINGLE | BARKERS 6 230.00 - BOGALUSA 230KV CKT 1 | 0 | 500025 | BARKERS 6 230.00 | 336136 | 6BOGALUS 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16WP | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2011AG2AFS91T2035016WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 95.1375 | 95 | [7 empty] | CATEGORYB | SINGLE | WATERFORD - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WGLEN 500.00 | 336150 | 8WATERFO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16WP | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T5705516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 95.1077 | 95 | [7 empty] | CATEGORYB | SINGLE | BARKERS 6 230.00 - BOGALUSA 230KV CKT 1 | 0 | 500025 | BARKERS 6 230.00 | 336136 | 6BOGALUS 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T2275017WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95.1366 | 95.1366 | 95 | [7 empty] | CATEGORYB | SINGLE | WATERFORD - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WGLEN 500.00 | 336150 | 8WATERFO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T6215517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95.1 | 95.0521 | 95 | [7 empty] | CATEGORYB | SINGLE | BARKERS 6 230.00 - BOGALUSA 230KV CKT 1 | 0 | 500025 | BARKERS 6 230.00 | 336136 | 6BOGALUS 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3245514WP | TO->FROM | AINSWORTH - AINSWORTH 115KV CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640050 | AINSWND7 115.00 | 640051 | AINSWRT7 115.00 | 0 |  | 1 | 17WP | 120 | 120 | 132 |  | 87.4213 | 95.7 | [7 empty] | CATEGORYB | SINGLE | GRAND ISLAND - SWEETWATER 345KV CKT 1 | 0 | 640374 | SWEET W3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T725512WP | FROM->TO | ANADARKO 138/13.8KV TRANSFORMER CKT 1 | E | WFEC | WFEC | FLA | FLA | 0 | 520811 | ANADRK4 13.800 | 520814 | ANADARK4 138.00 | 0 |  | 1 | 12WP | 125 | 140 | 140 | 96.9 | 96.9267 | 98.3 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WOODWARD DISTRICT EHV 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4885512WP | FROM->TO | ANADARKO 138/13.8KV TRANSFORMER CKT 1 | E | WFEC | WFEC | FLA | FLA | 0 | 520811 | ANADRK4 13.800 | 520814 | ANADARK4 138.00 | 0 |  | 1 | 12WP | 125 | 140 | 140 | 96.9 | 96.9006 | 98.1 | [7 empty] | CATEGORYB | SINGLE | WOODWARD DISTRICT EHV (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T755513WP | FROM->TO | ANADARKO 138/13.8KV TRANSFORMER CKT 1 | E | WFEC | WFEC | FLA | FLA | 0 | 520811 | ANADRK4 13.800 | 520814 | ANADARK4 138.00 | 0 |  | 1 | 13WP | 125 | 140 | 140 | 96.451 | 96.451 | 97.9 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WOODWARD DISTRICT EHV 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T5525513WP | FROM->TO | ANADARKO 138/13.8KV TRANSFORMER CKT 1 | E | WFEC | WFEC | FLA | FLA | 0 | 520811 | ANADRK4 13.800 | 520814 | ANADARK4 138.00 | 0 |  | 1 | 13WP | 125 | 140 | 140 | 96.4 | 96.3982 | 97.7 | [7 empty] | CATEGORYB | SINGLE | WOODWARD DISTRICT EHV (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T15485517SP | TO->FROM | AUSTIN - EAST LYNNE TAP 69KV CKT 1 | E | AECI | AECI | KAMO | KAMO | 0 | 300699 | 2ELYNTP 69.000 | 300688 | 2AUSTIN 69.000 | 0 |  | 1 | 17SP | 36 | 36 | 0 | 85.4053 | 85.4053 | 95.8 | [7 empty] | CATEGORYB | SINGLE | CLINTON - MONTROSE 161KV CKT 1 | 0 | 542995 | MONTROS5 161.00 | 300071 | 5CLINTN 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T22875522SP | TO->FROM | AUSTIN - EAST LYNNE TAP 69KV CKT 1 | E | AECI | AECI | KAMO | KAMO | 0 | 300699 | 2ELYNTP 69.000 | 300688 | 2AUSTIN 69.000 | 0 |  | 1 | 22SP | 36 | 36 | 0 | 80.5064 | 80.5064 | 97.2 | [7 empty] | CATEGORYB | SINGLE | CLINTON - MONTROSE 161KV CKT 1 | 0 | 542995 | MONTROS5 161.00 | 300071 | 5CLINTN 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4445513SP | FROM->TO | BEAVER - EUREKA SPRINGS 161KV CKT 1 | E | SWPA | AEPW | EMINTH | FAYETTEVILLE | 0 | 505480 | BEAVER 5 161.00 | 506932 | EUREKA 5 161.00 | 0 |  | 1 | 13SP | 236 | 247 | 0 | 93.6888 | 93.6888 | 99.9 | [7 empty] | CATEGORYB | SINGLE | 7JASPER 345.00 - MORGAN 345KV CKT 1 | 0 | 300045 | 7MORGAN 345.00 | 300949 | 7JASPER 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1705513SP | FROM->TO | BEAVER - EUREKA SPRINGS 161KV CKT 1 | E | SWPA | AEPW | EMINTH | FAYETTEVILLE | 0 | 505480 | BEAVER 5 161.00 | 506932 | EUREKA 5 161.00 | 0 |  | 1 | 13SP | 236 | 247 | 0 | 91.8122 | 91.8122 | 98.6 | [7 empty] | CATEGORYB | SINGLE | FT SMITH - MUSKOGEE 345KV CKT 1 | 0 | 515224 | MUSKOGE7 345.00 | 515302 | FTSMITH7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1015517SP | FROM->TO | BEAVER - EUREKA SPRINGS 161KV CKT 1 | E | SWPA | AEPW | EMINTH | FAYETTEVILLE | 0 | 505480 | BEAVER 5 161.00 | 506932 | EUREKA 5 161.00 | 0 |  | 1 | 17SP | 236 | 247 | 0 | 87.3893 | 87.3893 | 98.2 | [7 empty] | CATEGORYB | SINGLE | EROGERS7 345.00 - OSBOURNE 345KV CKT 1 | 0 | 506979 | SHIPERD7 345.00 | 506982 | EROGERS7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T13325517SP | FROM->TO | BEAVER - EUREKA SPRINGS 161KV CKT 1 | E | SWPA | AEPW | EMINTH | FAYETTEVILLE | 0 | 505480 | BEAVER 5 161.00 | 506932 | EUREKA 5 161.00 | 0 |  | 1 | 17SP | 236 | 247 | 0 | 86.4909 | 86.4909 | 97.4 | [7 empty] | CATEGORYB | SINGLE | EROGERS7 345.00 - OSAGE CREEK 345KV CKT 1 | 0 | 506982 | EROGERS7 345.00 | 338683 | 7OSAGECK 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T965516SP | FROM->TO | BEAVER - EUREKA SPRINGS 161KV CKT 1 | E | SWPA | AEPW | EMINTH | FAYETTEVILLE | 0 | 505480 | BEAVER 5 161.00 | 506932 | EUREKA 5 161.00 | 0 |  | 1 | 17SP | 236 | 247 | 0 |  | 87.1955 | 95 | [7 empty] | CATEGORYB | SINGLE | EROGERS7 345.00 - OSBOURNE 345KV CKT 1 | 0 | 506979 | SHIPERD7 345.00 | 506982 | EROGERS7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T6225012SP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 12SP | 68 | 68 | 0 | 97.7145 | 97.7145 | 97.9 | [7 empty] | CATEGORYB | SINGLE | JONESBORO - JONESBORO 161KV CKT 1 | 0 | 505418 | JONESBO5 161.00 | 338170 | 5JONES 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T4935012SP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 12SP | 68 | 68 | 0 | 96.4 | 96.365 | 96.2 | [7 empty] | CATEGORYB | SINGLE | INDEPENDENCE - MOOREFIELD 161KV CKT 1 | 0 | 338138 | 5MORFLD 161.00 | 338142 | 5ISES-1 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T7845513SP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 13SP | 68 | 68 | 0 | 95.5 | 95.4644 | 97.3 | [7 empty] | CATEGORYB | SINGLE | JONESBORO - JONESBORO 161KV CKT 1 | 0 | 505418 | JONESBO5 161.00 | 338170 | 5JONES 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19065522SP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 22SP | 68 | 68 | 0 | 93.6685 | 93.6685 | 96.9 | [7 empty] | CATEGORYB | SINGLE | JONESBORO - JONESBORO 161KV CKT 1 | 0 | 505418 | JONESBO5 161.00 | 338170 | 5JONES 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T5735522SP | TO->FROM | BETHANY - PATTONSBURG 69KV CKT 1 | E | AECI | AECI | NW | NW | 0 | 300209 | 2PATBRG 69.000 | 300220 | 2BETHNY 69.000 | 0 |  | 1 | 22SP | 36 | 36 | 0 | 91.5435 | 91.5435 | 96.2 | [7 empty] | CATEGORYB | SINGLE | TINDALL - TRENTON 69KV CKT 1 | 0 | 300237 | 2TINDAL 69.000 | 300239 | 2TRENTN 69.000 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3045516SP | FROM->TO | BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 | E | GMO | GMO |  |  | 0 | 541211 | BLSPS 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 | 17SP | 224 | 224 | 224 |  | 90.5395 | 99.6 | [7 empty] | CATEGORYB | SINGLE | DUNCAN ROAD - SIBLEYPL 161.00 161KV CKT 1 | 0 | 541235 | DUNCAN 5 161.00 | 541250 | SIBLEYPL 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T15075514SP | FROM->TO | BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 | E | GMO | GMO |  |  | 0 | 541211 | BLSPS 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 | 17SP | 224 | 224 | 224 |  | 85.3027 | 97.8 | [7 empty] | CATEGORYB | SINGLE | CLINTON - MONTROSE 161KV CKT 1 | 0 | 542995 | MONTROS5 161.00 | 300071 | 5CLINTN 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4185514SP | TO->FROM | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 | E | GMO | GMO |  |  | 0 | 541206 | PRALEE 5 161.00 | 541211 | BLSPS 5 161.00 | 0 |  | 1 | 17SP | 224 | 224 | 224 |  | 88.384 | 98.9 | [7 empty] | CATEGORYB | SINGLE | LOMA VISTA EAST - WINCHESTER JUNCTION NORTH 161KV CKT 1 | 0 | 542998 | LVISTAE5 161.00 | 543009 | WINJT N5 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19335514SP | TO->FROM | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 | E | GMO | GMO |  |  | 0 | 541206 | PRALEE 5 161.00 | 541211 | BLSPS 5 161.00 | 0 |  | 1 | 17SP | 224 | 224 | 224 |  | 88.1416 | 98.7 | [7 empty] | CATEGORYB | NONSINGLE | KCPL-MSL#10 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3195517SP | TO->FROM | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 | E | GMO | GMO |  |  | 0 | 541206 | PRALEE 5 161.00 | 541211 | BLSPS 5 161.00 | 0 |  | 1 | 17SP | 224 | 224 | 224 | 81.5184 | 81.5184 | 98.3 | [7 empty] | CATEGORYB | SINGLE | PLEASANT HILL - SIBLEY 345KV CKT 1 | 0 | 541200 | PHILL 7 345.00 | 541201 | SIBLEY 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3225517SP | TO->FROM | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 | E | GMO | GMO |  |  | 0 | 541206 | PRALEE 5 161.00 | 541211 | BLSPS 5 161.00 | 0 |  | 1 | 17SP | 224 | 224 | 224 | 88.2231 | 88.2231 | 98.1 | [7 empty] | CATEGORYB | SINGLE | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | 0 | 541205 | BLSPE 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2985516SP | TO->FROM | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 | E | GMO | GMO |  |  | 0 | 541206 | PRALEE 5 161.00 | 541211 | BLSPS 5 161.00 | 0 |  | 1 | 17SP | 224 | 224 | 224 |  | 88.0557 | 96.7 | [7 empty] | CATEGORYB | SINGLE | BLUE SPRINGS EAST - DUNCAN ROAD 161KV CKT 1 | 0 | 541205 | BLSPE 5 161.00 | 541235 | DUNCAN 5 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T22435517SP | TO->FROM | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 | E | GMO | GMO |  |  | 0 | 541206 | PRALEE 5 161.00 | 541211 | BLSPS 5 161.00 | 0 |  | 1 | 17SP | 224 | 224 | 224 | 83.9605 | 83.9605 | 96.5 | [7 empty] | CATEGORYB | GENOUT | GEN541151 3-SIBLEY GENERATING UNIT #3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-16SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T20225516SP | TO->FROM | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 | E | GMO | GMO |  |  | 0 | 541206 | PRALEE 5 161.00 | 541211 | BLSPS 5 161.00 | 0 |  | 1 | 17SP | 224 | 224 | 224 |  | 84.8043 | 96.1 | [7 empty] | CATEGORYB | GENOUT | GEN541151 3-SIBLEY GENERATING UNIT #3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-16SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3135516SP | TO->FROM | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 | E | GMO | GMO |  |  | 0 | 541206 | PRALEE 5 161.00 | 541211 | BLSPS 5 161.00 | 0 |  | 1 | 17SP | 224 | 224 | 224 |  | 84.5229 | 95.5 | [7 empty] | CATEGORYB | SINGLE | LEEDS - WINCHESTER JUNCTION NORTH 161KV CKT 1 | 0 | 542997 | LEEDS 5 161.00 | 543009 | WINJT N5 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4685522SP | TO->FROM | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 | E | GMO | GMO |  |  | 0 | 541206 | PRALEE 5 161.00 | 541211 | BLSPS 5 161.00 | 0 |  | 1 | 22SP | 224 | 224 | 224 | 87.0461 | 87.0461 | 99.5 | [7 empty] | CATEGORYB | SINGLE | LEEDS - WINCHESTER JUNCTION NORTH 161KV CKT 1 | 0 | 542997 | LEEDS 5 161.00 | 543009 | WINJT N5 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4695522SP | TO->FROM | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 | E | GMO | GMO |  |  | 0 | 541206 | PRALEE 5 161.00 | 541211 | BLSPS 5 161.00 | 0 |  | 1 | 22SP | 224 | 224 | 224 | 85.2215 | 85.2215 | 97.7 | [7 empty] | CATEGORYB | SINGLE | LOMA VISTA EAST - WINCHESTER JUNCTION NORTH 161KV CKT 1 | 0 | 542998 | LVISTAE5 161.00 | 543009 | WINJT N5 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4675522SP | FROM->TO | BLUE SPRINGS EAST - BLUE SPRINGS WEST 161KV CKT 1 | E | GMO | GMO |  |  | 0 | 541205 | BLSPE 5 161.00 | 541237 | BLSPW 5 161.00 | 0 |  | 1 | 22SP | 224 | 224 | 224 | 98.1 | 98.0794 | 98.6 | [7 empty] | CATEGORYB | SINGLE | LEEDS - WINCHESTER JUNCTION NORTH 161KV CKT 1 | 0 | 542997 | LEEDS 5 161.00 | 543009 | WINJT N5 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3095512WP | TO->FROM | BOGALUSA - FRANKLIN 500KV CKT 1 | E | EES | EES | AEC | AMSNSH | 0 | 336562 | 8FRKLIN 500.00 | 336130 | 8BOGALUS 500.00 | 0 |  | 1 | 12WP | 1200 | 1200 | 0 | 94.5215 | 94.5215 | 96.2 | [7 empty] | CATEGORYB | SINGLE | FRANKLIN - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 336562 | 8FRKLIN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T7365512WP | TO->FROM | BOGALUSA - FRANKLIN 500KV CKT 1 | E | EES | EES | AEC | AMSNSH | 0 | 336562 | 8FRKLIN 500.00 | 336130 | 8BOGALUS 500.00 | 0 |  | 1 | 12WP | 1200 | 1200 | 0 | 94.1049 | 94.1049 | 95.8 | [7 empty] | CATEGORYB | NONSINGLE | CELE-WELLOP1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3305513WP | TO->FROM | BOGALUSA - FRANKLIN 500KV CKT 1 | E | EES | EES | AEC | AMSNSH | 0 | 336562 | 8FRKLIN 500.00 | 336130 | 8BOGALUS 500.00 | 0 |  | 1 | 13WP | 1200 | 1200 | 0 | 97.6 | 97.6395 | 98.9 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8995513WP | TO->FROM | BOGALUSA - FRANKLIN 500KV CKT 1 | E | EES | EES | AEC | AMSNSH | 0 | 336562 | 8FRKLIN 500.00 | 336130 | 8BOGALUS 500.00 | 0 |  | 1 | 13WP | 1200 | 1200 | 0 | 97.1606 | 97.1606 | 98.6 | [7 empty] | CATEGORYB | GENOUT | GEN336153 1-WATERFORD UNIT#3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T9115513WP | TO->FROM | BOGALUSA - FRANKLIN 500KV CKT 1 | E | EES | EES | AEC | AMSNSH | 0 | 336562 | 8FRKLIN 500.00 | 336130 | 8BOGALUS 500.00 | 0 |  | 1 | 13WP | 1200 | 1200 | 0 | 95.5631 | 95.5631 | 96.9 | [7 empty] | CATEGORYB | GENOUT | GEN336251 1-NINEMILE POINT UNIT#4 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4435517WP | TO->FROM | BOGALUSA - FRANKLIN 500KV CKT 1 | E | EES | EES | AEC | AMSNSH | 0 | 336562 | 8FRKLIN 500.00 | 336130 | 8BOGALUS 500.00 | 0 |  | 1 | 17WP | 1200 | 1200 | 0 | 95.1841 | 95.1841 | 98.4 | [7 empty] | CATEGORYB | SINGLE | FRANKLIN - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 336562 | 8FRKLIN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10775517WP | TO->FROM | BOGALUSA - FRANKLIN 500KV CKT 1 | E | EES | EES | AEC | AMSNSH | 0 | 336562 | 8FRKLIN 500.00 | 336130 | 8BOGALUS 500.00 | 0 |  | 1 | 17WP | 1200 | 1200 | 0 | 94.7246 | 94.7246 | 97.9 | [7 empty] | CATEGORYB | NONSINGLE | CELE-WELLOP1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-16WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4095516WP | TO->FROM | BOGALUSA - FRANKLIN 500KV CKT 1 | E | EES | EES | AEC | AMSNSH | 0 | 336562 | 8FRKLIN 500.00 | 336130 | 8BOGALUS 500.00 | 0 |  | 1 | 17WP | 1200 | 1200 | 0 |  | 95.6465 | 97.3 | [7 empty] | CATEGORYB | SINGLE | FRANKLIN - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 336562 | 8FRKLIN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T5745514WP | TO->FROM | BOGALUSA - FRANKLIN 500KV CKT 1 | E | EES | EES | AEC | AMSNSH | 0 | 336562 | 8FRKLIN 500.00 | 336130 | 8BOGALUS 500.00 | 0 |  | 1 | 17WP | 1200 | 1200 | 0 |  | 95.6123 | 97.2 | [7 empty] | CATEGORYB | SINGLE | FRANKLIN - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 336562 | 8FRKLIN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T12075514WP | TO->FROM | BOGALUSA - FRANKLIN 500KV CKT 1 | E | EES | EES | AEC | AMSNSH | 0 | 336562 | 8FRKLIN 500.00 | 336130 | 8BOGALUS 500.00 | 0 |  | 1 | 17WP | 1200 | 1200 | 0 |  | 95.1508 | 96.8 | [7 empty] | CATEGORYB | NONSINGLE | CELE-WELLOP1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-16WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10125516WP | TO->FROM | BOGALUSA - FRANKLIN 500KV CKT 1 | E | EES | EES | AEC | AMSNSH | 0 | 336562 | 8FRKLIN 500.00 | 336130 | 8BOGALUS 500.00 | 0 |  | 1 | 17WP | 1200 | 1200 | 0 |  | 95.185 | 96.8 | [7 empty] | CATEGORYB | NONSINGLE | CELE-WELLOP1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3295513WP | FROM->TO | BOGALUSA 500/230KV TRANSFORMER CKT 1 | E | EES | EES | AMSNSH | AMSNSH | 0 | 336130 | 8BOGALUS 500.00 | 336131 | 6ADMSCRK 230.00 | 0 |  | 1 | 13WP | 1200 | 1200 | 0 | 94.4965 | 94.4965 | 95.6 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2075513WP | FROM->TO | BROKEN BOW - LOUP CITY 115KV CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640089 | BROKENB7 115.00 | 640259 | LOUPCTY7 115.00 | 0 |  | 1 | 13WP | 120 | 120 | 127 | 76.5545 | 76.5545 | 98.7 | [7 empty] | CATEGORYB | SINGLE | CROOKED CREEK - RIVERDALE 230KV CKT 1 | 0 | 640093 | C.CREEK4 230.00 | 640330 | RIVERDL4 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2055513WP | FROM->TO | BROKEN BOW - LOUP CITY 115KV CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640089 | BROKENB7 115.00 | 640259 | LOUPCTY7 115.00 | 0 |  | 1 | 13WP | 120 | 120 | 127 | 64.6913 | 64.6913 | 97.6 | [7 empty] | CATEGORYB | SINGLE | BROKEN BOW - CROOKED CREEK 115KV CKT 1 | 0 | 640089 | BROKENB7 115.00 | 640094 | C.CREEK7 115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T6505513WP | FROM->TO | BROKEN BOW - LOUP CITY 115KV CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640089 | BROKENB7 115.00 | 640259 | LOUPCTY7 115.00 | 0 |  | 1 | 13WP | 120 | 120 | 127 | 64.6164 | 64.6164 | 97.3 | [7 empty] | CATEGORYB | SINGLE | CROOKED CREEK (CR.CREEK T1) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 640093 | C.CREEK4 230.00 | 640094 | C.CREEK7 115.00 | 643026 | CRKDCREEKT1913.800 | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1615516WP | FROM->TO | BROKEN BOW - LOUP CITY 115KV CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640089 | BROKENB7 115.00 | 640259 | LOUPCTY7 115.00 | 0 |  | 1 | 17WP | 120 | 120 | 127 |  | 75.7926 | 99.6 | [7 empty] | CATEGORYB | SINGLE | GRAND ISLAND - SWEETWATER 345KV CKT 1 | 0 | 640374 | SWEET W3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1645517WP | FROM->TO | BROKEN BOW - LOUP CITY 115KV CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640089 | BROKENB7 115.00 | 640259 | LOUPCTY7 115.00 | 0 |  | 1 | 17WP | 120 | 120 | 127 | 63.8885 | 63.8885 | 98.4 | [7 empty] | CATEGORYB | SINGLE | BROKEN BOW - CROOKED CREEK 115KV CKT 1 | 0 | 640089 | BROKENB7 115.00 | 640094 | C.CREEK7 115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1545516WP | FROM->TO | BROKEN BOW - LOUP CITY 115KV CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640089 | BROKENB7 115.00 | 640259 | LOUPCTY7 115.00 | 0 |  | 1 | 17WP | 120 | 120 | 127 |  | 75.0316 | 98.1 | [7 empty] | CATEGORYB | SINGLE | CROOKED CREEK - RIVERDALE 230KV CKT 1 | 0 | 640093 | C.CREEK4 230.00 | 640330 | RIVERDL4 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3045514WP | FROM->TO | BROKEN BOW - LOUP CITY 115KV CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640089 | BROKENB7 115.00 | 640259 | LOUPCTY7 115.00 | 0 |  | 1 | 17WP | 120 | 120 | 127 |  | 72.6666 | 98 | [7 empty] | CATEGORYB | SINGLE | GERALD GENTLEMAN STATION - SWEETWATER 345KV CKT 2 | 0 | 640183 | GENTLMN3 345.00 | 640374 | SWEET W3 345.00 | 0 |  | 2 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8115517WP | FROM->TO | BROKEN BOW - LOUP CITY 115KV CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640089 | BROKENB7 115.00 | 640259 | LOUPCTY7 115.00 | 0 |  | 1 | 17WP | 120 | 120 | 127 | 63.8461 | 63.8461 | 98 | [7 empty] | CATEGORYB | SINGLE | CROOKED CREEK (CR.CREEK T1) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 640093 | C.CREEK4 230.00 | 640094 | C.CREEK7 115.00 | 643026 | CRKDCREEKT1913.800 | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3075514WP | FROM->TO | BROKEN BOW - LOUP CITY 115KV CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640089 | BROKENB7 115.00 | 640259 | LOUPCTY7 115.00 | 0 |  | 1 | 17WP | 120 | 120 | 127 |  | 72.6103 | 97.8 | [7 empty] | CATEGORYB | SINGLE | GRAND ISLAND - RIVERDALE 230KV CKT 1 | 0 | 640200 | GR ISLD4 230.00 | 640330 | RIVERDL4 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1615517WP | FROM->TO | BROKEN BOW - LOUP CITY 115KV CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640089 | BROKENB7 115.00 | 640259 | LOUPCTY7 115.00 | 0 |  | 1 | 17WP | 120 | 120 | 127 | 71.7814 | 71.7814 | 97.1 | [7 empty] | CATEGORYB | SINGLE | AINSWORTH - AINSWORTH 115KV CKT 1 | 0 | 640050 | AINSWND7 115.00 | 640051 | AINSWRT7 115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2895514WP | FROM->TO | BROKEN BOW - LOUP CITY 115KV CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640089 | BROKENB7 115.00 | 640259 | LOUPCTY7 115.00 | 0 |  | 1 | 17WP | 120 | 120 | 127 |  | 71.2158 | 96.8 | [7 empty] | CATEGORYB | SINGLE | AXTELL - PAULINE 345KV CKT 1 | 0 | 640065 | AXTELL 3 345.00 | 640312 | PAULINE3 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1525516WP | FROM->TO | BROKEN BOW - LOUP CITY 115KV CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640089 | BROKENB7 115.00 | 640259 | LOUPCTY7 115.00 | 0 |  | 1 | 17WP | 120 | 120 | 127 |  | 63.751 | 96.5 | [7 empty] | CATEGORYB | SINGLE | BROKEN BOW - CROOKED CREEK 115KV CKT 1 | 0 | 640089 | BROKENB7 115.00 | 640094 | C.CREEK7 115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1105522SP | FROM->TO | BROOKLINE - JUNCTION 161KV CKT 1 | E | SPRM | SPRM | SPRM > 69KV | SPRM > 69KV | 0 | 549969 | BROOKLINE 5161.00 | 549955 | JUNCTION 5161.00 | 0 |  | 1 | 22SP | 334.6 | 334.6 | 0 | 92.8434 | 92.8434 | 95.6 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE - SPRINGFIELD 161KV CKT 1 | 0 | 505492 | SPRGFLD5 161.00 | 549969 | BROOKLINE 5161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T15945517SP | FROM->TO | BROOKLINE (BRKLTX1) 345/161/13.2KV TRANSFORMER CKT 1 | E | SPRM | SPRM | SPRM > 69KV | SPRM > 69KV | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549988 | BRKLNE XF1 113.200 | 1 | 17SP | 400 | 400 | 0 | 92.8354 | 92.8354 | 96.6 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE (BRKLTX2) 345/161/13.2KV TRANSFORMER CKT 2 | 1 | 549969 | BROOKLINE 5161.00 | 549984 | BROOKLINE 7345.00 | 549989 | BRKLNE XF2 113.200 | 2 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T20415517SP | FROM->TO | BROOKLINE (BRKLTX1) 345/161/13.2KV TRANSFORMER CKT 1 | E | SPRM | SPRM | SPRM > 69KV | SPRM > 69KV | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549988 | BRKLNE XF1 113.200 | 1 | 17SP | 400 | 400 | 0 | 91.3592 | 91.3592 | 95.9 | [7 empty] | CATEGORYB | NONSINGLE | SPRM-OPGD-02 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-16SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T14495516SP | FROM->TO | BROOKLINE (BRKLTX1) 345/161/13.2KV TRANSFORMER CKT 1 | E | SPRM | SPRM | SPRM > 69KV | SPRM > 69KV | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549988 | BRKLNE XF1 113.200 | 1 | 17SP | 400 | 400 | 0 |  | 92.9155 | 95.6 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE (BRKLTX2) 345/161/13.2KV TRANSFORMER CKT 2 | 1 | 549969 | BROOKLINE 5161.00 | 549984 | BROOKLINE 7345.00 | 549989 | BRKLNE XF2 113.200 | 2 | Transfer Loading < 100%
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T15525514SP | FROM->TO | BROOKLINE (BRKLTX1) 345/161/13.2KV TRANSFORMER CKT 1 | E | SPRM | SPRM | SPRM > 69KV | SPRM > 69KV | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549988 | BRKLNE XF1 113.200 | 1 | 17SP | 400 | 400 | 0 |  | 92.8618 | 95.4 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE (BRKLTX2) 345/161/13.2KV TRANSFORMER CKT 2 | 1 | 549969 | BROOKLINE 5161.00 | 549984 | BROOKLINE 7345.00 | 549989 | BRKLNE XF2 113.200 | 2 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T15925517SP | FROM->TO | BROOKLINE (BRKLTX2) 345/161/13.2KV TRANSFORMER CKT 2 | E | SPRM | SPRM | SPRM > 69KV | SPRM > 69KV | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549989 | BRKLNE XF2 113.200 | 2 | 17SP | 400 | 400 | 0 | 92.5522 | 92.5522 | 96.3 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE (BRKLTX1) 345/161/13.2KV TRANSFORMER CKT 1 | 1 | 549969 | BROOKLINE 5161.00 | 549984 | BROOKLINE 7345.00 | 549988 | BRKLNE XF1 113.200 | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T20405517SP | FROM->TO | BROOKLINE (BRKLTX2) 345/161/13.2KV TRANSFORMER CKT 2 | E | SPRM | SPRM | SPRM > 69KV | SPRM > 69KV | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549989 | BRKLNE XF2 113.200 | 2 | 17SP | 400 | 400 | 0 | 91.098 | 91.098 | 95.7 | [7 empty] | CATEGORYB | NONSINGLE | SPRM-OPGD-01 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-16SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T14485516SP | FROM->TO | BROOKLINE (BRKLTX2) 345/161/13.2KV TRANSFORMER CKT 2 | E | SPRM | SPRM | SPRM > 69KV | SPRM > 69KV | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549989 | BRKLNE XF2 113.200 | 2 | 17SP | 400 | 400 | 0 |  | 92.6319 | 95.3 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE (BRKLTX1) 345/161/13.2KV TRANSFORMER CKT 1 | 1 | 549969 | BROOKLINE 5161.00 | 549984 | BROOKLINE 7345.00 | 549988 | BRKLNE XF1 113.200 | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T15515514SP | FROM->TO | BROOKLINE (BRKLTX2) 345/161/13.2KV TRANSFORMER CKT 2 | E | SPRM | SPRM | SPRM > 69KV | SPRM > 69KV | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549989 | BRKLNE XF2 113.200 | 2 | 17SP | 400 | 400 | 0 |  | 92.5784 | 95.1 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE (BRKLTX1) 345/161/13.2KV TRANSFORMER CKT 1 | 1 | 549969 | BROOKLINE 5161.00 | 549984 | BROOKLINE 7345.00 | 549988 | BRKLNE XF1 113.200 | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T9955514SP | FROM->TO | BULL SHOALS - MIDWAY (YVEPA) 161KV CKT 1 | E | SWPA | EES | EMINTH |  | 0 | 505460 | BULL SH5 161.00 | 338813 | 5MIDWAY# 161.00 | 0 |  | 1 | 17SP | 162 | 162 | 0 |  | 93.7357 | 99.8 | [7 empty] | CATEGORYB | SINGLE | BATESVILLE - CUSHMAN 161KV CKT 1 | 0 | 338135 | 5CUSHMN 161.00 | 338137 | 5BATEVL 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8835516SP | FROM->TO | BULL SHOALS - MIDWAY (YVEPA) 161KV CKT 1 | E | SWPA | EES | EMINTH |  | 0 | 505460 | BULL SH5 161.00 | 338813 | 5MIDWAY# 161.00 | 0 |  | 1 | 17SP | 162 | 162 | 0 |  | 93.3594 | 99.5 | [7 empty] | CATEGORYB | SINGLE | 5MTPLEASANT 161.00 - CUSHMAN 161KV CKT 1 | 0 | 338129 | 5MTPLEASANT 161.00 | 338135 | 5CUSHMN 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T9945514SP | FROM->TO | BULL SHOALS - MIDWAY (YVEPA) 161KV CKT 1 | E | SWPA | EES | EMINTH |  | 0 | 505460 | BULL SH5 161.00 | 338813 | 5MIDWAY# 161.00 | 0 |  | 1 | 17SP | 162 | 162 | 0 |  | 93.0906 | 98.9 | [7 empty] | CATEGORYB | SINGLE | 5MTPLEASANT 161.00 - CUSHMAN 161KV CKT 1 | 0 | 338129 | 5MTPLEASANT 161.00 | 338135 | 5CUSHMN 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8825516SP | FROM->TO | BULL SHOALS - MIDWAY (YVEPA) 161KV CKT 1 | E | SWPA | EES | EMINTH |  | 0 | 505460 | BULL SH5 161.00 | 338813 | 5MIDWAY# 161.00 | 0 |  | 1 | 17SP | 162 | 162 | 0 |  | 92.0935 | 98.2 | [7 empty] | CATEGORYB | SINGLE | 5MTPLEASANT 161.00 - SAGE SS 161KV CKT 1 | 0 | 338129 | 5MTPLEASANT 161.00 | 338132 | 5SAGE* 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19855516SP | FROM->TO | BULL SHOALS - MIDWAY (YVEPA) 161KV CKT 1 | E | SWPA | EES | EMINTH |  | 0 | 505460 | BULL SH5 161.00 | 338813 | 5MIDWAY# 161.00 | 0 |  | 1 | 17SP | 162 | 162 | 0 |  | 89.4514 | 97.9 | [7 empty] | CATEGORYB | GENOUT | GEN338143 1-INDEPENDENCE UNIT #1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T9935514SP | FROM->TO | BULL SHOALS - MIDWAY (YVEPA) 161KV CKT 1 | E | SWPA | EES | EMINTH |  | 0 | 505460 | BULL SH5 161.00 | 338813 | 5MIDWAY# 161.00 | 0 |  | 1 | 17SP | 162 | 162 | 0 |  | 91.8172 | 97.7 | [7 empty] | CATEGORYB | SINGLE | 5MTPLEASANT 161.00 - SAGE SS 161KV CKT 1 | 0 | 338129 | 5MTPLEASANT 161.00 | 338132 | 5SAGE* 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SPP_FG-EES-IDC-AFC-40094-BSMID_INDMOR | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T5405517WP | FROM->TO | BULL SHOALS - MIDWAY (YVEPA) 161KV CKT 1 | E | SWPA | EES | EMINTH |  | 0 | 505460 | BULL SH5 161.00 | 338813 | 5MIDWAY# 161.00 | 0 |  | 1 | 17WP | 162 | 162 | 0 | 88.0706 | 88.0706 | 95.7 | [7 empty] | CATEGORYB | SINGLE | INDEPENDENCE - MOOREFIELD 161KV CKT 1 | 0 | 338138 | 5MORFLD 161.00 | 338142 | 5ISES-1 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T5395517WP | FROM->TO | BULL SHOALS - MIDWAY (YVEPA) 161KV CKT 1 | E | SWPA | EES | EMINTH |  | 0 | 505460 | BULL SH5 161.00 | 338813 | 5MIDWAY# 161.00 | 0 |  | 1 | 17WP | 162 | 162 | 0 | 87.7514 | 87.7514 | 95.2 | [7 empty] | CATEGORYB | SINGLE | BATESVILLE - MOOREFIELD 161KV CKT 1 | 0 | 338137 | 5BATEVL 161.00 | 338138 | 5MORFLD 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T15325522SP | FROM->TO | BULL SHOALS - MIDWAY (YVEPA) 161KV CKT 1 | E | SWPA | EES | EMINTH |  | 0 | 505460 | BULL SH5 161.00 | 338813 | 5MIDWAY# 161.00 | 0 |  | 1 | 22SP | 162 | 162 | 0 | 89.4483 | 89.4483 | 96.5 | [7 empty] | CATEGORYB | SINGLE | MELBOURNE - SAGE SS 161KV CKT 1 | 0 | 338131 | 5MELBRN 161.00 | 338132 | 5SAGE* 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19375522SP | FROM->TO | BULL SHOALS - MIDWAY (YVEPA) 161KV CKT 1 | E | SWPA | EES | EMINTH |  | 0 | 505460 | BULL SH5 161.00 | 338813 | 5MIDWAY# 161.00 | 0 |  | 1 | 22SP | 162 | 162 | 0 | 88.9457 | 88.9457 | 95.9 | [7 empty] | CATEGORYB | SINGLE | CALICO ROCK - NORFORK 161KV CKT 1 | 0 | 505448 | NORFORK5 161.00 | 338130 | 5CALCR 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T15535522SP | FROM->TO | BULL SHOALS - MIDWAY (YVEPA) 161KV CKT 1 | E | SWPA | EES | EMINTH |  | 0 | 505460 | BULL SH5 161.00 | 338813 | 5MIDWAY# 161.00 | 0 |  | 1 | 22SP | 162 | 162 | 0 | 86.3391 | 86.3391 | 95.8 | [7 empty] | CATEGORYB | SINGLE | INDEPENDENCE - LS POWER OSCEOLA UNIT 500KV CKT 1 | 0 | 338144 | 8ISXF 500.00 | 338145 | 8ISES 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T945512WP | FROM->TO | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | 12WP | 329 | 360 | 0 | 93.798 | 93.798 | 96.6 | [7 empty] | CATEGORYB | SINGLE | AMARILLO SOUTH INTERCHANGE - NICHOLS STATION 230KV CKT 1 | 0 | 524044 | NICHOLS 6230.00 | 524415 | AMA_SOUTH 6230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8435512WP | FROM->TO | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | 12WP | 329 | 360 | 0 | 93.0228 | 93.0228 | 95.5 | [7 empty] | CATEGORYB | GENOUT | GEN527902 1-HOBBS PLANT #2 (CT) | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T16195513SP | FROM->TO | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | 13SP | 318 | 350 | 0 | 97.8587 | 97.8587 | 99.9 | [7 empty] | CATEGORYB | GENOUT | GEN525562 1-TOLK GEN #2 24 KV | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T16175513SP | FROM->TO | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | 13SP | 318 | 350 | 0 | 94.3665 | 94.3665 | 96.2 | [7 empty] | CATEGORYB | GENOUT | GEN525561 1-TOLK GEN #1 24 KV | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T755512WP | FROM->TO | CANTON - OKEENE 69KV CKT 1 | E | WFEC | WFEC | AEP-OP | AEP-IM | 0 | 520843 | CANTON-2 69.000 | 521015 | OKEENE 2 69.000 | 0 |  | 1 | 12WP | 48 | 48 | 48 | 93.9113 | 93.9113 | 99.6 | [7 empty] | CATEGORYB | SINGLE | CEDARDALE - MOORELAND 138KV CKT 1 | 0 | 520848 | CEDRDAL4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T795512WP | FROM->TO | CANTON - OKEENE 69KV CKT 1 | E | WFEC | WFEC | AEP-OP | AEP-IM | 0 | 520843 | CANTON-2 69.000 | 521015 | OKEENE 2 69.000 | 0 |  | 1 | 12WP | 48 | 48 | 48 | 92.585 | 92.585 | 98.3 | [7 empty] | CATEGORYB | SINGLE | CEDARDALE - OKEENE 138KV CKT 1 | 0 | 520848 | CEDRDAL4 138.00 | 521016 | OKEENE 4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1635513SP | FROM->TO | CANTON - OKEENE 69KV CKT 1 | E | WFEC | WFEC | AEP-OP | AEP-IM | 0 | 520843 | CANTON-2 69.000 | 521015 | OKEENE 2 69.000 | 0 |  | 1 | 13SP | 48 | 48 | 48 | 91.7391 | 91.7391 | 96.2 | [7 empty] | CATEGORYB | SINGLE | DEWEY - SOUTHARD 138KV CKT 1 | 0 | 514787 | DEWEY 4 138.00 | 514822 | SOUTHRD4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T675513WP | FROM->TO | CANTON - OKEENE 69KV CKT 1 | E | WFEC | WFEC | AEP-OP | AEP-IM | 0 | 520843 | CANTON-2 69.000 | 521015 | OKEENE 2 69.000 | 0 |  | 1 | 13WP | 48 | 48 | 48 | 91.9472 | 91.9472 | 96.6 | [7 empty] | CATEGORYB | SINGLE | DEWEY - SOUTHARD 138KV CKT 1 | 0 | 514787 | DEWEY 4 138.00 | 514822 | SOUTHRD4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1875516SP | FROM->TO | CANTON - OKEENE 69KV CKT 1 | E | WFEC | WFEC | AEP-OP | AEP-IM | 0 | 520843 | CANTON-2 69.000 | 521015 | OKEENE 2 69.000 | 0 |  | 1 | 17SP | 48 | 48 | 48 |  | 88.006 | 98.7 | [7 empty] | CATEGORYB | SINGLE | CEDARDALE - MOORELAND 138KV CKT 1 | 0 | 520848 | CEDRDAL4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1885516SP | FROM->TO | CANTON - OKEENE 69KV CKT 1 | E | WFEC | WFEC | AEP-OP | AEP-IM | 0 | 520843 | CANTON-2 69.000 | 521015 | OKEENE 2 69.000 | 0 |  | 1 | 17SP | 48 | 48 | 48 |  | 86.484 | 97.2 | [7 empty] | CATEGORYB | SINGLE | CEDARDALE - OKEENE 138KV CKT 1 | 0 | 520848 | CEDRDAL4 138.00 | 521016 | OKEENE 4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T915514WP | FROM->TO | CANTON - OKEENE 69KV CKT 1 | E | WFEC | WFEC | AEP-OP | AEP-IM | 0 | 520843 | CANTON-2 69.000 | 521015 | OKEENE 2 69.000 | 0 |  | 1 | 17WP | 48 | 48 | 48 |  | 82.8802 | 99.5 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T865517WP | FROM->TO | CANTON - OKEENE 69KV CKT 1 | E | WFEC | WFEC | AEP-OP | AEP-IM | 0 | 520843 | CANTON-2 69.000 | 521015 | OKEENE 2 69.000 | 0 |  | 1 | 17WP | 48 | 48 | 48 | 83.6993 | 83.6993 | 98.8 | [7 empty] | CATEGORYB | SINGLE | CEDARDALE - OKEENE 138KV CKT 1 | 0 | 520848 | CEDRDAL4 138.00 | 521016 | OKEENE 4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T915516WP | FROM->TO | CANTON - OKEENE 69KV CKT 1 | E | WFEC | WFEC | AEP-OP | AEP-IM | 0 | 520843 | CANTON-2 69.000 | 521015 | OKEENE 2 69.000 | 0 |  | 1 | 17WP | 48 | 48 | 48 |  | 85.2128 | 96.5 | [7 empty] | CATEGORYB | SINGLE | CEDARDALE - MOORELAND 138KV CKT 1 | 0 | 520848 | CEDRDAL4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T925516WP | FROM->TO | CANTON - OKEENE 69KV CKT 1 | E | WFEC | WFEC | AEP-OP | AEP-IM | 0 | 520843 | CANTON-2 69.000 | 521015 | OKEENE 2 69.000 | 0 |  | 1 | 17WP | 48 | 48 | 48 |  | 83.9656 | 95.2 | [7 empty] | CATEGORYB | SINGLE | CEDARDALE - OKEENE 138KV CKT 1 | 0 | 520848 | CEDRDAL4 138.00 | 521016 | OKEENE 4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2765522SP | FROM->TO | CANTON - OKEENE 69KV CKT 1 | E | WFEC | WFEC | AEP-OP | AEP-IM | 0 | 520843 | CANTON-2 69.000 | 521015 | OKEENE 2 69.000 | 0 |  | 1 | 22SP | 48 | 48 | 48 | 85.1376 | 85.1376 | 96.4 | [7 empty] | CATEGORYB | SINGLE | CEDARDALE - MOORELAND 138KV CKT 1 | 0 | 520848 | CEDRDAL4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T1875012SP | TO->FROM | CENTENNIAL - COWSKIN 138KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533038 | COWSKIN4 138.00 | 533034 | CENTENN4 138.00 | 0 |  | 1 | 12SP | 232 | 232 | 0 | 98.6 | 98.6324 | 98.6 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T21945522SP | FROM->TO | CHAVES COUNTY INTERCHANGE (GE M102125) 230/115/13.2KV TRANSFORMER CKT 2 | E | SPS | SPS | SPS-PECO | SPS-PECO | 1 | 527483 | CHAVES_CNTY6230.00 | 527482 | CHAVES_CNTY3115.00 | 527479 | CHAVES_TR2 113.200 | 2 | 22SP | 149 | 171 | 0 | 99.1 | 99.1345 | 99.5 | [7 empty] | CATEGORYB | SINGLE | CHAVES COUNTY INTERCHANGE (ABB 801429) 230/115/13.2KV TRANSFORMER CKT 1 | 1 | 527482 | CHAVES_CNTY3115.00 | 527483 | CHAVES_CNTY6230.00 | 527478 | CHAVES_TR1 113.200 | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T4145022SP | FROM->TO | CHILLICOTHE 161/69KV TRANSFORMER CKT 2 | E | AECI | AECI | NW | NW | 0 | 300068 | 5CHILLI 161.00 | 300194 | 2CHILLI 69.000 | 0 |  | 2 | 22SP | 56 | 56 | 0 | 96.5063 | 96.5063 | 96.8 | [7 empty] | CATEGORYB | SINGLE | CHILLICOTHE 161/69KV TRANSFORMER CKT 1 | 0 | 300068 | 5CHILLI 161.00 | 300194 | 2CHILLI 69.000 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14SP | INVALID |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3305514SP | TO->FROM | CHISHOLM - MAIZE 138KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533054 | MAIZE 4 138.00 | 533035 | CHISHLM4 138.00 | 0 |  | 1 | 17SP | 382 | 382 | 0 |  | 94.2419 | 97.0891 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER NORTH - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533040 | EVANS N4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | INVALID | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T1825012SP | FROM->TO | CHISHOLM - RIPLEY 69KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533786 | CHISHLM2 69.000 | 533832 | RIPLEYM2 69.000 | 0 |  | 1 | 12SP | 139 | 139 | 0 | 97.4909 | 97.4909 | 97.4921 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER NORTH - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533040 | EVANS N4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | INVALID | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T1835012SP | FROM->TO | CHISHOLM (CHISLM1X) 138/69/13.2KV TRANSFORMER CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 1 | 533035 | CHISHLM4 138.00 | 533786 | CHISHLM2 69.000 | 533103 | CHISOLM1 13.200 | 1 | 12SP | 150 | 165 | 187.5 | 97.593 | 97.593 | 97.5937 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER NORTH - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533040 | EVANS N4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1515514WP | TO->FROM | CIRCLE - MULLERGREN 230KV CKT 1 | E | SUNC | WERE | GREAT PL | WEST | 0 | 539679 | MULGREN6 230.00 | 532871 | CIRCLE 6 230.00 | 0 |  | 1 | 17WP | 319 | 319 | 0 |  | 62.1321 | 95.1 | [7 empty] | CATEGORYB | SINGLE | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4225513SP | TO->FROM | CLAY - SPRINGFIELD 161KV CKT 1 | E | SWPA | SPRM | EMINTH | SPRM > 69KV | 0 | 505492 | SPRGFLD5 161.00 | 549970 | CLAY 5161.00 | 0 |  | 1 | 13SP | 167 | 167 | 0 | 94.2546 | 94.2546 | 99.6 | [7 empty] | CATEGORYB | SINGLE | JAMES RIVER - SOUTHWEST 161KV CKT 1 | 0 | 549954 | SWPS 5161.00 | 549961 | JAMES RIVER5161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T7215513SP | TO->FROM | CLAY - SPRINGFIELD 161KV CKT 1 | E | SWPA | SPRM | EMINTH | SPRM > 69KV | 0 | 505492 | SPRGFLD5 161.00 | 549970 | CLAY 5161.00 | 0 |  | 1 | 13SP | 167 | 167 | 0 | 87.8328 | 87.8328 | 95 | [7 empty] | CATEGORYB | SINGLE | HUBEN - MORGAN 345KV CKT 1 | 0 | 300042 | 7HUBEN 345.00 | 300045 | 7MORGAN 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10275516WP | TO->FROM | CLAY - SPRINGFIELD 161KV CKT 1 | E | SWPA | SPRM | EMINTH | SPRM > 69KV | 0 | 505492 | SPRGFLD5 161.00 | 549970 | CLAY 5161.00 | 0 |  | 1 | 17WP | 167 | 167 | 0 |  | 89.9393 | 98.8 | [7 empty] | CATEGORYB | NONSINGLE | AI03 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-14WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T12485514WP | TO->FROM | CLAY - SPRINGFIELD 161KV CKT 1 | E | SWPA | SPRM | EMINTH | SPRM > 69KV | 0 | 505492 | SPRGFLD5 161.00 | 549970 | CLAY 5161.00 | 0 |  | 1 | 17WP | 167 | 167 | 0 |  | 89.162 | 97.3 | [7 empty] | CATEGORYB | NONSINGLE | AI03 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1855512WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | E | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 12WP | 110 | 110 | 0 | 89.6775 | 89.6775 | 96.7 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3925513SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | E | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13SP | 110 | 110 | 0 | 87.2977 | 87.2977 | 95.6 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS-CHECK-TC-Iteration Limit Exceeded. |  | FDNS-CHECK-TC-Iteration Limit Exceeded. |  | 5 | 5 | 2011AG2AFS91T9155513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | E | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 91.1513 | 91.1513 | 99.5 | [7 empty] | CATEGORYB | GENOUT | GEN336821 1-GRAND GULF UNIT | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T9335513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | E | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 91.1028 | 91.1028 | 99.4 | [7 empty] | CATEGORYB | GENOUT | GEN514805 1-SOONER UNIT 1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 | INVALID | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2905517SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | E | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 110 | 110 | 0 | 76.2281 | 76.2281 | 97.7059 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER NORTH - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533040 | EVANS N4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1685514WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | E | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17WP | 110 | 110 | 0 |  | 77.6062 | 99.7 | [7 empty] | CATEGORYB | SINGLE | MINGO - SETAB 345KV CKT 1 | 0 | 531451 | MINGO 7 345.00 | 531465 | SETAB 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1665514WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | E | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17WP | 110 | 110 | 0 |  | 77.4904 | 99.6 | [7 empty] | CATEGORYB | SINGLE | GRAY CO 345.00 - HOLCOMB 345KV CKT 1 | 0 | 531449 | HOLCOMB7 345.00 | 560005 | GRAY CO 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16WP | INVALID |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1255516WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | E | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17WP | 110 | 110 | 0 |  | 84.586 | 97.5148 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER NORTH - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533040 | EVANS N4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1165517WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | E | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17WP | 110 | 110 | 0 | 69.2133 | 69.2133 | 97 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T65514WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | E | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17WP | 110 | 110 | 0 |  | 76.3194 | 96.1 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 | INVALID | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4065522SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | E | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 22SP | 110 | 110 | 0 | 73.5089 | 73.5089 | 96.5972 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER NORTH - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533040 | EVANS N4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T9135513SP | TO->FROM | CLEO CORNER - GLASS MOUNTAIN 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514788 | GLASMTN4 138.00 | 514778 | CLEOCOR4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 | 94.8408 | 94.8408 | 97.4 | [7 empty] | CATEGORYB | SINGLE | WOODWARD DISTRICT EHV (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1745513SP | TO->FROM | CLEO CORNER - GLASS MOUNTAIN 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514788 | GLASMTN4 138.00 | 514778 | CLEOCOR4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 | 94.8315 | 94.8315 | 97.3 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WOODWARD DISTRICT EHV 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T5395522SP | FROM->TO | COON CREEK - TRENTON 69KV CKT 1 | E | AECI | AECI | NW | NW | 0 | 300197 | 2COONCK 69.000 | 300239 | 2TRENTN 69.000 | 0 |  | 1 | 22SP | 36 | 36 | 0 | 82.8665 | 82.8665 | 98.8 | [7 empty] | CATEGORYB | SINGLE | FAIRPORT - HICKORY CREEK 161KV CKT 1 | 0 | 300076 | 5FAIRPT 161.00 | 300087 | 5HICKCK 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4635522SP | TO->FROM | CROSSTOWN - GRAND AVENUE WEST 161KV CKT 1 | E | KCPL | KCPL | DWNTWN | DWNTWN | 0 | 542988 | GRAND W5 161.00 | 542990 | CROSTWN5 161.00 | 0 |  | 1 | 22SP | 259 | 259 | 0 | 99.7 | 99.7381 | 96.3 | [7 empty] | CATEGORYB | SINGLE | CROSSTOWN - NORTHEAST 161KV CKT 1 | 0 | 542985 | NEAST 5 161.00 | 542990 | CROSTWN5 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4765522SP | TO->FROM | CROSSTOWN - NORTHEAST 161KV CKT 1 | E | KCPL | KCPL | DWNTWN | DWNTWN | 0 | 542985 | NEAST 5 161.00 | 542990 | CROSTWN5 161.00 | 0 |  | 1 | 22SP | 259 | 259 | 0 | 97.1 | 97.1065 | 98.7 | [7 empty] | CATEGORYB | SINGLE | GRAND AVENUE REACTOR - NORTHEAST REACTOR 161KV CKT 1 | 0 | 543636 | GRANDREA 161.00 | 543637 | NEASTREA 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4645522SP | TO->FROM | CROSSTOWN - NORTHEAST 161KV CKT 1 | E | KCPL | KCPL | DWNTWN | DWNTWN | 0 | 542985 | NEAST 5 161.00 | 542990 | CROSTWN5 161.00 | 0 |  | 1 | 22SP | 259 | 259 | 0 | 96.8649 | 96.8649 | 98.5 | [7 empty] | CATEGORYB | SINGLE | NORTHEAST - NORTHEAST REACTOR 161KV CKT 1 | 0 | 542985 | NEAST 5 161.00 | 543637 | NEASTREA 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | CONT-0402 - JEC - Summit 345kV | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T3285022SP | TO->FROM | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | E | WERE | WERE | NEAST | NCENTRAL | 0 | 532852 | JEC 6 230.00 | 532861 | EMANHAT6 230.00 | 0 |  | 1 | 22SP | 446 | 446 | 0 | 104.1 | 104.1052 | 97.4 | [7 empty] | CATEGORYB | SINGLE | JEFFREY ENERGY CENTER - SUMMIT 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532773 | SUMMIT 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T14355514SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | E | WERE | WERE | NCENTRAL | NCENTRAL | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 17SP | 280 | 308 | 350 |  | 95.2903 | 96.7 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST MANHATTAN (NWMANH1X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532865 | NWMANHT6 230.00 | 533347 | NWMANHT3 115.00 | 532901 | NWMANHX1 18.000 | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T22205522SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | E | WERE | WERE | NCENTRAL | NCENTRAL | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 22SP | 280 | 308 | 350 | 95.0498 | 95.0498 | 95.6 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST MANHATTAN (NWMANH1X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532865 | NWMANHT6 230.00 | 533347 | NWMANHT3 115.00 | 532901 | NWMANHX1 18.000 | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T2995022SP | TO->FROM | EAST SANGER SUB - TAYLOR SWITCHING STATION 115KV CKT 1 | E | SPS | SPS | SPS-HOBB | SPS-HOBB | 0 | 528413 | TAYLOR 3115.00 | 528470 | E_SANGER 3115.00 | 0 |  | 1 | 22SP | 141 | 141 | 0 | 96.4466 | 96.4466 | 96.4 | [7 empty] | CATEGORYB | SINGLE | MADDOX STATION - MONUMENT SUB 115KV CKT 1 | 0 | 528355 | MADDOX 3115.00 | 528491 | MONUMENT 3115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4025513SP | FROM->TO | EASTOWN7 345.00 (EASTOWN 345) 345/161/13.8KV TRANSFORMER CKT 1 | E | GMO | GMO |  |  | 2 | 541400 | EASTOWN7 345.00 | 541401 | EASTWON5 161.00 | 541402 | EASTOWN1 13.800 | 1 | 13SP | 400 | 440 | 0 | 100.5057 | 100.5057 | 99 | [7 empty] | CATEGORYB | SINGLE | EASTOWN7 345.00 - ST JOE 345KV CKT 1 | 0 | 541199 | ST JOE 3 345.00 | 541400 | EASTOWN7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1795513WP | FROM->TO | EASTOWN7 345.00 (EASTOWN 345) 345/161/13.8KV TRANSFORMER CKT 1 | E | GMO | GMO |  |  | 1 | 541400 | EASTOWN7 345.00 | 541401 | EASTWON5 161.00 | 541402 | EASTOWN1 13.800 | 1 | 13WP | 400 | 440 | 0 | 101.124 | 101.124 | 99.1 | [7 empty] | CATEGORYB | SINGLE | EASTOWN7 345.00 - ST JOE 345KV CKT 1 | 0 | 541199 | ST JOE 3 345.00 | 541400 | EASTOWN7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3965514SP | FROM->TO | EASTOWN7 345.00 (EASTOWN 345) 345/161/13.8KV TRANSFORMER CKT 1 | E | GMO | GMO |  |  | 2 | 541400 | EASTOWN7 345.00 | 541401 | EASTWON5 161.00 | 541402 | EASTOWN1 13.800 | 1 | 17SP | 400 | 440 | 0 |  | 102.226 | 99.5 | [7 empty] | CATEGORYB | SINGLE | EASTOWN7 345.00 - ST JOE 345KV CKT 1 | 0 | 541199 | ST JOE 3 345.00 | 541400 | EASTOWN7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2615514WP | FROM->TO | EASTOWN7 345.00 (EASTOWN 345) 345/161/13.8KV TRANSFORMER CKT 1 | E | GMO | GMO |  |  | 2 | 541400 | EASTOWN7 345.00 | 541401 | EASTWON5 161.00 | 541402 | EASTOWN1 13.800 | 1 | 17WP | 400 | 440 | 0 |  | 103.344 | 99.4 | [7 empty] | CATEGORYB | SINGLE | EASTOWN7 345.00 - ST JOE 345KV CKT 1 | 0 | 541199 | ST JOE 3 345.00 | 541400 | EASTOWN7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T20195517SP | TO->FROM | ECKLES - SIBLEYPL 161.00 161KV CKT 1 | E | GMO | INDN |  | INDN | 0 | 541250 | SIBLEYPL 161.00 | 548808 | ECKLES-161 161.00 | 0 |  | 1 | 17SP | 280 | 308 | 308 | 90.1155 | 90.1155 | 95.5 | [7 empty] | CATEGORYB | NONSINGLE | KCPL-OL166-1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T20225517SP | TO->FROM | ECKLES - SIBLEYPL 161.00 161KV CKT 1 | E | GMO | INDN |  | INDN | 0 | 541250 | SIBLEYPL 161.00 | 548808 | ECKLES-161 161.00 | 0 |  | 1 | 17SP | 280 | 308 | 308 | 90.0536 | 90.0536 | 95.3 | [7 empty] | CATEGORYB | NONSINGLE | KCPL-OL166-2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1265513WP | TO->FROM | EDWARDSVILLE - MUND 115KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 533282 | MUND 3 115.00 | 533238 | EDWARVL3 115.00 | 0 |  | 1 | 13WP | 173 | 206 | 0 | 87.9146 | 87.9146 | 96.2 | [7 empty] | CATEGORYB | SINGLE | 87th STREET - CRAIG 345KV CKT 1 | 0 | 532775 | 87TH 7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1285512WP | FROM->TO | EDWARDSVILLE (EDWRDV4X) 161/115/12.47KV TRANSFORMER CKT 1 | E | WERE | WERE | NEAST | NEAST | 1 | 533238 | EDWARVL3 115.00 | 532912 | EDWRDVL5 161.00 | 532940 | EDWRDVL1 12.470 | 1 | 12WP | 168 | 184.8 | 210 | 90.0841 | 90.0841 | 95.6 | [7 empty] | CATEGORYB | SINGLE | 87th STREET - CRAIG 345KV CKT 1 | 0 | 532775 | 87TH 7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T20335517SP | FROM->TO | EL PASO - FARBER 138KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 | 17SP | 160 | 168 | 0 | 99.7131 | 99.7131 | 99.7 | [7 empty] | CATEGORYB | NONSINGLE | OGE3TERM7 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-16SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1765516SP | FROM->TO | EL PASO - FARBER 138KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 | 17SP | 160 | 168 | 0 |  | 98.2076 | 99.5 | [7 empty] | CATEGORYB | SINGLE | KILDARE4 - WHITE EAGLE 138KV CKT 1 | 0 | 514760 | KILDARE4 138.00 | 514761 | WHEAGLE4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1775514SP | FROM->TO | EL PASO - FARBER 138KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 | 17SP | 160 | 168 | 0 |  | 97.099 | 98 | [7 empty] | CATEGORYB | SINGLE | KILDARE4 - WHITE EAGLE 138KV CKT 1 | 0 | 514760 | KILDARE4 138.00 | 514761 | WHEAGLE4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1835514SP | FROM->TO | EL PASO - FARBER 138KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 | 17SP | 160 | 168 | 0 |  | 96.2121 | 96.5 | [7 empty] | CATEGORYB | SINGLE | MIDLTNT4 138.00 - PECKHAM TAP 138KV CKT 1 | 0 | 514804 | MIDLTNT4 138.00 | 515381 | PECKHMT4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T28825522SP | FROM->TO | EL PASO - FARBER 138KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 | 22SP | 160 | 168 | 0 | 94.6548 | 94.6548 | 95.2 | [7 empty] | CATEGORYB | NONSINGLE | OGE3TERM7 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4825512WP | TO->FROM | EL RENO - ROMAN NOSE 138KV CKT 1 | E | OKGE | OKGE |  |  | 0 | 514823 | ROMNOSE4 138.00 | 514819 | EL-RENO4 138.00 | 0 |  | 1 | 12WP | 171 | 185 | 0 | 96.3 | 96.3265 | 99.5 | [7 empty] | CATEGORYB | SINGLE | WOODWARD DISTRICT EHV (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4825512WP | TO->FROM | EL RENO - ROMAN NOSE 138KV CKT 1 | E | OKGE | OKGE |  |  | 0 | 514823 | ROMNOSE4 138.00 | 514819 | EL-RENO4 138.00 | 0 |  | 1 | 12WP | 171 | 185 | 0 | 96.3265 | 96.3265 | 99.5 | [7 empty] | CATEGORYB | SINGLE | WOODWARD DISTRICT EHV (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T665512WP | TO->FROM | EL RENO - ROMAN NOSE 138KV CKT 1 | E | OKGE | OKGE |  |  | 0 | 514823 | ROMNOSE4 138.00 | 514819 | EL-RENO4 138.00 | 0 |  | 1 | 12WP | 171 | 185 | 0 | 96.3 | 96.3 | 99.4 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WOODWARD DISTRICT EHV 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T665512WP | TO->FROM | EL RENO - ROMAN NOSE 138KV CKT 1 | E | OKGE | OKGE |  |  | 0 | 514823 | ROMNOSE4 138.00 | 514819 | EL-RENO4 138.00 | 0 |  | 1 | 12WP | 171 | 185 | 0 | 96.3 | 96.3 | 99.4 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WOODWARD DISTRICT EHV 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T5475513WP | TO->FROM | EL RENO - ROMAN NOSE 138KV CKT 1 | E | OKGE | OKGE |  |  | 0 | 514823 | ROMNOSE4 138.00 | 514819 | EL-RENO4 138.00 | 0 |  | 1 | 13WP | 171 | 185 | 0 | 94.7147 | 94.7147 | 98 | [7 empty] | CATEGORYB | SINGLE | WOODWARD DISTRICT EHV (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2975514WP | FROM->TO | ELM CREEK - KEARNEY 115KV CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640161 | ELMCRK_7 115.00 | 640250 | KEARNEY7 115.00 | 0 |  | 1 | 17WP | 80 | 80 | 88 |  | 84.1825 | 98.3 | [7 empty] | CATEGORYB | SINGLE | CROOKED CREEK - RIVERDALE 230KV CKT 1 | 0 | 640093 | C.CREEK4 230.00 | 640330 | RIVERDL4 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | INVALID | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T1815012SP | FROM->TO | EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533040 | EVANS N4 138.00 | 533054 | MAIZE 4 138.00 | 0 |  | 1 | 12SP | 382 | 382 | 0 | 96.1646 | 96.1646 | 96.1779 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER NORTH - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533040 | EVANS N4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | INVALID | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3665513SP | FROM->TO | EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533040 | EVANS N4 138.00 | 533054 | MAIZE 4 138.00 | 0 |  | 1 | 13SP | 382 | 382 | 0 | 95.5 | 95.5122 | 98.3275 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER NORTH - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533040 | EVANS N4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3885522SP | FROM->TO | EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533040 | EVANS N4 138.00 | 533054 | MAIZE 4 138.00 | 0 |  | 1 | 22SP | 382 | 382 | 0 | 80.3117 | 80.3117 | 95.1 | [7 empty] | CATEGORYB | SINGLE | BENTON - WICHITA 345KV CKT 1 | 0 | 532791 | BENTON 7 345.00 | 532796 | WICHITA7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T5495522SP | FROM->TO | FAIRPORT - PATTONSBURG 69KV CKT 1 | E | AECI | AECI | NW | NW | 0 | 300249 | 2FAIRPT 69.000 | 300209 | 2PATBRG 69.000 | 0 |  | 1 | 22SP | 36 | 36 | 0 | 92.3027 | 92.3027 | 97.1 | [7 empty] | CATEGORYB | SINGLE | HICKORY CREEK 161/69KV TRANSFORMER CKT 1 | 0 | 300087 | 5HICKCK 161.00 | 300226 | 2HICKRY 69.000 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T29955522SP | FROM->TO | FAIRPORT - PATTONSBURG 69KV CKT 1 | E | AECI | AECI | NW | NW | 0 | 300249 | 2FAIRPT 69.000 | 300209 | 2PATBRG 69.000 | 0 |  | 1 | 22SP | 36 | 36 | 0 | 91.8372 | 91.8372 | 96.9 | [7 empty] | CATEGORYB | GENOUT | GEN300003 1-THOMAS HILL UNIT 3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8585512WP | FROM->TO | FLATRDG3 - HARPER 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 12WP | 100 | 100 | 100 | 91.4821 | 91.4821 | 99.4 | [7 empty] | CATEGORYB | GENOUT | GEN640011 2-GERALD GENTLEMAN STATION UNIT 2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8355512WP | FROM->TO | FLATRDG3 - HARPER 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 12WP | 100 | 100 | 100 | 91.383 | 91.383 | 99.3 | [7 empty] | CATEGORYB | GENOUT | GEN525561 1-TOLK GEN #1 24 KV | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T9185513SP | FROM->TO | FPL SWITCH - MOORELAND 138KV CKT 1 | E | OKGE | WFEC | ENID | AEP-OP | 0 | 515785 | WINDFRM4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 13SP | 268 | 287 | 0 | 95.1 | 95.0724 | 95.5 | [7 empty] | CATEGORYB | SINGLE | WOODWARD DISTRICT EHV (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T5495513WP | FROM->TO | FPL SWITCH - MOORELAND 138KV CKT 1 | E | OKGE | WFEC | ENID | AEP-OP | 0 | 515785 | WINDFRM4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 13WP | 287 | 287 | 0 | 97 | 96.9884 | 97.5 | [7 empty] | CATEGORYB | SINGLE | WOODWARD DISTRICT EHV (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2125514SP | FROM->TO | KIOWA CO 115.00 - GREENSBURG 115KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 560500 | KIOWA CO 115.00 | 539664 | GRNBURG3 115.00 | 0 |  | 1 | 17SP | 120.7 | 129.5 | 0 |  | 73.175 | 98.5 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2565514SP | FROM->TO | KIOWA CO 115.00 - GREENSBURG 115KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 560500 | KIOWA CO 115.00 | 539664 | GRNBURG3 115.00 | 0 |  | 1 | 17SP | 120.7 | 129.5 | 0 |  | 69.9328 | 96.1 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1115514WP | FROM->TO | KIOWA CO 115.00 - GREENSBURG 115KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 560500 | KIOWA CO 115.00 | 539664 | GRNBURG3 115.00 | 0 |  | 1 | 17WP | 120.7 | 129.5 | 0 |  | 74.6313 | 97.7 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1435514WP | FROM->TO | KIOWA CO 115.00 - GREENSBURG 115KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 560500 | KIOWA CO 115.00 | 539664 | GRNBURG3 115.00 | 0 |  | 1 | 17WP | 120.7 | 129.5 | 0 |  | 71.3007 | 95 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2195512WP | TO->FROM | GRAND ISLAND - SWEETWATER 345KV CKT 1 | E | NPPD | NPPD | NPPD_686 | WAPA_1606 | 0 | 640374 | SWEET W3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 | 12WP | 717 | 717 | 789 | 92.4154 | 92.4154 | 99.1 | [7 empty] | CATEGORYB | SINGLE | AXTELL - SWEETWATER 345KV CKT 1 | 0 | 640065 | AXTELL 3 345.00 | 640374 | SWEET W3 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2035513WP | TO->FROM | GRAND ISLAND - SWEETWATER 345KV CKT 1 | E | NPPD | NPPD | NPPD_686 | WAPA_1606 | 0 | 640374 | SWEET W3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 | 13WP | 717 | 717 | 789 | 90.0661 | 90.0661 | 97 | [7 empty] | CATEGORYB | SINGLE | AXTELL - PAULINE 345KV CKT 1 | 0 | 640065 | AXTELL 3 345.00 | 640312 | PAULINE3 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T12315514WP | TO->FROM | GRAND ISLAND - SWEETWATER 345KV CKT 1 | E | NPPD | NPPD | NPPD_686 | WAPA_1606 | 0 | 640374 | SWEET W3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 | 17WP | 717 | 717 | 789 |  | 81.4087 | 97.4 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-14WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2945514WP | TO->FROM | GRAND ISLAND - SWEETWATER 345KV CKT 1 | E | NPPD | NPPD | NPPD_686 | WAPA_1606 | 0 | 640374 | SWEET W3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 | 17WP | 717 | 717 | 789 |  | 84.872 | 96.4 | [7 empty] | CATEGORYB | SINGLE | CROOKED CREEK - NORTH PLATTE 230KV CKT 1 | 0 | 640093 | C.CREEK4 230.00 | 640286 | N.PLATT4 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1505516WP | TO->FROM | GRAND ISLAND - SWEETWATER 345KV CKT 1 | E | NPPD | NPPD | NPPD_686 | WAPA_1606 | 0 | 640374 | SWEET W3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 | 17WP | 717 | 717 | 789 |  | 85.2895 | 95.5 | [7 empty] | CATEGORYB | SINGLE | AXTELL - PAULINE 345KV CKT 1 | 0 | 640065 | AXTELL 3 345.00 | 640312 | PAULINE3 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1935514WP | FROM->TO | GREENLEAF - KNOB HILL 115KV CKT 1 | E | SUNC | WERE | GREAT PL | NCENTRAL | 0 | 539665 | GRNLEAF3 115.00 | 533332 | KNOB HL3 115.00 | 0 |  | 1 | 17WP | 100 | 100 | 100 |  | 93.8407 | 98.8 | [7 empty] | CATEGORYB | SINGLE | ELM CREEK - NORTHWEST MANHATTAN 230KV CKT 1 | 0 | 532865 | NWMANHT6 230.00 | 539639 | ELMCREK6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2115514SP | FROM->TO | GREENSBURG - SUN CITY 115KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539664 | GRNBURG3 115.00 | 539697 | SUNCITY3 115.00 | 0 |  | 1 | 17SP | 120.7 | 129.5 | 0 |  | 69.7597 | 95.1 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1105514WP | FROM->TO | GREENSBURG - SUN CITY 115KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539664 | GRNBURG3 115.00 | 539697 | SUNCITY3 115.00 | 0 |  | 1 | 17WP | 120.7 | 129.5 | 0 |  | 73.7253 | 96.9 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2515513WP | FROM->TO | GRIMES 345/138KV TRANSFORMER CKT 1 | E | EES | EES |  | GSTNAV | 0 | 334028 | 7GRIMES 345.00 | 334026 | 4GRIMES 138.00 | 0 |  | 1 | 13WP | 525 | 525 | 0 | 94.9117 | 94.9117 | 97.6 | [7 empty] | CATEGORYB | SINGLE | GRIMES 345/138KV TRANSFORMER CKT 2 | 0 | 334026 | 4GRIMES 138.00 | 334028 | 7GRIMES 345.00 | 0 |  | 2 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2505513WP | FROM->TO | GRIMES 345/138KV TRANSFORMER CKT 2 | E | EES | EES |  | GSTNAV | 0 | 334028 | 7GRIMES 345.00 | 334026 | 4GRIMES 138.00 | 0 |  | 2 | 13WP | 525 | 525 | 0 | 94.9117 | 94.9117 | 97.6 | [7 empty] | CATEGORYB | SINGLE | GRIMES 345/138KV TRANSFORMER CKT 1 | 0 | 334026 | 4GRIMES 138.00 | 334028 | 7GRIMES 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1235512WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 12WP | 95.6 | 95.6 | 0 | 89.697 | 89.697 | 98.6 | [7 empty] | CATEGORYB | SINGLE | RENO COUNTY - WICHITA 345KV CKT 1 | 0 | 532771 | RENO 7 345.00 | 532796 | WICHITA7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1805512WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 12WP | 95.6 | 95.6 | 0 | 90.8105 | 90.8105 | 98.5 | [7 empty] | CATEGORYB | SINGLE | NINNESC3 115.00 - ST JOHN 115KV CKT 1 | 0 | 539648 | NINNESC3 115.00 | 539696 | ST-JOHN3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1455512WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 12WP | 95.6 | 95.6 | 0 | 88.5691 | 88.5691 | 98.4 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - MULLERGREN 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T14675513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 85.8996 | 85.8996 | 97.7 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3905513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 87.4618 | 87.4618 | 96.8 | [7 empty] | CATEGORYB | SINGLE | NINNESC3 115.00 - ST JOHN 115KV CKT 1 | 0 | 539648 | NINNESC3 115.00 | 539696 | ST-JOHN3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1715513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 88.597 | 88.597 | 97.5 | [7 empty] | CATEGORYB | SINGLE | JUDSON LARGE - NORTH JUDSON LARGE SUB 115KV CKT 1 | 0 | 539671 | FTDODGE3 115.00 | 539771 | NFTDODG3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T9695513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 87.6595 | 87.6595 | 97.1 | [7 empty] | CATEGORYB | GENOUT | GEN560502 1-KIOWA CO 0.6000 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T21475514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 74.5053 | 99.6 | [7 empty] | CATEGORYB | GENOUT | GEN560209 1-GRAY CO 0.5750 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T21455514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 79.9342 | 99.2 | [7 empty] | CATEGORYB | GENOUT | GEN560173 1-SCOTT CO 0.5750 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2865517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 75.6874 | 75.6874 | 99.2 | [7 empty] | CATEGORYB | SINGLE | CENTENNIAL - COWSKIN 138KV CKT 1 | 0 | 533034 | CENTENN4 138.00 | 533038 | COWSKIN4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T21515514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 73.911 | 99 | [7 empty] | CATEGORYB | GENOUT | GEN560353 1-HASKELL CO 0.6900 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T22365517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 75.6371 | 75.6371 | 98.9 | [7 empty] | CATEGORYB | GENOUT | GEN532722 1-EVANS ENERGY CENTER UNIT 2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2715517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 71.6177 | 71.6177 | 98.7 | [7 empty] | CATEGORYB | SINGLE | BENTON - WICHITA 345KV CKT 1 | 0 | 532791 | BENTON 7 345.00 | 532796 | WICHITA7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2725516SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 83.1654 | 97.7 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T15215517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 | 72.5649 | 72.5649 | 95.8 | [7 empty] | CATEGORYB | SINGLE | HARPER (HARPER 4) 138/34.5/8.66KV TRANSFORMER CKT 1 | 1 | 539668 | HARPER 4 138.00 | 539713 | HARPER 1 34.500 | 539913 | HARPER-T 8.6600 | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16SP | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2765516SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 80.7656 | 95.3 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2605516SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 75.6953 | 95.1 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T75517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 76.2323 | 76.2323 | 99.6 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-16WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T7015516WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 |  | 83.4289 | 98.3 | [7 empty] | CATEGORYB | SINGLE | WICHITA (WICHT11X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532796 | WICHITA7 345.00 | 533040 | EVANS N4 138.00 | 532829 | WICH11 1 13.800 | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10265516WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 |  | 83.4866 | 98.2 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 | CONT-LaCygne West Gardner 345kv | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1455517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 73.1246 | 73.1246 | 96.4 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1345517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 79.9378 | 79.9378 | 96.3 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 345/138KV TRANSFORMER CKT 1 | 0 | 539638 | FLATRDG3 138.00 | 539801 | THISTLE 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16WP | ISLAND-LOAD |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T7145516WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 |  | 81.5479 | 96.1 | [7 empty] | CATEGORYB | SINGLE | HARPER (HARPER 4) 138/34.5/8.66KV TRANSFORMER CKT 1 | 1 | 539668 | HARPER 4 138.00 | 539713 | HARPER 1 34.500 | 539913 | HARPER-T 8.6600 | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1055517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 72.485 | 72.485 | 96 | [7 empty] | CATEGORYB | SINGLE | GRAY CO 345.00 - SPEARVILLE 345KV CKT 1 | 0 | 531469 | SPERVIL7 345.00 | 560005 | GRAY CO 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T12545517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 | 72.5375 | 72.5375 | 95.8 | [7 empty] | CATEGORYB | GENOUT | GEN560353 1-HASKELL CO 0.6900 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-16WP | CONT-0301 - Rose Hill - Wolf Creek 345kV |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1145516WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 |  | 80.7307 | 95.2 | [7 empty] | CATEGORYB | SINGLE | ROSE HILL - WOLF CREEK 345KV CKT 1 | 0 | 532794 | ROSEHIL7 345.00 | 532797 | WOLFCRK7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T31455522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 74.719 | 74.719 | 98.9 | [7 empty] | CATEGORYB | GENOUT | GEN532751 1-WOLF CREEK GENERATING STATION UNIT 1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T29065522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 73.8375 | 73.8375 | 98.3 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4035522SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 22SP | 95.6 | 95.6 | 0 | 72.3213 | 72.3213 | 96.9 | [7 empty] | CATEGORYB | SINGLE | CENTENNIAL - COWSKIN 138KV CKT 1 | 0 | 533034 | CENTENN4 138.00 | 533038 | COWSKIN4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3755516SP | FROM->TO | HARRISONVILLE 161/69KV TRANSFORMER CKT 1 | E | GMO | AECI |  | KAMO | 0 | 541239 | HSNVL 5 161.00 | 300709 | 2SHARSNV 69.000 | 0 |  | 1 | 17SP | 56 | 56 | 0 |  | 95.2004 | 99.7 | [7 empty] | CATEGORYB | SINGLE | 5BUTLER 161/69KV TRANSFORMER CKT 1 | 0 | 300689 | 2BUTLER 69.000 | 301342 | 5BUTLER 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4875514SP | FROM->TO | HARRISONVILLE 161/69KV TRANSFORMER CKT 1 | E | GMO | AECI |  | KAMO | 0 | 541239 | HSNVL 5 161.00 | 300709 | 2SHARSNV 69.000 | 0 |  | 1 | 17SP | 56 | 56 | 0 |  | 94.8978 | 99.3 | [7 empty] | CATEGORYB | SINGLE | 5BUTLER 161/69KV TRANSFORMER CKT 1 | 0 | 300689 | 2BUTLER 69.000 | 301342 | 5BUTLER 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T23355522SP | FROM->TO | HARRISONVILLE 161/69KV TRANSFORMER CKT 1 | E | GMO | AECI |  | KAMO | 0 | 541239 | HSNVL 5 161.00 | 300709 | 2SHARSNV 69.000 | 0 |  | 1 | 22SP | 56 | 56 | 0 | 84.0507 | 84.0507 | 98.1 | [7 empty] | CATEGORYB | SINGLE | 5LEVASY 161.00 - ECKLES 161KV CKT 1 | 0 | 548808 | ECKLES-161 161.00 | 300320 | 5LEVASY 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T28665522SP | FROM->TO | HARRISONVILLE 161/69KV TRANSFORMER CKT 1 | E | GMO | AECI |  | KAMO | 0 | 541239 | HSNVL 5 161.00 | 300709 | 2SHARSNV 69.000 | 0 |  | 1 | 22SP | 56 | 56 | 0 | 83.4477 | 83.4477 | 97.4 | [7 empty] | CATEGORYB | NONSINGLE | SPP-INDN-29 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3185513SP | TO->FROM | HAYS PLANT - SOUTH HAYS 115KV CKT 1 | E | MIDW | MIDW | REG E-IL | REG E-IL | 0 | 530553 | S HAYS 3 115.00 | 530562 | HAYS 3 115.00 | 0 |  | 1 | 13SP | 80 | 99 | 0 | 84.9693 | 84.9693 | 95.3 | [7 empty] | CATEGORYB | SINGLE | KNOLL 230 - POSTROCK6 230.00 230KV CKT 1 | 0 | 530558 | KNOLL 6 230.00 | 530584 | POSTROCK6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T9015514WP | FROM->TO | HEIZER - MULLERGREN 115KV CKT 1 | E | MIDW | SUNC | REG E-IL | GREAT PL | 0 | 530601 | HEIZER 3 115.00 | 539678 | GRTBEND3 115.00 | 0 |  | 1 | 17WP | 120 | 120 | 0 |  | 76.8955 | 95.5 | [7 empty] | CATEGORYB | SINGLE | MULLERGREN (MULGREN6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539678 | GRTBEND3 115.00 | 539679 | MULGREN6 230.00 | 539920 | GRTBNDTT 13.800 | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T1435013SP | FROM->TO | HOBBS INTERCHANGE (ME C0482951) 230/115/13.2KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-HOBB | SPS-HOBB | 2 | 527894 | HOBBS_INT 6230.00 | 527891 | HOBBS_INT 3115.00 | 527890 | HOBBS_TR1 113.200 | 1 | 13SP | 150 | 150 | 0 | 95.3286 | 95.3286 | 96 | [7 empty] | CATEGORYB | SINGLE | HOBBS INTERCHANGE - LEA COUNTY INTERCHANGE 230KV CKT 1 | 0 | 527849 | LEA_CNTY 6230.00 | 527894 | HOBBS_INT 6230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T1435013SP | FROM->TO | HOBBS INTERCHANGE (ME C0482951) 230/115/13.2KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-HOBB | SPS-HOBB | 2 | 527894 | HOBBS_INT 6230.00 | 527891 | HOBBS_INT 3115.00 | 527890 | HOBBS_TR1 113.200 | 1 | 13SP | 150 | 150 | 0 | 95.3 | 95.3286 | 96 | [7 empty] | CATEGORYB | SINGLE | HOBBS INTERCHANGE - LEA COUNTY INTERCHANGE 230KV CKT 1 | 0 | 527849 | LEA_CNTY 6230.00 | 527894 | HOBBS_INT 6230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2775517SP | TO->FROM | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 | 17SP | 1076 | 1076 | 0 | 93.5055 | 93.5055 | 99.4 | [7 empty] | CATEGORYB | SINGLE | AUBURN ROAD - JEFFREY ENERGY CENTER 230KV CKT 1 | 0 | 532851 | AUBURN 6 230.00 | 532852 | JEC 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2505516SP | TO->FROM | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 | 17SP | 1076 | 1076 | 0 |  | 95.0907 | 98.9 | [7 empty] | CATEGORYB | SINGLE | JEFFREY ENERGY CENTER - MORRIS COUNTY 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532770 | MORRIS 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2635516SP | TO->FROM | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 | 17SP | 1076 | 1076 | 0 |  | 93.7387 | 97.2 | [7 empty] | CATEGORYB | SINGLE | AUBURN ROAD - JEFFREY ENERGY CENTER 230KV CKT 1 | 0 | 532851 | AUBURN 6 230.00 | 532852 | JEC 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3005514SP | TO->FROM | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 | 17SP | 1076 | 1076 | 0 |  | 91.5773 | 95.6 | [7 empty] | CATEGORYB | SINGLE | JEFFREY ENERGY CENTER - MORRIS COUNTY 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532770 | MORRIS 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3795522SP | TO->FROM | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 | 22SP | 1076 | 1076 | 0 | 92.9407 | 92.9407 | 98.6 | [7 empty] | CATEGORYB | SINGLE | JEFFREY ENERGY CENTER - MORRIS COUNTY 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532770 | MORRIS 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3955522SP | TO->FROM | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 | 22SP | 1076 | 1076 | 0 | 92.5889 | 92.5889 | 98.5 | [7 empty] | CATEGORYB | SINGLE | AUBURN ROAD - JEFFREY ENERGY CENTER 230KV CKT 1 | 0 | 532851 | AUBURN 6 230.00 | 532852 | JEC 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T23595522SP | FROM->TO | HUBEN 345/161KV TRANSFORMER CKT 1 | E | AECI | AECI | GSTBMM-C | GSTBMM-C | 0 | 300042 | 7HUBEN 345.00 | 300088 | 5HUBEN 161.00 | 0 |  | 1 | 22SP | 392 | 392 | 0 | 96.094 | 96.094 | 95.9 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE - MORGAN 345KV CKT 1 | 0 | 549984 | BROOKLINE 7345.00 | 300045 | 7MORGAN 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | CONT-1202 - Jarbalo - Stranger Creek 115kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T5085512SP | FROM->TO | IATAN - STRANGER CREEK 345KV CKT 1 | E | KCPL | WERE | KACP | NEAST | 0 | 542982 | IATAN 7 345.00 | 532772 | STRANGR7 345.00 | 0 |  | 1 | 12SP | 1099 | 1195 | 0 | 95.6 | 95.6002 | 96.3 | [7 empty] | CATEGORYB | SINGLE | IATAN - ST JOE 345KV CKT 1 | 0 | 541199 | ST JOE 3 345.00 | 542982 | IATAN 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | CONT-1202 - Jarbalo - Stranger Creek 115kV | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1995512WP | FROM->TO | IATAN - STRANGER CREEK 345KV CKT 1 | E | KCPL | WERE | KACP | NEAST | 0 | 542982 | IATAN 7 345.00 | 532772 | STRANGR7 345.00 | 0 |  | 1 | 12WP | 1195 | 1195 | 0 | 95.3271 | 95.3271 | 95.9 | [7 empty] | CATEGORYB | SINGLE | IATAN - ST JOE 345KV CKT 1 | 0 | 541199 | ST JOE 3 345.00 | 542982 | IATAN 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4065513SP | FROM->TO | IATAN - STRANGER CREEK 345KV CKT 1 | E | KCPL | WERE | KACP | NEAST | 0 | 542982 | IATAN 7 345.00 | 532772 | STRANGR7 345.00 | 0 |  | 1 | 13SP | 1099 | 1195 | 0 | 96.1 | 96.0957 | 96.6 | [7 empty] | CATEGORYB | SINGLE | EASTOWN7 345.00 - IATAN 345KV CKT 1 | 0 | 541400 | EASTOWN7 345.00 | 542982 | IATAN 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1805513WP | FROM->TO | IATAN - STRANGER CREEK 345KV CKT 1 | E | KCPL | WERE | KACP | NEAST | 0 | 542982 | IATAN 7 345.00 | 532772 | STRANGR7 345.00 | 0 |  | 1 | 13WP | 1195 | 1195 | 0 | 96.1814 | 96.1814 | 96.6 | [7 empty] | CATEGORYB | SINGLE | EASTOWN7 345.00 - IATAN 345KV CKT 1 | 0 | 541400 | EASTOWN7 345.00 | 542982 | IATAN 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 0 | 2011AG2AFS91T2405014SP | FROM->TO | IATAN - STRANGER CREEK 345KV CKT 1 | E | KCPL | WERE | KACP | NEAST | 0 | 542982 | IATAN 7 345.00 | 532772 | STRANGR7 345.00 | 0 |  | 1 | 17SP | 1099 | 1195 | 0 |  | 98.254 | 98.8 | [7 empty] | CATEGORYB | SINGLE | EASTOWN7 345.00 - IATAN 345KV CKT 1 | 0 | 541400 | EASTOWN7 345.00 | 542982 | IATAN 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2655514WP | FROM->TO | IATAN - STRANGER CREEK 345KV CKT 1 | E | KCPL | WERE | KACP | NEAST | 0 | 542982 | IATAN 7 345.00 | 532772 | STRANGR7 345.00 | 0 |  | 1 | 17WP | 1195 | 1195 | 0 |  | 96.3247 | 97 | [7 empty] | CATEGORYB | SINGLE | EASTOWN7 345.00 - IATAN 345KV CKT 1 | 0 | 541400 | EASTOWN7 345.00 | 542982 | IATAN 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T27265022SP | FROM->TO | INDEPENDENCE - LS POWER OSCEOLA UNIT 500KV CKT 1 | E | EES | EES | EAINTH | EAINTH | 0 | 338145 | 8ISES 500.00 | 338144 | 8ISXF 500.00 | 0 |  | 1 | 22SP | 850 | 850 | 0 | 97.9295 | 97.9295 | 96.2 | [7 empty] | CATEGORYB | GENOUT | GEN338143 1-INDEPENDENCE UNIT #1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4745512WP | TO->FROM | LAKE CREEK - LONEWOLF 69KV CKT 1 | E | WFEC | WFEC | AEP-CS | AEP-CS | 0 | 520982 | LONEWLF2 69.000 | 520978 | LKCREEK2 69.000 | 0 |  | 1 | 12WP | 48 | 48 | 48 | 68.7658 | 68.7658 | 96.4 | [7 empty] | CATEGORYB | SINGLE | ELK CITY (ELKCTY-4) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 511458 | ELKCTY-4 138.00 | 511459 | ELKCTY-2 69.000 | 511493 | ELKC4-1 13.800 | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T5375513WP | TO->FROM | LAKE CREEK - LONEWOLF 69KV CKT 1 | E | WFEC | WFEC | AEP-CS | AEP-CS | 0 | 520982 | LONEWLF2 69.000 | 520978 | LKCREEK2 69.000 | 0 |  | 1 | 13WP | 48 | 48 | 48 | 67.7426 | 67.7426 | 95.8 | [7 empty] | CATEGORYB | SINGLE | ELK CITY (ELKCTY-4) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 511458 | ELKCTY-4 138.00 | 511459 | ELKCTY-2 69.000 | 511493 | ELKC4-1 13.800 | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T7145517WP | TO->FROM | LAKE CREEK - LONEWOLF 69KV CKT 1 | E | WFEC | WFEC | AEP-CS | AEP-CS | 0 | 520982 | LONEWLF2 69.000 | 520978 | LKCREEK2 69.000 | 0 |  | 1 | 17WP | 48 | 48 | 48 | 67.2498 | 67.2498 | 96.8 | [7 empty] | CATEGORYB | SINGLE | ELK CITY (ELKCTY-4) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 511458 | ELKCTY-4 138.00 | 511459 | ELKCTY-2 69.000 | 511493 | ELKC4-1 13.800 | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T6675516WP | TO->FROM | LAKE CREEK - LONEWOLF 69KV CKT 1 | E | WFEC | WFEC | AEP-CS | AEP-CS | 0 | 520982 | LONEWLF2 69.000 | 520978 | LKCREEK2 69.000 | 0 |  | 1 | 17WP | 48 | 48 | 48 |  | 67.2608 | 96.5 | [7 empty] | CATEGORYB | SINGLE | ELK CITY (ELKCTY-4) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 511458 | ELKCTY-4 138.00 | 511459 | ELKCTY-2 69.000 | 511493 | ELKC4-1 13.800 | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8285514WP | TO->FROM | LAKE CREEK - LONEWOLF 69KV CKT 1 | E | WFEC | WFEC | AEP-CS | AEP-CS | 0 | 520982 | LONEWLF2 69.000 | 520978 | LKCREEK2 69.000 | 0 |  | 1 | 17WP | 48 | 48 | 48 |  | 67.3194 | 96.3 | [7 empty] | CATEGORYB | SINGLE | ELK CITY (ELKCTY-4) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 511458 | ELKCTY-4 138.00 | 511459 | ELKCTY-2 69.000 | 511493 | ELKC4-1 13.800 | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T5605512SP | FROM->TO | LAMAR 161/69KV TRANSFORMER CKT 1 | E | AECI | AECI | KAMO | KAMO | 0 | 300794 | 5LAMAR 161.00 | 300651 | 2LAMR 69.000 | 0 |  | 1 | 12SP | 84 | 84 | 0 | 97.3 | 97.341 | 97.4 | [7 empty] | CATEGORYB | SINGLE | 7JASPER 345.00 - MORGAN 345KV CKT 1 | 0 | 300045 | 7MORGAN 345.00 | 300949 | 7JASPER 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3505516SP | FROM->TO | LAMAR 161/69KV TRANSFORMER CKT 1 | E | AECI | AECI | KAMO | KAMO | 0 | 300794 | 5LAMAR 161.00 | 300651 | 2LAMR 69.000 | 0 |  | 1 | 17SP | 84 | 84 | 0 |  | 99.14 | 98.4 | [7 empty] | CATEGORYB | SINGLE | CLARK 161/69KV TRANSFORMER CKT 1 | 0 | 300070 | 5CLARK 161.00 | 300802 | 2CLARK 69.000 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4615514SP | FROM->TO | LAMAR 161/69KV TRANSFORMER CKT 1 | E | AECI | AECI | KAMO | KAMO | 0 | 300794 | 5LAMAR 161.00 | 300651 | 2LAMR 69.000 | 0 |  | 1 | 17SP | 84 | 84 | 0 |  | 98.9149 | 98.2 | [7 empty] | CATEGORYB | SINGLE | CLARK 161/69KV TRANSFORMER CKT 1 | 0 | 300070 | 5CLARK 161.00 | 300802 | 2CLARK 69.000 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3955517SP | FROM->TO | LAMAR 161/69KV TRANSFORMER CKT 1 | E | AECI | AECI | KAMO | KAMO | 0 | 300794 | 5LAMAR 161.00 | 300651 | 2LAMR 69.000 | 0 |  | 1 | 17SP | 84 | 84 | 0 | 99.2 | 99.2104 | 98.2 | [7 empty] | CATEGORYB | SINGLE | CLARK 161/69KV TRANSFORMER CKT 1 | 0 | 300070 | 5CLARK 161.00 | 300802 | 2CLARK 69.000 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T14765517SP | FROM->TO | LAMAR 161/69KV TRANSFORMER CKT 1 | E | AECI | AECI | KAMO | KAMO | 0 | 300794 | 5LAMAR 161.00 | 300651 | 2LAMR 69.000 | 0 |  | 1 | 17SP | 84 | 84 | 0 | 96.8333 | 96.8333 | 97.9 | [7 empty] | CATEGORYB | SINGLE | NEOSHO (NEOSHO2X) 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 532937 | NEOSHO 5 161.00 | 532825 | N345 2 1 13.800 | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T13465516SP | FROM->TO | LAMAR 161/69KV TRANSFORMER CKT 1 | E | AECI | AECI | KAMO | KAMO | 0 | 300794 | 5LAMAR 161.00 | 300651 | 2LAMR 69.000 | 0 |  | 1 | 17SP | 84 | 84 | 0 |  | 96.8366 | 97.8 | [7 empty] | CATEGORYB | SINGLE | NEOSHO (NEOSHO2X) 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 532937 | NEOSHO 5 161.00 | 532825 | N345 2 1 13.800 | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T14325514SP | FROM->TO | LAMAR 161/69KV TRANSFORMER CKT 1 | E | AECI | AECI | KAMO | KAMO | 0 | 300794 | 5LAMAR 161.00 | 300651 | 2LAMR 69.000 | 0 |  | 1 | 17SP | 84 | 84 | 0 |  | 96.5514 | 97.5 | [7 empty] | CATEGORYB | SINGLE | NEOSHO (NEOSHO2X) 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 532793 | NEOSHO 7 345.00 | 532937 | NEOSHO 5 161.00 | 532825 | N345 2 1 13.800 | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T14505516SP | FROM->TO | LAMAR 161/69KV TRANSFORMER CKT 1 | E | AECI | AECI | KAMO | KAMO | 0 | 300794 | 5LAMAR 161.00 | 300651 | 2LAMR 69.000 | 0 |  | 1 | 17SP | 84 | 84 | 0 |  | 95.7872 | 95.9 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE - MORGAN 345KV CKT 1 | 0 | 549984 | BROOKLINE 7345.00 | 300045 | 7MORGAN 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T15535514SP | FROM->TO | LAMAR 161/69KV TRANSFORMER CKT 1 | E | AECI | AECI | KAMO | KAMO | 0 | 300794 | 5LAMAR 161.00 | 300651 | 2LAMR 69.000 | 0 |  | 1 | 17SP | 84 | 84 | 0 |  | 95.6158 | 95.8 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE - MORGAN 345KV CKT 1 | 0 | 549984 | BROOKLINE 7345.00 | 300045 | 7MORGAN 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T31645522SP | FROM->TO | LAMAR 161/69KV TRANSFORMER CKT 1 | E | AECI | AECI | KAMO | KAMO | 0 | 300794 | 5LAMAR 161.00 | 300651 | 2LAMR 69.000 | 0 |  | 1 | 22SP | 84 | 84 | 0 | 99.6 | 99.6011 | 98.7 | [7 empty] | CATEGORYB | GENOUT | GEN547658 1-STATE LINE COMBINED CYCLE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 | INVALID | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2325522SP | FROM->TO | LAMAR 161/69KV TRANSFORMER CKT 1 | E | AECI | AECI | KAMO | KAMO | 0 | 300794 | 5LAMAR 161.00 | 300651 | 2LAMR 69.000 | 0 |  | 1 | 22SP | 84 | 84 | 0 | 98.1017 | 98.1017 | 97.1094 | [7 empty] | CATEGORYB | SINGLE | GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 | 0 | 512650 | GRDA1 7 345.00 | 512750 | TONECE7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4405522SP | FROM->TO | LEEDS - WINCHESTER JUNCTION NORTH 161KV CKT 1 | E | KCPL | KCPL | METRO | METRO | 0 | 542997 | LEEDS 5 161.00 | 543009 | WINJT N5 161.00 | 0 |  | 1 | 22SP | 224 | 224 | 0 | 96.7598 | 96.7598 | 97.3 | [7 empty] | CATEGORYB | SINGLE | BLUE SPRINGS EAST - BLUE SPRINGS WEST 161KV CKT 1 | 0 | 541205 | BLSPE 5 161.00 | 541237 | BLSPW 5 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4525522SP | FROM->TO | LIBERTY SOUTH 161/69KV TRANSFORMER CKT 1 | E | GMO | KCPL |  | 69KV | 0 | 541248 | LBRTYST5 161.00 | 543095 | LIBRTYS2 69.000 | 0 |  | 1 | 22SP | 60 | 66 | 66 | 98.6162 | 98.6162 | 96.8 | [7 empty] | CATEGORYB | SINGLE | ROANRIDGE - STALEY ROAD 69KV CKT 1 | 0 | 541260 | RNRDGE 2 69.000 | 541261 | STALEY 2 69.000 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4755522SP | FROM->TO | LIBERTY SOUTH 161/69KV TRANSFORMER CKT 1 | E | GMO | KCPL |  | 69KV | 0 | 541248 | LBRTYST5 161.00 | 543095 | LIBRTYS2 69.000 | 0 |  | 1 | 22SP | 60 | 66 | 66 | 94.2296 | 94.2296 | 95.6 | [7 empty] | CATEGORYB | SINGLE | COURTNEY - SUB H 69KV CKT 1 | 0 | 543085 | COURTNY2 69.000 | 548802 | SUB H 69.000 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T5685522SP | FROM->TO | LOCUST CREEK 161/69KV TRANSFORMER CKT 1 | E | AECI | AECI | NW | NW | 0 | 300094 | 5LOCUST 161.00 | 300278 | 2LOCUST 69.000 | 0 |  | 1 | 22SP | 56 | 56 | 0 | 95.8791 | 95.8791 | 98.8 | [7 empty] | CATEGORYB | SINGLE | GOSHEN - MERCER 69KV CKT 1 | 0 | 300224 | 2GOSHEN 69.000 | 300230 | 2MERCER 69.000 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T17905522SP | FROM->TO | LOCUST CREEK 161/69KV TRANSFORMER CKT 1 | E | AECI | AECI | NW | NW | 0 | 300094 | 5LOCUST 161.00 | 300278 | 2LOCUST 69.000 | 0 |  | 1 | 22SP | 56 | 56 | 0 | 97.4 | 97.393 | 98.4 | [7 empty] | CATEGORYB | SINGLE | HART - NEW CAMBRIA 69KV CKT 1 | 0 | 300392 | 2HART 69.000 | 300406 | 2NCAMBR 69.000 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T5675522SP | FROM->TO | LOCUST CREEK 161/69KV TRANSFORMER CKT 1 | E | AECI | AECI | NW | NW | 0 | 300094 | 5LOCUST 161.00 | 300278 | 2LOCUST 69.000 | 0 |  | 1 | 22SP | 56 | 56 | 0 | 94.6156 | 94.6156 | 97.1 | [7 empty] | CATEGORYB | SINGLE | BETHANY - RIDGEWAY 69KV CKT 1 | 0 | 300220 | 2BETHNY 69.000 | 300236 | 2RIDGWY 69.000 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4055514SP | FROM->TO | LONGVIEW - WESTERN ELECTRIC 161KV CKT 1 | E | GMO | GMO |  |  | 0 | 541224 | LNGVW 5 161.00 | 541222 | WSTELEC5 161.00 | 0 |  | 1 | 17SP | 228 | 259 | 224 |  | 89.9431 | 95.4 | [7 empty] | CATEGORYB | SINGLE | GREENWOOD ENERGY CENTER - LEES SUMMIT EAST 161KV CKT 1 | 0 | 541218 | GRNWD 5 161.00 | 541233 | LEESUM 5 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4475522SP | FROM->TO | LONGVIEW - WESTERN ELECTRIC 161KV CKT 1 | E | GMO | GMO |  |  | 0 | 541224 | LNGVW 5 161.00 | 541222 | WSTELEC5 161.00 | 0 |  | 1 | 22SP | 228 | 259 | 224 | 90.3192 | 90.3192 | 96.8 | [7 empty] | CATEGORYB | SINGLE | GREENWOOD ENERGY CENTER - LEES SUMMIT EAST 161KV CKT 1 | 0 | 541218 | GRNWD 5 161.00 | 541233 | LEESUM 5 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T14545513SP | TO->FROM | MARYVILLE - MIDWAY 161KV CKT 1 | E | GMO | GMO |  |  | 0 | 541369 | MIDWAY_5 161.00 | 541251 | MARYVLE5 161.00 | 0 |  | 1 | 13SP | 152 | 171 | 171 | 96.1 | 96.1304 | 97.1 | [7 empty] | CATEGORYB | NONSINGLE | LN-FAIRPORT | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4545514SP | TO->FROM | MARYVILLE - MIDWAY 161KV CKT 1 | E | GMO | GMO |  |  | 0 | 541369 | MIDWAY_5 161.00 | 541251 | MARYVLE5 161.00 | 0 |  | 1 | 17SP | 152 | 171 | 171 |  | 97.6281 | 99.2 | [7 empty] | CATEGORYB | SINGLE | FAIRPORT 345/161KV TRANSFORMER CKT 3 | 0 | 300039 | 7FAIRPT 345.00 | 300076 | 5FAIRPT 161.00 | 0 |  | 3 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T20275517SP | TO->FROM | MARYVILLE - MIDWAY 161KV CKT 1 | E | GMO | GMO |  |  | 0 | 541369 | MIDWAY_5 161.00 | 541251 | MARYVLE5 161.00 | 0 |  | 1 | 17SP | 152 | 171 | 171 | 95 | 95.017 | 98.9 | [7 empty] | CATEGORYB | NONSINGLE | LN-FAIRPORT | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-16SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3425516SP | TO->FROM | MARYVILLE - MIDWAY 161KV CKT 1 | E | GMO | GMO |  |  | 0 | 541369 | MIDWAY_5 161.00 | 541251 | MARYVLE5 161.00 | 0 |  | 1 | 17SP | 152 | 171 | 171 |  | 95.3885 | 97.5 | [7 empty] | CATEGORYB | SINGLE | FAIRPORT 345/161KV TRANSFORMER CKT 3 | 0 | 300039 | 7FAIRPT 345.00 | 300076 | 5FAIRPT 161.00 | 0 |  | 3 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP |  |  |  | FNSL | FDNS-Blown up | 5 | 0 | 2011AG2AFS92T45014WP | FROM->TO | MONETTE JUNCTION - PARAGOULD 161 161KV CKT 1 | E | EES | EES | EAINTH | EAINTH | 0 | 338186 | 5MONETE 161.00 | 338204 | 5PARAG 161.00 | 0 |  | 1 | 17WP | 148 | 148 | 0 |  | 92.0112 | 95 | [7 empty] | CATEGORYB | SINGLE | 8SHELBY TN 500.00 - PLUM POINT 500KV CKT 1 | 0 | 338188 | 8SANSOUC 500.00 | 360021 | 8SHELBY TN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T845522SP | FROM->TO | MONTROCLINTN | E |  |  |  |  | MONTROCLINTN | 0 |  | 0 |  | 0 |  |  | 22SP | 446 | 446 | 446 | 86.3128 | 86.3128 | 95.2 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T3005022SP | FROM->TO | MONUMENT SUB - WEST HOBBS SWITCHING STATION 115KV CKT 1 | E | SPS | SPS | SPS-HOBB | SPS-HOBB | 0 | 528491 | MONUMENT 3115.00 | 528498 | W_HOBBS 3115.00 | 0 |  | 1 | 22SP | 139 | 141 | 0 | 97.2008 | 97.2008 | 97.1 | [7 empty] | CATEGORYB | SINGLE | EAST SANGER SUB - TAYLOR SWITCHING STATION 115KV CKT 1 | 0 | 528413 | TAYLOR 3115.00 | 528470 | E_SANGER 3115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19565514SP | TO->FROM | MULLERGREN - SPEARVILLE 230KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539695 | SPEARVL6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | 17SP | 330.3 | 355.3 | 0 |  | 66.2757 | 96.6 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3235513SP | FROM->TO | MULLERGREN 115/13.8KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539677 | GRTBEND1 13.800 | 539678 | GRTBEND3 115.00 | 0 |  | 1 | 13SP | 106 | 106 | 106 | 90.0257 | 90.0257 | 95.1 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1275512WP | TO->FROM | MUND - PENTAGON 115KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 533261 | PENTAGN3 115.00 | 533282 | MUND 3 115.00 | 0 |  | 1 | 12WP | 173 | 206 | 0 | 92.5442 | 92.5442 | 97.2 | [7 empty] | CATEGORYB | SINGLE | 87th STREET - CRAIG 345KV CKT 1 | 0 | 532775 | 87TH 7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3505513SP | TO->FROM | MUND - PENTAGON 115KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 533261 | PENTAGN3 115.00 | 533282 | MUND 3 115.00 | 0 |  | 1 | 13SP | 173 | 206 | 0 | 93.8883 | 93.8883 | 98.4 | [7 empty] | CATEGORYB | SINGLE | 87th STREET - CRAIG 345KV CKT 1 | 0 | 532775 | 87TH 7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1845514WP | TO->FROM | MUND - PENTAGON 115KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 533261 | PENTAGN3 115.00 | 533282 | MUND 3 115.00 | 0 |  | 1 | 17WP | 173 | 206 | 0 |  | 87.6118 | 95.5 | [7 empty] | CATEGORYB | SINGLE | 87th STREET - CRAIG 345KV CKT 1 | 0 | 532775 | 87TH 7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T29535522SP | TO->FROM | NORTH WARSAW - TRUMAN 161KV CKT 1 | E | SWPA | GMO | EMINTH |  | 0 | 505502 | TRUMAN 5 161.00 | 541314 | NWARSAW5 161.00 | 0 |  | 1 | 22SP | 223 | 223 | 223 | 89.6796 | 89.6796 | 98.8 | [7 empty] | CATEGORYB | NONSINGLE | OVERTON-TRF | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T29125522SP | TO->FROM | NORTH WARSAW - TRUMAN 161KV CKT 1 | E | SWPA | GMO | EMINTH |  | 0 | 505502 | TRUMAN 5 161.00 | 541314 | NWARSAW5 161.00 | 0 |  | 1 | 22SP | 223 | 223 | 223 | 90.7877 | 90.7877 | 98.4 | [7 empty] | CATEGORYB | NONSINGLE | AI03 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4445522SP | TO->FROM | NORTH WARSAW - TRUMAN 161KV CKT 1 | E | SWPA | GMO | EMINTH |  | 0 | 505502 | TRUMAN 5 161.00 | 541314 | NWARSAW5 161.00 | 0 |  | 1 | 22SP | 223 | 223 | 223 | 90.8099 | 90.8099 | 98.1 | [7 empty] | CATEGORYB | SINGLE | CLINTON - WINDSOR 161KV CKT 1 | 0 | 541217 | WINDSR 5 161.00 | 541242 | CLINTON5 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T26705522SP | TO->FROM | NORTH WARSAW - TRUMAN 161KV CKT 1 | E | SWPA | GMO | EMINTH |  | 0 | 505502 | TRUMAN 5 161.00 | 541314 | NWARSAW5 161.00 | 0 |  | 1 | 22SP | 223 | 223 | 223 | 88.2192 | 88.2192 | 95.1 | [7 empty] | CATEGORYB | SINGLE | 5CAPE GIR 161.00 161/34.5KV TRANSFORMER CKT 99 | 0 | 344282 | 5CAPE GIR 161.00 | 345890 | 1VIAD 1 34.500 | 0 |  | 99 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T425513SP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 13SP | 103 | 129 | 103 | 93.2571 | 93.2571 | 98 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T2545013WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 13WP | 103 | 129 | 103 | 96.2833 | 96.2833 | 97.9 | [7 empty] | CATEGORYB | SINGLE | CHAR.CK4 230.00 - WATFORD 230KV CKT 1 | 0 | 652216 | WATFORD4 230.00 | 659302 | CHAR.CK4 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T2765013WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 13WP | 103 | 129 | 103 | 96.3 | 96.2737 | 97.9 | [7 empty] | CATEGORYB | SINGLE | CHARLIE CREEK 345/230KV TRANSFORMER CKT 1 | 0 | 659183 | CHAR.CK3 345.00 | 659302 | CHAR.CK4 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T6195013WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 13WP | 103 | 129 | 103 | 95.9108 | 95.9108 | 97.8 | [7 empty] | CATEGORYB | SINGLE | LELAND OLDS - STANTON 230KV CKT 1 | 0 | 659106 | LELANDO4 230.00 | 615901 | GRE-STANTON4230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T2755013WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 13WP | 103 | 129 | 103 | 95.6 | 95.581 | 96.7 | [7 empty] | CATEGORYB | SINGLE | LARAMIE RIVER - STEGALL 345KV CKT 1 | 0 | 659131 | LARAMIE3 345.00 | 659135 | STEGALL3 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T2665013WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 13WP | 103 | 129 | 103 | 94.5363 | 94.5363 | 96.1 | [7 empty] | CATEGORYB | SINGLE | STORLA - WESSINGTON 230KV CKT 1 | 0 | 652607 | WESSINGTON 4230.00 | 659122 | STORLA 4 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T2535013WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 13WP | 103 | 129 | 103 | 94.3777 | 94.3777 | 96 | [7 empty] | CATEGORYB | SINGLE | WATFORD - WILLISTON 230KV CKT 1 | 0 | 652216 | WATFORD4 230.00 | 652400 | WILISTN4 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T2695013WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 13WP | 103 | 129 | 103 | 94.4367 | 94.4367 | 96 | [7 empty] | CATEGORYB | SINGLE | GROTON - LELAND OLDS 345KV CKT 1 | 0 | 659105 | LELANDO3 345.00 | 659160 | GROTON 3 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T6455013WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 13WP | 103 | 129 | 103 | 94.3789 | 94.3789 | 96 | [7 empty] | CATEGORYB | NONSINGLE | DAK01WAPAB2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8035513WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 13WP | 103 | 129 | 103 | 92.2908 | 92.2908 | 96 | [7 empty] | CATEGORYB | SINGLE | FALLON (OF KY1A) 115/69/12.5KV TRANSFORMER CKT 1 | 1 | 652407 | FALLON 7 115.00 | 652213 | FALLON 8 69.000 | 652214 | FALLON 9 12.500 | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8155513WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 13WP | 103 | 129 | 103 | 92.3959 | 92.3959 | 96 | [7 empty] | CATEGORYB | SINGLE | PIERRE 115/69KV TRANSFORMER CKT 1 | 0 | 652489 | PIERRE 7 115.00 | 652223 | PIERRE 8 69.000 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FNSL | FDNS-Iteration limit exceeded | FNSL | FDNS-Iteration limit exceeded | 5 | 5 | 2011AG2AFS92T75513WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 13WP | 103 | 129 | 103 | 92.3862 | 92.3862 | 96 | [7 empty] | CATEGORYB | NONSINGLE | DAK10WAPAB3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8755513WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 13WP | 103 | 129 | 103 | 92.13 | 92.13 | 95.8 | [7 empty] | CATEGORYB | NONSINGLE | DAK25WAPAB2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8765513WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 13WP | 103 | 129 | 103 | 92.13 | 92.13 | 95.8 | [7 empty] | CATEGORYB | NONSINGLE | DAK26WAPAB2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T2725013WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 13WP | 103 | 129 | 103 | 93.9305 | 93.9305 | 95.5 | [7 empty] | CATEGORYB | SINGLE | LELAND OLDS - LOGAN 230KV CKT 1 | 0 | 659106 | LELANDO4 230.00 | 659108 | LOGAN 4 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8125513WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 13WP | 103 | 129 | 103 | 91.7939 | 91.7939 | 95.4 | [7 empty] | CATEGORYB | SINGLE | MIDLAND 115/69KV TRANSFORMER CKT 1 | 0 | 652481 | MIDLAND7 115.00 | 652263 | MIDLAND8 69.000 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8735513WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 13WP | 103 | 129 | 103 | 91.7845 | 91.7845 | 95.4 | [7 empty] | CATEGORYB | NONSINGLE | DAK06WAPAB2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T2525013WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 13WP | 103 | 129 | 103 | 93.829 | 93.829 | 95.3 | [7 empty] | CATEGORYB | SINGLE | COALHILL4 230.00 - FT PECK 230KV CKT 1 | 0 | 652111 | COALHILL4 230.00 | 652405 | FTPECK 4 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8745513WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 13WP | 103 | 129 | 103 | 91.6304 | 91.6304 | 95.3 | [7 empty] | CATEGORYB | NONSINGLE | DAK13WAPAB2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4215513WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 13WP | 103 | 129 | 103 | 91.5253 | 91.5253 | 95.2 | [7 empty] | CATEGORYB | SINGLE | BOTTNO - BOTTNOJCTCP7115.00 115KV CKT 1 | 0 | 652455 | BOTTNO 7 115.00 | 659151 | BOTTNOJCTCP7115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T2635013WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 13WP | 103 | 129 | 103 | 93.5153 | 93.5153 | 95.1 | [7 empty] | CATEGORYB | SINGLE | FT THOMPSON - LETCHER 230KV CKT 1 | 0 | 652507 | FTTHOMP4 230.00 | 652606 | LETCHER4 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8115513WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 13WP | 103 | 129 | 103 | 91.4243 | 91.4243 | 95.1 | [7 empty] | CATEGORYB | SINGLE | LAKOTA 115/12.5KV TRANSFORMER CKT 1 | 0 | 652448 | LAKOTA 7 115.00 | 652206 | LAKOTA 9 12.500 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2455513SP | FROM->TO | PLANT X STATION (WH ALM20171) 230/115/13.2KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 2 | 525481 | PLANT_X 6230.00 | 525480 | PLANT_X 3115.00 | 525479 | PLANTX_TR1 113.200 | 1 | 13SP | 239 | 239 | 0 | 99.2 | 99.158 | 99.9 | [7 empty] | CATEGORYB | SINGLE | HAPPY INTERCHANGE - TULIA TAP 115KV CKT 1 | 0 | 525154 | HAPPY_INT 3115.00 | 525179 | TULIA_TP 3115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2455513SP | FROM->TO | PLANT X STATION (WH ALM20171) 230/115/13.2KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 2 | 525481 | PLANT_X 6230.00 | 525480 | PLANT_X 3115.00 | 525479 | PLANTX_TR1 113.200 | 1 | 13SP | 239 | 239 | 0 | 99.158 | 99.158 | 99.9 | [7 empty] | CATEGORYB | SINGLE | HAPPY INTERCHANGE - TULIA TAP 115KV CKT 1 | 0 | 525154 | HAPPY_INT 3115.00 | 525179 | TULIA_TP 3115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10075513SP | FROM->TO | PLANT X STATION (WH ALM20171) 230/115/13.2KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 2 | 525481 | PLANT_X 6230.00 | 525480 | PLANT_X 3115.00 | 525479 | PLANTX_TR1 113.200 | 1 | 13SP | 239 | 239 | 0 | 99.2 | 99.1511 | 99.7 | [7 empty] | CATEGORYB | SINGLE | SUNDOWN INTERCHANGE (WH XDS70381) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 526434 | SUNDOWN 3115.00 | 526435 | SUNDOWN 6230.00 | 526432 | SUNDOWN_TR1113.800 | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T10075513SP | FROM->TO | PLANT X STATION (WH ALM20171) 230/115/13.2KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 2 | 525481 | PLANT_X 6230.00 | 525480 | PLANT_X 3115.00 | 525479 | PLANTX_TR1 113.200 | 1 | 13SP | 239 | 239 | 0 | 99.1511 | 99.1511 | 99.7 | [7 empty] | CATEGORYB | SINGLE | SUNDOWN INTERCHANGE (WH XDS70381) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 526434 | SUNDOWN 3115.00 | 526435 | SUNDOWN 6230.00 | 526432 | SUNDOWN_TR1113.800 | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T195513SP | FROM->TO | PLANT X STATION (WH ALM20171) 230/115/13.2KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 2 | 525481 | PLANT_X 6230.00 | 525480 | PLANT_X 3115.00 | 525479 | PLANTX_TR1 113.200 | 1 | 13SP | 239 | 239 | 0 | 96.2 | 96.2385 | 96.8 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T195513SP | FROM->TO | PLANT X STATION (WH ALM20171) 230/115/13.2KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 2 | 525481 | PLANT_X 6230.00 | 525480 | PLANT_X 3115.00 | 525479 | PLANTX_TR1 113.200 | 1 | 13SP | 239 | 239 | 0 | 96.2385 | 96.2385 | 96.8 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2805513SP | FROM->TO | PLANT X STATION (WH ALM20171) 230/115/13.2KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 2 | 525481 | PLANT_X 6230.00 | 525480 | PLANT_X 3115.00 | 525479 | PLANTX_TR1 113.200 | 1 | 13SP | 239 | 239 | 0 | 94.9578 | 94.9578 | 95.5 | [7 empty] | CATEGORYB | SINGLE | CROSBY COUNTY INTERCHANGE - SOUTH PLAINS REC-CROSBY COUNTY 69KV CKT 1 | 0 | 525915 | SP-CROSBY 269.000 | 525925 | CROSBY 269.000 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T14515517SP | FROM->TO | PLANT X STATION (WH ALM20171) 230/115/13.2KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 1 | 525481 | PLANT_X 6230.00 | 525480 | PLANT_X 3115.00 | 525479 | PLANTX_TR1 113.200 | 1 | 17SP | 239 | 239 | 0 | 96.0208 | 96.0208 | 97.8 | [7 empty] | CATEGORYB | SINGLE | LAMB COUNTY INTERCHANGE (WH ALM20172) 230/115/13.2KV TRANSFORMER CKT 1 | 1 | 525636 | LAMB_CNTY 3115.00 | 525637 | LAMB_CNTY 6230.00 | 525633 | LAMB_TR3 113.200 | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T13255516SP | FROM->TO | PLANT X STATION (WH ALM20171) 230/115/13.2KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 1 | 525481 | PLANT_X 6230.00 | 525480 | PLANT_X 3115.00 | 525479 | PLANTX_TR1 113.200 | 1 | 17SP | 239 | 239 | 0 |  | 95.9419 | 97.7 | [7 empty] | CATEGORYB | SINGLE | LAMB COUNTY INTERCHANGE (WH ALM20172) 230/115/13.2KV TRANSFORMER CKT 1 | 1 | 525636 | LAMB_CNTY 3115.00 | 525637 | LAMB_CNTY 6230.00 | 525633 | LAMB_TR3 113.200 | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T14075514SP | FROM->TO | PLANT X STATION (WH ALM20171) 230/115/13.2KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 1 | 525481 | PLANT_X 6230.00 | 525480 | PLANT_X 3115.00 | 525479 | PLANTX_TR1 113.200 | 1 | 17SP | 239 | 239 | 0 |  | 94.8291 | 96.4 | [7 empty] | CATEGORYB | SINGLE | LAMB COUNTY INTERCHANGE (WH ALM20172) 230/115/13.2KV TRANSFORMER CKT 1 | 1 | 525636 | LAMB_CNTY 3115.00 | 525637 | LAMB_CNTY 6230.00 | 525633 | LAMB_TR3 113.200 | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3465517SP | FROM->TO | PLATTE CITY 161/69KV TRANSFORMER CKT 1 | E | GMO | AECI |  | NW | 0 | 541221 | PLTCTY 5 161.00 | 300307 | 2PLATCTY 69.000 | 0 |  | 1 | 17SP | 56 | 56 | 0 | 93.4957 | 93.4957 | 95.4 | [7 empty] | CATEGORYB | SINGLE | EASTOWN7 345.00 - IATAN 345KV CKT 1 | 0 | 541400 | EASTOWN7 345.00 | 542982 | IATAN 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T15825517SP | FROM->TO | PLATTE CITY 161/69KV TRANSFORMER CKT 1 | E | GMO | AECI |  | NW | 0 | 541221 | PLTCTY 5 161.00 | 300307 | 2PLATCTY 69.000 | 0 |  | 1 | 17SP | 56 | 56 | 0 | 92.5993 | 92.5993 | 95.3 | [7 empty] | CATEGORYB | SINGLE | ECKLES - MISSOURI CITY 161KV CKT 1 | 0 | 548808 | ECKLES-161 161.00 | 300098 | 5MOCITY 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4005514SP | FROM->TO | PLATTE CITY 161/69KV TRANSFORMER CKT 1 | E | GMO | AECI |  | NW | 0 | 541221 | PLTCTY 5 161.00 | 300307 | 2PLATCTY 69.000 | 0 |  | 1 | 17SP | 56 | 56 | 0 |  | 94.2072 | 95.2 | [7 empty] | CATEGORYB | SINGLE | PLATTE CITY - SMITHVILLE 161KV CKT 1 | 0 | 541204 | SMTHVL 5 161.00 | 541221 | PLTCTY 5 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3435517SP | FROM->TO | PLATTE CITY 161/69KV TRANSFORMER CKT 1 | E | GMO | AECI |  | NW | 0 | 541221 | PLTCTY 5 161.00 | 300307 | 2PLATCTY 69.000 | 0 |  | 1 | 17SP | 56 | 56 | 0 | 92.642 | 92.642 | 95.2 | [7 empty] | CATEGORYB | SINGLE | ECKLES - SIBLEYPL 161.00 161KV CKT 1 | 0 | 541250 | SIBLEYPL 161.00 | 548808 | ECKLES-161 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T5445522SP | FROM->TO | PLATTE CITY 161/69KV TRANSFORMER CKT 1 | E | GMO | AECI |  | NW | 0 | 541221 | PLTCTY 5 161.00 | 300307 | 2PLATCTY 69.000 | 0 |  | 1 | 22SP | 56 | 56 | 0 | 93.4264 | 93.4264 | 97.2 | [7 empty] | CATEGORYB | SINGLE | FAIRPORT - OSBORN 161KV CKT 1 | 0 | 300076 | 5FAIRPT 161.00 | 300107 | 5OSBORN 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14SP | INVALID |  |  | FDNS |  | 5 | 0 | 2011AG2AFS91T2255014SP | FROM->TO | SEVENTEENTH (17TH 4X) 138/69/11.295KV TRANSFORMER CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 1 | 533064 | 17TH 4 138.00 | 533840 | 17TH 2 69.000 | 533112 | 17TH 4 1 11.295 | 1 | 17SP | 150 | 165 | 187.5 |  | 87.8536 | 98.0236 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER NORTH - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533040 | EVANS N4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | INVALID | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4095522SP | FROM->TO | SEVENTEENTH (17TH 4X) 138/69/11.295KV TRANSFORMER CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 1 | 533064 | 17TH 4 138.00 | 533840 | 17TH 2 69.000 | 533112 | 17TH 4 1 11.295 | 1 | 22SP | 150 | 165 | 187.5 | 94.273 | 94.273 | 97.3335 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER NORTH - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533040 | EVANS N4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3745514SP | FROM->TO | SEWARD - ST JOHN 115KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539692 | SEWARD 3 115.00 | 539696 | ST-JOHN3 115.00 | 0 |  | 1 | 17SP | 79.7 | 88 | 0 |  | 81.563 | 99.5 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3825514SP | FROM->TO | SEWARD - ST JOHN 115KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539692 | SEWARD 3 115.00 | 539696 | ST-JOHN3 115.00 | 0 |  | 1 | 17SP | 79.7 | 88 | 0 |  | 71.3622 | 98.5 | [7 empty] | CATEGORYB | SINGLE | KIOWA CO 115.00 - GREENSBURG 115KV CKT 1 | 0 | 539664 | GRNBURG3 115.00 | 560500 | KIOWA CO 115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3715514SP | FROM->TO | SEWARD - ST JOHN 115KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539692 | SEWARD 3 115.00 | 539696 | ST-JOHN3 115.00 | 0 |  | 1 | 17SP | 79.7 | 88 | 0 |  | 79.9235 | 97.7 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14SP | INVALID |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3805514SP | FROM->TO | SEWARD - ST JOHN 115KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539692 | SEWARD 3 115.00 | 539696 | ST-JOHN3 115.00 | 0 |  | 1 | 17SP | 79.7 | 88 | 0 |  | 69.382 | 96.5873 | [7 empty] | CATEGORYB | SINGLE | GREENSBURG - SUN CITY 115KV CKT 1 | 0 | 539664 | GRNBURG3 115.00 | 539697 | SUNCITY3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T12295514WP | FROM->TO | SEWARD - ST JOHN 115KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539692 | SEWARD 3 115.00 | 539696 | ST-JOHN3 115.00 | 0 |  | 1 | 17WP | 79.7 | 88 | 0 |  | 66.198 | 99.8 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2255512WP | FROM->TO | SHELDON - SW7TH & PLEASANT HILL 115KV CKT 2 | E | NPPD | LES | NPPD_686 | LES_696 | 0 | 640278 | SHELDON7 115.00 | 650242 | FOLSM&PHIL7 115.00 | 0 |  | 2 | 12WP | 105 | 105 | 105 | 91.0615 | 91.0615 | 98 | [7 empty] | CATEGORYB | SINGLE | SHELDON - SW7TH & PLEASANT HILL 115KV CKT 1 | 0 | 640278 | SHELDON7 115.00 | 650242 | FOLSM&PHIL7 115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1185514WP | FROM->TO | SHELDON 115/13.8KV TRANSFORMER CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640020 | SHELDN2G 13.800 | 640278 | SHELDON7 115.00 | 0 |  | 1 | 17WP | 140 | 140 | 140 |  | 73.8442 | 95 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | INVALID | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T925517SP | FROM->TO | SILOAM CITY - SILOAM SPRINGS 161KV CKT 1 | E | GRDA | AEPW | GRDA-MUN | FAYETTEVILLE | 0 | 512643 | SILMCTY5 161.00 | 506948 | SILOAM 5 161.00 | 0 |  | 1 | 17SP | 288 | 335 | 0 | 94.0045 | 94.0045 | 99.5138 | [7 empty] | CATEGORYB | SINGLE | FLINT CREEK - SILOAM SPRINGS TAP 345KV CKT 1 | 0 | 506935 | FLINTCR7 345.00 | 512750 | TONECE7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16SP | INVALID |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T875516SP | FROM->TO | SILOAM CITY - SILOAM SPRINGS 161KV CKT 1 | E | GRDA | AEPW | GRDA-MUN | FAYETTEVILLE | 0 | 512643 | SILMCTY5 161.00 | 506948 | SILOAM 5 161.00 | 0 |  | 1 | 17SP | 288 | 335 | 0 |  | 94.0119 | 97.9542 | [7 empty] | CATEGORYB | SINGLE | FLINT CREEK - SILOAM SPRINGS TAP 345KV CKT 1 | 0 | 506935 | FLINTCR7 345.00 | 512750 | TONECE7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14SP | INVALID |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T875514SP | FROM->TO | SILOAM CITY - SILOAM SPRINGS 161KV CKT 1 | E | GRDA | AEPW | GRDA-MUN | FAYETTEVILLE | 0 | 512643 | SILMCTY5 161.00 | 506948 | SILOAM 5 161.00 | 0 |  | 1 | 17SP | 288 | 335 | 0 |  | 93.9256 | 97.5204 | [7 empty] | CATEGORYB | SINGLE | FLINT CREEK - SILOAM SPRINGS TAP 345KV CKT 1 | 0 | 506935 | FLINTCR7 345.00 | 512750 | TONECE7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1435512WP | FROM->TO | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | E | MIDW | WERE | REG E-IL | WEST | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 12WP | 319 | 319 | 0 | 81.9176 | 81.9176 | 95.9 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - MULLERGREN 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T825513WP | FROM->TO | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | E | MIDW | WERE | REG E-IL | WEST | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 13WP | 319 | 319 | 0 | 84.6759 | 84.6759 | 96.2 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3175514SP | FROM->TO | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | E | MIDW | WERE | REG E-IL | WEST | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 17SP | 319 | 319 | 0 |  | 70.2789 | 96.6 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - MULLERGREN 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T21315514SP | FROM->TO | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | E | MIDW | WERE | REG E-IL | WEST | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 17SP | 319 | 319 | 0 |  | 73.6406 | 95.1 | [7 empty] | CATEGORYB | GENOUT | GEN532751 1-WOLF CREEK GENERATING STATION UNIT 1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-14WP | INVALID |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2245514WP | FROM->TO | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | E | MIDW | WERE | REG E-IL | WEST | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 17WP | 319 | 319 | 0 |  | 76.9727 | 99.9269 | [7 empty] | CATEGORYB | SINGLE | FLATRDG3 - HARPER 138KV CKT 1 | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP | CONT-0402 - JEC - Summit 345kV |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1805514WP | FROM->TO | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | E | MIDW | WERE | REG E-IL | WEST | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 17WP | 319 | 319 | 0 |  | 79.461 | 99.9 | [7 empty] | CATEGORYB | SINGLE | JEFFREY ENERGY CENTER - SUMMIT 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532773 | SUMMIT 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP |  |  |  | FNSL | FDNS-Blown up | 5 | 5 | 2011AG2AFS92T215514WP | FROM->TO | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | E | MIDW | WERE | REG E-IL | WEST | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 17WP | 319 | 319 | 0 |  | 77.9149 | 99.9 | [7 empty] | CATEGORYB | GENOUT | GEN542957 1-IATAN UNIT #1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-14WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3125514WP | FROM->TO | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | E | MIDW | WERE | REG E-IL | WEST | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 17WP | 319 | 319 | 0 |  | 76.7704 | 99.7 | [7 empty] | CATEGORYB | SINGLE | GRAND ISLAND - MCCOOL 345KV CKT 1 | 0 | 640271 | MCCOOL 3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T55514WP | FROM->TO | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | E | MIDW | WERE | REG E-IL | WEST | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 17WP | 319 | 319 | 0 |  | 73.7763 | 95.7 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 | INVALID | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1685512WP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | E | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 12WP | 86 | 86 | 86 | 86.2241 | 86.2241 | 95.998 | [7 empty] | CATEGORYB | SINGLE | FLATRDG3 - HARPER 138KV CKT 1 | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T8675513WP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | E | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 13WP | 86 | 86 | 86 | 86.2924 | 86.2924 | 95.8 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-34 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19685514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | E | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 72.9787 | 98 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WEPL-03A | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3185514SP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | E | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17SP | 86 | 86 | 86 |  | 67.1792 | 95.1 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - MULLERGREN 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T12265514WP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | E | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17WP | 86 | 86 | 86 |  | 67.8564 | 95.3 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-14WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T12405514WP | FROM->TO | ST JOHN - ST_JOHN 115KV CKT 1 | E | SUNC | MIDW | GREAT PL | REG E-IL | 0 | 539696 | ST-JOHN3 115.00 | 530624 | ST JOHN3 115.00 | 0 |  | 1 | 17WP | 86 | 86 | 86 |  | 70.3008 | 95 | [7 empty] | CATEGORYB | NONSINGLE | SPP-MKEC-08 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T5615517WP | FROM->TO | STEGALL - VICTORY HILL 230KV CKT 1 | E | WAPA | NPPD | WAPA_1603 | NPPD_686 | 0 | 652573 | STEGALL4 230.00 | 640396 | VICTRYH4 230.00 | 0 |  | 1 | 17WP | 240 | 240 | 264 | 92.371 | 92.371 | 98.6 | [7 empty] | CATEGORYB | SINGLE | STEGALL - WAYSIDE 230KV CKT 1 | 0 | 640404 | WAYSIDE4 230.00 | 652573 | STEGALL4 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T5155516WP | FROM->TO | STEGALL - VICTORY HILL 230KV CKT 1 | E | WAPA | NPPD | WAPA_1603 | NPPD_686 | 0 | 652573 | STEGALL4 230.00 | 640396 | VICTRYH4 230.00 | 0 |  | 1 | 17WP | 240 | 240 | 264 |  | 92.3352 | 96.5 | [7 empty] | CATEGORYB | SINGLE | STEGALL - WAYSIDE 230KV CKT 1 | 0 | 640404 | WAYSIDE4 230.00 | 652573 | STEGALL4 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16WP |  |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T335516WP | FROM->TO | STMDSJFASJCO | E |  |  |  |  | STMDSJFASJCO | 0 |  | 0 |  | 0 |  |  | 17WP | 171 | 171 | 171 |  | -75.5087 | 98.5 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4875522SP | TO->FROM | SUB 100 - JOPLIN 2ND ST. - SUB 284 - JOPLIN EAST 5TH ST. 69KV CKT 1 | E | EMDE | EMDE | JOPLIN | JOPLIN | 0 | 547557 | JOP284 2 69.000 | 547531 | JOP100 2 69.000 | 0 |  | 1 | 22SP | 54 | 65 | 0 | 95.1193 | 95.1193 | 95.2 | [7 empty] | CATEGORYB | SINGLE | SUB 109 - ATLAS JCT. - SUB 360 - JOPLIN NORTHEAST 69KV CKT 1 | 0 | 547533 | ATL109 2 69.000 | 547581 | JOP360 2 69.000 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4885522SP | FROM->TO | SUB 100 - JOPLIN 2ND ST. - SUB 372 - JOPLIN 2ND & DIVISION 69KV CKT 1 | E | EMDE | EMDE | JOPLIN | JOPLIN | 0 | 547531 | JOP100 2 69.000 | 547588 | JOP372 2 69.000 | 0 |  | 1 | 22SP | 51 | 61 | 0 | 95.9 | 95.9484 | 96 | [7 empty] | CATEGORYB | SINGLE | SUB 109 - ATLAS JCT. - SUB 360 - JOPLIN NORTHEAST 69KV CKT 1 | 0 | 547533 | ATL109 2 69.000 | 547581 | JOP360 2 69.000 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4855522SP | FROM->TO | SUB 109 - ATLAS JCT. - SUB 360 - JOPLIN NORTHEAST 69KV CKT 1 | E | EMDE | EMDE | WEBBCITY | JOPLIN | 0 | 547533 | ATL109 2 69.000 | 547581 | JOP360 2 69.000 | 0 |  | 1 | 22SP | 54 | 65 | 0 | 98.7825 | 98.7825 | 98.8 | [7 empty] | CATEGORYB | SINGLE | SUB 284 - JOPLIN EAST 5TH ST. - SUB 64 - JOPLIN 10TH ST. 69KV CKT 1 | 0 | 547526 | JOP 64 2 69.000 | 547557 | JOP284 2 69.000 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16SP |  |  |  | FDNS |  | 5 | 0 | 2011AG2AFS91T16795016SP | FROM->TO | SUB 1206 (S1206 T1) 161/69/13.8KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 1 | 646206 | S1206 5 161.00 | 647906 | S906 S 8 69.000 | 648206 | S1206T19 13.800 | 1 | 17SP | 201.6 | 201.6 | 201.6 |  | 94.3997 | 98.6 | [7 empty] | CATEGORYB | NONSINGLE | S1206T2 BSCL | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-14SP |  |  |  | FDNS |  | 5 | 0 | 2011AG2AFS91T16895014SP | FROM->TO | SUB 1206 (S1206 T1) 161/69/13.8KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 1 | 646206 | S1206 5 161.00 | 647906 | S906 S 8 69.000 | 648206 | S1206T19 13.800 | 1 | 17SP | 201.6 | 201.6 | 201.6 |  | 94.3767 | 98.5 | [7 empty] | CATEGORYB | NONSINGLE | S1206T2 BSCL | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T16875017SP | FROM->TO | SUB 1206 (S1206 T1) 161/69/13.8KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 1 | 646206 | S1206 5 161.00 | 647906 | S906 S 8 69.000 | 648206 | S1206T19 13.800 | 1 | 17SP | 201.6 | 201.6 | 201.6 | 94.3117 | 94.3117 | 98.3 | [7 empty] | CATEGORYB | NONSINGLE | S1206T2 BSCL | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T11525013SP | FROM->TO | SUB 1206 (S1206 T2) 161/69/13.8KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 1 | 646206 | S1206 5 161.00 | 647006 | S906 N 8 69.000 | 648306 | S1206T29 13.800 | 1 | 13SP | 201.6 | 201.6 | 201.6 | 96.31 | 96.31 | 95.1 | [7 empty] | CATEGORYB | NONSINGLE | S1206T1 BSCL | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T14585513SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 13SP | 250 | 250 | 250 | 95.3228 | 95.3228 | 95.4 | [7 empty] | CATEGORYB | NONSINGLE | S1217 AUTOV2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T11535013SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 13SP | 250 | 250 | 250 | 95.0901 | 95.0901 | 95.3 | [7 empty] | CATEGORYB | NONSINGLE | S1217 AUTOV2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-14SP | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T19475514SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 17SP | 250 | 250 | 250 |  | 98.4861 | 98.5 | [7 empty] | CATEGORYB | NONSINGLE | S1217 AUTOV2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-16SP | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T18605516SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 17SP | 250 | 250 | 250 |  | 98.4037 | 98.5 | [7 empty] | CATEGORYB | NONSINGLE | S1217 AUTOV2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T16895017SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 17SP | 250 | 250 | 250 | 98.2444 | 98.2444 | 98.5 | [7 empty] | CATEGORYB | NONSINGLE | S1217 AUTOV2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T20395517SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 17SP | 250 | 250 | 250 | 98.4 | 98.3948 | 98.5 | [7 empty] | CATEGORYB | NONSINGLE | S1217 AUTOV2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-14SP | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2011AG2AFS91T16915014SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 17SP | 250 | 250 | 250 |  | 98.7464 | 98.4 | [7 empty] | CATEGORYB | NONSINGLE | S1217 AUTOV2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9-16SP | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2011AG2AFS91T16815016SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 17SP | 250 | 250 | 250 |  | 98.7136 | 98.4 | [7 empty] | CATEGORYB | NONSINGLE | S1217 AUTOV2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T5205522SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 22SP | 250 | 250 | 250 | 95.9 | 95.909 | 96.2 | [7 empty] | CATEGORYB | SINGLE | SUB 3455 - SUB 3740 345KV CKT 1 | 0 | 645455 | S3455 3 345.00 | 645740 | S3740 3 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T4085022SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 22SP | 250 | 250 | 250 | 95.4371 | 95.4371 | 95.6 | [7 empty] | CATEGORYB | SINGLE | SUB 3455 - SUB 3740 345KV CKT 1 | 0 | 645455 | S3455 3 345.00 | 645740 | S3740 3 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T2245513WP | FROM->TO | SUB 167 - RIVERTON 69/13.2KV TRANSFORMER CKT 1 | E | EMDE | EMDE | BAXTER | BAXTER | 0 | 547645 | R8G167 1 13.200 | 547541 | RIV167 2 69.000 | 0 |  | 1 | 13WP | 52 | 52 | 0 | 95.8326 | 95.8326 | 98.8 | [7 empty] | CATEGORYB | SINGLE | 7JASPER 345.00 - MORGAN 345KV CKT 1 | 0 | 300045 | 7MORGAN 345.00 | 300949 | 7JASPER 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16WP | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1395516WP | FROM->TO | SUB 167 - RIVERTON 69/13.2KV TRANSFORMER CKT 1 | E | EMDE | EMDE | BAXTER | BAXTER | 0 | 547645 | R8G167 1 13.200 | 547541 | RIV167 2 69.000 | 0 |  | 1 | 17WP | 52 | 52 | 0 |  | 97.2987 | 97.8 | [7 empty] | CATEGORYB | SINGLE | SUB 368 - DADEVILLE EAST - SUB 431 - BOLIVAR SOUTH 161KV CKT 1 | 0 | 547478 | DAD368 5 161.00 | 547493 | BOL431 5 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP | SWINGBUS |  |  | FNSL | FDNS-Iteration limit exceeded | 5 | 5 | 2011AG2AFS92T15514WP | FROM->TO | SUB 167 - RIVERTON 69/13.2KV TRANSFORMER CKT 1 | E | EMDE | EMDE | BAXTER | BAXTER | 0 | 547645 | R8G167 1 13.200 | 547541 | RIV167 2 69.000 | 0 |  | 1 | 17WP | 52 | 52 | 0 |  | 96.9377 | 97.7 | [7 empty] | CATEGORYB | SINGLE | SUB 368 - DADEVILLE EAST - SUB 431 - BOLIVAR SOUTH 161KV CKT 1 | 0 | 547478 | DAD368 5 161.00 | 547493 | BOL431 5 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T1505517WP | FROM->TO | SUB 167 - RIVERTON 69/13.2KV TRANSFORMER CKT 1 | E | EMDE | EMDE | BAXTER | BAXTER | 0 | 547645 | R8G167 1 13.200 | 547541 | RIV167 2 69.000 | 0 |  | 1 | 17WP | 52 | 52 | 0 | 97.1 | 97.0668 | 97.3 | [7 empty] | CATEGORYB | SINGLE | SUB 368 - DADEVILLE EAST - SUB 431 - BOLIVAR SOUTH 161KV CKT 1 | 0 | 547478 | DAD368 5 161.00 | 547493 | BOL431 5 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4865522SP | TO->FROM | SUB 284 - JOPLIN EAST 5TH ST. - SUB 64 - JOPLIN 10TH ST. 69KV CKT 1 | E | EMDE | EMDE | JOPLIN | JOPLIN | 0 | 547526 | JOP 64 2 69.000 | 547557 | JOP284 2 69.000 | 0 |  | 1 | 22SP | 54 | 65 | 0 | 99 | 98.9585 | 99 | [7 empty] | CATEGORYB | SINGLE | SUB 109 - ATLAS JCT. - SUB 360 - JOPLIN NORTHEAST 69KV CKT 1 | 0 | 547533 | ATL109 2 69.000 | 547581 | JOP360 2 69.000 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T1925013SP | FROM->TO | SUB 389 - JOPLIN SOUTHWEST - SUB EXPLORER SPRING CITY TAP 69KV CKT 1 | E | EMDE | EMDE | JOPLIN | JOPLIN | 0 | 547592 | JOP389 2 69.000 | 547438 | EXP449T2 69.000 | 0 |  | 1 | 13SP | 33 | 39 | 0 | 95.608 | 95.608 | 95.7 | [7 empty] | CATEGORYB | SINGLE | SUB 184 - NEOSHO SOUTH JCT. - SUB 314 - NEOSHO LINDE 69KV CKT 1 | 0 | 547543 | NEO184 2 69.000 | 547563 | LIN314 2 69.000 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T5225522SP | FROM->TO | SUB 906 SOUTH - SUB 924 69KV CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 647906 | S906 S 8 69.000 | 647924 | S924 8 69.000 | 0 |  | 1 | 22SP | 95 | 95 | 95 | 93.71 | 93.71 | 97.8 | [7 empty] | CATEGORYB | SINGLE | SUB 901 - SUB 912 69KV CKT 1 | 0 | 647901 | S901 8 69.000 | 647912 | S912 8 69.000 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T4615522SP | TO->FROM | SUB C - Sterling Rd Junction 69KV CKT 1 | E | INDN | INDN | INDN-4 | INDN-7 | 0 | 548826 | STRLNGRD 69.000 | 548825 | SUB C 69.000 | 0 |  | 1 | 22SP | 72 | 72 | 0 | 94.2661 | 94.2661 | 96.2 | [7 empty] | CATEGORYB | SINGLE | HAWTHORN - SUBSTATION M 161KV CKT 1 | 0 | 542973 | HAWTHRN5 161.00 | 548814 | SUB M-161 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T2575022SP | FROM->TO | SUNDOWN INTERCHANGE (WH XDS70381) 230/115/13.8KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 1 | 526435 | SUNDOWN 6230.00 | 526434 | SUNDOWN 3115.00 | 526432 | SUNDOWN_TR1113.800 | 1 | 22SP | 187 | 187 | 0 | 97.6227 | 97.6227 | 97.5 | [7 empty] | CATEGORYB | SINGLE | HOCKLEY COUNTY INTERCHANGE - LAMB COUNTY INTERCHANGE 115KV CKT 1 | 0 | 525636 | LAMB_CNTY 3115.00 | 526020 | HOCKLEY 3115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP | SPP_FG-EES-AFC-20032-MARHRS_NEWIN |  |  | FDNS |  | 5 | 0 | 2011AG2AFS91T3305014WP | FROM->TO | TRUMANN - TRUMANN WEST AECC 161KV CKT 1 | E | EES | EES | EAINTH |  | 0 | 338169 | 5TRUMAN 161.00 | 338707 | 5TRUM-W# 161.00 | 0 |  | 1 | 17WP | 148 | 148 | 0 |  | 100.1653 | 99 | [7 empty] | CATEGORYB | SINGLE | NEWPORT - NEWPORT INDUSTRIAL 161KV CKT 1 | 0 | 338151 | 5NEWPO 161.00 | 338173 | 5NEW-IN 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16WP | SPP_FG-EES-AFC-20032-MARHRS_NEWIN |  |  | FDNS |  | 5 | 0 | 2011AG2AFS91T3275016WP | FROM->TO | TRUMANN - TRUMANN WEST AECC 161KV CKT 1 | E | EES | EES | EAINTH |  | 0 | 338169 | 5TRUMAN 161.00 | 338707 | 5TRUM-W# 161.00 | 0 |  | 1 | 17WP | 148 | 148 | 0 |  | 100.1484 | 99 | [7 empty] | CATEGORYB | SINGLE | NEWPORT - NEWPORT INDUSTRIAL 161KV CKT 1 | 0 | 338151 | 5NEWPO 161.00 | 338173 | 5NEW-IN 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP |  |  |  | FDNS |  | 5 | 0 | 2011AG2AFS91T3375014WP | FROM->TO | TRUMANN - TRUMANN WEST AECC 161KV CKT 1 | E | EES | EES | EAINTH |  | 0 | 338169 | 5TRUMAN 161.00 | 338707 | 5TRUM-W# 161.00 | 0 |  | 1 | 17WP | 148 | 148 | 0 |  | 98.6834 | 97.5 | [7 empty] | CATEGORYB | SINGLE | NEWPORT AB - NEWPORT INDUSTRIAL 161KV CKT 1 | 0 | 338172 | 5NEW-AB 161.00 | 338173 | 5NEW-IN 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16WP |  |  |  | FDNS |  | 5 | 0 | 2011AG2AFS91T3345016WP | FROM->TO | TRUMANN - TRUMANN WEST AECC 161KV CKT 1 | E | EES | EES | EAINTH |  | 0 | 338169 | 5TRUMAN 161.00 | 338707 | 5TRUM-W# 161.00 | 0 |  | 1 | 17WP | 148 | 148 | 0 |  | 98.6666 | 97.5 | [7 empty] | CATEGORYB | SINGLE | NEWPORT AB - NEWPORT INDUSTRIAL 161KV CKT 1 | 0 | 338172 | 5NEW-AB 161.00 | 338173 | 5NEW-IN 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 | SPP_FG-EES-AFC-20032-MARHRS_NEWIN | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T3565017WP | FROM->TO | TRUMANN - TRUMANN WEST AECC 161KV CKT 1 | E | EES | EES | EAINTH |  | 0 | 338169 | 5TRUMAN 161.00 | 338707 | 5TRUM-W# 161.00 | 0 |  | 1 | 17WP | 148 | 148 | 0 | 100.0904 | 100.0904 | 97.1 | [7 empty] | CATEGORYB | SINGLE | NEWPORT - NEWPORT INDUSTRIAL 161KV CKT 1 | 0 | 338151 | 5NEWPO 161.00 | 338173 | 5NEW-IN 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP |  |  |  | FDNS |  | 5 | 0 | 2011AG2AFS91T3355014WP | FROM->TO | TRUMANN - TRUMANN WEST AECC 161KV CKT 1 | E | EES | EES | EAINTH |  | 0 | 338169 | 5TRUMAN 161.00 | 338707 | 5TRUM-W# 161.00 | 0 |  | 1 | 17WP | 148 | 148 | 0 |  | 96.8812 | 95.7 | [7 empty] | CATEGORYB | SINGLE | CASH - NEWPORT AB 161KV CKT 1 | 0 | 338171 | 5CASH 161.00 | 338172 | 5NEW-AB 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16WP |  |  |  | FDNS |  | 5 | 0 | 2011AG2AFS91T3325016WP | FROM->TO | TRUMANN - TRUMANN WEST AECC 161KV CKT 1 | E | EES | EES | EAINTH |  | 0 | 338169 | 5TRUMAN 161.00 | 338707 | 5TRUM-W# 161.00 | 0 |  | 1 | 17WP | 148 | 148 | 0 |  | 96.8642 | 95.7 | [7 empty] | CATEGORYB | SINGLE | CASH - NEWPORT AB 161KV CKT 1 | 0 | 338171 | 5CASH 161.00 | 338172 | 5NEW-AB 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AG2AFS91T3575017WP | FROM->TO | TRUMANN - TRUMANN WEST AECC 161KV CKT 1 | E | EES | EES | EAINTH |  | 0 | 338169 | 5TRUMAN 161.00 | 338707 | 5TRUM-W# 161.00 | 0 |  | 1 | 17WP | 148 | 148 | 0 | 98.6 | 98.6086 | 95.6 | [7 empty] | CATEGORYB | SINGLE | NEWPORT AB - NEWPORT INDUSTRIAL 161KV CKT 1 | 0 | 338172 | 5NEW-AB 161.00 | 338173 | 5NEW-IN 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-14WP |  |  |  | FDNS |  | 5 | 0 | 2011AG2AFS91T3335014WP | FROM->TO | TRUMANN - TRUMANN WEST AECC 161KV CKT 1 | E | EES | EES | EAINTH |  | 0 | 338169 | 5TRUMAN 161.00 | 338707 | 5TRUM-W# 161.00 | 0 |  | 1 | 17WP | 148 | 148 | 0 |  | 96.2456 | 95.1 | [7 empty] | CATEGORYB | SINGLE | CASH - JONESBORO 161KV CKT 1 | 0 | 338170 | 5JONES 161.00 | 338171 | 5CASH 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9-16WP |  |  |  | FDNS |  | 5 | 0 | 2011AG2AFS91T3305016WP | FROM->TO | TRUMANN - TRUMANN WEST AECC 161KV CKT 1 | E | EES | EES | EAINTH |  | 0 | 338169 | 5TRUMAN 161.00 | 338707 | 5TRUM-W# 161.00 | 0 |  | 1 | 17WP | 148 | 148 | 0 |  | 96.2286 | 95 | [7 empty] | CATEGORYB | SINGLE | CASH - JONESBORO 161KV CKT 1 | 0 | 338170 | 5JONES 161.00 | 338171 | 5CASH 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3075512WP | FROM->TO | WEBRE - WILLOW GLEN 500KV CKT 1 | E | EES | EES | GSLBTR | GSLBTR | 0 | 335500 | 8WEBRE 500.00 | 335618 | 8WGLEN 500.00 | 0 |  | 1 | 12WP | 1732 | 1732 | 0 | 96.2 | 96.2124 | 97.1 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AG2 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AG2AFS91T3075512WP | FROM->TO | WEBRE - WILLOW GLEN 500KV CKT 1 | E | EES | EES | GSLBTR | GSLBTR | 0 | 335500 | 8WEBRE 500.00 | 335618 | 8WGLEN 500.00 | 0 |  | 1 | 12WP | 1732 | 1732 | 0 | 96.2124 | 96.2124 | 97.1 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%