## tblAllFacilityLog
STUDYDES | STUDYDES2 | EVENTTYPE | AssessmentSOLUTIONTYPE | AssessmenFDNS-TERMINATION | SOLUTIONTYPE | FDNS-TERMINATION | GROUP | SCENARIO | FGName | DIRECTION | FacilityName | FacilityUpgradeCode | ModelArea1 | ModelArea2 | FZONENAME | TZONENAME | MONTFLAG | MONTFB | MONTFNAME | MONTTB1 | MONTTNAME1 | MONTTB2 | MONTTNAME2 | MONTCKT | Case | RATEA | RATEB | RATEC | Assessment Loading | BaseCaseLoading | TransferCaseLoading | NameOfBusWithMonitoredVoltage | Assessment Voltage | BaseCaseVoltage | TransferCaseVoltage | VINIT | VMIN | VMAX | CATEGORY | CONTTYPE | CONTNAME | CONTXFMRFLAG | CONTFB | CONTFNAME | CONTTB1 | CONTTNAME1 | CONTTB2 | CONTTNAME2 | CONTCKT | TransmissionProviderSystemImpactStudyNotesComments | RequiredRateB | TransmissionOwnerComments | OwnerDesignation | UpgradeName | UpgradeComponentWithinFacility | NewSummerA | NewSummerB | NewOtherA | NewOtherB | DistToConstruct | TotalLead | ConstructionLeadOnly | NewOrConstructWhileEnergized | NewR | NewX | NewB | CommentsRegardingUpgradeRequirements | NewCost | EffDate | NetPlantDate | ReusableEx_GrossValue | ReusableEx_NetValue | Reusable_EndofDepr | SalvageValue | NewCostWhileExpediting | EffDateExpedited | StartDeprExpedited | EndDeprExpedited | NetPlantDateExpedited | ReusableEx_GrossExpedited | ReusableEx_NetExpedited | Reusable_EndofDeprExpedited | SalvageValueExpedited | Generation 1 Owner & Unit (Name) | Generation 1 Redispatch Cost ($) | Generation 1 Redispatch Date (M/D/Y) | Generation 2 Owner & Unit (Name) | Generation 2 Redispatch Cost ($) | Generation 2 Redispatch Date (M/D/Y) | Generation 3 Owner & Unit (Name) | Generation 3 Redispatch Cost ($) | Generation 3 Redispatch Date (M/D/Y) | ActualCompletion | ActualNewCost | ActualNetPlantDate | ActualReusableEx_GrossValue | ActualReusableEx_NetValue | ActualReusable_EndofDepr | ActualSalvageValue | Actual_NewCostWhileExpediting | Actual_StartDeprExp | Actual_EndDeprExp | Actual_NetPlantDateExpedited | ActualReusableEx_GrossExpedited | ActualReusableEx_NetExpedited | ActualReusable_EndofDeprExpedited | Actual_SalvageValueExpedited | SPPReliabilityDate | COD | EOC | EarliestDate
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1945517SP | TO->FROM | 5 TRIBES - PECAN CREEK 161KV CKT 1 | S | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515234 | PECANCK5 161.00 | 515228 | 5TRIBES5 161.00 | 0 |  | 1 | 17SP | 272 | 312 | 0 | 97.4 | 97.4221 | 101.9425 | [7 empty] | CATEGORYB | SINGLE | AGENCY - PECAN CREEK 161KV CKT 1 | 0 | 515230 | AGENCY 5 161.00 | 515234 | PECANCK5 161.00 | 0 |  | 1 |  |  |  | OKGE | 5 TRIBES - PECAN CREEK 161KV CKT 1 Accelerate | Reconductor 4.07 miles of transmission line to 1590AS52 Make 5 Tribes substation equipment 2000 amp | 471 | 542 | 558 | 558 | 2.87 | 26 | 8 | Y | 0.00111 | 0.011277 | 0.00685 |  | 2653475 | 2012-04-09 | [38 empty] | 2018-06-01 | 2014-06-01 | 2016-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2785522SP | TO->FROM | 5 TRIBES - PECAN CREEK 161KV CKT 1 | S | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515234 | PECANCK5 161.00 | 515228 | 5TRIBES5 161.00 | 0 |  | 1 | 22SP | 272 | 312 | 0 | 109.9 | 109.8822 | 114.8254 | [7 empty] | CATEGORYB | SINGLE | AGENCY - PECAN CREEK 161KV CKT 1 | 0 | 515230 | AGENCY 5 161.00 | 515234 | PECANCK5 161.00 | 0 |  | 1 |  |  |  | OKGE | 5 TRIBES - PECAN CREEK 161KV CKT 1 Accelerate | Reconductor 4.07 miles of transmission line to 1590AS52 Make 5 Tribes substation equipment 2000 amp | 471 | 542 | 558 | 558 | 2.87 | 26 | 8 | Y | 0.00111 | 0.011277 | 0.00685 |  | 2653475 | 2012-04-09 | [38 empty] | 2018-06-01 | 2014-06-01 | 2016-06-01
GEN | [10 empty] | ALBION - PETERSBURG 115KV CKT 1 | U | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640318 | PETRSBG7 115.00 | 640054 | ALBION 7 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | NPPD | ALBION - PETERSBURG 115KV CKT 1 | Replace Breaker Switch 1106-D and jumpers at Albion. Replace main bus at Petersburg. Upgrade and replace transmission structures on 115 kV lineto facilitate 100 degrees Centigrade line operation. | [53 empty] | 2013-01-01 | 2013-01-01
2011-AGP1 | AFS9 | INVALID | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1635512WP | FROM->TO | ALEXANDER - PRATT 115KV CKT 1 | CP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 | 12WP | 79.7 | 79.7 | 0 | 105.5 | 105.4941 | 138.0556 | [7 empty] | CATEGORYB | SINGLE | FLATRDG3 - HARPER 138KV CKT 1 | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 |  |  |  | MKEC | MEDICINE LODGE - PRATT 115KV CKT 1 | Rebuild 26 mile line | [5 empty] | 24 | 24 | [46 empty] | 2012-10-01 | 2014-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T7435512WP | FROM->TO | ALEXANDER - PRATT 115KV CKT 1 | CP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 | 12WP | 79.7 | 79.7 | 0 |  | 94.6607 | 127.056 | [7 empty] | CATEGORYB | NONSINGLE | SPP-MKEC-05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | MEDICINE LODGE - PRATT 115KV CKT 1 | Rebuild 26 mile line | [5 empty] | 24 | 24 | [46 empty] | 2012-10-01 | 2014-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T7595512WP | FROM->TO | ALEXANDER - PRATT 115KV CKT 1 | CP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 | 12WP | 79.7 | 79.7 | 0 |  | 94.6622 | 127.0515 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-34 | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | MEDICINE LODGE - PRATT 115KV CKT 1 | Rebuild 26 mile line | [5 empty] | 24 | 24 | [46 empty] | 2012-10-01 | 2014-01-01
2007-AG3 | AFS7 | [9 empty] | ALEXANDER - PRATT 115KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | MKEC | ALEXANDER - PRATT 115KV CKT 1 | Rebuild line | [53 empty] | 2009-12-01 | 2014-01-01
2007-AG3 | AFS7 | [9 empty] | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | MKEC | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | Rebuild line | [53 empty] | 2009-12-01 | 2014-01-01
2009-AGP1 | [10 empty] | ALTUS SW - NAVAJO 69KV CKT 1 | U | WFEC | WFEC | AEP-KP | AEP-KP | 0 | 521009 | NAVAJO 2 69.000 | 520805 | ALTUSSW2 69.000 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | WFEC | ALTUS SW - NAVAJO 69KV CKT 1 | Upgrade Terminal Equipment at Altus SW, 300-600A, new rating conductor 53/65MVA | [53 empty] | 2013-06-01 | 2013-06-01
2006-AG1 | 2006-AG1 | [9 empty] | ALUMAX TAP - BANN 138KV CKT 1 | U | AEPW | AEPW |  |  | 0 | 508049 | ALUMXT 4 138 | 508054 | BANN 4 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | AEPW | ALUMAX TAP - BANN 138KV CKT 1 | Replace six (6) 138 kV switches, five at Bann & one at Alumax Tap. Rebuild 0.67 miles of 1024 ACAR with 2156 ACSR. Replace wavetrap & jumpers @ Bann. Replace breaker 3300 @ Bann. | [53 empty] | 2008-06-01 | 2008-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T19315022SP | FROM->TO | ARTESIA INTERCHANGE (GE C254477) 115/69/13.2KV TRANSFORMER CKT 1 | REL | SPS | SPS | SPS-PECO | SPS-PECO | 2 | 527707 | ARTESIA 3115.00 | 527701 | ARTESIA 269.000 | 527699 | ARTSIA_TR1 113.200 | 1 | 22SP | 40 | 46 | 0 | 107 | 107.0489 | 107.0452 | [7 empty] | CATEGORYB | SINGLE | ARTESIA INTERCHANGE (MNLY 2118072) 115/69/13.2KV TRANSFORMER CKT 2 | 1 | 527701 | ARTESIA 269.000 | 527707 | ARTESIA 3115.00 | 527700 | ARTSIA_TR2 113.200 | 2 |  |  |  | SPS | ARTESIA INTERCHANGE (GE C254477) 115/69/13.2KV TRANSFORMER CKT 1 | Replace Transformer | 84 | 96 |  |  |  | 24 | 24 | [46 empty] | 2018-06-01 | 2018-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T19295022SP | FROM->TO | ARTESIA INTERCHANGE (MNLY 2118072) 115/69/13.2KV TRANSFORMER CKT 2 | REL | SPS | SPS | SPS-PECO | SPS-PECO | 2 | 527707 | ARTESIA 3115.00 | 527701 | ARTESIA 269.000 | 527700 | ARTSIA_TR2 113.200 | 2 | 22SP | 40 | 46 | 0 | 107.1 | 107.1388 | 107.1353 | [7 empty] | CATEGORYB | SINGLE | ARTESIA INTERCHANGE (GE C254477) 115/69/13.2KV TRANSFORMER CKT 1 | 1 | 527701 | ARTESIA 269.000 | 527707 | ARTESIA 3115.00 | 527699 | ARTSIA_TR1 113.200 | 1 |  |  |  | SPS | ARTESIA INTERCHANGE (MNLY 2118072) 115/69/13.2KV TRANSFORMER CKT 2 | Replace Transformer | 84 | 96 |  |  |  | 24 | 24 | [46 empty] | 2018-06-01 | 2018-06-01
GEN-2006-010 | Turk | [9 empty] | ASHDOWN REC (MILLWOOD) - OKAY 138KV CKT 1 | U | AEPW | AEPW | SARK | SARKAECC | 0 | 507428 | OKAY 4 138.00 | 507402 | ASHDWNR4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | AEPW | ASHDOWN REC (MILLWOOD) - OKAY 138KV CKT 1 | Recunductor and convert line to 138 kV and replace switches at Ashdown REC | [53 empty] | 2012-07-01 | 2012-07-01
GEN-2006-010 | Turk | [9 empty] | ASHDOWN REC (MILLWOOD) - PATTERSON 138KV CKT 1 | U | AEPW | AEPW | SARKAECC | SARK | 0 | 507402 | ASHDWNR4 138.00 | 507431 | PATTERS4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | AEPW | ASHDOWN REC (MILLWOOD) - PATTERSON 138KV CKT 1 | Reconductor Line & Convert Line to 138 kV and convert Patterson station to breaker-and-a half cofiguration | [53 empty] | 2012-07-01 | 2012-07-01
GEN-2006-010 | Turk | [9 empty] | BANN - RED SPRINGS REC 138KV CKT 1 | U | AEPW | AEPW | TEXARK | TXARNTEC | 0 | 508054 | BANN 4 138.00 | 508075 | REDSPRG4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | AEPW | BANN - RED SPRINGS REC 138KV CKT 1 | Replace 138 kV breakers 3300 & 3310 | [53 empty] | 2012-07-01 | 2012-07-01
2011-AGP1 | AFS9 | SPP_FG-5218 - BEAEURMONBRK |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3705513SP | FROM->TO | BEAVER - EUREKA SPRINGS 161KV CKT 1 | S | SWPA | AEPW | EMINTH | FAYETTEVILLE | 0 | 505480 | BEAVER 5 161.00 | 506932 | EUREKA 5 161.00 | 0 |  | 1 | 13SP | 236 | 247 | 0 |  | 92.2426 | 100.4823 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE - SUB 383 - MONETT 345KV CKT 1 | 0 | 547481 | MON383 7 345.00 | 549984 | BROOKLINE 7345.00 | 0 |  | 1 |  |  |  | AEPW | BEAVER - EUREKA SPRINGS 161KV CKT 1 AEPW | Rebuild 1.25 miles of 795 ACSR with 1590 ACSR. Replace wavetrap & jumpers @ Eureka Springs | 318 | 438 | 422 | 502 | 1.25 | 24 | 6 |  | 0.00032 | 0.003398 | 0.00196 | Ratings are for AEP equipment only. New limit is the switch @ Eureka Springs. | 2635665.7431 | 2012-04-12 | [39 empty] | 2013-06-01 | 2016-06-01
2011-AGP1 | AFS9 | SPP_FG-5218 - BEAEURMONBRK |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3705513SP | FROM->TO | BEAVER - EUREKA SPRINGS 161KV CKT 1 | S | SWPA | AEPW | EMINTH | FAYETTEVILLE | 0 | 505480 | BEAVER 5 161.00 | 506932 | EUREKA 5 161.00 | 0 |  | 1 | 13SP | 236 | 247 | 0 |  | 92.2426 | 100.4823 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE - SUB 383 - MONETT 345KV CKT 1 | 0 | 547481 | MON383 7 345.00 | 549984 | BROOKLINE 7345.00 | 0 |  | 1 |  |  |  | SWPA | BEAVER - EUREKA SPRINGS 161KV CKT 1 SWPA | Rebuild line using 1590MCM ACSR conductor on tubular steel H-frame structures. Replace breakers and switches at Beaver. Remove wave traps. | 335 | 368 | 335 | 368 | 6 | 15 | 4 | [5 empty] | 4130000 | 2012-04-10 | [39 empty] | 2013-06-01 | 2016-06-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T13995513SP | FROM->TO | BEAVER - EUREKA SPRINGS 161KV CKT 1 | S | SWPA | AEPW | EMINTH | FAYETTEVILLE | 0 | 505480 | BEAVER 5 161.00 | 506932 | EUREKA 5 161.00 | 0 |  | 1 | 13SP | 236 | 247 | 0 |  | 92.2275 | 100.4666 | [7 empty] | CATEGORYB | NONSINGLE | AI12 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SWPA | BEAVER - EUREKA SPRINGS 161KV CKT 1 SWPA | Rebuild line using 1590MCM ACSR conductor on tubular steel H-frame structures. Replace breakers and switches at Beaver. Remove wave traps. | 335 | 368 | 335 | 368 | 6 | 15 | 4 | [5 empty] | 4130000 | 2012-04-10 | [39 empty] | 2013-06-01 | 2016-06-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T13995513SP | FROM->TO | BEAVER - EUREKA SPRINGS 161KV CKT 1 | S | SWPA | AEPW | EMINTH | FAYETTEVILLE | 0 | 505480 | BEAVER 5 161.00 | 506932 | EUREKA 5 161.00 | 0 |  | 1 | 13SP | 236 | 247 | 0 |  | 92.2275 | 100.4666 | [7 empty] | CATEGORYB | NONSINGLE | AI12 | 0 | 0 |  | 0 |  | 0 | [5 empty] | AEPW | BEAVER - EUREKA SPRINGS 161KV CKT 1 AEPW | Rebuild 1.25 miles of 795 ACSR with 1590 ACSR. Replace wavetrap & jumpers @ Eureka Springs | 318 | 438 | 422 | 502 | 1.25 | 24 | 6 |  | 0.00032 | 0.003398 | 0.00196 | Ratings are for AEP equipment only. New limit is the switch @ Eureka Springs. | 2635665.7431 | 2012-04-12 | [39 empty] | 2013-06-01 | 2016-06-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T785513SP | FROM->TO | BEAVER - EUREKA SPRINGS 161KV CKT 1 | S | SWPA | AEPW | EMINTH | FAYETTEVILLE | 0 | 505480 | BEAVER 5 161.00 | 506932 | EUREKA 5 161.00 | 0 |  | 1 | 13SP | 236 | 247 | 0 |  | 92.1664 | 100.4141 | [7 empty] | CATEGORYB | SINGLE | FLINT CREEK - SUB 383 - MONETT 345KV CKT 1 | 0 | 506935 | FLINTCR7 345.00 | 547481 | MON383 7 345.00 | 0 |  | 1 |  |  |  | AEPW | BEAVER - EUREKA SPRINGS 161KV CKT 1 AEPW | Rebuild 1.25 miles of 795 ACSR with 1590 ACSR. Replace wavetrap & jumpers @ Eureka Springs | 318 | 438 | 422 | 502 | 1.25 | 24 | 6 |  | 0.00032 | 0.003398 | 0.00196 | Ratings are for AEP equipment only. New limit is the switch @ Eureka Springs. | 2635665.7431 | 2012-04-12 | [39 empty] | 2013-06-01 | 2016-06-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T785513SP | FROM->TO | BEAVER - EUREKA SPRINGS 161KV CKT 1 | S | SWPA | AEPW | EMINTH | FAYETTEVILLE | 0 | 505480 | BEAVER 5 161.00 | 506932 | EUREKA 5 161.00 | 0 |  | 1 | 13SP | 236 | 247 | 0 |  | 92.1664 | 100.4141 | [7 empty] | CATEGORYB | SINGLE | FLINT CREEK - SUB 383 - MONETT 345KV CKT 1 | 0 | 506935 | FLINTCR7 345.00 | 547481 | MON383 7 345.00 | 0 |  | 1 |  |  |  | SWPA | BEAVER - EUREKA SPRINGS 161KV CKT 1 SWPA | Rebuild line using 1590MCM ACSR conductor on tubular steel H-frame structures. Replace breakers and switches at Beaver. Remove wave traps. | 335 | 368 | 335 | 368 | 6 | 15 | 4 | [5 empty] | 4130000 | 2012-04-10 | [39 empty] | 2013-06-01 | 2016-06-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4055513SP | FROM->TO | BEAVER - EUREKA SPRINGS 161KV CKT 1 | S | SWPA | AEPW | EMINTH | FAYETTEVILLE | 0 | 505480 | BEAVER 5 161.00 | 506932 | EUREKA 5 161.00 | 0 |  | 1 | 13SP | 236 | 247 | 0 |  | 91.6969 | 100.1845 | [7 empty] | CATEGORYB | SINGLE | 7JASPER 345.00 - BLACKBERRY 345KV CKT 1 | 0 | 300739 | 7BLACKBERRY 345.00 | 300949 | 7JASPER 345.00 | 0 |  | 1 |  |  |  | AEPW | BEAVER - EUREKA SPRINGS 161KV CKT 1 AEPW | Rebuild 1.25 miles of 795 ACSR with 1590 ACSR. Replace wavetrap & jumpers @ Eureka Springs | 318 | 438 | 422 | 502 | 1.25 | 24 | 6 |  | 0.00032 | 0.003398 | 0.00196 | Ratings are for AEP equipment only. New limit is the switch @ Eureka Springs. | 2635665.7431 | 2012-04-12 | [39 empty] | 2013-06-01 | 2016-06-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4055513SP | FROM->TO | BEAVER - EUREKA SPRINGS 161KV CKT 1 | S | SWPA | AEPW | EMINTH | FAYETTEVILLE | 0 | 505480 | BEAVER 5 161.00 | 506932 | EUREKA 5 161.00 | 0 |  | 1 | 13SP | 236 | 247 | 0 |  | 91.6969 | 100.1845 | [7 empty] | CATEGORYB | SINGLE | 7JASPER 345.00 - BLACKBERRY 345KV CKT 1 | 0 | 300739 | 7BLACKBERRY 345.00 | 300949 | 7JASPER 345.00 | 0 |  | 1 |  |  |  | SWPA | BEAVER - EUREKA SPRINGS 161KV CKT 1 SWPA | Rebuild line using 1590MCM ACSR conductor on tubular steel H-frame structures. Replace breakers and switches at Beaver. Remove wave traps. | 335 | 368 | 335 | 368 | 6 | 15 | 4 | [5 empty] | 4130000 | 2012-04-10 | [39 empty] | 2013-06-01 | 2016-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1365522SP | FROM->TO | BEAVER - EUREKA SPRINGS 161KV CKT 1 | S | SWPA | AEPW | EMINTH | FAYETTEVILLE | 0 | 505480 | BEAVER 5 161.00 | 506932 | EUREKA 5 161.00 | 0 |  | 1 | 22SP | 236 | 247 | 0 | 95.4 | 95.3666 | 105.1104 | [7 empty] | CATEGORYB | SINGLE | EROGERS7 345.00 - OSBOURNE 345KV CKT 1 | 0 | 506979 | SHIPERD7 345.00 | 506982 | EROGERS7 345.00 | 0 |  | 1 |  |  |  | AEPW | BEAVER - EUREKA SPRINGS 161KV CKT 1 AEPW | Rebuild 1.25 miles of 795 ACSR with 1590 ACSR. Replace wavetrap & jumpers @ Eureka Springs | 318 | 438 | 422 | 502 | 1.25 | 24 | 6 |  | 0.00032 | 0.003398 | 0.00196 | Ratings are for AEP equipment only. New limit is the switch @ Eureka Springs. | 2635665.7431 | 2012-04-12 | [39 empty] | 2013-06-01 | 2016-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1365522SP | FROM->TO | BEAVER - EUREKA SPRINGS 161KV CKT 1 | S | SWPA | AEPW | EMINTH | FAYETTEVILLE | 0 | 505480 | BEAVER 5 161.00 | 506932 | EUREKA 5 161.00 | 0 |  | 1 | 22SP | 236 | 247 | 0 | 95.4 | 95.3666 | 105.1104 | [7 empty] | CATEGORYB | SINGLE | EROGERS7 345.00 - OSBOURNE 345KV CKT 1 | 0 | 506979 | SHIPERD7 345.00 | 506982 | EROGERS7 345.00 | 0 |  | 1 |  |  |  | SWPA | BEAVER - EUREKA SPRINGS 161KV CKT 1 SWPA | Rebuild line using 1590MCM ACSR conductor on tubular steel H-frame structures. Replace breakers and switches at Beaver. Remove wave traps. | 335 | 368 | 335 | 368 | 6 | 15 | 4 | [5 empty] | 4130000 | 2012-04-10 | [39 empty] | 2013-06-01 | 2016-06-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T19755522SP | FROM->TO | BEAVER - EUREKA SPRINGS 161KV CKT 1 | S | SWPA | AEPW | EMINTH | FAYETTEVILLE | 0 | 505480 | BEAVER 5 161.00 | 506932 | EUREKA 5 161.00 | 0 |  | 1 | 22SP | 236 | 247 | 0 |  | 94.9057 | 104.293 | [7 empty] | CATEGORYB | SINGLE | EROGERS7 345.00 - OSAGE CREEK 345KV CKT 1 | 0 | 506982 | EROGERS7 345.00 | 338683 | 7OSAGECK 345.00 | 0 |  | 1 |  |  |  | AEPW | BEAVER - EUREKA SPRINGS 161KV CKT 1 AEPW | Rebuild 1.25 miles of 795 ACSR with 1590 ACSR. Replace wavetrap & jumpers @ Eureka Springs | 318 | 438 | 422 | 502 | 1.25 | 24 | 6 |  | 0.00032 | 0.003398 | 0.00196 | Ratings are for AEP equipment only. New limit is the switch @ Eureka Springs. | 2635665.7431 | 2012-04-12 | [39 empty] | 2013-06-01 | 2016-06-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T19755522SP | FROM->TO | BEAVER - EUREKA SPRINGS 161KV CKT 1 | S | SWPA | AEPW | EMINTH | FAYETTEVILLE | 0 | 505480 | BEAVER 5 161.00 | 506932 | EUREKA 5 161.00 | 0 |  | 1 | 22SP | 236 | 247 | 0 |  | 94.9057 | 104.293 | [7 empty] | CATEGORYB | SINGLE | EROGERS7 345.00 - OSAGE CREEK 345KV CKT 1 | 0 | 506982 | EROGERS7 345.00 | 338683 | 7OSAGECK 345.00 | 0 |  | 1 |  |  |  | SWPA | BEAVER - EUREKA SPRINGS 161KV CKT 1 SWPA | Rebuild line using 1590MCM ACSR conductor on tubular steel H-frame structures. Replace breakers and switches at Beaver. Remove wave traps. | 335 | 368 | 335 | 368 | 6 | 15 | 4 | [5 empty] | 4130000 | 2012-04-10 | [39 empty] | 2013-06-01 | 2016-06-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T15725522SP | FROM->TO | BEAVER - EUREKA SPRINGS 161KV CKT 1 | S | SWPA | AEPW | EMINTH | FAYETTEVILLE | 0 | 505480 | BEAVER 5 161.00 | 506932 | EUREKA 5 161.00 | 0 |  | 1 | 22SP | 236 | 247 | 0 |  | 94.7362 | 104.2907 | [7 empty] | CATEGORYB | SINGLE | OSAGE CREEK 345/161KV TRANSFORMER CKT 2 | 0 | 338682 | 5OSAGE # 161.00 | 338683 | 7OSAGECK 345.00 | 0 |  | 2 |  |  |  | AEPW | BEAVER - EUREKA SPRINGS 161KV CKT 1 AEPW | Rebuild 1.25 miles of 795 ACSR with 1590 ACSR. Replace wavetrap & jumpers @ Eureka Springs | 318 | 438 | 422 | 502 | 1.25 | 24 | 6 |  | 0.00032 | 0.003398 | 0.00196 | Ratings are for AEP equipment only. New limit is the switch @ Eureka Springs. | 2635665.7431 | 2012-04-12 | [39 empty] | 2013-06-01 | 2016-06-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T15725522SP | FROM->TO | BEAVER - EUREKA SPRINGS 161KV CKT 1 | S | SWPA | AEPW | EMINTH | FAYETTEVILLE | 0 | 505480 | BEAVER 5 161.00 | 506932 | EUREKA 5 161.00 | 0 |  | 1 | 22SP | 236 | 247 | 0 |  | 94.7362 | 104.2907 | [7 empty] | CATEGORYB | SINGLE | OSAGE CREEK 345/161KV TRANSFORMER CKT 2 | 0 | 338682 | 5OSAGE # 161.00 | 338683 | 7OSAGECK 345.00 | 0 |  | 2 |  |  |  | SWPA | BEAVER - EUREKA SPRINGS 161KV CKT 1 SWPA | Rebuild line using 1590MCM ACSR conductor on tubular steel H-frame structures. Replace breakers and switches at Beaver. Remove wave traps. | 335 | 368 | 335 | 368 | 6 | 15 | 4 | [5 empty] | 4130000 | 2012-04-10 | [39 empty] | 2013-06-01 | 2016-06-01
2005-AG2 | [10 empty] | BEELINE - EXPLORER GLENPOOL 138KV CKT 1 | U | OKGE | OKGE |  |  | 0 | 515248 | EXPLGLN4 138 | 515247 | BEELINE4 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | OKGE | BEELINE - EXPLORER GLENPOOL 138KV CKT 1 | Reconductor .92miles of line with Drake ACCC/TW. | [53 empty] | 2009-06-01 | 2009-06-01
2011-AGP1 | AFS9-14 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3125514SP | TO->FROM | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 | REL | GMO | GMO |  |  | 0 | 541206 | PRALEE 5 161.00 | 541211 | BLSPS 5 161.00 | 0 |  | 1 | 17SP | 224 | 224 | 224 | 96.9 | 96.8874 | 101.0181 | [7 empty] | CATEGORYB | SINGLE | PLEASANT HILL - SIBLEY 345KV CKT 1 | 0 | 541200 | PHILL 7 345.00 | 541201 | SIBLEY 7 345.00 | 0 |  | 1 |  |  |  | MIPU | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #1 | Upgrade Prairie Lee wave trap to 2000 Amps. | 228 | 259 |  |  |  | 18 | 6 | [5 empty] | 19775 | 2012-03-29 | [39 empty] | 2014-06-01 | 2015-06-01
2011-AGP1 | AFS9 | SPP_FG-5331 - PRABLURSSEXG | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T1515022SP | TO->FROM | BLUEBELL - PRATTVILLE 138KV CKT 1 | REL | AEPW | OKGE | PSO_TULSA | MUSKOGEE | 0 | 509758 | PRATTV-4 138.00 | 515242 | BLUEBEL4 138.00 | 0 |  | 1 | 22SP | 212 | 212 | 0 | 100.8 | 100.7734 | 100.1015 | [7 empty] | CATEGORYB | SINGLE | EXPLORER GLENPOOL - RIVERSIDE STATION 138KV CKT 1 | 0 | 509783 | R.S.S.-4 138.00 | 515248 | EXPLGLN4 138.00 | 0 |  | 1 |  |  |  | AEPW | BLUEBELL - PRATTVILLE 138KV CKT 1 | Rebuild 9.0 mile Prattville-Bluebell 138 kV line from 795 ACSR to 1590 ACSR. Replace line switch near Prattville. New summer ratings 287/287 limited by breaker, switches, CTs, wave trap. | [12 empty] | 8764620.57 | 2011-11-15 | [39 empty] | 2018-06-01 | 2018-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T10365513SP | FROM->TO | BROOKLINE (BRKLTX1) 345/161/13.2KV TRANSFORMER CKT 1 | REL | SPRM | SPRM | SPRM > 69KV | SPRM > 69KV | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549988 | BRKLNE XF1 113.200 | 1 | 13SP | 400 | 400 | 0 | 100.8 | 100.8494 | 104.1593 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE (BRKLTX2) 345/161/13.2KV TRANSFORMER CKT 2 | 1 | 549969 | BROOKLINE 5161.00 | 549984 | BROOKLINE 7345.00 | 549989 | BRKLNE XF2 113.200 | 2 |  |  |  | SPRM | Brookline – Compton Ridge 345 kV SPRM | Build approx. 30 mile 345 kV line | [5 empty] | 60 | 60 | [46 empty] | 2013-06-01 | 2019-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T10365513SP | FROM->TO | BROOKLINE (BRKLTX1) 345/161/13.2KV TRANSFORMER CKT 1 | REL | SPRM | SPRM | SPRM > 69KV | SPRM > 69KV | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549988 | BRKLNE XF1 113.200 | 1 | 13SP | 400 | 400 | 0 | 100.8 | 100.8494 | 104.1593 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE (BRKLTX2) 345/161/13.2KV TRANSFORMER CKT 2 | 1 | 549969 | BROOKLINE 5161.00 | 549984 | BROOKLINE 7345.00 | 549989 | BRKLNE XF2 113.200 | 2 |  |  |  | EMDE | Brookline – Compton Ridge 345 kV EMDE | Build approx. 50% of 30 mile 345 kV line | [5 empty] | 60 | 60 | [46 empty] | 2013-06-01 | 2019-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T10365513SP | FROM->TO | BROOKLINE (BRKLTX1) 345/161/13.2KV TRANSFORMER CKT 1 | REL | SPRM | SPRM | SPRM > 69KV | SPRM > 69KV | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549988 | BRKLNE XF1 113.200 | 1 | 13SP | 400 | 400 | 0 | 100.8 | 100.8494 | 104.1593 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE (BRKLTX2) 345/161/13.2KV TRANSFORMER CKT 2 | 1 | 549969 | BROOKLINE 5161.00 | 549984 | BROOKLINE 7345.00 | 549989 | BRKLNE XF2 113.200 | 2 |  |  |  | EMDE | Compton Ridge 345/161 kV Transformer | Install 500 MVA, 345/161 kV transformer and Cut EDE Reeds Spring‐ Branson line at 50% and route in & out of Compton Ridge | [5 empty] | 60 | 60 | [46 empty] | 2013-06-01 | 2019-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T23305522SP | FROM->TO | BROOKLINE (BRKLTX1) 345/161/13.2KV TRANSFORMER CKT 1 | REL | SPRM | SPRM | SPRM > 69KV | SPRM > 69KV | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549988 | BRKLNE XF1 113.200 | 1 | 22SP | 400 | 400 | 0 | 100.4 | 100.434 | 104.0014 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE (BRKLTX2) 345/161/13.2KV TRANSFORMER CKT 2 | 1 | 549969 | BROOKLINE 5161.00 | 549984 | BROOKLINE 7345.00 | 549989 | BRKLNE XF2 113.200 | 2 |  |  |  | SPRM | Brookline – Compton Ridge 345 kV SPRM | Build approx. 30 mile 345 kV line | [5 empty] | 60 | 60 | [46 empty] | 2013-06-01 | 2019-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T23305522SP | FROM->TO | BROOKLINE (BRKLTX1) 345/161/13.2KV TRANSFORMER CKT 1 | REL | SPRM | SPRM | SPRM > 69KV | SPRM > 69KV | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549988 | BRKLNE XF1 113.200 | 1 | 22SP | 400 | 400 | 0 | 100.4 | 100.434 | 104.0014 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE (BRKLTX2) 345/161/13.2KV TRANSFORMER CKT 2 | 1 | 549969 | BROOKLINE 5161.00 | 549984 | BROOKLINE 7345.00 | 549989 | BRKLNE XF2 113.200 | 2 |  |  |  | EMDE | Brookline – Compton Ridge 345 kV EMDE | Build approx. 50% of 30 mile 345 kV line | [5 empty] | 60 | 60 | [46 empty] | 2013-06-01 | 2019-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T23305522SP | FROM->TO | BROOKLINE (BRKLTX1) 345/161/13.2KV TRANSFORMER CKT 1 | REL | SPRM | SPRM | SPRM > 69KV | SPRM > 69KV | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549988 | BRKLNE XF1 113.200 | 1 | 22SP | 400 | 400 | 0 | 100.4 | 100.434 | 104.0014 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE (BRKLTX2) 345/161/13.2KV TRANSFORMER CKT 2 | 1 | 549969 | BROOKLINE 5161.00 | 549984 | BROOKLINE 7345.00 | 549989 | BRKLNE XF2 113.200 | 2 |  |  |  | EMDE | Compton Ridge 345/161 kV Transformer | Install 500 MVA, 345/161 kV transformer and Cut EDE Reeds Spring‐ Branson line at 50% and route in & out of Compton Ridge | [5 empty] | 60 | 60 | [46 empty] | 2013-06-01 | 2019-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T10345513SP | FROM->TO | BROOKLINE (BRKLTX2) 345/161/13.2KV TRANSFORMER CKT 2 | REL | SPRM | SPRM | SPRM > 69KV | SPRM > 69KV | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549989 | BRKLNE XF2 113.200 | 2 | 13SP | 400 | 400 | 0 | 100.5 | 100.5471 | 103.8442 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE (BRKLTX1) 345/161/13.2KV TRANSFORMER CKT 1 | 1 | 549969 | BROOKLINE 5161.00 | 549984 | BROOKLINE 7345.00 | 549988 | BRKLNE XF1 113.200 | 1 |  |  |  | SPRM | Brookline – Compton Ridge 345 kV SPRM | Build approx. 30 mile 345 kV line | [5 empty] | 60 | 60 | [46 empty] | 2013-06-01 | 2019-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T10345513SP | FROM->TO | BROOKLINE (BRKLTX2) 345/161/13.2KV TRANSFORMER CKT 2 | REL | SPRM | SPRM | SPRM > 69KV | SPRM > 69KV | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549989 | BRKLNE XF2 113.200 | 2 | 13SP | 400 | 400 | 0 | 100.5 | 100.5471 | 103.8442 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE (BRKLTX1) 345/161/13.2KV TRANSFORMER CKT 1 | 1 | 549969 | BROOKLINE 5161.00 | 549984 | BROOKLINE 7345.00 | 549988 | BRKLNE XF1 113.200 | 1 |  |  |  | EMDE | Brookline – Compton Ridge 345 kV EMDE | Build approx. 50% of 30 mile 345 kV line | [5 empty] | 60 | 60 | [46 empty] | 2013-06-01 | 2019-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T10345513SP | FROM->TO | BROOKLINE (BRKLTX2) 345/161/13.2KV TRANSFORMER CKT 2 | REL | SPRM | SPRM | SPRM > 69KV | SPRM > 69KV | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549989 | BRKLNE XF2 113.200 | 2 | 13SP | 400 | 400 | 0 | 100.5 | 100.5471 | 103.8442 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE (BRKLTX1) 345/161/13.2KV TRANSFORMER CKT 1 | 1 | 549969 | BROOKLINE 5161.00 | 549984 | BROOKLINE 7345.00 | 549988 | BRKLNE XF1 113.200 | 1 |  |  |  | EMDE | Compton Ridge 345/161 kV Transformer | Install 500 MVA, 345/161 kV transformer and Cut EDE Reeds Spring‐ Branson line at 50% and route in & out of Compton Ridge | [5 empty] | 60 | 60 | [46 empty] | 2013-06-01 | 2019-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T23285522SP | FROM->TO | BROOKLINE (BRKLTX2) 345/161/13.2KV TRANSFORMER CKT 2 | REL | SPRM | SPRM | SPRM > 69KV | SPRM > 69KV | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549989 | BRKLNE XF2 113.200 | 2 | 22SP | 400 | 400 | 0 | 100.1 | 100.1306 | 103.6869 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE (BRKLTX1) 345/161/13.2KV TRANSFORMER CKT 1 | 1 | 549969 | BROOKLINE 5161.00 | 549984 | BROOKLINE 7345.00 | 549988 | BRKLNE XF1 113.200 | 1 |  |  |  | SPRM | Brookline – Compton Ridge 345 kV SPRM | Build approx. 30 mile 345 kV line | [5 empty] | 60 | 60 | [46 empty] | 2013-06-01 | 2019-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T23285522SP | FROM->TO | BROOKLINE (BRKLTX2) 345/161/13.2KV TRANSFORMER CKT 2 | REL | SPRM | SPRM | SPRM > 69KV | SPRM > 69KV | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549989 | BRKLNE XF2 113.200 | 2 | 22SP | 400 | 400 | 0 | 100.1 | 100.1306 | 103.6869 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE (BRKLTX1) 345/161/13.2KV TRANSFORMER CKT 1 | 1 | 549969 | BROOKLINE 5161.00 | 549984 | BROOKLINE 7345.00 | 549988 | BRKLNE XF1 113.200 | 1 |  |  |  | EMDE | Brookline – Compton Ridge 345 kV EMDE | Build approx. 50% of 30 mile 345 kV line | [5 empty] | 60 | 60 | [46 empty] | 2013-06-01 | 2019-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T23285522SP | FROM->TO | BROOKLINE (BRKLTX2) 345/161/13.2KV TRANSFORMER CKT 2 | REL | SPRM | SPRM | SPRM > 69KV | SPRM > 69KV | 1 | 549984 | BROOKLINE 7345.00 | 549969 | BROOKLINE 5161.00 | 549989 | BRKLNE XF2 113.200 | 2 | 22SP | 400 | 400 | 0 | 100.1 | 100.1306 | 103.6869 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE (BRKLTX1) 345/161/13.2KV TRANSFORMER CKT 1 | 1 | 549969 | BROOKLINE 5161.00 | 549984 | BROOKLINE 7345.00 | 549988 | BRKLNE XF1 113.200 | 1 |  |  |  | EMDE | Compton Ridge 345/161 kV Transformer | Install 500 MVA, 345/161 kV transformer and Cut EDE Reeds Spring‐ Branson line at 50% and route in & out of Compton Ridge | [5 empty] | 60 | 60 | [46 empty] | 2013-06-01 | 2019-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T965513WP | FROM->TO | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | EXP | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | 13WP | 329 | 360 | 0 | 105.4 | 105.4103 | 106.2321 | [7 empty] | CATEGORYB | SINGLE | PLANT X STATION - POTTER COUNTY INTERCHANGE 230KV CKT 1 | 0 | 523959 | POTTER_CO 6230.00 | 525481 | PLANT_X 6230.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T965513WP | FROM->TO | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | EXP | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | 13WP | 329 | 360 | 0 | 105.4 | 105.4103 | 106.2321 | [7 empty] | CATEGORYB | SINGLE | PLANT X STATION - POTTER COUNTY INTERCHANGE 230KV CKT 1 | 0 | 523959 | POTTER_CO 6230.00 | 525481 | PLANT_X 6230.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T965513WP | FROM->TO | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | EXP | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | 13WP | 329 | 360 | 0 | 105.4 | 105.4103 | 106.2321 | [7 empty] | CATEGORYB | SINGLE | PLANT X STATION - POTTER COUNTY INTERCHANGE 230KV CKT 1 | 0 | 523959 | POTTER_CO 6230.00 | 525481 | PLANT_X 6230.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T965513WP | FROM->TO | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | EXP | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | 13WP | 329 | 360 | 0 | 105.4 | 105.4103 | 106.2321 | [7 empty] | CATEGORYB | SINGLE | PLANT X STATION - POTTER COUNTY INTERCHANGE 230KV CKT 1 | 0 | 523959 | POTTER_CO 6230.00 | 525481 | PLANT_X 6230.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGE's Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T725512SP | TO->FROM | CANTON - TALOGA 69KV CKT 1 | CP | WFEC | WFEC | AEP-OP |  | 0 | 521064 | TALOGA 2 69.000 | 520843 | CANTON-2 69.000 | 0 |  | 1 | 12SP | 33 | 39 | 39 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | WFEC | CANTON - TALOGA 69KV CKT 1 | UPGRADE CANTON TO TALOGA TO 336.4 | 106 | 132 |  |  | 9.7 | 24 | 24 |  | 0.04013 | 0.16101 | 0.00252 | [42 empty] | 2013-06-01 | 2013-06-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T725512WP | TO->FROM | CANTON - TALOGA 69KV CKT 1 | CP | WFEC | WFEC | AEP-OP |  | 0 | 521064 | TALOGA 2 69.000 | 520843 | CANTON-2 69.000 | 0 |  | 1 | 12WP | 42 | 46 | 46 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | WFEC | CANTON - TALOGA 69KV CKT 1 | UPGRADE CANTON TO TALOGA TO 336.4 | 106 | 132 |  |  | 9.7 | 24 | 24 |  | 0.04013 | 0.16101 | 0.00252 | [42 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS5 | [9 empty] | CANTON - TALOGA 69KV CKT 1 | U | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521064 | TALOGA 2 69.000 | 520843 | CANTON-2 69.000 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | WFEC | CANTON - TALOGA 69KV CKT 1 | UPGRADE CANTON TO TALOGA TO 336.4 | 106 | 132 |  |  | 9.7 | 24 | 24 |  | 0.04013 | 0.16101 | 0.00252 | [42 empty] | 2011-06-01 | 2013-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T21745522SP | FROM->TO | CHAVES COUNTY INTERCHANGE (GE M102125) 230/115/13.2KV TRANSFORMER CKT 2 | EXP | SPS | SPS | SPS-PECO | SPS-PECO | 1 | 527483 | CHAVES_CNTY6230.00 | 527482 | CHAVES_CNTY3115.00 | 527479 | CHAVES_TR2 113.200 | 2 | 22SP | 149 | 171 | 0 | 102.1 | 102.1442 | 101.813 | [7 empty] | CATEGORYB | SINGLE | CHAVES COUNTY INTERCHANGE (ABB 801429) 230/115/13.2KV TRANSFORMER CKT 1 | 1 | 527482 | CHAVES_CNTY3115.00 | 527483 | CHAVES_CNTY6230.00 | 527478 | CHAVES_TR1 113.200 | 1 |  |  |  | SPS | CHAVES COUNTY INTERCHANGE 230/115KV TRANSFORMER CKT 2 | Upgrade Chaves 230/115 kV to 225/258 MVA. |  | 258 |  |  |  | 24 | 24 | [46 empty] | 2020-06-01 | 2020-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T21745522SP | FROM->TO | CHAVES COUNTY INTERCHANGE (GE M102125) 230/115/13.2KV TRANSFORMER CKT 2 | REL | SPS | SPS | SPS-PECO | SPS-PECO | 1 | 527483 | CHAVES_CNTY6230.00 | 527482 | CHAVES_CNTY3115.00 | 527479 | CHAVES_TR2 113.200 | 2 | 22SP | 149 | 171 | 0 | 102.1 | 102.1442 | 101.813 | [7 empty] | CATEGORYB | SINGLE | CHAVES COUNTY INTERCHANGE (ABB 801429) 230/115/13.2KV TRANSFORMER CKT 1 | 1 | 527482 | CHAVES_CNTY3115.00 | 527483 | CHAVES_CNTY6230.00 | 527478 | CHAVES_TR1 113.200 | 1 |  |  |  | SPS | CHAVES COUNTY INTERCHANGE - SAMSON SUB 115KV CKT 1 | Reconductor 7.78 miles of Chaves - Sampson 115 kV | [53 empty] | 2020-06-01 | 2020-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T21745522SP | FROM->TO | CHAVES COUNTY INTERCHANGE (GE M102125) 230/115/13.2KV TRANSFORMER CKT 2 | REL | SPS | SPS | SPS-PECO | SPS-PECO | 1 | 527483 | CHAVES_CNTY6230.00 | 527482 | CHAVES_CNTY3115.00 | 527479 | CHAVES_TR2 113.200 | 2 | 22SP | 149 | 171 | 0 | 102.1 | 102.1442 | 101.813 | [7 empty] | CATEGORYB | SINGLE | CHAVES COUNTY INTERCHANGE (ABB 801429) 230/115/13.2KV TRANSFORMER CKT 1 | 1 | 527482 | CHAVES_CNTY3115.00 | 527483 | CHAVES_CNTY6230.00 | 527478 | CHAVES_TR1 113.200 | 1 |  |  |  | SPS | CHAVES COUNTY INTERCHANGE - URTON SUB 115KV CKT 1 | Reconductor 3.70 miles of Chaves - Urton 115 kV | [53 empty] | 2020-06-01 | 2020-06-01
2009-AGP1 | [10 empty] | CHERRY6 230.00 - Harrington Station East Bus 230KV CKT 1 | U | SPS | SPS | SPS-AMA |  | 0 | 523977 |  | 524010 |  | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | SPS | CHERRY6 230.00 - Harrington Station East Bus 230KV CKT 1 | Replace wavetrap at Harrington East | [53 empty] | 2015-06-01 | 2015-06-01
GI | [10 empty] | CIRCLE - RICE_CO 230KV CKT 1 | U | WERE | MIDW |  |  | 0 | 560012 | RICECO 230.00 | 532871 | CIRCLE 6 230.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | MIDW | CIRCLE - RICE_CO 230KV CKT 1 | Convert from 115kV to 230kV operation | [53 empty] | 2012-10-01 | 2012-11-15
2011-AGP1 | AFS9-CCP |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9CCP1T725517SP | FROM->TO | CLARKCO - G11-008 345KV CKT 1 | EXP | SUNC | SUNC |  | SPS-MUNI | 0 | 560688 | G11-008 | 539800 | CLARKCO 7 | 0 |  | 1 | 17SP | 100 | 100 | 100 |  | 999 | 999 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-CCP |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9CCP1T725517SP | FROM->TO | CLARKCO - G11-008 345KV CKT 1 | EXP | SUNC | SUNC |  | SPS-MUNI | 0 | 560688 | G11-008 | 539800 | CLARKCO 7 | 0 |  | 1 | 17SP | 100 | 100 | 100 |  | 999 | 999 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9-CCP |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9CCP1T725517SP | FROM->TO | CLARKCO - G11-008 345KV CKT 1 | EXP | SUNC | SUNC |  | SPS-MUNI | 0 | 560688 | G11-008 | 539800 | CLARKCO 7 | 0 |  | 1 | 17SP | 100 | 100 | 100 |  | 999 | 999 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9-CCP |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9CCP1T725517SP | FROM->TO | CLARKCO - G11-008 345KV CKT 1 | EXP | SUNC | SUNC |  | SPS-MUNI | 0 | 560688 | G11-008 | 539800 | CLARKCO 7 | 0 |  | 1 | 17SP | 100 | 100 | 100 |  | 999 | 999 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-CCP |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9CCP1T725517SP | FROM->TO | CLARKCO - G11-008 345KV CKT 1 | EXP | SUNC | SUNC |  | SPS-MUNI | 0 | 560688 | G11-008 | 539800 | CLARKCO 7 | 0 |  | 1 | 17SP | 100 | 100 | 100 |  | 999 | 999 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-CCP |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9CCP1T725517SP | FROM->TO | CLARKCO - G11-008 345KV CKT 1 | EXP | SUNC | SUNC |  | SPS-MUNI | 0 | 560688 | G11-008 | 539800 | CLARKCO 7 | 0 |  | 1 | 17SP | 100 | 100 | 100 |  | 999 | 999 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-CCP |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9CCP1T725517SP | FROM->TO | CLARKCO - G11-008 345KV CKT 1 | EXP | SUNC | SUNC |  | SPS-MUNI | 0 | 560688 | G11-008 | 539800 | CLARKCO 7 | 0 |  | 1 | 17SP | 100 | 100 | 100 |  | 999 | 999 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-CCP |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9CCP1T725517SP | FROM->TO | CLARKCO - G11-008 345KV CKT 1 | EXP | SUNC | SUNC |  | SPS-MUNI | 0 | 560688 | G11-008 | 539800 | CLARKCO 7 | 0 |  | 1 | 17SP | 100 | 100 | 100 |  | 999 | 999 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-CCP |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9CCP1T725517SP | FROM->TO | CLARKCO - G11-008 345KV CKT 1 | EXP | SUNC | SUNC |  | SPS-MUNI | 0 | 560688 | G11-008 | 539800 | CLARKCO 7 | 0 |  | 1 | 17SP | 100 | 100 | 100 |  | 999 | 999 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9-CCP |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9CCP1T725517SP | FROM->TO | CLARKCO - G11-008 345KV CKT 1 | EXP | SUNC | SUNC |  | SPS-MUNI | 0 | 560688 | G11-008 | 539800 | CLARKCO 7 | 0 |  | 1 | 17SP | 100 | 100 | 100 |  | 999 | 999 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGE's Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9-CCP |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9CCP1T725517SP | FROM->TO | CLARKCO - G11-008 345KV CKT 1 | EXP | SUNC | SUNC |  | SPS-MUNI | 0 | 560688 | G11-008 | 539800 | CLARKCO 7 | 0 |  | 1 | 17SP | 100 | 100 | 100 |  | 999 | 999 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1655513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 100 | 100 | 0 | 98 | 98.0175 | 125.9 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1655513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 100 | 100 | 0 | 98 | 98.0175 | 125.9 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1655513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 100 | 100 | 0 | 98 | 98.0175 | 125.9 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1655513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 100 | 100 | 0 | 98 | 98.0175 | 125.9 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGE's Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1635513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 100 | 100 | 0 | 96.9 | 96.885 | 124.7043 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1635513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 100 | 100 | 0 | 96.9 | 96.885 | 124.7043 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1635513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 100 | 100 | 0 | 96.9 | 96.885 | 124.7043 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1635513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 100 | 100 | 0 | 96.9 | 96.885 | 124.7043 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGE's Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1675513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 100 | 100 | 0 | 95.3 | 95.3174 | 123.2855 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1675513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 100 | 100 | 0 | 95.3 | 95.3174 | 123.2855 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1675513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 100 | 100 | 0 | 95.3 | 95.3174 | 123.2855 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1675513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 100 | 100 | 0 | 95.3 | 95.3174 | 123.2855 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGE's Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2012-06-01 | 2014-06-01
2007-AG3 | AFS7 | [9 empty] | CLIFTON - GREENLEAF 115KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539656 | CLIFTON3 115.00 | 539665 | GRNLEAF3 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | MKEC | CLIFTON - GREENLEAF 115KV CKT 1 | Rebuild 14.4 miles | [53 empty] | 2011-06-01 | 2013-06-01
2007-AG3 | AFS9 | [9 empty] | DEARING 138KV | U | WERE |  | SEAST |  |  | 533002 | DEARING4 138.00 | [20 empty] | BASECASE | BASE CASE | [11 empty] | WERE | DEARING 138KV Capacitor | Dearing 138 kV 20 MVAR Capacitor Addition | [53 empty] | 2012-06-01 | 2012-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1825513WP | FROM->TO | EASTOWN7 345.00 (EASTOWN 345) 345/161/13.8KV TRANSFORMER CKT 1 | EXP | GMO | GMO |  |  | 1 | 541400 | EASTOWN7 345.00 | 541401 | EASTWON5 161.00 | 541402 | EASTOWN1 13.800 | 1 | 13WP | 400 | 440 | 0 | 102.5 | 102.4928 | 100.8775 | [7 empty] | CATEGORYB | SINGLE | EASTOWN7 345.00 - ST JOE 345KV CKT 1 | 0 | 541199 | ST JOE 3 345.00 | 541400 | EASTOWN7 345.00 | 0 |  | 1 |  |  |  | KACP | IATAN - NASHUA 345KV CKT 1 | Tap Nashua 345kV bus in Hawthorn - St. Joseph 345 kV line. Build new 345 kV line from Iatan to Nashua,Add Nashua 345/161 kV | [53 empty] | 2012-10-01 | 2015-06-01
2011-AGP1 | AFS9-14 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3105514SP | FROM->TO | EASTOWN7 345.00 (EASTOWN 345) 345/161/13.8KV TRANSFORMER CKT 1 | EXP | GMO | GMO |  |  | 2 | 541400 | EASTOWN7 345.00 | 541401 | EASTWON5 161.00 | 541402 | EASTOWN1 13.800 | 1 | 17SP | 400 | 440 | 0 | 98.2 | 98.2403 | 102.029 | [7 empty] | CATEGORYB | SINGLE | EASTOWN7 345.00 - ST JOE 345KV CKT 1 | 0 | 541199 | ST JOE 3 345.00 | 541400 | EASTOWN7 345.00 | 0 |  | 1 |  |  |  | KACP | IATAN - NASHUA 345KV CKT 1 | Tap Nashua 345kV bus in Hawthorn - St. Joseph 345 kV line. Build new 345 kV line from Iatan to Nashua,Add Nashua 345/161 kV | [53 empty] | 2012-10-01 | 2015-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1185512WP | TO->FROM | EDWARDSVILLE - MUND 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533282 | MUND 3 115.00 | 533238 | EDWARVL3 115.00 | 0 |  | 1 | 12WP | 179 | 179 | 0 | 100.1 | 100.1088 | 101.545 | [7 empty] | CATEGORYB | SINGLE | 87th STREET - CRAIG 345KV CKT 1 | 0 | 532775 | 87TH 7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  |  |  | KACP | IATAN - NASHUA 345KV CKT 1 | Tap Nashua 345kV bus in Hawthorn - St. Joseph 345 kV line. Build new 345 kV line from Iatan to Nashua,Add Nashua 345/161 kV | [53 empty] | 2012-10-01 | 2015-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1325513WP | TO->FROM | EDWARDSVILLE - MUND 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533282 | MUND 3 115.00 | 533238 | EDWARVL3 115.00 | 0 |  | 1 | 13WP | 179 | 179 | 0 | 101.3 | 101.2705 | 103.6215 | [7 empty] | CATEGORYB | SINGLE | 87th STREET - CRAIG 345KV CKT 1 | 0 | 532775 | 87TH 7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  |  |  | KACP | IATAN - NASHUA 345KV CKT 1 | Tap Nashua 345kV bus in Hawthorn - St. Joseph 345 kV line. Build new 345 kV line from Iatan to Nashua,Add Nashua 345/161 kV | [53 empty] | 2012-10-01 | 2015-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2535522SP | FROM->TO | EL PASO - FARBER 138KV CKT 1 | CP | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 | 22SP | 160 | 168 | 0 | 100.4 | 100.4281 | 100.9951 | [7 empty] | CATEGORYB | SINGLE | KILDARE4 - WHITE EAGLE 138KV CKT 1 | 0 | 514760 | KILDARE4 138.00 | 514761 | WHEAGLE4 138.00 | 0 |  | 1 |  |  |  | WERE | EL PASO - FARBER 138KV CKT 1 | Tear down / Rebuild 3.1 miles with dual 477 ACSR | 286 | 286 | 286 | 286 | 3.1 | 24 | 24 |  | 0.001395 | 0.01178 | 0.00372 | [42 empty] | 2018-06-01 | 2018-06-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985512SP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 12SP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985512SP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 12SP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985512SP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 12SP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985512SP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 12SP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985512SP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 12SP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985512SP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 12SP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985512SP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 12SP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985512SP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 12SP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985512SP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 12SP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985512SP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 12SP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGE's Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985512SP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 12SP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985512WP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 12WP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985512WP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 12WP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985512WP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 12WP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985512WP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 12WP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985512WP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 12WP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985512WP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 12WP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985512WP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 12WP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985512WP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 12WP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985512WP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 12WP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985512WP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 12WP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGE's Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985512WP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 12WP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985513SP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 13SP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985513SP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 13SP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985513SP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 13SP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985513SP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 13SP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985513SP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 13SP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985513SP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 13SP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985513SP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 13SP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985513SP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 13SP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985513SP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 13SP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985513SP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 13SP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGE's Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985513SP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 13SP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985513WP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 13WP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985513WP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 13WP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985513WP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 13WP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985513WP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 13WP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985513WP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 13WP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985513WP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 13WP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985513WP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 13WP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985513WP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 13WP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985513WP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 13WP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985513WP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 13WP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGE's Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T1985513WP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 13WP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2012-06-01 | 2015-01-01
2005-AG2 | [10 empty] | EXPLORER GLENPOOL - RIVERSIDE STATION 138KV CKT 1 AEPW | U | AEPW | OKGE |  |  | 0 | 509783 | R.S.S.-4 138 | 515248 | EXPLGLN4 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | AEPW | EXPLORER GLENPOOL - RIVERSIDE STATION 138KV CKT 1 AEPW | Reconductor 1.82 miles with ACCC. Replace wave trap jumpers at Riverside. | [53 empty] | 2009-06-01 | 2009-06-01
2005-AG2 | [10 empty] | EXPLORER GLENPOOL - RIVERSIDE STATION 138KV CKT 1 OKGE | U | AEPW | OKGE |  |  | 0 | 509783 | R.S.S.-4 138 | 515248 | EXPLGLN4 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | OKGE | EXPLORER GLENPOOL - RIVERSIDE STATION 138KV CKT 1 OKGE | Reconductor 1.82 miles line with Drake ACCC/TW. | [53 empty] | 2009-06-01 | 2009-06-01
2007-AG3 | AFS7 | [9 empty] | FLATRDG3 138.00 - MEDICINE LODGE 138KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539674 | MED-LDG4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | MKEC | FLATRDG3 138.00 - MEDICINE LODGE 138KV CKT 1 | Rebuild 8.05 mile line | [53 empty] | 2009-12-01 | 2013-06-01
2007-AG3 | AFS7 | [9 empty] | FLATRDG3 138.00 - HARPER 138KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 |  |  | 24.15 | 24 | 24 | [46 empty] | 2009-12-01 | 2013-06-15
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1765512WP | FROM->TO | FLATRDG3 - HARPER 138KV CKT 1 | CP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 12WP | 100 | 100 | 100 | 103.7 | 103.6568 | 126.6617 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 |  |  | 24.15 | 36 | 36 | [46 empty] | 2012-10-01 | 2013-06-15
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1735512WP | FROM->TO | FLATRDG3 - HARPER 138KV CKT 1 | CP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 12WP | 100 | 100 | 100 | 102.7 | 102.7212 | 125.7273 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 |  |  | 24.15 | 36 | 36 | [46 empty] | 2012-10-01 | 2013-06-15
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1795512WP | FROM->TO | FLATRDG3 - HARPER 138KV CKT 1 | CP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 12WP | 100 | 100 | 100 | 102.7 | 102.7307 | 124.7994 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 |  |  | 24.15 | 36 | 36 | [46 empty] | 2012-10-01 | 2013-06-15
2011-AGP1 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1555512WP | FROM->TO | FLATRDG3 - HARPER 138KV CKT 1 | CP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 12WP | 100 | 100 | 100 |  | 87.5857 | 100.8188 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 |  |  | 24.15 | 36 | 36 | [46 empty] | 2012-10-01 | 2013-06-15
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T7585512WP | FROM->TO | FLATRDG3 - HARPER 138KV CKT 1 | CP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 12WP | 100 | 100 | 100 |  | 86.5904 | 100.0569 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-32 | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 |  |  | 24.15 | 36 | 36 | [46 empty] | 2012-10-01 | 2013-06-15
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005512SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 12SP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005512SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 12SP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005512SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 12SP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005512SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 12SP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005512SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 12SP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005512SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 12SP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005512SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 12SP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005512SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 12SP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005512SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 12SP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005512SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 12SP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGE's Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005512SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 12SP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005512WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 12WP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005512WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 12WP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005512WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 12WP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005512WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 12WP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005512WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 12WP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005512WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 12WP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005512WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 12WP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005512WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 12WP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005512WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 12WP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005512WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 12WP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGE's Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005512WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 12WP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005513SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005513SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005513SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005513SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005513SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005513SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005513SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005513SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005513SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005513SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGE's Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005513SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005513WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 13WP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005513WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 13WP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005513WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 13WP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005513WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 13WP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005513WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 13WP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005513WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 13WP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005513WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 13WP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005513WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 13WP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005513WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 13WP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005513WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 13WP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGE's Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2005513WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 13WP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2012-06-01 | 2015-01-01
GEN | [10 empty] | FT RANDAL - MADISONCO 230.00 230KV CKT 1 | U | NPPD | WAPA | NPPD_686 | WAPA_1604 | 0 | 560006 | MADISONCO 230.00 | 652509 | FTRANDL4 230.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | NPPD | FT RANDAL - MADISONCO 230.00 230KV CKT 1 | Raise structures and line clearances as necessary to re-rate the transmission line to 320MVA | [53 empty] | 2013-10-01 | 2014-11-01
2006-AG1 | 2006-AG1 | [9 empty] | FT SUPPLY 138/69KV TRANSFORMER CKT 1 | U | WFEC | WFEC |  |  | 1 | 520920 | FTSUPLY4 138 | 520919 | FTSUPLY269.0 | 521182 |  | 2 | [15 empty] | BASECASE | BASE CASE | [11 empty] | WFEC | FT SUPPLY 138/69KV TRANSFORMER CKT 1 | Install 2nd 70 MVA auto at Ft Supply | [53 empty] | 2006-12-01 | 2008-06-01
2009-AGP1 | [10 empty] | G03-05T 138.00 - PARADISE 138KV CKT 1 | U | WFEC | WFEC | AEP-OP-I | AEP-KP | 0 | 521129 | G03-05T 138.00 | 521024 | PARADSE4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | WFEC | G03-05T 138.00 - PARADISE 138KV CKT 1 | Upgrade Paradise to G03-05T to 1113 | [53 empty] | 2010-06-01 | 2013-06-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2015512SP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | CP | WFEC | OKGE | ENID |  | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 12SP | 152 | 152 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Mathewson - Tatonga 345 kV Ckt 1 | Build new 61 mile Tatonga - Mathewson 345 kV line. | [53 empty] | 2013-06-01 | 2019-06-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T685512WP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | CP | WFEC | OKGE | ENID |  | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 12WP | 152 | 152 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Mathewson - Tatonga 345 kV Ckt 1 | Build new 61 mile Tatonga - Mathewson 345 kV line. | [53 empty] | 2013-06-01 | 2019-06-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2015513SP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | CP | WFEC | OKGE | ENID |  | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 13SP | 152 | 152 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Mathewson - Tatonga 345 kV Ckt 1 | Build new 61 mile Tatonga - Mathewson 345 kV line. | [53 empty] | 2013-06-01 | 2019-06-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T685513WP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | CP | WFEC | OKGE | ENID |  | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 13WP | 152 | 152 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Mathewson - Tatonga 345 kV Ckt 1 | Build new 61 mile Tatonga - Mathewson 345 kV line. | [53 empty] | 2013-06-01 | 2019-06-01
GEN | [10 empty] | GRACMNT4 138.00 - WASHITA 138KV CKT 2 OKGE | U | WFEC | OKGE | AEP-CS | ARDMORE | 0 | 521089 | WASHITA4 138.00 | 515802 | GRACMNT4 138.00 | 0 |  | 2 | [15 empty] | BASECASE | BASE CASE | [11 empty] | OKGE | GRACMNT4 138.00 - WASHITA 138KV CKT 2 OKGE | Build 138kV Terminal. | [53 empty] | 2012-01-01 | 2012-01-01
GEN | [10 empty] | GRACMNT4 138.00 - WASHITA 138KV CKT 2 WFEC | U | WFEC | OKGE | AEP-CS | ARDMORE | 0 | 521089 | WASHITA4 138.00 | 515802 | GRACMNT4 138.00 | 0 |  | 2 | [15 empty] | BASECASE | BASE CASE | [11 empty] | WFEC | GRACMNT4 138.00 - WASHITA 138KV CKT 2 WFEC | Build approximately 6 miles of 138kV. | [53 empty] | 2012-01-01 | 2012-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1605517WP | TO->FROM | GRAND ISLAND - SWEETWATER 345KV CKT 1 | REL | NPPD | NPPD | NPPD_686 | WAPA_1606 | 0 | 640374 | SWEET W3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 | 17WP | 717 | 717 | 789 |  | 90.9424 | 101.9156 | [7 empty] | CATEGORYB | SINGLE | AXTELL - SWEETWATER 345KV CKT 1 | 0 | 640065 | AXTELL 3 345.00 | 640374 | SWEET W3 345.00 | 0 |  | 1 |  |  |  | NPPD | Cherry Co - Gentleman 345 kV Ckt1 | Build new 345 kV Transmission Line from GGS 345 kV Substation to a new Cherry County 345 kV Substation (76 miles). | [5 empty] | 72 | 72 | [46 empty] | 2014-10-01 | 2018-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1605517WP | TO->FROM | GRAND ISLAND - SWEETWATER 345KV CKT 1 | REL | NPPD | NPPD | NPPD_686 | WAPA_1606 | 0 | 640374 | SWEET W3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 | 17WP | 717 | 717 | 789 |  | 90.9424 | 101.9156 | [7 empty] | CATEGORYB | SINGLE | AXTELL - SWEETWATER 345KV CKT 1 | 0 | 640065 | AXTELL 3 345.00 | 640374 | SWEET W3 345.00 | 0 |  | 1 |  |  |  | NPPD | Cherry Co - Holt Co 345 kV Ckt1 | Build new 345 kV Transmission Line from new Cherry County 345 kV Substation to new 345 kV Holt County Substation. (Estimated 146 miles). | [5 empty] | 72 | [47 empty] | 2014-10-01 | 2018-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1605517WP | TO->FROM | GRAND ISLAND - SWEETWATER 345KV CKT 1 | REL | NPPD | NPPD | NPPD_686 | WAPA_1606 | 0 | 640374 | SWEET W3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 | 17WP | 717 | 717 | 789 |  | 90.9424 | 101.9156 | [7 empty] | CATEGORYB | SINGLE | AXTELL - SWEETWATER 345KV CKT 1 | 0 | 640065 | AXTELL 3 345.00 | 640374 | SWEET W3 345.00 | 0 |  | 1 |  |  |  | NPPD | Cherry Co 345 kV Terminal Upgrades | Build new Cherry County 345 kV Substation. | [5 empty] | 72 | [47 empty] | 2014-10-01 | 2018-01-01
2008-AGP1 | AFS6 | [9 empty] | GREENLEAF - KNOB HILL 115KV CKT 1 | U | SUNC | WERE |  | NCENTRAL | 0 | 539665 | GRNLEAF3 115.00 | 533332 | KNOB HL3 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | MKEC | GREENLEAF - KNOB HILL 115KV CKT 1 MKEC | Rebuild 43.5% Ownership of 20.9 miles | [53 empty] | 2013-06-01 | 2013-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1775512WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 12WP | 95.6 | 95.6 | 0 | 96.8 | 96.7986 | 113.5852 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 Accelerate | Replace Wave Trap at Harper Substation |  | 100 |  |  |  | 18 | 18 | [5 empty] | 225000 | 2011-01-01 | [38 empty] | 2020-03-01 | 2012-10-01 | 2015-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1775512WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 12WP | 95.6 | 95.6 | 0 | 96.8 | 96.7986 | 113.5852 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1775512WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 12WP | 95.6 | 95.6 | 0 | 96.8 | 96.7986 | 113.5852 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1775512WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 12WP | 95.6 | 95.6 | 0 | 96.8 | 96.7986 | 113.5852 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1775512WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 12WP | 95.6 | 95.6 | 0 | 96.8 | 96.7986 | 113.5852 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1775512WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 12WP | 95.6 | 95.6 | 0 | 96.8 | 96.7986 | 113.5852 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1775512WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 12WP | 95.6 | 95.6 | 0 | 96.8 | 96.7986 | 113.5852 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1775512WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 12WP | 95.6 | 95.6 | 0 | 96.8 | 96.7986 | 113.5852 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1775512WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 12WP | 95.6 | 95.6 | 0 | 96.8 | 96.7986 | 113.5852 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1775512WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 12WP | 95.6 | 95.6 | 0 | 96.8 | 96.7986 | 113.5852 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1775512WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 12WP | 95.6 | 95.6 | 0 | 96.8 | 96.7986 | 113.5852 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGE's Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1775512WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 12WP | 95.6 | 95.6 | 0 | 96.8 | 96.7986 | 113.5852 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1745512WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 12WP | 95.6 | 95.6 | 0 | 95.8 | 95.8048 | 112.6265 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 Accelerate | Replace Wave Trap at Harper Substation |  | 100 |  |  |  | 18 | 18 | [5 empty] | 225000 | 2011-01-01 | [38 empty] | 2020-03-01 | 2012-10-01 | 2015-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1745512WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 12WP | 95.6 | 95.6 | 0 | 95.8 | 95.8048 | 112.6265 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1745512WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 12WP | 95.6 | 95.6 | 0 | 95.8 | 95.8048 | 112.6265 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1745512WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 12WP | 95.6 | 95.6 | 0 | 95.8 | 95.8048 | 112.6265 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1745512WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 12WP | 95.6 | 95.6 | 0 | 95.8 | 95.8048 | 112.6265 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1745512WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 12WP | 95.6 | 95.6 | 0 | 95.8 | 95.8048 | 112.6265 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1745512WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 12WP | 95.6 | 95.6 | 0 | 95.8 | 95.8048 | 112.6265 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1745512WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 12WP | 95.6 | 95.6 | 0 | 95.8 | 95.8048 | 112.6265 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1745512WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 12WP | 95.6 | 95.6 | 0 | 95.8 | 95.8048 | 112.6265 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1745512WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 12WP | 95.6 | 95.6 | 0 | 95.8 | 95.8048 | 112.6265 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1745512WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 12WP | 95.6 | 95.6 | 0 | 95.8 | 95.8048 | 112.6265 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGE's Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1745512WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 12WP | 95.6 | 95.6 | 0 | 95.8 | 95.8048 | 112.6265 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1805512WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 12WP | 95.6 | 95.6 | 0 | 95.8 | 95.7984 | 111.871 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 Accelerate | Replace Wave Trap at Harper Substation |  | 100 |  |  |  | 18 | 18 | [5 empty] | 225000 | 2011-01-01 | [38 empty] | 2020-03-01 | 2012-10-01 | 2015-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1805512WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 12WP | 95.6 | 95.6 | 0 | 95.8 | 95.7984 | 111.871 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1805512WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 12WP | 95.6 | 95.6 | 0 | 95.8 | 95.7984 | 111.871 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1805512WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 12WP | 95.6 | 95.6 | 0 | 95.8 | 95.7984 | 111.871 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1805512WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 12WP | 95.6 | 95.6 | 0 | 95.8 | 95.7984 | 111.871 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1805512WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 12WP | 95.6 | 95.6 | 0 | 95.8 | 95.7984 | 111.871 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1805512WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 12WP | 95.6 | 95.6 | 0 | 95.8 | 95.7984 | 111.871 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1805512WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 12WP | 95.6 | 95.6 | 0 | 95.8 | 95.7984 | 111.871 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1805512WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 12WP | 95.6 | 95.6 | 0 | 95.8 | 95.7984 | 111.871 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1805512WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 12WP | 95.6 | 95.6 | 0 | 95.8 | 95.7984 | 111.871 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1805512WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 12WP | 95.6 | 95.6 | 0 | 95.8 | 95.7984 | 111.871 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGE's Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1805512WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 12WP | 95.6 | 95.6 | 0 | 95.8 | 95.7984 | 111.871 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3485513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 |  | 92.3861 | 112.7262 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 Accelerate | Replace Wave Trap at Harper Substation |  | 100 |  |  |  | 18 | 18 | [5 empty] | 225000 | 2011-01-01 | [38 empty] | 2020-03-01 | 2012-10-01 | 2015-06-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3485513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 |  | 92.3861 | 112.7262 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3485513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 |  | 92.3861 | 112.7262 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3485513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 |  | 92.3861 | 112.7262 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3485513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 |  | 92.3861 | 112.7262 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3485513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 |  | 92.3861 | 112.7262 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3485513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 |  | 92.3861 | 112.7262 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3485513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 |  | 92.3861 | 112.7262 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3485513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 |  | 92.3861 | 112.7262 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3485513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 |  | 92.3861 | 112.7262 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3485513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 |  | 92.3861 | 112.7262 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGE's Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3485513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 |  | 92.3861 | 112.7262 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3465513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 |  | 90.8464 | 111.1879 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 Accelerate | Replace Wave Trap at Harper Substation |  | 100 |  |  |  | 18 | 18 | [5 empty] | 225000 | 2011-01-01 | [38 empty] | 2020-03-01 | 2012-10-01 | 2015-06-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3465513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 |  | 90.8464 | 111.1879 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3465513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 |  | 90.8464 | 111.1879 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3465513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 |  | 90.8464 | 111.1879 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3465513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 |  | 90.8464 | 111.1879 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3465513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 |  | 90.8464 | 111.1879 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3465513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 |  | 90.8464 | 111.1879 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3465513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 |  | 90.8464 | 111.1879 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3465513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 |  | 90.8464 | 111.1879 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3465513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 |  | 90.8464 | 111.1879 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3465513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 |  | 90.8464 | 111.1879 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGE's Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3465513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 |  | 90.8464 | 111.1879 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3495513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 |  | 89.0502 | 109.6343 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 Accelerate | Replace Wave Trap at Harper Substation |  | 100 |  |  |  | 18 | 18 | [5 empty] | 225000 | 2011-01-01 | [38 empty] | 2020-03-01 | 2012-10-01 | 2015-06-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3495513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 |  | 89.0502 | 109.6343 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3495513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 |  | 89.0502 | 109.6343 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3495513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 |  | 89.0502 | 109.6343 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3495513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 |  | 89.0502 | 109.6343 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3495513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 |  | 89.0502 | 109.6343 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3495513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 |  | 89.0502 | 109.6343 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3495513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 |  | 89.0502 | 109.6343 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3495513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 |  | 89.0502 | 109.6343 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3495513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 |  | 89.0502 | 109.6343 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3495513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 |  | 89.0502 | 109.6343 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGE's Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3495513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 |  | 89.0502 | 109.6343 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1665513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 111 | 111.0245 | 140.1073 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 Accelerate | Replace Wave Trap at Harper Substation |  | 100 |  |  |  | 18 | 18 | [5 empty] | 225000 | 2011-01-01 | [38 empty] | 2020-03-01 | 2012-10-01 | 2015-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1665513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 111 | 111.0245 | 140.1073 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1665513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 111 | 111.0245 | 140.1073 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1665513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 111 | 111.0245 | 140.1073 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1665513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 111 | 111.0245 | 140.1073 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1665513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 111 | 111.0245 | 140.1073 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1665513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 111 | 111.0245 | 140.1073 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1665513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 111 | 111.0245 | 140.1073 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1665513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 111 | 111.0245 | 140.1073 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1665513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 111 | 111.0245 | 140.1073 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1665513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 111 | 111.0245 | 140.1073 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGE's Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1665513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 111 | 111.0245 | 140.1073 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1645513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 109.8 | 109.8478 | 138.8693 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 Accelerate | Replace Wave Trap at Harper Substation |  | 100 |  |  |  | 18 | 18 | [5 empty] | 225000 | 2011-01-01 | [38 empty] | 2020-03-01 | 2012-10-01 | 2015-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1645513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 109.8 | 109.8478 | 138.8693 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1645513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 109.8 | 109.8478 | 138.8693 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1645513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 109.8 | 109.8478 | 138.8693 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1645513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 109.8 | 109.8478 | 138.8693 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1645513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 109.8 | 109.8478 | 138.8693 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1645513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 109.8 | 109.8478 | 138.8693 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1645513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 109.8 | 109.8478 | 138.8693 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1645513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 109.8 | 109.8478 | 138.8693 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1645513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 109.8 | 109.8478 | 138.8693 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1645513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 109.8 | 109.8478 | 138.8693 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGE's Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1645513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 109.8 | 109.8478 | 138.8693 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1685513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 108.4 | 108.3944 | 137.5294 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 Accelerate | Replace Wave Trap at Harper Substation |  | 100 |  |  |  | 18 | 18 | [5 empty] | 225000 | 2011-01-01 | [38 empty] | 2020-03-01 | 2012-10-01 | 2015-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1685513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 108.4 | 108.3944 | 137.5294 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1685513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 108.4 | 108.3944 | 137.5294 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1685513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 108.4 | 108.3944 | 137.5294 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1685513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 108.4 | 108.3944 | 137.5294 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1685513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 108.4 | 108.3944 | 137.5294 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1685513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 108.4 | 108.3944 | 137.5294 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1685513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 108.4 | 108.3944 | 137.5294 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1685513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 108.4 | 108.3944 | 137.5294 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1685513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 108.4 | 108.3944 | 137.5294 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1685513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 108.4 | 108.3944 | 137.5294 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGE's Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1685513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 108.4 | 108.3944 | 137.5294 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8725513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 95.6 | 95.5774 | 113.5633 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 Accelerate | Replace Wave Trap at Harper Substation |  | 100 |  |  |  | 18 | 18 | [5 empty] | 225000 | 2011-01-01 | [38 empty] | 2020-03-01 | 2012-10-01 | 2015-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8725513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 95.6 | 95.5774 | 113.5633 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8725513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 95.6 | 95.5774 | 113.5633 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8725513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 95.6 | 95.5774 | 113.5633 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8725513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 95.6 | 95.5774 | 113.5633 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8725513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 95.6 | 95.5774 | 113.5633 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8725513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 95.6 | 95.5774 | 113.5633 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8725513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 95.6 | 95.5774 | 113.5633 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8725513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 95.6 | 95.5774 | 113.5633 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8725513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 95.6 | 95.5774 | 113.5633 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8725513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 95.6 | 95.5774 | 113.5633 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGE's Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8725513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 | 95.6 | 95.5774 | 113.5633 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8695513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 92.9569 | 110.8497 | [7 empty] | CATEGORYB | NONSINGLE | MIDW-CATB05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 Accelerate | Replace Wave Trap at Harper Substation |  | 100 |  |  |  | 18 | 18 | [5 empty] | 225000 | 2011-01-01 | [38 empty] | 2020-03-01 | 2012-10-01 | 2015-06-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8695513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 92.9569 | 110.8497 | [7 empty] | CATEGORYB | NONSINGLE | MIDW-CATB05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8695513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 92.9569 | 110.8497 | [7 empty] | CATEGORYB | NONSINGLE | MIDW-CATB05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8695513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 92.9569 | 110.8497 | [7 empty] | CATEGORYB | NONSINGLE | MIDW-CATB05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8695513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 92.9569 | 110.8497 | [7 empty] | CATEGORYB | NONSINGLE | MIDW-CATB05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8695513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 92.9569 | 110.8497 | [7 empty] | CATEGORYB | NONSINGLE | MIDW-CATB05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8695513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 92.9569 | 110.8497 | [7 empty] | CATEGORYB | NONSINGLE | MIDW-CATB05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8695513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 92.9569 | 110.8497 | [7 empty] | CATEGORYB | NONSINGLE | MIDW-CATB05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8695513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 92.9569 | 110.8497 | [7 empty] | CATEGORYB | NONSINGLE | MIDW-CATB05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8695513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 92.9569 | 110.8497 | [7 empty] | CATEGORYB | NONSINGLE | MIDW-CATB05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8695513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 92.9569 | 110.8497 | [7 empty] | CATEGORYB | NONSINGLE | MIDW-CATB05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGE's Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8695513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 92.9569 | 110.8497 | [7 empty] | CATEGORYB | NONSINGLE | MIDW-CATB05 | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8755513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 90.7586 | 110.4078 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WEPL-01 | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 Accelerate | Replace Wave Trap at Harper Substation |  | 100 |  |  |  | 18 | 18 | [5 empty] | 225000 | 2011-01-01 | [38 empty] | 2020-03-01 | 2012-10-01 | 2015-06-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8755513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 90.7586 | 110.4078 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WEPL-01 | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8755513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 90.7586 | 110.4078 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WEPL-01 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8755513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 90.7586 | 110.4078 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WEPL-01 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8755513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 90.7586 | 110.4078 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WEPL-01 | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8755513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 90.7586 | 110.4078 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WEPL-01 | 0 | 0 |  | 0 |  | 0 | [5 empty] | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8755513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 90.7586 | 110.4078 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WEPL-01 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8755513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 90.7586 | 110.4078 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WEPL-01 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8755513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 90.7586 | 110.4078 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WEPL-01 | 0 | 0 |  | 0 |  | 0 | [5 empty] | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8755513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 90.7586 | 110.4078 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WEPL-01 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8755513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 90.7586 | 110.4078 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WEPL-01 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGE's Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8755513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 90.7586 | 110.4078 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WEPL-01 | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T45513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 88.6736 | 106.8152 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 Accelerate | Replace Wave Trap at Harper Substation |  | 100 |  |  |  | 18 | 18 | [5 empty] | 225000 | 2011-01-01 | [38 empty] | 2020-03-01 | 2012-10-01 | 2015-06-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T45513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 88.6736 | 106.8152 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T45513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 88.6736 | 106.8152 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T45513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 88.6736 | 106.8152 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T45513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 88.6736 | 106.8152 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T45513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 88.6736 | 106.8152 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T45513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 88.6736 | 106.8152 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T45513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 88.6736 | 106.8152 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T45513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 88.6736 | 106.8152 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T45513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 88.6736 | 106.8152 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T45513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 88.6736 | 106.8152 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGE's Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T45513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 88.6736 | 106.8152 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 | CONT-1213 - Circle - Hutchinson |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1495513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 85.8273 | 103.7737 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | 0 | 533413 | CIRCLE 3 115.00 | 533419 | HEC 3 115.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 Accelerate | Replace Wave Trap at Harper Substation |  | 100 |  |  |  | 18 | 18 | [5 empty] | 225000 | 2011-01-01 | [38 empty] | 2020-03-01 | 2012-10-01 | 2015-06-01
2011-AGP1 | AFS9 | CONT-1213 - Circle - Hutchinson |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1495513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 85.8273 | 103.7737 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | 0 | 533413 | CIRCLE 3 115.00 | 533419 | HEC 3 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 | CONT-1213 - Circle - Hutchinson |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1495513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 85.8273 | 103.7737 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | 0 | 533413 | CIRCLE 3 115.00 | 533419 | HEC 3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9 | CONT-1213 - Circle - Hutchinson |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1495513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 85.8273 | 103.7737 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | 0 | 533413 | CIRCLE 3 115.00 | 533419 | HEC 3 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9 | CONT-1213 - Circle - Hutchinson |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1495513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 85.8273 | 103.7737 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | 0 | 533413 | CIRCLE 3 115.00 | 533419 | HEC 3 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 | CONT-1213 - Circle - Hutchinson |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1495513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 85.8273 | 103.7737 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | 0 | 533413 | CIRCLE 3 115.00 | 533419 | HEC 3 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 | CONT-1213 - Circle - Hutchinson |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1495513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 85.8273 | 103.7737 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | 0 | 533413 | CIRCLE 3 115.00 | 533419 | HEC 3 115.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 | CONT-1213 - Circle - Hutchinson |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1495513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 85.8273 | 103.7737 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | 0 | 533413 | CIRCLE 3 115.00 | 533419 | HEC 3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 | CONT-1213 - Circle - Hutchinson |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1495513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 85.8273 | 103.7737 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | 0 | 533413 | CIRCLE 3 115.00 | 533419 | HEC 3 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 | CONT-1213 - Circle - Hutchinson |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1495513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 85.8273 | 103.7737 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | 0 | 533413 | CIRCLE 3 115.00 | 533419 | HEC 3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9 | CONT-1213 - Circle - Hutchinson |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1495513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 85.8273 | 103.7737 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | 0 | 533413 | CIRCLE 3 115.00 | 533419 | HEC 3 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGE's Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9 | CONT-1213 - Circle - Hutchinson |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1495513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 85.8273 | 103.7737 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | 0 | 533413 | CIRCLE 3 115.00 | 533419 | HEC 3 115.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 | CONT-LaCygne West Gardner 345kv |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1865513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 84.7156 | 102.701 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 Accelerate | Replace Wave Trap at Harper Substation |  | 100 |  |  |  | 18 | 18 | [5 empty] | 225000 | 2011-01-01 | [38 empty] | 2020-03-01 | 2012-10-01 | 2015-06-01
2011-AGP1 | AFS9 | CONT-LaCygne West Gardner 345kv |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1865513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 84.7156 | 102.701 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 | CONT-LaCygne West Gardner 345kv |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1865513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 84.7156 | 102.701 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9 | CONT-LaCygne West Gardner 345kv |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1865513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 84.7156 | 102.701 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9 | CONT-LaCygne West Gardner 345kv |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1865513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 84.7156 | 102.701 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 | CONT-LaCygne West Gardner 345kv |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1865513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 84.7156 | 102.701 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 | CONT-LaCygne West Gardner 345kv |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1865513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 84.7156 | 102.701 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 | CONT-LaCygne West Gardner 345kv |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1865513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 84.7156 | 102.701 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 | CONT-LaCygne West Gardner 345kv |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1865513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 84.7156 | 102.701 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 | CONT-LaCygne West Gardner 345kv |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1865513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 84.7156 | 102.701 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9 | CONT-LaCygne West Gardner 345kv |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1865513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 84.7156 | 102.701 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGE's Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9 | CONT-LaCygne West Gardner 345kv |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1865513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 84.7156 | 102.701 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3045514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 88.9131 | 113.8333 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 Accelerate | Replace Wave Trap at Harper Substation |  | 100 |  |  |  | 18 | 18 | [5 empty] | 225000 | 2011-01-01 | [38 empty] | 2020-03-01 | 2012-10-01 | 2015-06-01
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3045514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 88.9131 | 113.8333 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3045514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 88.9131 | 113.8333 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3045514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 88.9131 | 113.8333 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3045514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 88.9131 | 113.8333 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3045514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 88.9131 | 113.8333 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3045514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 88.9131 | 113.8333 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3045514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 88.9131 | 113.8333 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3045514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 88.9131 | 113.8333 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3045514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 88.9131 | 113.8333 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3045514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 88.9131 | 113.8333 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGE's Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3045514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 88.9131 | 113.8333 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3025514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 87.3471 | 112.1858 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 Accelerate | Replace Wave Trap at Harper Substation |  | 100 |  |  |  | 18 | 18 | [5 empty] | 225000 | 2011-01-01 | [38 empty] | 2020-03-01 | 2012-10-01 | 2015-06-01
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3025514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 87.3471 | 112.1858 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3025514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 87.3471 | 112.1858 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3025514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 87.3471 | 112.1858 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3025514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 87.3471 | 112.1858 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3025514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 87.3471 | 112.1858 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3025514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 87.3471 | 112.1858 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3025514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 87.3471 | 112.1858 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3025514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 87.3471 | 112.1858 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3025514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 87.3471 | 112.1858 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3025514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 87.3471 | 112.1858 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGE's Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3025514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 87.3471 | 112.1858 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3055514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 87.5461 | 110.8382 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 Accelerate | Replace Wave Trap at Harper Substation |  | 100 |  |  |  | 18 | 18 | [5 empty] | 225000 | 2011-01-01 | [38 empty] | 2020-03-01 | 2012-10-01 | 2015-06-01
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3055514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 87.5461 | 110.8382 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3055514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 87.5461 | 110.8382 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3055514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 87.5461 | 110.8382 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3055514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 87.5461 | 110.8382 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3055514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 87.5461 | 110.8382 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3055514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 87.5461 | 110.8382 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3055514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 87.5461 | 110.8382 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3055514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 87.5461 | 110.8382 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3055514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 87.5461 | 110.8382 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3055514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 87.5461 | 110.8382 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGE's Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3055514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 87.5461 | 110.8382 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1305517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 |  | 83.1084 | 107.7564 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 Accelerate | Replace Wave Trap at Harper Substation |  | 100 |  |  |  | 18 | 18 | [5 empty] | 225000 | 2011-01-01 | [38 empty] | 2020-03-01 | 2012-10-01 | 2015-06-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1305517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 |  | 83.1084 | 107.7564 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1305517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 |  | 83.1084 | 107.7564 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1305517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 |  | 83.1084 | 107.7564 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1305517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 |  | 83.1084 | 107.7564 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1305517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 |  | 83.1084 | 107.7564 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1305517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 |  | 83.1084 | 107.7564 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1305517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 |  | 83.1084 | 107.7564 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1305517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 |  | 83.1084 | 107.7564 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1305517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 |  | 83.1084 | 107.7564 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1305517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 |  | 83.1084 | 107.7564 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGE's Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1305517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 |  | 83.1084 | 107.7564 | [7 empty] | CATEGORYB | SINGLE | THISTLE 7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE 7 345.00 | 0 |  | 2 |  |  |  | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T13415517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 |  | 84.5392 | 104.0458 | [7 empty] | CATEGORYB | GENOUT | GEN532751 1-WOLF CREEK GENERATING STATION UNIT 1 | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 Accelerate | Replace Wave Trap at Harper Substation |  | 100 |  |  |  | 18 | 18 | [5 empty] | 225000 | 2011-01-01 | [38 empty] | 2020-03-01 | 2012-10-01 | 2015-06-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T13415517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 |  | 84.5392 | 104.0458 | [7 empty] | CATEGORYB | GENOUT | GEN532751 1-WOLF CREEK GENERATING STATION UNIT 1 | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T13415517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 |  | 84.5392 | 104.0458 | [7 empty] | CATEGORYB | GENOUT | GEN532751 1-WOLF CREEK GENERATING STATION UNIT 1 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T13415517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 |  | 84.5392 | 104.0458 | [7 empty] | CATEGORYB | GENOUT | GEN532751 1-WOLF CREEK GENERATING STATION UNIT 1 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2014-07-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T13415517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 |  | 84.5392 | 104.0458 | [7 empty] | CATEGORYB | GENOUT | GEN532751 1-WOLF CREEK GENERATING STATION UNIT 1 | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T13415517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 |  | 84.5392 | 104.0458 | [7 empty] | CATEGORYB | GENOUT | GEN532751 1-WOLF CREEK GENERATING STATION UNIT 1 | 0 | 0 |  | 0 |  | 0 | [5 empty] | PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T13415517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 |  | 84.5392 | 104.0458 | [7 empty] | CATEGORYB | GENOUT | GEN532751 1-WOLF CREEK GENERATING STATION UNIT 1 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | [53 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T13415517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 |  | 84.5392 | 104.0458 | [7 empty] | CATEGORYB | GENOUT | GEN532751 1-WOLF CREEK GENERATING STATION UNIT 1 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T13415517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 |  | 84.5392 | 104.0458 | [7 empty] | CATEGORYB | GENOUT | GEN532751 1-WOLF CREEK GENERATING STATION UNIT 1 | 0 | 0 |  | 0 |  | 0 | [5 empty] | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T13415517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 |  | 84.5392 | 104.0458 | [7 empty] | CATEGORYB | GENOUT | GEN532751 1-WOLF CREEK GENERATING STATION UNIT 1 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T13415517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 |  | 84.5392 | 104.0458 | [7 empty] | CATEGORYB | GENOUT | GEN532751 1-WOLF CREEK GENERATING STATION UNIT 1 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGE's Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T13415517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 |  | 84.5392 | 104.0458 | [7 empty] | CATEGORYB | GENOUT | GEN532751 1-WOLF CREEK GENERATING STATION UNIT 1 | 0 | 0 |  | 0 |  | 0 | [5 empty] | ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 400 | 400 | 400 | 400 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T9455513SP | TO->FROM | HAYS PLANT - SOUTH HAYS 115KV CKT 1 | S | MIDW | MIDW | REG E-IL | REG E-IL | 0 | 530553 | S HAYS 3 115.00 | 530562 | HAYS 3 115.00 | 0 |  | 1 | 13SP | 80 | 99 | 0 |  | 85.2154 | 116.2706 | [7 empty] | CATEGORYB | SINGLE | KNOLL 230 (KNOLL T1) 230/115/11.49KV TRANSFORMER CKT 1 | 1 | 530558 | KNOLL 6 230.00 | 530561 | KNOLL 3 115.00 | 530629 | KNLL1 1 11.490 | 1 |  |  |  | MIDW | HAYS PLANT - SOUTH HAYS 115KV CKT 1 #2 | Tear down and rebuild of exisiting South Hays - Hays Plant 115 kV line. Tentative plans include rebuilding on existing right-of-way with the possibility of re-routing a portion of the line to new right-of-way as necessary. | 164 | 199 | 164 | 199 |  | 24 | 24 | [5 empty] | 4734005.6233 | 2012-04-09 | [39 empty] | 2013-06-01 | 2016-06-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T14085517SP | TO->FROM | HAYS PLANT - SOUTH HAYS 115KV CKT 1 | S | MIDW | MIDW | REG E-IL | REG E-IL | 0 | 530553 | S HAYS 3 115.00 | 530562 | HAYS 3 115.00 | 0 |  | 1 | 17SP | 80 | 99 | 0 |  | 76.7205 | 109.1059 | [7 empty] | CATEGORYB | SINGLE | KNOLL 230 (KNOLL T1) 230/115/11.49KV TRANSFORMER CKT 1 | 1 | 530558 | KNOLL 6 230.00 | 530561 | KNOLL 3 115.00 | 530629 | KNLL1 1 11.490 | 1 |  |  |  | MIDW | HAYS PLANT - SOUTH HAYS 115KV CKT 1 #2 | Tear down and rebuild of exisiting South Hays - Hays Plant 115 kV line. Tentative plans include rebuilding on existing right-of-way with the possibility of re-routing a portion of the line to new right-of-way as necessary. | 164 | 199 | 164 | 199 |  | 24 | 24 | [5 empty] | 4734005.6233 | 2012-04-09 | [39 empty] | 2013-06-01 | 2016-06-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T21845522SP | TO->FROM | HAYS PLANT - SOUTH HAYS 115KV CKT 1 | S | MIDW | MIDW | REG E-IL | REG E-IL | 0 | 530553 | S HAYS 3 115.00 | 530562 | HAYS 3 115.00 | 0 |  | 1 | 22SP | 80 | 99 | 0 |  | 84.2301 | 114.384 | [7 empty] | CATEGORYB | SINGLE | KNOLL 230 (KNOLL T1) 230/115/11.49KV TRANSFORMER CKT 1 | 1 | 530558 | KNOLL 6 230.00 | 530561 | KNOLL 3 115.00 | 530629 | KNLL1 1 11.490 | 1 |  |  |  | MIDW | HAYS PLANT - SOUTH HAYS 115KV CKT 1 #2 | Tear down and rebuild of exisiting South Hays - Hays Plant 115 kV line. Tentative plans include rebuilding on existing right-of-way with the possibility of re-routing a portion of the line to new right-of-way as necessary. | 164 | 199 | 164 | 199 |  | 24 | 24 | [5 empty] | 4734005.6233 | 2012-04-09 | [39 empty] | 2013-06-01 | 2016-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3065522SP | FROM->TO | HITCHLAND INTERCHANGE (H TP80148301) 230/115/13.2KV TRANSFORMER CKT 1 | EXP | SPS | SPS | SPS-OKLA | SPS-OKLA | 1 | 523095 | HITCHLAND 6230.00 | 523093 | HITCHLAND 3115.00 | 523092 | HITCHLD_TR1113.200 | 1 | 22SP | 250 | 250 | 0 | 99 | 99.0457 | 100.812 | [7 empty] | CATEGORYB | SINGLE | OCHILTREE 230/115KV TRANSFORMER CKT 1 | 0 | 523154 | OCHILTREE 3115.00 | 523155 | OCHILTREE 6230.00 | 0 |  | 1 |  |  |  | SPS | HITCHLAND INTERCHANGE () 230/115/13.2KV TRANSFORMER CKT 2 | Add 2nd transformer | [53 empty] | 2021-06-01 | 2021-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3035522SP | FROM->TO | HITCHLAND INTERCHANGE (H TP80148301) 230/115/13.2KV TRANSFORMER CKT 1 | EXP | SPS | SPS | SPS-OKLA | SPS-OKLA | 1 | 523095 | HITCHLAND 6230.00 | 523093 | HITCHLAND 3115.00 | 523092 | HITCHLD_TR1113.200 | 1 | 22SP | 250 | 250 | 0 | 98.9 | 98.8798 | 100.6042 | [7 empty] | CATEGORYB | SINGLE | HITCHLAND INTERCHANGE - OCHILTREE 230KV CKT 1 | 0 | 523095 | HITCHLAND 6230.00 | 523155 | OCHILTREE 6230.00 | 0 |  | 1 |  |  |  | SPS | HITCHLAND INTERCHANGE () 230/115/13.2KV TRANSFORMER CKT 2 | Add 2nd transformer | [53 empty] | 2021-06-01 | 2021-06-01
2005-AG2 | 2005-AG2 | [9 empty] | HUGO POWER PLANT - VALLIANT 138KV CKT 1 | U | WFEC | AEPW |  |  | 0 | 521157 | HUGO PP4 138 | 510911 | VALIANT4 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | AEPW | HUGO POWER PLANT - VALLIANT 345 KV AEPW | Vallient 345 KV line terminal | [53 empty] | 2012-07-01 | 2012-07-01
2005-AG2 | 2005-AG2 | [9 empty] | HUGO POWER PLANT - VALLIANT 345KV CKT 1 AEPW | U | WFEC | AEPW |  |  | 0 | 521157 | HUGO PP4 138 | 510911 | VALIANT4 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | AEPW | HUGO POWER PLANT - VALLIANT 345KV CKT 1 AEPW | Vallient 345 KV line terminal | [53 empty] | 2012-07-01 | 2012-07-01
2005-AG2 | 2005-AG2 | [9 empty] | HUGO POWER PLANT - VALLIANT 345KV CKT 1 WFEC | U | WFEC | AEPW |  |  | 0 | 521157 | HUGO PP4 138 | 510911 | VALIANT4 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | WFEC | HUGO POWER PLANT - VALLIANT 345KV CKT 1 WFEC | New 19 miles 345 KV | [53 empty] | 2012-07-01 | 2012-07-01
2005-AG2 | 2005-AG2 | [9 empty] | HUGO POWER PLANT 345/138KV TRANSFORMER CKT 1 | U | WFEC | AEPW |  |  | 1 | 521157 | HUGO PP4 138 | 520948 | HUGO PP4 138.00 | 521189 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | WFEC | HUGO POWER PLANT 345/138KV TRANSFORMER CKT 1 | New 345/138 kv Auto | [53 empty] | 2012-07-01 | 2012-07-01
GEN | [10 empty] | KELLY - MADISONCO 230.00 230KV CKT 1 | U | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 560006 | MADISONCO 230.00 | 640133 | COLMBUS4 230.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | NPPD | KELLY - MADISONCO 230.00 230KV CKT 1 | Raise structures and line clearances as necessary to re-rate the transmission line to 320MVA | 320 | 320 |  |  |  | 24 | 24 | [5 empty] | 480000 | 2011-01-01 | [39 empty] | 2013-10-01 | 2014-11-01
2006-AG1 | 2006-AG1 | [9 empty] | KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1 | U | OKGE |  |  |  | 1 | 514795 | KNOBHIL4 138 | 514794 | KNOBHIL269.0 | 515732 | KNOBHIL113.2 | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | OKGE | KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1 | Replace bus tie with 100MVA transformer | [53 empty] | 2006-06-01 | 2008-06-01
NA | [10 empty] | LACYGNE - WEST GARDNER 345KV CKT 1 | U | KACP | KACP |  |  | 0 | 542981 | LACYGNE7 | 542965 | W.GRDNR7 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | KACP | LACYGNE - WEST GARDNER 345KV CKT 1 | KCPL Sponsored Project to Reconductor Line to be In-Service by 6/1/2006 | [53 empty] | 2006-06-01 | 2006-06-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1355512WP | TO->FROM | LYONS - RICE_CO 115KV CKT 1 | CP | MIDW | WERE | REG E-IL | REG E-IL | 0 | 530623 | RICE 3 115.00 | 530620 | LYONS 3 115.00 | 0 |  | 1 | 12WP | 100 | 100 | 0 |  | 17.0617 | 192.0444 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICECO 230.00 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 560012 | RICECO 230.00 | 0 |  | 1 |  |  |  | WERE | LYONS - WHEATLAND 115KV CKT 1 #1 | Replace CTs | [5 empty] | 24 | 24 | [46 empty] | 2012-10-01 | 2013-07-15
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1355512WP | TO->FROM | LYONS - RICE_CO 115KV CKT 1 | CP | MIDW | WERE | REG E-IL | REG E-IL | 0 | 530623 | RICE 3 115.00 | 530620 | LYONS 3 115.00 | 0 |  | 1 | 12WP | 100 | 100 | 0 |  | 17.0617 | 192.0444 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICECO 230.00 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 560012 | RICECO 230.00 | 0 |  | 1 |  |  |  | MIDW | CIRCLE - RICE_CO 230KV CKT 1 | Convert from 115kV to 230kV operation | [5 empty] | 24 | 24 | [46 empty] | 2012-10-01 | 2012-11-15
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1355512WP | TO->FROM | LYONS - RICE_CO 115KV CKT 1 | CP | MIDW | WERE | REG E-IL | REG E-IL | 0 | 530623 | RICE 3 115.00 | 530620 | LYONS 3 115.00 | 0 |  | 1 | 12WP | 100 | 100 | 0 |  | 17.0617 | 192.0444 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICECO 230.00 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 560012 | RICECO 230.00 | 0 |  | 1 |  |  |  | MIDW | LYONS - RICE_CO 115KV CKT 1 | Rebuild 11.7 mile line | [5 empty] | 24 | 24 | [46 empty] | 2012-10-01 | 2013-04-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1355512WP | TO->FROM | LYONS - RICE_CO 115KV CKT 1 | CP | MIDW | WERE | REG E-IL | REG E-IL | 0 | 530623 | RICE 3 115.00 | 530620 | LYONS 3 115.00 | 0 |  | 1 | 12WP | 100 | 100 | 0 |  | 17.0617 | 192.0444 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICECO 230.00 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 560012 | RICECO 230.00 | 0 |  | 1 |  |  |  | WERE | LYONS - WHEATLAND 115KV CKT 1 #2 | Rerate circuit to 1000 amps | [5 empty] | 12 | 12 | [46 empty] | 2012-10-01 | 2013-07-15
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1355512WP | TO->FROM | LYONS - RICE_CO 115KV CKT 1 | CP | MIDW | WERE | REG E-IL | REG E-IL | 0 | 530623 | RICE 3 115.00 | 530620 | LYONS 3 115.00 | 0 |  | 1 | 12WP | 100 | 100 | 0 |  | 17.0617 | 192.0444 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICECO 230.00 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 560012 | RICECO 230.00 | 0 |  | 1 |  |  |  | MIDW | RICE_CO 230/115KV TRANSFORMER CKT 1 | Add 230/115kV Transformer | [5 empty] | 24 | 24 | [46 empty] | 2012-10-01 | 2012-11-15
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3195513SP | TO->FROM | LYONS - RICE_CO 115KV CKT 1 | CP | MIDW | WERE | REG E-IL | REG E-IL | 0 | 530623 | RICE 3 115.00 | 530620 | LYONS 3 115.00 | 0 |  | 1 | 13SP | 100 | 100 | 0 |  | 26.7663 | 183.7151 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICECO 230.00 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 560012 | RICECO 230.00 | 0 |  | 1 |  |  |  | WERE | LYONS - WHEATLAND 115KV CKT 1 #1 | Replace CTs | [5 empty] | 24 | 24 | [46 empty] | 2012-10-01 | 2013-07-15
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3195513SP | TO->FROM | LYONS - RICE_CO 115KV CKT 1 | CP | MIDW | WERE | REG E-IL | REG E-IL | 0 | 530623 | RICE 3 115.00 | 530620 | LYONS 3 115.00 | 0 |  | 1 | 13SP | 100 | 100 | 0 |  | 26.7663 | 183.7151 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICECO 230.00 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 560012 | RICECO 230.00 | 0 |  | 1 |  |  |  | MIDW | CIRCLE - RICE_CO 230KV CKT 1 | Convert from 115kV to 230kV operation | [5 empty] | 24 | 24 | [46 empty] | 2012-10-01 | 2012-11-15
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3195513SP | TO->FROM | LYONS - RICE_CO 115KV CKT 1 | CP | MIDW | WERE | REG E-IL | REG E-IL | 0 | 530623 | RICE 3 115.00 | 530620 | LYONS 3 115.00 | 0 |  | 1 | 13SP | 100 | 100 | 0 |  | 26.7663 | 183.7151 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICECO 230.00 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 560012 | RICECO 230.00 | 0 |  | 1 |  |  |  | MIDW | LYONS - RICE_CO 115KV CKT 1 | Rebuild 11.7 mile line | [5 empty] | 24 | 24 | [46 empty] | 2012-10-01 | 2013-04-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3195513SP | TO->FROM | LYONS - RICE_CO 115KV CKT 1 | CP | MIDW | WERE | REG E-IL | REG E-IL | 0 | 530623 | RICE 3 115.00 | 530620 | LYONS 3 115.00 | 0 |  | 1 | 13SP | 100 | 100 | 0 |  | 26.7663 | 183.7151 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICECO 230.00 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 560012 | RICECO 230.00 | 0 |  | 1 |  |  |  | WERE | LYONS - WHEATLAND 115KV CKT 1 #2 | Rerate circuit to 1000 amps | [5 empty] | 12 | 12 | [46 empty] | 2012-10-01 | 2013-07-15
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3195513SP | TO->FROM | LYONS - RICE_CO 115KV CKT 1 | CP | MIDW | WERE | REG E-IL | REG E-IL | 0 | 530623 | RICE 3 115.00 | 530620 | LYONS 3 115.00 | 0 |  | 1 | 13SP | 100 | 100 | 0 |  | 26.7663 | 183.7151 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICECO 230.00 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 560012 | RICECO 230.00 | 0 |  | 1 |  |  |  | MIDW | RICE_CO 230/115KV TRANSFORMER CKT 1 | Add 230/115kV Transformer | [5 empty] | 24 | 24 | [46 empty] | 2012-10-01 | 2012-11-15
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1415513WP | TO->FROM | LYONS - RICE_CO 115KV CKT 1 | CP | MIDW | WERE | REG E-IL | REG E-IL | 0 | 530623 | RICE 3 115.00 | 530620 | LYONS 3 115.00 | 0 |  | 1 | 13WP | 100 | 100 | 0 |  | 17.4462 | 191.2848 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICECO 230.00 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 560012 | RICECO 230.00 | 0 |  | 1 |  |  |  | WERE | LYONS - WHEATLAND 115KV CKT 1 #1 | Replace CTs | [5 empty] | 24 | 24 | [46 empty] | 2012-10-01 | 2013-07-15
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1415513WP | TO->FROM | LYONS - RICE_CO 115KV CKT 1 | CP | MIDW | WERE | REG E-IL | REG E-IL | 0 | 530623 | RICE 3 115.00 | 530620 | LYONS 3 115.00 | 0 |  | 1 | 13WP | 100 | 100 | 0 |  | 17.4462 | 191.2848 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICECO 230.00 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 560012 | RICECO 230.00 | 0 |  | 1 |  |  |  | MIDW | CIRCLE - RICE_CO 230KV CKT 1 | Convert from 115kV to 230kV operation | [5 empty] | 24 | 24 | [46 empty] | 2012-10-01 | 2012-11-15
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1415513WP | TO->FROM | LYONS - RICE_CO 115KV CKT 1 | CP | MIDW | WERE | REG E-IL | REG E-IL | 0 | 530623 | RICE 3 115.00 | 530620 | LYONS 3 115.00 | 0 |  | 1 | 13WP | 100 | 100 | 0 |  | 17.4462 | 191.2848 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICECO 230.00 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 560012 | RICECO 230.00 | 0 |  | 1 |  |  |  | MIDW | LYONS - RICE_CO 115KV CKT 1 | Rebuild 11.7 mile line | [5 empty] | 24 | 24 | [46 empty] | 2012-10-01 | 2013-04-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1415513WP | TO->FROM | LYONS - RICE_CO 115KV CKT 1 | CP | MIDW | WERE | REG E-IL | REG E-IL | 0 | 530623 | RICE 3 115.00 | 530620 | LYONS 3 115.00 | 0 |  | 1 | 13WP | 100 | 100 | 0 |  | 17.4462 | 191.2848 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICECO 230.00 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 560012 | RICECO 230.00 | 0 |  | 1 |  |  |  | WERE | LYONS - WHEATLAND 115KV CKT 1 #2 | Rerate circuit to 1000 amps | [5 empty] | 12 | 12 | [46 empty] | 2012-10-01 | 2013-07-15
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1415513WP | TO->FROM | LYONS - RICE_CO 115KV CKT 1 | CP | MIDW | WERE | REG E-IL | REG E-IL | 0 | 530623 | RICE 3 115.00 | 530620 | LYONS 3 115.00 | 0 |  | 1 | 13WP | 100 | 100 | 0 |  | 17.4462 | 191.2848 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICECO 230.00 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 560012 | RICECO 230.00 | 0 |  | 1 |  |  |  | MIDW | RICE_CO 230/115KV TRANSFORMER CKT 1 | Add 230/115kV Transformer | [5 empty] | 24 | 24 | [46 empty] | 2012-10-01 | 2012-11-15
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2805517SP | TO->FROM | LYONS - RICE_CO 115KV CKT 1 | CP | MIDW | WERE | REG E-IL | REG E-IL | 0 | 530623 | RICE 3 115.00 | 530620 | LYONS 3 115.00 | 0 |  | 1 | 17SP | 100 | 100 | 0 |  | 29.9404 | 128.9643 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICECO 230.00 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 560012 | RICECO 230.00 | 0 |  | 1 |  |  |  | WERE | LYONS - WHEATLAND 115KV CKT 1 #1 | Replace CTs | [5 empty] | 24 | 24 | [46 empty] | 2012-10-01 | 2013-07-15
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2805517SP | TO->FROM | LYONS - RICE_CO 115KV CKT 1 | CP | MIDW | WERE | REG E-IL | REG E-IL | 0 | 530623 | RICE 3 115.00 | 530620 | LYONS 3 115.00 | 0 |  | 1 | 17SP | 100 | 100 | 0 |  | 29.9404 | 128.9643 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICECO 230.00 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 560012 | RICECO 230.00 | 0 |  | 1 |  |  |  | MIDW | CIRCLE - RICE_CO 230KV CKT 1 | Convert from 115kV to 230kV operation | [5 empty] | 24 | 24 | [46 empty] | 2012-10-01 | 2012-11-15
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2805517SP | TO->FROM | LYONS - RICE_CO 115KV CKT 1 | CP | MIDW | WERE | REG E-IL | REG E-IL | 0 | 530623 | RICE 3 115.00 | 530620 | LYONS 3 115.00 | 0 |  | 1 | 17SP | 100 | 100 | 0 |  | 29.9404 | 128.9643 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICECO 230.00 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 560012 | RICECO 230.00 | 0 |  | 1 |  |  |  | MIDW | LYONS - RICE_CO 115KV CKT 1 | Rebuild 11.7 mile line | [5 empty] | 24 | 24 | [46 empty] | 2012-10-01 | 2013-04-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2805517SP | TO->FROM | LYONS - RICE_CO 115KV CKT 1 | CP | MIDW | WERE | REG E-IL | REG E-IL | 0 | 530623 | RICE 3 115.00 | 530620 | LYONS 3 115.00 | 0 |  | 1 | 17SP | 100 | 100 | 0 |  | 29.9404 | 128.9643 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICECO 230.00 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 560012 | RICECO 230.00 | 0 |  | 1 |  |  |  | WERE | LYONS - WHEATLAND 115KV CKT 1 #2 | Rerate circuit to 1000 amps | [5 empty] | 12 | 12 | [46 empty] | 2012-10-01 | 2013-07-15
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2805517SP | TO->FROM | LYONS - RICE_CO 115KV CKT 1 | CP | MIDW | WERE | REG E-IL | REG E-IL | 0 | 530623 | RICE 3 115.00 | 530620 | LYONS 3 115.00 | 0 |  | 1 | 17SP | 100 | 100 | 0 |  | 29.9404 | 128.9643 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICECO 230.00 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 560012 | RICECO 230.00 | 0 |  | 1 |  |  |  | MIDW | RICE_CO 230/115KV TRANSFORMER CKT 1 | Add 230/115kV Transformer | [5 empty] | 24 | 24 | [46 empty] | 2012-10-01 | 2012-11-15
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1345517WP | TO->FROM | LYONS - RICE_CO 115KV CKT 1 | CP | MIDW | WERE | REG E-IL | REG E-IL | 0 | 530623 | RICE 3 115.00 | 530620 | LYONS 3 115.00 | 0 |  | 1 | 17WP | 100 | 100 | 0 |  | 16.1388 | 138.8864 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICECO 230.00 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 560012 | RICECO 230.00 | 0 |  | 1 |  |  |  | WERE | LYONS - WHEATLAND 115KV CKT 1 #1 | Replace CTs | [5 empty] | 24 | 24 | [46 empty] | 2012-10-01 | 2013-07-15
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1345517WP | TO->FROM | LYONS - RICE_CO 115KV CKT 1 | CP | MIDW | WERE | REG E-IL | REG E-IL | 0 | 530623 | RICE 3 115.00 | 530620 | LYONS 3 115.00 | 0 |  | 1 | 17WP | 100 | 100 | 0 |  | 16.1388 | 138.8864 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICECO 230.00 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 560012 | RICECO 230.00 | 0 |  | 1 |  |  |  | MIDW | CIRCLE - RICE_CO 230KV CKT 1 | Convert from 115kV to 230kV operation | [5 empty] | 24 | 24 | [46 empty] | 2012-10-01 | 2012-11-15
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1345517WP | TO->FROM | LYONS - RICE_CO 115KV CKT 1 | CP | MIDW | WERE | REG E-IL | REG E-IL | 0 | 530623 | RICE 3 115.00 | 530620 | LYONS 3 115.00 | 0 |  | 1 | 17WP | 100 | 100 | 0 |  | 16.1388 | 138.8864 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICECO 230.00 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 560012 | RICECO 230.00 | 0 |  | 1 |  |  |  | MIDW | LYONS - RICE_CO 115KV CKT 1 | Rebuild 11.7 mile line | [5 empty] | 24 | 24 | [46 empty] | 2012-10-01 | 2013-04-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1345517WP | TO->FROM | LYONS - RICE_CO 115KV CKT 1 | CP | MIDW | WERE | REG E-IL | REG E-IL | 0 | 530623 | RICE 3 115.00 | 530620 | LYONS 3 115.00 | 0 |  | 1 | 17WP | 100 | 100 | 0 |  | 16.1388 | 138.8864 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICECO 230.00 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 560012 | RICECO 230.00 | 0 |  | 1 |  |  |  | WERE | LYONS - WHEATLAND 115KV CKT 1 #2 | Rerate circuit to 1000 amps | [5 empty] | 12 | 12 | [46 empty] | 2012-10-01 | 2013-07-15
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1345517WP | TO->FROM | LYONS - RICE_CO 115KV CKT 1 | CP | MIDW | WERE | REG E-IL | REG E-IL | 0 | 530623 | RICE 3 115.00 | 530620 | LYONS 3 115.00 | 0 |  | 1 | 17WP | 100 | 100 | 0 |  | 16.1388 | 138.8864 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICECO 230.00 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 560012 | RICECO 230.00 | 0 |  | 1 |  |  |  | MIDW | RICE_CO 230/115KV TRANSFORMER CKT 1 | Add 230/115kV Transformer | [5 empty] | 24 | 24 | [46 empty] | 2012-10-01 | 2012-11-15
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3985522SP | TO->FROM | LYONS - RICE_CO 115KV CKT 1 | CP | MIDW | WERE | REG E-IL | REG E-IL | 0 | 530623 | RICE 3 115.00 | 530620 | LYONS 3 115.00 | 0 |  | 1 | 22SP | 100 | 100 | 0 |  | 32.3655 | 126.9282 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICECO 230.00 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 560012 | RICECO 230.00 | 0 |  | 1 |  |  |  | WERE | LYONS - WHEATLAND 115KV CKT 1 #1 | Replace CTs | [5 empty] | 24 | 24 | [46 empty] | 2012-10-01 | 2013-07-15
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3985522SP | TO->FROM | LYONS - RICE_CO 115KV CKT 1 | CP | MIDW | WERE | REG E-IL | REG E-IL | 0 | 530623 | RICE 3 115.00 | 530620 | LYONS 3 115.00 | 0 |  | 1 | 22SP | 100 | 100 | 0 |  | 32.3655 | 126.9282 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICECO 230.00 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 560012 | RICECO 230.00 | 0 |  | 1 |  |  |  | MIDW | CIRCLE - RICE_CO 230KV CKT 1 | Convert from 115kV to 230kV operation | [5 empty] | 24 | 24 | [46 empty] | 2012-10-01 | 2012-11-15
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3985522SP | TO->FROM | LYONS - RICE_CO 115KV CKT 1 | CP | MIDW | WERE | REG E-IL | REG E-IL | 0 | 530623 | RICE 3 115.00 | 530620 | LYONS 3 115.00 | 0 |  | 1 | 22SP | 100 | 100 | 0 |  | 32.3655 | 126.9282 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICECO 230.00 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 560012 | RICECO 230.00 | 0 |  | 1 |  |  |  | MIDW | LYONS - RICE_CO 115KV CKT 1 | Rebuild 11.7 mile line | [5 empty] | 24 | 24 | [46 empty] | 2012-10-01 | 2013-04-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3985522SP | TO->FROM | LYONS - RICE_CO 115KV CKT 1 | CP | MIDW | WERE | REG E-IL | REG E-IL | 0 | 530623 | RICE 3 115.00 | 530620 | LYONS 3 115.00 | 0 |  | 1 | 22SP | 100 | 100 | 0 |  | 32.3655 | 126.9282 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICECO 230.00 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 560012 | RICECO 230.00 | 0 |  | 1 |  |  |  | WERE | LYONS - WHEATLAND 115KV CKT 1 #2 | Rerate circuit to 1000 amps | [5 empty] | 12 | 12 | [46 empty] | 2012-10-01 | 2013-07-15
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3985522SP | TO->FROM | LYONS - RICE_CO 115KV CKT 1 | CP | MIDW | WERE | REG E-IL | REG E-IL | 0 | 530623 | RICE 3 115.00 | 530620 | LYONS 3 115.00 | 0 |  | 1 | 22SP | 100 | 100 | 0 |  | 32.3655 | 126.9282 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICECO 230.00 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 560012 | RICECO 230.00 | 0 |  | 1 |  |  |  | MIDW | RICE_CO 230/115KV TRANSFORMER CKT 1 | Add 230/115kV Transformer | [5 empty] | 24 | 24 | [46 empty] | 2012-10-01 | 2012-11-15
GI | [10 empty] | LYONS - RICE_CO 115KV CKT 1 | U | MIDW | WERE |  |  | 0 | 530623 | RICE 3 115.00 | 530620 | LYONS 3 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | MIDW | LYONS - RICE_CO 115KV CKT 1 | Rebuild 11.7 mile line | [53 empty] | 2012-10-01 | 2013-04-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1365512WP | FROM->TO | LYONS - WHEATLAND 115KV CKT 1 | CP | WERE | WERE | REG E-IL | WEST | 0 | 530620 | LYONS 3 115.00 | 533439 | WHEATLD3 115.00 | 0 |  | 1 | 12WP | 159 | 159 | 0 |  | 24.4384 | 106.7293 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICECO 230.00 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 560012 | RICECO 230.00 | 0 |  | 1 |  |  |  | WERE | LYONS - WHEATLAND 115KV CKT 1 #1 | Replace CTs | [5 empty] | 24 | 24 | [46 empty] | 2012-10-01 | 2013-07-15
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1365512WP | FROM->TO | LYONS - WHEATLAND 115KV CKT 1 | CP | WERE | WERE | REG E-IL | WEST | 0 | 530620 | LYONS 3 115.00 | 533439 | WHEATLD3 115.00 | 0 |  | 1 | 12WP | 159 | 159 | 0 |  | 24.4384 | 106.7293 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICECO 230.00 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 560012 | RICECO 230.00 | 0 |  | 1 |  |  |  | MIDW | CIRCLE - RICE_CO 230KV CKT 1 | Convert from 115kV to 230kV operation | [5 empty] | 24 | 24 | [46 empty] | 2012-10-01 | 2012-11-15
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1365512WP | FROM->TO | LYONS - WHEATLAND 115KV CKT 1 | CP | WERE | WERE | REG E-IL | WEST | 0 | 530620 | LYONS 3 115.00 | 533439 | WHEATLD3 115.00 | 0 |  | 1 | 12WP | 159 | 159 | 0 |  | 24.4384 | 106.7293 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICECO 230.00 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 560012 | RICECO 230.00 | 0 |  | 1 |  |  |  | MIDW | LYONS - RICE_CO 115KV CKT 1 | Rebuild 11.7 mile line | [5 empty] | 24 | 24 | [46 empty] | 2012-10-01 | 2013-04-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1365512WP | FROM->TO | LYONS - WHEATLAND 115KV CKT 1 | CP | WERE | WERE | REG E-IL | WEST | 0 | 530620 | LYONS 3 115.00 | 533439 | WHEATLD3 115.00 | 0 |  | 1 | 12WP | 159 | 159 | 0 |  | 24.4384 | 106.7293 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICECO 230.00 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 560012 | RICECO 230.00 | 0 |  | 1 |  |  |  | WERE | LYONS - WHEATLAND 115KV CKT 1 #2 | Rerate circuit to 1000 amps | [5 empty] | 12 | 12 | [46 empty] | 2012-10-01 | 2013-07-15
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1365512WP | FROM->TO | LYONS - WHEATLAND 115KV CKT 1 | CP | WERE | WERE | REG E-IL | WEST | 0 | 530620 | LYONS 3 115.00 | 533439 | WHEATLD3 115.00 | 0 |  | 1 | 12WP | 159 | 159 | 0 |  | 24.4384 | 106.7293 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICECO 230.00 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 560012 | RICECO 230.00 | 0 |  | 1 |  |  |  | MIDW | RICE_CO 230/115KV TRANSFORMER CKT 1 | Add 230/115kV Transformer | [5 empty] | 24 | 24 | [46 empty] | 2012-10-01 | 2012-11-15
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1425513WP | FROM->TO | LYONS - WHEATLAND 115KV CKT 1 | CP | WERE | WERE | REG E-IL | WEST | 0 | 530620 | LYONS 3 115.00 | 533439 | WHEATLD3 115.00 | 0 |  | 1 | 13WP | 159 | 159 | 0 |  | 25.1176 | 106.3399 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICECO 230.00 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 560012 | RICECO 230.00 | 0 |  | 1 |  |  |  | WERE | LYONS - WHEATLAND 115KV CKT 1 #1 | Replace CTs | [5 empty] | 24 | 24 | [46 empty] | 2012-10-01 | 2013-07-15
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1425513WP | FROM->TO | LYONS - WHEATLAND 115KV CKT 1 | CP | WERE | WERE | REG E-IL | WEST | 0 | 530620 | LYONS 3 115.00 | 533439 | WHEATLD3 115.00 | 0 |  | 1 | 13WP | 159 | 159 | 0 |  | 25.1176 | 106.3399 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICECO 230.00 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 560012 | RICECO 230.00 | 0 |  | 1 |  |  |  | MIDW | CIRCLE - RICE_CO 230KV CKT 1 | Convert from 115kV to 230kV operation | [5 empty] | 24 | 24 | [46 empty] | 2012-10-01 | 2012-11-15
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1425513WP | FROM->TO | LYONS - WHEATLAND 115KV CKT 1 | CP | WERE | WERE | REG E-IL | WEST | 0 | 530620 | LYONS 3 115.00 | 533439 | WHEATLD3 115.00 | 0 |  | 1 | 13WP | 159 | 159 | 0 |  | 25.1176 | 106.3399 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICECO 230.00 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 560012 | RICECO 230.00 | 0 |  | 1 |  |  |  | MIDW | LYONS - RICE_CO 115KV CKT 1 | Rebuild 11.7 mile line | [5 empty] | 24 | 24 | [46 empty] | 2012-10-01 | 2013-04-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1425513WP | FROM->TO | LYONS - WHEATLAND 115KV CKT 1 | CP | WERE | WERE | REG E-IL | WEST | 0 | 530620 | LYONS 3 115.00 | 533439 | WHEATLD3 115.00 | 0 |  | 1 | 13WP | 159 | 159 | 0 |  | 25.1176 | 106.3399 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICECO 230.00 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 560012 | RICECO 230.00 | 0 |  | 1 |  |  |  | WERE | LYONS - WHEATLAND 115KV CKT 1 #2 | Rerate circuit to 1000 amps | [5 empty] | 12 | 12 | [46 empty] | 2012-10-01 | 2013-07-15
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1425513WP | FROM->TO | LYONS - WHEATLAND 115KV CKT 1 | CP | WERE | WERE | REG E-IL | WEST | 0 | 530620 | LYONS 3 115.00 | 533439 | WHEATLD3 115.00 | 0 |  | 1 | 13WP | 159 | 159 | 0 |  | 25.1176 | 106.3399 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICECO 230.00 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 560012 | RICECO 230.00 | 0 |  | 1 |  |  |  | MIDW | RICE_CO 230/115KV TRANSFORMER CKT 1 | Add 230/115kV Transformer | [5 empty] | 24 | 24 | [46 empty] | 2012-10-01 | 2012-11-15
GI | [10 empty] | LYONS - WHEATLAND 115KV CKT 1 #1 | U | WERE | WERE |  |  | 0 | 530620 | LYONS 3 115.00 | 533439 | WHEATLD3 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | WERE | LYONS - WHEATLAND 115KV CKT 1 #1 | Replace CTs | [53 empty] | 2012-10-01 | 2013-07-15
GI | [10 empty] | LYONS - WHEATLAND 115KV CKT 1 #1 | CP | WERE | WERE |  |  | 0 | 530620 | LYONS 3 115.00 | 533439 | WHEATLD3 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | MIDW | CIRCLE - RICE_CO 230KV CKT 1 | Convert from 115kV to 230kV operation | [5 empty] | 24 | 24 | [46 empty] | 2012-10-01 | 2012-11-15
GI | [10 empty] | LYONS - WHEATLAND 115KV CKT 1 #1 | CP | WERE | WERE |  |  | 0 | 530620 | LYONS 3 115.00 | 533439 | WHEATLD3 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | MIDW | LYONS - RICE_CO 115KV CKT 1 | Rebuild 11.7 mile line | [5 empty] | 24 | 24 | [46 empty] | 2012-10-01 | 2013-04-01
GI | [10 empty] | LYONS - WHEATLAND 115KV CKT 1 #1 | CP | WERE | WERE |  |  | 0 | 530620 | LYONS 3 115.00 | 533439 | WHEATLD3 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | WERE | LYONS - WHEATLAND 115KV CKT 1 #2 | Rerate circuit to 1000 amps | [5 empty] | 12 | 12 | [46 empty] | 2012-10-01 | 2013-07-15
GI | [10 empty] | LYONS - WHEATLAND 115KV CKT 1 #1 | CP | WERE | WERE |  |  | 0 | 530620 | LYONS 3 115.00 | 533439 | WHEATLD3 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | MIDW | RICE_CO 230/115KV TRANSFORMER CKT 1 | Add 230/115kV Transformer | [5 empty] | 24 | 24 | [46 empty] | 2012-10-01 | 2012-11-15
GI | [10 empty] | LYONS - WHEATLAND 115KV CKT 1 #2 | U | WERE | WERE |  |  | 0 | 530620 | LYONS 3 115.00 | 533439 | WHEATLD3 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | WERE | LYONS - WHEATLAND 115KV CKT 1 #2 | Rerate circuit to 1000 amps | [53 empty] | 2012-10-01 | 2013-07-15
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3555517SP | TO->FROM | MARYVILLE - MIDWAY 161KV CKT 1 | S | GMO | GMO |  |  | 0 | 541369 | MIDWAY_5 161.00 | 541251 | MARYVLE5 161.00 | 0 |  | 1 | 17SP | 152 | 171 | 171 |  | 66.5368 | 101.6403 | [7 empty] | CATEGORYB | SINGLE | FAIRPORT 345/161KV TRANSFORMER CKT 3 | 0 | 300039 | 7FAIRPT 345.00 | 300076 | 5FAIRPT 161.00 | 0 |  | 3 |  |  |  | MIPU | MIDWAY - ST JOE 161KV CKT 1 Reactor | Install three series reactors in the Midway-St Joseph line at St Joseph Substation. The reactors will be rated 6% impedance and 1200 Amps. | [5 empty] | 18 | 18 | [5 empty] | 425000 | 2012-07-18 | [39 empty] | 2014-06-01 | 2015-06-01
GEN-2006-010 | Turk | [9 empty] | MCNAB REC - TURK 115KV CKT 1 | U | AEPW | AEPW | SARK | SARKAECC | 0 | 504122 | MCNAB 3 115.00 | 507456 | HEMPSTD3 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | AEPW | MCNAB REC - TURK 115KV CKT 1 | Build a new two mile, 138 kV, 1590 ACSR line section (operated at 115 kV) from Turk Substation to the existing Okay- Hope 115 kV line to form a Turk - Hope 115 kV line. | [53 empty] | 2012-07-01 | 2012-07-01
2007-AG3 | AFS7 | [9 empty] | MEDICINE LODGE - SAWYER 115KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539673 | MED-LDG3 115.00 | 539649 | SAWYER 3 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | MKEC | MEDICINE LODGE - SAWYER 115KV CKT 1 | Rebuild line | [53 empty] | 2009-12-01 | 2013-06-01
2007-AG3 | AFS7 | [9 empty] | MEDICINE LODGE (MED-LDG4) 138/115/2.72KV TRANSFORMER CKT 1 | U | MKEC |  |  |  | 2 | 539674 | MED-LDG4 138.00 | 539673 | MED-LDG3 115.00 | 539917 | MEDLGT-T 2.7200 | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | MKEC | MEDICINE LODGE 138/115KV TRANSFORMER CKT 1 Displacement | Upgrade transformer | [53 empty] | 2009-12-01 | 2013-06-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3565517SP | TO->FROM | MIDWAY - ST JOE 161KV CKT 1 | S | GMO | GMO |  |  | 0 | 541253 | ST JOE 5 161.00 | 541369 | MIDWAY_5 161.00 | 0 |  | 1 | 17SP | 152 | 171 | 171 |  | 76.7055 | 112.55 | [7 empty] | CATEGORYB | SINGLE | FAIRPORT 345/161KV TRANSFORMER CKT 3 | 0 | 300039 | 7FAIRPT 345.00 | 300076 | 5FAIRPT 161.00 | 0 |  | 3 |  |  |  | MIPU | MIDWAY - ST JOE 161KV CKT 1 Reactor | Install three series reactors in the Midway-St Joseph line at St Joseph Substation. The reactors will be rated 6% impedance and 1200 Amps. | [5 empty] | 18 | 18 | [5 empty] | 425000 | 2012-07-18 | [39 empty] | 2014-06-01 | 2015-06-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T19335517SP | TO->FROM | MIDWAY - ST JOE 161KV CKT 1 | S | GMO | GMO |  |  | 0 | 541253 | ST JOE 5 161.00 | 541369 | MIDWAY_5 161.00 | 0 |  | 1 | 17SP | 152 | 171 | 171 |  | 75.5669 | 110.5639 | [7 empty] | CATEGORYB | NONSINGLE | LN-FAIRPORT | 0 | 0 |  | 0 |  | 0 | [5 empty] | MIPU | MIDWAY - ST JOE 161KV CKT 1 Reactor | Install three series reactors in the Midway-St Joseph line at St Joseph Substation. The reactors will be rated 6% impedance and 1200 Amps. | [5 empty] | 18 | 18 | [5 empty] | 425000 | 2012-07-18 | [39 empty] | 2014-06-01 | 2015-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1175512WP | FROM->TO | MOUNDRIDGE (MOUND10X) 138/115/13.8KV TRANSFORMER CKT 1 | REL | WERE | WERE | WEST | SCENTRAL | 2 | 533429 | MOUNDRG3 115.00 | 533013 | MOUND 4 138.00 | 533096 | MOUNDRI1 13.800 | 1 | 12WP | 100 | 110 | 125 | 100.7 | 100.7063 | 109.5767 | [7 empty] | CATEGORYB | SINGLE | RENO COUNTY - WICHITA 345KV CKT 1 | 0 | 532771 | RENO 7 345.00 | 532796 | WICHITA7 345.00 | 0 |  | 1 |  |  |  | WERE | MOUNDRIDGE 138/115KV TRANSFORMER CKT 2 | Install second 138/115 kV transformer at Moundridge. Operate both 138/115 kV transformers normally closed. | 100 | 110 |  |  |  | 24 | 24 | [46 empty] | 2012-10-01 | 2014-12-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1315513WP | FROM->TO | MOUNDRIDGE (MOUND10X) 138/115/13.8KV TRANSFORMER CKT 1 | REL | WERE | WERE | WEST | SCENTRAL | 2 | 533429 | MOUNDRG3 115.00 | 533013 | MOUND 4 138.00 | 533096 | MOUNDRI1 13.800 | 1 | 13WP | 100 | 110 | 125 |  | 91.7841 | 101.4109 | [7 empty] | CATEGORYB | SINGLE | RENO COUNTY - WICHITA 345KV CKT 1 | 0 | 532771 | RENO 7 345.00 | 532796 | WICHITA7 345.00 | 0 |  | 1 |  |  |  | WERE | MOUNDRIDGE 138/115KV TRANSFORMER CKT 2 | Install second 138/115 kV transformer at Moundridge. Operate both 138/115 kV transformers normally closed. | 100 | 110 |  |  |  | 24 | 24 | [46 empty] | 2012-10-01 | 2014-12-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1335513WP | TO->FROM | MUND - PENTAGON 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533261 | PENTAGN3 115.00 | 533282 | MUND 3 115.00 | 0 |  | 1 | 13WP | 179 | 194 | 0 | 99.6 | 99.5609 | 101.7443 | [7 empty] | CATEGORYB | SINGLE | 87th STREET - CRAIG 345KV CKT 1 | 0 | 532775 | 87TH 7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  |  |  | KACP | IATAN - NASHUA 345KV CKT 1 | Tap Nashua 345kV bus in Hawthorn - St. Joseph 345 kV line. Build new 345 kV line from Iatan to Nashua,Add Nashua 345/161 kV | [53 empty] | 2012-10-01 | 2015-06-01
GEN | [10 empty] | NELIGH - PETERSBURG 115KV CKT 1 | U | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640444 |  | 640293 | NELIGH 7 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | NPPD | NELIGH - PETERSBURG 115KV CKT 1 | Replace Breaker 1106, jumpers, and 115 kV Switch 1106-D2 at Neligh. Replace main bus at Petersburg. Upgrade and replace transmission structures on 115 kV lineto facilitate 100 degrees Centigrade line operation. | [53 empty] | 2013-01-01 | 2013-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T29025522SP | TO->FROM | NORTH WARSAW - TRUMAN 161KV CKT 1 | S | SWPA | GMO | EMINTH |  | 0 | 505502 | TRUMAN 5 161.00 | 541314 | NWARSAW5 161.00 | 0 |  | 1 | 22SP | 223 | 223 | 223 | 97.2 | 97.2206 | 101.0893 | [7 empty] | CATEGORYB | NONSINGLE | OVERTON-TRF | 0 | 0 |  | 0 |  | 0 | [5 empty] | SWPA | NORTH WARSAW - TRUMAN 161KV CKT 1 SWPA | Replace wave trap and CTs at Truman. | 286 | 286 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 70000 | 2010-09-29 | [39 empty] | 2018-06-01 | 2018-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T28625522SP | TO->FROM | NORTH WARSAW - TRUMAN 161KV CKT 1 | S | SWPA | GMO | EMINTH |  | 0 | 505502 | TRUMAN 5 161.00 | 541314 | NWARSAW5 161.00 | 0 |  | 1 | 22SP | 223 | 223 | 223 | 97.8 | 97.8005 | 100.857 | [7 empty] | CATEGORYB | NONSINGLE | AI03 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SWPA | NORTH WARSAW - TRUMAN 161KV CKT 1 SWPA | Replace wave trap and CTs at Truman. | 286 | 286 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 70000 | 2010-09-29 | [39 empty] | 2018-06-01 | 2018-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4345522SP | TO->FROM | NORTH WARSAW - TRUMAN 161KV CKT 1 | S | SWPA | GMO | EMINTH |  | 0 | 505502 | TRUMAN 5 161.00 | 541314 | NWARSAW5 161.00 | 0 |  | 1 | 22SP | 223 | 223 | 223 | 98.7 | 98.7188 | 100.6031 | [7 empty] | CATEGORYB | SINGLE | CLINTON - WINDSOR 161KV CKT 1 | 0 | 541217 | WINDSR 5 161.00 | 541242 | CLINTON5 161.00 | 0 |  | 1 |  |  |  | SWPA | NORTH WARSAW - TRUMAN 161KV CKT 1 SWPA | Replace wave trap and CTs at Truman. | 286 | 286 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 70000 | 2010-09-29 | [39 empty] | 2018-06-01 | 2018-06-01
NA | [10 empty] | NORTHWEST - TATONGA 345KV CKT 1 | U | OKGE | OKGE | ENID | ENID | 0 | 515407 |  | 514880 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | OKGE | NORTHWEST - TATONGA 345KV CKT 1 | Build 345 kV line | [53 empty] | 2010-01-01 | 2010-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8255513SP | FROM->TO | NORTHWEST (NORTWST2) 345/138/13.8KV TRANSFORMER CKT 1 | CP | OKGE | OKGE |  |  | 2 | 514880 | NORTWST7 345.00 | 514879 | NORTWST4 138.00 | 515742 | NORTWS21 13.800 | 1 | 13SP | 493 | 493 | 0 | 101.2 | 101.174 | 101.7982 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST (NORTWST3) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514879 | NORTWST4 138.00 | 514880 | NORTWST7 345.00 | 515743 | NORTWS31 13.800 | 1 |  |  |  | OKGE | NORTHWEST 345/138/13.8KV TRANSFORMER CKT 3 Accelerated | Install third 345/138 kV Bus Tie in Northwest Sub | [5 empty] | 40 | 40 | [46 empty] | 2013-06-01 | 2015-06-01
GEN-2006-010 | Turk | [9 empty] | OKAY - TURK 138KV CKT 1 | U | AEPW | AEPW | SARK | SARK | 0 | 507454 | HEMPSTD4 138.00 | 507428 | OKAY 4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | AEPW | OKAY - TURK 138KV CKT 1 | Build two mile, 138 kV, 1590ACSR line section from Turk Sub to existing Okay-Hope 115 kV line and rebuild twelve miles of 115 kV line to Okay Sub to 138 kV, 1590 ACSR , to form a Turk-Okay 138 kV line | [53 empty] | 2012-07-01 | 2012-07-01
GEN-2006-010 | Turk | [9 empty] | OKAY 138/69KV TRANSFORMER CKT 1 | U | AEPW | AEPW | SARK | SARK | 1 | 507428 | OKAY 4 138.00 | 507427 | OKAY 2 69.000 | 507442 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | AEPW | OKAY 138/69KV TRANSFORMER CKT 1 | Replace three single-phase 115-69 kV autotransformers with one 90 MVA, three-phase 138-69 kV autotransformer and convert high side of station to 138 kV | [53 empty] | 2012-07-01 | 2012-07-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2505513SP | FROM->TO | PLANT X STATION (WH ALM20171) 230/115/13.2KV TRANSFORMER CKT 1 | EXP | SPS | SPS | SPS-CNPL | SPS-CNPL | 2 | 525481 | PLANT_X 6230.00 | 525480 | PLANT_X 3115.00 | 525479 | PLANTX_TR1 113.200 | 1 | 13SP | 239 | 239 | 0 | 104.2 | 104.1985 | 122.1612 | [7 empty] | CATEGORYB | SINGLE | LAMB COUNTY INTERCHANGE - TOLK STATION WEST 230KV CKT 1 | 0 | 525531 | TOLK_WEST 6230.00 | 525637 | LAMB_CNTY 6230.00 | 0 |  | 1 |  |  |  | SPS | NEWHART INTERCHANGE PROJECT | Tap the Potter Interchange - Plant X Station 230 kV line for new Newhart Substation and install 230/115 kV, 150/173 MVA transformer. New 15 mile Lampton Interchange - Hart Industrial Substation 115 kV line. New 19 mile Swisher County Interchange - Newhart | [53 empty] | 2013-06-01 | 2015-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2505513SP | FROM->TO | PLANT X STATION (WH ALM20171) 230/115/13.2KV TRANSFORMER CKT 1 | EXP | SPS | SPS | SPS-CNPL | SPS-CNPL | 2 | 525481 | PLANT_X 6230.00 | 525480 | PLANT_X 3115.00 | 525479 | PLANTX_TR1 113.200 | 1 | 13SP | 239 | 239 | 0 | 104.2 | 104.1985 | 122.1612 | 526_SPS_22S_BAILEY CO- CURRY CO 115 kV_2011-05-18.idv | [6 empty] | CATEGORYB | SINGLE | LAMB COUNTY INTERCHANGE - TOLK STATION WEST 230KV CKT 1 | 0 | 525531 | TOLK_WEST 6230.00 | 525637 | LAMB_CNTY 6230.00 | 0 |  | 1 |  |  |  | SPS | BAILEY COUNTY INTERCHANGE - CURRY COUNTY INTERCHANGE 115KV CKT 1 | 40 miles 115 kV between Bailey and Curry. | [5 empty] | 30 | 30 | [46 empty] | 2012-06-01 | 2015-06-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8885513SP | FROM->TO | PLANT X STATION (WH ALM20171) 230/115/13.2KV TRANSFORMER CKT 1 | EXP | SPS | SPS | SPS-CNPL | SPS-CNPL | 2 | 525481 | PLANT_X 6230.00 | 525480 | PLANT_X 3115.00 | 525479 | PLANTX_TR1 113.200 | 1 | 13SP | 239 | 239 | 0 |  | -999 | 122.1495 | [7 empty] | CATEGORYB | SINGLE | LAMB COUNTY INTERCHANGE (WH ALM20172) 230/115/13.2KV TRANSFORMER CKT 1 | 1 | 525636 | LAMB_CNTY 3115.00 | 525637 | LAMB_CNTY 6230.00 | 525633 | LAMB_TR3 113.200 | 1 |  |  |  | SPS | NEWHART INTERCHANGE PROJECT | Tap the Potter Interchange - Plant X Station 230 kV line for new Newhart Substation and install 230/115 kV, 150/173 MVA transformer. New 15 mile Lampton Interchange - Hart Industrial Substation 115 kV line. New 19 mile Swisher County Interchange - Newhart | [53 empty] | 2013-06-01 | 2015-06-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8885513SP | FROM->TO | PLANT X STATION (WH ALM20171) 230/115/13.2KV TRANSFORMER CKT 1 | EXP | SPS | SPS | SPS-CNPL | SPS-CNPL | 2 | 525481 | PLANT_X 6230.00 | 525480 | PLANT_X 3115.00 | 525479 | PLANTX_TR1 113.200 | 1 | 13SP | 239 | 239 | 0 |  | -999 | 122.1495 | 526_SPS_22S_BAILEY CO- CURRY CO 115 kV_2011-05-18.idv | [6 empty] | CATEGORYB | SINGLE | LAMB COUNTY INTERCHANGE (WH ALM20172) 230/115/13.2KV TRANSFORMER CKT 1 | 1 | 525636 | LAMB_CNTY 3115.00 | 525637 | LAMB_CNTY 6230.00 | 525633 | LAMB_TR3 113.200 | 1 |  |  |  | SPS | BAILEY COUNTY INTERCHANGE - CURRY COUNTY INTERCHANGE 115KV CKT 1 | 40 miles 115 kV between Bailey and Curry. | [5 empty] | 30 | 30 | [46 empty] | 2012-06-01 | 2015-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T13705513SP | FROM->TO | PLANT X STATION (WH ALM20171) 230/115/13.2KV TRANSFORMER CKT 1 | EXP | SPS | SPS | SPS-CNPL | SPS-CNPL | 2 | 525481 | PLANT_X 6230.00 | 525480 | PLANT_X 3115.00 | 525479 | PLANTX_TR1 113.200 | 1 | 13SP | 239 | 239 | 0 | 97.8 | 97.8454 | 116.2974 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-T04 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | NEWHART INTERCHANGE PROJECT | Tap the Potter Interchange - Plant X Station 230 kV line for new Newhart Substation and install 230/115 kV, 150/173 MVA transformer. New 15 mile Lampton Interchange - Hart Industrial Substation 115 kV line. New 19 mile Swisher County Interchange - Newhart | [53 empty] | 2013-06-01 | 2015-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T13705513SP | FROM->TO | PLANT X STATION (WH ALM20171) 230/115/13.2KV TRANSFORMER CKT 1 | EXP | SPS | SPS | SPS-CNPL | SPS-CNPL | 2 | 525481 | PLANT_X 6230.00 | 525480 | PLANT_X 3115.00 | 525479 | PLANTX_TR1 113.200 | 1 | 13SP | 239 | 239 | 0 | 97.8 | 97.8454 | 116.2974 | 526_SPS_22S_BAILEY CO- CURRY CO 115 kV_2011-05-18.idv | [6 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-T04 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | BAILEY COUNTY INTERCHANGE - CURRY COUNTY INTERCHANGE 115KV CKT 1 | 40 miles 115 kV between Bailey and Curry. | [5 empty] | 30 | 30 | [46 empty] | 2012-06-01 | 2015-06-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T13725513SP | FROM->TO | PLANT X STATION (WH ALM20171) 230/115/13.2KV TRANSFORMER CKT 1 | EXP | SPS | SPS | SPS-CNPL | SPS-CNPL | 2 | 525481 | PLANT_X 6230.00 | 525480 | PLANT_X 3115.00 | 525479 | PLANTX_TR1 113.200 | 1 | 13SP | 239 | 239 | 0 |  | 84.5452 | 101.2816 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-T66 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | NEWHART INTERCHANGE PROJECT | Tap the Potter Interchange - Plant X Station 230 kV line for new Newhart Substation and install 230/115 kV, 150/173 MVA transformer. New 15 mile Lampton Interchange - Hart Industrial Substation 115 kV line. New 19 mile Swisher County Interchange - Newhart | [53 empty] | 2013-06-01 | 2015-06-01
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T13725513SP | FROM->TO | PLANT X STATION (WH ALM20171) 230/115/13.2KV TRANSFORMER CKT 1 | EXP | SPS | SPS | SPS-CNPL | SPS-CNPL | 2 | 525481 | PLANT_X 6230.00 | 525480 | PLANT_X 3115.00 | 525479 | PLANTX_TR1 113.200 | 1 | 13SP | 239 | 239 | 0 |  | 84.5452 | 101.2816 | 526_SPS_22S_BAILEY CO- CURRY CO 115 kV_2011-05-18.idv | [6 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-T66 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | BAILEY COUNTY INTERCHANGE - CURRY COUNTY INTERCHANGE 115KV CKT 1 | 40 miles 115 kV between Bailey and Curry. | [5 empty] | 30 | 30 | [46 empty] | 2012-06-01 | 2015-06-01
GI | [10 empty] | RICE_CO 230/115KV TRANSFORMER CKT 1 | U | MIDW | MIDW |  |  | 0 | 560012 | RICECO 230.00 | 530623 | RICE 3 115.00 |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | MIDW | RICE_CO 230/115KV TRANSFORMER CKT 1 | Add 230/115kV Transformer | [53 empty] | 2012-10-01 | 2012-11-15
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2035512SP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | CP | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 12SP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Mathewson - Tatonga 345 kV Ckt 1 | Build new 61 mile Tatonga - Mathewson 345 kV line. | [53 empty] | 2013-06-01 | 2019-06-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2035512WP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | CP | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 12WP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Mathewson - Tatonga 345 kV Ckt 1 | Build new 61 mile Tatonga - Mathewson 345 kV line. | [53 empty] | 2013-06-01 | 2019-06-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2035513SP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | CP | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 13SP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Mathewson - Tatonga 345 kV Ckt 1 | Build new 61 mile Tatonga - Mathewson 345 kV line. | [53 empty] | 2013-06-01 | 2019-06-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T2035513WP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | CP | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 13WP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Mathewson - Tatonga 345 kV Ckt 1 | Build new 61 mile Tatonga - Mathewson 345 kV line. | [53 empty] | 2013-06-01 | 2019-06-01
GEN-2006-010 | Turk | [9 empty] | SE TEXARKANA - TURK 138KV CKT 1 | U | AEPW | AEPW | SARK | TEXARK | 0 | 507454 | HEMPSTD4 138.00 | 508078 | SETEXAR4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | AEPW | SE TEXARKANA - TURK 138KV CKT 1 | Build new Turk-SE Texarkana 138 kV line and add SE Texarkana 138 kV terminal. | [53 empty] | 2012-07-01 | 2012-07-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T285512WP | FROM->TO | SPS North-South Stability Limit | EXP | SPS | SPS |  |  | SPSNORTH_STH | 0 |  | 0 |  | 0 |  |  | 12WP | 800 | 800 | 800 | 119.9 | 119.9253 | 121.3436 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T285512WP | FROM->TO | SPS North-South Stability Limit | EXP | SPS | SPS |  |  | SPSNORTH_STH | 0 |  | 0 |  | 0 |  |  | 12WP | 800 | 800 | 800 | 119.9 | 119.9253 | 121.3436 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T285512WP | FROM->TO | SPS North-South Stability Limit | EXP | SPS | SPS |  |  | SPSNORTH_STH | 0 |  | 0 |  | 0 |  |  | 12WP | 800 | 800 | 800 | 119.9 | 119.9253 | 121.3436 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T285512WP | FROM->TO | SPS North-South Stability Limit | EXP | SPS | SPS |  |  | SPSNORTH_STH | 0 |  | 0 |  | 0 |  |  | 12WP | 800 | 800 | 800 | 119.9 | 119.9253 | 121.3436 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGE's Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T335513WP | FROM->TO | SPS North-South Stability Limit | EXP | SPS | SPS |  |  | SPSNORTH_STH | 0 |  | 0 |  | 0 |  |  | 13WP | 800 | 800 | 800 | 117.8 | 117.7994 | 119.3012 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T335513WP | FROM->TO | SPS North-South Stability Limit | EXP | SPS | SPS |  |  | SPSNORTH_STH | 0 |  | 0 |  | 0 |  |  | 13WP | 800 | 800 | 800 | 117.8 | 117.7994 | 119.3012 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 1792 | 1792 | 1792 | 1792 | [49 empty] | 2012-06-01 | 2015-01-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T335513WP | FROM->TO | SPS North-South Stability Limit | EXP | SPS | SPS |  |  | SPSNORTH_STH | 0 |  | 0 |  | 0 |  |  | 13WP | 800 | 800 | 800 | 117.8 | 117.7994 | 119.3012 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | [53 empty] | 2012-06-01 | 2014-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T335513WP | FROM->TO | SPS North-South Stability Limit | EXP | SPS | SPS |  |  | SPSNORTH_STH | 0 |  | 0 |  | 0 |  |  | 13WP | 800 | 800 | 800 | 117.8 | 117.7994 | 119.3012 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGE's Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | [53 empty] | 2012-06-01 | 2014-06-01
2005-AG2 | 2005-AG2 | [9 empty] | SUB 110 - ORONOGO JCT. - SUB 167 - RIVERTON 161KV CKT 1 | U | EMDE | EMDE |  |  | 0 | 547469 | RIV167 5 161 | 547467 | ORO110 5 161 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | EMDE | SUB 110 - ORONOGO JCT. - SUB 167 - RIVERTON 161KV CKT 1 | Reconductor Oronogo 59467 to Riverton 59469 with Bundled 556 ACSR | [53 empty] | 2011-06-01 | 2011-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T5005522SP | FROM->TO | SUB 906 NORTH - SUB 928 69KV CKT 1 | REL | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 647006 | S906 N 8 69.000 | 647928 | S928 8 69.000 | 0 |  | 1 | 22SP | 89 | 89 | 89 | 103.3 | 103.3251 | 103.3616 | [7 empty] | CATEGORYB | SINGLE | SUB 921 - SUB 942 69KV CKT 1 | 0 | 647921 | S921 8 69.000 | 647942 | S942 8 69.000 | 0 |  | 1 |  |  |  | OPPD | SUB 906 NORTH - SUB 928 69KV CKT 1 | Rebuild 2.00 miles of line, change CT tap settings, and replace line jumpers. Rating after rebuild and other modifications will be 110 MVA. | 110 | 110 | 110 | 110 |  | 24 | 24 | [46 empty] | 2021-06-01 | 2021-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T4185022SP | FROM->TO | SUB 907 - SUB 919 69KV CKT 1 | REL | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 647907 | S907 8 69.000 | 647919 | S919 8 69.000 | 0 |  | 1 | 22SP | 65 | 65 | 65 | 107.9 | 107.8854 | 105.8039 | [7 empty] | CATEGORYB | SINGLE | SUB 1250 - SUB 919 69KV CKT 1 | 0 | 647919 | S919 8 69.000 | 647950 | S950 8 69.000 | 0 |  | 1 |  |  |  | OPPD | SUB 907 - SUB 919 69KV CKT 1 | Increase clearance. At least 77 MVA rating | [5 empty] | 24 | 24 | [46 empty] | 2018-06-01 | 2018-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T20985022SP | FROM->TO | SUB 907 - SUB 919 69KV CKT 1 | REL | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 647907 | S907 8 69.000 | 647919 | S919 8 69.000 | 0 |  | 1 | 22SP | 65 | 65 | 65 | 107.8 | 107.8425 | 105.7932 | [7 empty] | CATEGORYB | SINGLE | SUB 1250 (S1250 T1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 646250 | S1250 5 161.00 | 647950 | S950 8 69.000 | 648250 | S1250T19 13.800 | 1 |  |  |  | OPPD | SUB 907 - SUB 919 69KV CKT 1 | Increase clearance. At least 77 MVA rating | [5 empty] | 24 | 24 | [46 empty] | 2018-06-01 | 2018-06-01
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4985522SP | FROM->TO | SUB 921 - SUB 942 69KV CKT 1 | REL | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 647921 | S921 8 69.000 | 647942 | S942 8 69.000 | 0 |  | 1 | 22SP | 93 | 93 | 93 | 100.8 | 100.7662 | 100.7745 | [7 empty] | CATEGORYB | SINGLE | SUB 906 NORTH - SUB 928 69KV CKT 1 | 0 | 647006 | S906 N 8 69.000 | 647928 | S928 8 69.000 | 0 |  | 1 |  |  |  | OPPD | SUB 921 - SUB 942 69KV CKT 1 | Increase line clearances to allow the use of a higher conductor rating and change CT tap settings. | 103 | 103 | 103 | 103 |  | 12 | 12 | [46 empty] | 2018-06-01 | 2018-06-01
GEN-2006-010 | Turk | [9 empty] | SUGAR HILL - TURK 138KV CKT 1 | U | AEPW | AEPW | SARK | TEXARK | 0 | 507454 | HEMPSTD4 138.00 | 508080 | SUGARHL4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | AEPW | SUGAR HILL - TURK 138KV CKT 1 | Build new Turk-Sugar Hill 138 kV line and add Sugar Hill 138 kV terminal. | [53 empty] | 2012-07-01 | 2012-07-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T765512SP | FROM->TO | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | CP | WFEC | WFEC | AEP-OP |  | 2 | 521065 | TALOGA 4 138.00 | 521064 | TALOGA 2 69.000 | 521178 | TLGTERT 13.800 | 1 | 12SP | 56 | 56 | 56 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | WFEC | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | Auto XFMR 56 to 112MVA | 112 | 112 | 112 | 112 |  | 24 | 24 | [46 empty] | 2013-06-01 | 2013-06-01
2011-AGP1 | AFS9-NW-TAT |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS9ADD1T765512WP | FROM->TO | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | CP | WFEC | WFEC | AEP-OP |  | 2 | 521065 | TALOGA 4 138.00 | 521064 | TALOGA 2 69.000 | 521178 | TLGTERT 13.800 | 1 | 12WP | 56 | 56 | 56 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | WFEC | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | Auto XFMR 56 to 112MVA | 112 | 112 | 112 | 112 |  | 24 | 24 | [46 empty] | 2013-06-01 | 2013-06-01
2009-AGP2 | AFS5 | [9 empty] | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | U | WFEC | WFEC | AEP-OP | AEP-OP | 2 | 521065 | TALOGA 4 138.00 | 521064 | TALOGA 2 69.000 | 521178 | TLGTERT 13.800 | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | WFEC | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | Auto XFMR 56 to 112MVA | 112 | 112 | 112 | 112 |  | 24 | 24 | [46 empty] | 2010-10-01 | 2013-06-01
NA | [10 empty] | TATONGA - WOODWARD 345KV CKT 1 | U | OKGE | OKGE | ENID | ENID | 0 | 515407 |  | 515375 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | OKGE | TATONGA - WOODWARD 345KV CKT 1 | Build 345 kV line | [53 empty] | 2010-01-01 | 2010-01-01
GEN-2006-010 | Turk | [9 empty] | TURK (HEMP 1) 138/115/13.8KV TRANSFORMER CKT 1 | U | AEPW |  | SARK |  | 1 | 507454 | HEMPSTD4 138.00 | 507456 | HEMPSTD3 115.00 | 507458 | HEMP1 1 13.800 | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | AEPW | TURK (HEMP 1) 138/115/13.8KV TRANSFORMER CKT 1 | Build Turk 138-115 kV station and relocate autotransformer (and spare) from Patterson to this new Turk station | [53 empty] | 2012-07-01 | 2012-07-01
NA | [10 empty] | WOODWARD - IODINE 138KV CKT 1 | U | OKGE | OKGE | ENID | ENID | 0 | 515376 |  | 514796 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | OKGE | WOODWARD - IODINE 138KV CKT 1 | Tap Iodine to Woodward 138 kV line | [53 empty] | 2010-01-01 | 2010-01-01
NA | [10 empty] | WOODWARD - WOODWARD EHV 138KV CKT 1 | U | OKGE | OKGE | ENID | ENID | 0 | 515376 |  | 514785 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | OKGE | WOODWARD - WOODWARD EHV 138KV CKT 1 | Build .5 miles of 138 kV and install terminal equipment | [53 empty] | 2010-01-01 | 2010-01-01
NA | [10 empty] | WOODWARD - WOODWARD EHV 138KV CKT 2 | U | OKGE | OKGE | ENID | ENID | 0 | 515376 |  | 514785 |  |  |  | 2 | [15 empty] | BASECASE | BASE CASE | [11 empty] | OKGE | WOODWARD - WOODWARD EHV 138KV CKT 2 | Build .5 miles of 138 kV and install terminal equipment | [53 empty] | 2010-01-01 | 2010-01-01
NA | [10 empty] | WOODWARD 345/138KV TRANSFORMER CKT 1 | U | OKGE | OKGE | ENID | ENID | 1 | 515375 |  | 515376 |  | 515795 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | OKGE | WOODWARD 345/138KV TRANSFORMER CKT 1 | Install 345/138 kV XF | [53 empty] | 2010-01-01 | 2010-01-01

## tblAllFacilityLog < 100%
STUDYDES | STUDYDES2 | EVENTTYPE | AssessmentSOLUTIONTYPE | AssessmenFDNS-TERMINATION | SOLUTIONTYPE | FDNS-TERMINATION | GROUP | SCENARIO | FGName | DIRECTION | FacilityName | FacilityUpgradeCode | ModelArea1 | ModelArea2 | FZONENAME | TZONENAME | MONTFLAG | MONTFB | MONTFNAME | MONTTB1 | MONTTNAME1 | MONTTB2 | MONTTNAME2 | MONTCKT | Case | RATEA | RATEB | RATEC | Assessment Loading | BaseCaseLoading | TransferCaseLoading | NameOfBusWithMonitoredVoltage | Assessment Voltage | BaseCaseVoltage | TransferCaseVoltage | VINIT | VMIN | VMAX | CATEGORY | CONTTYPE | CONTNAME | CONTXFMRFLAG | CONTFB | CONTFNAME | CONTTB1 | CONTTNAME1 | CONTTB2 | CONTTNAME2 | CONTCKT | TransmissionProviderSystemImpactStudyNotesComments | RequiredRateB | TransmissionOwnerComments | OwnerDesignation | UpgradeName | UpgradeComponentWithinFacility | NewSummerA | NewSummerB | NewOtherA | NewOtherB | DistToConstruct | TotalLead | ConstructionLeadOnly | NewOrConstructWhileEnergized | NewR | NewX | NewB | CommentsRegardingUpgradeRequirements | NewCost | EffDate | NetPlantDate | ReusableEx_GrossValue | ReusableEx_NetValue | Reusable_EndofDepr | SalvageValue | NewCostWhileExpediting | EffDateExpedited | StartDeprExpedited | EndDeprExpedited | NetPlantDateExpedited | ReusableEx_GrossExpedited | ReusableEx_NetExpedited | Reusable_EndofDeprExpedited | SalvageValueExpedited | Generation 1 Owner & Unit (Name) | Generation 1 Redispatch Cost ($) | Generation 1 Redispatch Date (M/D/Y) | Generation 2 Owner & Unit (Name) | Generation 2 Redispatch Cost ($) | Generation 2 Redispatch Date (M/D/Y) | Generation 3 Owner & Unit (Name) | Generation 3 Redispatch Cost ($) | Generation 3 Redispatch Date (M/D/Y) | ActualCompletion | ActualNewCost | ActualNetPlantDate | ActualReusableEx_GrossValue | ActualReusableEx_NetValue | ActualReusable_EndofDepr | ActualSalvageValue | Actual_NewCostWhileExpediting | Actual_StartDeprExp | Actual_EndDeprExp | Actual_NetPlantDateExpedited | ActualReusableEx_GrossExpedited | ActualReusableEx_NetExpedited | ActualReusable_EndofDeprExpedited | Actual_SalvageValueExpedited | SPPReliabilityDate | COD | EOC | EarliestDate
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3715512WP | FROM->TO | 7OVERTON 345.00 () 345/161/13.8KV TRANSFORMER CKT 1 | E | AMMO | AMMO | AMRNMO | AMRNMO | 1 | 345408 | 7OVERTON 345.00 | 345409 | 5OVERTON 161.00 | 345410 | 1OVERTERT 13.800 | 1 | 12WP | 300 | 300 | 0 |  | 93.6845 | 97.8 | [7 empty] | CATEGORYB | SINGLE | KINGDOM CITY 345/161KV TRANSFORMER CKT 1 | 0 | 300043 | 7KINGDM 345.00 | 300090 | 5KINGDM 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3735512WP | FROM->TO | 7OVERTON 345.00 () 345/161/13.8KV TRANSFORMER CKT 1 | E | AMMO | AMMO | AMRNMO | AMRNMO | 1 | 345408 | 7OVERTON 345.00 | 345409 | 5OVERTON 161.00 | 345410 | 1OVERTERT 13.800 | 1 | 12WP | 300 | 300 | 0 |  | 91.0954 | 95.4 | [7 empty] | CATEGORYB | SINGLE | THOMAS HILL 345/161KV TRANSFORMER CKT 1 | 0 | 300049 | 7THOMHL 345.00 | 300120 | 5THMHIL 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T1045012WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 95.3 | 95.3242 | 95.4 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2175512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 95.8 | 95.8429 | 95.8 | [7 empty] | CATEGORYB | SINGLE | 8CAJUN2 - WEBRE 500KV CKT 1 | 0 | 303005 | 8CAJUN2 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2405512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 95.4 | 95.3762 | 95.5 | [7 empty] | CATEGORYB | SINGLE | NELSON - RICHARD 500KV CKT 1 | 0 | 335192 | 8NELSON 500.00 | 335367 | 8RICHARD 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2425512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 95.5 | 95.5248 | 95.5 | [7 empty] | CATEGORYB | SINGLE | WEBRE - WELLS 500KV CKT 1 | 0 | 335368 | 8WELLS 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2565512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 96.2 | 96.1798 | 96.2 | [7 empty] | CATEGORYB | SINGLE | COLY - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WGLEN 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2615512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 96.7 | 96.7158 | 96.8 | [7 empty] | CATEGORYB | SINGLE | WATERFORD - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WGLEN 500.00 | 336150 | 8WATERFO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2685512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 96.2 | 96.1995 | 96.2 | [7 empty] | CATEGORYB | SINGLE | JAGUAR - POINT ESSO TAP 230KV CKT 1 | 0 | 335641 | 6TP.ESSO 230.00 | 335770 | 6JAGUAR 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2725512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 95.8 | 95.8042 | 95.8 | [7 empty] | CATEGORYB | SINGLE | ENJAY - JAGUAR 230KV CKT 1 | 0 | 335770 | 6JAGUAR 230.00 | 335772 | 6ENJAY 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2765512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 95.9 | 95.9389 | 96 | [7 empty] | CATEGORYB | SINGLE | ENJAY - FANCY POINT 230KV CKT 1 | 0 | 335772 | 6ENJAY 230.00 | 335825 | 6FANCY 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2895512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 97.1 | 97.1113 | 97.1 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T295512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 95.5 | 95.4889 | 95.5 | [7 empty] | CATEGORYB | SINGLE | BARKERS 6 230.00 - RAMSAY 230KV CKT 1 | 0 | 500025 | BARKERS 6 230.00 | 500750 | RAMSAY 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3105512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 96.1 | 96.1401 | 96.1 | [7 empty] | CATEGORYB | SINGLE | BOGALUSA 500/230KV TRANSFORMER CKT 1 | 0 | 336130 | 8BOGALUS 500.00 | 336131 | 6ADMSCRK 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T315512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 95.5 | 95.5497 | 95.6 | [7 empty] | CATEGORYB | SINGLE | BAYOU SALE - TECHE 138KV CKT 1 | 0 | 500050 | BSALES 4 138.00 | 500820 | TECHE 4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3215512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 96.3 | 96.3167 | 96.4 | [7 empty] | CATEGORYB | SINGLE | BOGALUSA - FRANKLIN 500KV CKT 1 | 0 | 336130 | 8BOGALUS 500.00 | 336562 | 8FRKLIN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3275512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 96.2 | 96.2346 | 96.3 | [7 empty] | CATEGORYB | SINGLE | WATERFORD 500/230KV TRANSFORMER CKT 1 | 0 | 336150 | 8WATERFO 500.00 | 336154 | 6WATFRD 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T335512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 95.5 | 95.5362 | 95.6 | [7 empty] | CATEGORYB | SINGLE | BAYOU SALE - WAXLAKE 138KV CKT 1 | 0 | 500050 | BSALES 4 138.00 | 500890 | WAXLAKE4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T355512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 95.3 | 95.3333 | 95.4 | [7 empty] | CATEGORYB | SINGLE | EL PASO TAP - WAXLAKE 138KV CKT 1 | 0 | 500290 | ELPTAP 4 138.00 | 500890 | WAXLAKE4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3915512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 95.7 | 95.6582 | 95.7 | [7 empty] | CATEGORYB | SINGLE | BARKERS 6 230.00 - BOGALUSA 230KV CKT 1 | 0 | 500025 | BARKERS 6 230.00 | 336136 | 6BOGALUS 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T5285012WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 95.3 | 95.2693 | 95.5 | [7 empty] | CATEGORYB | GENOUT | GEN336153 1-WATERFORD UNIT#3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T7365512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 95.5 | 95.4667 | 95.5 | [7 empty] | CATEGORYB | NONSINGLE | CELE-WELLOP2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T7645512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 95.4 | 95.4349 | 95.5 | [7 empty] | CATEGORYB | NONSINGLE | SERCW-21 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T7685512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 95.3 | 95.3342 | 95.4 | [7 empty] | CATEGORYB | GENOUT | GEN303006 1-1BC2 U1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T7735512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 95.4 | 95.4311 | 95.5 | [7 empty] | CATEGORYB | GENOUT | GEN303008 1-1BC2 U3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T7795512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 95.9 | 95.8644 | 96 | [7 empty] | CATEGORYB | GENOUT | GEN335831 1-RIVERBEND UNIT#1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T7895512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 98.9 | 98.8898 | 99 | [7 empty] | CATEGORYB | GENOUT | GEN336153 1-WATERFORD UNIT#3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T7955512WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 | 96.4 | 96.4135 | 96.6 | [7 empty] | CATEGORYB | GENOUT | GEN336251 1-NINEMILE POINT UNIT#4 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T915012WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 12WP | 615 | 615 | 0 |  | 94.9286 | 95 | [7 empty] | CATEGORYB | SINGLE | JAGUAR - POINT ESSO TAP 230KV CKT 1 | 0 | 335641 | 6TP.ESSO 230.00 | 335770 | 6JAGUAR 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3235512WP | FROM->TO | ADAMS CREEK - BOGALUSA 230KV CKT 1 | E | EES | EES | AMSNSH |  | 0 | 336131 | 6ADMSCRK 230.00 | 336136 | 6BOGALUS 230.00 | 0 |  | 1 | 12WP | 883 | 883 | 0 | 95.5 | 95.526 | 96.2 | [7 empty] | CATEGORYB | SINGLE | ADAMS CREEK - BOGALUSA 230KV CKT 2 | 0 | 336131 | 6ADMSCRK 230.00 | 336136 | 6BOGALUS 230.00 | 0 |  | 2 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3225512WP | FROM->TO | ADAMS CREEK - BOGALUSA 230KV CKT 2 | E | EES | EES | AMSNSH |  | 0 | 336131 | 6ADMSCRK 230.00 | 336136 | 6BOGALUS 230.00 | 0 |  | 2 | 12WP | 883 | 883 | 0 | 95.5 | 95.4828 | 96.1 | [7 empty] | CATEGORYB | SINGLE | ADAMS CREEK - BOGALUSA 230KV CKT 1 | 0 | 336131 | 6ADMSCRK 230.00 | 336136 | 6BOGALUS 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4695512WP | FROM->TO | ANADARKO 138/13.8KV TRANSFORMER CKT 1 | E | WFEC | WFEC | FLA | FLA | 0 | 520811 | ANADRK4 13.800 | 520814 | ANADARK4 138.00 | 0 |  | 1 | 12WP | 125 | 140 | 140 |  | 93.7292 | 96.6 | [7 empty] | CATEGORYB | SINGLE | WOODWARD DISTRICT EHV (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T735512WP | FROM->TO | ANADARKO 138/13.8KV TRANSFORMER CKT 1 | E | WFEC | WFEC | FLA | FLA | 0 | 520811 | ANADRK4 13.800 | 520814 | ANADARK4 138.00 | 0 |  | 1 | 12WP | 125 | 140 | 140 |  | 93.7708 | 96.7 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WOODWARD DISTRICT EHV 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2305512WP | TO->FROM | BARKERS 6 230.00 - BOGALUSA 230KV CKT 1 | E | EES | CLEC |  | CLE_EAST | 0 | 336136 | 6BOGALUS 230.00 | 500025 | BARKERS 6 230.00 | 0 |  | 1 | 12WP | 431 | 454 | 0 | 98.4 | 98.4122 | 99.1 | [7 empty] | CATEGORYB | SINGLE | 6TALISK - BOGALUSA 230KV CKT 1 | 0 | 303221 | 6TALISK 230.00 | 336136 | 6BOGALUS 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2905512WP | TO->FROM | BOGALUSA - FRANKLIN 500KV CKT 1 | E | EES | EES | AEC | AMSNSH | 0 | 336562 | 8FRKLIN 500.00 | 336130 | 8BOGALUS 500.00 | 0 |  | 1 | 12WP | 1200 | 1200 | 0 |  | 93.9798 | 95.7 | [7 empty] | CATEGORYB | SINGLE | FRANKLIN - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 336562 | 8FRKLIN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T7335512WP | TO->FROM | BOGALUSA - FRANKLIN 500KV CKT 1 | E | EES | EES | AEC | AMSNSH | 0 | 336562 | 8FRKLIN 500.00 | 336130 | 8BOGALUS 500.00 | 0 |  | 1 | 12WP | 1200 | 1200 | 0 |  | 93.5689 | 95.2 | [7 empty] | CATEGORYB | NONSINGLE | CELE-WELLOP1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1725512WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | E | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 12WP | 100 | 100 | 0 |  | 84.5334 | 97.4 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1755512WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | E | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 12WP | 100 | 100 | 0 |  | 85.5056 | 98.3 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1785512WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | E | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 12WP | 100 | 100 | 0 |  | 84.5134 | 96.7 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - PRATT 115KV CKT 1 | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | INVALID |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1675512WP | TO->FROM | COVERT 3 115.00 - SMITH CENTER 115KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539693 | SMITH-C3 115.00 | 539644 | COVERT 3 115.00 | 0 |  | 1 | 12WP | 59.8 | 59.8 | 0 |  | 81.523 | 98.609 | [7 empty] | CATEGORYB | SINGLE | ELLSWTP3 115.00 - MULLERGREN 115KV CKT 1 | 0 | 539642 | ELLSWTP3 115.00 | 539678 | GRTBEND3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | INVALID |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1685512WP | FROM->TO | COVERT 3 115.00 - WALDO 115KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539644 | COVERT 3 115.00 | 539698 | WALDO 3 115.00 | 0 |  | 1 | 12WP | 59.8 | 59.8 | 0 |  | 80.9123 | 98.035 | [7 empty] | CATEGORYB | SINGLE | ELLSWTP3 115.00 - MULLERGREN 115KV CKT 1 | 0 | 539642 | ELLSWTP3 115.00 | 539678 | GRTBEND3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | CONT-0400 - JEC - Hoyt 345kV |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1125512WP | FROM->TO | FLATRDG3 - HARPER 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 12WP | 100 | 100 | 100 |  | 85.9882 | 99.1 | [7 empty] | CATEGORYB | SINGLE | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | CONT-0300 - Benton - Wolf Creek 345kV |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1225512WP | FROM->TO | FLATRDG3 - HARPER 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 12WP | 100 | 100 | 100 |  | 87.8918 | 99.4 | [7 empty] | CATEGORYB | SINGLE | BENTON - WOLF CREEK 345KV CKT 1 | 0 | 532791 | BENTON 7 345.00 | 532797 | WOLFCRK7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1425512WP | FROM->TO | FLATRDG3 - HARPER 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 12WP | 100 | 100 | 100 |  | 86.3961 | 99.9 | [7 empty] | CATEGORYB | SINGLE | CENTENNIAL - COWSKIN 138KV CKT 1 | 0 | 533034 | CENTENN4 138.00 | 533038 | COWSKIN4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T35512WP | FROM->TO | FLATRDG3 - HARPER 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 12WP | 100 | 100 | 100 |  | 83.9904 | 95.7 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T7765512WP | FROM->TO | FLATRDG3 - HARPER 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 12WP | 100 | 100 | 100 |  | 87.4877 | 99.8 | [7 empty] | CATEGORYB | GENOUT | GEN335831 1-RIVERBEND UNIT#1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4665512WP | FROM->TO | FPL SWITCH - MOORELAND 138KV CKT 1 | E | OKGE | WFEC | ENID | AEP-OP | 0 | 515785 | WINDFRM4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 12WP | 287 | 287 | 0 | 97.9 | 97.9425 | 97.4 | [7 empty] | CATEGORYB | SINGLE | WOODWARD DISTRICT EHV (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4625512WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 12WP | 171 | 185 | 0 | 100.7 | 100.7251 | 99.9 | [7 empty] | CATEGORYB | SINGLE | WOODWARD DISTRICT EHV (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1325512WP | FROM->TO | GREENLEAF - KNOB HILL 115KV CKT 1 | E | SUNC | WERE | GREAT PL | NCENTRAL | 0 | 539665 | GRNLEAF3 115.00 | 533332 | KNOB HL3 115.00 | 0 |  | 1 | 12WP | 92 | 92 | 0 |  | 93.2707 | 97.5 | [7 empty] | CATEGORYB | SINGLE | ELM CREEK - NORTHWEST MANHATTAN 230KV CKT 1 | 0 | 532865 | NWMANHT6 230.00 | 539639 | ELMCREK6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1705512WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 12WP | 95.6 | 95.6 | 0 |  | 82.4529 | 95.5 | [7 empty] | CATEGORYB | SINGLE | NINNESC3 115.00 - PRATT 115KV CKT 1 | 0 | 539648 | NINNESC3 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | ISLAND-LOAD |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T5205512WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 12WP | 95.6 | 95.6 | 0 |  | 84.4345 | 96.7 | [7 empty] | CATEGORYB | SINGLE | HARPER (HARPER 4) 138/34.5/8.66KV TRANSFORMER CKT 1 | 1 | 539668 | HARPER 4 138.00 | 539713 | HARPER 1 34.500 | 539913 | HARPER-T 8.6600 | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T905512WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 12WP | 95.6 | 95.6 | 0 |  | 89.3688 | 96.8 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | CONT-1202 - Jarbalo - Stranger Creek 115kV | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1895512WP | FROM->TO | IATAN - STRANGER CREEK 345KV CKT 1 | E | KCPL | WERE | KACP | NEAST | 0 | 542982 | IATAN 7 345.00 | 532772 | STRANGR7 345.00 | 0 |  | 1 | 12WP | 1195 | 1195 | 0 | 96 | 95.9885 | 95.7 | [7 empty] | CATEGORYB | SINGLE | IATAN - ST JOE 345KV CKT 1 | 0 | 541199 | ST JOE 3 345.00 | 542982 | IATAN 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2155512WP | FROM->TO | JAGUAR - POINT ESSO TAP 230KV CKT 1 | E | EES | EES | GSLBTR | GSLBTR | 0 | 335770 | 6JAGUAR 230.00 | 335641 | 6TP.ESSO 230.00 | 0 |  | 1 | 12WP | 685 | 685 | 0 | 97 | 96.9737 | 97.2 | [7 empty] | CATEGORYB | SINGLE | 6CAJUN1 - WATERLOO 230KV CKT 1 | 0 | 303000 | 6CAJUN1 230.00 | 335827 | 6WATLOO 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2555512WP | FROM->TO | JAGUAR - POINT ESSO TAP 230KV CKT 1 | E | EES | EES | GSLBTR | GSLBTR | 0 | 335770 | 6JAGUAR 230.00 | 335641 | 6TP.ESSO 230.00 | 0 |  | 1 | 12WP | 685 | 685 | 0 | 96.2 | 96.2177 | 96.4 | [7 empty] | CATEGORYB | SINGLE | COLY - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WGLEN 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1195512WP | TO->FROM | MUND - PENTAGON 115KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 533261 | PENTAGN3 115.00 | 533282 | MUND 3 115.00 | 0 |  | 1 | 12WP | 179 | 194 | 0 | 98.5 | 98.4673 | 99.8 | [7 empty] | CATEGORYB | SINGLE | 87th STREET - CRAIG 345KV CKT 1 | 0 | 532775 | 87TH 7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T7935512WP | TO->FROM | NINEMILE POINT 230 - WATERFORD 230KV CKT 1 | E | EES | EES | AMSCOR | METDSG | 0 | 336154 | 6WATFRD 230.00 | 336250 | 69MILE 230.00 | 0 |  | 1 | 12WP | 797 | 797 | 0 |  | 94.8283 | 95.1 | [7 empty] | CATEGORYB | GENOUT | GEN336251 1-NINEMILE POINT UNIT#4 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T365512WP | TO->FROM | RAPIDES - RODEMACHER 230KV CKT 1 | E | CLEC | CLEC | CLE_CENTRAL | CLE_CENTRAL | 0 | 500770 | RODEMR 6 230.00 | 500760 | RAPIDES6 230.00 | 0 |  | 1 | 12WP | 725 | 735 | 0 |  | 93.5385 | 95.1 | [7 empty] | CATEGORYB | SINGLE | RODEMACHER - SHERWOOD 230KV CKT 1 | 0 | 500770 | RODEMR 6 230.00 | 500790 | SHERWD 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T2725012WP | FROM->TO | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 2 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532826 | ROSEH1 1 13.800 | 1 | 12WP | 400 | 440 | 500 | 96.6 | 96.6008 | 96.2 | [7 empty] | CATEGORYB | SINGLE | ROSE HILL (ROSEHL3X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532827 | ROSEH3 1 13.800 | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T2715012WP | FROM->TO | ROSE HILL (ROSEHL3X) 345/138/13.8KV TRANSFORMER CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 2 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532827 | ROSEH3 1 13.800 | 1 | 12WP | 400 | 440 | 500 | 96.6 | 96.645 | 96.3 | [7 empty] | CATEGORYB | SINGLE | ROSE HILL (ROSEHL1X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532794 | ROSEHIL7 345.00 | 533062 | ROSEHIL4 138.00 | 532826 | ROSEH1 1 13.800 | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2885512WP | FROM->TO | WEBRE - WILLOW GLEN 500KV CKT 1 | E | EES | EES | GSLBTR | GSLBTR | 0 | 335500 | 8WEBRE 500.00 | 335618 | 8WGLEN 500.00 | 0 |  | 1 | 12WP | 1732 | 1732 | 0 | 96 | 96.0433 | 96.7 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SPP_FG-EES-IDC-15730 | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2475512WP | FROM->TO | WILLOW GLEN 500/138KV TRANSFORMER CKT 1 | E | EES | EES | GSLBTR | GSLBTR | 0 | 335618 | 8WGLEN 500.00 | 335601 | 4WGLEN-2 138.00 | 0 |  | 1 | 12WP | 560 | 560 | 0 | 97.4 | 97.3517 | 98 | [7 empty] | CATEGORYB | SINGLE | WILLOW GLEN 500/230KV TRANSFORMER CKT 1 | 0 | 335568 | 6WGLEN 230.00 | 335618 | 8WGLEN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2295512WP | FROM->TO | WILLOW GLEN 500/230KV TRANSFORMER CKT 1 | E | EES | EES | GSLBTR | GSLBTR | 0 | 335618 | 8WGLEN 500.00 | 335568 | 6WGLEN 230.00 | 0 |  | 1 | 12WP | 672 | 672 | 0 | 97 | 97.0415 | 97.5 | [7 empty] | CATEGORYB | SINGLE | 6VIGNES - COLY 230KV CKT 1 | 0 | 303200 | 6VIGNES 230.00 | 335771 | 6COLY 2 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2455512WP | FROM->TO | WILLOW GLEN 500/230KV TRANSFORMER CKT 1 | E | EES | EES | GSLBTR | GSLBTR | 0 | 335618 | 8WGLEN 500.00 | 335568 | 6WGLEN 230.00 | 0 |  | 1 | 12WP | 672 | 672 | 0 | 97.5 | 97.5067 | 97.9 | [7 empty] | CATEGORYB | SINGLE | WILLOW GLEN 230/138KV TRANSFORMER CKT 1 | 0 | 335568 | 6WGLEN 230.00 | 335601 | 4WGLEN-2 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3335513SP | TO->FROM | 3RD & VAN BUREN - MEADOWLARK 115KV CKT 1 | E | WERE | WERE | WEST | WEST | 0 | 533441 | MEADOW 115.00 | 533435 | 3 VANBU3 115.00 | 0 |  | 1 | 13SP | 68 | 68 | 0 |  | 90.8377 | 97.2 | [7 empty] | CATEGORYB | SINGLE | 3RD & VAN BUREN - MEADOWLARK 115KV CKT 2 | 0 | 533435 | 3 VANBU3 115.00 | 533441 | MEADOW 115.00 | 0 |  | 2 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T5575513SP | TO->FROM | 3WOODW-S 115.00 - PINE BLUFF ARSENAL D 115KV CKT 1 | E | EES | EES | EAISTH | EAISTH | 0 | 337647 | 3PB-ARD 115.00 | 337619 | 3WOODW-S 115.00 | 0 |  | 1 | 13SP | 239 | 239 | 0 | 97.4 | 97.3736 | 99.1 | [7 empty] | CATEGORYB | SINGLE | PINE BLUFF INDUSTRIAL - PINE BLUFF WHITE HALL 115KV CKT 1 | 0 | 337644 | 3PB IND 115.00 | 337645 | 3PB-WH 115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4145513SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13SP | 615 | 615 | 0 | 95.1 | 95.0925 | 95.1 | [7 empty] | CATEGORYB | SINGLE | 8CAJUN2 - WEBRE 500KV CKT 1 | 0 | 303005 | 8CAJUN2 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T4385013SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13SP | 615 | 615 | 0 | 95.3 | 95.2513 | 95.1 | [7 empty] | CATEGORYB | SINGLE | ELDORADO EHV - STERLINGTON 500KV CKT 1 | 0 | 337420 | 8STERL 500.00 | 337561 | 8ELDEHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4585513SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13SP | 615 | 615 | 0 | 95.1 | 95.0715 | 95 | [7 empty] | CATEGORYB | SINGLE | DYNEGY - PECAN GROVE 230KV CKT 1 | 0 | 335074 | 6DYNEGY 230.00 | 335077 | 6PGROVE 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4715513SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13SP | 615 | 615 | 0 | 95.1 | 95.1483 | 95.1 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T4195013SP | FROM->TO | BAXTER WILSON SES - SOUTHEAST VICKSBURG 115KV CKT 1 | E | EES | EES | EMI-VICK | EMI-VICK | 0 | 336800 | 3B.WLSN 115.00 | 336960 | 3SE-VKS 115.00 | 0 |  | 1 | 13SP | 161 | 161 | 0 | 96.1 | 96.0625 | 99 | [7 empty] | CATEGORYB | SINGLE | 3HAINRD 115.00 - VICKSBURG WEST 115KV CKT 1 | 0 | 336959 | 3HAINRD 115.00 | 336962 | 3VKSB-W 115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3935513SP | FROM->TO | BEAVER - EUREKA SPRINGS 161KV CKT 1 | E | SWPA | AEPW | EMINTH | FAYETTEVILLE | 0 | 505480 | BEAVER 5 161.00 | 506932 | EUREKA 5 161.00 | 0 |  | 1 | 13SP | 236 | 247 | 0 |  | 88.0974 | 96.5 | [7 empty] | CATEGORYB | SINGLE | 7JASPER 345.00 - MORGAN 345KV CKT 1 | 0 | 300045 | 7MORGAN 345.00 | 300949 | 7JASPER 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T6215013SP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 13SP | 68 | 68 | 0 | 96.9 | 96.8769 | 95 | [7 empty] | CATEGORYB | SINGLE | JONESBORO - JONESBORO 161KV CKT 1 | 0 | 505418 | JONESBO5 161.00 | 338170 | 5JONES 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T7115513SP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 13SP | 68 | 68 | 0 |  | 92.9118 | 96.3 | [7 empty] | CATEGORYB | SINGLE | JONESBORO - JONESBORO 161KV CKT 1 | 0 | 505418 | JONESBO5 161.00 | 338170 | 5JONES 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T7505013SP | FROM->TO | BORDEN COUNTY INTERCHANGE (ABB LL58862) 230/138/13.2KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CAPR | 1 | 526830 | BORDEN 6230.00 | 522896 | CR-VEALMOOR4138.00 | 526827 | BORDEN_TR1 113.200 | 1 | 13SP | 168 | 168 | 0 | 97.2 | 97.2061 | 97.2 | [7 empty] | CATEGORYB | SINGLE | MIDLAND COUNTY INTERCHANGE (ABB LLL58861) 230/138/13.2KV TRANSFORMER CKT 1 | 1 | 522992 | CR-GARNDALE4138.00 | 527914 | MIDLAND 6230.00 | 527912 | MIDLND_TR1 113.200 | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T13655513SP | FROM->TO | BULL SHOALS - MIDWAY (YVEPA) 161KV CKT 1 | E | SWPA | EES | EMINTH |  | 0 | 505460 | BULL SH5 161.00 | 338813 | 5MIDWAY# 161.00 | 0 |  | 1 | 13SP | 162 | 162 | 0 |  | 82.8802 | 96.2 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPA-05 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T635513SP | FROM->TO | BULL SHOALS - MIDWAY (YVEPA) 161KV CKT 1 | E | SWPA | EES | EMINTH |  | 0 | 505460 | BULL SH5 161.00 | 338813 | 5MIDWAY# 161.00 | 0 |  | 1 | 13SP | 162 | 162 | 0 |  | 82.5257 | 95.8 | [7 empty] | CATEGORYB | SINGLE | BUFORD 5 161.00 - NORFORK 161KV CKT 1 | 0 | 504440 | BUFORD 5 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T645513SP | FROM->TO | BULL SHOALS - MIDWAY (YVEPA) 161KV CKT 1 | E | SWPA | EES | EMINTH |  | 0 | 505460 | BULL SH5 161.00 | 338813 | 5MIDWAY# 161.00 | 0 |  | 1 | 13SP | 162 | 162 | 0 |  | 84.1683 | 97.4 | [7 empty] | CATEGORYB | SINGLE | BUFORD 5 161.00 - BULL SHOALS 161KV CKT 1 | 0 | 504440 | BUFORD 5 161.00 | 505460 | BULL SH5 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T13945513SP | TO->FROM | CLAY - SPRINGFIELD 161KV CKT 1 | E | SWPA | SPRM | EMINTH | SPRM > 69KV | 0 | 505492 | SPRGFLD5 161.00 | 549970 | CLAY 5161.00 | 0 |  | 1 | 13SP | 167 | 167 | 0 |  | 88.8314 | 97.6 | [7 empty] | CATEGORYB | NONSINGLE | AI03 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3745513SP | TO->FROM | CLAY - SPRINGFIELD 161KV CKT 1 | E | SWPA | SPRM | EMINTH | SPRM > 69KV | 0 | 505492 | SPRGFLD5 161.00 | 549970 | CLAY 5161.00 | 0 |  | 1 | 13SP | 167 | 167 | 0 |  | 89.4582 | 96.7 | [7 empty] | CATEGORYB | SINGLE | JAMES RIVER - SOUTHWEST 161KV CKT 1 | 0 | 549954 | SWPS 5161.00 | 549961 | JAMES RIVER5161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3455513SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | E | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13SP | 100 | 100 | 0 |  | 76.315 | 95.6 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3475513SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | E | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13SP | 100 | 100 | 0 |  | 77.7952 | 97.1 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8655513SP | FROM->TO | DEAF SMITH COUNTY INTERCHANGE (ELCO 13458-1) 230/115/13.8KV TRANSFORMER CKT 2 | E | SPS | SPS | SPS-CLHF | SPS-CLHF | 1 | 524623 | DEAFSMITH 6230.00 | 524622 | DEAFSMITH 3115.00 | 524621 | DEFSMTH_TR2113.800 | 2 | 13SP | 168 | 193 | 0 | 97.6 | 97.5871 | 99.3 | [7 empty] | CATEGORYB | SINGLE | DEAF SMITH COUNTY INTERCHANGE (GE M101353) 230/115/13.2KV TRANSFORMER CKT 1 | 1 | 524622 | DEAFSMITH 3115.00 | 524623 | DEAFSMITH 6230.00 | 524620 | DEFSMTH_TR1113.200 | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8625513SP | FROM->TO | DEAF SMITH COUNTY INTERCHANGE (GE M101353) 230/115/13.2KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CLHF | SPS-CLHF | 1 | 524623 | DEAFSMITH 6230.00 | 524622 | DEAFSMITH 3115.00 | 524620 | DEFSMTH_TR1113.200 | 1 | 13SP | 168 | 193 | 0 | 95.9 | 95.8706 | 97.6 | [7 empty] | CATEGORYB | SINGLE | DEAF SMITH COUNTY INTERCHANGE (ELCO 13458-1) 230/115/13.8KV TRANSFORMER CKT 2 | 1 | 524622 | DEAFSMITH 3115.00 | 524623 | DEAFSMITH 6230.00 | 524621 | DEFSMTH_TR2113.800 | 2 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3575513SP | FROM->TO | EASTOWN7 345.00 (EASTOWN 345) 345/161/13.8KV TRANSFORMER CKT 1 | E | GMO | GMO |  |  | 2 | 541400 | EASTOWN7 345.00 | 541401 | EASTWON5 161.00 | 541402 | EASTOWN1 13.800 | 1 | 13SP | 400 | 440 | 0 | 97.7 | 97.7356 | 98.5 | [7 empty] | CATEGORYB | SINGLE | EASTOWN7 345.00 - ST JOE 345KV CKT 1 | 0 | 541199 | ST JOE 3 345.00 | 541400 | EASTOWN7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | INVALID |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3245513SP | FROM->TO | EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533040 | EVANS N4 138.00 | 533054 | MAIZE 4 138.00 | 0 |  | 1 | 13SP | 382 | 382 | 0 |  | 91.9557 | 96.2701 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER NORTH - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533040 | EVANS N4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T1285013SP | FROM->TO | FRANKLIN SW (FRANKLIN) 138/69/13.8KV TRANSFORMER CKT 1 | E | WFEC | WFEC | AEP-IM-I | AEP-IM-I | 1 | 520917 | FRNKLNS4 138.00 | 520916 | FRNKLNS2 69.000 | 521169 | FRNKTERT 13.800 | 1 | 13SP | 70 | 70 | 70 | 95.8 | 95.7765 | 95.6 | [7 empty] | CATEGORYB | SINGLE | CANADIAN SW - GOLDSBY 138KV CKT 1 | 0 | 520842 | CANADNS4 138.00 | 520924 | GOLDSBY4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T4265013SP | FROM->TO | GREENVILLE - GREENVILLE EAST 115KV CKT 1 | E | EES | EES | EMI-GRNVL | EMI-GRNVL | 0 | 337044 | 3GRNVIL 115.00 | 337076 | 3GRNV-E 115.00 | 0 |  | 1 | 13SP | 120 | 120 | 0 |  | 84.9294 | 97 | [7 empty] | CATEGORYB | SINGLE | GREENVILLE - GREENVILLE MIDTOWN 115KV CKT 1 | 0 | 337044 | 3GRNVIL 115.00 | 337075 | 3GR-MID 115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1965513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 |  | 81.7852 | 96.5 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T9465513SP | FROM->TO | HAYS PLANT - VINE STREET 115KV CKT 1 | E | MIDW | MIDW | REG E-IL | REG E-IL | 0 | 530562 | HAYS 3 115.00 | 530591 | VINE 3 115.00 | 0 |  | 1 | 13SP | 80 | 88 | 0 |  | 62.6821 | 97.6 | [7 empty] | CATEGORYB | SINGLE | KNOLL 230 (KNOLL T1) 230/115/11.49KV TRANSFORMER CKT 1 | 1 | 530558 | KNOLL 6 230.00 | 530561 | KNOLL 3 115.00 | 530629 | KNLL1 1 11.490 | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | TOD Dolett OP Guide | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T475013SP | FROM->TO | INTERNATIONAL PAPER - WALLACE LAKE 138KV CKT 1 | E | CLEC | AEPW | CLE_IND | SHREVEPORT | 0 | 500430 | IPAPER 4 138.00 | 507765 | WALLAKE4 138.00 | 0 |  | 1 | 13SP | 180 | 209 | 0 | 100.3 | 100.3174 | 96.6 | [7 empty] | CATEGORYB | SINGLE | DOLET HILLS - SOUTHWEST SHREVEPORT 345KV CKT 1 | 0 | 500250 | DOLHILL7 345.00 | 507760 | SW SHV 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | INVALID | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T1495013SP | TO->FROM | LEA COUNTY REC -MHOON - LEA COUNTY REC-LOVINGTON INTERCHANGE 69KV CKT 1 | E | SPS | SPS | SPS-LEA | SPS-LEA | 0 | 528618 | LE-LOVINTON269.000 | 528667 | LE-MHOON 269.000 | 0 |  | 1 | 13SP | 41 | 54 | 0 | 96.8 | 96.7736 | 96.0828 | [7 empty] | CATEGORYB | SINGLE | BUCKEYE TAP - CUNNINGHAM STATION 115KV CKT 1 | 0 | 527864 | CUNNINHAM 3115.00 | 528348 | BUCKEYE_TP 3115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3205513SP | FROM->TO | LYONS - WHEATLAND 115KV CKT 1 | E | WERE | WERE | REG E-IL | WEST | 0 | 530620 | LYONS 3 115.00 | 533439 | WHEATLD3 115.00 | 0 |  | 1 | 13SP | 159 | 159 | 0 |  | 37.4677 | 96.5 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - RICECO 230.00 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 560012 | RICECO 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1975513SP | FROM->TO | MULLERGREN 115/13.8KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539677 | GRTBEND1 13.800 | 539678 | GRTBEND3 115.00 | 0 |  | 1 | 13SP | 106 | 106 | 106 | 97.5 | 97.5458 | 98 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T7595013SP | FROM->TO | OASIS INTERCHANGE (ABB LLM60041) 230/115/13.2KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CLHF | SPS-CLHF | 1 | 524875 | OASIS 6230.00 | 524874 | OASIS 3115.00 | 524872 | OASIS_TR1 113.200 | 1 | 13SP | 248 | 285 | 0 | 97.9 | 97.9499 | 97.7 | [7 empty] | CATEGORYB | SINGLE | ROOSEVELT COUNTY INTERCHANGE (ABB LMM60042) 230/115/13.2KV TRANSFORMER CKT 1 | 1 | 524908 | ROOSEVELT 3115.00 | 524909 | ROSEVELT_N 6230.00 | 524907 | ROSEVLT_TR1113.200 | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T4225013SP | FROM->TO | ONWARD - ROLLING FORK 115KV CKT 1 | E | EES | EES | EMI-GRNVL | EMI-GRNVL | 0 | 336967 | 3ONWARD 115.00 | 336968 | 3R.FORK 115.00 | 0 |  | 1 | 13SP | 87 | 87 | 0 |  | 89.8095 | 96.3 | [7 empty] | CATEGORYB | SINGLE | GERALD ANDRUS SES 230/115KV TRANSFORMER CKT 1 | 0 | 337040 | 6ANDRUS 230.00 | 337042 | 3ANDRUS 115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T7455013SP | FROM->TO | OUSW4 (OW SW) 138/69/13.8KV TRANSFORMER CKT 1 | E | WFEC | WFEC | AEP-IM-I | AEP-IM-I | 1 | 521104 | OU SW 4 138.00 | 521018 | OU SW 2 69.000 | 521183 | OUSWTERT 13.800 | 1 | 13SP | 70 | 70 | 70 | 95.5 | 95.4971 | 95.2 | [7 empty] | CATEGORYB | SINGLE | FRANKLIN SW (FRANKLIN) 138/69/13.8KV TRANSFORMER CKT 1 | 1 | 520916 | FRNKLNS2 69.000 | 520917 | FRNKLNS4 138.00 | 521169 | FRNKTERT 13.800 | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T5635513SP | FROM->TO | PINE BLUFF ARSENAL C - PINE BLUFF WHITE HALL 115KV CKT 1 | E | EES | EES | EAISTH | EAISTH | 0 | 337646 | 3PB-ARC 115.00 | 337645 | 3PB-WH 115.00 | 0 |  | 1 | 13SP | 266 | 266 | 0 |  | 94.6618 | 96.2 | [7 empty] | CATEGORYB | SINGLE | PINE BLUFF ARSENAL D - WHITE BLUFF 115KV CKT 1 | 0 | 337647 | 3PB-ARD 115.00 | 337648 | 3WH BLF 115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T5585513SP | TO->FROM | PINE BLUFF ARSENAL D - WHITE BLUFF 115KV CKT 1 | E | EES | EES | EAISTH | EAISTH | 0 | 337648 | 3WH BLF 115.00 | 337647 | 3PB-ARD 115.00 | 0 |  | 1 | 13SP | 255 | 255 | 0 | 96.7 | 96.7129 | 98.3 | [7 empty] | CATEGORYB | SINGLE | PINE BLUFF INDUSTRIAL - PINE BLUFF WHITE HALL 115KV CKT 1 | 0 | 337644 | 3PB IND 115.00 | 337645 | 3PB-WH 115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T215513SP | FROM->TO | PLANT X STATION (WH ALM20171) 230/115/13.2KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 2 | 525481 | PLANT_X 6230.00 | 525480 | PLANT_X 3115.00 | 525479 | PLANTX_TR1 113.200 | 1 | 13SP | 239 | 239 | 0 |  | 79.0665 | 95.6 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2405513SP | FROM->TO | PLANT X STATION (WH ALM20171) 230/115/13.2KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 2 | 525481 | PLANT_X 6230.00 | 525480 | PLANT_X 3115.00 | 525479 | PLANTX_TR1 113.200 | 1 | 13SP | 239 | 239 | 0 |  | 82.7853 | 99.8 | [7 empty] | CATEGORYB | SINGLE | HALE CO INTERCHANGE - KRESS INTERCHANGE 115KV CKT 1 | 0 | 525192 | KRESS_INT 3115.00 | 525454 | HALE_CNTY 3115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2665513SP | FROM->TO | PLANT X STATION (WH ALM20171) 230/115/13.2KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 2 | 525481 | PLANT_X 6230.00 | 525480 | PLANT_X 3115.00 | 525479 | PLANTX_TR1 113.200 | 1 | 13SP | 239 | 239 | 0 |  | 82.5248 | 99.3 | [7 empty] | CATEGORYB | SINGLE | SUNDOWN INTERCHANGE - WOLFFORTH INTERCHANGE 230KV CKT 1 | 0 | 526435 | SUNDOWN 6230.00 | 526525 | WOLFFORTH 6230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8675513SP | FROM->TO | PLANT X STATION (WH ALM20171) 230/115/13.2KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 1 | 525481 | PLANT_X 6230.00 | 525480 | PLANT_X 3115.00 | 525479 | PLANTX_TR1 113.200 | 1 | 13SP | 239 | 239 | 0 |  | 83.1505 | 99.7 | [7 empty] | CATEGORYB | SINGLE | DEAF SMITH COUNTY INTERCHANGE (GE M101353) 230/115/13.2KV TRANSFORMER CKT 1 | 1 | 524622 | DEAFSMITH 3115.00 | 524623 | DEAFSMITH 6230.00 | 524620 | DEFSMTH_TR1113.200 | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SPP_FG-5219 - STIREDSTIPEC | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3565513SP | TO->FROM | REDEL - STILWELL 161KV CKT 1 | E | KCPL | KCPL | JOCO | JOCO | 0 | 542969 | STILWEL5 161.00 | 543053 | REDEL 5 161.00 | 0 |  | 1 | 13SP | 293 | 334 | 0 | 95.9 | 95.9495 | 99.5 | [7 empty] | CATEGORYB | SINGLE | PECULIAR - STILWELL 345KV CKT 1 | 0 | 541198 | PECULR 7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T1395013SP | FROM->TO | ROOSEVELT COUNTY INTERCHANGE (ABB LMM60042) 230/115/13.2KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CLHF | SPS-CLHF | 2 | 524909 | ROSEVELT_N 6230.00 | 524908 | ROOSEVELT 3115.00 | 524907 | ROSEVLT_TR1113.200 | 1 | 13SP | 252 | 290 | 0 |  | 94.9252 | 95 | [7 empty] | CATEGORYB | SINGLE | OASIS INTERCHANGE - Roosevelt County Interchange SWITCH #4K33 230KV CKT 1 | 0 | 524875 | OASIS 6230.00 | 524915 | SW_4K33 6230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T7575013SP | FROM->TO | ROOSEVELT COUNTY INTERCHANGE (ABB LMM60042) 230/115/13.2KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CLHF | SPS-CLHF | 1 | 524909 | ROSEVELT_N 6230.00 | 524908 | ROOSEVELT 3115.00 | 524907 | ROSEVLT_TR1113.200 | 1 | 13SP | 252 | 290 | 0 | 99.5 | 99.5487 | 99.3 | [7 empty] | CATEGORYB | SINGLE | OASIS INTERCHANGE (ABB LLM60041) 230/115/13.2KV TRANSFORMER CKT 1 | 1 | 524874 | OASIS 3115.00 | 524875 | OASIS 6230.00 | 524872 | OASIS_TR1 113.200 | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | INVALID | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T1795013SP | FROM->TO | SEVENTEENTH (17TH 4X) 138/69/11.295KV TRANSFORMER CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 1 | 533064 | 17TH 4 138.00 | 533840 | 17TH 2 69.000 | 533112 | 17TH 4 1 11.295 | 1 | 13SP | 150 | 165 | 187.5 | 99.4 | 99.444 | 98.4207 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER NORTH - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533040 | EVANS N4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T11805013SP | FROM->TO | SUB 1206 (S1206 T2) 161/69/13.8KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 1 | 646206 | S1206 5 161.00 | 647006 | S906 N 8 69.000 | 648306 | S1206T29 13.800 | 1 | 13SP | 201.6 | 201.6 | 201.6 | 96.3 | 96.3162 | 95.7 | [7 empty] | CATEGORYB | NONSINGLE | S1206T1 BSCL | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T11815013SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 13SP | 250 | 250 | 250 | 95.1 | 95.0904 | 95.3 | [7 empty] | CATEGORYB | NONSINGLE | S1217 AUTOV2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T13595513SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 13SP | 250 | 250 | 250 | 95.3 | 95.32 | 95.3 | [7 empty] | CATEGORYB | NONSINGLE | S1217 AUTOV2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T5285013SP | FROM->TO | TRUMANN - TRUMANN WEST AECC 161KV CKT 1 | E | EES | EES | EAINTH |  | 0 | 338169 | 5TRUMAN 161.00 | 338707 | 5TRUM-W# 161.00 | 0 |  | 1 | 13SP | 148 | 148 | 0 | 96.7 | 96.7176 | 96.9 | [7 empty] | CATEGORYB | SINGLE | CASH - NEWPORT AB 161KV CKT 1 | 0 | 338171 | 5CASH 161.00 | 338172 | 5NEW-AB 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T5295013SP | FROM->TO | TRUMANN - TRUMANN WEST AECC 161KV CKT 1 | E | EES | EES | EAINTH |  | 0 | 338169 | 5TRUMAN 161.00 | 338707 | 5TRUM-W# 161.00 | 0 |  | 1 | 13SP | 148 | 148 | 0 | 99.5 | 99.4933 | 99.7 | [7 empty] | CATEGORYB | SINGLE | NEWPORT AB - NEWPORT INDUSTRIAL 161KV CKT 1 | 0 | 338172 | 5NEW-AB 161.00 | 338173 | 5NEW-IN 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T1415013WP | FROM->TO | 6AIRLINE 230.00 - SORRENTO 230KV CKT 1 | E | LAGN | EES | WECC | AMSCOR | 0 | 303199 | 6AIRLINE 230.00 | 336060 | 6SORR 2 230.00 | 0 |  | 1 | 13WP | 519 | 519 | 0 | 97.1 | 97.1196 | 98.5 | [7 empty] | CATEGORYB | SINGLE | WATERFORD - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WGLEN 500.00 | 336150 | 8WATERFO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T2345013WP | FROM->TO | 6AIRLINE 230.00 - SORRENTO 230KV CKT 1 | E | LAGN | EES | WECC | AMSCOR | 0 | 303199 | 6AIRLINE 230.00 | 336060 | 6SORR 2 230.00 | 0 |  | 1 | 13WP | 519 | 519 | 0 | 97 | 97.0329 | 98.4 | [7 empty] | CATEGORYB | SINGLE | WATERFORD 500/230KV TRANSFORMER CKT 1 | 0 | 336150 | 8WATERFO 500.00 | 336154 | 6WATFRD 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T1155013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 96.2 | 96.1731 | 96.4 | [7 empty] | CATEGORYB | SINGLE | NELSON - RICHARD 500KV CKT 1 | 0 | 335192 | 8NELSON 500.00 | 335367 | 8RICHARD 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T1195013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 96.1 | 96.0525 | 96.2 | [7 empty] | CATEGORYB | SINGLE | WEBRE - WELLS 500KV CKT 1 | 0 | 335368 | 8WELLS 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T1395013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 96.7 | 96.6977 | 97 | [7 empty] | CATEGORYB | SINGLE | COLY - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WGLEN 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T1455013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 97.7 | 97.7156 | 97.9 | [7 empty] | CATEGORYB | SINGLE | WATERFORD - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WGLEN 500.00 | 336150 | 8WATERFO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T1545013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 96.7 | 96.7368 | 96.9 | [7 empty] | CATEGORYB | SINGLE | JAGUAR - POINT ESSO TAP 230KV CKT 1 | 0 | 335641 | 6TP.ESSO 230.00 | 335770 | 6JAGUAR 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T1685013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 96.4 | 96.357 | 96.5 | [7 empty] | CATEGORYB | SINGLE | ENJAY - JAGUAR 230KV CKT 1 | 0 | 335770 | 6JAGUAR 230.00 | 335772 | 6ENJAY 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T1745013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 96.5 | 96.5029 | 96.6 | [7 empty] | CATEGORYB | SINGLE | ENJAY - FANCY POINT 230KV CKT 1 | 0 | 335772 | 6ENJAY 230.00 | 335825 | 6FANCY 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T185513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 95.4 | 95.4445 | 95.6 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T1935013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 98 | 98.0496 | 98.2 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T205013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 96 | 95.9853 | 96.1 | [7 empty] | CATEGORYB | SINGLE | BARKERS 6 230.00 - RAMSAY 230KV CKT 1 | 0 | 500025 | BARKERS 6 230.00 | 500750 | RAMSAY 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T2175013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 96.8 | 96.7913 | 97 | [7 empty] | CATEGORYB | SINGLE | BOGALUSA 500/230KV TRANSFORMER CKT 1 | 0 | 336130 | 8BOGALUS 500.00 | 336131 | 6ADMSCRK 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2205513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 96.8 | 96.7737 | 96.9 | [7 empty] | CATEGORYB | SINGLE | 8CAJUN2 - WEBRE 500KV CKT 1 | 0 | 303005 | 8CAJUN2 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T225013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 95.8 | 95.8376 | 96 | [7 empty] | CATEGORYB | SINGLE | BAYOU SALE - TECHE 138KV CKT 1 | 0 | 500050 | BSALES 4 138.00 | 500820 | TECHE 4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T2305013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 97 | 97.0412 | 97.2 | [7 empty] | CATEGORYB | SINGLE | BOGALUSA - FRANKLIN 500KV CKT 1 | 0 | 336130 | 8BOGALUS 500.00 | 336562 | 8FRKLIN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T235013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 95.8 | 95.8425 | 96 | [7 empty] | CATEGORYB | SINGLE | BAYOU SALE - WAXLAKE 138KV CKT 1 | 0 | 500050 | BSALES 4 138.00 | 500890 | WAXLAKE4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T2385013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 97.1 | 97.1124 | 97.3 | [7 empty] | CATEGORYB | SINGLE | WATERFORD 500/230KV TRANSFORMER CKT 1 | 0 | 336150 | 8WATERFO 500.00 | 336154 | 6WATFRD 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T2545013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 95.9 | 95.8568 | 95.9 | [7 empty] | CATEGORYB | SINGLE | FRANKLIN - GRAND GULF 500KV CKT 1 | 0 | 336562 | 8FRKLIN 500.00 | 336820 | 8G.GULF 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2555513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 96.6 | 96.5552 | 96.7 | [7 empty] | CATEGORYB | SINGLE | HARTBURG - MOUNT OLIVE 500KV CKT 1 | 0 | 334325 | 8HARTBRG 500.00 | 337368 | 8MTOLIV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2625513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 |  | 95.8817 | 96.1 | [7 empty] | CATEGORYB | SINGLE | NELSON - RICHARD 500KV CKT 1 | 0 | 335192 | 8NELSON 500.00 | 335367 | 8RICHARD 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T265013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 96 | 95.9707 | 96.1 | [7 empty] | CATEGORYB | SINGLE | COCODRIE - VILLE PLATTE 230KV CKT 1 | 0 | 500190 | COCODR 6 230.00 | 500880 | VILPLT 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T2655013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 95.7 | 95.6516 | 95.8 | [7 empty] | CATEGORYB | SINGLE | ELDORADO EHV - MOUNT OLIVE 500KV CKT 1 | 0 | 337368 | 8MTOLIV 500.00 | 337561 | 8ELDEHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2665513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 96.4 | 96.4439 | 96.6 | [7 empty] | CATEGORYB | SINGLE | WEBRE - WELLS 500KV CKT 1 | 0 | 335368 | 8WELLS 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T2695013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 95.8 | 95.7768 | 95.8 | [7 empty] | CATEGORYB | SINGLE | ELDORADO EHV - STERLINGTON 500KV CKT 1 | 0 | 337420 | 8STERL 500.00 | 337561 | 8ELDEHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T275013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 95.8 | 95.756 | 95.9 | [7 empty] | CATEGORYB | SINGLE | COUGHLIN - PLAISANCE 138KV CKT 1 | 0 | 500230 | COUGH 4 138.00 | 500720 | PLAISAN4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2815513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 97.4 | 97.4032 | 97.6 | [7 empty] | CATEGORYB | SINGLE | COLY - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WGLEN 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T285013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 95.6 | 95.6444 | 95.9 | [7 empty] | CATEGORYB | SINGLE | EL PASO TAP - WAXLAKE 138KV CKT 1 | 0 | 500290 | ELPTAP 4 138.00 | 500890 | WAXLAKE4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2885513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 98 | 98.0017 | 98.2 | [7 empty] | CATEGORYB | SINGLE | WATERFORD - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WGLEN 500.00 | 336150 | 8WATERFO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T295013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 95.7 | 95.6929 | 95.8 | [7 empty] | CATEGORYB | SINGLE | MADISONVILLE - RAMSAY 230KV CKT 1 | 0 | 500510 | MADISON6 230.00 | 500750 | RAMSAY 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2975513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 97.1 | 97.0564 | 97.2 | [7 empty] | CATEGORYB | SINGLE | JAGUAR - POINT ESSO TAP 230KV CKT 1 | 0 | 335641 | 6TP.ESSO 230.00 | 335770 | 6JAGUAR 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3095513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 96.8 | 96.8343 | 97 | [7 empty] | CATEGORYB | SINGLE | ENJAY - FANCY POINT 230KV CKT 1 | 0 | 335772 | 6ENJAY 230.00 | 335825 | 6FANCY 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T3145013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 96.2 | 96.1768 | 96.3 | [7 empty] | CATEGORYB | SINGLE | BARKERS 6 230.00 - BOGALUSA 230KV CKT 1 | 0 | 500025 | BARKERS 6 230.00 | 336136 | 6BOGALUS 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3295513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 98.9 | -999 | 99 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3335513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 |  | 94.9771 | 95 | [7 empty] | CATEGORYB | SINGLE | FRANKLIN - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 336562 | 8FRKLIN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T335013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 95.8 | 95.8298 | 96 | [7 empty] | CATEGORYB | SINGLE | VILLE PLATTE - WESTFORK 230KV CKT 1 | 0 | 500880 | VILPLT 6 230.00 | 500920 | WSTFORK6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T345513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 96.3 | 96.3421 | 96.5 | [7 empty] | CATEGORYB | SINGLE | BARKERS 6 230.00 - RAMSAY 230KV CKT 1 | 0 | 500025 | BARKERS 6 230.00 | 500750 | RAMSAY 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS-CHECK-TC-Iteration Limit Exceeded. |  | 5 | 5 | 2011AGP1AFS91T3525513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 97 | 97.0404 | 97.2 | [7 empty] | CATEGORYB | SINGLE | BOGALUSA 500/230KV TRANSFORMER CKT 1 | 0 | 336130 | 8BOGALUS 500.00 | 336131 | 6ADMSCRK 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T355013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 95.7 | 95.714 | 95.8 | [7 empty] | CATEGORYB | SINGLE | WELLS - WESTFORK 230KV CKT 1 | 0 | 500920 | WSTFORK6 230.00 | 500940 | WELLS 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T355513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 96.1 | 96.0861 | 96.2 | [7 empty] | CATEGORYB | SINGLE | BAYOU SALE - TECHE 138KV CKT 1 | 0 | 500050 | BSALES 4 138.00 | 500820 | TECHE 4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS-CHECK-TC-Iteration Limit Exceeded. |  | 5 | 5 | 2011AGP1AFS91T3645513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 97.4 | 97.3765 | 97.5 | [7 empty] | CATEGORYB | SINGLE | BOGALUSA - FRANKLIN 500KV CKT 1 | 0 | 336130 | 8BOGALUS 500.00 | 336562 | 8FRKLIN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T365513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 96.1 | 96.0906 | 96.2 | [7 empty] | CATEGORYB | SINGLE | BAYOU SALE - WAXLAKE 138KV CKT 1 | 0 | 500050 | BSALES 4 138.00 | 500890 | WAXLAKE4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3735513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 97.3 | 97.2862 | 97.5 | [7 empty] | CATEGORYB | SINGLE | WATERFORD 500/230KV TRANSFORMER CKT 1 | 0 | 336150 | 8WATERFO 500.00 | 336154 | 6WATFRD 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3865513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 96.2 | 96.2213 | 96.2 | [7 empty] | CATEGORYB | SINGLE | FRANKLIN - GRAND GULF 500KV CKT 1 | 0 | 336562 | 8FRKLIN 500.00 | 336820 | 8G.GULF 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3925513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 |  | 95.8898 | 96.1 | [7 empty] | CATEGORYB | SINGLE | BAXTER WILSON SES - RAY BRASWELL SES 500KV CKT 1 | 0 | 336830 | 8B.WLSN 500.00 | 336839 | 8R.BRAS 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T395513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 96.2 | 96.2063 | 96.4 | [7 empty] | CATEGORYB | SINGLE | COCODRIE - VILLE PLATTE 230KV CKT 1 | 0 | 500190 | COCODR 6 230.00 | 500880 | VILPLT 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4025513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 96.6 | 96.5818 | 96.7 | [7 empty] | CATEGORYB | SINGLE | ELDORADO EHV - MOUNT OLIVE 500KV CKT 1 | 0 | 337368 | 8MTOLIV 500.00 | 337561 | 8ELDEHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T425513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 95.9 | 95.9397 | 96.1 | [7 empty] | CATEGORYB | SINGLE | COUGHLIN - PLAISANCE 138KV CKT 1 | 0 | 500230 | COUGH 4 138.00 | 500720 | PLAISAN4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T455513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 96 | 96.0499 | 96.2 | [7 empty] | CATEGORYB | SINGLE | MADISONVILLE - RAMSAY 230KV CKT 1 | 0 | 500510 | MADISON6 230.00 | 500750 | RAMSAY 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4755513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 96.5 | 96.5447 | 96.7 | [7 empty] | CATEGORYB | SINGLE | BARKERS 6 230.00 - BOGALUSA 230KV CKT 1 | 0 | 500025 | BARKERS 6 230.00 | 336136 | 6BOGALUS 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T495513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 96.1 | 96.0515 | 96.2 | [7 empty] | CATEGORYB | SINGLE | VILLE PLATTE - WESTFORK 230KV CKT 1 | 0 | 500880 | VILPLT 6 230.00 | 500920 | WSTFORK6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T515513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 |  | 95.9271 | 96.1 | [7 empty] | CATEGORYB | SINGLE | WELLS - WESTFORK 230KV CKT 1 | 0 | 500920 | WSTFORK6 230.00 | 500940 | WELLS 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T65013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 95.2 | 95.1541 | 95.2 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T6815013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 95.9 | 95.9238 | 96.1 | [7 empty] | CATEGORYB | NONSINGLE | CELE-WELLOP2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T6885013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 96 | 96.0175 | 96.2 | [7 empty] | CATEGORYB | NONSINGLE | SERCW-21 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T6915013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 96.4 | 96.4081 | 96.6 | [7 empty] | CATEGORYB | GENOUT | GEN303006 1-1BC2 U1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T6985013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 96.5 | 96.4902 | 96.7 | [7 empty] | CATEGORYB | GENOUT | GEN303008 1-1BC2 U3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T7115013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 96.8 | 96.8554 | 97 | [7 empty] | CATEGORYB | GENOUT | GEN335831 1-RIVERBEND UNIT#1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T7245013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 95.7 | 95.6682 | 95.8 | [7 empty] | CATEGORYB | GENOUT | GEN336170 1-GULF OXY U4 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T7315013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 97.6 | 97.6382 | 97.8 | [7 empty] | CATEGORYB | GENOUT | GEN336251 1-NINEMILE POINT UNIT#4 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T7635013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 |  | 95.6415 | 95.7 | [7 empty] | CATEGORYB | GENOUT | GEN501910 1-ACADIA UNIT ST1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8665513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 96.1 | 96.1271 | 96.3 | [7 empty] | CATEGORYB | NONSINGLE | CELE-WELLOP2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8815513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 96.1 | 96.1208 | 96.3 | [7 empty] | CATEGORYB | NONSINGLE | SERCW-21 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8875513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 96.9 | 96.9393 | 97.2 | [7 empty] | CATEGORYB | GENOUT | GEN303006 1-1BC2 U1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8905513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 97 | 97.0375 | 97.3 | [7 empty] | CATEGORYB | GENOUT | GEN303008 1-1BC2 U3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T895013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 96.4 | 96.366 | 96.4 | [7 empty] | CATEGORYB | SINGLE | 8CAJUN2 - WEBRE 500KV CKT 1 | 0 | 303005 | 8CAJUN2 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T9045513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 97.2 | 97.2552 | 97.6 | [7 empty] | CATEGORYB | GENOUT | GEN335831 1-RIVERBEND UNIT#1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T9195513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 96 | 96.0129 | 96.1 | [7 empty] | CATEGORYB | GENOUT | GEN336170 1-GULF OXY U4 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T9275513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 98.3 | 98.3125 | 98.5 | [7 empty] | CATEGORYB | GENOUT | GEN336251 1-NINEMILE POINT UNIT#4 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T9495513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 96 | 95.9807 | 96.1 | [7 empty] | CATEGORYB | GENOUT | GEN501910 1-ACADIA UNIT ST1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T5555513WP | FROM->TO | ANADARKO 138/13.8KV TRANSFORMER CKT 1 | E | WFEC | WFEC | FLA | FLA | 0 | 520811 | ANADRK4 13.800 | 520814 | ANADARK4 138.00 | 0 |  | 1 | 13WP | 125 | 140 | 140 |  | 93.1333 | 96.6 | [7 empty] | CATEGORYB | SINGLE | WOODWARD DISTRICT EHV (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T835513WP | FROM->TO | ANADARKO 138/13.8KV TRANSFORMER CKT 1 | E | WFEC | WFEC | FLA | FLA | 0 | 520811 | ANADRK4 13.800 | 520814 | ANADARK4 138.00 | 0 |  | 1 | 13WP | 125 | 140 | 140 |  | 93.1733 | 96.7 | [7 empty] | CATEGORYB | SINGLE | TATONGA7 345.00 - WOODWARD DISTRICT EHV 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3325513WP | TO->FROM | BARKERS 6 230.00 - BOGALUSA 230KV CKT 1 | E | EES | CLEC |  | CLE_EAST | 0 | 336136 | 6BOGALUS 230.00 | 500025 | BARKERS 6 230.00 | 0 |  | 1 | 13WP | 431 | 454 | 0 | 96.7 | 96.6655 | 98.9 | [7 empty] | CATEGORYB | SINGLE | FRANKLIN - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 336562 | 8FRKLIN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8645513WP | TO->FROM | BARKERS 6 230.00 - BOGALUSA 230KV CKT 1 | E | EES | CLEC |  | CLE_EAST | 0 | 336136 | 6BOGALUS 230.00 | 500025 | BARKERS 6 230.00 | 0 |  | 1 | 13WP | 431 | 454 | 0 | 96.2 | 96.2242 | 98.4 | [7 empty] | CATEGORYB | NONSINGLE | CELE-WELLOP1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T9135513WP | TO->FROM | BARKERS 6 230.00 - BOGALUSA 230KV CKT 1 | E | EES | CLEC |  | CLE_EAST | 0 | 336136 | 6BOGALUS 230.00 | 500025 | BARKERS 6 230.00 | 0 |  | 1 | 13WP | 431 | 454 | 0 | 97.7 | 97.7491 | 98.5 | [7 empty] | CATEGORYB | GENOUT | GEN336153 1-WATERFORD UNIT#3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2375513WP | FROM->TO | BARKERS 6 230.00 - RAMSAY 230KV CKT 1 | E | CLEC | CLEC | CLE_EAST | CLE_EAST | 0 | 500025 | BARKERS 6 230.00 | 500750 | RAMSAY 6 230.00 | 0 |  | 1 | 13WP | 431 | 464 | 0 |  | 93.8065 | 95.2 | [7 empty] | CATEGORYB | SINGLE | 6TALISK - BOGALUSA 230KV CKT 1 | 0 | 303221 | 6TALISK 230.00 | 336136 | 6BOGALUS 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3275513WP | TO->FROM | BOGALUSA - FRANKLIN 500KV CKT 1 | E | EES | EES | AEC | AMSNSH | 0 | 336562 | 8FRKLIN 500.00 | 336130 | 8BOGALUS 500.00 | 0 |  | 1 | 13WP | 1200 | 1200 | 0 | 97.1 | -999 | 98.4 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T9115513WP | TO->FROM | BOGALUSA - FRANKLIN 500KV CKT 1 | E | EES | EES | AEC | AMSNSH | 0 | 336562 | 8FRKLIN 500.00 | 336130 | 8BOGALUS 500.00 | 0 |  | 1 | 13WP | 1200 | 1200 | 0 | 96.9 | 96.8101 | 98 | [7 empty] | CATEGORYB | GENOUT | GEN336153 1-WATERFORD UNIT#3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T9245513WP | TO->FROM | BOGALUSA - FRANKLIN 500KV CKT 1 | E | EES | EES | AEC | AMSNSH | 0 | 336562 | 8FRKLIN 500.00 | 336130 | 8BOGALUS 500.00 | 0 |  | 1 | 13WP | 1200 | 1200 | 0 | 95.5 | 95.4387 | 96.4 | [7 empty] | CATEGORYB | GENOUT | GEN336251 1-NINEMILE POINT UNIT#4 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3265513WP | FROM->TO | BOGALUSA 500/230KV TRANSFORMER CKT 1 | E | EES | EES | AMSNSH | AMSNSH | 0 | 336130 | 8BOGALUS 500.00 | 336131 | 6ADMSCRK 230.00 | 0 |  | 1 | 13WP | 1200 | 1200 | 0 |  | -999 | 95.2 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T9665513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | E | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 100 | 100 | 0 |  | 82.1454 | 99.8 | [7 empty] | CATEGORYB | GENOUT | GEN514806 1-SOONER UNIT 2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FNSL | FDNS-Iteration limit exceeded | 5 | 5 | 2011AGP1AFS92T25513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | E | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 100 | 100 | 0 |  | 81.915 | 99.9 | [7 empty] | CATEGORYB | GENOUT | GEN336821 1-GRAND GULF UNIT | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FNSL | FDNS-Iteration limit exceeded | 5 | 5 | 2011AGP1AFS92T45513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | E | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 100 | 100 | 0 |  | 81.7338 | 99.6 | [7 empty] | CATEGORYB | GENOUT | GEN337911 1-ARKANSAS NUCLEAR ONE UNIT #2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | INVALID |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1575513WP | TO->FROM | COVERT 3 115.00 - SMITH CENTER 115KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539693 | SMITH-C3 115.00 | 539644 | COVERT 3 115.00 | 0 |  | 1 | 13WP | 59.8 | 59.8 | 0 |  | 80.5453 | 99.8706 | [7 empty] | CATEGORYB | SINGLE | ELLSWTP3 115.00 - MULLERGREN 115KV CKT 1 | 0 | 539642 | ELLSWTP3 115.00 | 539678 | GRTBEND3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | INVALID |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1585513WP | FROM->TO | COVERT 3 115.00 - WALDO 115KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539644 | COVERT 3 115.00 | 539698 | WALDO 3 115.00 | 0 |  | 1 | 13WP | 59.8 | 59.8 | 0 |  | 79.9207 | 99.2943 | [7 empty] | CATEGORYB | SINGLE | ELLSWTP3 115.00 - MULLERGREN 115KV CKT 1 | 0 | 539642 | ELLSWTP3 115.00 | 539678 | GRTBEND3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T5525513WP | FROM->TO | FPL SWITCH - MOORELAND 138KV CKT 1 | E | OKGE | WFEC | ENID | AEP-OP | 0 | 515785 | WINDFRM4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 13WP | 287 | 287 | 0 | 97.5 | 97.53 | 97 | [7 empty] | CATEGORYB | SINGLE | WOODWARD DISTRICT EHV (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T5495513WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 13WP | 171 | 185 | 0 | 100.2 | 100.1565 | 99.3 | [7 empty] | CATEGORYB | SINGLE | WOODWARD DISTRICT EHV (WWDEHV) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515375 | WWRDEHV7 345.00 | 515376 | WWRDEHV4 138.00 | 515795 | WWDEHV31 13.800 | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2015513WP | TO->FROM | GRAND ISLAND - SWEETWATER 345KV CKT 1 | E | NPPD | NPPD | NPPD_686 | WAPA_1606 | 0 | 640374 | SWEET W3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 | 13WP | 717 | 717 | 789 |  | 90.4968 | 96.5 | [7 empty] | CATEGORYB | SINGLE | AXTELL - SWEETWATER 345KV CKT 1 | 0 | 640065 | AXTELL 3 345.00 | 640374 | SWEET W3 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2455513WP | FROM->TO | GRIMES - MT. ZION 138KV CKT 1 | E | EES | EES | GSTNAV | GSTHNT | 0 | 334026 | 4GRIMES 138.00 | 334060 | 4MT.ZION 138.00 | 0 |  | 1 | 13WP | 206 | 206 | 0 |  | 93.0359 | 97.9 | [7 empty] | CATEGORYB | SINGLE | 4BENTWATER 138.00 - WALDEN 138KV CKT 1 | 0 | 334039 | 4BENTWATER 138.00 | 334040 | 4WALDEN 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2425513WP | FROM->TO | GRIMES 345/138KV TRANSFORMER CKT 1 | E | EES | EES |  | GSTNAV | 0 | 334028 | 7GRIMES 345.00 | 334026 | 4GRIMES 138.00 | 0 |  | 1 | 13WP | 525 | 525 | 0 |  | 92.3019 | 96.1 | [7 empty] | CATEGORYB | SINGLE | GRIMES 345/138KV TRANSFORMER CKT 2 | 0 | 334026 | 4GRIMES 138.00 | 334028 | 7GRIMES 345.00 | 0 |  | 2 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2415513WP | FROM->TO | GRIMES 345/138KV TRANSFORMER CKT 2 | E | EES | EES |  | GSTNAV | 0 | 334028 | 7GRIMES 345.00 | 334026 | 4GRIMES 138.00 | 0 |  | 2 | 13WP | 525 | 525 | 0 |  | 92.3019 | 96.1 | [7 empty] | CATEGORYB | SINGLE | GRIMES 345/138KV TRANSFORMER CKT 1 | 0 | 334026 | 4GRIMES 138.00 | 334028 | 7GRIMES 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T10015513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 81.5616 | 99.8 | [7 empty] | CATEGORYB | GENOUT | GEN560353 1-G10-52 0.6900 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T10025513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 80.2099 | 98.5 | [7 empty] | CATEGORYB | GENOUT | GEN560432 1-G08-124 0.6900 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T10035513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 95.6 | 95.6 | 0 |  | 81.3075 | 99.5 | [7 empty] | CATEGORYB | GENOUT | GEN599950 1-PSCO LAMAR DC TIE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1835513WP | FROM->TO | IATAN - STRANGER CREEK 345KV CKT 1 | E | KCPL | WERE | KACP | NEAST | 0 | 542982 | IATAN 7 345.00 | 532772 | STRANGR7 345.00 | 0 |  | 1 | 13WP | 1195 | 1195 | 0 | 96.5 | 96.534 | 96.3 | [7 empty] | CATEGORYB | SINGLE | EASTOWN7 345.00 - IATAN 345KV CKT 1 | 0 | 541400 | EASTOWN7 345.00 | 542982 | IATAN 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T1215013WP | FROM->TO | JAGUAR - POINT ESSO TAP 230KV CKT 1 | E | EES | EES | GSLBTR | GSLBTR | 0 | 335770 | 6JAGUAR 230.00 | 335641 | 6TP.ESSO 230.00 | 0 |  | 1 | 13WP | 685 | 685 | 0 |  | 94.5621 | 95.3 | [7 empty] | CATEGORYB | SINGLE | WEBRE - WILLOW GLEN 500KV CKT 1 | 0 | 335500 | 8WEBRE 500.00 | 335618 | 8WGLEN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T2435013WP | TO->FROM | LITTLE GYPSY - WATERFORD 230KV CKT 1 | E | EES | EES | AMSCOR | AMSCOR | 0 | 336154 | 6WATFRD 230.00 | 336190 | 6GYPSY 230.00 | 0 |  | 1 | 13WP | 580 | 580 | 0 | 95.1 | 95.0916 | 96.2 | [7 empty] | CATEGORYB | SINGLE | NINEMILE POINT 230 - WATERFORD 230KV CKT 1 | 0 | 336154 | 6WATFRD 230.00 | 336250 | 69MILE 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T2445013WP | TO->FROM | LITTLE GYPSY - WATERFORD 230KV CKT 2 | E | EES | EES | AMSCOR | AMSCOR | 0 | 336154 | 6WATFRD 230.00 | 336190 | 6GYPSY 230.00 | 0 |  | 2 | 13WP | 580 | 580 | 0 |  | 94.1946 | 95.3 | [7 empty] | CATEGORYB | SINGLE | NINEMILE POINT 230 - WATERFORD 230KV CKT 1 | 0 | 336154 | 6WATFRD 230.00 | 336250 | 69MILE 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T5605513WP | FROM->TO | MIDLAND COUNTY INTERCHANGE (ABB LLL58861) 230/138/13.2KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-PECO | SPS-CAPR | 1 | 527914 | MIDLAND 6230.00 | 522992 | CR-GARNDALE4138.00 | 527912 | MIDLND_TR1 113.200 | 1 | 13WP | 168 | 210 | 0 | 95.9 | 95.858 | 95.8 | [7 empty] | CATEGORYB | SINGLE | BORDEN COUNTY INTERCHANGE (ABB LL58862) 230/138/13.2KV TRANSFORMER CKT 1 | 1 | 522896 | CR-VEALMOOR4138.00 | 526830 | BORDEN 6230.00 | 526827 | BORDEN_TR1 113.200 | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T7295013WP | TO->FROM | NINEMILE POINT 230 - WATERFORD 230KV CKT 1 | E | EES | EES | AMSCOR | METDSG | 0 | 336154 | 6WATFRD 230.00 | 336250 | 69MILE 230.00 | 0 |  | 1 | 13WP | 797 | 797 | 0 | 95.9 | 95.9624 | 96.2 | [7 empty] | CATEGORYB | GENOUT | GEN336251 1-NINEMILE POINT UNIT#4 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2075513WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 13WP | 103 | 129 | 103 |  | 96.1725 | 99.5 | [7 empty] | CATEGORYB | SINGLE | GRAND ISLAND - MCCOOL 345KV CKT 1 | 0 | 640271 | MCCOOL 3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4115513WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 13WP | 103 | 129 | 103 | 97.7 | 97.7239 | 99.9 | [7 empty] | CATEGORYB | SINGLE | ANITA TAP POINT TO CRESTON AND DENISON - EXIRA 161KV CKT 1 | 0 | 631069 | ANTA TP5 161.00 | 652603 | EXIRA 5 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4125513WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 13WP | 103 | 129 | 103 |  | 96.3899 | 99.8 | [7 empty] | CATEGORYB | SINGLE | ATCHSNT3 345.00 - BOONEVILLE 345KV CKT 1 | 0 | 635017 | ATCHSNT3 345.00 | 635630 | BOONVIL3 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4165513WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 13WP | 103 | 129 | 103 | 96.6 | 96.636 | 99.4 | [7 empty] | CATEGORYB | SINGLE | COALHILL4 230.00 - DAWSON CREEK 230KV CKT 1 | 0 | 652111 | COALHILL4 230.00 | 652403 | DAWSONC4 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4255513WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 13WP | 103 | 129 | 103 | 96.6 | 96.6363 | 99.3 | [7 empty] | CATEGORYB | SINGLE | GARRISON - JAMES TOWN 230KV CKT 1 | 0 | 652441 | GARRISN4 230.00 | 652444 | JAMESTN4 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4275513WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 13WP | 103 | 129 | 103 |  | 94.5876 | 99.3 | [7 empty] | CATEGORYB | SINGLE | NUNDRWD - PHILIP TAP 230KV CKT 1 | 0 | 652484 | NUNDRWD4 230.00 | 652488 | PHILTAP4 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4285513WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 13WP | 103 | 129 | 103 |  | 96.4072 | 99.2 | [7 empty] | CATEGORYB | SINGLE | BROOKINGS - WHITE 115KV CKT 1 | 0 | 652504 | BROOKNG7 115.00 | 652538 | WHITE 7 115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4345513WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 13WP | 103 | 129 | 103 | 97 | 97.0245 | 99.8 | [7 empty] | CATEGORYB | SINGLE | FT THOMPSON - WESSINGTON 230KV CKT 1 | 0 | 652507 | FTTHOMP4 230.00 | 652607 | WESSINGTON 4230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4355513WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 13WP | 103 | 129 | 103 |  | -999 | 99.7 | [7 empty] | CATEGORYB | SINGLE | GROTON - ORDWAY 115KV CKT 1 | 0 | 652512 | GROTON 7 115.00 | 652534 | ORDWAY 7 115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4395513WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 13WP | 103 | 129 | 103 |  | 96.2759 | 99.2 | [7 empty] | CATEGORYB | SINGLE | CARPENTER - HURON 230KV CKT 1 | 0 | 652514 | HURON 4 230.00 | 652614 | CARPENTER 4 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4425513WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 13WP | 103 | 129 | 103 |  | 96.4136 | 99.2 | [7 empty] | CATEGORYB | SINGLE | LETCHER - SIOUX FALLS 230KV CKT 1 | 0 | 652523 | SIOUXFL4 230.00 | 652606 | LETCHER4 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4435513WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 13WP | 103 | 129 | 103 | 96.9 | 96.9312 | 99.9 | [7 empty] | CATEGORYB | SINGLE | GLENHAM - WHITLOK 230KV CKT 1 | 0 | 652527 | WHITLOK4 230.00 | 661038 | GLENHAM4 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4445513WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 13WP | 103 | 129 | 103 | 97.2 | 97.2122 | 100 | [7 empty] | CATEGORYB | SINGLE | GROTON - WATERTOWN 345KV CKT 1 | 0 | 652529 | WATERTN3 345.00 | 659160 | GROTON 3 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4565513WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 13WP | 103 | 129 | 103 |  | 95.7255 | 99.6 | [7 empty] | CATEGORYB | SINGLE | SIDNEY - STEGALL 345KV CKT 1 | 0 | 659133 | SIDNEY 3 345.00 | 659135 | STEGALL3 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8065513WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 13WP | 103 | 129 | 103 | 97 | 97.0129 | 99.9 | [7 empty] | CATEGORYB | SINGLE | WEBSTER () 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 636000 | WEBSTER3 345.00 | 636001 | WEBSTER5 161.00 | 636002 | WEBS1XT9 13.800 | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8125513WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 13WP | 103 | 129 | 103 | 96.6 | 96.5625 | 99.3 | [7 empty] | CATEGORYB | SINGLE | BELFIELD (BEF KU1A) 345/230/13.8KV TRANSFORMER CKT 1 | 1 | 652424 | BELFELD3 345.00 | 652425 | BELFELD4 230.00 | 652221 | BELFELD9 13.800 | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8335513WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 13WP | 103 | 129 | 103 | 96.5 | 96.5425 | 99.3 | [7 empty] | CATEGORYB | SINGLE | WHITE (WHT KU1A) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 652537 | WHITE 3 345.00 | 652538 | WHITE 7 115.00 | 652293 | WHITE 9 13.800 | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T915513WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 13WP | 103 | 129 | 103 |  | 96.157 | 99.2 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T305013WP | TO->FROM | RAPIDES - RODEMACHER 230KV CKT 1 | E | CLEC | CLEC | CLE_CENTRAL | CLE_CENTRAL | 0 | 500770 | RODEMR 6 230.00 | 500760 | RAPIDES6 230.00 | 0 |  | 1 | 13WP | 725 | 735 | 0 | 95.1 | 95.0735 | 96.3 | [7 empty] | CATEGORYB | SINGLE | RODEMACHER - SHERWOOD 230KV CKT 1 | 0 | 500770 | RODEMR 6 230.00 | 500790 | SHERWD 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2105513WP | FROM->TO | SUB 167 - RIVERTON 69/13.2KV TRANSFORMER CKT 1 | E | EMDE | EMDE | BAXTER | BAXTER | 0 | 547645 | R8G167 1 13.200 | 547541 | RIV167 2 69.000 | 0 |  | 1 | 13WP | 52 | 52 | 0 | 95.2 | 95.1567 | 99.2 | [7 empty] | CATEGORYB | SINGLE | 7JASPER 345.00 - MORGAN 345KV CKT 1 | 0 | 300045 | 7MORGAN 345.00 | 300949 | 7JASPER 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T1015013WP | FROM->TO | WILLOW GLEN 500/230KV TRANSFORMER CKT 1 | E | EES | EES | GSLBTR | GSLBTR | 0 | 335618 | 8WGLEN 500.00 | 335568 | 6WGLEN 230.00 | 0 |  | 1 | 13WP | 672 | 672 | 0 | 99.3 | 99.324 | 99.9 | [7 empty] | CATEGORYB | SINGLE | 6AIRLINE 230.00 - 6VIGNES 230KV CKT 1 | 0 | 303199 | 6AIRLINE 230.00 | 303200 | 6VIGNES 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T1035013WP | FROM->TO | WILLOW GLEN 500/230KV TRANSFORMER CKT 1 | E | EES | EES | GSLBTR | GSLBTR | 0 | 335618 | 8WGLEN 500.00 | 335568 | 6WGLEN 230.00 | 0 |  | 1 | 13WP | 672 | 672 | 0 | 98.7 | 98.7092 | 99.4 | [7 empty] | CATEGORYB | SINGLE | 6AIRLINE 230.00 - SORRENTO 230KV CKT 1 | 0 | 303199 | 6AIRLINE 230.00 | 336060 | 6SORR 2 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T2015013WP | FROM->TO | WILLOW GLEN 500/230KV TRANSFORMER CKT 1 | E | EES | EES | GSLBTR | GSLBTR | 0 | 335618 | 8WGLEN 500.00 | 335568 | 6WGLEN 230.00 | 0 |  | 1 | 13WP | 672 | 672 | 0 | 99 | 99.0246 | 99.6 | [7 empty] | CATEGORYB | SINGLE | 6TEZCUCO 230.00 - WATERFORD 230KV CKT 1 | 0 | 336069 | 6TEZCUCO 230.00 | 336154 | 6WATFRD 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1845514SP | TO->FROM | 5 TRIBES - PECAN CREEK 161KV CKT 1 | E | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515234 | PECANCK5 161.00 | 515228 | 5TRIBES5 161.00 | 0 |  | 1 | 17SP | 272 | 312 | 0 | 97.7 | 97.683 | 99.6 | [7 empty] | CATEGORYB | SINGLE | AGENCY - PECAN CREEK 161KV CKT 1 | 0 | 515230 | AGENCY 5 161.00 | 515234 | PECANCK5 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T7005514SP | FROM->TO | 5ALLEN FP 161.00 - HORN LAKE 161KV CKT 1 | E | TVA | EES | MEMPHIS | EMI-SHVN | 0 | 360174 | 5ALLEN FP 161.00 | 337181 | 5HN LAK 161.00 | 0 |  | 1 | 17SP | 226 | 226 | 226 | 95 | 95.0176 | 96.2 | [7 empty] | CATEGORYB | SINGLE | FREEPORT - HORN LAKE 230KV CKT 1 | 0 | 337162 | 6FRPORT 230.00 | 337180 | 6HN LAK 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T18745514SP | TO->FROM | 5PERCHE 161.00 - HUNTSDALE 161KV CKT 1 | E | AECI | CWLD | CENTRAL | CMWL | 0 | 300500 | 5HUNTSDL 161.00 | 343004 | 5PERCHE 161.00 | 0 |  | 1 | 17SP | 223 | 223 | 223 |  | 93.7926 | 95.3 | [7 empty] | CATEGORYB | NONSINGLE | AM1_A_OG | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T4125014SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17SP | 615 | 615 | 0 | 95.2 | 95.1649 | 95 | [7 empty] | CATEGORYB | SINGLE | DYNEGY - PECAN GROVE 230KV CKT 1 | 0 | 335074 | 6DYNEGY 230.00 | 335077 | 6PGROVE 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T4165014SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17SP | 615 | 615 | 0 | 95.9 | 95.8933 | 95.5 | [7 empty] | CATEGORYB | SINGLE | WEBRE - WELLS 500KV CKT 1 | 0 | 335368 | 8WELLS 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4165514SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17SP | 615 | 615 | 0 | 95.2 | 95.217 | 95.1 | [7 empty] | CATEGORYB | SINGLE | 8CAJUN2 - WEBRE 500KV CKT 1 | 0 | 303005 | 8CAJUN2 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T5325514SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17SP | 615 | 615 | 0 | 95.3 | 95.2691 | 95.2 | [7 empty] | CATEGORYB | SINGLE | DYNEGY - PECAN GROVE 230KV CKT 1 | 0 | 335074 | 6DYNEGY 230.00 | 335077 | 6PGROVE 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T5355514SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17SP | 615 | 615 | 0 | 95.8 | 95.7571 | 95.6 | [7 empty] | CATEGORYB | SINGLE | WEBRE - WELLS 500KV CKT 1 | 0 | 335368 | 8WELLS 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T5665014SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17SP | 615 | 615 | 0 | 95.8 | 95.8326 | 95.4 | [7 empty] | CATEGORYB | SINGLE | ELDORADO EHV - STERLINGTON 500KV CKT 1 | 0 | 337420 | 8STERL 500.00 | 337561 | 8ELDEHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T5815514SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17SP | 615 | 615 | 0 | 95.3 | 95.2684 | 95.1 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T7065514SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17SP | 615 | 615 | 0 | 95.5 | 95.4618 | 95.2 | [7 empty] | CATEGORYB | SINGLE | ELDORADO EHV - STERLINGTON 500KV CKT 1 | 0 | 337420 | 8STERL 500.00 | 337561 | 8ELDEHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T10075014SP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 17SP | 68 | 68 | 0 | 96.5 | 96.5183 | 95.5 | [7 empty] | CATEGORYB | SINGLE | JONESBORO - JONESBORO 161KV CKT 1 | 0 | 505418 | JONESBO5 161.00 | 338170 | 5JONES 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T13945514SP | TO->FROM | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 | E | GMO | GMO |  |  | 0 | 541206 | PRALEE 5 161.00 | 541211 | BLSPS 5 161.00 | 0 |  | 1 | 17SP | 224 | 224 | 224 |  | 93.9165 | 96.7 | [7 empty] | CATEGORYB | SINGLE | CLINTON - MONTROSE 161KV CKT 1 | 0 | 542995 | MONTROS5 161.00 | 300071 | 5CLINTN 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T18275514SP | FROM->TO | BULL SHOALS - MIDWAY (YVEPA) 161KV CKT 1 | E | SWPA | EES | EMINTH |  | 0 | 505460 | BULL SH5 161.00 | 338813 | 5MIDWAY# 161.00 | 0 |  | 1 | 17SP | 162 | 162 | 0 |  | 91.6905 | 97.8 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPA-05 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T745514SP | FROM->TO | BULL SHOALS - MIDWAY (YVEPA) 161KV CKT 1 | E | SWPA | EES | EMINTH |  | 0 | 505460 | BULL SH5 161.00 | 338813 | 5MIDWAY# 161.00 | 0 |  | 1 | 17SP | 162 | 162 | 0 |  | 93.0053 | 99.1 | [7 empty] | CATEGORYB | SINGLE | BUFORD 5 161.00 - BULL SHOALS 161KV CKT 1 | 0 | 504440 | BUFORD 5 161.00 | 505460 | BULL SH5 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SPP_FG-EES-IDC-AFC-20222-SAGMEL_ISDEL | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T7295014SP | TO->FROM | CALICO ROCK - MELBOURNE 161KV CKT 1 | E | EES | EES | EAINTH |  | 0 | 338131 | 5MELBRN 161.00 | 338130 | 5CALCR 161.00 | 0 |  | 1 | 17SP | 148 | 148 | 0 | 100.3 | 100.318 | 99.5 | [7 empty] | CATEGORYB | SINGLE | DELL 500 - INDEPENDENCE 500KV CKT 1 | 0 | 338145 | 8ISES 500.00 | 338187 | 8DELL 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3035514SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | E | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 100 | 100 | 0 |  | 71.1873 | 95.1 | [7 empty] | CATEGORYB | SINGLE | MEDICINE LODGE - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539673 | MED-LDG3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T135514SP | TO->FROM | DODGE CITY BEEF - JUDSON LARGE 115KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539671 | FTDODGE3 115.00 | 539645 | DCBEEF3 115.00 | 0 |  | 1 | 17SP | 83.9 | 89.6 | 0 | 95.4 | 95.4047 | 95.5 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T13405514SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | E | WERE | WERE | NCENTRAL | NCENTRAL | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 17SP | 280 | 308 | 350 | 98.9 | 98.8627 | 96.6 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST MANHATTAN (NWMANH1X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532865 | NWMANHT6 230.00 | 533347 | NWMANHT3 115.00 | 532901 | NWMANHX1 18.000 | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T2005014SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | E | WERE | WERE | NCENTRAL | NCENTRAL | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 17SP | 280 | 308 | 350 | 99.3 | 99.3268 | 97.3 | [7 empty] | CATEGORYB | SINGLE | EAST MANHATTAN - NORTHWEST MANHATTAN 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 532865 | NWMANHT6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T11965014SP | FROM->TO | EDDY COUNTY INTERCHANGE (WH XHS70551) 230/115/13.2KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-PECO | SPS-PECO | 1 | 527800 | EDDY_SOUTH 6230.00 | 527798 | EDDY_CNTY 3115.00 | 527797 | EDDY_TR2 113.200 | 1 | 17SP | 167 | 167 | 0 | 96.2 | 96.1523 | 95.7 | [7 empty] | CATEGORYB | SINGLE | EDDY COUNTY INTERCHANGE (WH XHS70551) 230/115/13.2KV TRANSFORMER CKT 2 | 1 | 527798 | EDDY_CNTY 3115.00 | 527800 | EDDY_SOUTH 6230.00 | 527795 | EDDY_TR3 1 13.200 | 2 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T11955014SP | FROM->TO | EDDY COUNTY INTERCHANGE (WH XHS70551) 230/115/13.2KV TRANSFORMER CKT 2 | E | SPS | SPS | SPS-PECO | SPS-PECO | 1 | 527800 | EDDY_SOUTH 6230.00 | 527798 | EDDY_CNTY 3115.00 | 527795 | EDDY_TR3 1 13.200 | 2 | 17SP | 167 | 167 | 0 | 96.2 | 96.1524 | 95.7 | [7 empty] | CATEGORYB | SINGLE | EDDY COUNTY INTERCHANGE (WH XHS70551) 230/115/13.2KV TRANSFORMER CKT 1 | 1 | 527798 | EDDY_CNTY 3115.00 | 527800 | EDDY_SOUTH 6230.00 | 527797 | EDDY_TR2 113.200 | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | INVALID |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2785514SP | FROM->TO | EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533040 | EVANS N4 138.00 | 533054 | MAIZE 4 138.00 | 0 |  | 1 | 17SP | 382 | 382 | 0 |  | 94.6837 | 98.7385 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER NORTH - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533040 | EVANS N4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T3195014SP | FROM->TO | GRIMES - MT. ZION 138KV CKT 1 | E | EES | EES | GSTNAV | GSTHNT | 0 | 334026 | 4GRIMES 138.00 | 334060 | 4MT.ZION 138.00 | 0 |  | 1 | 17SP | 206 | 206 | 0 |  | 89.3583 | 98.7 | [7 empty] | CATEGORYB | SINGLE | 4BENTWATER 138.00 - GRIMES 138KV CKT 1 | 0 | 334026 | 4GRIMES 138.00 | 334039 | 4BENTWATER 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | INVALID |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2795514SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 78.0731 | 96.8787 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER NORTH - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533040 | EVANS N4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T11665014SP | FROM->TO | INDEPENDENCE - MOOREFIELD 161KV CKT 1 | E | EES | EES | EAINTH | EAINTH | 0 | 338142 | 5ISES-1 161.00 | 338138 | 5MORFLD 161.00 | 0 |  | 1 | 17SP | 303 | 303 | 0 | 96.9 | 96.937 | 95.7 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T7305014SP | FROM->TO | INDEPENDENCE - MOOREFIELD 161KV CKT 1 | E | EES | EES | EAINTH | EAINTH | 0 | 338142 | 5ISES-1 161.00 | 338138 | 5MORFLD 161.00 | 0 |  | 1 | 17SP | 303 | 303 | 0 | 98.6 | 98.5636 | 98.2 | [7 empty] | CATEGORYB | SINGLE | DELL 500 - INDEPENDENCE 500KV CKT 1 | 0 | 338145 | 8ISES 500.00 | 338187 | 8DELL 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T18135514SP | TO->FROM | MARYVILLE - MIDWAY 161KV CKT 1 | E | GMO | GMO |  |  | 0 | 541369 | MIDWAY_5 161.00 | 541251 | MARYVLE5 161.00 | 0 |  | 1 | 17SP | 152 | 171 | 171 |  | 66.0468 | 95.1 | [7 empty] | CATEGORYB | NONSINGLE | LN-FAIRPORT | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3545514SP | TO->FROM | MARYVILLE - MIDWAY 161KV CKT 1 | E | GMO | GMO |  |  | 0 | 541369 | MIDWAY_5 161.00 | 541251 | MARYVLE5 161.00 | 0 |  | 1 | 17SP | 152 | 171 | 171 |  | 68.2778 | 98.7 | [7 empty] | CATEGORYB | SINGLE | FAIRPORT 345/161KV TRANSFORMER CKT 3 | 0 | 300039 | 7FAIRPT 345.00 | 300076 | 5FAIRPT 161.00 | 0 |  | 3 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2395514SP | TO->FROM | MULLERGREN - SPEARVILLE 230KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539695 | SPEARVL6 230.00 | 539679 | MULGREN6 230.00 | 0 |  | 1 | 17SP | 330.3 | 355.3 | 0 |  | 93.7315 | 97.5 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2665514SP | TO->FROM | MUND - PENTAGON 115KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 533261 | PENTAGN3 115.00 | 533282 | MUND 3 115.00 | 0 |  | 1 | 17SP | 179 | 194 | 0 | 98.9 | 98.8575 | 99.5 | [7 empty] | CATEGORYB | SINGLE | 87th STREET - CRAIG 345KV CKT 1 | 0 | 532775 | 87TH 7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T14845014SP | FROM->TO | PLEASANT HILL 500/161KV TRANSFORMER CKT 1 | E | EES | EES | EAICEN | EAICEN | 0 | 337922 | 8P HILL 500.00 | 337923 | 5P HILL 161.00 | 0 |  | 1 | 17SP | 600 | 600 | 0 | 97.4 | 97.4223 | 97.3 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE (ANO) 500/161/22.0KV TRANSFORMER CKT 1 | 1 | 337909 | 8ANO 50 500.00 | 337912 | 5ANO 161.00 | 337913 | 1ANOACCD 22.000 | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | INVALID | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T845514SP | FROM->TO | SILOAM CITY - SILOAM SPRINGS 161KV CKT 1 | E | GRDA | AEPW | GRDA-MUN | FAYETTEVILLE | 0 | 512643 | SILMCTY5 161.00 | 506948 | SILOAM 5 161.00 | 0 |  | 1 | 17SP | 288 | 335 | 0 | 96.9 | 96.8514 | 97.1829 | [7 empty] | CATEGORYB | SINGLE | FLINT CREEK - SILOAM SPRINGS TAP 345KV CKT 1 | 0 | 506935 | FLINTCR7 345.00 | 512750 | TONECE7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T17175014SP | FROM->TO | SUB 1206 (S1206 T1) 161/69/13.8KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 1 | 646206 | S1206 5 161.00 | 647906 | S906 S 8 69.000 | 648206 | S1206T19 13.800 | 1 | 17SP | 201.6 | 201.6 | 201.6 |  | 94.3963 | 98.9 | [7 empty] | CATEGORYB | NONSINGLE | S1206T2 BSCL | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T17195014SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 17SP | 250 | 250 | 250 | 98.7 | 98.7088 | 98.4 | [7 empty] | CATEGORYB | NONSINGLE | S1217 AUTOV2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T18235514SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 17SP | 250 | 250 | 250 | 98.4 | 98.4191 | 98.5 | [7 empty] | CATEGORYB | NONSINGLE | S1217 AUTOV2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3585514SP | FROM->TO | SUB 167 - RIVERTON 69/13.2KV TRANSFORMER CKT 1 | E | EMDE | EMDE | BAXTER | BAXTER | 0 | 547645 | R8G167 1 13.200 | 547541 | RIV167 2 69.000 | 0 |  | 1 | 17SP | 52 | 52 | 0 | 97.8 | 97.7572 | 99.7 | [7 empty] | CATEGORYB | SINGLE | 7JASPER 345.00 - MORGAN 345KV CKT 1 | 0 | 300045 | 7MORGAN 345.00 | 300949 | 7JASPER 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1865516SP | TO->FROM | 5 TRIBES - PECAN CREEK 161KV CKT 1 | E | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515234 | PECANCK5 161.00 | 515228 | 5TRIBES5 161.00 | 0 |  | 1 | 17SP | 272 | 312 | 0 | 97.4 | 97.4488 | 99.4 | [7 empty] | CATEGORYB | SINGLE | AGENCY - PECAN CREEK 161KV CKT 1 | 0 | 515230 | AGENCY 5 161.00 | 515234 | PECANCK5 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T6705516SP | FROM->TO | 5ALLEN FP 161.00 - HORN LAKE 161KV CKT 1 | E | TVA | EES | MEMPHIS | EMI-SHVN | 0 | 360174 | 5ALLEN FP 161.00 | 337181 | 5HN LAK 161.00 | 0 |  | 1 | 17SP | 226 | 226 | 226 | 95 | 95.0259 | 96.2 | [7 empty] | CATEGORYB | SINGLE | FREEPORT - HORN LAKE 230KV CKT 1 | 0 | 337162 | 6FRPORT 230.00 | 337180 | 6HN LAK 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T18445516SP | TO->FROM | 5PERCHE 161.00 - HUNTSDALE 161KV CKT 1 | E | AECI | CWLD | CENTRAL | CMWL | 0 | 300500 | 5HUNTSDL 161.00 | 343004 | 5PERCHE 161.00 | 0 |  | 1 | 17SP | 223 | 223 | 223 | 96.1 | 96.0943 | 97.7 | [7 empty] | CATEGORYB | NONSINGLE | AM1_A_OG | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3865516SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17SP | 615 | 615 | 0 | 95.2 | 95.2172 | 95.2 | [7 empty] | CATEGORYB | SINGLE | 8CAJUN2 - WEBRE 500KV CKT 1 | 0 | 303005 | 8CAJUN2 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T4065016SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17SP | 615 | 615 | 0 | 95.2 | 95.1652 | 95 | [7 empty] | CATEGORYB | SINGLE | DYNEGY - PECAN GROVE 230KV CKT 1 | 0 | 335074 | 6DYNEGY 230.00 | 335077 | 6PGROVE 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T4105016SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17SP | 615 | 615 | 0 | 95.9 | 95.8937 | 95.5 | [7 empty] | CATEGORYB | SINGLE | WEBRE - WELLS 500KV CKT 1 | 0 | 335368 | 8WELLS 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T5025516SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17SP | 615 | 615 | 0 | 95.3 | 95.2694 | 95.2 | [7 empty] | CATEGORYB | SINGLE | DYNEGY - PECAN GROVE 230KV CKT 1 | 0 | 335074 | 6DYNEGY 230.00 | 335077 | 6PGROVE 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T5055516SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17SP | 615 | 615 | 0 | 95.8 | 95.756 | 95.6 | [7 empty] | CATEGORYB | SINGLE | WEBRE - WELLS 500KV CKT 1 | 0 | 335368 | 8WELLS 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T5515516SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17SP | 615 | 615 | 0 | 95.3 | 95.2684 | 95.1 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T5605016SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17SP | 615 | 615 | 0 | 95.8 | 95.8334 | 95.4 | [7 empty] | CATEGORYB | SINGLE | ELDORADO EHV - STERLINGTON 500KV CKT 1 | 0 | 337420 | 8STERL 500.00 | 337561 | 8ELDEHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T6765516SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17SP | 615 | 615 | 0 | 95.5 | 95.4596 | 95.2 | [7 empty] | CATEGORYB | SINGLE | ELDORADO EHV - STERLINGTON 500KV CKT 1 | 0 | 337420 | 8STERL 500.00 | 337561 | 8ELDEHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T10065016SP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 17SP | 68 | 68 | 0 | 96.5 | 96.5176 | 95.4 | [7 empty] | CATEGORYB | SINGLE | JONESBORO - JONESBORO 161KV CKT 1 | 0 | 505418 | JONESBO5 161.00 | 338170 | 5JONES 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T17985516SP | FROM->TO | BULL SHOALS - MIDWAY (YVEPA) 161KV CKT 1 | E | SWPA | EES | EMINTH |  | 0 | 505460 | BULL SH5 161.00 | 338813 | 5MIDWAY# 161.00 | 0 |  | 1 | 17SP | 162 | 162 | 0 |  | 92.2759 | 98.4 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPA-05 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T755516SP | FROM->TO | BULL SHOALS - MIDWAY (YVEPA) 161KV CKT 1 | E | SWPA | EES | EMINTH |  | 0 | 505460 | BULL SH5 161.00 | 338813 | 5MIDWAY# 161.00 | 0 |  | 1 | 17SP | 162 | 162 | 0 |  | 91.7642 | 97.9 | [7 empty] | CATEGORYB | SINGLE | BUFORD 5 161.00 - NORFORK 161KV CKT 1 | 0 | 504440 | BUFORD 5 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T765516SP | FROM->TO | BULL SHOALS - MIDWAY (YVEPA) 161KV CKT 1 | E | SWPA | EES | EMINTH |  | 0 | 505460 | BULL SH5 161.00 | 338813 | 5MIDWAY# 161.00 | 0 |  | 1 | 17SP | 162 | 162 | 0 |  | 93.5958 | 99.8 | [7 empty] | CATEGORYB | SINGLE | BUFORD 5 161.00 - BULL SHOALS 161KV CKT 1 | 0 | 504440 | BUFORD 5 161.00 | 505460 | BULL SH5 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SPP_FG-EES-IDC-AFC-20222-SAGMEL_ISDEL | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T7235016SP | TO->FROM | CALICO ROCK - MELBOURNE 161KV CKT 1 | E | EES | EES | EAINTH |  | 0 | 338131 | 5MELBRN 161.00 | 338130 | 5CALCR 161.00 | 0 |  | 1 | 17SP | 148 | 148 | 0 | 100.4 | 100.3615 | 99.5 | [7 empty] | CATEGORYB | SINGLE | DELL 500 - INDEPENDENCE 500KV CKT 1 | 0 | 338145 | 8ISES 500.00 | 338187 | 8DELL 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | INVALID |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2695516SP | TO->FROM | CHISHOLM - MAIZE 138KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533054 | MAIZE 4 138.00 | 533035 | CHISHLM4 138.00 | 0 |  | 1 | 17SP | 382 | 382 | 0 |  | 91.8512 | 96.469 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER NORTH - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533040 | EVANS N4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T145516SP | TO->FROM | DODGE CITY BEEF - JUDSON LARGE 115KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539671 | FTDODGE3 115.00 | 539645 | DCBEEF3 115.00 | 0 |  | 1 | 17SP | 83.9 | 89.6 | 0 | 95.3 | 95.2811 | 95.5 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T13215516SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | E | WERE | WERE | NCENTRAL | NCENTRAL | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 17SP | 280 | 308 | 350 | 97.4 | 97.3914 | 95.1 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST MANHATTAN (NWMANH1X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532865 | NWMANHT6 230.00 | 533347 | NWMANHT3 115.00 | 532901 | NWMANHX1 18.000 | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T1975016SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | E | WERE | WERE | NCENTRAL | NCENTRAL | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 17SP | 280 | 308 | 350 | 98 | 98.0422 | 96.3 | [7 empty] | CATEGORYB | SINGLE | EAST MANHATTAN - NORTHWEST MANHATTAN 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 532865 | NWMANHT6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T11955016SP | FROM->TO | EDDY COUNTY INTERCHANGE (WH XHS70551) 230/115/13.2KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-PECO | SPS-PECO | 1 | 527800 | EDDY_SOUTH 6230.00 | 527798 | EDDY_CNTY 3115.00 | 527797 | EDDY_TR2 113.200 | 1 | 17SP | 167 | 167 | 0 | 96.2 | 96.1533 | 95.7 | [7 empty] | CATEGORYB | SINGLE | EDDY COUNTY INTERCHANGE (WH XHS70551) 230/115/13.2KV TRANSFORMER CKT 2 | 1 | 527798 | EDDY_CNTY 3115.00 | 527800 | EDDY_SOUTH 6230.00 | 527795 | EDDY_TR3 1 13.200 | 2 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T11945016SP | FROM->TO | EDDY COUNTY INTERCHANGE (WH XHS70551) 230/115/13.2KV TRANSFORMER CKT 2 | E | SPS | SPS | SPS-PECO | SPS-PECO | 1 | 527800 | EDDY_SOUTH 6230.00 | 527798 | EDDY_CNTY 3115.00 | 527795 | EDDY_TR3 1 13.200 | 2 | 17SP | 167 | 167 | 0 | 96.2 | 96.1533 | 95.7 | [7 empty] | CATEGORYB | SINGLE | EDDY COUNTY INTERCHANGE (WH XHS70551) 230/115/13.2KV TRANSFORMER CKT 1 | 1 | 527798 | EDDY_CNTY 3115.00 | 527800 | EDDY_SOUTH 6230.00 | 527797 | EDDY_TR2 113.200 | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1745516SP | FROM->TO | EL PASO - FARBER 138KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 | 17SP | 160 | 168 | 0 | 96.3 | 96.3473 | 98.7 | [7 empty] | CATEGORYB | SINGLE | KILDARE4 - WHITE EAGLE 138KV CKT 1 | 0 | 514760 | KILDARE4 138.00 | 514761 | WHEAGLE4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  |  |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T3135016SP | FROM->TO | GRIMES - MT. ZION 138KV CKT 1 | E | EES | EES | GSTNAV | GSTHNT | 0 | 334026 | 4GRIMES 138.00 | 334060 | 4MT.ZION 138.00 | 0 |  | 1 | 17SP | 206 | 206 | 0 |  | 89.3425 | 98.7 | [7 empty] | CATEGORYB | SINGLE | 4BENTWATER 138.00 - GRIMES 138KV CKT 1 | 0 | 334026 | 4GRIMES 138.00 | 334039 | 4BENTWATER 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2525516SP | TO->FROM | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 | 17SP | 1076 | 1076 | 0 |  | 92.1801 | 95.6 | [7 empty] | CATEGORYB | SINGLE | JEFFREY ENERGY CENTER - MORRIS COUNTY 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532770 | MORRIS 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T11655016SP | FROM->TO | INDEPENDENCE - MOOREFIELD 161KV CKT 1 | E | EES | EES | EAINTH | EAINTH | 0 | 338142 | 5ISES-1 161.00 | 338138 | 5MORFLD 161.00 | 0 |  | 1 | 17SP | 303 | 303 | 0 | 97 | 96.992 | 95.7 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T7245016SP | FROM->TO | INDEPENDENCE - MOOREFIELD 161KV CKT 1 | E | EES | EES | EAINTH | EAINTH | 0 | 338142 | 5ISES-1 161.00 | 338138 | 5MORFLD 161.00 | 0 |  | 1 | 17SP | 303 | 303 | 0 | 98.6 | 98.585 | 98.2 | [7 empty] | CATEGORYB | SINGLE | DELL 500 - INDEPENDENCE 500KV CKT 1 | 0 | 338145 | 8ISES 500.00 | 338187 | 8DELL 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T13195516SP | FROM->TO | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | E | WERE | WERE | NEAST | NEAST | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 17SP | 280 | 308 | 350 | 97.5 | 97.454 | 97.3 | [7 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3255516SP | TO->FROM | MARYVILLE - MIDWAY 161KV CKT 1 | E | GMO | GMO |  |  | 0 | 541369 | MIDWAY_5 161.00 | 541251 | MARYVLE5 161.00 | 0 |  | 1 | 17SP | 152 | 171 | 171 |  | 65.3472 | 96.4 | [7 empty] | CATEGORYB | SINGLE | FAIRPORT 345/161KV TRANSFORMER CKT 3 | 0 | 300039 | 7FAIRPT 345.00 | 300076 | 5FAIRPT 161.00 | 0 |  | 3 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T14775016SP | FROM->TO | PLEASANT HILL 500/161KV TRANSFORMER CKT 1 | E | EES | EES | EAICEN | EAICEN | 0 | 337922 | 8P HILL 500.00 | 337923 | 5P HILL 161.00 | 0 |  | 1 | 17SP | 600 | 600 | 0 | 97.4 | 97.4402 | 97.4 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE (ANO) 500/161/22.0KV TRANSFORMER CKT 1 | 1 | 337909 | 8ANO 50 500.00 | 337912 | 5ANO 161.00 | 337913 | 1ANOACCD 22.000 | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | INVALID |  |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T2035016SP | FROM->TO | SEVENTEENTH (17TH 4X) 138/69/11.295KV TRANSFORMER CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 1 | 533064 | 17TH 4 138.00 | 533840 | 17TH 2 69.000 | 533112 | 17TH 4 1 11.295 | 1 | 17SP | 150 | 165 | 187.5 |  | 89.3887 | 96.3176 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER NORTH - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533040 | EVANS N4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | INVALID | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T865516SP | FROM->TO | SILOAM CITY - SILOAM SPRINGS 161KV CKT 1 | E | GRDA | AEPW | GRDA-MUN | FAYETTEVILLE | 0 | 512643 | SILMCTY5 161.00 | 506948 | SILOAM 5 161.00 | 0 |  | 1 | 17SP | 288 | 335 | 0 | 96.9 | 96.906 | 97.2513 | [7 empty] | CATEGORYB | SINGLE | FLINT CREEK - SILOAM SPRINGS TAP 345KV CKT 1 | 0 | 506935 | FLINTCR7 345.00 | 512750 | TONECE7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  |  |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T17135016SP | FROM->TO | SUB 1206 (S1206 T1) 161/69/13.8KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 1 | 646206 | S1206 5 161.00 | 647906 | S906 S 8 69.000 | 648206 | S1206T19 13.800 | 1 | 17SP | 201.6 | 201.6 | 201.6 |  | 94.4208 | 99 | [7 empty] | CATEGORYB | NONSINGLE | S1206T2 BSCL | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T17155016SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 17SP | 250 | 250 | 250 | 98.7 | 98.6808 | 98.4 | [7 empty] | CATEGORYB | NONSINGLE | S1217 AUTOV2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T17965516SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 17SP | 250 | 250 | 250 | 98.3 | 98.3454 | 98.4 | [7 empty] | CATEGORYB | NONSINGLE | S1217 AUTOV2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T7225517SP | FROM->TO | 5ALLEN FP 161.00 - HORN LAKE 161KV CKT 1 | E | TVA | EES | MEMPHIS | EMI-SHVN | 0 | 360174 | 5ALLEN FP 161.00 | 337181 | 5HN LAK 161.00 | 0 |  | 1 | 17SP | 226 | 226 | 226 | 95 | 95.0355 | 96.1 | [7 empty] | CATEGORYB | SINGLE | FREEPORT - HORN LAKE 230KV CKT 1 | 0 | 337162 | 6FRPORT 230.00 | 337180 | 6HN LAK 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | INVALID |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1665517SP | TO->FROM | 7JASPER 345.00 - BLACKBERRY 345KV CKT 1 | E | AECI | AECI | KAMO | KAMO | 0 | 300739 | 7BLACKBERRY 345.00 | 300949 | 7JASPER 345.00 | 0 |  | 1 | 17SP | 870 | 870 | 0 |  | 86.4123 | 95.67 | [7 empty] | CATEGORYB | SINGLE | GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 | 0 | 512650 | GRDA1 7 345.00 | 512750 | TONECE7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T19175517SP | TO->FROM | 7JASPER 345.00 - BLACKBERRY 345KV CKT 1 | E | AECI | AECI | KAMO | KAMO | 0 | 300739 | 7BLACKBERRY 345.00 | 300949 | 7JASPER 345.00 | 0 |  | 1 | 17SP | 870 | 870 | 0 |  | 86.6338 | 95.9 | [7 empty] | CATEGORYB | NONSINGLE | GRDA-OPGD-05 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T4265017SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17SP | 615 | 615 | 0 | 95.9 | 95.8901 | 95.4 | [7 empty] | CATEGORYB | SINGLE | WEBRE - WELLS 500KV CKT 1 | 0 | 335368 | 8WELLS 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4285517SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17SP | 615 | 615 | 0 | 95.2 | 95.2165 | 95.1 | [7 empty] | CATEGORYB | SINGLE | 8CAJUN2 - WEBRE 500KV CKT 1 | 0 | 303005 | 8CAJUN2 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T5535517SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17SP | 615 | 615 | 0 | 95.3 | 95.2688 | 95.2 | [7 empty] | CATEGORYB | SINGLE | DYNEGY - PECAN GROVE 230KV CKT 1 | 0 | 335074 | 6DYNEGY 230.00 | 335077 | 6PGROVE 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T5565517SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17SP | 615 | 615 | 0 | 95.8 | 95.7532 | 95.4 | [7 empty] | CATEGORYB | SINGLE | WEBRE - WELLS 500KV CKT 1 | 0 | 335368 | 8WELLS 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T5775017SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17SP | 615 | 615 | 0 | 95.8 | 95.8296 | 95.2 | [7 empty] | CATEGORYB | SINGLE | ELDORADO EHV - STERLINGTON 500KV CKT 1 | 0 | 337420 | 8STERL 500.00 | 337561 | 8ELDEHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T7285517SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17SP | 615 | 615 | 0 | 95.5 | 95.4558 | 95.1 | [7 empty] | CATEGORYB | SINGLE | ELDORADO EHV - STERLINGTON 500KV CKT 1 | 0 | 337420 | 8STERL 500.00 | 337561 | 8ELDEHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2835517SP | TO->FROM | BELL - PECK 69KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533830 | PECK 2 69.000 | 533783 | BELL 2 69.000 | 0 |  | 1 | 17SP | 37 | 37 | 0 |  | 88.6613 | 97.2 | [7 empty] | CATEGORYB | SINGLE | EL PASO - FARBER 138KV CKT 1 | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T20845517SP | FROM->TO | BULL SHOALS - MIDWAY (YVEPA) 161KV CKT 1 | E | SWPA | EES | EMINTH |  | 0 | 505460 | BULL SH5 161.00 | 338813 | 5MIDWAY# 161.00 | 0 |  | 1 | 17SP | 162 | 162 | 0 |  | 90.023 | 99.2 | [7 empty] | CATEGORYB | GENOUT | GEN338143 1-INDEPENDENCE UNIT #1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | INVALID |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2855517SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | E | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17SP | 100 | 100 | 0 |  | 76.7897 | 97.7842 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER NORTH - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533040 | EVANS N4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T145517SP | TO->FROM | DODGE CITY BEEF - JUDSON LARGE 115KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539671 | FTDODGE3 115.00 | 539645 | DCBEEF3 115.00 | 0 |  | 1 | 17SP | 83.9 | 89.6 | 0 | 95.3 | 95.2778 | 95.8 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T2075017SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | E | WERE | WERE | NCENTRAL | NCENTRAL | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 17SP | 280 | 308 | 350 | 98.3 | 98.3232 | 95.1 | [7 empty] | CATEGORYB | SINGLE | EAST MANHATTAN - NORTHWEST MANHATTAN 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 532865 | NWMANHT6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T12075017SP | FROM->TO | EDDY COUNTY INTERCHANGE (WH XHS70551) 230/115/13.2KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-PECO | SPS-PECO | 1 | 527800 | EDDY_SOUTH 6230.00 | 527798 | EDDY_CNTY 3115.00 | 527797 | EDDY_TR2 113.200 | 1 | 17SP | 167 | 167 | 0 | 96.2 | 96.1527 | 95.7 | [7 empty] | CATEGORYB | SINGLE | EDDY COUNTY INTERCHANGE (WH XHS70551) 230/115/13.2KV TRANSFORMER CKT 2 | 1 | 527798 | EDDY_CNTY 3115.00 | 527800 | EDDY_SOUTH 6230.00 | 527795 | EDDY_TR3 1 13.200 | 2 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T12065017SP | FROM->TO | EDDY COUNTY INTERCHANGE (WH XHS70551) 230/115/13.2KV TRANSFORMER CKT 2 | E | SPS | SPS | SPS-PECO | SPS-PECO | 1 | 527800 | EDDY_SOUTH 6230.00 | 527798 | EDDY_CNTY 3115.00 | 527795 | EDDY_TR3 1 13.200 | 2 | 17SP | 167 | 167 | 0 | 96.2 | 96.1527 | 95.7 | [7 empty] | CATEGORYB | SINGLE | EDDY COUNTY INTERCHANGE (WH XHS70551) 230/115/13.2KV TRANSFORMER CKT 1 | 1 | 527798 | EDDY_CNTY 3115.00 | 527800 | EDDY_SOUTH 6230.00 | 527797 | EDDY_TR2 113.200 | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1825517SP | FROM->TO | EL PASO - FARBER 138KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533039 | ELPASO 4 138.00 | 533042 | FARBER 4 138.00 | 0 |  | 1 | 17SP | 160 | 168 | 0 | 96.4 | 96.3612 | 99.8 | [7 empty] | CATEGORYB | SINGLE | KILDARE4 - WHITE EAGLE 138KV CKT 1 | 0 | 514760 | KILDARE4 138.00 | 514761 | WHEAGLE4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T3315017SP | FROM->TO | GRIMES - MT. ZION 138KV CKT 1 | E | EES | EES | GSTNAV | GSTHNT | 0 | 334026 | 4GRIMES 138.00 | 334060 | 4MT.ZION 138.00 | 0 |  | 1 | 17SP | 206 | 206 | 0 |  | 84.6992 | 96.9 | [7 empty] | CATEGORYB | SINGLE | 4BENTWATER 138.00 - WALDEN 138KV CKT 1 | 0 | 334039 | 4BENTWATER 138.00 | 334040 | 4WALDEN 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2825517SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17SP | 95.6 | 95.6 | 0 |  | 76.0114 | 96.3 | [7 empty] | CATEGORYB | SINGLE | COWSKIN - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2645517SP | TO->FROM | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 | 17SP | 1076 | 1076 | 0 |  | 91.9209 | 98.9 | [7 empty] | CATEGORYB | SINGLE | JEFFREY ENERGY CENTER - MORRIS COUNTY 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532770 | MORRIS 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2755517SP | TO->FROM | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 | 17SP | 1076 | 1076 | 0 |  | 91.0397 | 97.9 | [7 empty] | CATEGORYB | SINGLE | AUBURN ROAD - JEFFREY ENERGY CENTER 230KV CKT 1 | 0 | 532851 | AUBURN 6 230.00 | 532852 | JEC 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T7435017SP | FROM->TO | INDEPENDENCE - MOOREFIELD 161KV CKT 1 | E | EES | EES | EAINTH | EAINTH | 0 | 338142 | 5ISES-1 161.00 | 338138 | 5MORFLD 161.00 | 0 |  | 1 | 17SP | 303 | 303 | 0 | 98.5 | 98.4665 | 95.6 | [7 empty] | CATEGORYB | SINGLE | DELL 500 - INDEPENDENCE 500KV CKT 1 | 0 | 338145 | 8ISES 500.00 | 338187 | 8DELL 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T14185517SP | FROM->TO | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | E | WERE | WERE | NEAST | NEAST | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 17SP | 280 | 308 | 350 | 97.2 | 97.1887 | 99.2 | [7 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2785517SP | FROM->TO | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | E | WERE | WERE | NEAST | NEAST | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 17SP | 280 | 308 | 350 | 97.2 | 97.1759 | 99.3 | [7 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T19325517SP | TO->FROM | MARYVILLE - MIDWAY 161KV CKT 1 | E | GMO | GMO |  |  | 0 | 541369 | MIDWAY_5 161.00 | 541251 | MARYVLE5 161.00 | 0 |  | 1 | 17SP | 152 | 171 | 171 |  | 65.562 | 99.7 | [7 empty] | CATEGORYB | NONSINGLE | LN-FAIRPORT | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2115517SP | FROM->TO | MULLERGREN 115/13.8KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539677 | GRTBEND1 13.800 | 539678 | GRTBEND3 115.00 | 0 |  | 1 | 17SP | 106 | 106 | 106 |  | 88.5301 | 95.7 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T14925017SP | FROM->TO | PLEASANT HILL 500/161KV TRANSFORMER CKT 1 | E | EES | EES | EAICEN | EAICEN | 0 | 337922 | 8P HILL 500.00 | 337923 | 5P HILL 161.00 | 0 |  | 1 | 17SP | 600 | 600 | 0 | 97.4 | 97.3906 | 96.3 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE (ANO) 500/161/22.0KV TRANSFORMER CKT 1 | 1 | 337909 | 8ANO 50 500.00 | 337912 | 5ANO 161.00 | 337913 | 1ANOACCD 22.000 | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | INVALID |  |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T2135017SP | FROM->TO | SEVENTEENTH (17TH 4X) 138/69/11.295KV TRANSFORMER CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 1 | 533064 | 17TH 4 138.00 | 533840 | 17TH 2 69.000 | 533112 | 17TH 4 1 11.295 | 1 | 17SP | 150 | 165 | 187.5 |  | 89.4136 | 96.0434 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER NORTH - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533040 | EVANS N4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | INVALID | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T915517SP | FROM->TO | SILOAM CITY - SILOAM SPRINGS 161KV CKT 1 | E | GRDA | AEPW | GRDA-MUN | FAYETTEVILLE | 0 | 512643 | SILMCTY5 161.00 | 506948 | SILOAM 5 161.00 | 0 |  | 1 | 17SP | 288 | 335 | 0 | 96.9 | 96.8696 | 99.8818 | [7 empty] | CATEGORYB | SINGLE | FLINT CREEK - SILOAM SPRINGS TAP 345KV CKT 1 | 0 | 506935 | FLINTCR7 345.00 | 512750 | TONECE7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T17245017SP | FROM->TO | SUB 1206 (S1206 T1) 161/69/13.8KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 1 | 646206 | S1206 5 161.00 | 647906 | S906 S 8 69.000 | 648206 | S1206T19 13.800 | 1 | 17SP | 201.6 | 201.6 | 201.6 |  | 94.3326 | 98.6 | [7 empty] | CATEGORYB | NONSINGLE | S1206T2 BSCL | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T17265017SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 17SP | 250 | 250 | 250 | 98.2 | 98.2419 | 98.2 | [7 empty] | CATEGORYB | NONSINGLE | S1217 AUTOV2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T19435517SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 17SP | 250 | 250 | 250 | 98.3 | 98.336 | 98.3 | [7 empty] | CATEGORYB | NONSINGLE | S1217 AUTOV2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2575514WP | TO->FROM | 4BENTWATER 138.00 - GRIMES 138KV CKT 1 | E | EES | EES | GSTNAV | GSTNAV | 0 | 334026 | 4GRIMES 138.00 | 334039 | 4BENTWATER 138.00 | 0 |  | 1 | 17WP | 206 | 206 | 0 |  | 88.5155 | 97.5 | [7 empty] | CATEGORYB | SINGLE | GRIMES - MT. ZION 138KV CKT 1 | 0 | 334026 | 4GRIMES 138.00 | 334060 | 4MT.ZION 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T10935514WP | FROM->TO | 5OVERTON 161.00 - HUNTSDALE 161KV CKT 1 | E | AMMO | AECI | AMRNMO | CENTRAL | 0 | 345409 | 5OVERTON 161.00 | 300500 | 5HUNTSDL 161.00 | 0 |  | 1 | 17WP | 223 | 223 | 203 |  | 93.6553 | 96.7 | [7 empty] | CATEGORYB | NONSINGLE | AM1_A_OG | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T10125014WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96 | 95.9741 | 95.9 | [7 empty] | CATEGORYB | GENOUT | GEN303006 1-1BC2 U1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T10195014WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96 | 96.0316 | 95.9 | [7 empty] | CATEGORYB | GENOUT | GEN303008 1-1BC2 U3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T10485014WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 98.6 | 98.6178 | 98.6 | [7 empty] | CATEGORYB | GENOUT | GEN336153 1-WATERFORD UNIT#3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T10665514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.2 | 96.2364 | 96.2 | [7 empty] | CATEGORYB | NONSINGLE | CELE-WELLOP2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T11075514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 97 | 97.0106 | 97.2 | [7 empty] | CATEGORYB | GENOUT | GEN303006 1-1BC2 U1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T11225514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 97.1 | 97.0939 | 97.2 | [7 empty] | CATEGORYB | GENOUT | GEN303008 1-1BC2 U3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T1145014WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.4 | 96.4425 | 96.3 | [7 empty] | CATEGORYB | SINGLE | 8CAJUN2 - WEBRE 500KV CKT 1 | 0 | 303005 | 8CAJUN2 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T11795514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 96.1086 | 96.2 | [7 empty] | CATEGORYB | GENOUT | GEN336170 1-GULF OXY U4 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T11885514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.8 | 96.7881 | 96.8 | [7 empty] | CATEGORYB | GENOUT | GEN336251 1-NINEMILE POINT UNIT#4 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T11995514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.8 | 96.8027 | 96.9 | [7 empty] | CATEGORYB | GENOUT | GEN336252 1-NINEMILE POINT UNIT#5 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T12235514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.2 | 96.1629 | 96.2 | [7 empty] | CATEGORYB | GENOUT | GEN501910 1-ACADIA UNIT ST1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T125014WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95.1 | 95.1489 | 95.1 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2005514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 97 | 97.0005 | 97 | [7 empty] | CATEGORYB | SINGLE | 8CAJUN2 - WEBRE 500KV CKT 1 | 0 | 303005 | 8CAJUN2 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T2015014WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.3 | 96.2867 | 96.1 | [7 empty] | CATEGORYB | SINGLE | WEBRE - WELLS 500KV CKT 1 | 0 | 335368 | 8WELLS 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2035514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95 | 95.0041 | 95 | [7 empty] | CATEGORYB | SINGLE | 8CAJUN2 - FANCY POINT 500KV CKT 1 | 0 | 303005 | 8CAJUN2 500.00 | 335835 | 8FANCY 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T2315014WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.7 | 96.7212 | 96.6 | [7 empty] | CATEGORYB | SINGLE | COLY - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WGLEN 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2335514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 95.1758 | 95.2 | [7 empty] | CATEGORYB | SINGLE | 6FRNSTL - SORRENTO 230KV CKT 1 | 0 | 303204 | 6FRNSTL 230.00 | 336060 | 6SORR 2 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T235514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95.6 | 95.6289 | 95.7 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T2365014WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.8 | 96.7692 | 96.7 | [7 empty] | CATEGORYB | SINGLE | WATERFORD - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WGLEN 500.00 | 336150 | 8WATERFO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T2475014WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.7 | 96.6749 | 96.6 | [7 empty] | CATEGORYB | SINGLE | JAGUAR - POINT ESSO TAP 230KV CKT 1 | 0 | 335641 | 6TP.ESSO 230.00 | 335770 | 6JAGUAR 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T2615014WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.4 | 96.3862 | 96.3 | [7 empty] | CATEGORYB | SINGLE | ENJAY - JAGUAR 230KV CKT 1 | 0 | 335770 | 6JAGUAR 230.00 | 335772 | 6ENJAY 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T265014WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95.9 | 95.8579 | 95.8 | [7 empty] | CATEGORYB | SINGLE | BARKERS 6 230.00 - RAMSAY 230KV CKT 1 | 0 | 500025 | BARKERS 6 230.00 | 500750 | RAMSAY 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T2695014WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.5 | 96.4839 | 96.4 | [7 empty] | CATEGORYB | SINGLE | ENJAY - FANCY POINT 230KV CKT 1 | 0 | 335772 | 6ENJAY 230.00 | 335825 | 6FANCY 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T285014WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95.7 | 95.693 | 95.6 | [7 empty] | CATEGORYB | SINGLE | BAYOU SALE - TECHE 138KV CKT 1 | 0 | 500050 | BSALES 4 138.00 | 500820 | TECHE 4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T2955014WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 97.8 | 97.8161 | 97.6 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3115514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.4 | 96.4393 | 96.5 | [7 empty] | CATEGORYB | SINGLE | HARTBURG - MOUNT OLIVE 500KV CKT 1 | 0 | 334325 | 8HARTBRG 500.00 | 337368 | 8MTOLIV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3175514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.2 | 96.1669 | 96.4 | [7 empty] | CATEGORYB | SINGLE | NELSON - RICHARD 500KV CKT 1 | 0 | 335192 | 8NELSON 500.00 | 335367 | 8RICHARD 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T3235014WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.4 | 96.3908 | 96.3 | [7 empty] | CATEGORYB | SINGLE | BOGALUSA 500/230KV TRANSFORMER CKT 1 | 0 | 336130 | 8BOGALUS 500.00 | 336131 | 6ADMSCRK 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3235514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.7 | 96.6875 | 96.6 | [7 empty] | CATEGORYB | SINGLE | WEBRE - WELLS 500KV CKT 1 | 0 | 335368 | 8WELLS 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T335014WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96 | 95.9818 | 95.9 | [7 empty] | CATEGORYB | SINGLE | COCODRIE - VILLE PLATTE 230KV CKT 1 | 0 | 500190 | COCODR 6 230.00 | 500880 | VILPLT 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T3355014WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.6 | 96.606 | 96.5 | [7 empty] | CATEGORYB | SINGLE | BOGALUSA - FRANKLIN 500KV CKT 1 | 0 | 336130 | 8BOGALUS 500.00 | 336562 | 8FRKLIN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T3425014WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.2 | 96.2211 | 96.2 | [7 empty] | CATEGORYB | SINGLE | WATERFORD 500/230KV TRANSFORMER CKT 1 | 0 | 336150 | 8WATERFO 500.00 | 336154 | 6WATFRD 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T345014WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95.7 | 95.7054 | 95.7 | [7 empty] | CATEGORYB | SINGLE | COUGHLIN - PLAISANCE 138KV CKT 1 | 0 | 500230 | COUGH 4 138.00 | 500720 | PLAISAN4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T3595014WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95.7 | 95.6662 | 95.6 | [7 empty] | CATEGORYB | SINGLE | ELDORADO EHV - MOUNT OLIVE 500KV CKT 1 | 0 | 337368 | 8MTOLIV 500.00 | 337561 | 8ELDEHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T3625014WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.2 | 96.2025 | 96 | [7 empty] | CATEGORYB | SINGLE | ELDORADO EHV - STERLINGTON 500KV CKT 1 | 0 | 337420 | 8STERL 500.00 | 337561 | 8ELDEHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3715514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 97.4 | 97.4377 | 97.5 | [7 empty] | CATEGORYB | SINGLE | COLY - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WGLEN 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3775514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 97.7 | 97.7376 | 98.1 | [7 empty] | CATEGORYB | SINGLE | WATERFORD - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WGLEN 500.00 | 336150 | 8WATERFO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3885514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 97.3 | 97.2909 | 97.2 | [7 empty] | CATEGORYB | SINGLE | JAGUAR - POINT ESSO TAP 230KV CKT 1 | 0 | 335641 | 6TP.ESSO 230.00 | 335770 | 6JAGUAR 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T395014WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95.8 | 95.8438 | 95.8 | [7 empty] | CATEGORYB | SINGLE | VILLE PLATTE - WESTFORK 230KV CKT 1 | 0 | 500880 | VILPLT 6 230.00 | 500920 | WSTFORK6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T405514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.5 | 96.4879 | 96.5 | [7 empty] | CATEGORYB | SINGLE | BARKERS 6 230.00 - RAMSAY 230KV CKT 1 | 0 | 500025 | BARKERS 6 230.00 | 500750 | RAMSAY 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4095514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 97 | 96.9964 | 97.1 | [7 empty] | CATEGORYB | SINGLE | ENJAY - JAGUAR 230KV CKT 1 | 0 | 335770 | 6JAGUAR 230.00 | 335772 | 6ENJAY 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T415014WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95.7 | 95.7162 | 95.7 | [7 empty] | CATEGORYB | SINGLE | WELLS - WESTFORK 230KV CKT 1 | 0 | 500920 | WSTFORK6 230.00 | 500940 | WELLS 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4185514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 97.2 | 97.165 | 97.2 | [7 empty] | CATEGORYB | SINGLE | ENJAY - FANCY POINT 230KV CKT 1 | 0 | 335772 | 6ENJAY 230.00 | 335825 | 6FANCY 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T425514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.2 | 96.2331 | 96.3 | [7 empty] | CATEGORYB | SINGLE | BAYOU SALE - TECHE 138KV CKT 1 | 0 | 500050 | BSALES 4 138.00 | 500820 | TECHE 4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4445514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 98.9 | 98.858 | 98.9 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T445514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.1 | 96.1318 | 96.2 | [7 empty] | CATEGORYB | SINGLE | BAYOU SALE - WAXLAKE 138KV CKT 1 | 0 | 500050 | BSALES 4 138.00 | 500890 | WAXLAKE4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4805514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 97.2 | 97.234 | 97.3 | [7 empty] | CATEGORYB | SINGLE | BOGALUSA 500/230KV TRANSFORMER CKT 1 | 0 | 336130 | 8BOGALUS 500.00 | 336131 | 6ADMSCRK 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T495514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.5 | 96.5151 | 96.6 | [7 empty] | CATEGORYB | SINGLE | COCODRIE - VILLE PLATTE 230KV CKT 1 | 0 | 500190 | COCODR 6 230.00 | 500880 | VILPLT 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4955514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 97.5 | 97.5223 | 97.5 | [7 empty] | CATEGORYB | SINGLE | BOGALUSA - FRANKLIN 500KV CKT 1 | 0 | 336130 | 8BOGALUS 500.00 | 336562 | 8FRKLIN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T5045514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 97.1 | 97.0933 | 97.2 | [7 empty] | CATEGORYB | SINGLE | WATERFORD 500/230KV TRANSFORMER CKT 1 | 0 | 336150 | 8WATERFO 500.00 | 336154 | 6WATFRD 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T5185514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.3 | 96.2762 | 96.3 | [7 empty] | CATEGORYB | SINGLE | FRANKLIN - GRAND GULF 500KV CKT 1 | 0 | 336562 | 8FRKLIN 500.00 | 336820 | 8G.GULF 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T5305514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.6 | 96.6179 | 96.7 | [7 empty] | CATEGORYB | SINGLE | ELDORADO EHV - MOUNT OLIVE 500KV CKT 1 | 0 | 337368 | 8MTOLIV 500.00 | 337561 | 8ELDEHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T535514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.3 | 96.2896 | 96.4 | [7 empty] | CATEGORYB | SINGLE | COUGHLIN - PLAISANCE 138KV CKT 1 | 0 | 500230 | COUGH 4 138.00 | 500720 | PLAISAN4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T5365514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.3 | 96.3132 | 96.2 | [7 empty] | CATEGORYB | SINGLE | ELDORADO EHV - STERLINGTON 500KV CKT 1 | 0 | 337420 | 8STERL 500.00 | 337561 | 8ELDEHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T605514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95 | 95.005 | 95 | [7 empty] | CATEGORYB | SINGLE | MARKSVILLE - YELLOW BAYOU 138KV CKT 1 | 0 | 500560 | MARKSVL4 138.00 | 500960 | YBAYOU 4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T6215514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.7 | 96.701 | 96.7 | [7 empty] | CATEGORYB | SINGLE | BARKERS 6 230.00 - BOGALUSA 230KV CKT 1 | 0 | 500025 | BARKERS 6 230.00 | 336136 | 6BOGALUS 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T635514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.4 | 96.3755 | 96.5 | [7 empty] | CATEGORYB | SINGLE | VILLE PLATTE - WESTFORK 230KV CKT 1 | 0 | 500880 | VILPLT 6 230.00 | 500920 | WSTFORK6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T655514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.2 | 96.2321 | 96.3 | [7 empty] | CATEGORYB | SINGLE | WELLS - WESTFORK 230KV CKT 1 | 0 | 500920 | WSTFORK6 230.00 | 500940 | WELLS 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T9865014WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95.7 | 95.7402 | 95.6 | [7 empty] | CATEGORYB | NONSINGLE | CELE-WELLOP2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FNSL | FDNS-Blown up | FNSL | FDNS-Blown up | 5 | 0 | 2011AGP1AFS92T115014WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.3 | 96.2989 | 96.2 | [7 empty] | CATEGORYB | GENOUT | GEN335831 1-RIVERBEND UNIT#1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FNSL | FDNS-Blown up | FNSL | FDNS-Blown up | 5 | 5 | 2011AGP1AFS92T125514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 97.1 | 97.1569 | 97.2 | [7 empty] | CATEGORYB | GENOUT | GEN335831 1-RIVERBEND UNIT#1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FNSL | FDNS-Blown up | FNSL | FDNS-Blown up | 5 | 0 | 2011AGP1AFS92T215014WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.2 | 96.2157 | 96.2 | [7 empty] | CATEGORYB | GENOUT | GEN336251 1-NINEMILE POINT UNIT#4 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FNSL | FDNS-Blown up | FNSL | FDNS-Blown up | 5 | 0 | 2011AGP1AFS92T315014WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.3 | 96.2622 | 96.2 | [7 empty] | CATEGORYB | GENOUT | GEN336252 1-NINEMILE POINT UNIT#5 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T11675514WP | TO->FROM | BARKERS 6 230.00 - BOGALUSA 230KV CKT 1 | E | EES | CLEC |  | CLE_EAST | 0 | 336136 | 6BOGALUS 230.00 | 500025 | BARKERS 6 230.00 | 0 |  | 1 | 17WP | 431 | 454 | 0 | 96.5 | 96.4631 | 97.4 | [7 empty] | CATEGORYB | GENOUT | GEN336153 1-WATERFORD UNIT#3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T6295514WP | TO->FROM | BARKERS 6 230.00 - BOGALUSA 230KV CKT 1 | E | EES | CLEC |  | CLE_EAST | 0 | 336136 | 6BOGALUS 230.00 | 500025 | BARKERS 6 230.00 | 0 |  | 1 | 17WP | 431 | 454 | 0 | 97.5 | 97.5434 | 98.8 | [7 empty] | CATEGORYB | SINGLE | 6TALISK - NORTH SLIDELL 230KV CKT 1 | 0 | 500640 | NSLID 6 230.00 | 303221 | 6TALISK 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T10635514WP | TO->FROM | BOGALUSA - FRANKLIN 500KV CKT 1 | E | EES | EES | AEC | AMSNSH | 0 | 336562 | 8FRKLIN 500.00 | 336130 | 8BOGALUS 500.00 | 0 |  | 1 | 17WP | 1200 | 1200 | 0 |  | 93.3483 | 95.6 | [7 empty] | CATEGORYB | NONSINGLE | CELE-WELLOP1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4475514WP | TO->FROM | BOGALUSA - FRANKLIN 500KV CKT 1 | E | EES | EES | AEC | AMSNSH | 0 | 336562 | 8FRKLIN 500.00 | 336130 | 8BOGALUS 500.00 | 0 |  | 1 | 17WP | 1200 | 1200 | 0 |  | 93.8297 | 96 | [7 empty] | CATEGORYB | SINGLE | FRANKLIN - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 336562 | 8FRKLIN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T4305014WP | TO->FROM | CALICO ROCK - MELBOURNE 161KV CKT 1 | E | EES | EES | EAINTH |  | 0 | 338131 | 5MELBRN 161.00 | 338130 | 5CALCR 161.00 | 0 |  | 1 | 17WP | 148 | 148 | 0 | 103.7 | 103.6949 | 99.5 | [7 empty] | CATEGORYB | SINGLE | HARDY NORTH - MAMMOTH SPRINGS (AECC) 161KV CKT 1 | 0 | 338214 | 5HRDY-N 161.00 | 338815 | 5MAMSPR# 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T4375014WP | TO->FROM | CALICO ROCK - MELBOURNE 161KV CKT 1 | E | EES | EES | EAINTH |  | 0 | 338131 | 5MELBRN 161.00 | 338130 | 5CALCR 161.00 | 0 |  | 1 | 17WP | 148 | 148 | 0 | 104.1 | 104.0924 | 99.9 | [7 empty] | CATEGORYB | SINGLE | BEE BRANCH (AECC) - CLINTON 161KV CKT 1 | 0 | 338831 | 5BEE BR# 161.00 | 338833 | 5CLIN-IN# 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | CONT-Hayti-Blytheville 161kV Line Overload | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T9005014WP | TO->FROM | CALICO ROCK - MELBOURNE 161KV CKT 1 | E | EES | EES | EAINTH |  | 0 | 338131 | 5MELBRN 161.00 | 338130 | 5CALCR 161.00 | 0 |  | 1 | 17WP | 148 | 148 | 0 | 102.5 | 102.5117 | 99.2 | [7 empty] | CATEGORYB | SINGLE | DELL 500 - NEW MADRID 500KV CKT 1 | 0 | 338187 | 8DELL 500.00 | 300035 | 8NEWMAD 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T6315014WP | FROM->TO | CALICO ROCK - NORFORK 161KV CKT 1 | E | EES | SWPA |  | EMINTH | 0 | 338130 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 17WP | 148 | 148 | 0 | 103.4 | 103.3632 | 98 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1795514WP | FROM->TO | CANADAY - ELM CREEK 115KV CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640103 | CANADAY7 115.00 | 640161 | ELMCRK_7 115.00 | 0 |  | 1 | 17WP | 80 | 80 | 88 |  | 81.7311 | 96.5 | [7 empty] | CATEGORYB | SINGLE | CROOKED CREEK - RIVERDALE 230KV CKT 1 | 0 | 640093 | C.CREEK4 230.00 | 640330 | RIVERDL4 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T10805514WP | TO->FROM | CLAY - SPRINGFIELD 161KV CKT 1 | E | SWPA | SPRM | EMINTH | SPRM > 69KV | 0 | 505492 | SPRGFLD5 161.00 | 549970 | CLAY 5161.00 | 0 |  | 1 | 17WP | 167 | 167 | 0 |  | 89.5442 | 97.6 | [7 empty] | CATEGORYB | NONSINGLE | AI03 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T10765514WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | E | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17WP | 100 | 100 | 0 |  | 84.7471 | 98.8 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T12405514WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | E | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17WP | 100 | 100 | 0 |  | 82.8584 | 97.8 | [7 empty] | CATEGORYB | GENOUT | GEN532751 1-WOLF CREEK GENERATING STATION UNIT 1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | INVALID |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1425514WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | E | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 17WP | 100 | 100 | 0 |  | 85.3564 | 99.4024 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER NORTH - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533040 | EVANS N4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1765514WP | TO->FROM | GRAND ISLAND - SWEETWATER 345KV CKT 1 | E | NPPD | NPPD | NPPD_686 | WAPA_1606 | 0 | 640374 | SWEET W3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 | 17WP | 717 | 717 | 789 |  | 89.2377 | 95.6 | [7 empty] | CATEGORYB | SINGLE | AXTELL - PAULINE 345KV CKT 1 | 0 | 640065 | AXTELL 3 345.00 | 640312 | PAULINE3 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SPP_FG-EES-IDC-15974 |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2505514WP | FROM->TO | GRIMES - MT. ZION 138KV CKT 1 | E | EES | EES | GSTNAV | GSTHNT | 0 | 334026 | 4GRIMES 138.00 | 334060 | 4MT.ZION 138.00 | 0 |  | 1 | 17WP | 206 | 206 | 0 |  | 87.6292 | 96.2 | [7 empty] | CATEGORYB | SINGLE | GRIMES - MAGNOLIA ANDERSON 138KV CKT 1 | 0 | 334025 | 4MAG AND 138.00 | 334026 | 4GRIMES 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2635514WP | FROM->TO | GRIMES - MT. ZION 138KV CKT 1 | E | EES | EES | GSTNAV | GSTHNT | 0 | 334026 | 4GRIMES 138.00 | 334060 | 4MT.ZION 138.00 | 0 |  | 1 | 17WP | 206 | 206 | 0 |  | 88.2836 | 98.6 | [7 empty] | CATEGORYB | SINGLE | LAKE FOREST - WOODHAVEN 138KV CKT 1 | 0 | 334042 | 4LFOREST 138.00 | 334105 | 4WDHAVN 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3095514WP | FROM->TO | GRIMES - MT. ZION 138KV CKT 1 | E | EES | EES | GSTNAV | GSTHNT | 0 | 334026 | 4GRIMES 138.00 | 334060 | 4MT.ZION 138.00 | 0 |  | 1 | 17WP | 206 | 206 | 0 |  | 91.0375 | 99.8 | [7 empty] | CATEGORYB | SINGLE | HARTBURG - MOUNT OLIVE 500KV CKT 1 | 0 | 334325 | 8HARTBRG 500.00 | 337368 | 8MTOLIV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T12425514WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 |  | 79.6954 | 95.3 | [7 empty] | CATEGORYB | GENOUT | GEN539670 4-JUDSON LARGE GENERATOR | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T12455514WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 |  | 83.6656 | 95.6 | [7 empty] | CATEGORYB | GENOUT | GEN560669 1-G10_057 0.6900 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | CONT-1213 - Circle - Hutchinson |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1465514WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 |  | 80.7189 | 95.9 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - HUTCHINSON ENERGY CENTER 115KV CKT 1 | 0 | 533413 | CIRCLE 3 115.00 | 533419 | HEC 3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1635514WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 |  | 80.0369 | 95.4 | [7 empty] | CATEGORYB | SINGLE | EASTOWN7 345.00 - IATAN 345KV CKT 1 | 0 | 541400 | EASTOWN7 345.00 | 542982 | IATAN 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T75514WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 |  | 83.6656 | 99 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2545514WP | TO->FROM | HUNTSVILLE - LINE 558 TAP 138KV CKT 1 | E | EES | EES | GSTHNT | GSTHNT | 0 | 334058 | 4L558T485 138.00 | 334057 | 4HUNTSVL 138.00 | 0 |  | 1 | 17WP | 206 | 206 | 0 |  | 84.5864 | 95 | [7 empty] | CATEGORYB | SINGLE | 4BENTWATER 138.00 - GRIMES 138KV CKT 1 | 0 | 334026 | 4GRIMES 138.00 | 334039 | 4BENTWATER 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1625514WP | FROM->TO | IATAN - STRANGER CREEK 345KV CKT 1 | E | KCPL | WERE | KACP | NEAST | 0 | 542982 | IATAN 7 345.00 | 532772 | STRANGR7 345.00 | 0 |  | 1 | 17WP | 1195 | 1195 | 0 | 95.9 | 95.9137 | 96.4 | [7 empty] | CATEGORYB | SINGLE | EASTOWN7 345.00 - IATAN 345KV CKT 1 | 0 | 541400 | EASTOWN7 345.00 | 542982 | IATAN 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3695514WP | FROM->TO | JAGUAR - POINT ESSO TAP 230KV CKT 1 | E | EES | EES | GSLBTR | GSLBTR | 0 | 335770 | 6JAGUAR 230.00 | 335641 | 6TP.ESSO 230.00 | 0 |  | 1 | 17WP | 685 | 685 | 0 | 97.8 | 97.7524 | 98.2 | [7 empty] | CATEGORYB | SINGLE | COLY - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WGLEN 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T10755014WP | FROM->TO | KN WRITESVILLE (KNWRIVL1) 500/13.8/13.8KV TRANSFORMER CKT 1 | E | EES | EES | EAILTR | EAILTR-A | 2 | 338507 | 1C1KNWRI 13.800 | 337860 | 8KNWRIVL 500.00 | 338508 | 1C3KNWRI 13.800 | 1 | 17WP | 235 | 235 | 0 | 95.8 | 95.8177 | 95.7 | [7 empty] | CATEGORYB | GENOUT | GEN338510 1-1S1KNWRI | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T10765014WP | FROM->TO | KN WRITESVILLE (KNWRIVL1) 500/13.8/13.8KV TRANSFORMER CKT 1 | E | EES | EES | EAILTR | EAILTR-A | 2 | 338507 | 1C1KNWRI 13.800 | 337860 | 8KNWRIVL 500.00 | 338508 | 1C3KNWRI 13.800 | 1 | 17WP | 235 | 235 | 0 | 95.6 | 95.6468 | 95.5 | [7 empty] | CATEGORYB | GENOUT | GEN338511 1-1C7KNWRI | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T3655014WP | FROM->TO | KN WRITESVILLE (KNWRIVL1) 500/13.8/13.8KV TRANSFORMER CKT 1 | E | EES | EES | EAILTR | EAILTR-A | 2 | 338507 | 1C1KNWRI 13.800 | 337860 | 8KNWRIVL 500.00 | 338508 | 1C3KNWRI 13.800 | 1 | 17WP | 235 | 235 | 0 | 99.2 | 99.173 | 98.4 | [7 empty] | CATEGORYB | SINGLE | KEO EHV - WHITE BLUFF 500KV CKT 1 | 0 | 337651 | 8WH BLF 500.00 | 337957 | 8KEO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T10725014WP | FROM->TO | KN WRITESVILLE (KNWRIVL2) 500/13.8/13.8KV TRANSFORMER CKT 1 | E | EES | EES | EAILTR | EAILTR-A | 2 | 338509 | 1C5KNWRI 13.800 | 337860 | 8KNWRIVL 500.00 | 338510 | 1S1KNWRI 13.800 | 1 | 17WP | 235 | 235 | 0 | 99.6 | 99.6429 | 99.2 | [7 empty] | CATEGORYB | GENOUT | GEN338146 1-INDEPENDENCE UNIT #2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T10775014WP | FROM->TO | KN WRITESVILLE (KNWRIVL2) 500/13.8/13.8KV TRANSFORMER CKT 1 | E | EES | EES | EAILTR | EAILTR-A | 2 | 338509 | 1C5KNWRI 13.800 | 337860 | 8KNWRIVL 500.00 | 338510 | 1S1KNWRI 13.800 | 1 | 17WP | 235 | 235 | 0 | 99.4 | 99.4443 | 99.3 | [7 empty] | CATEGORYB | GENOUT | GEN338511 1-1C7KNWRI | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T10785014WP | FROM->TO | KN WRITESVILLE (KNWRIVL2) 500/13.8/13.8KV TRANSFORMER CKT 1 | E | EES | EES | EAILTR | EAILTR-A | 2 | 338509 | 1C5KNWRI 13.800 | 337860 | 8KNWRIVL 500.00 | 338510 | 1S1KNWRI 13.800 | 1 | 17WP | 235 | 235 | 0 | 98 | 98.0147 | 97.9 | [7 empty] | CATEGORYB | GENOUT | GEN338512 1-1S2KNWRI | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T185014WP | FROM->TO | KN WRITESVILLE (KNWRIVL2) 500/13.8/13.8KV TRANSFORMER CKT 1 | E | EES | EES | EAILTR | EAILTR-A | 2 | 338509 | 1C5KNWRI 13.800 | 337860 | 8KNWRIVL 500.00 | 338510 | 1S1KNWRI 13.800 | 1 | 17WP | 235 | 235 | 0 | 95.6 | 95.5566 | 95.4 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2605514WP | TO->FROM | LINE 558 TAP - MT. ZION 138KV CKT 1 | E | EES | EES | GSTHNT | GSTHNT | 0 | 334060 | 4MT.ZION 138.00 | 334058 | 4L558T485 138.00 | 0 |  | 1 | 17WP | 206 | 206 | 0 |  | 88.8953 | 99.3 | [7 empty] | CATEGORYB | SINGLE | 4BENTWATER 138.00 - WALDEN 138KV CKT 1 | 0 | 334039 | 4BENTWATER 138.00 | 334040 | 4WALDEN 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  |  |  | FNSL | FDNS-Blown up | 5 | 0 | 2011AGP1AFS92T75014WP | FROM->TO | MONETTE JUNCTION - PARAGOULD 161 161KV CKT 1 | E | EES | EES | EAINTH | EAINTH | 0 | 338186 | 5MONETE 161.00 | 338204 | 5PARAG 161.00 | 0 |  | 1 | 17WP | 148 | 148 | 0 |  | 92.6276 | 98.3 | [7 empty] | CATEGORYB | SINGLE | 8SHELBY TN 500.00 - PLUM POINT 500KV CKT 1 | 0 | 338188 | 8SANSOUC 500.00 | 360021 | 8SHELBY TN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1315514WP | TO->FROM | MUND - PENTAGON 115KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 533261 | PENTAGN3 115.00 | 533282 | MUND 3 115.00 | 0 |  | 1 | 17WP | 179 | 194 | 0 | 100.6 | 100.5658 | 95.4 | [7 empty] | CATEGORYB | SINGLE | 87th STREET - CRAIG 345KV CKT 1 | 0 | 532775 | 87TH 7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T385514WP | FROM->TO | SPSNORTH_STX | E |  |  |  |  | SPSNORTH_STX | 0 |  | 0 |  | 0 |  |  | 17WP | 800 | 800 | 800 | 98.7 | 98.9383 | 99.5 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T5695514WP | FROM->TO | STEGALL - VICTORY HILL 230KV CKT 1 | E | WAPA | NPPD | WAPA_1603 | NPPD_686 | 0 | 652573 | STEGALL4 230.00 | 640396 | VICTRYH4 230.00 | 0 |  | 1 | 17WP | 240 | 240 | 264 |  | 92.6752 | 95.5 | [7 empty] | CATEGORYB | SINGLE | STEGALL - WAYSIDE 230KV CKT 1 | 0 | 640404 | WAYSIDE4 230.00 | 652573 | STEGALL4 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SWINGBUS | FNSL | FDNS-Iteration limit exceeded | FNSL | FDNS-Iteration limit exceeded | 5 | 5 | 2011AGP1AFS92T15514WP | FROM->TO | SUB 167 - RIVERTON 69/13.2KV TRANSFORMER CKT 1 | E | EMDE | EMDE | BAXTER | BAXTER | 0 | 547645 | R8G167 1 13.200 | 547541 | RIV167 2 69.000 | 0 |  | 1 | 17WP | 52 | 52 | 0 | 97 | 96.9735 | 97.1 | [7 empty] | CATEGORYB | SINGLE | SUB 368 - DADEVILLE EAST - SUB 431 - BOLIVAR SOUTH 161KV CKT 1 | 0 | 547478 | DAD368 5 161.00 | 547493 | BOL431 5 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 | SPP_FG-EES-IDC-15730 | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3505514WP | FROM->TO | WILLOW GLEN 500/138KV TRANSFORMER CKT 1 | E | EES | EES | GSLBTR | GSLBTR | 0 | 335618 | 8WGLEN 500.00 | 335601 | 4WGLEN-2 138.00 | 0 |  | 1 | 17WP | 560 | 560 | 0 | 99 | 99.0145 | 99.9 | [7 empty] | CATEGORYB | SINGLE | WILLOW GLEN 500/230KV TRANSFORMER CKT 1 | 0 | 335568 | 6WGLEN 230.00 | 335618 | 8WGLEN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3485514WP | FROM->TO | WILLOW GLEN 500/230KV TRANSFORMER CKT 1 | E | EES | EES | GSLBTR | GSLBTR | 0 | 335618 | 8WGLEN 500.00 | 335568 | 6WGLEN 230.00 | 0 |  | 1 | 17WP | 672 | 672 | 0 | 98.5 | 98.4852 | 99.2 | [7 empty] | CATEGORYB | SINGLE | WILLOW GLEN 230/138KV TRANSFORMER CKT 1 | 0 | 335568 | 6WGLEN 230.00 | 335601 | 4WGLEN-2 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-14 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4285514WP | FROM->TO | WILLOW GLEN 500/230KV TRANSFORMER CKT 1 | E | EES | EES | GSLBTR | GSLBTR | 0 | 335618 | 8WGLEN 500.00 | 335568 | 6WGLEN 230.00 | 0 |  | 1 | 17WP | 672 | 672 | 0 | 98.7 | 98.6791 | 99.4 | [7 empty] | CATEGORYB | SINGLE | FANCY POINT - WATERLOO 230KV CKT 1 | 0 | 335825 | 6FANCY 230.00 | 335827 | 6WATLOO 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2125516WP | TO->FROM | 4BENTWATER 138.00 - GRIMES 138KV CKT 1 | E | EES | EES | GSTNAV | GSTNAV | 0 | 334026 | 4GRIMES 138.00 | 334039 | 4BENTWATER 138.00 | 0 |  | 1 | 17WP | 206 | 206 | 0 |  | 88.4689 | 97.5 | [7 empty] | CATEGORYB | SINGLE | GRIMES - MT. ZION 138KV CKT 1 | 0 | 334026 | 4GRIMES 138.00 | 334060 | 4MT.ZION 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T10515516WP | FROM->TO | 5OVERTON 161.00 - HUNTSDALE 161KV CKT 1 | E | AMMO | AECI | AMRNMO | CENTRAL | 0 | 345409 | 5OVERTON 161.00 | 300500 | 5HUNTSDL 161.00 | 0 |  | 1 | 17WP | 223 | 223 | 203 | 96 | 96.021 | 99.1 | [7 empty] | CATEGORYB | NONSINGLE | AM1_A_OG | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T10525516WP | TO->FROM | 5PERCHE 161.00 - HUNTSDALE 161KV CKT 1 | E | AECI | CWLD | CENTRAL | CMWL | 0 | 300500 | 5HUNTSDL 161.00 | 343004 | 5PERCHE 161.00 | 0 |  | 1 | 17WP | 223 | 223 | 223 |  | 92.4826 | 95.6 | [7 empty] | CATEGORYB | NONSINGLE | AM1_A_OG | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T10225016WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96 | 95.9775 | 95.9 | [7 empty] | CATEGORYB | GENOUT | GEN303006 1-1BC2 U1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T10255516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.2 | 96.2366 | 96.2 | [7 empty] | CATEGORYB | NONSINGLE | CELE-WELLOP2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T10295016WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96 | 96.0351 | 95.9 | [7 empty] | CATEGORYB | GENOUT | GEN303008 1-1BC2 U3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T10585016WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 98.6 | 98.6245 | 98.6 | [7 empty] | CATEGORYB | GENOUT | GEN336153 1-WATERFORD UNIT#3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T11175516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 96.1099 | 96.2 | [7 empty] | CATEGORYB | GENOUT | GEN336170 1-GULF OXY U4 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T11265516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.8 | 96.7916 | 96.8 | [7 empty] | CATEGORYB | GENOUT | GEN336251 1-NINEMILE POINT UNIT#4 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T11375516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.8 | 96.8062 | 96.9 | [7 empty] | CATEGORYB | GENOUT | GEN336252 1-NINEMILE POINT UNIT#5 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T11585516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.2 | 96.1639 | 96.2 | [7 empty] | CATEGORYB | GENOUT | GEN501910 1-ACADIA UNIT ST1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T1165016WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.4 | 96.4411 | 96.3 | [7 empty] | CATEGORYB | SINGLE | 8CAJUN2 - WEBRE 500KV CKT 1 | 0 | 303005 | 8CAJUN2 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T125016WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95.1 | 95.1481 | 95.1 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1565516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 97 | 97.0008 | 97 | [7 empty] | CATEGORYB | SINGLE | 8CAJUN2 - WEBRE 500KV CKT 1 | 0 | 303005 | 8CAJUN2 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1595516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95 | 95.0042 | 95 | [7 empty] | CATEGORYB | SINGLE | 8CAJUN2 - FANCY POINT 500KV CKT 1 | 0 | 303005 | 8CAJUN2 500.00 | 335835 | 8FANCY 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1895516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 95.1762 | 95.2 | [7 empty] | CATEGORYB | SINGLE | 6FRNSTL - SORRENTO 230KV CKT 1 | 0 | 303204 | 6FRNSTL 230.00 | 336060 | 6SORR 2 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T2035016WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.3 | 96.2847 | 96.1 | [7 empty] | CATEGORYB | SINGLE | WEBRE - WELLS 500KV CKT 1 | 0 | 335368 | 8WELLS 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T225516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95.6 | 95.6287 | 95.7 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T2335016WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.7 | 96.7197 | 96.6 | [7 empty] | CATEGORYB | SINGLE | COLY - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WGLEN 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T2385016WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.8 | 96.7683 | 96.7 | [7 empty] | CATEGORYB | SINGLE | WATERFORD - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WGLEN 500.00 | 336150 | 8WATERFO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T2495016WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.7 | 96.6737 | 96.6 | [7 empty] | CATEGORYB | SINGLE | JAGUAR - POINT ESSO TAP 230KV CKT 1 | 0 | 335641 | 6TP.ESSO 230.00 | 335770 | 6JAGUAR 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T2635016WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.4 | 96.3851 | 96.3 | [7 empty] | CATEGORYB | SINGLE | ENJAY - JAGUAR 230KV CKT 1 | 0 | 335770 | 6JAGUAR 230.00 | 335772 | 6ENJAY 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T265016WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95.9 | 95.8568 | 95.8 | [7 empty] | CATEGORYB | SINGLE | BARKERS 6 230.00 - RAMSAY 230KV CKT 1 | 0 | 500025 | BARKERS 6 230.00 | 500750 | RAMSAY 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2665516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.4 | 96.4413 | 96.5 | [7 empty] | CATEGORYB | SINGLE | HARTBURG - MOUNT OLIVE 500KV CKT 1 | 0 | 334325 | 8HARTBRG 500.00 | 337368 | 8MTOLIV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T2715016WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.5 | 96.4828 | 96.4 | [7 empty] | CATEGORYB | SINGLE | ENJAY - FANCY POINT 230KV CKT 1 | 0 | 335772 | 6ENJAY 230.00 | 335825 | 6FANCY 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2725516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.2 | 96.1682 | 96.4 | [7 empty] | CATEGORYB | SINGLE | NELSON - RICHARD 500KV CKT 1 | 0 | 335192 | 8NELSON 500.00 | 335367 | 8RICHARD 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2785516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.7 | 96.687 | 96.6 | [7 empty] | CATEGORYB | SINGLE | WEBRE - WELLS 500KV CKT 1 | 0 | 335368 | 8WELLS 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T285016WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95.7 | 95.6836 | 95.6 | [7 empty] | CATEGORYB | SINGLE | BAYOU SALE - TECHE 138KV CKT 1 | 0 | 500050 | BSALES 4 138.00 | 500820 | TECHE 4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T2975016WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 97.8 | 97.8141 | 97.6 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T3255016WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.4 | 96.39 | 96.3 | [7 empty] | CATEGORYB | SINGLE | BOGALUSA 500/230KV TRANSFORMER CKT 1 | 0 | 336130 | 8BOGALUS 500.00 | 336131 | 6ADMSCRK 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3265516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 97.4 | 97.4377 | 97.5 | [7 empty] | CATEGORYB | SINGLE | COLY - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WGLEN 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3325516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 97.7 | 97.738 | 98.1 | [7 empty] | CATEGORYB | SINGLE | WATERFORD - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WGLEN 500.00 | 336150 | 8WATERFO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T335016WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96 | 95.9811 | 95.9 | [7 empty] | CATEGORYB | SINGLE | COCODRIE - VILLE PLATTE 230KV CKT 1 | 0 | 500190 | COCODR 6 230.00 | 500880 | VILPLT 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T3375016WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.6 | 96.6053 | 96.5 | [7 empty] | CATEGORYB | SINGLE | BOGALUSA - FRANKLIN 500KV CKT 1 | 0 | 336130 | 8BOGALUS 500.00 | 336562 | 8FRKLIN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3435516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 97.3 | 97.2915 | 97.2 | [7 empty] | CATEGORYB | SINGLE | JAGUAR - POINT ESSO TAP 230KV CKT 1 | 0 | 335641 | 6TP.ESSO 230.00 | 335770 | 6JAGUAR 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T3445016WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.2 | 96.2202 | 96.2 | [7 empty] | CATEGORYB | SINGLE | WATERFORD 500/230KV TRANSFORMER CKT 1 | 0 | 336150 | 8WATERFO 500.00 | 336154 | 6WATFRD 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T345016WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95.7 | 95.7046 | 95.6 | [7 empty] | CATEGORYB | SINGLE | COUGHLIN - PLAISANCE 138KV CKT 1 | 0 | 500230 | COUGH 4 138.00 | 500720 | PLAISAN4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T3615016WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95.7 | 95.665 | 95.6 | [7 empty] | CATEGORYB | SINGLE | ELDORADO EHV - MOUNT OLIVE 500KV CKT 1 | 0 | 337368 | 8MTOLIV 500.00 | 337561 | 8ELDEHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T3645016WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.2 | 96.2002 | 96 | [7 empty] | CATEGORYB | SINGLE | ELDORADO EHV - STERLINGTON 500KV CKT 1 | 0 | 337420 | 8STERL 500.00 | 337561 | 8ELDEHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3645516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 97 | 96.997 | 97.1 | [7 empty] | CATEGORYB | SINGLE | ENJAY - JAGUAR 230KV CKT 1 | 0 | 335770 | 6JAGUAR 230.00 | 335772 | 6ENJAY 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3735516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 97.2 | 97.1656 | 97.2 | [7 empty] | CATEGORYB | SINGLE | ENJAY - FANCY POINT 230KV CKT 1 | 0 | 335772 | 6ENJAY 230.00 | 335825 | 6FANCY 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T395016WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95.8 | 95.8432 | 95.8 | [7 empty] | CATEGORYB | SINGLE | VILLE PLATTE - WESTFORK 230KV CKT 1 | 0 | 500880 | VILPLT 6 230.00 | 500920 | WSTFORK6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T395516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.5 | 96.488 | 96.5 | [7 empty] | CATEGORYB | SINGLE | BARKERS 6 230.00 - RAMSAY 230KV CKT 1 | 0 | 500025 | BARKERS 6 230.00 | 500750 | RAMSAY 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3995516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 98.9 | 98.8571 | 98.9 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T415016WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95.7 | 95.7156 | 95.7 | [7 empty] | CATEGORYB | SINGLE | WELLS - WESTFORK 230KV CKT 1 | 0 | 500920 | WSTFORK6 230.00 | 500940 | WELLS 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T415516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.2 | 96.2339 | 96.3 | [7 empty] | CATEGORYB | SINGLE | BAYOU SALE - TECHE 138KV CKT 1 | 0 | 500050 | BSALES 4 138.00 | 500820 | TECHE 4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T435516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.1 | 96.1324 | 96.2 | [7 empty] | CATEGORYB | SINGLE | BAYOU SALE - WAXLAKE 138KV CKT 1 | 0 | 500050 | BSALES 4 138.00 | 500890 | WAXLAKE4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4355516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 97.2 | 97.2416 | 97.3 | [7 empty] | CATEGORYB | SINGLE | BOGALUSA 500/230KV TRANSFORMER CKT 1 | 0 | 336130 | 8BOGALUS 500.00 | 336131 | 6ADMSCRK 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4505516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 97.5 | 97.5299 | 97.5 | [7 empty] | CATEGORYB | SINGLE | BOGALUSA - FRANKLIN 500KV CKT 1 | 0 | 336130 | 8BOGALUS 500.00 | 336562 | 8FRKLIN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4595516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 97.1 | 97.094 | 97.2 | [7 empty] | CATEGORYB | SINGLE | WATERFORD 500/230KV TRANSFORMER CKT 1 | 0 | 336150 | 8WATERFO 500.00 | 336154 | 6WATFRD 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4735516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.3 | 96.264 | 96.3 | [7 empty] | CATEGORYB | SINGLE | FRANKLIN - GRAND GULF 500KV CKT 1 | 0 | 336562 | 8FRKLIN 500.00 | 336820 | 8G.GULF 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T485516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.5 | 96.5156 | 96.6 | [7 empty] | CATEGORYB | SINGLE | COCODRIE - VILLE PLATTE 230KV CKT 1 | 0 | 500190 | COCODR 6 230.00 | 500880 | VILPLT 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4855516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.6 | 96.6195 | 96.7 | [7 empty] | CATEGORYB | SINGLE | ELDORADO EHV - MOUNT OLIVE 500KV CKT 1 | 0 | 337368 | 8MTOLIV 500.00 | 337561 | 8ELDEHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4915516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.3 | 96.3115 | 96.2 | [7 empty] | CATEGORYB | SINGLE | ELDORADO EHV - STERLINGTON 500KV CKT 1 | 0 | 337420 | 8STERL 500.00 | 337561 | 8ELDEHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T525516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.3 | 96.2902 | 96.4 | [7 empty] | CATEGORYB | SINGLE | COUGHLIN - PLAISANCE 138KV CKT 1 | 0 | 500230 | COUGH 4 138.00 | 500720 | PLAISAN4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T5845516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.7 | 96.701 | 96.7 | [7 empty] | CATEGORYB | SINGLE | BARKERS 6 230.00 - BOGALUSA 230KV CKT 1 | 0 | 500025 | BARKERS 6 230.00 | 336136 | 6BOGALUS 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T595516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95 | 95.0055 | 95 | [7 empty] | CATEGORYB | SINGLE | MARKSVILLE - YELLOW BAYOU 138KV CKT 1 | 0 | 500560 | MARKSVL4 138.00 | 500960 | YBAYOU 4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T625516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.4 | 96.3761 | 96.5 | [7 empty] | CATEGORYB | SINGLE | VILLE PLATTE - WESTFORK 230KV CKT 1 | 0 | 500880 | VILPLT 6 230.00 | 500920 | WSTFORK6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T645516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.2 | 96.2328 | 96.3 | [7 empty] | CATEGORYB | SINGLE | WELLS - WESTFORK 230KV CKT 1 | 0 | 500920 | WSTFORK6 230.00 | 500940 | WELLS 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T9965016WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95.7 | 95.739 | 95.6 | [7 empty] | CATEGORYB | NONSINGLE | CELE-WELLOP2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FNSL | FDNS-Blown up | FNSL | FDNS-Blown up | 5 | 0 | 2011AGP1AFS92T115016WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.3 | 96.3043 | 96.2 | [7 empty] | CATEGORYB | GENOUT | GEN335831 1-RIVERBEND UNIT#1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FNSL | FDNS-Blown up | FNSL | FDNS-Blown up | 5 | 0 | 2011AGP1AFS92T215016WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.2 | 96.2184 | 96.2 | [7 empty] | CATEGORYB | GENOUT | GEN336251 1-NINEMILE POINT UNIT#4 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FNSL | FDNS-Blown up | 5 | 5 | 2011AGP1AFS92T245516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 97.1 | 97.0991 | 97.2 | [7 empty] | CATEGORYB | GENOUT | GEN303008 1-1BC2 U3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FNSL | FDNS-Blown up | FNSL | FDNS-Blown up | 5 | 0 | 2011AGP1AFS92T315016WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.3 | 96.2651 | 96.2 | [7 empty] | CATEGORYB | GENOUT | GEN336252 1-NINEMILE POINT UNIT#5 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FNSL | FDNS-Blown up | FNSL | FDNS-Blown up | 5 | 5 | 2011AGP1AFS92T325516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 97.2 | 97.1642 | 97.2 | [7 empty] | CATEGORYB | GENOUT | GEN335831 1-RIVERBEND UNIT#1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FDNS |  | FNSL | FDNS-Blown up | 5 | 5 | 2011AGP1AFS92T95516WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 97 | 97.0157 | 97.2 | [7 empty] | CATEGORYB | GENOUT | GEN303006 1-1BC2 U1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T11055516WP | TO->FROM | BARKERS 6 230.00 - BOGALUSA 230KV CKT 1 | E | EES | CLEC |  | CLE_EAST | 0 | 336136 | 6BOGALUS 230.00 | 500025 | BARKERS 6 230.00 | 0 |  | 1 | 17WP | 431 | 454 | 0 | 96.5 | 96.5379 | 97.4 | [7 empty] | CATEGORYB | GENOUT | GEN336153 1-WATERFORD UNIT#3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T5925516WP | TO->FROM | BARKERS 6 230.00 - BOGALUSA 230KV CKT 1 | E | EES | CLEC |  | CLE_EAST | 0 | 336136 | 6BOGALUS 230.00 | 500025 | BARKERS 6 230.00 | 0 |  | 1 | 17WP | 431 | 454 | 0 | 97.5 | 97.5406 | 98.8 | [7 empty] | CATEGORYB | SINGLE | 6TALISK - NORTH SLIDELL 230KV CKT 1 | 0 | 500640 | NSLID 6 230.00 | 303221 | 6TALISK 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T10225516WP | TO->FROM | BOGALUSA - FRANKLIN 500KV CKT 1 | E | EES | EES | AEC | AMSNSH | 0 | 336562 | 8FRKLIN 500.00 | 336130 | 8BOGALUS 500.00 | 0 |  | 1 | 17WP | 1200 | 1200 | 0 |  | 93.3725 | 95.6 | [7 empty] | CATEGORYB | NONSINGLE | CELE-WELLOP1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4025516WP | TO->FROM | BOGALUSA - FRANKLIN 500KV CKT 1 | E | EES | EES | AEC | AMSNSH | 0 | 336562 | 8FRKLIN 500.00 | 336130 | 8BOGALUS 500.00 | 0 |  | 1 | 17WP | 1200 | 1200 | 0 |  | 93.8547 | 95.9 | [7 empty] | CATEGORYB | SINGLE | FRANKLIN - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 336562 | 8FRKLIN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T4395016WP | TO->FROM | CALICO ROCK - MELBOURNE 161KV CKT 1 | E | EES | EES | EAINTH |  | 0 | 338131 | 5MELBRN 161.00 | 338130 | 5CALCR 161.00 | 0 |  | 1 | 17WP | 148 | 148 | 0 | 104.1 | 104.1406 | 99.8 | [7 empty] | CATEGORYB | SINGLE | BEE BRANCH (AECC) - CLINTON 161KV CKT 1 | 0 | 338831 | 5BEE BR# 161.00 | 338833 | 5CLIN-IN# 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | CONT-Hayti-Blytheville 161kV Line Overload | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T9055016WP | TO->FROM | CALICO ROCK - MELBOURNE 161KV CKT 1 | E | EES | EES | EAINTH |  | 0 | 338131 | 5MELBRN 161.00 | 338130 | 5CALCR 161.00 | 0 |  | 1 | 17WP | 148 | 148 | 0 | 102.5 | 102.5434 | 99.1 | [7 empty] | CATEGORYB | SINGLE | DELL 500 - NEW MADRID 500KV CKT 1 | 0 | 338187 | 8DELL 500.00 | 300035 | 8NEWMAD 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T6355016WP | FROM->TO | CALICO ROCK - NORFORK 161KV CKT 1 | E | EES | SWPA |  | EMINTH | 0 | 338130 | 5CALCR 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 17WP | 148 | 148 | 0 | 103.4 | 103.3961 | 97.9 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 50 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T10365516WP | TO->FROM | CLAY - SPRINGFIELD 161KV CKT 1 | E | SWPA | SPRM | EMINTH | SPRM > 69KV | 0 | 505492 | SPRGFLD5 161.00 | 549970 | CLAY 5161.00 | 0 |  | 1 | 17WP | 167 | 167 | 0 |  | 90.291 | 98.4 | [7 empty] | CATEGORYB | NONSINGLE | AI03 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1355516WP | TO->FROM | GRAND ISLAND - SWEETWATER 345KV CKT 1 | E | NPPD | NPPD | NPPD_686 | WAPA_1606 | 0 | 640374 | SWEET W3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 | 17WP | 717 | 717 | 789 |  | 90.623 | 96.1 | [7 empty] | CATEGORYB | SINGLE | AXTELL - SWEETWATER 345KV CKT 1 | 0 | 640065 | AXTELL 3 345.00 | 640374 | SWEET W3 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SPP_FG-EES-IDC-15974 |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2065516WP | FROM->TO | GRIMES - MT. ZION 138KV CKT 1 | E | EES | EES | GSTNAV | GSTHNT | 0 | 334026 | 4GRIMES 138.00 | 334060 | 4MT.ZION 138.00 | 0 |  | 1 | 17WP | 206 | 206 | 0 |  | 87.585 | 96.2 | [7 empty] | CATEGORYB | SINGLE | GRIMES - MAGNOLIA ANDERSON 138KV CKT 1 | 0 | 334025 | 4MAG AND 138.00 | 334026 | 4GRIMES 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2185516WP | FROM->TO | GRIMES - MT. ZION 138KV CKT 1 | E | EES | EES | GSTNAV | GSTHNT | 0 | 334026 | 4GRIMES 138.00 | 334060 | 4MT.ZION 138.00 | 0 |  | 1 | 17WP | 206 | 206 | 0 |  | 88.2137 | 98.5 | [7 empty] | CATEGORYB | SINGLE | LAKE FOREST - WOODHAVEN 138KV CKT 1 | 0 | 334042 | 4LFOREST 138.00 | 334105 | 4WDHAVN 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2645516WP | FROM->TO | GRIMES - MT. ZION 138KV CKT 1 | E | EES | EES | GSTNAV | GSTHNT | 0 | 334026 | 4GRIMES 138.00 | 334060 | 4MT.ZION 138.00 | 0 |  | 1 | 17WP | 206 | 206 | 0 |  | 91.0137 | 99.8 | [7 empty] | CATEGORYB | SINGLE | HARTBURG - MOUNT OLIVE 500KV CKT 1 | 0 | 334325 | 8HARTBRG 500.00 | 337368 | 8MTOLIV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3245516WP | FROM->TO | JAGUAR - POINT ESSO TAP 230KV CKT 1 | E | EES | EES | GSLBTR | GSLBTR | 0 | 335770 | 6JAGUAR 230.00 | 335641 | 6TP.ESSO 230.00 | 0 |  | 1 | 17WP | 685 | 685 | 0 | 97.7 | 97.7492 | 98.2 | [7 empty] | CATEGORYB | SINGLE | COLY - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WGLEN 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T10825016WP | FROM->TO | KN WRITESVILLE (KNWRIVL1) 500/13.8/13.8KV TRANSFORMER CKT 1 | E | EES | EES | EAILTR | EAILTR-A | 2 | 338507 | 1C1KNWRI 13.800 | 337860 | 8KNWRIVL 500.00 | 338508 | 1C3KNWRI 13.800 | 1 | 17WP | 235 | 235 | 0 | 95.8 | 95.8208 | 95.7 | [7 empty] | CATEGORYB | GENOUT | GEN338510 1-1S1KNWRI | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T10835016WP | FROM->TO | KN WRITESVILLE (KNWRIVL1) 500/13.8/13.8KV TRANSFORMER CKT 1 | E | EES | EES | EAILTR | EAILTR-A | 2 | 338507 | 1C1KNWRI 13.800 | 337860 | 8KNWRIVL 500.00 | 338508 | 1C3KNWRI 13.800 | 1 | 17WP | 235 | 235 | 0 | 95.6 | 95.6498 | 95.5 | [7 empty] | CATEGORYB | GENOUT | GEN338511 1-1C7KNWRI | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T3675016WP | FROM->TO | KN WRITESVILLE (KNWRIVL1) 500/13.8/13.8KV TRANSFORMER CKT 1 | E | EES | EES | EAILTR | EAILTR-A | 2 | 338507 | 1C1KNWRI 13.800 | 337860 | 8KNWRIVL 500.00 | 338508 | 1C3KNWRI 13.800 | 1 | 17WP | 235 | 235 | 0 | 99.2 | 99.1759 | 98.4 | [7 empty] | CATEGORYB | SINGLE | KEO EHV - WHITE BLUFF 500KV CKT 1 | 0 | 337651 | 8WH BLF 500.00 | 337957 | 8KEO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T10795016WP | FROM->TO | KN WRITESVILLE (KNWRIVL2) 500/13.8/13.8KV TRANSFORMER CKT 1 | E | EES | EES | EAILTR | EAILTR-A | 2 | 338509 | 1C5KNWRI 13.800 | 337860 | 8KNWRIVL 500.00 | 338510 | 1S1KNWRI 13.800 | 1 | 17WP | 235 | 235 | 0 | 99.6 | 99.6809 | 99.2 | [7 empty] | CATEGORYB | GENOUT | GEN338146 1-INDEPENDENCE UNIT #2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T10845016WP | FROM->TO | KN WRITESVILLE (KNWRIVL2) 500/13.8/13.8KV TRANSFORMER CKT 1 | E | EES | EES | EAILTR | EAILTR-A | 2 | 338509 | 1C5KNWRI 13.800 | 337860 | 8KNWRIVL 500.00 | 338510 | 1S1KNWRI 13.800 | 1 | 17WP | 235 | 235 | 0 | 99.4 | 99.4474 | 99.3 | [7 empty] | CATEGORYB | GENOUT | GEN338511 1-1C7KNWRI | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T10855016WP | FROM->TO | KN WRITESVILLE (KNWRIVL2) 500/13.8/13.8KV TRANSFORMER CKT 1 | E | EES | EES | EAILTR | EAILTR-A | 2 | 338509 | 1C5KNWRI 13.800 | 337860 | 8KNWRIVL 500.00 | 338510 | 1S1KNWRI 13.800 | 1 | 17WP | 235 | 235 | 0 | 98 | 98.017 | 97.9 | [7 empty] | CATEGORYB | GENOUT | GEN338512 1-1S2KNWRI | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T185016WP | FROM->TO | KN WRITESVILLE (KNWRIVL2) 500/13.8/13.8KV TRANSFORMER CKT 1 | E | EES | EES | EAILTR | EAILTR-A | 2 | 338509 | 1C5KNWRI 13.800 | 337860 | 8KNWRIVL 500.00 | 338510 | 1S1KNWRI 13.800 | 1 | 17WP | 235 | 235 | 0 | 95.6 | 95.5579 | 95.4 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2155516WP | TO->FROM | LINE 558 TAP - MT. ZION 138KV CKT 1 | E | EES | EES | GSTHNT | GSTHNT | 0 | 334060 | 4MT.ZION 138.00 | 334058 | 4L558T485 138.00 | 0 |  | 1 | 17WP | 206 | 206 | 0 |  | 88.8421 | 99.2 | [7 empty] | CATEGORYB | SINGLE | 4BENTWATER 138.00 - WALDEN 138KV CKT 1 | 0 | 334039 | 4BENTWATER 138.00 | 334040 | 4WALDEN 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  |  |  | FNSL | FDNS-Blown up | 5 | 0 | 2011AGP1AFS92T75016WP | FROM->TO | MONETTE JUNCTION - PARAGOULD 161 161KV CKT 1 | E | EES | EES | EAINTH | EAINTH | 0 | 338186 | 5MONETE 161.00 | 338204 | 5PARAG 161.00 | 0 |  | 1 | 17WP | 148 | 148 | 0 |  | 92.6348 | 98.3 | [7 empty] | CATEGORYB | SINGLE | 8SHELBY TN 500.00 - PLUM POINT 500KV CKT 1 | 0 | 338188 | 8SANSOUC 500.00 | 360021 | 8SHELBY TN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T375516WP | FROM->TO | SPSNORTH_STX | E |  |  |  |  | SPSNORTH_STX | 0 |  | 0 |  | 0 |  |  | 17WP | 800 | 800 | 800 | 97.1 | 97.2745 | 97.7 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SWINGBUS | FNSL | FDNS-Iteration limit exceeded | FNSL | FDNS-Iteration limit exceeded | 5 | 5 | 2011AGP1AFS92T15516WP | FROM->TO | SUB 167 - RIVERTON 69/13.2KV TRANSFORMER CKT 1 | E | EMDE | EMDE | BAXTER | BAXTER | 0 | 547645 | R8G167 1 13.200 | 547541 | RIV167 2 69.000 | 0 |  | 1 | 17WP | 52 | 52 | 0 | 96.9 | 96.912 | 97.2 | [7 empty] | CATEGORYB | SINGLE | SUB 368 - DADEVILLE EAST - SUB 431 - BOLIVAR SOUTH 161KV CKT 1 | 0 | 547478 | DAD368 5 161.00 | 547493 | BOL431 5 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 | SPP_FG-EES-IDC-15730 | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3055516WP | FROM->TO | WILLOW GLEN 500/138KV TRANSFORMER CKT 1 | E | EES | EES | GSLBTR | GSLBTR | 0 | 335618 | 8WGLEN 500.00 | 335601 | 4WGLEN-2 138.00 | 0 |  | 1 | 17WP | 560 | 560 | 0 | 99 | 99.0151 | 99.9 | [7 empty] | CATEGORYB | SINGLE | WILLOW GLEN 500/230KV TRANSFORMER CKT 1 | 0 | 335568 | 6WGLEN 230.00 | 335618 | 8WGLEN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3035516WP | FROM->TO | WILLOW GLEN 500/230KV TRANSFORMER CKT 1 | E | EES | EES | GSLBTR | GSLBTR | 0 | 335618 | 8WGLEN 500.00 | 335568 | 6WGLEN 230.00 | 0 |  | 1 | 17WP | 672 | 672 | 0 | 98.5 | 98.4863 | 99.2 | [7 empty] | CATEGORYB | SINGLE | WILLOW GLEN 230/138KV TRANSFORMER CKT 1 | 0 | 335568 | 6WGLEN 230.00 | 335601 | 4WGLEN-2 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9-16 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3835516WP | FROM->TO | WILLOW GLEN 500/230KV TRANSFORMER CKT 1 | E | EES | EES | GSLBTR | GSLBTR | 0 | 335618 | 8WGLEN 500.00 | 335568 | 6WGLEN 230.00 | 0 |  | 1 | 17WP | 672 | 672 | 0 | 98.7 | 98.6801 | 99.4 | [7 empty] | CATEGORYB | SINGLE | FANCY POINT - WATERLOO 230KV CKT 1 | 0 | 335825 | 6FANCY 230.00 | 335827 | 6WATLOO 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2515517WP | TO->FROM | 4BENTWATER 138.00 - GRIMES 138KV CKT 1 | E | EES | EES | GSTNAV | GSTNAV | 0 | 334026 | 4GRIMES 138.00 | 334039 | 4BENTWATER 138.00 | 0 |  | 1 | 17WP | 206 | 206 | 0 |  | 85.8805 | 97.4 | [7 empty] | CATEGORYB | SINGLE | LINE 558 TAP - MT. ZION 138KV CKT 1 | 0 | 334058 | 4L558T485 138.00 | 334060 | 4MT.ZION 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | INVALID | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T895017WP | FROM->TO | 59TH ST - GILL ENERGY CENTER SOUTH 138KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533029 | 59TH ST4 138.00 | 533046 | GILL S 4 138.00 | 0 |  | 1 | 17WP | 191 | 210 | 0 | 103.5 | 103.4548 | 99.4615 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER NORTH - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533040 | EVANS N4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T5895517WP | TO->FROM | 5ELDON - BARNETT 161KV CKT 1 | E | AECI | AMMO | CENTRAL | AMRNMO | 0 | 300057 | 5BARNET 161.00 | 344532 | 5ELDON 161.00 | 0 |  | 1 | 17WP | 167 | 167 | 167 |  | 84.24 | 99.6 | [7 empty] | CATEGORYB | SINGLE | 7MCCREDIE 345.00 - 7MONTGMRY 345.00 345KV CKT 1 | 0 | 345088 | 7MCCREDIE 345.00 | 345230 | 7MONTGMRY 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T1115017WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.4 | 96.4404 | 96.3 | [7 empty] | CATEGORYB | SINGLE | 8CAJUN2 - WEBRE 500KV CKT 1 | 0 | 303005 | 8CAJUN2 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T11375517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.2 | 96.2358 | 96.2 | [7 empty] | CATEGORYB | NONSINGLE | CELE-WELLOP2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T11875517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 96.0509 | 96.1 | [7 empty] | CATEGORYB | NONSINGLE | SERCW-21 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T12005517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 97 | 97.0098 | 97.1 | [7 empty] | CATEGORYB | GENOUT | GEN303006 1-1BC2 U1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T12155517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 97.1 | 97.093 | 97.2 | [7 empty] | CATEGORYB | GENOUT | GEN303008 1-1BC2 U3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T125017WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95.2 | 95.1509 | 95 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FNSL | FDNS-Blown up | FDNS |  | 5 | 5 | 2011AGP1AFS91T12605517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 97.2 | -999 | 97.2 | [7 empty] | CATEGORYB | GENOUT | GEN335831 1-RIVERBEND UNIT#1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T12845517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 96.108 | 96.1 | [7 empty] | CATEGORYB | GENOUT | GEN336170 1-GULF OXY U4 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T12935517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.8 | 96.7881 | 96.8 | [7 empty] | CATEGORYB | GENOUT | GEN336251 1-NINEMILE POINT UNIT#4 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T13045517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.8 | 96.8027 | 96.8 | [7 empty] | CATEGORYB | GENOUT | GEN336252 1-NINEMILE POINT UNIT#5 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1845517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 97 | 96.9997 | 97 | [7 empty] | CATEGORYB | SINGLE | 8CAJUN2 - WEBRE 500KV CKT 1 | 0 | 303005 | 8CAJUN2 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1875517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95 | 95.0042 | 95 | [7 empty] | CATEGORYB | SINGLE | 8CAJUN2 - FANCY POINT 500KV CKT 1 | 0 | 303005 | 8CAJUN2 500.00 | 335835 | 8FANCY 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T1945017WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.3 | 96.2828 | 96 | [7 empty] | CATEGORYB | SINGLE | WEBRE - WELLS 500KV CKT 1 | 0 | 335368 | 8WELLS 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2175517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 |  | 95.1752 | 95.1 | [7 empty] | CATEGORYB | SINGLE | 6FRNSTL - SORRENTO 230KV CKT 1 | 0 | 303204 | 6FRNSTL 230.00 | 336060 | 6SORR 2 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T2245017WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.7 | 96.7184 | 96.5 | [7 empty] | CATEGORYB | SINGLE | COLY - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WGLEN 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T2295017WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.8 | 96.7675 | 96.7 | [7 empty] | CATEGORYB | SINGLE | WATERFORD - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WGLEN 500.00 | 336150 | 8WATERFO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T235517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95.6 | 95.6281 | 95.6 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T2415017WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.7 | 96.673 | 96.5 | [7 empty] | CATEGORYB | SINGLE | JAGUAR - POINT ESSO TAP 230KV CKT 1 | 0 | 335641 | 6TP.ESSO 230.00 | 335770 | 6JAGUAR 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T2555017WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.4 | 96.3844 | 96.3 | [7 empty] | CATEGORYB | SINGLE | ENJAY - JAGUAR 230KV CKT 1 | 0 | 335770 | 6JAGUAR 230.00 | 335772 | 6ENJAY 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T2635017WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.5 | 96.4819 | 96.4 | [7 empty] | CATEGORYB | SINGLE | ENJAY - FANCY POINT 230KV CKT 1 | 0 | 335772 | 6ENJAY 230.00 | 335825 | 6FANCY 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T265017WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95.9 | 95.856 | 95.7 | [7 empty] | CATEGORYB | SINGLE | BARKERS 6 230.00 - RAMSAY 230KV CKT 1 | 0 | 500025 | BARKERS 6 230.00 | 500750 | RAMSAY 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T285017WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95.7 | 95.6916 | 95.6 | [7 empty] | CATEGORYB | SINGLE | BAYOU SALE - TECHE 138KV CKT 1 | 0 | 500050 | BSALES 4 138.00 | 500820 | TECHE 4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T2875017WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 97.8 | 97.8122 | 97.5 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3045517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.4 | 96.4401 | 96.5 | [7 empty] | CATEGORYB | SINGLE | HARTBURG - MOUNT OLIVE 500KV CKT 1 | 0 | 334325 | 8HARTBRG 500.00 | 337368 | 8MTOLIV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3105517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.2 | 96.1705 | 96.4 | [7 empty] | CATEGORYB | SINGLE | NELSON - RICHARD 500KV CKT 1 | 0 | 335192 | 8NELSON 500.00 | 335367 | 8RICHARD 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T3155017WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.4 | 96.3894 | 96.3 | [7 empty] | CATEGORYB | SINGLE | BOGALUSA 500/230KV TRANSFORMER CKT 1 | 0 | 336130 | 8BOGALUS 500.00 | 336131 | 6ADMSCRK 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3165517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.7 | 96.6856 | 96.5 | [7 empty] | CATEGORYB | SINGLE | WEBRE - WELLS 500KV CKT 1 | 0 | 335368 | 8WELLS 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T3265017WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.6 | 96.6046 | 96.5 | [7 empty] | CATEGORYB | SINGLE | BOGALUSA - FRANKLIN 500KV CKT 1 | 0 | 336130 | 8BOGALUS 500.00 | 336562 | 8FRKLIN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T3335017WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.2 | 96.2195 | 96.1 | [7 empty] | CATEGORYB | SINGLE | WATERFORD 500/230KV TRANSFORMER CKT 1 | 0 | 336150 | 8WATERFO 500.00 | 336154 | 6WATFRD 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T335017WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96 | 95.9804 | 95.9 | [7 empty] | CATEGORYB | SINGLE | COCODRIE - VILLE PLATTE 230KV CKT 1 | 0 | 500190 | COCODR 6 230.00 | 500880 | VILPLT 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T3495017WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95.7 | 95.6643 | 95.5 | [7 empty] | CATEGORYB | SINGLE | ELDORADO EHV - MOUNT OLIVE 500KV CKT 1 | 0 | 337368 | 8MTOLIV 500.00 | 337561 | 8ELDEHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T3525017WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.2 | 96.1976 | 95.8 | [7 empty] | CATEGORYB | SINGLE | ELDORADO EHV - STERLINGTON 500KV CKT 1 | 0 | 337420 | 8STERL 500.00 | 337561 | 8ELDEHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T355017WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95.7 | 95.704 | 95.6 | [7 empty] | CATEGORYB | SINGLE | COUGHLIN - PLAISANCE 138KV CKT 1 | 0 | 500230 | COUGH 4 138.00 | 500720 | PLAISAN4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3655517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 97.4 | 97.4362 | 97.4 | [7 empty] | CATEGORYB | SINGLE | COLY - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WGLEN 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3715517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 97.7 | 97.7368 | 98 | [7 empty] | CATEGORYB | SINGLE | WATERFORD - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WGLEN 500.00 | 336150 | 8WATERFO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3825517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 97.3 | 97.2904 | 97.2 | [7 empty] | CATEGORYB | SINGLE | JAGUAR - POINT ESSO TAP 230KV CKT 1 | 0 | 335641 | 6TP.ESSO 230.00 | 335770 | 6JAGUAR 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4035517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 97 | 96.9959 | 97 | [7 empty] | CATEGORYB | SINGLE | ENJAY - JAGUAR 230KV CKT 1 | 0 | 335770 | 6JAGUAR 230.00 | 335772 | 6ENJAY 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T405517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.5 | 96.4868 | 96.5 | [7 empty] | CATEGORYB | SINGLE | BARKERS 6 230.00 - RAMSAY 230KV CKT 1 | 0 | 500025 | BARKERS 6 230.00 | 500750 | RAMSAY 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4125517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 97.2 | 97.1644 | 97.2 | [7 empty] | CATEGORYB | SINGLE | ENJAY - FANCY POINT 230KV CKT 1 | 0 | 335772 | 6ENJAY 230.00 | 335825 | 6FANCY 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T425017WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95.8 | 95.8426 | 95.8 | [7 empty] | CATEGORYB | SINGLE | VILLE PLATTE - WESTFORK 230KV CKT 1 | 0 | 500880 | VILPLT 6 230.00 | 500920 | WSTFORK6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T425517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.2 | 96.2331 | 96.3 | [7 empty] | CATEGORYB | SINGLE | BAYOU SALE - TECHE 138KV CKT 1 | 0 | 500050 | BSALES 4 138.00 | 500820 | TECHE 4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4375517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 98.9 | 98.8544 | 98.8 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T445017WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95.7 | 95.7149 | 95.7 | [7 empty] | CATEGORYB | SINGLE | WELLS - WESTFORK 230KV CKT 1 | 0 | 500920 | WSTFORK6 230.00 | 500940 | WELLS 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T445517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.1 | 96.1317 | 96.2 | [7 empty] | CATEGORYB | SINGLE | BAYOU SALE - WAXLAKE 138KV CKT 1 | 0 | 500050 | BSALES 4 138.00 | 500890 | WAXLAKE4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4735517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 97.2 | 97.2408 | 97.3 | [7 empty] | CATEGORYB | SINGLE | BOGALUSA 500/230KV TRANSFORMER CKT 1 | 0 | 336130 | 8BOGALUS 500.00 | 336131 | 6ADMSCRK 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4885517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 97.5 | 97.5291 | 97.4 | [7 empty] | CATEGORYB | SINGLE | BOGALUSA - FRANKLIN 500KV CKT 1 | 0 | 336130 | 8BOGALUS 500.00 | 336562 | 8FRKLIN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T495517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.5 | 96.5161 | 96.6 | [7 empty] | CATEGORYB | SINGLE | COCODRIE - VILLE PLATTE 230KV CKT 1 | 0 | 500190 | COCODR 6 230.00 | 500880 | VILPLT 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4975517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 97.1 | 97.0929 | 97.2 | [7 empty] | CATEGORYB | SINGLE | WATERFORD 500/230KV TRANSFORMER CKT 1 | 0 | 336150 | 8WATERFO 500.00 | 336154 | 6WATFRD 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T5115517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.3 | 96.2628 | 96.3 | [7 empty] | CATEGORYB | SINGLE | FRANKLIN - GRAND GULF 500KV CKT 1 | 0 | 336562 | 8FRKLIN 500.00 | 336820 | 8G.GULF 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T5235517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.6 | 96.6184 | 96.7 | [7 empty] | CATEGORYB | SINGLE | ELDORADO EHV - MOUNT OLIVE 500KV CKT 1 | 0 | 337368 | 8MTOLIV 500.00 | 337561 | 8ELDEHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T535517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.3 | 96.2894 | 96.3 | [7 empty] | CATEGORYB | SINGLE | COUGHLIN - PLAISANCE 138KV CKT 1 | 0 | 500230 | COUGH 4 138.00 | 500720 | PLAISAN4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T605517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95 | 95.0047 | 95 | [7 empty] | CATEGORYB | SINGLE | MARKSVILLE - YELLOW BAYOU 138KV CKT 1 | 0 | 500560 | MARKSVL4 138.00 | 500960 | YBAYOU 4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T635517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.4 | 96.3754 | 96.5 | [7 empty] | CATEGORYB | SINGLE | VILLE PLATTE - WESTFORK 230KV CKT 1 | 0 | 500880 | VILPLT 6 230.00 | 500920 | WSTFORK6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T655517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.2 | 96.2319 | 96.3 | [7 empty] | CATEGORYB | SINGLE | WELLS - WESTFORK 230KV CKT 1 | 0 | 500920 | WSTFORK6 230.00 | 500940 | WELLS 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T6735517WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.7 | 96.6999 | 96.7 | [7 empty] | CATEGORYB | SINGLE | BARKERS 6 230.00 - BOGALUSA 230KV CKT 1 | 0 | 500025 | BARKERS 6 230.00 | 336136 | 6BOGALUS 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T8815017WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 95.7 | 95.738 | 95.5 | [7 empty] | CATEGORYB | NONSINGLE | CELE-WELLOP2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T9015017WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96 | 95.9799 | 95.8 | [7 empty] | CATEGORYB | GENOUT | GEN303006 1-1BC2 U1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T9085017WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96 | 96.0375 | 95.9 | [7 empty] | CATEGORYB | GENOUT | GEN303008 1-1BC2 U3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T9375017WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 98.6 | 98.6271 | 98.6 | [7 empty] | CATEGORYB | GENOUT | GEN336153 1-WATERFORD UNIT#3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FNSL | FDNS-Blown up | FNSL | FDNS-Blown up | 5 | 0 | 2011AGP1AFS92T195017WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.2 | 96.2212 | 96.1 | [7 empty] | CATEGORYB | GENOUT | GEN336251 1-NINEMILE POINT UNIT#4 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FNSL | FDNS-Blown up | FNSL | FDNS-Blown up | 5 | 0 | 2011AGP1AFS92T295017WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.3 | 96.2678 | 96.1 | [7 empty] | CATEGORYB | GENOUT | GEN336252 1-NINEMILE POINT UNIT#5 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FNSL | FDNS-Blown up | 5 | 0 | 2011AGP1AFS92T95017WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 17WP | 615 | 615 | 0 | 96.3 | 96.307 | 96.2 | [7 empty] | CATEGORYB | GENOUT | GEN335831 1-RIVERBEND UNIT#1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T12715517WP | TO->FROM | BARKERS 6 230.00 - BOGALUSA 230KV CKT 1 | E | EES | CLEC |  | CLE_EAST | 0 | 336136 | 6BOGALUS 230.00 | 500025 | BARKERS 6 230.00 | 0 |  | 1 | 17WP | 431 | 454 | 0 | 96.5 | 96.4564 | 97 | [7 empty] | CATEGORYB | GENOUT | GEN336153 1-WATERFORD UNIT#3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T6815517WP | TO->FROM | BARKERS 6 230.00 - BOGALUSA 230KV CKT 1 | E | EES | CLEC |  | CLE_EAST | 0 | 336136 | 6BOGALUS 230.00 | 500025 | BARKERS 6 230.00 | 0 |  | 1 | 17WP | 431 | 454 | 0 | 97.5 | 97.5314 | 98.4 | [7 empty] | CATEGORYB | SINGLE | 6TALISK - NORTH SLIDELL 230KV CKT 1 | 0 | 500640 | NSLID 6 230.00 | 303221 | 6TALISK 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T11345517WP | TO->FROM | BOGALUSA - FRANKLIN 500KV CKT 1 | E | EES | EES | AEC | AMSNSH | 0 | 336562 | 8FRKLIN 500.00 | 336130 | 8BOGALUS 500.00 | 0 |  | 1 | 17WP | 1200 | 1200 | 0 |  | 93.3751 | 95.9 | [7 empty] | CATEGORYB | NONSINGLE | CELE-WELLOP1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4405517WP | TO->FROM | BOGALUSA - FRANKLIN 500KV CKT 1 | E | EES | EES | AEC | AMSNSH | 0 | 336562 | 8FRKLIN 500.00 | 336130 | 8BOGALUS 500.00 | 0 |  | 1 | 17WP | 1200 | 1200 | 0 |  | 93.8548 | 96.4 | [7 empty] | CATEGORYB | SINGLE | FRANKLIN - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 336562 | 8FRKLIN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T5505517WP | FROM->TO | BULL SHOALS - MIDWAY (YVEPA) 161KV CKT 1 | E | SWPA | EES | EMINTH |  | 0 | 505460 | BULL SH5 161.00 | 338813 | 5MIDWAY# 161.00 | 0 |  | 1 | 17WP | 162 | 162 | 0 |  | 86.6799 | 95.4 | [7 empty] | CATEGORYB | SINGLE | BATESVILLE - MOOREFIELD 161KV CKT 1 | 0 | 338137 | 5BATEVL 161.00 | 338138 | 5MORFLD 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SPP_FG-EES-IDC-AFC-40094-BSMID_INDMOR |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T5515517WP | FROM->TO | BULL SHOALS - MIDWAY (YVEPA) 161KV CKT 1 | E | SWPA | EES | EMINTH |  | 0 | 505460 | BULL SH5 161.00 | 338813 | 5MIDWAY# 161.00 | 0 |  | 1 | 17WP | 162 | 162 | 0 |  | 86.9556 | 95.9 | [7 empty] | CATEGORYB | SINGLE | INDEPENDENCE - MOOREFIELD 161KV CKT 1 | 0 | 338138 | 5MORFLD 161.00 | 338142 | 5ISES-1 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1625517WP | FROM->TO | CANADAY - ELM CREEK 115KV CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640103 | CANADAY7 115.00 | 640161 | ELMCRK_7 115.00 | 0 |  | 1 | 17WP | 80 | 80 | 88 |  | 78.6177 | 96.7 | [7 empty] | CATEGORYB | SINGLE | CROOKED CREEK - RIVERDALE 230KV CKT 1 | 0 | 640093 | C.CREEK4 230.00 | 640330 | RIVERDL4 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T6315517WP | TO->FROM | CLAY - SPRINGFIELD 161KV CKT 1 | E | SWPA | SPRM | EMINTH | SPRM > 69KV | 0 | 505492 | SPRGFLD5 161.00 | 549970 | CLAY 5161.00 | 0 |  | 1 | 17WP | 167 | 167 | 0 |  | 80.8454 | 98.1 | [7 empty] | CATEGORYB | SINGLE | HUBEN - MORGAN 345KV CKT 1 | 0 | 300042 | 7HUBEN 345.00 | 300045 | 7MORGAN 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1595517WP | TO->FROM | GRAND ISLAND - SWEETWATER 345KV CKT 1 | E | NPPD | NPPD | NPPD_686 | WAPA_1606 | 0 | 640374 | SWEET W3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 | 17WP | 717 | 717 | 789 |  | 80.2953 | 95.8 | [7 empty] | CATEGORYB | SINGLE | AXTELL - PAULINE 345KV CKT 1 | 0 | 640065 | AXTELL 3 345.00 | 640312 | PAULINE3 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SPP_FG-EES-IDC-15974 |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2345517WP | FROM->TO | GRIMES - MT. ZION 138KV CKT 1 | E | EES | EES | GSTNAV | GSTHNT | 0 | 334026 | 4GRIMES 138.00 | 334060 | 4MT.ZION 138.00 | 0 |  | 1 | 17WP | 206 | 206 | 0 |  | 87.6088 | 98.6 | [7 empty] | CATEGORYB | SINGLE | GRIMES - MAGNOLIA ANDERSON 138KV CKT 1 | 0 | 334025 | 4MAG AND 138.00 | 334026 | 4GRIMES 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2575517WP | FROM->TO | GRIMES - MT. ZION 138KV CKT 1 | E | EES | EES | GSTNAV | GSTHNT | 0 | 334026 | 4GRIMES 138.00 | 334060 | 4MT.ZION 138.00 | 0 |  | 1 | 17WP | 206 | 206 | 0 |  | 86.1585 | 99.4 | [7 empty] | CATEGORYB | SINGLE | CONROE BULK - WOODHAVEN 138KV CKT 1 | 0 | 334104 | 4CONROE1 138.00 | 334105 | 4WDHAVN 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T5215517WP | FROM->TO | GRIMES - MT. ZION 138KV CKT 1 | E | EES | EES | GSTNAV | GSTHNT | 0 | 334026 | 4GRIMES 138.00 | 334060 | 4MT.ZION 138.00 | 0 |  | 1 | 17WP | 206 | 206 | 0 |  | 88.939 | 99.6 | [7 empty] | CATEGORYB | SINGLE | ELDORADO EHV - MOUNT OLIVE 500KV CKT 1 | 0 | 337368 | 8MTOLIV 500.00 | 337561 | 8ELDEHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1255517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 |  | 75.4763 | 97.2 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1425517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 |  | 79.9012 | 98.8 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T7995517WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 17WP | 95.6 | 95.6 | 0 |  | 79.5662 | 98.7 | [7 empty] | CATEGORYB | SINGLE | WICHITA (WICHT12X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532796 | WICHITA7 345.00 | 533040 | EVANS N4 138.00 | 532830 | WICH12 1 13.800 | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2385517WP | TO->FROM | HUNTSVILLE - LINE 558 TAP 138KV CKT 1 | E | EES | EES | GSTHNT | GSTHNT | 0 | 334058 | 4L558T485 138.00 | 334057 | 4HUNTSVL 138.00 | 0 |  | 1 | 17WP | 206 | 206 | 0 |  | 84.5581 | 98 | [7 empty] | CATEGORYB | SINGLE | 4BENTWATER 138.00 - GRIMES 138KV CKT 1 | 0 | 334026 | 4GRIMES 138.00 | 334039 | 4BENTWATER 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3635517WP | FROM->TO | JAGUAR - POINT ESSO TAP 230KV CKT 1 | E | EES | EES | GSLBTR | GSLBTR | 0 | 335770 | 6JAGUAR 230.00 | 335641 | 6TP.ESSO 230.00 | 0 |  | 1 | 17WP | 685 | 685 | 0 | 97.7 | 97.7439 | 98 | [7 empty] | CATEGORYB | SINGLE | COLY - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WGLEN 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T3545017WP | FROM->TO | KN WRITESVILLE (KNWRIVL1) 500/13.8/13.8KV TRANSFORMER CKT 1 | E | EES | EES | EAILTR | EAILTR-A | 2 | 338507 | 1C1KNWRI 13.800 | 337860 | 8KNWRIVL 500.00 | 338508 | 1C3KNWRI 13.800 | 1 | 17WP | 235 | 235 | 0 | 99.2 | 99.1816 | 97.5 | [7 empty] | CATEGORYB | SINGLE | KEO EHV - WHITE BLUFF 500KV CKT 1 | 0 | 337651 | 8WH BLF 500.00 | 337957 | 8KEO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T9575017WP | FROM->TO | KN WRITESVILLE (KNWRIVL1) 500/13.8/13.8KV TRANSFORMER CKT 1 | E | EES | EES | EAILTR | EAILTR-A | 2 | 338507 | 1C1KNWRI 13.800 | 337860 | 8KNWRIVL 500.00 | 338508 | 1C3KNWRI 13.800 | 1 | 17WP | 235 | 235 | 0 | 99.9 | 99.9134 | 99.2 | [7 empty] | CATEGORYB | GENOUT | GEN337653 1-WHITE BLUFF UNIT #2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T9645017WP | FROM->TO | KN WRITESVILLE (KNWRIVL1) 500/13.8/13.8KV TRANSFORMER CKT 1 | E | EES | EES | EAILTR | EAILTR-A | 2 | 338507 | 1C1KNWRI 13.800 | 337860 | 8KNWRIVL 500.00 | 338508 | 1C3KNWRI 13.800 | 1 | 17WP | 235 | 235 | 0 | 95.8 | 95.8253 | 95.4 | [7 empty] | CATEGORYB | GENOUT | GEN338510 1-1S1KNWRI | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T185017WP | FROM->TO | KN WRITESVILLE (KNWRIVL2) 500/13.8/13.8KV TRANSFORMER CKT 1 | E | EES | EES | EAILTR | EAILTR-A | 2 | 338509 | 1C5KNWRI 13.800 | 337860 | 8KNWRIVL 500.00 | 338510 | 1S1KNWRI 13.800 | 1 | 17WP | 235 | 235 | 0 | 95.6 | 95.5611 | 95.2 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T9615017WP | FROM->TO | KN WRITESVILLE (KNWRIVL2) 500/13.8/13.8KV TRANSFORMER CKT 1 | E | EES | EES | EAILTR | EAILTR-A | 2 | 338509 | 1C5KNWRI 13.800 | 337860 | 8KNWRIVL 500.00 | 338510 | 1S1KNWRI 13.800 | 1 | 17WP | 235 | 235 | 0 | 99.6 | 99.6816 | 98.8 | [7 empty] | CATEGORYB | GENOUT | GEN338146 1-INDEPENDENCE UNIT #2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T9665017WP | FROM->TO | KN WRITESVILLE (KNWRIVL2) 500/13.8/13.8KV TRANSFORMER CKT 1 | E | EES | EES | EAILTR | EAILTR-A | 2 | 338509 | 1C5KNWRI 13.800 | 337860 | 8KNWRIVL 500.00 | 338510 | 1S1KNWRI 13.800 | 1 | 17WP | 235 | 235 | 0 | 99.5 | 99.452 | 99 | [7 empty] | CATEGORYB | GENOUT | GEN338511 1-1C7KNWRI | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T9675017WP | FROM->TO | KN WRITESVILLE (KNWRIVL2) 500/13.8/13.8KV TRANSFORMER CKT 1 | E | EES | EES | EAILTR | EAILTR-A | 2 | 338509 | 1C5KNWRI 13.800 | 337860 | 8KNWRIVL 500.00 | 338510 | 1S1KNWRI 13.800 | 1 | 17WP | 235 | 235 | 0 | 98 | 98.0213 | 97.6 | [7 empty] | CATEGORYB | GENOUT | GEN338512 1-1S2KNWRI | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2465517WP | TO->FROM | LINE 558 TAP - MT. ZION 138KV CKT 1 | E | EES | EES | GSTHNT | GSTHNT | 0 | 334060 | 4MT.ZION 138.00 | 334058 | 4L558T485 138.00 | 0 |  | 1 | 17WP | 206 | 206 | 0 |  | 83.5167 | 96.8 | [7 empty] | CATEGORYB | SINGLE | APRIL - WALDEN 138KV CKT 1 | 0 | 334040 | 4WALDEN 138.00 | 334041 | 4APRILTX 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2975517WP | TO->FROM | LINE 558 TAP - MT. ZION 138KV CKT 1 | E | EES | EES | GSTHNT | GSTHNT | 0 | 334060 | 4MT.ZION 138.00 | 334058 | 4L558T485 138.00 | 0 |  | 1 | 17WP | 206 | 206 | 0 |  | 86.7475 | 96.5 | [7 empty] | CATEGORYB | SINGLE | CYPRESS - HARTBURG 500KV CKT 1 | 0 | 334320 | 8CYPRESS 500.00 | 334325 | 8HARTBRG 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T8085017WP | FROM->TO | MONETTE JUNCTION - PARAGOULD 161 161KV CKT 1 | E | EES | EES | EAINTH | EAINTH | 0 | 338186 | 5MONETE 161.00 | 338204 | 5PARAG 161.00 | 0 |  | 1 | 17WP | 148 | 148 | 0 |  | -999 | 97.6 | [7 empty] | CATEGORYB | SINGLE | 8SHELBY TN 500.00 - PLUM POINT 500KV CKT 1 | 0 | 338188 | 8SANSOUC 500.00 | 360021 | 8SHELBY TN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T385517WP | FROM->TO | SPSNORTH_STX | E |  |  |  |  | SPSNORTH_STX | 0 |  | 0 |  | 0 |  |  | 17WP | 800 | 800 | 800 | 97 | 97.2269 | 99.2 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T6105517WP | FROM->TO | STEGALL - VICTORY HILL 230KV CKT 1 | E | WAPA | NPPD | WAPA_1603 | NPPD_686 | 0 | 652573 | STEGALL4 230.00 | 640396 | VICTRYH4 230.00 | 0 |  | 1 | 17WP | 240 | 240 | 264 |  | 90.0765 | 95.9 | [7 empty] | CATEGORYB | SINGLE | STEGALL - WAYSIDE 230KV CKT 1 | 0 | 640404 | WAYSIDE4 230.00 | 652573 | STEGALL4 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FNSL | FDNS-Iteration limit exceeded | FDNS |  | 5 | 5 | 2011AGP1AFS91T1515517WP | FROM->TO | SUB 167 - RIVERTON 69/13.2KV TRANSFORMER CKT 1 | E | EMDE | EMDE | BAXTER | BAXTER | 0 | 547645 | R8G167 1 13.200 | 547541 | RIV167 2 69.000 | 0 |  | 1 | 17WP | 52 | 52 | 0 | 96.7 | -999 | 98.2 | [7 empty] | CATEGORYB | SINGLE | SUB 368 - DADEVILLE EAST - SUB 431 - BOLIVAR SOUTH 161KV CKT 1 | 0 | 547478 | DAD368 5 161.00 | 547493 | BOL431 5 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T3825017WP | FROM->TO | TRUMANN - TRUMANN WEST AECC 161KV CKT 1 | E | EES | EES | EAINTH |  | 0 | 338169 | 5TRUMAN 161.00 | 338707 | 5TRUM-W# 161.00 | 0 |  | 1 | 17WP | 148 | 148 | 0 | 96.3 | 96.3012 | 98.3 | [7 empty] | CATEGORYB | SINGLE | CASH - JONESBORO 161KV CKT 1 | 0 | 338170 | 5JONES 161.00 | 338171 | 5CASH 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T3845017WP | FROM->TO | TRUMANN - TRUMANN WEST AECC 161KV CKT 1 | E | EES | EES | EAINTH |  | 0 | 338169 | 5TRUMAN 161.00 | 338707 | 5TRUM-W# 161.00 | 0 |  | 1 | 17WP | 148 | 148 | 0 | 96.9 | 96.9368 | 98.9 | [7 empty] | CATEGORYB | SINGLE | CASH - NEWPORT AB 161KV CKT 1 | 0 | 338171 | 5CASH 161.00 | 338172 | 5NEW-AB 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T12705517WP | FROM->TO | WATERFORD 500/230KV TRANSFORMER CKT 1 | E | EES | EES | AMSCOR | AMSCOR | 0 | 336150 | 8WATERFO 500.00 | 336154 | 6WATFRD 230.00 | 0 |  | 1 | 17WP | 1200 | 1200 | 0 |  | 93.5054 | 95.1 | [7 empty] | CATEGORYB | GENOUT | GEN336153 1-WATERFORD UNIT#3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3425517WP | FROM->TO | WILLOW GLEN 500/230KV TRANSFORMER CKT 1 | E | EES | EES | GSLBTR | GSLBTR | 0 | 335618 | 8WGLEN 500.00 | 335568 | 6WGLEN 230.00 | 0 |  | 1 | 17WP | 672 | 672 | 0 | 98.5 | 98.4875 | 99.3 | [7 empty] | CATEGORYB | SINGLE | WILLOW GLEN 230/138KV TRANSFORMER CKT 1 | 0 | 335568 | 6WGLEN 230.00 | 335601 | 4WGLEN-2 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4225517WP | FROM->TO | WILLOW GLEN 500/230KV TRANSFORMER CKT 1 | E | EES | EES | GSLBTR | GSLBTR | 0 | 335618 | 8WGLEN 500.00 | 335568 | 6WGLEN 230.00 | 0 |  | 1 | 17WP | 672 | 672 | 0 | 98.7 | 98.6807 | 99.6 | [7 empty] | CATEGORYB | SINGLE | FANCY POINT - WATERLOO 230KV CKT 1 | 0 | 335825 | 6FANCY 230.00 | 335827 | 6WATLOO 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T1535022SP | FROM->TO | 36TH & LEWIS - 52ND & DELAWARE TAP 138KV CKT 1 | E | AEPW | AEPW | PSO_TULSA | PSO_TULSA | 0 | 509800 | 36LEWIS4 138.00 | 509776 | 52DELTP4 138.00 | 0 |  | 1 | 22SP | 278 | 278 | 0 |  | 94.763 | 96.1 | [7 empty] | CATEGORYB | SINGLE | 81ST & YALE TAP - SOUTHERN HILLS EAST TAP 138KV CKT 1 | 0 | 509809 | 81YALTP4 138.00 | 509813 | SHILETP4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T1545022SP | FROM->TO | 36TH & LEWIS - 52ND & DELAWARE TAP 138KV CKT 1 | E | AEPW | AEPW | PSO_TULSA | PSO_TULSA | 0 | 509800 | 36LEWIS4 138.00 | 509776 | 52DELTP4 138.00 | 0 |  | 1 | 22SP | 278 | 278 | 0 | 98.2 | 98.2141 | 99.5 | [7 empty] | CATEGORYB | SINGLE | ORU WEST TAP - SOUTHERN HILLS EAST TAP 138KV CKT 1 | 0 | 509813 | SHILETP4 138.00 | 509853 | ORU-WTP4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T1585022SP | FROM->TO | 36TH & LEWIS - 52ND & DELAWARE TAP 138KV CKT 1 | E | AEPW | AEPW | PSO_TULSA | PSO_TULSA | 0 | 509800 | 36LEWIS4 138.00 | 509776 | 52DELTP4 138.00 | 0 |  | 1 | 22SP | 278 | 278 | 0 |  | 93.999 | 95.3 | [7 empty] | CATEGORYB | SINGLE | 96TH & YALE - WARREN TAP 138KV CKT 1 | 0 | 509847 | 96YALE-4 138.00 | 509858 | WARNTAP4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T10655522SP | TO->FROM | 3WOODW-S 115.00 - PINE BLUFF ARSENAL D 115KV CKT 1 | E | EES | EES | EAISTH | EAISTH | 0 | 337647 | 3PB-ARD 115.00 | 337619 | 3WOODW-S 115.00 | 0 |  | 1 | 22SP | 239 | 239 | 0 |  | 86.0908 | 97.2 | [7 empty] | CATEGORYB | SINGLE | PINE BLUFF INDUSTRIAL - PINE BLUFF WHITE HALL 115KV CKT 1 | 0 | 337644 | 3PB IND 115.00 | 337645 | 3PB-WH 115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T5545022SP | TO->FROM | 4BENTWATER 138.00 - GRIMES 138KV CKT 1 | E | EES | EES | GSTNAV | GSTNAV | 0 | 334026 | 4GRIMES 138.00 | 334039 | 4BENTWATER 138.00 | 0 |  | 1 | 22SP | 206 | 206 | 0 |  | 90.3784 | 99.9 | [7 empty] | CATEGORYB | SINGLE | HUNTSVILLE - LINE 558 TAP 138KV CKT 1 | 0 | 334057 | 4HUNTSVL 138.00 | 334058 | 4L558T485 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | INVALID |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2365522SP | TO->FROM | 7JASPER 345.00 - BLACKBERRY 345KV CKT 1 | E | AECI | AECI | KAMO | KAMO | 0 | 300739 | 7BLACKBERRY 345.00 | 300949 | 7JASPER 345.00 | 0 |  | 1 | 22SP | 870 | 870 | 0 |  | 89.2148 | 99.1556 | [7 empty] | CATEGORYB | SINGLE | GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 | 0 | 512650 | GRDA1 7 345.00 | 512750 | TONECE7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T28175522SP | TO->FROM | 7JASPER 345.00 - BLACKBERRY 345KV CKT 1 | E | AECI | AECI | KAMO | KAMO | 0 | 300739 | 7BLACKBERRY 345.00 | 300949 | 7JASPER 345.00 | 0 |  | 1 | 22SP | 870 | 870 | 0 |  | 89.4453 | 99.4 | [7 empty] | CATEGORYB | NONSINGLE | GRDA-OPGD-05 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T6875022SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 22SP | 615 | 615 | 0 | 96.3 | 96.3217 | 95.3 | [7 empty] | CATEGORYB | SINGLE | WEBRE - WELLS 500KV CKT 1 | 0 | 335368 | 8WELLS 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T8215522SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 22SP | 615 | 615 | 0 | 96.4 | 96.3893 | 95.8 | [7 empty] | CATEGORYB | SINGLE | WEBRE - WELLS 500KV CKT 1 | 0 | 335368 | 8WELLS 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T9285022SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 22SP | 615 | 615 | 0 | 95.9 | 95.8901 | 95.2 | [7 empty] | CATEGORYB | SINGLE | ELDORADO EHV - STERLINGTON 500KV CKT 1 | 0 | 337420 | 8STERL 500.00 | 337561 | 8ELDEHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T14435522SP | TO->FROM | ALTHEIMER SS - WOODWARD 115KV CKT 1 | E | EES | EES | EAISTH | EAICEN | 0 | 337620 | 3WOODW-N 115.00 | 337962 | 3ALTHEI* 115.00 | 0 |  | 1 | 22SP | 106 | 106 | 0 |  | 85.3916 | 98.1 | [7 empty] | CATEGORYB | SINGLE | STUTTGART RICUSKEY 230 230/115KV TRANSFORMER CKT 1 | 0 | 337967 | 3RICUS 115.00 | 337968 | 6RICUS 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T7455522SP | FROM->TO | AMELIA BULK - CHINA 230KV CKT 1 | E | EES | EES | GSTBMM | GSTBMR | 0 | 334327 | 6AMELIA 230.00 | 334204 | 6CHINA 230.00 | 0 |  | 1 | 22SP | 797 | 797 | 0 | 103.9 | 103.8503 | 99.9 | [7 empty] | CATEGORYB | SINGLE | CHINA - SABINE 230KV CKT 1 | 0 | 334204 | 6CHINA 230.00 | 334434 | 6SABINE 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T18815522SP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 22SP | 68 | 68 | 0 |  | 94.2789 | 96.8 | [7 empty] | CATEGORYB | SINGLE | JONESBORO - JONESBORO 161KV CKT 1 | 0 | 505418 | JONESBO5 161.00 | 338170 | 5JONES 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T5485522SP | TO->FROM | BETHANY - PATTONSBURG 69KV CKT 1 | E | AECI | AECI | NW | NW | 0 | 300209 | 2PATBRG 69.000 | 300220 | 2BETHNY 69.000 | 0 |  | 1 | 22SP | 36 | 36 | 0 |  | 92.2559 | 95.9 | [7 empty] | CATEGORYB | SINGLE | TINDALL - TRENTON 69KV CKT 1 | 0 | 300237 | 2TINDAL 69.000 | 300239 | 2TRENTN 69.000 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T2325022SP | TO->FROM | BLUEBELL - PRATTVILLE 138KV CKT 1 | E | AEPW | OKGE | PSO_TULSA | MUSKOGEE | 0 | 509758 | PRATTV-4 138.00 | 515242 | BLUEBEL4 138.00 | 0 |  | 1 | 22SP | 212 | 212 | 0 | 100.1 | 100.1196 | 99.4 | [7 empty] | CATEGORYB | SINGLE | BEELINE - EXPLORER GLENPOOL 138KV CKT 1 | 0 | 515247 | BEELINE4 138.00 | 515248 | EXPLGLN4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T15045522SP | FROM->TO | BULL SHOALS - MIDWAY (YVEPA) 161KV CKT 1 | E | SWPA | EES | EMINTH |  | 0 | 505460 | BULL SH5 161.00 | 338813 | 5MIDWAY# 161.00 | 0 |  | 1 | 22SP | 162 | 162 | 0 |  | 90.0406 | 96.6 | [7 empty] | CATEGORYB | SINGLE | MELBOURNE - SAGE SS 161KV CKT 1 | 0 | 338131 | 5MELBRN 161.00 | 338132 | 5SAGE* 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T19125522SP | FROM->TO | BULL SHOALS - MIDWAY (YVEPA) 161KV CKT 1 | E | SWPA | EES | EMINTH |  | 0 | 505460 | BULL SH5 161.00 | 338813 | 5MIDWAY# 161.00 | 0 |  | 1 | 22SP | 162 | 162 | 0 |  | 89.511 | 96 | [7 empty] | CATEGORYB | SINGLE | CALICO ROCK - NORFORK 161KV CKT 1 | 0 | 505448 | NORFORK5 161.00 | 338130 | 5CALCR 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T3035022SP | TO->FROM | BYRD SUB - MONUMENT TAP 115KV CKT 1 | E | SPS | SPS | SPS-HOBB | SPS-HOBB | 0 | 528568 | MONUMNT_TP 3115.00 | 528582 | BYRD 3115.00 | 0 |  | 1 | 22SP | 141 | 141 | 0 | 97.1 | 97.0859 | 98.1 | [7 empty] | CATEGORYB | SINGLE | DRINKARD TAP - WEST HOBBS SWITCHING STATION 115KV CKT 1 | 0 | 528498 | W_HOBBS 3115.00 | 528533 | DRINKARD_TP3115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1215522SP | FROM->TO | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | E | AEPW | AEPW | FAYETTEVILLE | FAYETVL AECC | 0 | 506944 | CHAMSPR5 161.00 | 504020 | FARMNGTN 5 161.00 | 0 |  | 1 | 22SP | 294 | 353 | 0 | 98.8 | 98.758 | 99.3 | [7 empty] | CATEGORYB | SINGLE | DYESS - SOUTH SPRINGDALE 161KV CKT 1 | 0 | 506927 | DYESS 5 161.00 | 506949 | SOSPRDL5 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1305522SP | FROM->TO | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | E | AEPW | AEPW | FAYETTEVILLE | FAYETVL AECC | 0 | 506944 | CHAMSPR5 161.00 | 504020 | FARMNGTN 5 161.00 | 0 |  | 1 | 22SP | 294 | 353 | 0 | 96.7 | 96.7334 | 98 | [7 empty] | CATEGORYB | SINGLE | CHAMBER SPRINGS - TONTITOWN 345KV CKT 1 | 0 | 506945 | CHAMSPR7 345.00 | 506959 | TONTITN7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T15522SP | FROM->TO | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | E | AEPW | AEPW | FAYETTEVILLE | FAYETVL AECC | 0 | 506944 | CHAMSPR5 161.00 | 504020 | FARMNGTN 5 161.00 | 0 |  | 1 | 22SP | 294 | 353 | 0 |  | 94.2993 | 95 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | INVALID |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4025522SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | E | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 22SP | 100 | 100 | 0 |  | 59.0621 | 96.5289 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER NORTH - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533040 | EVANS N4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T5145522SP | TO->FROM | COON CREEK - JAMESPORT 69KV CKT 1 | E | AECI | AECI | NW | NW | 0 | 300228 | 2JMSPRT 69.000 | 300197 | 2COONCK 69.000 | 0 |  | 1 | 22SP | 36 | 36 | 0 |  | 86.795 | 99.5 | [7 empty] | CATEGORYB | SINGLE | FAIRPORT - HICKORY CREEK 161KV CKT 1 | 0 | 300076 | 5FAIRPT 161.00 | 300087 | 5HICKCK 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T5155522SP | FROM->TO | COON CREEK - TRENTON 69KV CKT 1 | E | AECI | AECI | NW | NW | 0 | 300197 | 2COONCK 69.000 | 300239 | 2TRENTN 69.000 | 0 |  | 1 | 22SP | 36 | 36 | 0 |  | 85.3115 | 97.9 | [7 empty] | CATEGORYB | SINGLE | FAIRPORT - HICKORY CREEK 161KV CKT 1 | 0 | 300076 | 5FAIRPT 161.00 | 300087 | 5HICKCK 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T175522SP | TO->FROM | DODGE CITY BEEF - JUDSON LARGE 115KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539671 | FTDODGE3 115.00 | 539645 | DCBEEF3 115.00 | 0 |  | 1 | 22SP | 83.9 | 89.6 | 0 | 96 | 96.0253 | 96.5 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T25725022SP | TO->FROM | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | E | WERE | WERE | NEAST | NCENTRAL | 0 | 532852 | JEC 6 230.00 | 532861 | EMANHAT6 230.00 | 0 |  | 1 | 22SP | 446 | 446 | 0 | 98.1 | 98.0532 | 95.2 | [7 empty] | CATEGORYB | NONSINGLE | WRTOD400 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | CONT-0402 - JEC - Summit 345kV | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T3275022SP | TO->FROM | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | E | WERE | WERE | NEAST | NCENTRAL | 0 | 532852 | JEC 6 230.00 | 532861 | EMANHAT6 230.00 | 0 |  | 1 | 22SP | 446 | 446 | 0 | 104.7 | 104.7254 | 96.7 | [7 empty] | CATEGORYB | SINGLE | JEFFREY ENERGY CENTER - SUMMIT 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532773 | SUMMIT 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T22005522SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | E | WERE | WERE | NCENTRAL | NCENTRAL | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 22SP | 280 | 308 | 350 | 96.3 | 96.2869 | 95.5 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST MANHATTAN (NWMANH1X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532865 | NWMANHT6 230.00 | 533347 | NWMANHT3 115.00 | 532901 | NWMANHX1 18.000 | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T1225522SP | TO->FROM | ELM SPRINGS REC - TONTITOWN 161KV CKT 1 | E | AEPW | AEPW | FAYETTEVILLE | FAYETVL AECC | 0 | 506957 | TONTITN5 161.00 | 504010 | ELMSPRGS 5 161.00 | 0 |  | 1 | 22SP | 451 | 580 | 0 | 95.4 | 95.4442 | 96 | [7 empty] | CATEGORYB | SINGLE | DYESS - TONTITOWN 161KV CKT 1 | 0 | 506927 | DYESS 5 161.00 | 506957 | TONTITN5 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T29415522SP | FROM->TO | FAIRPORT - PATTONSBURG 69KV CKT 1 | E | AECI | AECI | NW | NW | 0 | 300249 | 2FAIRPT 69.000 | 300209 | 2PATBRG 69.000 | 0 |  | 1 | 22SP | 36 | 36 | 0 |  | 92.5394 | 96.5 | [7 empty] | CATEGORYB | GENOUT | GEN300003 1-THOMAS HILL UNIT 3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T5255522SP | FROM->TO | FAIRPORT - PATTONSBURG 69KV CKT 1 | E | AECI | AECI | NW | NW | 0 | 300249 | 2FAIRPT 69.000 | 300209 | 2PATBRG 69.000 | 0 |  | 1 | 22SP | 36 | 36 | 0 |  | 92.9764 | 96.8 | [7 empty] | CATEGORYB | SINGLE | HICKORY CREEK 161/69KV TRANSFORMER CKT 1 | 0 | 300087 | 5HICKCK 161.00 | 300226 | 2HICKRY 69.000 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SPP_FG-EES-AFC-40036-ANDRXF_ANIND | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T10265522SP | FROM->TO | GERALD ANDRUS SES 230/115KV TRANSFORMER CKT 1 | E | EES | EES | EMI-GRNVL | EMI-GRNVL | 0 | 337040 | 6ANDRUS 230.00 | 337042 | 3ANDRUS 115.00 | 0 |  | 1 | 22SP | 392 | 392 | 0 | 95.1 | 95.1347 | 95.5 | [7 empty] | CATEGORYB | SINGLE | GERALD ANDRUS SES - INDIANOLA 230KV CKT 1 | 0 | 337040 | 6ANDRUS 230.00 | 337050 | 6INDOLA 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T26705022SP | FROM->TO | GRIMES - MT. ZION 138KV CKT 1 | E | EES | EES | GSTNAV | GSTHNT | 0 | 334026 | 4GRIMES 138.00 | 334060 | 4MT.ZION 138.00 | 0 |  | 1 | 22SP | 206 | 206 | 0 |  | 89.8034 | 98 | [7 empty] | CATEGORYB | GENOUT | GEN334440 1-SABINE UNIT 4 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 | SPP_FG-EES-IDC-15974 |  |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T5215022SP | FROM->TO | GRIMES - MT. ZION 138KV CKT 1 | E | EES | EES | GSTNAV | GSTHNT | 0 | 334026 | 4GRIMES 138.00 | 334060 | 4MT.ZION 138.00 | 0 |  | 1 | 22SP | 206 | 206 | 0 |  | 88.1396 | 97.5 | [7 empty] | CATEGORYB | SINGLE | GRIMES - MAGNOLIA ANDERSON 138KV CKT 1 | 0 | 334025 | 4MAG AND 138.00 | 334026 | 4GRIMES 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T5505022SP | FROM->TO | GRIMES - MT. ZION 138KV CKT 1 | E | EES | EES | GSTNAV | GSTHNT | 0 | 334026 | 4GRIMES 138.00 | 334060 | 4MT.ZION 138.00 | 0 |  | 1 | 22SP | 206 | 206 | 0 |  | 87.5819 | 99 | [7 empty] | CATEGORYB | SINGLE | LAKE FOREST - WOODHAVEN 138KV CKT 1 | 0 | 334042 | 4LFOREST 138.00 | 334105 | 4WDHAVN 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | CONT-Webre - Richard 500kV |  |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T6835022SP | FROM->TO | GRIMES - MT. ZION 138KV CKT 1 | E | EES | EES | GSTNAV | GSTHNT | 0 | 334026 | 4GRIMES 138.00 | 334060 | 4MT.ZION 138.00 | 0 |  | 1 | 22SP | 206 | 206 | 0 |  | 90.7545 | 98.2 | [7 empty] | CATEGORYB | SINGLE | WEBRE - WELLS 500KV CKT 1 | 0 | 335368 | 8WELLS 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T21285522SP | FROM->TO | HITCHLAND INTERCHANGE (H TP80148301) 230/115/13.2KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-OKLA | SPS-OKLA | 1 | 523095 | HITCHLAND 6230.00 | 523093 | HITCHLAND 3115.00 | 523092 | HITCHLD_TR1113.200 | 1 | 22SP | 250 | 250 | 0 | 96.2 | 96.2399 | 97.7 | [7 empty] | CATEGORYB | SINGLE | MOORE COUNTY INTERCHANGE (ENRCO 136402) 230/115/13.2KV TRANSFORMER CKT 1 | 1 | 523308 | MOORE_E 3115.00 | 523309 | MOORE_CNTY 6230.00 | 523302 | MOORE_TR1 113.200 | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T2015522SP | TO->FROM | HOBART - HOBART JUNCTION 69KV CKT 1 | E | AEPW | AEPW | PSO_WESTERN | PSO_WESTERN | 0 | 511464 | HOB-JCT2 69.000 | 511465 | HOBART-2 69.000 | 0 |  | 1 | 22SP | 52 | 69 | 0 |  | 73.4939 | 95.8 | [7 empty] | CATEGORYB | SINGLE | HOBART JUNCTION - OMPA-ALTUS TAMARACK 138KV CKT 1 | 0 | 511463 | HOB-JCT4 138.00 | 529302 | OMALTUS4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T10405522SP | FROM->TO | HORN LAKE 230/115KV TRANSFORMER CKT 1 | E | EES | EES | EMI-SHVN | EMI-SHVN | 0 | 337180 | 6HN LAK 230.00 | 337150 | 3HN LAK 115.00 | 0 |  | 1 | 22SP | 392 | 392 | 0 |  | 94.6362 | 97.6 | [7 empty] | CATEGORYB | SINGLE | GETWELL 230/115KV TRANSFORMER CKT 1 | 0 | 337139 | 3GETWEL 115.00 | 337140 | 6GETWELL 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3825522SP | TO->FROM | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 | 22SP | 1076 | 1076 | 0 |  | 90.5717 | 97.2 | [7 empty] | CATEGORYB | SINGLE | JEFFREY ENERGY CENTER - MORRIS COUNTY 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532770 | MORRIS 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3935522SP | TO->FROM | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 | 22SP | 1076 | 1076 | 0 |  | 89.9588 | 97.3 | [7 empty] | CATEGORYB | SINGLE | AUBURN ROAD - JEFFREY ENERGY CENTER 230KV CKT 1 | 0 | 532851 | AUBURN 6 230.00 | 532852 | JEC 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T27635022SP | FROM->TO | INDEPENDENCE - LS POWER OSCEOLA UNIT 500KV CKT 1 | E | EES | EES | EAINTH | EAINTH | 0 | 338145 | 8ISES 500.00 | 338144 | 8ISXF 500.00 | 0 |  | 1 | 22SP | 850 | 850 | 0 | 98.1 | 98.0904 | 95.7 | [7 empty] | CATEGORYB | GENOUT | GEN338143 1-INDEPENDENCE UNIT #1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T12885022SP | FROM->TO | INDEPENDENCE - MOOREFIELD 161KV CKT 1 | E | EES | EES | EAINTH | EAINTH | 0 | 338142 | 5ISES-1 161.00 | 338138 | 5MORFLD 161.00 | 0 |  | 1 | 22SP | 303 | 303 | 0 | 97 | 96.9515 | 95.6 | [7 empty] | CATEGORYB | SINGLE | DELL 500 - INDEPENDENCE 500KV CKT 1 | 0 | 338145 | 8ISES 500.00 | 338187 | 8DELL 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T6415022SP | TO->FROM | LINE 558 TAP - MT. ZION 138KV CKT 1 | E | EES | EES | GSTHNT | GSTHNT | 0 | 334060 | 4MT.ZION 138.00 | 334058 | 4L558T485 138.00 | 0 |  | 1 | 22SP | 206 | 206 | 0 |  | 88.4936 | 96.2 | [7 empty] | CATEGORYB | SINGLE | CYPRESS - HARTBURG 500KV CKT 1 | 0 | 334320 | 8CYPRESS 500.00 | 334325 | 8HARTBRG 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T17625522SP | FROM->TO | LOCUST CREEK 161/69KV TRANSFORMER CKT 1 | E | AECI | AECI | NW | NW | 0 | 300094 | 5LOCUST 161.00 | 300278 | 2LOCUST 69.000 | 0 |  | 1 | 22SP | 56 | 56 | 0 | 97.5 | 97.5334 | 98.9 | [7 empty] | CATEGORYB | SINGLE | HART - NEW CAMBRIA 69KV CKT 1 | 0 | 300392 | 2HART 69.000 | 300406 | 2NCAMBR 69.000 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T17655522SP | FROM->TO | LOCUST CREEK 161/69KV TRANSFORMER CKT 1 | E | AECI | AECI | NW | NW | 0 | 300094 | 5LOCUST 161.00 | 300278 | 2LOCUST 69.000 | 0 |  | 1 | 22SP | 56 | 56 | 0 | 98 | 98.0377 | 99.4 | [7 empty] | CATEGORYB | SINGLE | MARCELINE TAP - NEW CAMBRIA 69KV CKT 1 | 0 | 300404 | 2MARCTP 69.000 | 300406 | 2NCAMBR 69.000 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T15365522SP | FROM->TO | MCCRORY - MOSES 161KV CKT 1 | E | EES | EES | EAICEN | EAICEN | 0 | 338044 | 5MCRORY 161.00 | 338022 | 5MOSES 161.00 | 0 |  | 1 | 22SP | 148 | 148 | 0 |  | 89.5196 | 97.7 | [7 empty] | CATEGORYB | SINGLE | WEST MEMPHIS 500 500/161KV TRANSFORMER CKT 1 | 0 | 338161 | 5WM-EHV 161.00 | 338162 | 8WM-EHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T26005522SP | FROM->TO | MCCRORY - MOSES 161KV CKT 1 | E | EES | EES | EAICEN | EAICEN | 0 | 338044 | 5MCRORY 161.00 | 338022 | 5MOSES 161.00 | 0 |  | 1 | 22SP | 148 | 148 | 0 |  | 88.1594 | 97.6 | [7 empty] | CATEGORYB | SINGLE | 8SHELBY TN 500.00 - PLUM POINT 500KV CKT 1 | 0 | 338188 | 8SANSOUC 500.00 | 360021 | 8SHELBY TN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T3045522SP | FROM->TO | MULLERGREN 115/13.8KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539677 | GRTBEND1 13.800 | 539678 | GRTBEND3 115.00 | 0 |  | 1 | 22SP | 106 | 106 | 106 |  | 89.8846 | 97.2 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T1265022SP | FROM->TO | NEW GLADEWATER - PERDUE 138KV CKT 1 | E | AEPW | AEPW | LONGVW-MARSH | MT PLES NTEC | 0 | 508560 | NEWGLAD4 138.00 | 508351 | PERDUE 4 138.00 | 0 |  | 1 | 22SP | 215 | 237 | 0 |  | 86.9224 | 97.1 | [7 empty] | CATEGORYB | SINGLE | DIANA - PERDUE 138KV CKT 1 | 0 | 508351 | PERDUE 4 138.00 | 508831 | DIANA 4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T15825522SP | TO->FROM | NORTH WARSAW - TRUMAN 161KV CKT 1 | E | SWPA | GMO | EMINTH |  | 0 | 505502 | TRUMAN 5 161.00 | 541314 | NWARSAW5 161.00 | 0 |  | 1 | 22SP | 223 | 223 | 223 | 97.6 | 97.6181 | 99.9 | [7 empty] | CATEGORYB | SINGLE | 5 CALIF 161.00 - 5OVERTON 2 161.00 161KV CKT 1 | 0 | 344233 | 5 CALIF 161.00 | 345411 | 5OVERTON 2 161.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | ISLAND-LOAD | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T26325522SP | TO->FROM | NORTH WARSAW - TRUMAN 161KV CKT 1 | E | SWPA | GMO | EMINTH |  | 0 | 505502 | TRUMAN 5 161.00 | 541314 | NWARSAW5 161.00 | 0 |  | 1 | 22SP | 223 | 223 | 223 | 95.1 | 95.1031 | 97.1 | [7 empty] | CATEGORYB | SINGLE | 5CAPE GIR 161.00 161/34.5KV TRANSFORMER CKT 99 | 0 | 344282 | 5CAPE GIR 161.00 | 345890 | 1VIAD 1 34.500 | 0 |  | 99 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T5025522SP | TO->FROM | NORTH WARSAW - TRUMAN 161KV CKT 1 | E | SWPA | GMO | EMINTH |  | 0 | 505502 | TRUMAN 5 161.00 | 541314 | NWARSAW5 161.00 | 0 |  | 1 | 22SP | 223 | 223 | 223 | 96.4 | 96.363 | 99.3 | [7 empty] | CATEGORYB | SINGLE | 7JASPER 345.00 - MORGAN 345KV CKT 1 | 0 | 300045 | 7MORGAN 345.00 | 300949 | 7JASPER 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T10665522SP | TO->FROM | PINE BLUFF ARSENAL D - WHITE BLUFF 115KV CKT 1 | E | EES | EES | EAISTH | EAISTH | 0 | 337648 | 3WH BLF 115.00 | 337647 | 3PB-ARD 115.00 | 0 |  | 1 | 22SP | 255 | 255 | 0 |  | 86.0943 | 96.6 | [7 empty] | CATEGORYB | SINGLE | PINE BLUFF INDUSTRIAL - PINE BLUFF WHITE HALL 115KV CKT 1 | 0 | 337644 | 3PB IND 115.00 | 337645 | 3PB-WH 115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  |  |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T10685522SP | TO->FROM | PINE BLUFF ARSENAL D - WHITE BLUFF 115KV CKT 1 | E | EES | EES | EAISTH | EAISTH | 0 | 337648 | 3WH BLF 115.00 | 337647 | 3PB-ARD 115.00 | 0 |  | 1 | 22SP | 255 | 255 | 0 |  | 88.7918 | 99.3 | [7 empty] | CATEGORYB | SINGLE | PINE BLUFF ARSENAL C - PINE BLUFF WHITE HALL 115KV CKT 1 | 0 | 337645 | 3PB-WH 115.00 | 337646 | 3PB-ARC 115.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | INVALID |  |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T3405022SP | FROM->TO | SEVENTEENTH (17TH 4X) 138/69/11.295KV TRANSFORMER CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 1 | 533064 | 17TH 4 138.00 | 533840 | 17TH 2 69.000 | 533112 | 17TH 4 1 11.295 | 1 | 22SP | 150 | 165 | 187.5 |  | 81.8376 | 97.1652 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER NORTH - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533040 | EVANS N4 138.00 | 533041 | EVANS S4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T4155022SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 22SP | 250 | 250 | 250 | 95.4 | 95.4409 | 95.5 | [7 empty] | CATEGORYB | SINGLE | SUB 3455 - SUB 3740 345KV CKT 1 | 0 | 645455 | S3455 3 345.00 | 645740 | S3740 3 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2011AGP1AFS91T4975522SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 22SP | 250 | 250 | 250 | 95.9 | 95.8911 | 96.1 | [7 empty] | CATEGORYB | SINGLE | SUB 3455 - SUB 3740 345KV CKT 1 | 0 | 645455 | S3455 3 345.00 | 645740 | S3740 3 345.00 | 0 |  | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 |  | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T20975022SP | TO->FROM | SUB 907 - SUB 911 69KV CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 647911 | S911 8 69.000 | 647907 | S907 8 69.000 | 0 |  | 1 | 22SP | 95 | 95 | 95 | 96.6 | 96.6127 | 95.2 | [7 empty] | CATEGORYB | SINGLE | SUB 1250 (S1250 T1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 646250 | S1250 5 161.00 | 647950 | S950 8 69.000 | 648250 | S1250T19 13.800 | 1 | Transfer Loading < 100%
2011-AGP1 | AFS9 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2011AGP1AFS91T26075022SP | FROM->TO | THOMAS HILL 161/22.0KV TRANSFORMER CKT 1 | E | AECI | AECI | CENTRAL | CENTRAL | 0 | 300002 | 1THLG2 22.000 | 300120 | 5THMHIL 161.00 | 0 |  | 1 | 22SP | 325 | 325 | 0 | 112.1 | 112.1349 | 95.6 | [7 empty] | CATEGORYB | NONSINGLE | ESEX-IDAL | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%