## tblAllFacilityLog
STUDYDES | STUDYDES2 | EVENTTYPE | AssessmentSOLUTIONTYPE | AssessmenFDNS-TERMINATION | SOLUTIONTYPE | FDNS-TERMINATION | GROUP | SCENARIO | FGName | DIRECTION | FacilityName | FacilityUpgradeCode | ModelArea1 | ModelArea2 | FZONENAME | TZONENAME | MONTFLAG | MONTFB | MONTFNAME | MONTTB1 | MONTTNAME1 | MONTTB2 | MONTTNAME2 | MONTCKT | Case | RATEA | RATEB | RATEC | Assessment Loading | BaseCaseLoading | TransferCaseLoading | NameOfBusWithMonitoredVoltage | Assessment Voltage | BaseCaseVoltage | TransferCaseVoltage | VINIT | VMIN | VMAX | CATEGORY | CONTTYPE | CONTNAME | CONTXFMRFLAG | CONTFB | CONTFNAME | CONTTB1 | CONTTNAME1 | CONTTB2 | CONTTNAME2 | CONTCKT | TransmissionProviderCommentsNotes | RequiredRateB | TransmissionOwnerComments | OwnerDesignation | UpgradeName | UpgradeComponentWithinFacility | NewSummerA | NewSummerB | NewOtherA | NewOtherB | DistToConstruct | TotalLead | ConstructionLeadOnly | NewOrConstructWhileEnergized | NewR | NewX | NewB | CommentsRegardingUpgradeRequirements | NewCost | EffDate | NetPlantDate | ReusableEx_GrossValue | ReusableEx_NetValue | Reusable_EndofDepr | SalvageValue | NewCostWhileExpediting | EffDateExpedited | StartDeprExpedited | EndDeprExpedited | NetPlantDateExpedited | ReusableEx_GrossExpedited | ReusableEx_NetExpedited | Reusable_EndofDeprExpedited | SalvageValueExpedited | Generation 1 Owner & Unit (Name) | Generation 1 Redispatch Cost ($) | Generation 1 Redispatch Date (M/D/Y) | Generation 2 Owner & Unit (Name) | Generation 2 Redispatch Cost ($) | Generation 2 Redispatch Date (M/D/Y) | Generation 3 Owner & Unit (Name) | Generation 3 Redispatch Cost ($) | Generation 3 Redispatch Date (M/D/Y) | ActualCompletion | ActualNewCost | ActualNetPlantDate | ActualReusableEx_GrossValue | ActualReusableEx_NetValue | ActualReusable_EndofDepr | ActualSalvageValue | Actual_NewCostWhileExpediting | Actual_StartDeprExp | Actual_EndDeprExp | Actual_NetPlantDateExpedited | ActualReusableEx_GrossExpedited | ActualReusableEx_NetExpedited | ActualReusable_EndofDeprExpedited | Actual_SalvageValueExpedited | SPPReliabilityDate | DUN | EOC | EarliestDate
2006-AG1 | 2006-AG1 | [9 empty] | ALUMAX TAP - BANN 138KV CKT 1 | U | AEPW | AEPW |  |  | 0 | 508049 | ALUMXT 4 138 | 508054 | BANN 4 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | AEPW | ALUMAX TAP - BANN 138KV CKT 1 | Replace six (6) 138 kV switches, five at Bann & one at Alumax Tap. Rebuild 0.67 miles of 1024 ACAR with 2156 ACSR. Replace wavetrap & jumpers @ Bann. Replace breaker 3300 @ Bann. | [53 empty] | 2008-06-01 | 2008-06-01
GEN-2006-010 | Turk | [9 empty] | ASHDOWN REC (MILLWOOD) - OKAY 138KV CKT 1 | U | AEPW | AEPW | SARK | SARKAECC | 0 | 507428 | OKAY 4 138.00 | 507402 | ASHDWNR4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | AEPW | ASHDOWN REC (MILLWOOD) - OKAY 138KV CKT 1 | Recunductor and convert line to 138 kV and replace switches at Ashdown REC | [53 empty] | 2012-07-01 | 2012-07-01
GEN-2006-010 | Turk | [9 empty] | ASHDOWN REC (MILLWOOD) - PATTERSON 138KV CKT 1 | U | AEPW | AEPW | SARKAECC | SARK | 0 | 507402 | ASHDWNR4 138.00 | 507431 | PATTERS4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | AEPW | ASHDOWN REC (MILLWOOD) - PATTERSON 138KV CKT 1 | Reconductor Line & Convert Line to 138 kV and convert Patterson station to breaker-and-a half cofiguration | [53 empty] | 2012-07-01 | 2012-07-01
GEN-2006-010 | Turk | [9 empty] | BANN - RED SPRINGS REC 138KV CKT 1 | U | AEPW | AEPW | TEXARK | TXARNTEC | 0 | 508054 | BANN 4 138.00 | 508075 | REDSPRG4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | AEPW | BANN - RED SPRINGS REC 138KV CKT 1 | Replace 138 kV breakers 3300 & 3310 | [53 empty] | 2012-07-01 | 2012-07-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1045514SP | FROM->TO | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | EXP | AEPW | AEPW | FAYETTEVILLE | FAYETVL AECC | 0 | 506944 | CHAMSPR5 161.00 | 504020 | FARMNGTN 5 161.00 | 0 |  | 1 | 14SP | 294 | 317 | 0 | 101.8 | 101.8413 | 102.3753 | [7 empty] | CATEGORYB | SINGLE | CHAMBER SPRINGS - TONTITOWN 345KV CKT 1 | 0 | 506945 | CHAMSPR7 345.00 | 506959 | TONTITN7 345.00 | 0 |  | 1 |  | 325 |  | AEPW | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | Rebuild and reconductor 11.1-mile 161 kV line from Chamber Springs to Farmington REC with 2-959.6 ACSR/TW. Upgrade wavetraps, CT ratios, and relay settings at Chamber Springs. | [53 empty] | 2014-06-01 | 2015-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T11875514SP | FROM->TO | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | EXP | AEPW | AEPW | FAYETTEVILLE | FAYETVL AECC | 0 | 506944 | CHAMSPR5 161.00 | 504020 | FARMNGTN 5 161.00 | 0 |  | 1 | 14SP | 294 | 317 | 0 | 101.8 | 101.795 | 102.3302 | [7 empty] | CATEGORYB | SINGLE | TONTITOWN () 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 506957 | TONTITN5 161.00 | 506959 | TONTITN7 345.00 | 506958 | TONTITN1 13.800 | 1 |  | 325 |  | AEPW | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | Rebuild and reconductor 11.1-mile 161 kV line from Chamber Springs to Farmington REC with 2-959.6 ACSR/TW. Upgrade wavetraps, CT ratios, and relay settings at Chamber Springs. | [53 empty] | 2014-06-01 | 2015-06-01
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1145518SP | FROM->TO | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | EXP | AEPW | AEPW | FAYETTEVILLE | FAYETVL AECC | 0 | 506944 | CHAMSPR5 161.00 | 504020 | FARMNGTN 5 161.00 | 0 |  | 1 | 18SP | 294 | 360 | 0 |  | 90.6488 | 102.0435 | [7 empty] | CATEGORYB | SINGLE | CHAMBER SPRINGS - TONTITOWN 345KV CKT 1 | 0 | 506945 | CHAMSPR7 345.00 | 506959 | TONTITN7 345.00 | 0 |  | 1 |  | 368 |  | AEPW | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | Rebuild and reconductor 11.1-mile 161 kV line from Chamber Springs to Farmington REC with 2-959.6 ACSR/TW. Upgrade wavetraps, CT ratios, and relay settings at Chamber Springs. | [53 empty] | 2014-06-01 | 2015-06-01
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T13635518SP | FROM->TO | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | EXP | AEPW | AEPW | FAYETTEVILLE | FAYETVL AECC | 0 | 506944 | CHAMSPR5 161.00 | 504020 | FARMNGTN 5 161.00 | 0 |  | 1 | 18SP | 294 | 360 | 0 |  | 90.6047 | 102.0006 | [7 empty] | CATEGORYB | SINGLE | TONTITOWN () 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 506957 | TONTITN5 161.00 | 506959 | TONTITN7 345.00 | 506958 | TONTITN1 13.800 | 1 |  | 368 |  | AEPW | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | Rebuild and reconductor 11.1-mile 161 kV line from Chamber Springs to Farmington REC with 2-959.6 ACSR/TW. Upgrade wavetraps, CT ratios, and relay settings at Chamber Springs. | [53 empty] | 2014-06-01 | 2015-06-01
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T25518SP | FROM->TO | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | EXP | AEPW | AEPW | FAYETTEVILLE | FAYETVL AECC | 0 | 506944 | CHAMSPR5 161.00 | 504020 | FARMNGTN 5 161.00 | 0 |  | 1 | 18SP | 294 | 360 | 0 |  | 88.062 | 100.289 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  | 362 |  | AEPW | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | Rebuild and reconductor 11.1-mile 161 kV line from Chamber Springs to Farmington REC with 2-959.6 ACSR/TW. Upgrade wavetraps, CT ratios, and relay settings at Chamber Springs. | [53 empty] | 2014-06-01 | 2015-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1425523SP | FROM->TO | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | EXP | AEPW | AEPW | FAYETTEVILLE | FAYETVL AECC | 0 | 506944 | CHAMSPR5 161.00 | 504020 | FARMNGTN 5 161.00 | 0 |  | 1 | 23SP | 294 | 360 | 0 | 99.8 | 99.7792 | 110.612 | [7 empty] | CATEGORYB | SINGLE | CHAMBER SPRINGS - TONTITOWN 345KV CKT 1 | 0 | 506945 | CHAMSPR7 345.00 | 506959 | TONTITN7 345.00 | 0 |  | 1 |  | 399 |  | AEPW | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | Rebuild and reconductor 11.1-mile 161 kV line from Chamber Springs to Farmington REC with 2-959.6 ACSR/TW. Upgrade wavetraps, CT ratios, and relay settings at Chamber Springs. | [53 empty] | 2014-06-01 | 2015-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T15415523SP | FROM->TO | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | EXP | AEPW | AEPW | FAYETTEVILLE | FAYETVL AECC | 0 | 506944 | CHAMSPR5 161.00 | 504020 | FARMNGTN 5 161.00 | 0 |  | 1 | 23SP | 294 | 360 | 0 | 99.7 | 99.6898 | 110.5124 | [7 empty] | CATEGORYB | SINGLE | TONTITOWN () 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 506957 | TONTITN5 161.00 | 506959 | TONTITN7 345.00 | 506958 | TONTITN1 13.800 | 1 |  | 398 |  | AEPW | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | Rebuild and reconductor 11.1-mile 161 kV line from Chamber Springs to Farmington REC with 2-959.6 ACSR/TW. Upgrade wavetraps, CT ratios, and relay settings at Chamber Springs. | [53 empty] | 2014-06-01 | 2015-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T25523SP | FROM->TO | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | EXP | AEPW | AEPW | FAYETTEVILLE | FAYETVL AECC | 0 | 506944 | CHAMSPR5 161.00 | 504020 | FARMNGTN 5 161.00 | 0 |  | 1 | 23SP | 294 | 360 | 0 | 96 | 96.0113 | 107.5534 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  | 388 |  | AEPW | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | Rebuild and reconductor 11.1-mile 161 kV line from Chamber Springs to Farmington REC with 2-959.6 ACSR/TW. Upgrade wavetraps, CT ratios, and relay settings at Chamber Springs. | [53 empty] | 2014-06-01 | 2015-06-01
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1315523SP | FROM->TO | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | EXP | AEPW | AEPW | FAYETTEVILLE | FAYETVL AECC | 0 | 506944 | CHAMSPR5 161.00 | 504020 | FARMNGTN 5 161.00 | 0 |  | 1 | 23SP | 294 | 360 | 0 |  | 94.1121 | 104.3886 | [7 empty] | CATEGORYB | SINGLE | DYESS - SOUTH SPRINGDALE 161KV CKT 1 | 0 | 506927 | DYESS 5 161.00 | 506949 | SOSPRDL5 161.00 | 0 |  | 1 |  | 376 |  | AEPW | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | Rebuild and reconductor 11.1-mile 161 kV line from Chamber Springs to Farmington REC with 2-959.6 ACSR/TW. Upgrade wavetraps, CT ratios, and relay settings at Chamber Springs. | [53 empty] | 2014-06-01 | 2015-06-01
2005-AG2 | [10 empty] | EXPLORER GLENPOOL - EXPLORER GLENPOOL TAP 138KV CKT 1 AEPW | U | AEPW | OKGE |  |  | 0 | 515473 | EXPGLNT4 | 515248 | EXPLGLN4 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | AEPW | EXPLORER GLENPOOL - EXPLORER GLENPOOL TAP 138KV CKT 1 AEPW | Reconductor 1.82 miles with ACCC. Replace wave trap jumpers at Riverside. | [53 empty] | 2009-06-01 | 2009-06-01
2005-AG2 | [10 empty] | EXPLORER GLENPOOL - EXPLORER GLENPOOL TAP 138KV CKT 1 OKGE | U | AEPW | OKGE |  |  | 0 | 515473 | EXPGLNT4 | 515248 | EXPLGLN4 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | OKGE | EXPLORER GLENPOOL - EXPLORER GLENPOOL TAP 138KV CKT 1 OKGE | Reconductor 1.82 miles line with Drake ACCC/TW. | [53 empty] | 2009-06-01 | 2009-06-01
2005-AG2 | [10 empty] | EXPLORER GLENPOOL TAP - RIVERSIDE STATION 138KV CKT 1 AEPW | U | AEPW | OKGE |  |  | 0 | 509783 | R.S.S.-4 138 | 515473 | EXPGLNT4 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | AEPW | EXPLORER GLENPOOL TAP - RIVERSIDE STATION 138KV CKT 1 AEPW | Reconductor 1.82 miles with ACCC. Replace wave trap jumpers at Riverside. | [53 empty] | 2009-06-01 | 2009-06-01
2005-AG2 | [10 empty] | EXPLORER GLENPOOL TAP - RIVERSIDE STATION 138KV CKT 1 OKGE | U | AEPW | OKGE |  |  | 0 | 509783 | R.S.S.-4 138 | 515473 | EXPGLNT4 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | OKGE | EXPLORER GLENPOOL TAP - RIVERSIDE STATION 138KV CKT 1 OKGE | Reconductor 1.82 miles line with Drake ACCC/TW. | [53 empty] | 2009-06-01 | 2009-06-01
GEN-2006-010 | Turk | [9 empty] | MANDEVILTP4 - SE TEXARKANA 138KV CKT 1 | U | AEPW | AEPW | SARK | TEXARK | 0 | 508105 | MANDEVILTP4 | 508078 | SETEXAR4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | AEPW | MANDEVILTP4 - SE TEXARKANA 138KV CKT 1 | Build new Turk-SE Texarkana 138 kV line and add SE Texarkana 138 kV terminal. | [53 empty] | 2012-07-01 | 2012-07-01
GEN-2006-010 | Turk | [9 empty] | MANDEVILTP4 - TURK 138KV CKT 1 | U | AEPW | AEPW | SARK | TEXARK | 0 | 507454 | TURK 4 138.00 | 508105 | MANDEVILTP4 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | AEPW | MANDEVILTP4 - TURK 138KV CKT 1 | Build new Turk-SE Texarkana 138 kV line and add SE Texarkana 138 kV terminal. | [53 empty] | 2012-07-01 | 2012-07-01
GEN-2006-010 | Turk | [9 empty] | MCNAB REC - TURK 115KV CKT 1 | U | AEPW | AEPW | SARK | SARKAECC | 0 | 504122 | MCNAB 3 115.00 | 507456 | HEMPSTD3 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | AEPW | MCNAB REC - TURK 115KV CKT 1 | Build a new two mile, 138 kV, 1590 ACSR line section (operated at 115 kV) from Turk Substation to the existing Okay- Hope 115 kV line to form a Turk - Hope 115 kV line. | [53 empty] | 2012-07-01 | 2012-07-01
GEN-2006-010 | Turk | [9 empty] | OKAY - TURK 138KV CKT 1 | U | AEPW | AEPW | SARK | SARK | 0 | 507454 | HEMPSTD4 138.00 | 507428 | OKAY 4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | AEPW | OKAY - TURK 138KV CKT 1 | Build two mile, 138 kV, 1590ACSR line section from Turk Sub to existing Okay-Hope 115 kV line and rebuild twelve miles of 115 kV line to Okay Sub to 138 kV, 1590 ACSR , to form a Turk-Okay 138 kV line | [53 empty] | 2012-07-01 | 2012-07-01
GEN-2006-010 | Turk | [9 empty] | OKAY 138/69KV TRANSFORMER CKT 1 | U | AEPW | AEPW | SARK | SARK | 1 | 507428 | OKAY 4 138.00 | 507427 | OKAY 2 69.000 | 507442 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | AEPW | OKAY 138/69KV TRANSFORMER CKT 1 | Replace three single-phase 115-69 kV autotransformers with one 90 MVA, three-phase 138-69 kV autotransformer and convert high side of station to 138 kV | [53 empty] | 2012-07-01 | 2012-07-01
GEN-2006-010 | Turk | [9 empty] | SUGAR HILL - TURK 138KV CKT 1 | U | AEPW | AEPW | SARK | TEXARK | 0 | 507454 | HEMPSTD4 138.00 | 508080 | SUGARHL4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | AEPW | SUGAR HILL - TURK 138KV CKT 1 | Build new Turk-Sugar Hill 138 kV line and add Sugar Hill 138 kV terminal. | [53 empty] | 2012-07-01 | 2012-07-01
GEN-2006-010 | Turk | [9 empty] | TURK (HEMP 1) 138/115/13.8KV TRANSFORMER CKT 1 | U | AEPW |  | SARK |  | 1 | 507454 | HEMPSTD4 138.00 | 507456 | HEMPSTD3 115.00 | 507458 | HEMP1 1 13.800 | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | AEPW | TURK (HEMP 1) 138/115/13.8KV TRANSFORMER CKT 1 | Build Turk 138-115 kV station and relocate autotransformer (and spare) from Patterson to this new Turk station | [53 empty] | 2012-07-01 | 2012-07-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5795514WP | FROM->TO | 7OVERTON 345.00 () 345/161/13.8KV TRANSFORMER CKT 1 | S | AMMO | AMMO | AMRNMO | AMRNMO | 2 | 345408 | 7OVERTON 345.00 | 345409 | 5OVERTON 161.00 | 345410 | 1OVERTERT 13.800 | 1 | 14WP | 300 | 300 | 0 | 98.4 | 98.429 | 109.0306 | [7 empty] | CATEGORYB | SINGLE | 7MCCREDIE 345.00 - 7OVERTON 345.00 345KV CKT 1 | 0 | 345088 | 7MCCREDIE 345.00 | 345408 | 7OVERTON 345.00 | 0 |  | 1 |  | 328 |  | AMMO | 7OVERTON 345.00 () 345/161/13.8KV TRANSFORMER CKT 1 | Replace existing 345-161kV transformer with 560MVA unit, install 345kV high side breaker, 161kV XFMR low side breaker and bus to obtain 2000A min | [53 empty] | 2014-10-01 | 2014-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T11475514WP | FROM->TO | 7OVERTON 345.00 () 345/161/13.8KV TRANSFORMER CKT 1 | S | AMMO | AMMO | AMRNMO | AMRNMO | 2 | 345408 | 7OVERTON 345.00 | 345409 | 5OVERTON 161.00 | 345410 | 1OVERTERT 13.800 | 1 | 14WP | 300 | 300 | 0 | 99.2 | 99.2485 | 108.6942 | [7 empty] | CATEGORYB | NONSINGLE | KCPL-MSL#03 | 0 | 0 |  | 0 |  | 0 |  |  |  | 327 |  | AMMO | 7OVERTON 345.00 () 345/161/13.8KV TRANSFORMER CKT 1 | Replace existing 345-161kV transformer with 560MVA unit, install 345kV high side breaker, 161kV XFMR low side breaker and bus to obtain 2000A min | [53 empty] | 2014-10-01 | 2014-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T11765514WP | FROM->TO | 7OVERTON 345.00 () 345/161/13.8KV TRANSFORMER CKT 1 | S | AMMO | AMMO | AMRNMO | AMRNMO | 2 | 345408 | 7OVERTON 345.00 | 345409 | 5OVERTON 161.00 | 345410 | 1OVERTERT 13.800 | 1 | 14WP | 300 | 300 | 0 | 99.2 | 99.2482 | 108.694 | [7 empty] | CATEGORYB | NONSINGLE | MTGY-OVER-5 | 0 | 0 |  | 0 |  | 0 |  |  |  | 327 |  | AMMO | 7OVERTON 345.00 () 345/161/13.8KV TRANSFORMER CKT 1 | Replace existing 345-161kV transformer with 560MVA unit, install 345kV high side breaker, 161kV XFMR low side breaker and bus to obtain 2000A min | [53 empty] | 2014-10-01 | 2014-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T4035523WP | FROM->TO | GRIMES - MT. ZION 138KV CKT 1 | S | EES | EES | ISONE_ME_CMP |  | 0 | 334026 | 4GRIMES% 138.00 | 334060 | 4MT.ZION 138.00 | 0 |  | 1 | 23WP | 206 | 206 | 0 | 105.3 | 105.3076 | 107.9789 | [7 empty] | CATEGORYB | SINGLE | 4BENTWATER 138.00 - GRIMES 138KV CKT 1 | 0 | 334026 | 4GRIMES% 138.00 | 334039 | 4BENTWATER 138.00 | 0 |  | 1 |  | 223 |  | EES | GRIMES - MT. ZION 138KV CKT 1 | Upgrade Transmission Line 19.19 miles | [12 empty] | 14966895 | 2012-01-01 | [39 empty] | 2019-10-01 | 2019-10-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T4115523WP | FROM->TO | GRIMES - MT. ZION 138KV CKT 1 | S | EES | EES | ISONE_ME_CMP |  | 0 | 334026 | 4GRIMES% 138.00 | 334060 | 4MT.ZION 138.00 | 0 |  | 1 | 23WP | 206 | 206 | 0 | 101.9 | 101.8626 | 104.527 | [7 empty] | CATEGORYB | SINGLE | 4BENTWATER 138.00 - WALDEN 138KV CKT 1 | 0 | 334039 | 4BENTWATER 138.00 | 334040 | 4WALDEN 138.00 | 0 |  | 1 |  | 216 |  | EES | GRIMES - MT. ZION 138KV CKT 1 | Upgrade Transmission Line 19.19 miles | [12 empty] | 14966895 | 2012-01-01 | [39 empty] | 2019-10-01 | 2019-10-01
2005-AG2 | 2005-AG2 | [9 empty] | SUB 110 - ORONOGO JCT. - SUB 167 - RIVERTON 161KV CKT 1 | U | EMDE | EMDE |  |  | 0 | 547469 | RIV167 5 161 | 547467 | ORO110 5 161 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | EMDE | SUB 110 - ORONOGO JCT. - SUB 167 - RIVERTON 161KV CKT 1 | Reconductor Oronogo 59467 to Riverton 59469 with Bundled 556 ACSR | [53 empty] | 2011-06-01 | 2011-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T4295513WP | FROM->TO | EASTOWN7 345.00 (EASTOWN 345) 345/161/13.8KV TRANSFORMER CKT 1 | EXP | GMO | GMO |  |  | 2 | 541400 | EASTOWN7 345.00 | 541401 | EASTOWN5 161.00 | 541402 | EASTOWN1 13.800 | 1 | 13WP | 400 | 440 | 440 | 103.3 | 103.3346 | 103.9754 | [7 empty] | CATEGORYB | SINGLE | EASTOWN7 345.00 - ST JOE 345KV CKT 1 | 0 | 541199 | ST JOE 3 345.00 | 541400 | EASTOWN7 345.00 | 0 |  | 1 |  | 458 |  | KACP | IATAN - NASHUA 345KV CKT 1 | Tap Nashua 345kV bus in Hawthorn - St. Joseph 345 kV line. Build new 345 kV line from Iatan to Nashua,Add Nashua 345/161 kV | [53 empty] | 2013-10-01 | 2015-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5595514SP | FROM->TO | EASTOWN7 345.00 (EASTOWN 345) 345/161/13.8KV TRANSFORMER CKT 1 | EXP | GMO | GMO |  |  | 1 | 541400 | EASTOWN7 345.00 | 541401 | EASTOWN5 161.00 | 541402 | EASTOWN1 13.800 | 1 | 14SP | 400 | 440 | 440 | 104.3 | 104.2839 | 105.7129 | [7 empty] | CATEGORYB | SINGLE | EASTOWN7 345.00 - ST JOE 345KV CKT 1 | 0 | 541199 | ST JOE 3 345.00 | 541400 | EASTOWN7 345.00 | 0 |  | 1 |  | 466 |  | KACP | IATAN - NASHUA 345KV CKT 1 | Tap Nashua 345kV bus in Hawthorn - St. Joseph 345 kV line. Build new 345 kV line from Iatan to Nashua,Add Nashua 345/161 kV | [53 empty] | 2013-10-01 | 2015-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3025514WP | FROM->TO | EASTOWN7 345.00 (EASTOWN 345) 345/161/13.8KV TRANSFORMER CKT 1 | EXP | GMO | GMO |  |  | 2 | 541400 | EASTOWN7 345.00 | 541401 | EASTOWN5 161.00 | 541402 | EASTOWN1 13.800 | 1 | 14WP | 400 | 440 | 440 | 111.7 | 111.6626 | 115.412 | [7 empty] | CATEGORYB | SINGLE | EASTOWN7 345.00 - ST JOE 345KV CKT 1 | 0 | 541199 | ST JOE 3 345.00 | 541400 | EASTOWN7 345.00 | 0 |  | 1 |  | 508 |  | KACP | IATAN - NASHUA 345KV CKT 1 | Tap Nashua 345kV bus in Hawthorn - St. Joseph 345 kV line. Build new 345 kV line from Iatan to Nashua,Add Nashua 345/161 kV | [53 empty] | 2013-10-01 | 2015-06-01
2012-AG1 | AFS4 | INVALID | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2735523SP | FROM->TO | 412SUB - KANSAS TAP 161KV CKT 1 | REL | GRDA | GRDA | GRDA-NEO | GRDA | 0 | 512637 | 412SUB 5 161.00 | 512714 | KANSATP5 161.00 | 0 |  | 1 | 23SP | 335 | 335 | 0 | 115.8 | 115.8106 | 120.0399 | [7 empty] | CATEGORYB | SINGLE | GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 | 0 | 512650 | GRDA1 7 345.00 | 512750 | TONECE7 345.00 | 0 |  | 1 |  | 403 |  | GRDA | 412SUB - KANSAS TAP 161KV CKT 1 | Remove limiting Element, Line Switches 1200A increase to 2000A | 356 | 432 | [51 empty] | 2015-06-01 | 2017-06-01
2012-AG1 | AFS4 | INVALID | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1545523WP | FROM->TO | 412SUB - KANSAS TAP 161KV CKT 1 | REL | GRDA | GRDA | GRDA-NEO | GRDA | 0 | 512637 | 412SUB 5 161.00 | 512714 | KANSATP5 161.00 | 0 |  | 1 | 23WP | 335 | 335 | 0 | 104.2 | 104.2186 | 105.5302 | [7 empty] | CATEGORYB | SINGLE | GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 | 0 | 512650 | GRDA1 7 345.00 | 512750 | TONECE7 345.00 | 0 |  | 1 |  | 354 |  | GRDA | 412SUB - KANSAS TAP 161KV CKT 1 | Remove limiting Element, Line Switches 1200A increase to 2000A | 356 | 432 | [51 empty] | 2015-06-01 | 2017-06-01
2012-AG1 | AFS4 | INVALID | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2035518SP | FROM->TO | 412SUB - KANSAS TAP 161KV CKT 1 | REL | GRDA | GRDA | GRDA-NEO | GRDA | 0 | 512637 | 412SUB 5 161.00 | 512714 | KANSATP5 161.00 | 0 |  | 1 | 18SP | 335 | 335 | 0 | 103 | 103.018 | 109.4859 | [7 empty] | CATEGORYB | SINGLE | GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 | 0 | 512650 | GRDA1 7 345.00 | 512750 | TONECE7 345.00 | 0 |  | 1 |  | 367 |  | GRDA | 412SUB - KANSAS TAP 161KV CKT 1 | Remove limiting Element, Line Switches 1200A increase to 2000A | 356 | 432 | [51 empty] | 2015-06-01 | 2017-06-01
2012-AG1 | AFS4 | INVALID | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2025518SP | TO->FROM | 412SUB - KERR 161KV CKT 1 | REL | GRDA | GRDA | GRDA | GRDA-NEO | 0 | 512635 | KERR GR5 161.00 | 512637 | 412SUB 5 161.00 | 0 |  | 1 | 18SP | 335 | 335 | 0 | 104 | 104.0034 | 110.4761 | [7 empty] | CATEGORYB | SINGLE | GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 | 0 | 512650 | GRDA1 7 345.00 | 512750 | TONECE7 345.00 | 0 |  | 1 |  | 371 |  | GRDA | 412SUB - KERR 161KV CKT 1 | Replace 161kV,1200A switch with a 2000A Switch at Kerr Substation bus. | 356 | 432 | [51 empty] | 2015-06-01 | 2017-06-01
2012-AG1 | AFS4 | INVALID | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2725523SP | TO->FROM | 412SUB - KERR 161KV CKT 1 | REL | GRDA | GRDA | GRDA | GRDA-NEO | 0 | 512635 | KERR GR5 161.00 | 512637 | 412SUB 5 161.00 | 0 |  | 1 | 23SP | 335 | 335 | 0 | 117 | 117.0015 | 121.2391 | [7 empty] | CATEGORYB | SINGLE | GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 | 0 | 512650 | GRDA1 7 345.00 | 512750 | TONECE7 345.00 | 0 |  | 1 |  | 407 |  | GRDA | 412SUB - KERR 161KV CKT 1 | Replace 161kV,1200A switch with a 2000A Switch at Kerr Substation bus. | 356 | 432 | [51 empty] | 2015-06-01 | 2017-06-01
2012-AG1 | AFS4 | INVALID | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1535523WP | TO->FROM | 412SUB - KERR 161KV CKT 1 | REL | GRDA | GRDA | GRDA | GRDA-NEO | 0 | 512635 | KERR GR5 161.00 | 512637 | 412SUB 5 161.00 | 0 |  | 1 | 23WP | 335 | 335 | 0 | 104.8 | 104.8223 | 106.1333 | [7 empty] | CATEGORYB | SINGLE | GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 | 0 | 512650 | GRDA1 7 345.00 | 512750 | TONECE7 345.00 | 0 |  | 1 |  | 356 |  | GRDA | 412SUB - KERR 161KV CKT 1 | Replace 161kV,1200A switch with a 2000A Switch at Kerr Substation bus. | 356 | 432 | [51 empty] | 2015-06-01 | 2017-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1475523SP | FROM->TO | GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 | S | GRDA | GRDA | GRDA | GRDA-MUN | 0 | 512650 | GRDA1 7 345.00 | 512750 | TONECE7 345.00 | 0 |  | 1 | 23SP | 1064 | 1064 | 0 | 110.6 | 110.5886 | 116.1753 | [7 empty] | CATEGORYB | SINGLE | CHAMBER SPRINGS - CLARKSVILLE 345KV CKT 1 | 0 | 506945 | CHAMSPR7 345.00 | 509745 | CLARKSV7 345.00 | 0 |  | 1 |  | 1237 |  | GRDA | GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #2 | Replace Terminal Equipment | 1434 | 1616 |  |  |  | 24 | 24 | [5 empty] | 3300000 | 2010-01-01 | [39 empty] | 2019-06-01 | 2019-06-01
2012-AG1 | AFS4 | INVALID | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2055518SP | FROM->TO | KANSAS TAP - WEST SILOAM SPRINGS 161KV CKT 1 | REL | GRDA | GRDA | GRDA | GRDA-NEO | 0 | 512714 | KANSATP5 161.00 | 512642 | SILSPWW5 161.00 | 0 |  | 1 | 18SP | 307 | 307 | 0 | 101.7 | 101.7055 | 108.688 | [7 empty] | CATEGORYB | SINGLE | GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 | 0 | 512650 | GRDA1 7 345.00 | 512750 | TONECE7 345.00 | 0 |  | 1 |  | 334 |  | GRDA | KANSAS TAP - WEST SILOAM SPRINGS 161KV CKT 1 #2 | Replace Terminal Equipment | 347 | 403 | [51 empty] | 2015-06-01 | 2017-06-01
2012-AG1 | AFS4 | INVALID | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2755523SP | FROM->TO | KANSAS TAP - WEST SILOAM SPRINGS 161KV CKT 1 | REL | GRDA | GRDA | GRDA | GRDA-NEO | 0 | 512714 | KANSATP5 161.00 | 512642 | SILSPWW5 161.00 | 0 |  | 1 | 23SP | 307 | 307 | 0 | 116.6 | 116.6275 | 121.2547 | [7 empty] | CATEGORYB | SINGLE | GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 | 0 | 512650 | GRDA1 7 345.00 | 512750 | TONECE7 345.00 | 0 |  | 1 |  | 373 |  | GRDA | KANSAS TAP - WEST SILOAM SPRINGS 161KV CKT 1 #2 | Replace Terminal Equipment | 347 | 403 | [51 empty] | 2015-06-01 | 2017-06-01
2012-AG1 | AFS4 | INVALID | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1565523WP | FROM->TO | KANSAS TAP - WEST SILOAM SPRINGS 161KV CKT 1 | REL | GRDA | GRDA | GRDA | GRDA-NEO | 0 | 512714 | KANSATP5 161.00 | 512642 | SILSPWW5 161.00 | 0 |  | 1 | 23WP | 307 | 307 | 0 | 105.8 | 105.8352 | 106.9833 | [7 empty] | CATEGORYB | SINGLE | GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 | 0 | 512650 | GRDA1 7 345.00 | 512750 | TONECE7 345.00 | 0 |  | 1 |  | 329 |  | GRDA | KANSAS TAP - WEST SILOAM SPRINGS 161KV CKT 1 #2 | Replace Terminal Equipment | 347 | 403 | [51 empty] | 2015-06-01 | 2017-06-01
2012-AG1 | AFS4 | INVALID | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2745523SP | TO->FROM | SILOAM CITY - WEST SILOAM SPRINGS 161KV CKT 1 | REL | GRDA | GRDA | GRDA-NEO | GRDA-MUN | 0 | 512642 | SILSPWW5 161.00 | 512643 | SILMCTY5 161.00 | 0 |  | 1 | 23SP | 307 | 335 | 0 | 105.1 | 105.0688 | 109.2949 | [7 empty] | CATEGORYB | SINGLE | GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 | 0 | 512650 | GRDA1 7 345.00 | 512750 | TONECE7 345.00 | 0 |  | 1 |  | 367 |  | GRDA | SILOAM CITY - WEST SILOAM SPRINGS 161KV CKT 1 #2 | Replace Terminal Equipment | 347 | 403 | [51 empty] | 2019-06-01 | 2019-06-01
NA | [10 empty] | LACYGNE - WEST GARDNER 345KV CKT 1 | U | KACP | KACP |  |  | 0 | 542981 | LACYGNE7 | 542965 | W.GRDNR7 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | KACP | LACYGNE - WEST GARDNER 345KV CKT 1 | KCPL Sponsored Project to Reconductor Line to be In-Service by 6/1/2006 | [53 empty] | 2006-06-01 | 2006-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5955514SP | FROM->TO | CRAIG - LENEXA NORTH 161KV CKT 1 | EXP | KCPL | KCPL | JOCO | JOCO | 0 | 542978 | CRAIG 5 161.00 | 543039 | LENEXAN5 161.00 | 0 |  | 1 | 14SP | 293 | 334 | 0 | 103.6 | 103.5685 | 104.6101 | [7 empty] | CATEGORYB | SINGLE | CEDAR CREEK - GREENWOOD 161KV CKT 1 | 0 | 543031 | SHWNMSN5 161.00 | 543049 | CEDRCRK5 161.00 | 0 |  | 1 |  | 350 |  | KACP | IATAN - NASHUA 345KV CKT 1 | Tap Nashua 345kV bus in Hawthorn - St. Joseph 345 kV line. Build new 345 kV line from Iatan to Nashua,Add Nashua 345/161 kV | [53 empty] | 2013-10-01 | 2015-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2665513WP | TO->FROM | HAYS PLANT - SOUTH HAYS 115KV CKT 1 | EXP | MIDW | MIDW | REG E-IL | REG E-IL | 0 | 530553 | S HAYS 3 115.00 | 530562 | HAYS 3 115.00 | 0 |  | 1 | 13WP | 83 | 99 | 0 | 122 | 122.0301 | 122.3557 | [7 empty] | CATEGORYB | SINGLE | KNOLL 230 - POSTROCK6 230.00 230KV CKT 1 | 0 | 530558 | KNOLL 6 230.00 | 530584 | POSTROCK6 230.00 | 0 |  | 1 |  | 122 |  | MIDW | HAYS PLANT - SOUTH HAYS 115KV CKT 1 #2 | Tear down and rebuild of exisiting South Hays - Hays Plant 115 kV line. Tentative plans include rebuilding on existing right-of-way with the possibility of re-routing a portion of the line to new right-of-way as necessary. | [53 empty] | 2013-10-01 | 2015-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2675513WP | FROM->TO | HAYS PLANT - VINE STREET 115KV CKT 1 | EXP | MIDW | MIDW | REG E-IL | REG E-IL | 0 | 530562 | HAYS 3 115.00 | 530591 | VINE 3 115.00 | 0 |  | 1 | 13WP | 80 | 88 | 0 | 113 | 112.9692 | 113.3316 | [7 empty] | CATEGORYB | SINGLE | KNOLL 230 - POSTROCK6 230.00 230KV CKT 1 | 0 | 530558 | KNOLL 6 230.00 | 530584 | POSTROCK6 230.00 | 0 |  | 1 |  | 100 |  | MIDW | HAYS PLANT - SOUTH HAYS 115KV CKT 1 #2 | Tear down and rebuild of exisiting South Hays - Hays Plant 115 kV line. Tentative plans include rebuilding on existing right-of-way with the possibility of re-routing a portion of the line to new right-of-way as necessary. | [53 empty] | 2013-10-01 | 2015-06-01
GI | [10 empty] | LYONS - RICE_CO 115KV CKT 1 | U | MIDW | WERE |  |  | 0 | 530623 | RICE 3 115.00 | 530620 | LYONS 3 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | MIDW | LYONS - RICE_CO 115KV CKT 1 | Rebuild 11.7 mile line | [53 empty] | 2012-10-01 | 2013-04-01
GI | [10 empty] | RICE_CO 230/115KV TRANSFORMER CKT 1 | U | MIDW | MIDW |  |  | 1 | 530686 | RICECO 230.00 | 530623 | RICE 3 115.00 | 530687 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | MIDW | RICE_CO 230/115KV TRANSFORMER CKT 1 | Add 230/115kV Transformer | [53 empty] | 2012-10-01 | 2012-11-15
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1795513WP | FROM->TO | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | EXP | MIDW | WERE | REG E-IL | WEST | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 13WP | 319 | 319 | 0 | 111.8 | 111.7564 | 111.4204 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 |  | 356 |  |  | Priority Projects | [54 empty] | 2013-10-01 | 2015-01-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2825513WP | FROM->TO | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | EXP | MIDW | WERE | REG E-IL | WEST | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 13WP | 319 | 319 | 0 | 108.4 | 108.4157 | 108.6749 | [7 empty] | CATEGORYB | SINGLE | AXTELL - POST ROCK 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 640065 | AXTELL 3 345.00 | 0 |  | 1 |  | 347 |  |  | Priority Projects | [54 empty] | 2013-10-01 | 2015-01-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3505513WP | FROM->TO | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | EXP | MIDW | WERE | REG E-IL | WEST | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 13WP | 319 | 319 | 0 | 107.6 | 107.622 | 107.3922 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - MULLERGREN 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 539679 | GRTBEND6 230.00 | 0 |  | 1 |  | 343 |  |  | Priority Projects | [54 empty] | 2013-10-01 | 2015-01-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T12295513WP | FROM->TO | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | EXP | MIDW | WERE | REG E-IL | WEST | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 13WP | 319 | 319 | 0 | 101.2 | 101.1658 | 100.6208 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05 | 0 | 0 |  | 0 |  | 0 |  |  |  | 321 |  |  | Priority Projects | [54 empty] | 2013-10-01 | 2015-01-01
2007-AG3 | AFS7 | [9 empty] | ALEXANDER - PRATT 115KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | MKEC | ALEXANDER - PRATT 115KV CKT 1 | Rebuild line | [53 empty] | 2009-12-01 | 2013-06-01
2007-AG3 | AFS7 | [9 empty] | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539651 | RVROAD 115.00 | 539687 | PRATT 3 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | MKEC | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | Rebuild line | [53 empty] | 2009-12-01 | 2013-06-01
2007-AG3 | AFS7 | [9 empty] | BARBER - MEDICINE LODGE 115KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539673 | MED-LDG3 115.00 | 539760 | BARBER 3 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | MKEC | BARBER - MEDICINE LODGE 115KV CKT 1 | Rebuild line | [53 empty] | 2009-12-01 | 2013-06-01
2007-AG3 | AFS7 | [9 empty] | BARBER - SAWYER 115KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539760 | BARBER 3 | 539649 | SAWYER 3 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | MKEC | BARBER - SAWYER 115KV CKT 1 | Rebuild line | [53 empty] | 2009-12-01 | 2013-06-01
2007-AG3 | AFS7 | [9 empty] | BARBER (BARBER 4) 138/115/2.72KV TRANSFORMER CKT 1 | U | MKEC |  |  |  | 2 | 539674 | BARBER 4 | 539760 | BARBER 3 | 539917 | BARBER-T | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | MKEC | BARBER (BARBER 4) 138/115/2.72KV TRANSFORMER CKT 1 | Upgrade transformer | [53 empty] | 2009-12-01 | 2013-06-01
2007-AG3 | AFS7 | [9 empty] | CLIFTON - GREENLEAF 115KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539656 | CLIFTON3 115.00 | 539665 | GRNLEAF3 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | MKEC | CLIFTON - GREENLEAF 115KV CKT 1 | Rebuild 14.4 miles | [53 empty] | 2011-06-01 | 2013-06-01
2007-AG3 | AFS7 | [9 empty] | FLATRDG3 138.00 - MEDICINE LODGE 138KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539674 | MED-LDG4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | MKEC | FLATRDG3 138.00 - MEDICINE LODGE 138KV CKT 1 | Rebuild 8.05 mile line | [53 empty] | 2009-12-01 | 2013-06-01
2007-AG3 | AFS7 | [9 empty] | FLATRDG3 138.00 - HARPER 138KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 |  |  | 24.15 | 24 | 24 | [46 empty] | 2009-12-01 | 2013-06-01
2011-AG3 | [10 empty] | Judson Large - North Judson Large 115KV CKT 2 | U | MKEC | MKEC |  |  | 0 | 539671 |  | 539771 |  |  |  | 2 | [15 empty] | BASECASE | BASE CASE | [11 empty] | MKEC | Judson Large - North Judson Large 115KV CKT 2 | Construct approximately 1 mile of new 115kV for 2nd circuit | [53 empty] | 2013-10-01 | 2015-06-01
2011-AG3 | [10 empty] | North Judson Large - Spearville 115KV CKT 2 | U | MKEC | MKEC |  |  | 0 | 539694 |  | 539771 |  |  |  | 2 | [15 empty] | BASECASE | BASE CASE | [11 empty] | MKEC | North Judson Large - Spearville 115KV CKT 2 | Construct approximately 15 miles of new 115kV for 2nd circuit | [53 empty] | 2013-10-01 | 2015-06-01
2011-AG3 | [10 empty] | Spearville 345/115/13.8kV Transformer CKT 3 | U | MKEC | MKEC |  |  | 1 | 539694 |  | 531469 |  | 560007 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | MKEC | Spearville 345/115/13.8kV Transformer CKT 3 | Install 345/115/13.8kV Transformer CKT 3 at Spearville | [53 empty] | 2013-10-01 | 2015-06-01
GEN | [10 empty] | ALBION - PETERSBURG 115KV CKT 1 | U | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640318 | PETRSBG7 115.00 | 640054 | ALBION 7 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | NPPD | ALBION - PETERSBURG 115KV CKT 1 | Replace Breaker Switch 1106-D and jumpers at Albion. Replace main bus at Petersburg. Upgrade and replace transmission structures on 115 kV lineto facilitate 100 degrees Centigrade line operation. | [53 empty] | 2013-01-01 | 2013-01-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T4785513WP | FROM->TO | BROKEN BOW - LOUP CITY 115KV CKT 1 | REL | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640089 | BROKENB7 115.00 | 640259 | LOUPCTY7 115.00 | 0 |  | 1 | 13WP | 120 | 120 | 127 | 102.7 | 102.732 | 103.2389 | [7 empty] | CATEGORYB | SINGLE | GRAND ISLAND - SWEETWATER 345KV CKT 1 | 0 | 640374 | SWEET W3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 |  | 124 |  | NPPD | Cherry Co - Gentleman 345 kV Ckt1 | Build new 345 kV Transmission Line from GGS 345 kV Substation to a new Cherry County 345 kV Substation (76 miles). | [5 empty] | 72 | 72 | Y | [45 empty] | 2013-10-01 | 2018-01-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3355514WP | FROM->TO | BROKEN BOW - LOUP CITY 115KV CKT 1 | REL | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640089 | BROKENB7 115.00 | 640259 | LOUPCTY7 115.00 | 0 |  | 1 | 14WP | 120 | 120 | 127 | 99.1 | 99.0747 | 103.8938 | [7 empty] | CATEGORYB | SINGLE | GRAND ISLAND - SWEETWATER 345KV CKT 1 | 0 | 640374 | SWEET W3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 |  | 125 |  | NPPD | Cherry Co - Gentleman 345 kV Ckt1 | Build new 345 kV Transmission Line from GGS 345 kV Substation to a new Cherry County 345 kV Substation (76 miles). | [5 empty] | 72 | 72 | Y | [45 empty] | 2013-10-01 | 2018-01-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3275514WP | FROM->TO | BROKEN BOW - LOUP CITY 115KV CKT 1 | REL | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640089 | BROKENB7 115.00 | 640259 | LOUPCTY7 115.00 | 0 |  | 1 | 14WP | 120 | 120 | 127 | 96.6 | 96.6227 | 100.5958 | [7 empty] | CATEGORYB | SINGLE | CROOKED CREEK - RIVERDALE 230KV CKT 1 | 0 | 640093 | C.CREEK4 230.00 | 640330 | RIVERDL4 230.00 | 0 |  | 1 |  | 121 |  | NPPD | Cherry Co - Gentleman 345 kV Ckt1 | Build new 345 kV Transmission Line from GGS 345 kV Substation to a new Cherry County 345 kV Substation (76 miles). | [5 empty] | 72 | 72 | Y | [45 empty] | 2013-10-01 | 2018-01-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T4635513WP | FROM->TO | CANADAY - ELM CREEK 115KV CKT 1 | REL | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640103 | CANADAY7 115.00 | 640161 | ELMCRK_7 115.00 | 0 |  | 1 | 13WP | 80 | 80 | 88 | 100.7 | 100.739 | 101.4677 | [7 empty] | CATEGORYB | SINGLE | CROOKED CREEK - RIVERDALE 230KV CKT 1 | 0 | 640093 | C.CREEK4 230.00 | 640330 | RIVERDL4 230.00 | 0 |  | 1 |  | 82 |  | NPPD | Cherry Co - Gentleman 345 kV Ckt1 | Build new 345 kV Transmission Line from GGS 345 kV Substation to a new Cherry County 345 kV Substation (76 miles). | [5 empty] | 72 | 72 | Y | [45 empty] | 2013-10-01 | 2018-01-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T4585513WP | TO->FROM | GRAND ISLAND - SWEETWATER 345KV CKT 1 | REL | NPPD | NPPD | NPPD_686 | WAPA_1606 | 0 | 640374 | SWEET W3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 | 13WP | 717 | 717 | 789 | 104.7 | 104.6518 | 105.4588 | [7 empty] | CATEGORYB | SINGLE | AXTELL - SWEETWATER 345KV CKT 1 | 0 | 640065 | AXTELL 3 345.00 | 640374 | SWEET W3 345.00 | 0 |  | 1 |  | 757 |  | NPPD | Cherry Co - Gentleman 345 kV Ckt1 | Build new 345 kV Transmission Line from GGS 345 kV Substation to a new Cherry County 345 kV Substation (76 miles). | [5 empty] | 72 | 72 | Y | [45 empty] | 2013-10-01 | 2018-01-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T4575513WP | TO->FROM | GRAND ISLAND - SWEETWATER 345KV CKT 1 | REL | NPPD | NPPD | NPPD_686 | WAPA_1606 | 0 | 640374 | SWEET W3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 | 13WP | 717 | 717 | 789 | 103.4 | 103.439 | 104.4563 | [7 empty] | CATEGORYB | SINGLE | AXTELL - PAULINE 345KV CKT 1 | 0 | 640065 | AXTELL 3 345.00 | 640312 | PAULINE3 345.00 | 0 |  | 1 |  | 749 |  | NPPD | Cherry Co - Gentleman 345 kV Ckt1 | Build new 345 kV Transmission Line from GGS 345 kV Substation to a new Cherry County 345 kV Substation (76 miles). | [5 empty] | 72 | 72 | Y | [45 empty] | 2013-10-01 | 2018-01-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3235514WP | TO->FROM | GRAND ISLAND - SWEETWATER 345KV CKT 1 | REL | NPPD | NPPD | NPPD_686 | WAPA_1606 | 0 | 640374 | SWEET W3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 | 14WP | 717 | 717 | 789 | 101.6 | 101.6032 | 107.0098 | [7 empty] | CATEGORYB | SINGLE | AXTELL - SWEETWATER 345KV CKT 1 | 0 | 640065 | AXTELL 3 345.00 | 640374 | SWEET W3 345.00 | 0 |  | 1 |  | 768 |  | NPPD | Cherry Co - Gentleman 345 kV Ckt1 | Build new 345 kV Transmission Line from GGS 345 kV Substation to a new Cherry County 345 kV Substation (76 miles). | [5 empty] | 72 | 72 | Y | [45 empty] | 2013-10-01 | 2018-01-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3225514WP | TO->FROM | GRAND ISLAND - SWEETWATER 345KV CKT 1 | REL | NPPD | NPPD | NPPD_686 | WAPA_1606 | 0 | 640374 | SWEET W3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 | 14WP | 717 | 717 | 789 | 96.7 | 96.6656 | 105.8824 | [7 empty] | CATEGORYB | SINGLE | AXTELL - PAULINE 345KV CKT 1 | 0 | 640065 | AXTELL 3 345.00 | 640312 | PAULINE3 345.00 | 0 |  | 1 |  | 760 |  | NPPD | Cherry Co - Gentleman 345 kV Ckt1 | Build new 345 kV Transmission Line from GGS 345 kV Substation to a new Cherry County 345 kV Substation (76 miles). | [5 empty] | 72 | 72 | Y | [45 empty] | 2013-10-01 | 2018-01-01
GEN | [10 empty] | NELIGH - PETERSBURG 115KV CKT 1 | U | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640444 |  | 640293 | NELIGH 7 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | NPPD | NELIGH - PETERSBURG 115KV CKT 1 | Replace Breaker 1106, jumpers, and 115 kV Switch 1106-D2 at Neligh. Replace main bus at Petersburg. Upgrade and replace transmission structures on 115 kV lineto facilitate 100 degrees Centigrade line operation. | [53 empty] | 2013-01-01 | 2013-01-01
2005-AG2 | [10 empty] | BEELINE - EXPLORER GLENPOOL TAP 138KV CKT 1 | U | OKGE | OKGE |  |  | 0 | 515473 | EXPGLNT4 | 515247 | BEELINE4 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | OKGE | BEELINE - EXPLORER GLENPOOL TAP 138KV CKT 1 | Reconductor .92miles of line with Drake ACCC/TW. | [53 empty] | 2009-06-01 | 2009-06-01
GEN | [10 empty] | CIMARRON - DRAPER LAKE 345KV CKT 1 | U | OKGE | OKGE |  |  | 0 | 514901 | CIMARON7 345.00 | 514934 | DRAPER 7 345.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | OKGE | CIMARRON - DRAPER LAKE 345KV CKT 1 | Increase capacity of Draper Lake CT and Cimarron wave trap | 956 | 956 | 956 | 956 |  | 16 | 3 | [5 empty] | 150000 | 2012-02-14 | [39 empty] | 2014-10-01 | 2016-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3245523SP | FROM->TO | DIVISION AVE - LAKESIDE 138KV CKT 1 | S | OKGE | OKGE |  |  | 0 | 514853 | DVISION4 138.00 | 514849 | LAKESID4 138.00 | 0 |  | 1 | 23SP | 268 | 308 | 0 | 101.8 | 101.8192 | 103.9355 | [7 empty] | CATEGORYB | SINGLE | MEMORIAL - TENNESSEE TAP 138KV CKT 1 | 0 | 514835 | MEMRIAL4 138.00 | 514837 | TENESTP4 138.00 | 0 |  | 1 |  | 321 |  | OKGE | DIVISION AVE - LAKESIDE 138KV CKT 1 | Rebuild 3.58 mile line with 1590AS52 Conductor | 478 | 478 | 478 | 478 |  | 24 | 6 |  |  |  |  | SCERT estimate | 1720000 | 2013-07-01 | [39 empty] | 2019-06-01 | 2019-06-01
2005-AG2 | [10 empty] | EXPLORER GLENPOOL - EXPLORER GLENPOOL TAP 138KV CKT 1 | U | OKGE | OKGE |  |  | 0 | 515248 | EXPLGLN4 138 | 515473 | EXPGLNT4 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | OKGE | EXPLORER GLENPOOL - EXPLORER GLENPOOL TAP 138KV CKT 1 | Reconductor .92miles of line with Drake ACCC/TW. | [53 empty] | 2009-06-01 | 2009-06-01
2012-AG1 | AFS4-ADD | [5 empty] | 5 | 5 | 2012AG1AFS4ADD1T2005513WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID |  | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 13WP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  |  | Priority Projects | [54 empty] | 2013-10-01 | 2015-01-01
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T16985523SP | FROM->TO | FT SMITH (FTSMITH5) 345/161/13.8KV TRANSFORMER CKT 5 | S | OKGE | OKGE | FT SMITH | FT SMITH | 1 | 515302 | FTSMITH7 345.00 | 515301 | FTSMTHW5 161.00 | 515728 | FTSMTH51 13.800 | 5 | 23SP | 493 | 493 | 0 |  | 87.9851 | 100.0658 | [7 empty] | CATEGORYB | SINGLE | FT SMITH (FTSMITH1) 500/345/13.8KV TRANSFORMER CKT 1 | 1 | 515302 | FTSMITH7 345.00 | 515305 | FTSMITH8 500.00 | 515726 | FTSMTH11 13.800 | 1 |  | 494 |  | OKGE | FT SMITH (FTSMITH1) 500/345/13.8KV TRANSFORMER CKT 1 | Install 2nd 500/345 kV bus tie in Ft. Smith Sub | 600 | 600 | 600 | 600 |  | 36 | 14 | [5 empty] | 14500000 | 2010-07-09 | [39 empty] | 2019-06-01 | 2019-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2655514SP | FROM->TO | HANCOCK - MUSKOGEE 161KV CKT 1 | S | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515250 | HANCOK-5 161.00 | 515222 | MUSKOGE5 161.00 | 0 |  | 1 | 14SP | 223 | 223 | 0 | 96.9 | 96.8865 | 100.0663 | [7 empty] | CATEGORYB | SINGLE | AGENCY - PECAN CREEK 161KV CKT 1 | 0 | 515230 | AGENCY 5 161.00 | 515234 | PECANCK5 161.00 | 0 |  | 1 |  | 224 |  | OKGE | HANCOCK - MUSKOGEE 161KV CKT 1 Accelerate | Upgrade the Muskogee CT rating from 800 amps to 1200 amps | 248 | 310 | 334 | 334 |  | 16 | 3 | [5 empty] | 150000 | 2013-04-02 | [38 empty] | 2019-06-01 | 2014-06-01 | 2016-06-01
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2725518SP | FROM->TO | HANCOCK - MUSKOGEE 161KV CKT 1 | S | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515250 | HANCOK-5 161.00 | 515222 | MUSKOGE5 161.00 | 0 |  | 1 | 18SP | 223 | 223 | 0 |  | 90.9951 | 105.5503 | [7 empty] | CATEGORYB | SINGLE | AGENCY - EUCLID 161KV CKT 1 | 0 | 515230 | AGENCY 5 161.00 | 515251 | EUCLID 5 161.00 | 0 |  | 1 |  | 236 |  | OKGE | HANCOCK - MUSKOGEE 161KV CKT 1 Accelerate | Upgrade the Muskogee CT rating from 800 amps to 1200 amps | 248 | 310 | 334 | 334 |  | 16 | 3 | [5 empty] | 150000 | 2013-04-02 | [38 empty] | 2019-06-01 | 2014-06-01 | 2016-06-01
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2705518SP | FROM->TO | HANCOCK - MUSKOGEE 161KV CKT 1 | S | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515250 | HANCOK-5 161.00 | 515222 | MUSKOGE5 161.00 | 0 |  | 1 | 18SP | 223 | 223 | 0 |  | 91.6499 | 104.4915 | [7 empty] | CATEGORYB | SINGLE | AGENCY - PECAN CREEK 161KV CKT 1 | 0 | 515230 | AGENCY 5 161.00 | 515234 | PECANCK5 161.00 | 0 |  | 1 |  | 234 |  | OKGE | HANCOCK - MUSKOGEE 161KV CKT 1 Accelerate | Upgrade the Muskogee CT rating from 800 amps to 1200 amps | 248 | 310 | 334 | 334 |  | 16 | 3 | [5 empty] | 150000 | 2013-04-02 | [38 empty] | 2019-06-01 | 2014-06-01 | 2016-06-01
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2745518SP | FROM->TO | HANCOCK - MUSKOGEE 161KV CKT 1 | S | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515250 | HANCOK-5 161.00 | 515222 | MUSKOGE5 161.00 | 0 |  | 1 | 18SP | 223 | 223 | 0 |  | 85.818 | 100.3818 | [7 empty] | CATEGORYB | SINGLE | EUCLID - MUSKOGEE PORT 161KV CKT 1 | 0 | 515232 | MSKPTAP5 161.00 | 515251 | EUCLID 5 161.00 | 0 |  | 1 |  | 224 |  | OKGE | HANCOCK - MUSKOGEE 161KV CKT 1 Accelerate | Upgrade the Muskogee CT rating from 800 amps to 1200 amps | 248 | 310 | 334 | 334 |  | 16 | 3 | [5 empty] | 150000 | 2013-04-02 | [38 empty] | 2019-06-01 | 2014-06-01 | 2016-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3515523SP | FROM->TO | HANCOCK - MUSKOGEE 161KV CKT 1 | S | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515250 | HANCOK-5 161.00 | 515222 | MUSKOGE5 161.00 | 0 |  | 1 | 23SP | 223 | 223 | 0 | 105.3 | 105.334 | 114.5013 | [7 empty] | CATEGORYB | SINGLE | AGENCY - EUCLID 161KV CKT 1 | 0 | 515230 | AGENCY 5 161.00 | 515251 | EUCLID 5 161.00 | 0 |  | 1 |  | 256 |  | OKGE | HANCOCK - MUSKOGEE 161KV CKT 1 Accelerate | Upgrade the Muskogee CT rating from 800 amps to 1200 amps | 248 | 310 | 334 | 334 |  | 16 | 3 | [5 empty] | 150000 | 2013-04-02 | [38 empty] | 2019-06-01 | 2014-06-01 | 2016-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3495523SP | FROM->TO | HANCOCK - MUSKOGEE 161KV CKT 1 | S | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515250 | HANCOK-5 161.00 | 515222 | MUSKOGE5 161.00 | 0 |  | 1 | 23SP | 223 | 223 | 0 | 104.2 | 104.2428 | 112.5776 | [7 empty] | CATEGORYB | SINGLE | AGENCY - PECAN CREEK 161KV CKT 1 | 0 | 515230 | AGENCY 5 161.00 | 515234 | PECANCK5 161.00 | 0 |  | 1 |  | 252 |  | OKGE | HANCOCK - MUSKOGEE 161KV CKT 1 Accelerate | Upgrade the Muskogee CT rating from 800 amps to 1200 amps | 248 | 310 | 334 | 334 |  | 16 | 3 | [5 empty] | 150000 | 2013-04-02 | [38 empty] | 2019-06-01 | 2014-06-01 | 2016-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3535523SP | FROM->TO | HANCOCK - MUSKOGEE 161KV CKT 1 | S | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515250 | HANCOK-5 161.00 | 515222 | MUSKOGE5 161.00 | 0 |  | 1 | 23SP | 223 | 223 | 0 | 99.6 | 99.5966 | 108.7757 | [7 empty] | CATEGORYB | SINGLE | EUCLID - MUSKOGEE PORT 161KV CKT 1 | 0 | 515232 | MSKPTAP5 161.00 | 515251 | EUCLID 5 161.00 | 0 |  | 1 |  | 243 |  | OKGE | HANCOCK - MUSKOGEE 161KV CKT 1 Accelerate | Upgrade the Muskogee CT rating from 800 amps to 1200 amps | 248 | 310 | 334 | 334 |  | 16 | 3 | [5 empty] | 150000 | 2013-04-02 | [38 empty] | 2019-06-01 | 2014-06-01 | 2016-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3255523SP | FROM->TO | HEFNER - TULSA 138KV CKT 1 | S | OKGE | OKGE |  |  | 0 | 514848 | HEFNER 4 138.00 | 514847 | TULSA 4 138.00 | 0 |  | 1 | 23SP | 194 | 222 | 0 | 98.3 | 98.325 | 101.3612 | [7 empty] | CATEGORYB | SINGLE | 84TH ST - TENNESSEE TAP 138KV CKT 1 | 0 | 514837 | TENESTP4 138.00 | 514843 | 84TH ST4 138.00 | 0 |  | 1 |  | 226 |  | OKGE | HEFNER - TULSA 138KV CKT 1 | Reconductor 1.25 miles of line to 1590AS52 | 404 | 465 | 478 | 478 | 1.25 | 26 | 6 |  | 0.00043 | 0.00487 | 0.00141 |  | 750000 | 2012-06-19 | [39 empty] | 2019-06-01 | 2019-06-01
2006-AG1 | 2006-AG1 | [9 empty] | KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1 | U | OKGE |  |  |  | 1 | 514795 | KNOBHIL4 138 | 514794 | KNOBHIL269.0 | 515732 | KNOBHIL113.2 | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | OKGE | KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1 | Replace bus tie with 100MVA transformer | [53 empty] | 2006-06-01 | 2008-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2635514SP | TO->FROM | MUSKOGEE - MUSKOGEE PORT 161KV CKT 1 | S | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515232 | MSKPTAP5 161.00 | 515222 | MUSKOGE5 161.00 | 0 |  | 1 | 14SP | 223 | 223 | 0 | 98.7 | 98.7272 | 101.9013 | [7 empty] | CATEGORYB | SINGLE | 5 TRIBES - PECAN CREEK 161KV CKT 1 | 0 | 515228 | 5TRIBES5 161.00 | 515234 | PECANCK5 161.00 | 0 |  | 1 |  | 228 |  | OKGE | MUSKOGEE - MUSKOGEE PORT 161KV CKT 1 Accelerate | Upgrade the Muskogee CT rating from 800 amps to 1200 amps | 248 | 310 | 334 | 334 |  | 16 | 3 | [5 empty] | 50000 | 2013-02-11 | [38 empty] | 2019-06-01 | 2014-06-01 | 2016-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2645514SP | TO->FROM | MUSKOGEE - MUSKOGEE PORT 161KV CKT 1 | S | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515232 | MSKPTAP5 161.00 | 515222 | MUSKOGE5 161.00 | 0 |  | 1 | 14SP | 223 | 223 | 0 | 97.2 | 97.1627 | 100.7041 | [7 empty] | CATEGORYB | SINGLE | 5 TRIBES - HANCOCK 161KV CKT 1 | 0 | 515228 | 5TRIBES5 161.00 | 515250 | HANCOK-5 161.00 | 0 |  | 1 |  | 225 |  | OKGE | MUSKOGEE - MUSKOGEE PORT 161KV CKT 1 Accelerate | Upgrade the Muskogee CT rating from 800 amps to 1200 amps | 248 | 310 | 334 | 334 |  | 16 | 3 | [5 empty] | 50000 | 2013-02-11 | [38 empty] | 2019-06-01 | 2014-06-01 | 2016-06-01
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2685518SP | TO->FROM | MUSKOGEE - MUSKOGEE PORT 161KV CKT 1 | S | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515232 | MSKPTAP5 161.00 | 515222 | MUSKOGE5 161.00 | 0 |  | 1 | 18SP | 223 | 223 | 0 |  | 92.4214 | 105.2933 | [7 empty] | CATEGORYB | SINGLE | 5 TRIBES - PECAN CREEK 161KV CKT 1 | 0 | 515228 | 5TRIBES5 161.00 | 515234 | PECANCK5 161.00 | 0 |  | 1 |  | 235 |  | OKGE | MUSKOGEE - MUSKOGEE PORT 161KV CKT 1 Accelerate | Upgrade the Muskogee CT rating from 800 amps to 1200 amps | 248 | 310 | 334 | 334 |  | 16 | 3 | [5 empty] | 50000 | 2013-02-11 | [38 empty] | 2019-06-01 | 2014-06-01 | 2016-06-01
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2695518SP | TO->FROM | MUSKOGEE - MUSKOGEE PORT 161KV CKT 1 | S | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515232 | MSKPTAP5 161.00 | 515222 | MUSKOGE5 161.00 | 0 |  | 1 | 18SP | 223 | 223 | 0 |  | 91.0804 | 105.2889 | [7 empty] | CATEGORYB | SINGLE | 5 TRIBES - HANCOCK 161KV CKT 1 | 0 | 515228 | 5TRIBES5 161.00 | 515250 | HANCOK-5 161.00 | 0 |  | 1 |  | 235 |  | OKGE | MUSKOGEE - MUSKOGEE PORT 161KV CKT 1 Accelerate | Upgrade the Muskogee CT rating from 800 amps to 1200 amps | 248 | 310 | 334 | 334 |  | 16 | 3 | [5 empty] | 50000 | 2013-02-11 | [38 empty] | 2019-06-01 | 2014-06-01 | 2016-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3485523SP | TO->FROM | MUSKOGEE - MUSKOGEE PORT 161KV CKT 1 | S | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515232 | MSKPTAP5 161.00 | 515222 | MUSKOGE5 161.00 | 0 |  | 1 | 23SP | 223 | 223 | 0 | 104.5 | 104.5044 | 113.4111 | [7 empty] | CATEGORYB | SINGLE | 5 TRIBES - HANCOCK 161KV CKT 1 | 0 | 515228 | 5TRIBES5 161.00 | 515250 | HANCOK-5 161.00 | 0 |  | 1 |  | 253 |  | OKGE | MUSKOGEE - MUSKOGEE PORT 161KV CKT 1 Accelerate | Upgrade the Muskogee CT rating from 800 amps to 1200 amps | 248 | 310 | 334 | 334 |  | 16 | 3 | [5 empty] | 50000 | 2013-02-11 | [38 empty] | 2019-06-01 | 2014-06-01 | 2016-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3465523SP | TO->FROM | MUSKOGEE - MUSKOGEE PORT 161KV CKT 1 | S | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515232 | MSKPTAP5 161.00 | 515222 | MUSKOGE5 161.00 | 0 |  | 1 | 23SP | 223 | 223 | 0 | 104.4 | 104.4152 | 112.5927 | [7 empty] | CATEGORYB | SINGLE | 5 TRIBES - PECAN CREEK 161KV CKT 1 | 0 | 515228 | 5TRIBES5 161.00 | 515234 | PECANCK5 161.00 | 0 |  | 1 |  | 252 |  | OKGE | MUSKOGEE - MUSKOGEE PORT 161KV CKT 1 Accelerate | Upgrade the Muskogee CT rating from 800 amps to 1200 amps | 248 | 310 | 334 | 334 |  | 16 | 3 | [5 empty] | 50000 | 2013-02-11 | [38 empty] | 2019-06-01 | 2014-06-01 | 2016-06-01
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3385523SP | TO->FROM | MUSKOGEE - MUSKOGEE PORT 161KV CKT 1 | S | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515232 | MSKPTAP5 161.00 | 515222 | MUSKOGE5 161.00 | 0 |  | 1 | 23SP | 223 | 223 | 0 |  | 94.1612 | 103.061 | [7 empty] | CATEGORYB | SINGLE | HANCOCK - MUSKOGEE 161KV CKT 1 | 0 | 515222 | MUSKOGE5 161.00 | 515250 | HANCOK-5 161.00 | 0 |  | 1 |  | 230 |  | OKGE | MUSKOGEE - MUSKOGEE PORT 161KV CKT 1 Accelerate | Upgrade the Muskogee CT rating from 800 amps to 1200 amps | 248 | 310 | 334 | 334 |  | 16 | 3 | [5 empty] | 50000 | 2013-02-11 | [38 empty] | 2019-06-01 | 2014-06-01 | 2016-06-01
NA | [10 empty] | NORTHWEST - TATONGA 345KV CKT 1 | U | OKGE | OKGE | ENID | ENID | 0 | 515407 |  | 514880 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | OKGE | NORTHWEST - TATONGA 345KV CKT 1 | Build 345 kV line | [53 empty] | 2010-01-01 | 2010-01-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T7845513WP | FROM->TO | NORTHWEST (NORTWST2) 345/138/13.8KV TRANSFORMER CKT 1 | CP | OKGE | OKGE |  |  | 2 | 514880 | NORTWST7 345.00 | 514879 | NORTWST4 138.00 | 515742 | NORTWS21 13.800 | 1 | 13WP | 493 | 493 | 0 | 106.9 | 106.8558 | 108.5255 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST (NORTWST3) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514879 | NORTWST4 138.00 | 514880 | NORTWST7 345.00 | 515743 | NORTWS31 13.800 | 1 |  | 536 |  | OKGE | NORTHWEST 345/138/13.8KV TRANSFORMER CKT 3 Accelerated | Install third 345/138 kV Bus Tie in Northwest Sub | [5 empty] | 40 | 40 | [46 empty] | 2013-10-01 | 2015-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T12455514SP | FROM->TO | NORTHWEST (NORTWST2) 345/138/13.8KV TRANSFORMER CKT 1 | CP | OKGE | OKGE |  |  | 2 | 514880 | NORTWST7 345.00 | 514879 | NORTWST4 138.00 | 515742 | NORTWS21 13.800 | 1 | 14SP | 493 | 493 | 0 | 109.1 | 109.1075 | 112.2658 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST (NORTWST3) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514879 | NORTWST4 138.00 | 514880 | NORTWST7 345.00 | 515743 | NORTWS31 13.800 | 1 |  | 554 |  | OKGE | NORTHWEST 345/138/13.8KV TRANSFORMER CKT 3 Accelerated | Install third 345/138 kV Bus Tie in Northwest Sub | [5 empty] | 40 | 40 | [46 empty] | 2013-10-01 | 2015-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T7125514WP | FROM->TO | NORTHWEST (NORTWST2) 345/138/13.8KV TRANSFORMER CKT 1 | CP | OKGE | OKGE |  |  | 2 | 514880 | NORTWST7 345.00 | 514879 | NORTWST4 138.00 | 515742 | NORTWS21 13.800 | 1 | 14WP | 493 | 493 | 0 | 108.3 | 108.2549 | 111.8916 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST (NORTWST3) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514879 | NORTWST4 138.00 | 514880 | NORTWST7 345.00 | 515743 | NORTWS31 13.800 | 1 |  | 552 |  | OKGE | NORTHWEST 345/138/13.8KV TRANSFORMER CKT 3 Accelerated | Install third 345/138 kV Bus Tie in Northwest Sub | [5 empty] | 40 | 40 | [46 empty] | 2013-10-01 | 2015-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T12435514SP | FROM->TO | NORTHWEST (NORTWST3) 345/138/13.8KV TRANSFORMER CKT 1 | CP | OKGE | OKGE |  |  | 2 | 514880 | NORTWST7 345.00 | 514879 | NORTWST4 138.00 | 515743 | NORTWS31 13.800 | 1 | 14SP | 493 | 493 | 0 | 100 | 100.0124 | 102.9272 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST (NORTWST2) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514879 | NORTWST4 138.00 | 514880 | NORTWST7 345.00 | 515742 | NORTWS21 13.800 | 1 |  | 508 |  | OKGE | NORTHWEST 345/138/13.8KV TRANSFORMER CKT 3 Accelerated | Install third 345/138 kV Bus Tie in Northwest Sub | [5 empty] | 40 | 40 | [46 empty] | 2013-10-01 | 2015-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T7105514WP | FROM->TO | NORTHWEST (NORTWST3) 345/138/13.8KV TRANSFORMER CKT 1 | CP | OKGE | OKGE |  |  | 2 | 514880 | NORTWST7 345.00 | 514879 | NORTWST4 138.00 | 515743 | NORTWS31 13.800 | 1 | 14WP | 493 | 493 | 0 | 99.1 | 99.1389 | 102.4856 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST (NORTWST2) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514879 | NORTWST4 138.00 | 514880 | NORTWST7 345.00 | 515742 | NORTWS21 13.800 | 1 |  | 506 |  | OKGE | NORTHWEST 345/138/13.8KV TRANSFORMER CKT 3 Accelerated | Install third 345/138 kV Bus Tie in Northwest Sub | [5 empty] | 40 | 40 | [46 empty] | 2013-10-01 | 2015-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T16975523SP | FROM->TO | PECAN CREEK (PECANCK1) 345/161/13.8KV TRANSFORMER CKT 1 | S | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 2 | 515235 | PECANCK7 345.00 | 515234 | PECANCK5 161.00 | 515749 | PECANC11 13.800 | 1 | 23SP | 370 | 370 | 0 | 96 | 96.0012 | 101.6147 | [7 empty] | CATEGORYB | SINGLE | PECAN CREEK (PECANCK1) 345/161/13.8KV TRANSFORMER CKT 2 | 1 | 515234 | PECANCK5 161.00 | 515235 | PECANCK7 345.00 | 515759 | PECANC21 13.800 | 2 |  | 376 |  | OKGE | PECAN CREEK (PECANCK1) 345/161/13.8KV TRANSFORMER CKT 1 | Replace Transformer | [12 empty] | 5500000 | 2010-01-01 | [39 empty] | 2019-06-01 | 2019-06-01
2012-AG1 | AFS4-ADD | [5 empty] | 5 | 5 | 2012AG1AFS4ADD1T2035513WP | TO->FROM | ROMAN NOSE - SOUTHARD 138KV CKT 1 | EXP | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 138.00 | 514823 | ROMNOSE4 138.00 | 0 |  | 1 | 13WP | 133 | 153 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  |  | Priority Projects | [54 empty] | 2013-10-01 | 2015-01-01
NA | [10 empty] | TATONGA - WOODWARD 345KV CKT 1 | U | OKGE | OKGE | ENID | ENID | 0 | 515407 |  | 515375 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | OKGE | TATONGA - WOODWARD 345KV CKT 1 | Build 345 kV line | [53 empty] | 2010-01-01 | 2010-01-01
NA | [10 empty] | WOODWARD - IODINE 138KV CKT 1 | U | OKGE | OKGE | ENID | ENID | 0 | 515376 |  | 514796 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | OKGE | WOODWARD - IODINE 138KV CKT 1 | Tap Iodine to Woodward 138 kV line | [53 empty] | 2010-01-01 | 2010-01-01
NA | [10 empty] | WOODWARD - WOODWARD EHV 138KV CKT 1 | U | OKGE | OKGE | ENID | ENID | 0 | 515376 |  | 514785 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | OKGE | WOODWARD - WOODWARD EHV 138KV CKT 1 | Build .5 miles of 138 kV and install terminal equipment | [53 empty] | 2010-01-01 | 2010-01-01
NA | [10 empty] | WOODWARD - WOODWARD EHV 138KV CKT 2 | U | OKGE | OKGE | ENID | ENID | 0 | 515376 |  | 514785 |  |  |  | 2 | [15 empty] | BASECASE | BASE CASE | [11 empty] | OKGE | WOODWARD - WOODWARD EHV 138KV CKT 2 | Build .5 miles of 138 kV and install terminal equipment | [53 empty] | 2010-01-01 | 2010-01-01
NA | [10 empty] | WOODWARD 345/138KV TRANSFORMER CKT 1 | U | OKGE | OKGE | ENID | ENID | 1 | 515375 |  | 515376 |  | 515795 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | OKGE | WOODWARD 345/138KV TRANSFORMER CKT 1 | Install 345/138 kV XF | [53 empty] | 2010-01-01 | 2010-01-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2095513WP | FROM->TO | AMARILLO SOUTH INTERCHANGE - SWISHER COUNTY INTERCHANGE 230KV CKT 1 | CP | SPS | SPS | SPS-AMA | SPS-CNPL | 0 | 524415 | AMA_SOUTH 6230.00 | 525213 | SWISHER 6230.00 | 0 |  | 1 | 13WP | 329 | 361 | 0 | 106.5 | 106.52 | 113.5133 | [7 empty] | CATEGORYB | SINGLE | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 |  | 410 |  | SPS | Potter to Tolk 345 kV | Build 111 mile 345 kV line from Potter to Tolk. Further study analysis will be performed with regard to the SPS North-South Stability Limit to determine whether its rating may be increased based on approved SPP Expansion Plan Network Upgrades scheduled to be placed in service. Pending this analysis, the Potter – Tolk 345 kV Service Upgrade requirement will be re-evaluated. |  |  |  |  | 130 | [6 empty] | SCERT Estimate | 168852765 | 2013-07-05 | [39 empty] | 2013-10-01 | 2018-12-31
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2035513WP | FROM->TO | AMARILLO SOUTH INTERCHANGE - SWISHER COUNTY INTERCHANGE 230KV CKT 1 | CP | SPS | SPS | SPS-AMA | SPS-CNPL | 0 | 524415 | AMA_SOUTH 6230.00 | 525213 | SWISHER 6230.00 | 0 |  | 1 | 13WP | 329 | 361 | 0 | 101 | 101.0454 | 107.9085 | [7 empty] | CATEGORYB | SINGLE | PLANT X STATION - POTTER COUNTY INTERCHANGE 230KV CKT 1 | 0 | 523959 | POTTER_CO 6230.00 | 525481 | PLANT_X 6230.00 | 0 |  | 1 |  | 390 |  | SPS | Potter to Tolk 345 kV | Build 111 mile 345 kV line from Potter to Tolk. Further study analysis will be performed with regard to the SPS North-South Stability Limit to determine whether its rating may be increased based on approved SPP Expansion Plan Network Upgrades scheduled to be placed in service. Pending this analysis, the Potter – Tolk 345 kV Service Upgrade requirement will be re-evaluated. |  |  |  |  | 130 | [6 empty] | SCERT Estimate | 168852765 | 2013-07-05 | [39 empty] | 2013-10-01 | 2018-12-31
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T12445513WP | FROM->TO | AMARILLO SOUTH INTERCHANGE - SWISHER COUNTY INTERCHANGE 230KV CKT 1 | CP | SPS | SPS | SPS-AMA | SPS-CNPL | 0 | 524415 | AMA_SOUTH 6230.00 | 525213 | SWISHER 6230.00 | 0 |  | 1 | 13WP | 329 | 361 | 0 | 99.9 | 99.9208 | 106.7982 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-T66 | 0 | 0 |  | 0 |  | 0 |  |  |  | 386 |  | SPS | Potter to Tolk 345 kV | Build 111 mile 345 kV line from Potter to Tolk. Further study analysis will be performed with regard to the SPS North-South Stability Limit to determine whether its rating may be increased based on approved SPP Expansion Plan Network Upgrades scheduled to be placed in service. Pending this analysis, the Potter – Tolk 345 kV Service Upgrade requirement will be re-evaluated. |  |  |  |  | 130 | [6 empty] | SCERT Estimate | 168852765 | 2013-07-05 | [39 empty] | 2013-10-01 | 2018-12-31
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T12465513WP | FROM->TO | AMARILLO SOUTH INTERCHANGE - SWISHER COUNTY INTERCHANGE 230KV CKT 1 | CP | SPS | SPS | SPS-AMA | SPS-CNPL | 0 | 524415 | AMA_SOUTH 6230.00 | 525213 | SWISHER 6230.00 | 0 |  | 1 | 13WP | 329 | 361 | 0 | 98 | 97.9779 | 104.885 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-T67 | 0 | 0 |  | 0 |  | 0 |  |  |  | 379 |  | SPS | Potter to Tolk 345 kV | Build 111 mile 345 kV line from Potter to Tolk. Further study analysis will be performed with regard to the SPS North-South Stability Limit to determine whether its rating may be increased based on approved SPP Expansion Plan Network Upgrades scheduled to be placed in service. Pending this analysis, the Potter – Tolk 345 kV Service Upgrade requirement will be re-evaluated. |  |  |  |  | 130 | [6 empty] | SCERT Estimate | 168852765 | 2013-07-05 | [39 empty] | 2013-10-01 | 2018-12-31
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T75513WP | FROM->TO | AMARILLO SOUTH INTERCHANGE - SWISHER COUNTY INTERCHANGE 230KV CKT 1 | CP | SPS | SPS | SPS-AMA | SPS-CNPL | 0 | 524415 | AMA_SOUTH 6230.00 | 525213 | SWISHER 6230.00 | 0 |  | 1 | 13WP | 329 | 361 | 0 | 96.6 | 96.5586 | 103.1719 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  | 373 |  | SPS | Potter to Tolk 345 kV | Build 111 mile 345 kV line from Potter to Tolk. Further study analysis will be performed with regard to the SPS North-South Stability Limit to determine whether its rating may be increased based on approved SPP Expansion Plan Network Upgrades scheduled to be placed in service. Pending this analysis, the Potter – Tolk 345 kV Service Upgrade requirement will be re-evaluated. |  |  |  |  | 130 | [6 empty] | SCERT Estimate | 168852765 | 2013-07-05 | [39 empty] | 2013-10-01 | 2018-12-31
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1325514WP | FROM->TO | AMARILLO SOUTH INTERCHANGE - SWISHER COUNTY INTERCHANGE 230KV CKT 1 | CP | SPS | SPS | SPS-AMA | SPS-CNPL | 0 | 524415 | AMA_SOUTH 6230.00 | 525213 | SWISHER 6230.00 | 0 |  | 1 | 14WP | 329 | 361 | 0 |  | 91.349 | 100.1338 | [7 empty] | CATEGORYB | SINGLE | BORDER 7345.00 - TUCO INTERCHANGE 345KV CKT 1 | 0 | 515458 | BORDER 7345.00 | 525832 | TUCO_INT 7345.00 | 0 |  | 1 |  | 362 |  | SPS | Potter to Tolk 345 kV | Build 111 mile 345 kV line from Potter to Tolk. Further study analysis will be performed with regard to the SPS North-South Stability Limit to determine whether its rating may be increased based on approved SPP Expansion Plan Network Upgrades scheduled to be placed in service. Pending this analysis, the Potter – Tolk 345 kV Service Upgrade requirement will be re-evaluated. |  |  |  |  | 130 | [6 empty] | SCERT Estimate | 168852765 | 2013-07-05 | [39 empty] | 2013-10-01 | 2018-12-31
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1295514WP | FROM->TO | AMARILLO SOUTH INTERCHANGE - SWISHER COUNTY INTERCHANGE 230KV CKT 1 | CP | SPS | SPS | SPS-AMA | SPS-CNPL | 0 | 524415 | AMA_SOUTH 6230.00 | 525213 | SWISHER 6230.00 | 0 |  | 1 | 14WP | 329 | 361 | 0 |  | 91.3526 | 100.1195 | [7 empty] | CATEGORYB | SINGLE | BORDER 7345.00 - WOODWARD DISTRICT EHV 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515458 | BORDER 7345.00 | 0 |  | 1 |  | 362 |  | SPS | Potter to Tolk 345 kV | Build 111 mile 345 kV line from Potter to Tolk. Further study analysis will be performed with regard to the SPS North-South Stability Limit to determine whether its rating may be increased based on approved SPP Expansion Plan Network Upgrades scheduled to be placed in service. Pending this analysis, the Potter – Tolk 345 kV Service Upgrade requirement will be re-evaluated. |  |  |  |  | 130 | [6 empty] | SCERT Estimate | 168852765 | 2013-07-05 | [39 empty] | 2013-10-01 | 2018-12-31
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T13215513WP | FROM->TO | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | CP | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | 13WP | 329 | 360 | 0 | 121.2 | 121.183 | 127.0594 | [7 empty] | CATEGORYB | GENOUT | GEN525562 1-TOLK GEN #2 24 KV | 0 | 0 |  | 0 |  | 0 |  |  |  | 458 |  | SPS | Potter to Tolk 345 kV | Build 111 mile 345 kV line from Potter to Tolk. Further study analysis will be performed with regard to the SPS North-South Stability Limit to determine whether its rating may be increased based on approved SPP Expansion Plan Network Upgrades scheduled to be placed in service. Pending this analysis, the Potter – Tolk 345 kV Service Upgrade requirement will be re-evaluated. |  |  |  |  | 130 | [6 empty] | SCERT Estimate | 168852765 | 2013-07-05 | [39 empty] | 2013-10-01 | 2018-12-31
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T13165513WP | FROM->TO | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | CP | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | 13WP | 329 | 360 | 0 | 116.6 | 116.6904 | 122.2011 | [7 empty] | CATEGORYB | GENOUT | GEN525561 1-TOLK GEN #1 24 KV | 0 | 0 |  | 0 |  | 0 |  |  |  | 440 |  | SPS | Potter to Tolk 345 kV | Build 111 mile 345 kV line from Potter to Tolk. Further study analysis will be performed with regard to the SPS North-South Stability Limit to determine whether its rating may be increased based on approved SPP Expansion Plan Network Upgrades scheduled to be placed in service. Pending this analysis, the Potter – Tolk 345 kV Service Upgrade requirement will be re-evaluated. |  |  |  |  | 130 | [6 empty] | SCERT Estimate | 168852765 | 2013-07-05 | [39 empty] | 2013-10-01 | 2018-12-31
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2025513WP | FROM->TO | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | CP | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | 13WP | 329 | 360 | 0 | 109.6 | 109.5591 | 116.2451 | [7 empty] | CATEGORYB | SINGLE | PLANT X STATION - POTTER COUNTY INTERCHANGE 230KV CKT 1 | 0 | 523959 | POTTER_CO 6230.00 | 525481 | PLANT_X 6230.00 | 0 |  | 1 |  | 419 |  | SPS | Potter to Tolk 345 kV | Build 111 mile 345 kV line from Potter to Tolk. Further study analysis will be performed with regard to the SPS North-South Stability Limit to determine whether its rating may be increased based on approved SPP Expansion Plan Network Upgrades scheduled to be placed in service. Pending this analysis, the Potter – Tolk 345 kV Service Upgrade requirement will be re-evaluated. |  |  |  |  | 130 | [6 empty] | SCERT Estimate | 168852765 | 2013-07-05 | [39 empty] | 2013-10-01 | 2018-12-31
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T20035514SP | FROM->TO | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | CP | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | 14SP | 319 | 351 | 0 | 96.6 | 96.5843 | 100.08 | [7 empty] | CATEGORYB | GENOUT | GEN525562 1-TOLK GEN #2 24 KV | 0 | 0 |  | 0 |  | 0 |  |  |  | 352 |  | SPS | Potter to Tolk 345 kV | Build 111 mile 345 kV line from Potter to Tolk. Further study analysis will be performed with regard to the SPS North-South Stability Limit to determine whether its rating may be increased based on approved SPP Expansion Plan Network Upgrades scheduled to be placed in service. Pending this analysis, the Potter – Tolk 345 kV Service Upgrade requirement will be re-evaluated. |  |  |  |  | 130 | [6 empty] | SCERT Estimate | 168852765 | 2013-07-05 | [39 empty] | 2013-10-01 | 2018-12-31
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T12025514WP | FROM->TO | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | CP | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | 14WP | 329 | 360 | 0 | 113.8 | 113.8347 | 120.091 | [7 empty] | CATEGORYB | GENOUT | GEN525562 1-TOLK GEN #2 24 KV | 0 | 0 |  | 0 |  | 0 |  |  |  | 433 |  | SPS | Potter to Tolk 345 kV | Build 111 mile 345 kV line from Potter to Tolk. Further study analysis will be performed with regard to the SPS North-South Stability Limit to determine whether its rating may be increased based on approved SPP Expansion Plan Network Upgrades scheduled to be placed in service. Pending this analysis, the Potter – Tolk 345 kV Service Upgrade requirement will be re-evaluated. |  |  |  |  | 130 | [6 empty] | SCERT Estimate | 168852765 | 2013-07-05 | [39 empty] | 2013-10-01 | 2018-12-31
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T12015514WP | FROM->TO | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | CP | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | 14WP | 329 | 360 | 0 | 109.4 | 109.4868 | 115.5303 | [7 empty] | CATEGORYB | GENOUT | GEN525561 1-TOLK GEN #1 24 KV | 0 | 0 |  | 0 |  | 0 |  |  |  | 416 |  | SPS | Potter to Tolk 345 kV | Build 111 mile 345 kV line from Potter to Tolk. Further study analysis will be performed with regard to the SPS North-South Stability Limit to determine whether its rating may be increased based on approved SPP Expansion Plan Network Upgrades scheduled to be placed in service. Pending this analysis, the Potter – Tolk 345 kV Service Upgrade requirement will be re-evaluated. |  |  |  |  | 130 | [6 empty] | SCERT Estimate | 168852765 | 2013-07-05 | [39 empty] | 2013-10-01 | 2018-12-31
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1805514WP | FROM->TO | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | CP | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | 14WP | 329 | 360 | 0 | 99.7 | 99.7477 | 106.6377 | [7 empty] | CATEGORYB | SINGLE | PLANT X STATION - POTTER COUNTY INTERCHANGE 230KV CKT 1 | 0 | 523959 | POTTER_CO 6230.00 | 525481 | PLANT_X 6230.00 | 0 |  | 1 |  | 384 |  | SPS | Potter to Tolk 345 kV | Build 111 mile 345 kV line from Potter to Tolk. Further study analysis will be performed with regard to the SPS North-South Stability Limit to determine whether its rating may be increased based on approved SPP Expansion Plan Network Upgrades scheduled to be placed in service. Pending this analysis, the Potter – Tolk 345 kV Service Upgrade requirement will be re-evaluated. |  |  |  |  | 130 | [6 empty] | SCERT Estimate | 168852765 | 2013-07-05 | [39 empty] | 2013-10-01 | 2018-12-31
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T10555518WP | FROM->TO | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | CP | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | 18WP | 329 | 360 | 0 | 104.2 | 104.2273 | 109.1609 | [7 empty] | CATEGORYB | GENOUT | GEN525562 1-TOLK GEN #2 24 KV | 0 | 0 |  | 0 |  | 0 |  |  |  | 393 |  | SPS | Potter to Tolk 345 kV | Build 111 mile 345 kV line from Potter to Tolk. Further study analysis will be performed with regard to the SPS North-South Stability Limit to determine whether its rating may be increased based on approved SPP Expansion Plan Network Upgrades scheduled to be placed in service. Pending this analysis, the Potter – Tolk 345 kV Service Upgrade requirement will be re-evaluated. |  |  |  |  | 130 | [6 empty] | SCERT Estimate | 168852765 | 2013-07-05 | [39 empty] | 2013-10-01 | 2018-12-31
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T10545518WP | FROM->TO | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | CP | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | 18WP | 329 | 360 | 0 | 100.5 | 100.6305 | 105.5515 | [7 empty] | CATEGORYB | GENOUT | GEN525561 1-TOLK GEN #1 24 KV | 0 | 0 |  | 0 |  | 0 |  |  |  | 380 |  | SPS | Potter to Tolk 345 kV | Build 111 mile 345 kV line from Potter to Tolk. Further study analysis will be performed with regard to the SPS North-South Stability Limit to determine whether its rating may be increased based on approved SPP Expansion Plan Network Upgrades scheduled to be placed in service. Pending this analysis, the Potter – Tolk 345 kV Service Upgrade requirement will be re-evaluated. |  |  |  |  | 130 | [6 empty] | SCERT Estimate | 168852765 | 2013-07-05 | [39 empty] | 2013-10-01 | 2018-12-31
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T15835523WP | FROM->TO | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | CP | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | 23WP | 329 | 360 | 0 | 101.3 | 101.2467 | 105.859 | [7 empty] | CATEGORYB | GENOUT | GEN525562 1-TOLK GEN #2 24 KV | 0 | 0 |  | 0 |  | 0 |  |  |  | 382 |  | SPS | Potter to Tolk 345 kV | Build 111 mile 345 kV line from Potter to Tolk. Further study analysis will be performed with regard to the SPS North-South Stability Limit to determine whether its rating may be increased based on approved SPP Expansion Plan Network Upgrades scheduled to be placed in service. Pending this analysis, the Potter – Tolk 345 kV Service Upgrade requirement will be re-evaluated. |  |  |  |  | 130 | [6 empty] | SCERT Estimate | 168852765 | 2013-07-05 | [39 empty] | 2013-10-01 | 2018-12-31
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T15825523WP | FROM->TO | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | CP | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | 23WP | 329 | 360 | 0 | 97.7 | 97.7837 | 102.3359 | [7 empty] | CATEGORYB | GENOUT | GEN525561 1-TOLK GEN #1 24 KV | 0 | 0 |  | 0 |  | 0 |  |  |  | 369 |  | SPS | Potter to Tolk 345 kV | Build 111 mile 345 kV line from Potter to Tolk. Further study analysis will be performed with regard to the SPS North-South Stability Limit to determine whether its rating may be increased based on approved SPP Expansion Plan Network Upgrades scheduled to be placed in service. Pending this analysis, the Potter – Tolk 345 kV Service Upgrade requirement will be re-evaluated. |  |  |  |  | 130 | [6 empty] | SCERT Estimate | 168852765 | 2013-07-05 | [39 empty] | 2013-10-01 | 2018-12-31
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2105513WP | FROM->TO | CANYON EAST SUB - CANYON WEST SUB 115KV CKT 1 | CP | SPS | SPS | SPS-CLHF | SPS-CLHF | 0 | 524523 | CANYON_EAST3115.00 | 524516 | CANYON_WEST3115.00 | 0 |  | 1 | 13WP | 106 | 106 | 0 | 115.1 | 115.1422 | 122.796 | [7 empty] | CATEGORYB | SINGLE | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 |  | 131 |  | SPS | Potter to Tolk 345 kV | Build 111 mile 345 kV line from Potter to Tolk. Further study analysis will be performed with regard to the SPS North-South Stability Limit to determine whether its rating may be increased based on approved SPP Expansion Plan Network Upgrades scheduled to be placed in service. Pending this analysis, the Potter – Tolk 345 kV Service Upgrade requirement will be re-evaluated. |  |  |  |  | 130 | [6 empty] | SCERT Estimate | 168852765 | 2013-07-05 | [39 empty] | 2013-10-01 | 2018-12-31
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1845514WP | FROM->TO | CANYON EAST SUB - CANYON WEST SUB 115KV CKT 1 | CP | SPS | SPS | SPS-CLHF | SPS-CLHF | 0 | 524523 | CANYON_EAST3115.00 | 524516 | CANYON_WEST3115.00 | 0 |  | 1 | 14WP | 106 | 106 | 0 | 105 | 105.042 | 112.9302 | [7 empty] | CATEGORYB | SINGLE | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 |  | 120 |  | SPS | Potter to Tolk 345 kV | Build 111 mile 345 kV line from Potter to Tolk. Further study analysis will be performed with regard to the SPS North-South Stability Limit to determine whether its rating may be increased based on approved SPP Expansion Plan Network Upgrades scheduled to be placed in service. Pending this analysis, the Potter – Tolk 345 kV Service Upgrade requirement will be re-evaluated. |  |  |  |  | 130 | [6 empty] | SCERT Estimate | 168852765 | 2013-07-05 | [39 empty] | 2013-10-01 | 2018-12-31
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2085513WP | TO->FROM | CANYON EAST SUB - OSAGE SWITCHING STATION 115KV CKT 1 | CP | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524345 | OSAGE 3115.00 | 524523 | CANYON_EAST3115.00 | 0 |  | 1 | 13WP | 106 | 106 | 0 | 128.6 | 128.6261 | 136.4147 | [7 empty] | CATEGORYB | SINGLE | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 |  | 145 |  | SPS | Potter to Tolk 345 kV | Build 111 mile 345 kV line from Potter to Tolk. Further study analysis will be performed with regard to the SPS North-South Stability Limit to determine whether its rating may be increased based on approved SPP Expansion Plan Network Upgrades scheduled to be placed in service. Pending this analysis, the Potter – Tolk 345 kV Service Upgrade requirement will be re-evaluated. |  |  |  |  | 130 | [6 empty] | SCERT Estimate | 168852765 | 2013-07-05 | [39 empty] | 2013-10-01 | 2018-12-31
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3905514SP | TO->FROM | CANYON EAST SUB - OSAGE SWITCHING STATION 115KV CKT 1 | CP | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524345 | OSAGE 3115.00 | 524523 | CANYON_EAST3115.00 | 0 |  | 1 | 14SP | 96 | 96 | 0 | 111.2 | 111.1652 | 116.6757 | [7 empty] | CATEGORYB | SINGLE | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 |  | 113 |  | SPS | Potter to Tolk 345 kV | Build 111 mile 345 kV line from Potter to Tolk. Further study analysis will be performed with regard to the SPS North-South Stability Limit to determine whether its rating may be increased based on approved SPP Expansion Plan Network Upgrades scheduled to be placed in service. Pending this analysis, the Potter – Tolk 345 kV Service Upgrade requirement will be re-evaluated. |  |  |  |  | 130 | [6 empty] | SCERT Estimate | 168852765 | 2013-07-05 | [39 empty] | 2013-10-01 | 2018-12-31
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1825514WP | TO->FROM | CANYON EAST SUB - OSAGE SWITCHING STATION 115KV CKT 1 | CP | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524345 | OSAGE 3115.00 | 524523 | CANYON_EAST3115.00 | 0 |  | 1 | 14WP | 106 | 106 | 0 | 118.7 | 118.672 | 126.5741 | [7 empty] | CATEGORYB | SINGLE | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 |  | 135 |  | SPS | Potter to Tolk 345 kV | Build 111 mile 345 kV line from Potter to Tolk. Further study analysis will be performed with regard to the SPS North-South Stability Limit to determine whether its rating may be increased based on approved SPP Expansion Plan Network Upgrades scheduled to be placed in service. Pending this analysis, the Potter – Tolk 345 kV Service Upgrade requirement will be re-evaluated. |  |  |  |  | 130 | [6 empty] | SCERT Estimate | 168852765 | 2013-07-05 | [39 empty] | 2013-10-01 | 2018-12-31
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1595518WP | TO->FROM | CANYON EAST SUB - RANDALL COUNTY INTERCHANGE 115KV CKT 1 | CP | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524364 | RANDALL 3115.00 | 524523 | CANYON_EAST3115.00 | 0 |  | 1 | 18WP | 106 | 106 | 0 | 100.9 | 100.9173 | 107.2914 | [7 empty] | CATEGORYB | SINGLE | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 |  | 114 |  | SPS | Potter to Tolk 345 kV | Build 111 mile 345 kV line from Potter to Tolk. Further study analysis will be performed with regard to the SPS North-South Stability Limit to determine whether its rating may be increased based on approved SPP Expansion Plan Network Upgrades scheduled to be placed in service. Pending this analysis, the Potter – Tolk 345 kV Service Upgrade requirement will be re-evaluated. |  |  |  |  | 130 | [6 empty] | SCERT Estimate | 168852765 | 2013-07-05 | [39 empty] | 2013-10-01 | 2018-12-31
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2445523WP | TO->FROM | CANYON EAST SUB - RANDALL COUNTY INTERCHANGE 115KV CKT 1 | CP | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524364 | RANDALL 3115.00 | 524523 | CANYON_EAST3115.00 | 0 |  | 1 | 23WP | 106 | 106 | 0 | 99.3 | 99.2813 | 105.4103 | [7 empty] | CATEGORYB | SINGLE | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 |  | 112 |  | SPS | Potter to Tolk 345 kV | Build 111 mile 345 kV line from Potter to Tolk. Further study analysis will be performed with regard to the SPS North-South Stability Limit to determine whether its rating may be increased based on approved SPP Expansion Plan Network Upgrades scheduled to be placed in service. Pending this analysis, the Potter – Tolk 345 kV Service Upgrade requirement will be re-evaluated. |  |  |  |  | 130 | [6 empty] | SCERT Estimate | 168852765 | 2013-07-05 | [39 empty] | 2013-10-01 | 2018-12-31
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2115513WP | FROM->TO | CANYON WEST SUB - DAWN SUB 115KV CKT 1 | CP | SPS | SPS | SPS-CLHF | SPS-CLHF | 0 | 524516 | CANYON_WEST3115.00 | 524590 | DAWN 3115.00 | 0 |  | 1 | 13WP | 106 | 106 | 0 | 101.9 | 101.9458 | 109.4029 | [7 empty] | CATEGORYB | SINGLE | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 |  | 116 |  | SPS | Potter to Tolk 345 kV | Build 111 mile 345 kV line from Potter to Tolk. Further study analysis will be performed with regard to the SPS North-South Stability Limit to determine whether its rating may be increased based on approved SPP Expansion Plan Network Upgrades scheduled to be placed in service. Pending this analysis, the Potter – Tolk 345 kV Service Upgrade requirement will be re-evaluated. |  |  |  |  | 130 | [6 empty] | SCERT Estimate | 168852765 | 2013-07-05 | [39 empty] | 2013-10-01 | 2018-12-31
2009-AGP1 | [10 empty] | CHERRY6 230.00 - Harrington Station East Bus 230KV CKT 1 | U | SPS | SPS | SPS-AMA |  | 0 | 523977 |  | 524010 |  | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | SPS | CHERRY6 230.00 - Harrington Station East Bus 230KV CKT 1 | Replace wavetrap at Harrington East | [53 empty] | 2015-06-01 | 2015-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2125513WP | FROM->TO | DAWN SUB - Panda Energy Substation Hereford 115KV CKT 1 | CP | SPS | SPS | SPS-CLHF | SPS-CLHF | 0 | 524590 | DAWN 3115.00 | 524597 | PANDAHFD 3115.00 | 0 |  | 1 | 13WP | 106 | 106 | 0 | 98.6 | 98.5868 | 106.02 | [7 empty] | CATEGORYB | SINGLE | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 |  | 113 |  | SPS | Potter to Tolk 345 kV | Build 111 mile 345 kV line from Potter to Tolk. Further study analysis will be performed with regard to the SPS North-South Stability Limit to determine whether its rating may be increased based on approved SPP Expansion Plan Network Upgrades scheduled to be placed in service. Pending this analysis, the Potter – Tolk 345 kV Service Upgrade requirement will be re-evaluated. |  |  |  |  | 130 | [6 empty] | SCERT Estimate | 168852765 | 2013-07-05 | [39 empty] | 2013-10-01 | 2018-12-31
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2135513WP | TO->FROM | DEAF SMITH COUNTY INTERCHANGE - Panda Energy Substation Hereford 115KV CKT 1 | CP | SPS | SPS | SPS-CLHF | SPS-CLHF | 0 | 524597 | PANDAHFD 3115.00 | 524622 | DEAFSMITH 3115.00 | 0 |  | 1 | 13WP | 106 | 106 | 0 | 96.6 | 96.5744 | 103.9962 | [7 empty] | CATEGORYB | SINGLE | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 |  | 111 |  | SPS | Potter to Tolk 345 kV | Build 111 mile 345 kV line from Potter to Tolk. Further study analysis will be performed with regard to the SPS North-South Stability Limit to determine whether its rating may be increased based on approved SPP Expansion Plan Network Upgrades scheduled to be placed in service. Pending this analysis, the Potter – Tolk 345 kV Service Upgrade requirement will be re-evaluated. |  |  |  |  | 130 | [6 empty] | SCERT Estimate | 168852765 | 2013-07-05 | [39 empty] | 2013-10-01 | 2018-12-31
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2455513WP | TO->FROM | HALE CO INTERCHANGE - KRESS INTERCHANGE 115KV CKT 1 | EXP | SPS | SPS | SPS-CNPL | SPS-CNPL | 0 | 525192 | KRESS_INT 3115.00 | 525454 | HALE_CNTY 3115.00 | 0 |  | 1 | 13WP | 143 | 173 | 0 | 95.3 | 95.3378 | 102.4067 | [7 empty] | CATEGORYB | SINGLE | SWISHER COUNTY INTERCHANGE - TUCO INTERCHANGE 230KV CKT 1 | 0 | 525213 | SWISHER 6230.00 | 525830 | TUCO_INT 6230.00 | 0 |  | 1 |  | 178 |  | SPS | Kiser Substation 115/69 kV Ckt 1 | Build new substation at Kiser and install a 115/69 kV transformer and 69 kV terminal equipment to connect to the local 69 kV system. | [53 empty] | 2013-10-01 | 2014-02-28
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2465513WP | FROM->TO | HALE CO INTERCHANGE - TUCO INTERCHANGE 115KV CKT 1 | EXP | SPS | SPS | SPS-CNPL | SPS-CNPL | 0 | 525454 | HALE_CNTY 3115.00 | 525828 | TUCO_INT 3115.00 | 0 |  | 1 | 13WP | 106 | 106 | 0 | 104.3 | 104.3056 | 113.4929 | [7 empty] | CATEGORYB | SINGLE | SWISHER COUNTY INTERCHANGE - TUCO INTERCHANGE 230KV CKT 1 | 0 | 525213 | SWISHER 6230.00 | 525830 | TUCO_INT 6230.00 | 0 |  | 1 |  | 121 |  | SPS | Kiser Substation 115/69 kV Ckt 1 | Build new substation at Kiser and install a 115/69 kV transformer and 69 kV terminal equipment to connect to the local 69 kV system. | [53 empty] | 2013-10-01 | 2014-02-28
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T325513WP | FROM->TO | SPS North-South Stability Limit | CP | SPS | SPS |  |  | SPSNORTH_STH | 0 |  | 0 |  | 0 |  |  | 13WP | 800 | 800 | 800 | 119.8 | 119.7774 | 127.1697 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  | 1018 |  | SPS | Potter to Tolk 345 kV | Build 111 mile 345 kV line from Potter to Tolk. Further study analysis will be performed with regard to the SPS North-South Stability Limit to determine whether its rating may be increased based on approved SPP Expansion Plan Network Upgrades scheduled to be placed in service. Pending this analysis, the Potter – Tolk 345 kV Service Upgrade requirement will be re-evaluated. |  |  |  |  | 130 | [6 empty] | SCERT Estimate | 168852765 | 2013-07-05 | [39 empty] | 2013-10-01 | 2018-12-31
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T355514WP | FROM->TO | SPS North-South Stability Limit | CP | SPS | SPS |  |  | SPSNORTH_STH | 0 |  | 0 |  | 0 |  |  | 14WP | 800 | 800 | 800 | 109.9 | 109.8853 | 117.9831 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  | 944 |  | SPS | Potter to Tolk 345 kV | Build 111 mile 345 kV line from Potter to Tolk. Further study analysis will be performed with regard to the SPS North-South Stability Limit to determine whether its rating may be increased based on approved SPP Expansion Plan Network Upgrades scheduled to be placed in service. Pending this analysis, the Potter – Tolk 345 kV Service Upgrade requirement will be re-evaluated. |  |  |  |  | 130 | [6 empty] | SCERT Estimate | 168852765 | 2013-07-05 | [39 empty] | 2013-10-01 | 2018-12-31
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T365518WP | FROM->TO | SPS North-South Stability Limit | CP | SPS | SPS |  |  | SPSNORTH_STX | 0 |  | 0 |  | 0 |  |  | 18WP | 800 | 800 | 800 | 99.5 | 99.7095 | 107.2097 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  | 858 |  | SPS | Potter to Tolk 345 kV | Build 111 mile 345 kV line from Potter to Tolk. Further study analysis will be performed with regard to the SPS North-South Stability Limit to determine whether its rating may be increased based on approved SPP Expansion Plan Network Upgrades scheduled to be placed in service. Pending this analysis, the Potter – Tolk 345 kV Service Upgrade requirement will be re-evaluated. |  |  |  |  | 130 | [6 empty] | SCERT Estimate | 168852765 | 2013-07-05 | [39 empty] | 2013-10-01 | 2018-12-31
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T535523WP | FROM->TO | SPS North-South Stability Limit | CP | SPS | SPS |  |  | SPSNORTH_STX | 0 |  | 0 |  | 0 |  |  | 23WP | 800 | 800 | 800 | 95.6 | 95.8483 | 103.0575 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  |  | 825 |  | SPS | Potter to Tolk 345 kV | Build 111 mile 345 kV line from Potter to Tolk. Further study analysis will be performed with regard to the SPS North-South Stability Limit to determine whether its rating may be increased based on approved SPP Expansion Plan Network Upgrades scheduled to be placed in service. Pending this analysis, the Potter – Tolk 345 kV Service Upgrade requirement will be re-evaluated. |  |  |  |  | 130 | [6 empty] | SCERT Estimate | 168852765 | 2013-07-05 | [39 empty] | 2013-10-01 | 2018-12-31
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2145513WP | FROM->TO | SWISHER COUNTY INTERCHANGE - TUCO INTERCHANGE 230KV CKT 1 | CP | SPS | SPS | SPS-CNPL | SPS-CNPL | 0 | 525213 | SWISHER 6230.00 | 525830 | TUCO_INT 6230.00 | 0 |  | 1 | 13WP | 329 | 361 | 0 |  | 94.8923 | 102.3788 | [7 empty] | CATEGORYB | SINGLE | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 |  | 370 |  | SPS | Potter to Tolk 345 kV | Build 111 mile 345 kV line from Potter to Tolk. Further study analysis will be performed with regard to the SPS North-South Stability Limit to determine whether its rating may be increased based on approved SPP Expansion Plan Network Upgrades scheduled to be placed in service. Pending this analysis, the Potter – Tolk 345 kV Service Upgrade requirement will be re-evaluated. |  |  |  |  | 130 | [6 empty] | SCERT Estimate | 168852765 | 2013-07-05 | [39 empty] | 2013-10-01 | 2018-12-31
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2525513WP | FROM->TO | SWISHER COUNTY INTERCHANGE - TUCO INTERCHANGE 230KV CKT 1 | CP | SPS | SPS | SPS-CNPL | SPS-CNPL | 0 | 525213 | SWISHER 6230.00 | 525830 | TUCO_INT 6230.00 | 0 |  | 1 | 13WP | 329 | 361 | 0 |  | 93.4467 | 101.2211 | [7 empty] | CATEGORYB | SINGLE | TOLK STATION EAST - TUCO INTERCHANGE 230KV CKT 1 | 0 | 525524 | TOLK_EAST 6230.00 | 525830 | TUCO_INT 6230.00 | 0 |  | 1 |  | 366 |  | SPS | Potter to Tolk 345 kV | Build 111 mile 345 kV line from Potter to Tolk. Further study analysis will be performed with regard to the SPS North-South Stability Limit to determine whether its rating may be increased based on approved SPP Expansion Plan Network Upgrades scheduled to be placed in service. Pending this analysis, the Potter – Tolk 345 kV Service Upgrade requirement will be re-evaluated. |  |  |  |  | 130 | [6 empty] | SCERT Estimate | 168852765 | 2013-07-05 | [39 empty] | 2013-10-01 | 2018-12-31
2012-AG1 | AFS4LAMAR |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS4LAMAR1T4115518SP | TO->FROM | CIMARRON RIVER TAP - KISMET 3 115.00 115KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539646 | KISMET 3 115.00 | 539652 | CMRIVTP3 115.00 | 0 |  | 1 | 18SP | 120.7 | 129.5 | 0.0 |  | 81.7515 | 108.5328 | [7 empty] | CATEGORYB | SINGLE | BUCKNER7 345.00 - HOLCOMB 345KV CKT 1 | 0 | 531449 | HOLCOMB7 345.00 | 531501 | BUCKNER7 345.00 | 0 |  | 1 |  | 141 |  | MKEC | CUDAHY - KISMET 3 115.00 115KV CKT 1 | Rebuild 32 miles and Substation work | [5 empty] | 36 | 36 |  |  |  |  | MKEC Estimate | 22000000 | 2013-01-01 | [39 empty] | 2015-06-01 | 2017-06-01
2012-AG1 | AFS4LAMAR |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS4LAMAR1T4115518SP | TO->FROM | CIMARRON RIVER TAP - KISMET 3 115.00 115KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539646 | KISMET 3 115.00 | 539652 | CMRIVTP3 115.00 | 0 |  | 1 | 18SP | 120.7 | 129.5 | 0.0 |  | 81.7515 | 108.5328 | [7 empty] | CATEGORYB | SINGLE | BUCKNER7 345.00 - HOLCOMB 345KV CKT 1 | 0 | 531449 | HOLCOMB7 345.00 | 531501 | BUCKNER7 345.00 | 0 |  | 1 |  | 141 |  | MKEC | CIMARRON RIVER PLANT - CIMARRON RIVER TAP 115KV CKT 1 | Rebuild 4 miles and Substation work | [11 empty] | MKEC Estimate | 6120760 | 2013-01-01 | [39 empty] | 2015-06-01 | 2017-06-01
2012-AG1 | AFS4LAMAR |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS4LAMAR1T4115518SP | TO->FROM | CIMARRON RIVER TAP - KISMET 3 115.00 115KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539646 | KISMET 3 115.00 | 539652 | CMRIVTP3 115.00 | 0 |  | 1 | 18SP | 120.7 | 129.5 | 0.0 |  | 81.7515 | 108.5328 | [7 empty] | CATEGORYB | SINGLE | BUCKNER7 345.00 - HOLCOMB 345KV CKT 1 | 0 | 531449 | HOLCOMB7 345.00 | 531501 | BUCKNER7 345.00 | 0 |  | 1 |  | 141 |  | MKEC | CIMARRON RIVER TAP - KISMET 3 115.00 115KV CKT 1 | Rebuild 3.37 miles and Substation work | [11 empty] | MKEC Estimate | 4129240 | 2013-01-01 | [39 empty] | 2015-06-01 | 2017-06-01
2012-AG1 | AFS4LAMAR |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS4LAMAR1T5315523SP | TO->FROM | CIMARRON RIVER TAP - KISMET 3 115.00 115KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539646 | KISMET 3 115.00 | 539652 | CMRIVTP3 115.00 | 0 |  | 1 | 23SP | 120.7 | 129.5 | 0.0 |  | 83.6284 | 108.4465 | [7 empty] | CATEGORYB | SINGLE | BUCKNER7 345.00 - HOLCOMB 345KV CKT 1 | 0 | 531449 | HOLCOMB7 345.00 | 531501 | BUCKNER7 345.00 | 0 |  | 1 |  | 141 |  | MKEC | CUDAHY - KISMET 3 115.00 115KV CKT 1 | Rebuild 32 miles and Substation work | [5 empty] | 36 | 36 |  |  |  |  | MKEC Estimate | 22000000 | 2013-01-01 | [39 empty] | 2015-06-01 | 2017-06-01
2012-AG1 | AFS4LAMAR |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS4LAMAR1T5315523SP | TO->FROM | CIMARRON RIVER TAP - KISMET 3 115.00 115KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539646 | KISMET 3 115.00 | 539652 | CMRIVTP3 115.00 | 0 |  | 1 | 23SP | 120.7 | 129.5 | 0.0 |  | 83.6284 | 108.4465 | [7 empty] | CATEGORYB | SINGLE | BUCKNER7 345.00 - HOLCOMB 345KV CKT 1 | 0 | 531449 | HOLCOMB7 345.00 | 531501 | BUCKNER7 345.00 | 0 |  | 1 |  | 141 |  | MKEC | CIMARRON RIVER PLANT - CIMARRON RIVER TAP 115KV CKT 1 | Rebuild 4 miles and Substation work | [11 empty] | MKEC Estimate | 6120760 | 2013-01-01 | [39 empty] | 2015-06-01 | 2017-06-01
2012-AG1 | AFS4LAMAR |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS4LAMAR1T5315523SP | TO->FROM | CIMARRON RIVER TAP - KISMET 3 115.00 115KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539646 | KISMET 3 115.00 | 539652 | CMRIVTP3 115.00 | 0 |  | 1 | 23SP | 120.7 | 129.5 | 0.0 |  | 83.6284 | 108.4465 | [7 empty] | CATEGORYB | SINGLE | BUCKNER7 345.00 - HOLCOMB 345KV CKT 1 | 0 | 531449 | HOLCOMB7 345.00 | 531501 | BUCKNER7 345.00 | 0 |  | 1 |  | 141 |  | MKEC | CIMARRON RIVER TAP - KISMET 3 115.00 115KV CKT 1 | Rebuild 3.37 miles and Substation work | [11 empty] | MKEC Estimate | 4129240 | 2013-01-01 | [39 empty] | 2015-06-01 | 2017-06-01
2012-AG1 | AFS4-ADD | [5 empty] | 5 | 5 | 2012AG1AFS4ADDCLCL1T9995514WP | FROM->TO | CLARKCO - CLARKCO 345KV CKT 1 | EXP | SUNC | SUNC |  | SPS-MUNI | 0 | 560688 | CLARKCO 7 | 539800 | CLARKCO 7 | 0 |  | 1 | 14WP | 100 | 100 | 100 |  | -999 | 999 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [6 empty] | Priority Projects | [54 empty] | 2013-10-01 | 2015-01-01
2012-AG1 | AFS4NC1 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS4NC11T115514WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 14WP | 110 | 110 | 0 |  | 92.5157 | 107.0642 | [7 empty] | CATEGORYB | SINGLE | THISTLE7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE7 345.00 | 0 |  | 2 |  | 118 |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 | Replace Wave Trap at Harper Substation |  | 110 |  |  |  | 18 | 18 | [5 empty] | 385244 | 2012-11-12 | [39 empty] | 2014-10-01 | 2016-06-01
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1205514WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | EXP | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 14WP | 110 | 110 | 0 |  | 94.0727 | 106.3076 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 117 |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 | Replace Wave Trap at Harper Substation |  | 110 |  |  |  | 18 | 18 | [5 empty] | 385244 | 2012-11-12 | [39 empty] | 2014-10-01 | 2016-06-01
2012-AG1 | AFS4LAMAR |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS4LAMAR1T4135518SP | TO->FROM | CUDAHY - CROOKED CREEK 115.00 115KV CKT 1 | S | SUNC | SUNC | BEPC_1630 | GREAT PL | 0 | 560229 | CROOKED CREEK 115.00 | 539659 | CUDAHY 3 115.00 | 0 |  | 1 | 18SP | 120.7 | 129.5 | 0.0 |  | 89.5503 | 116.4372 | [7 empty] | CATEGORYB | SINGLE | BUCKNER7 345.00 - HOLCOMB 345KV CKT 1 | 0 | 531449 | HOLCOMB7 345.00 | 531501 | BUCKNER7 345.00 | 0 |  | 1 |  | 151 |  | MKEC | CUDAHY - KISMET 3 115.00 115KV CKT 1 | Rebuild 32 miles and Substation work | [5 empty] | 36 | 36 |  |  |  |  | MKEC Estimate | 22000000 | 2013-01-01 | [39 empty] | 2015-06-01 | 2017-06-01
2012-AG1 | AFS4LAMAR |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS4LAMAR1T4135518SP | TO->FROM | CUDAHY - CROOKED CREEK 115.00 115KV CKT 1 | S | SUNC | SUNC | BEPC_1630 | GREAT PL | 0 | 560229 | CROOKED CREEK 115.00 | 539659 | CUDAHY 3 115.00 | 0 |  | 1 | 18SP | 120.7 | 129.5 | 0.0 |  | 89.5503 | 116.4372 | [7 empty] | CATEGORYB | SINGLE | BUCKNER7 345.00 - HOLCOMB 345KV CKT 1 | 0 | 531449 | HOLCOMB7 345.00 | 531501 | BUCKNER7 345.00 | 0 |  | 1 |  | 151 |  | MKEC | CIMARRON RIVER PLANT - CIMARRON RIVER TAP 115KV CKT 1 | Rebuild 4 miles and Substation work | [11 empty] | MKEC Estimate | 6120760 | 2013-01-01 | [39 empty] | 2015-06-01 | 2017-06-01
2012-AG1 | AFS4LAMAR |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS4LAMAR1T4135518SP | TO->FROM | CUDAHY - CROOKED CREEK 115.00 115KV CKT 1 | S | SUNC | SUNC | BEPC_1630 | GREAT PL | 0 | 560229 | CROOKED CREEK 115.00 | 539659 | CUDAHY 3 115.00 | 0 |  | 1 | 18SP | 120.7 | 129.5 | 0.0 |  | 89.5503 | 116.4372 | [7 empty] | CATEGORYB | SINGLE | BUCKNER7 345.00 - HOLCOMB 345KV CKT 1 | 0 | 531449 | HOLCOMB7 345.00 | 531501 | BUCKNER7 345.00 | 0 |  | 1 |  | 151 |  | MKEC | CIMARRON RIVER TAP - KISMET 3 115.00 115KV CKT 1 | Rebuild 3.37 miles and Substation work | [11 empty] | MKEC Estimate | 4129240 | 2013-01-01 | [39 empty] | 2015-06-01 | 2017-06-01
2012-AG1 | AFS4LAMAR |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS4LAMAR1T5335523SP | TO->FROM | CUDAHY - CROOKED CREEK 115.00 115KV CKT 1 | S | SUNC | SUNC | BEPC_1630 | GREAT PL | 0 | 560229 | CROOKED CREEK 115.00 | 539659 | CUDAHY 3 115.00 | 0 |  | 1 | 23SP | 120.7 | 129.5 | 0.0 |  | 92.6256 | 117.5474 | [7 empty] | CATEGORYB | SINGLE | BUCKNER7 345.00 - HOLCOMB 345KV CKT 1 | 0 | 531449 | HOLCOMB7 345.00 | 531501 | BUCKNER7 345.00 | 0 |  | 1 |  | 153 |  | MKEC | CUDAHY - KISMET 3 115.00 115KV CKT 1 | Rebuild 32 miles and Substation work | [5 empty] | 36 | 36 |  |  |  |  | MKEC Estimate | 22000000 | 2013-01-01 | [39 empty] | 2015-06-01 | 2017-06-01
2012-AG1 | AFS4LAMAR |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS4LAMAR1T5335523SP | TO->FROM | CUDAHY - CROOKED CREEK 115.00 115KV CKT 1 | S | SUNC | SUNC | BEPC_1630 | GREAT PL | 0 | 560229 | CROOKED CREEK 115.00 | 539659 | CUDAHY 3 115.00 | 0 |  | 1 | 23SP | 120.7 | 129.5 | 0.0 |  | 92.6256 | 117.5474 | [7 empty] | CATEGORYB | SINGLE | BUCKNER7 345.00 - HOLCOMB 345KV CKT 1 | 0 | 531449 | HOLCOMB7 345.00 | 531501 | BUCKNER7 345.00 | 0 |  | 1 |  | 153 |  | MKEC | CIMARRON RIVER PLANT - CIMARRON RIVER TAP 115KV CKT 1 | Rebuild 4 miles and Substation work | [11 empty] | MKEC Estimate | 6120760 | 2013-01-01 | [39 empty] | 2015-06-01 | 2017-06-01
2012-AG1 | AFS4LAMAR |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS4LAMAR1T5335523SP | TO->FROM | CUDAHY - CROOKED CREEK 115.00 115KV CKT 1 | S | SUNC | SUNC | BEPC_1630 | GREAT PL | 0 | 560229 | CROOKED CREEK 115.00 | 539659 | CUDAHY 3 115.00 | 0 |  | 1 | 23SP | 120.7 | 129.5 | 0.0 |  | 92.6256 | 117.5474 | [7 empty] | CATEGORYB | SINGLE | BUCKNER7 345.00 - HOLCOMB 345KV CKT 1 | 0 | 531449 | HOLCOMB7 345.00 | 531501 | BUCKNER7 345.00 | 0 |  | 1 |  | 153 |  | MKEC | CIMARRON RIVER TAP - KISMET 3 115.00 115KV CKT 1 | Rebuild 3.37 miles and Substation work | [11 empty] | MKEC Estimate | 4129240 | 2013-01-01 | [39 empty] | 2015-06-01 | 2017-06-01
2012-AG1 | AFS4LAMAR |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS4LAMAR1T4125518SP | FROM->TO | CUDAHY - KISMET 3 115.00 115KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539659 | CUDAHY 3 115.00 | 539646 | KISMET 3 115.00 | 0 |  | 1 | 18SP | 120.7 | 129.5 | 0.0 |  | 83.719 | 110.4773 | [7 empty] | CATEGORYB | SINGLE | BUCKNER7 345.00 - HOLCOMB 345KV CKT 1 | 0 | 531449 | HOLCOMB7 345.00 | 531501 | BUCKNER7 345.00 | 0 |  | 1 |  | 144 |  | MKEC | CUDAHY - KISMET 3 115.00 115KV CKT 1 | Rebuild 32 miles and Substation work | [5 empty] | 36 | 36 |  |  |  |  | MKEC Estimate | 22000000 | 2013-01-01 | [39 empty] | 2015-06-01 | 2017-06-01
2012-AG1 | AFS4LAMAR |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS4LAMAR1T4125518SP | FROM->TO | CUDAHY - KISMET 3 115.00 115KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539659 | CUDAHY 3 115.00 | 539646 | KISMET 3 115.00 | 0 |  | 1 | 18SP | 120.7 | 129.5 | 0.0 |  | 83.719 | 110.4773 | [7 empty] | CATEGORYB | SINGLE | BUCKNER7 345.00 - HOLCOMB 345KV CKT 1 | 0 | 531449 | HOLCOMB7 345.00 | 531501 | BUCKNER7 345.00 | 0 |  | 1 |  | 144 |  | MKEC | CIMARRON RIVER PLANT - CIMARRON RIVER TAP 115KV CKT 1 | Rebuild 4 miles and Substation work | [11 empty] | MKEC Estimate | 6120760 | 2013-01-01 | [39 empty] | 2015-06-01 | 2017-06-01
2012-AG1 | AFS4LAMAR |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS4LAMAR1T4125518SP | FROM->TO | CUDAHY - KISMET 3 115.00 115KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539659 | CUDAHY 3 115.00 | 539646 | KISMET 3 115.00 | 0 |  | 1 | 18SP | 120.7 | 129.5 | 0.0 |  | 83.719 | 110.4773 | [7 empty] | CATEGORYB | SINGLE | BUCKNER7 345.00 - HOLCOMB 345KV CKT 1 | 0 | 531449 | HOLCOMB7 345.00 | 531501 | BUCKNER7 345.00 | 0 |  | 1 |  | 144 |  | MKEC | CIMARRON RIVER TAP - KISMET 3 115.00 115KV CKT 1 | Rebuild 3.37 miles and Substation work | [11 empty] | MKEC Estimate | 4129240 | 2013-01-01 | [39 empty] | 2015-06-01 | 2017-06-01
2012-AG1 | AFS4LAMAR |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS4LAMAR1T1725518WP | FROM->TO | CUDAHY - KISMET 3 115.00 115KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539659 | CUDAHY 3 115.00 | 539646 | KISMET 3 115.00 | 0 |  | 1 | 18WP | 120.7 | 129.5 | 0.0 |  | 68.9861 | 101.232 | [7 empty] | CATEGORYB | SINGLE | BUCKNER7 345.00 - HOLCOMB 345KV CKT 1 | 0 | 531449 | HOLCOMB7 345.00 | 531501 | BUCKNER7 345.00 | 0 |  | 1 |  | 132 |  | MKEC | CUDAHY - KISMET 3 115.00 115KV CKT 1 | Rebuild 32 miles and Substation work | [5 empty] | 36 | 36 |  |  |  |  | MKEC Estimate | 22000000 | 2013-01-01 | [39 empty] | 2015-06-01 | 2017-06-01
2012-AG1 | AFS4LAMAR |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS4LAMAR1T1725518WP | FROM->TO | CUDAHY - KISMET 3 115.00 115KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539659 | CUDAHY 3 115.00 | 539646 | KISMET 3 115.00 | 0 |  | 1 | 18WP | 120.7 | 129.5 | 0.0 |  | 68.9861 | 101.232 | [7 empty] | CATEGORYB | SINGLE | BUCKNER7 345.00 - HOLCOMB 345KV CKT 1 | 0 | 531449 | HOLCOMB7 345.00 | 531501 | BUCKNER7 345.00 | 0 |  | 1 |  | 132 |  | MKEC | CIMARRON RIVER PLANT - CIMARRON RIVER TAP 115KV CKT 1 | Rebuild 4 miles and Substation work | [11 empty] | MKEC Estimate | 6120760 | 2013-01-01 | [39 empty] | 2015-06-01 | 2017-06-01
2012-AG1 | AFS4LAMAR |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS4LAMAR1T1725518WP | FROM->TO | CUDAHY - KISMET 3 115.00 115KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539659 | CUDAHY 3 115.00 | 539646 | KISMET 3 115.00 | 0 |  | 1 | 18WP | 120.7 | 129.5 | 0.0 |  | 68.9861 | 101.232 | [7 empty] | CATEGORYB | SINGLE | BUCKNER7 345.00 - HOLCOMB 345KV CKT 1 | 0 | 531449 | HOLCOMB7 345.00 | 531501 | BUCKNER7 345.00 | 0 |  | 1 |  | 132 |  | MKEC | CIMARRON RIVER TAP - KISMET 3 115.00 115KV CKT 1 | Rebuild 3.37 miles and Substation work | [11 empty] | MKEC Estimate | 4129240 | 2013-01-01 | [39 empty] | 2015-06-01 | 2017-06-01
2012-AG1 | AFS4LAMAR |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS4LAMAR1T5325523SP | FROM->TO | CUDAHY - KISMET 3 115.00 115KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539659 | CUDAHY 3 115.00 | 539646 | KISMET 3 115.00 | 0 |  | 1 | 23SP | 120.7 | 129.5 | 0.0 |  | 85.951 | 110.7273 | [7 empty] | CATEGORYB | SINGLE | BUCKNER7 345.00 - HOLCOMB 345KV CKT 1 | 0 | 531449 | HOLCOMB7 345.00 | 531501 | BUCKNER7 345.00 | 0 |  | 1 |  | 144 |  | MKEC | CUDAHY - KISMET 3 115.00 115KV CKT 1 | Rebuild 32 miles and Substation work | [5 empty] | 36 | 36 |  |  |  |  | MKEC Estimate | 22000000 | 2013-01-01 | [39 empty] | 2015-06-01 | 2017-06-01
2012-AG1 | AFS4LAMAR |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS4LAMAR1T5325523SP | FROM->TO | CUDAHY - KISMET 3 115.00 115KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539659 | CUDAHY 3 115.00 | 539646 | KISMET 3 115.00 | 0 |  | 1 | 23SP | 120.7 | 129.5 | 0.0 |  | 85.951 | 110.7273 | [7 empty] | CATEGORYB | SINGLE | BUCKNER7 345.00 - HOLCOMB 345KV CKT 1 | 0 | 531449 | HOLCOMB7 345.00 | 531501 | BUCKNER7 345.00 | 0 |  | 1 |  | 144 |  | MKEC | CIMARRON RIVER PLANT - CIMARRON RIVER TAP 115KV CKT 1 | Rebuild 4 miles and Substation work | [11 empty] | MKEC Estimate | 6120760 | 2013-01-01 | [39 empty] | 2015-06-01 | 2017-06-01
2012-AG1 | AFS4LAMAR |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS4LAMAR1T5325523SP | FROM->TO | CUDAHY - KISMET 3 115.00 115KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539659 | CUDAHY 3 115.00 | 539646 | KISMET 3 115.00 | 0 |  | 1 | 23SP | 120.7 | 129.5 | 0.0 |  | 85.951 | 110.7273 | [7 empty] | CATEGORYB | SINGLE | BUCKNER7 345.00 - HOLCOMB 345KV CKT 1 | 0 | 531449 | HOLCOMB7 345.00 | 531501 | BUCKNER7 345.00 | 0 |  | 1 |  | 144 |  | MKEC | CIMARRON RIVER TAP - KISMET 3 115.00 115KV CKT 1 | Rebuild 3.37 miles and Substation work | [11 empty] | MKEC Estimate | 4129240 | 2013-01-01 | [39 empty] | 2015-06-01 | 2017-06-01
2008-AGP1 | AFS6 | [9 empty] | GREENLEAF - KNOB HILL 115KV CKT 1 | U | SUNC | WERE |  | NCENTRAL | 0 | 539665 | GRNLEAF3 115.00 | 533332 | KNOB HL3 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | MKEC | GREENLEAF - KNOB HILL 115KV CKT 1 MKEC | Rebuild 43.5% Ownership of 20.9 miles | [53 empty] | 2013-06-01 | 2013-06-01
2012-AG1 | AFS4NC1 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS4NC11T125514WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 14WP | 110 | 110 | 0 | 99.9 | 99.8388 | 114.3234 | [7 empty] | CATEGORYB | SINGLE | THISTLE7 345.00 - WICHITA 345KV CKT 2 | 0 | 532796 | WICHITA7 345.00 | 539801 | THISTLE7 345.00 | 0 |  | 2 |  | 126 |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 | Replace Wave Trap at Harper Substation |  | 110 |  |  |  | 18 | 18 | [5 empty] | 385244 | 2012-11-12 | [39 empty] | 2014-10-01 | 2016-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1215514WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 14WP | 110 | 110 | 0 | 101.4 | 101.3726 | 113.5748 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 125 |  | MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 | Replace Wave Trap at Harper Substation |  | 110 |  |  |  | 18 | 18 | [5 empty] | 385244 | 2012-11-12 | [39 empty] | 2014-10-01 | 2016-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T4405514SP | TO->FROM | MULLERGREN - SPEARVILLE 230KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539695 | SPEARVL6 230.00 | 539679 | GRTBEND6 230.00 | 0 |  | 1 | 14SP | 330.3 | 355.3 | 0 | 107.3 | 107.281 | 106.0386 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 |  | 377 |  |  | Priority Projects | [54 empty] | 2013-10-01 | 2015-01-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3555513WP | FROM->TO | SEWARD - ST JOHN 115KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539692 | SEWARD 3 115.00 | 539696 | ST-JOHN3 115.00 | 0 |  | 1 | 13WP | 79.7 | 87.6 | 0 | 102.4 | 102.4302 | 101.5481 | [7 empty] | CATEGORYB | SINGLE | CIRCLE - MULLERGREN 230KV CKT 1 | 0 | 532871 | CIRCLE 6 230.00 | 539679 | GRTBEND6 230.00 | 0 |  | 1 |  | 89 |  |  | Priority Projects | [54 empty] | 2013-10-01 | 2015-01-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T13175518SP | TO->FROM | BUFORD 5 161.00 - BULL SHOALS 161KV CKT 1 | S | SWPA | SWPA | EMINTH | EMINTH | 0 | 505460 | BULL SH5 161.00 | 504440 | BUFORD 5 161.00 | 0 |  | 1 | 18SP | 167 | 167 | 0 | 101.5 | 101.4697 | 118.2139 | [7 empty] | CATEGORYB | SINGLE | BULL SHOALS - MIDWAY (YVEPA) 161KV CKT 1 | 0 | 505460 | BULL SH5 161.00 | 338813 | 5MIDWY JRDN#161.00 | 0 |  | 1 |  | 198 |  | SWPA | BUFORD 5 161.00 - BULL SHOALS 161KV CKT 1 Upgrade #1 | Replace one structure and make two structures floating deadends | 189 | 227 | 236 | 236 | 15.3 | 24 | 6 | [5 empty] | 125000 | 2012-09-18 | [39 empty] | 2015-06-01 | 2016-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T14945523SP | TO->FROM | BUFORD 5 161.00 - BULL SHOALS 161KV CKT 1 | S | SWPA | SWPA | EMINTH | EMINTH | 0 | 505460 | BULL SH5 161.00 | 504440 | BUFORD 5 161.00 | 0 |  | 1 | 23SP | 167 | 167 | 0 | 109.4 | 109.4051 | 119.8457 | [7 empty] | CATEGORYB | SINGLE | BULL SHOALS - MIDWAY (YVEPA) 161KV CKT 1 | 0 | 505460 | BULL SH5 161.00 | 338813 | 5MIDWY JRDN#161.00 | 0 |  | 1 |  | 201 |  | SWPA | BUFORD 5 161.00 - BULL SHOALS 161KV CKT 1 Upgrade #1 | Replace one structure and make two structures floating deadends | 189 | 227 | 236 | 236 | 15.3 | 24 | 6 | [5 empty] | 125000 | 2012-09-18 | [39 empty] | 2015-06-01 | 2016-06-01
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T13165518SP | FROM->TO | BUFORD 5 161.00 - NORFORK 161KV CKT 1 | S | SWPA | SWPA | EMINTH | EMINTH | 0 | 504440 | BUFORD 5 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 18SP | 189 | 189 | 0 |  | 86.545 | 101.3415 | [7 empty] | CATEGORYB | SINGLE | BULL SHOALS - MIDWAY (YVEPA) 161KV CKT 1 | 0 | 505460 | BULL SH5 161.00 | 338813 | 5MIDWY JRDN#161.00 | 0 |  | 1 |  | 192 |  | SWPA | BUFORD 5 161.00 - NORFORK 161KV CKT 1 Upgrade #1 | Replace two structures | 189 | 223 | 234 | 234 | 10.9 | 24 | 6 | [5 empty] | 100000 | 2012-09-18 | [39 empty] | 2015-06-01 | 2016-06-01
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T14935523SP | FROM->TO | BUFORD 5 161.00 - NORFORK 161KV CKT 1 | S | SWPA | SWPA | EMINTH | EMINTH | 0 | 504440 | BUFORD 5 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | 23SP | 189 | 189 | 0 |  | 92.6813 | 101.8994 | [7 empty] | CATEGORYB | SINGLE | BULL SHOALS - MIDWAY (YVEPA) 161KV CKT 1 | 0 | 505460 | BULL SH5 161.00 | 338813 | 5MIDWY JRDN#161.00 | 0 |  | 1 |  | 193 |  | SWPA | BUFORD 5 161.00 - NORFORK 161KV CKT 1 Upgrade #1 | Replace two structures | 189 | 223 | 234 | 234 | 10.9 | 24 | 6 | [5 empty] | 100000 | 2012-09-18 | [39 empty] | 2015-06-01 | 2016-06-01
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3415523SP | TO->FROM | GORE - MUSKOGEE TAP 161KV CKT 1 | S | SWPA | SWPA | EMINTH | EMINTH | 0 | 505558 | MUSKTAP5 161.00 | 505552 | GORE 5 161.00 | 0 |  | 1 | 23SP | 171 | 206 | 0 |  | 86.5486 | 100.9902 | [7 empty] | CATEGORYB | SINGLE | FT SMITH - MUSKOGEE 345KV CKT 1 | 0 | 515224 | MUSKOGE7 345.00 | 515302 | FTSMITH7 345.00 | 0 |  | 1 |  | 209 |  | SWPA | GORE - MUSKOGEE TAP 161KV CKT 1 | Rebuild w/ 1192 ACSR. Upgrade terminal equipment. | 296 | 335 | 335 | 335 | 16 | 30 | 6 |  | 0.00559 | 0.04595 | 0.02361 |  | 8000000 | 2012-09-18 | [39 empty] | 2019-06-01 | 2019-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T14665523WP | TO->FROM | NORTH WARSAW - TRUMAN 161KV CKT 1 | S | SWPA | GMO | EMINTH |  | 0 | 505502 | TRUMAN 5 161.00 | 541314 | NWARSAW5 161.00 | 0 |  | 1 | 23WP | 234 | 234 | 234 | 100.1 | 100.1166 | 105.4803 | [7 empty] | CATEGORYB | NONSINGLE | AI03 | 0 | 0 |  | 0 |  | 0 |  |  |  | 247 |  | SWPA | NORTH WARSAW - TRUMAN 161KV CKT 1 SWPA #1 | Replace wave trap and CTs at Truman. | 286 | 286 |  |  |  | 12 | 12 | [5 empty] | 70000 | 2010-09-29 | [39 empty] | 2019-10-01 | 2019-10-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T14755523WP | TO->FROM | NORTH WARSAW - TRUMAN 161KV CKT 1 | S | SWPA | GMO | EMINTH |  | 0 | 505502 | TRUMAN 5 161.00 | 541314 | NWARSAW5 161.00 | 0 |  | 1 | 23WP | 234 | 234 | 234 | 98.6 | 98.6395 | 104.7724 | [7 empty] | CATEGORYB | NONSINGLE | OVERTON-TRF | 0 | 0 |  | 0 |  | 0 |  |  |  | 246 |  | SWPA | NORTH WARSAW - TRUMAN 161KV CKT 1 SWPA #1 | Replace wave trap and CTs at Truman. | 286 | 286 |  |  |  | 12 | 12 | [5 empty] | 70000 | 2010-09-29 | [39 empty] | 2019-10-01 | 2019-10-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T7505523WP | TO->FROM | NORTH WARSAW - TRUMAN 161KV CKT 1 | S | SWPA | GMO | EMINTH |  | 0 | 505502 | TRUMAN 5 161.00 | 541314 | NWARSAW5 161.00 | 0 |  | 1 | 23WP | 234 | 234 | 234 | 98.8 | 98.7582 | 103.8977 | [7 empty] | CATEGORYB | SINGLE | 5CALIF UE 161.00 - 5OVERTON 2 161.00 161KV CKT 1 | 0 | 344233 | 5CALIF UE 161.00 | 345411 | 5OVERTON 2 161.00 | 0 |  | 1 |  | 244 |  | SWPA | NORTH WARSAW - TRUMAN 161KV CKT 1 SWPA #1 | Replace wave trap and CTs at Truman. | 286 | 286 |  |  |  | 12 | 12 | [5 empty] | 70000 | 2010-09-29 | [39 empty] | 2019-10-01 | 2019-10-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T14705523WP | TO->FROM | NORTH WARSAW - TRUMAN 161KV CKT 1 | S | SWPA | GMO | EMINTH |  | 0 | 505502 | TRUMAN 5 161.00 | 541314 | NWARSAW5 161.00 | 0 |  | 1 | 23WP | 234 | 234 | 234 | 96.6 | 96.5969 | 101.9158 | [7 empty] | CATEGORYB | NONSINGLE | AI28 | 0 | 0 |  | 0 |  | 0 |  |  |  | 239 |  | SWPA | NORTH WARSAW - TRUMAN 161KV CKT 1 SWPA #1 | Replace wave trap and CTs at Truman. | 286 | 286 |  |  |  | 12 | 12 | [5 empty] | 70000 | 2010-09-29 | [39 empty] | 2019-10-01 | 2019-10-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5215518SP | TO->FROM | BUTLER - WEAVER 138KV CKT 1 | REL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 532991 | WEAVER 4 138.00 | 532987 | BUTLER 4 138.00 | 0 |  | 1 | 18SP | 160 | 160 | 0 | 105.5 | 105.5285 | 108.0631 | [7 empty] | CATEGORYB | SINGLE | BENTON - MIDIAN 138KV CKT 1 | 0 | 532986 | BENTON 4 138.00 | 532990 | MIDIAN 4 138.00 | 0 |  | 1 |  | 173 |  | WERE | BUTLER - WEAVER 138KV CKT 1 | Rebuild 16.31 miles | [53 empty] | 2013-10-01 | 2017-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5615523SP | TO->FROM | BUTLER - WEAVER 138KV CKT 1 | REL | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 532991 | WEAVER 4 138.00 | 532987 | BUTLER 4 138.00 | 0 |  | 1 | 23SP | 160 | 160 | 0 | 108 | 108.0412 | 110.4336 | [7 empty] | CATEGORYB | SINGLE | BENTON - MIDIAN 138KV CKT 1 | 0 | 532986 | BENTON 4 138.00 | 532990 | MIDIAN 4 138.00 | 0 |  | 1 |  | 177 |  | WERE | BUTLER - WEAVER 138KV CKT 1 | Rebuild 16.31 miles | [53 empty] | 2013-10-01 | 2017-06-01
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5445523SP | TO->FROM | CHISHOLM - MAIZEE 4 138.00 138KV CKT 1 | S | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533391 | MAIZEE 4 138.00 | 533035 | CHISHLM4 138.00 | 0 |  | 1 | 23SP | 382 | 382 | 0 |  | 94.9731 | 102.008 | [7 empty] | CATEGORYB | SINGLE | BENTON - WICHITA 345KV CKT 1 | 0 | 532791 | BENTON 7 345.00 | 532796 | WICHITA7 345.00 | 0 |  | 1 |  | 390 |  | WERE | CHISHOLM - MAIZEE 4 138.00 138KV CKT 1 | Upgrade disconnect switches, wavetrap, breaker, jumpers | [12 empty] | 827424 | 2013-07-03 | [39 empty] | 2019-06-01 | 2019-06-01
GI | [10 empty] | CIRCLE - RICE_CO 230KV CKT 1 | U | WERE | MIDW |  |  | 0 | 530686 | RICECO 230.00 | 532871 | CIRCLE 6 230.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | MIDW | CIRCLE - RICE_CO 230KV CKT 1 | Convert from 115kV to 230kV operation | [53 empty] | 2012-10-01 | 2012-11-15
2007-AG3 | AFS9 | [9 empty] | DEARING 138KV | U | WERE |  | SEAST |  |  | 533002 | DEARING4 138.00 | [20 empty] | BASECASE | BASE CASE | [11 empty] | WERE | DEARING 138KV Capacitor | Dearing 138 kV 20 MVAR Capacitor Addition | [53 empty] | 2012-06-01 | 2012-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T3885023SP | TO->FROM | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | REL | WERE | WERE | NEAST | NCENTRAL | 0 | 532852 | JEC 6 230.00 | 532861 | EMANHAT6 230.00 | 0 |  | 1 | 23SP | 446 | 446 | 0 | 105.9 | 105.8614 | 100.9619 | [7 empty] | CATEGORYB | SINGLE | GEARY 7 345.00 - JEFFREY ENERGY CENTER 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532767 | GEARY 7 345.00 | 0 |  | 1 |  | 451 |  | WERE | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | Rebuild existing line to 345 kV operated as 230 kV using bundled 1590 ACSR conductor. Upgrade terminal equipment at JEC and East Manhattan to a minimum emergency rating of 2000 Amps. | [53 empty] | 2019-06-01 | 2019-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3295513WP | TO->FROM | EDWARDSVILLE - MUND 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533282 | MUND 3 115.00 | 533238 | EDWARVL3 115.00 | 0 |  | 1 | 13WP | 173 | 206 | 0 | 107.5 | 107.4637 | 107.8633 | [7 empty] | CATEGORYB | SINGLE | 87th STREET - CRAIG 345KV CKT 1 | 0 | 532775 | 87TH 7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  | 223 |  | KACP | IATAN - NASHUA 345KV CKT 1 | Tap Nashua 345kV bus in Hawthorn - St. Joseph 345 kV line. Build new 345 kV line from Iatan to Nashua,Add Nashua 345/161 kV | [53 empty] | 2013-10-01 | 2015-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2355514WP | TO->FROM | EDWARDSVILLE - MUND 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533282 | MUND 3 115.00 | 533238 | EDWARVL3 115.00 | 0 |  | 1 | 14WP | 173 | 206 | 0 | 108.2 | 108.1921 | 111.7841 | [7 empty] | CATEGORYB | SINGLE | 87th STREET - CRAIG 345KV CKT 1 | 0 | 532775 | 87TH 7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  | 231 |  | KACP | IATAN - NASHUA 345KV CKT 1 | Tap Nashua 345kV bus in Hawthorn - St. Joseph 345 kV line. Build new 345 kV line from Iatan to Nashua,Add Nashua 345/161 kV | [53 empty] | 2013-10-01 | 2015-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3315513WP | FROM->TO | EDWARDSVILLE (EDWRDV4X) 161/115/12.47KV TRANSFORMER CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 1 | 533238 | EDWARVL3 115.00 | 532912 | EDWRDVL5 161.00 | 532940 | EDWRDVL1 12.470 | 1 | 13WP | 168 | 184.8 | 210 | 115.3 | 115.2892 | 115.6733 | [7 empty] | CATEGORYB | SINGLE | 87th STREET - CRAIG 345KV CKT 1 | 0 | 532775 | 87TH 7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  | 214 |  | KACP | IATAN - NASHUA 345KV CKT 1 | Tap Nashua 345kV bus in Hawthorn - St. Joseph 345 kV line. Build new 345 kV line from Iatan to Nashua,Add Nashua 345/161 kV | [53 empty] | 2013-10-01 | 2015-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2375514WP | FROM->TO | EDWARDSVILLE (EDWRDV4X) 161/115/12.47KV TRANSFORMER CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 1 | 533238 | EDWARVL3 115.00 | 532912 | EDWRDVL5 161.00 | 532940 | EDWRDVL1 12.470 | 1 | 14WP | 168 | 184.8 | 210 | 115.9 | 115.8714 | 120.9007 | [7 empty] | CATEGORYB | SINGLE | 87th STREET - CRAIG 345KV CKT 1 | 0 | 532775 | 87TH 7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  | 224 |  | KACP | IATAN - NASHUA 345KV CKT 1 | Tap Nashua 345kV bus in Hawthorn - St. Joseph 345 kV line. Build new 345 kV line from Iatan to Nashua,Add Nashua 345/161 kV | [53 empty] | 2013-10-01 | 2015-06-01
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5035518SP | FROM->TO | EVANS ENERGY CENTER NORTH - MAIZEW 4 138.00 138KV CKT 1 | CP | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533040 | EVANS N4 138.00 | 533390 | MAIZEW 4 138.00 | 0 |  | 1 | 18SP | 382 | 382 | 0 |  | 94.2731 | 101.9603 | [7 empty] | CATEGORYB | SINGLE | BENTON - WICHITA 345KV CKT 1 | 0 | 532791 | BENTON 7 345.00 | 532796 | WICHITA7 345.00 | 0 |  | 1 |  | 390 |  | WERE | EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 #1 | Upgrade disconnect switches, wavetrap, breaker, jumpers | [12 empty] | 827424 | 2013-07-03 | [39 empty] | 2015-06-01 | 2015-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5455523SP | FROM->TO | EVANS ENERGY CENTER NORTH - MAIZEW 4 138.00 138KV CKT 1 | CP | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533040 | EVANS N4 138.00 | 533390 | MAIZEW 4 138.00 | 0 |  | 1 | 23SP | 382 | 382 | 0 | 99.9 | 99.8703 | 106.9148 | [7 empty] | CATEGORYB | SINGLE | BENTON - WICHITA 345KV CKT 1 | 0 | 532791 | BENTON 7 345.00 | 532796 | WICHITA7 345.00 | 0 |  | 1 |  | 409 |  | WERE | EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 #1 | Upgrade disconnect switches, wavetrap, breaker, jumpers | [12 empty] | 827424 | 2013-07-03 | [39 empty] | 2015-06-01 | 2015-06-01
2012-AG1 | AFS4 | CONT-0803 - Hoyt - Stranger 345kV | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T4705514SP | TO->FROM | GOODYEAR JUNCTION - NORTHLAND 115KV CKT 1 | REL | WERE | WERE | NEAST | NEAST | 0 | 533169 | NTHLAND3 115.00 | 533162 | GOODYR 3 115.00 | 0 |  | 1 | 14SP | 159 | 159 | 0 | 113 | 112.9844 | 113.4238 | [7 empty] | CATEGORYB | SINGLE | HOYT - STRANGER CREEK 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532772 | STRANGR7 345.00 | 0 |  | 1 |  | 181 |  | WERE | GOODYEAR JUNCTION - NORTHLAND 115KV CKT 1 | Rebuild 3.44 miles and replace buses and jumper to at least 187 MVA Summer Rate B | [5 empty] | 24 | 24 |  |  |  |  | SCERT estimate | 6641120 | 2013-07-03 | [39 empty] | 2014-06-01 | 2016-06-01
2012-AG1 | AFS4 | CONT-0803 - Hoyt - Stranger 345kV | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T4835518SP | TO->FROM | GOODYEAR JUNCTION - NORTHLAND 115KV CKT 1 | REL | WERE | WERE | NEAST | NEAST | 0 | 533169 | NTHLAND3 115.00 | 533162 | GOODYR 3 115.00 | 0 |  | 1 | 18SP | 159 | 159 | 0 | 106.7 | 106.7449 | 110.057 | [7 empty] | CATEGORYB | SINGLE | HOYT - STRANGER CREEK 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532772 | STRANGR7 345.00 | 0 |  | 1 |  | 175 |  | WERE | GOODYEAR JUNCTION - NORTHLAND 115KV CKT 1 | Rebuild 3.44 miles and replace buses and jumper to at least 187 MVA Summer Rate B | [5 empty] | 24 | 24 |  |  |  |  | SCERT estimate | 6641120 | 2013-07-03 | [39 empty] | 2014-06-01 | 2016-06-01
2012-AG1 | AFS4 | CONT-0803 - Hoyt - Stranger 345kV | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5335523SP | TO->FROM | GOODYEAR JUNCTION - NORTHLAND 115KV CKT 1 | REL | WERE | WERE | NEAST | NEAST | 0 | 533169 | NTHLAND3 115.00 | 533162 | GOODYR 3 115.00 | 0 |  | 1 | 23SP | 159 | 159 | 0 | 110 | 110.0363 | 112.8714 | [7 empty] | CATEGORYB | SINGLE | HOYT - STRANGER CREEK 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532772 | STRANGR7 345.00 | 0 |  | 1 |  | 180 |  | WERE | GOODYEAR JUNCTION - NORTHLAND 115KV CKT 1 | Rebuild 3.44 miles and replace buses and jumper to at least 187 MVA Summer Rate B | [5 empty] | 24 | 24 |  |  |  |  | SCERT estimate | 6641120 | 2013-07-03 | [39 empty] | 2014-06-01 | 2016-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5125518SP | TO->FROM | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | CP | WERE | WERE | NEAST | NEAST | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 | 18SP | 1076 | 1076 | 0 | 98.6 | 98.6103 | 104.0828 | [7 empty] | CATEGORYB | SINGLE | AUBURN ROAD - JEFFREY ENERGY CENTER 230KV CKT 1 | 0 | 532851 | AUBURN 6 230.00 | 532852 | JEC 6 230.00 | 0 |  | 1 |  | 1120 |  | WERE | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | Rebuild the JEC - Hoyt 345kV line as a single circuit with new conductor, poles, and shield wire and substation work | [5 empty] | 48 | 48 |  |  |  |  | Includes redispatch requirements | 49623119 | 2011-03-27 | [39 empty] | 2015-06-01 | 2018-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T4915518SP | TO->FROM | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | CP | WERE | WERE | NEAST | NEAST | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 | 18SP | 1076 | 1076 | 0 | 96.7 | 96.7059 | 101.4601 | [7 empty] | CATEGORYB | SINGLE | JEFFREY ENERGY CENTER - MORRIS COUNTY 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532770 | MORRIS 7 345.00 | 0 |  | 1 |  | 1092 |  | WERE | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | Rebuild the JEC - Hoyt 345kV line as a single circuit with new conductor, poles, and shield wire and substation work | [5 empty] | 48 | 48 |  |  |  |  | Includes redispatch requirements | 49623119 | 2011-03-27 | [39 empty] | 2015-06-01 | 2018-06-01
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T4995518SP | TO->FROM | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | CP | WERE | WERE | NEAST | NEAST | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 | 18SP | 1076 | 1076 | 0 |  | 94.9065 | 101.0921 | [7 empty] | CATEGORYB | SINGLE | SWISSVALE - WEST GARDNER 345KV CKT 1 | 0 | 532774 | SWISVAL7 345.00 | 542965 | W.GRDNR7 345.00 | 0 |  | 1 |  | 1088 |  | WERE | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | Rebuild the JEC - Hoyt 345kV line as a single circuit with new conductor, poles, and shield wire and substation work | [5 empty] | 48 | 48 |  |  |  |  | Includes redispatch requirements | 49623119 | 2011-03-27 | [39 empty] | 2015-06-01 | 2018-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5545523SP | TO->FROM | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | CP | WERE | WERE | NEAST | NEAST | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 | 23SP | 1076 | 1076 | 0 | 100.6 | 100.5517 | 105.0496 | [7 empty] | CATEGORYB | SINGLE | AUBURN ROAD - JEFFREY ENERGY CENTER 230KV CKT 1 | 0 | 532851 | AUBURN 6 230.00 | 532852 | JEC 6 230.00 | 0 |  | 1 |  | 1131 |  | WERE | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | Rebuild the JEC - Hoyt 345kV line as a single circuit with new conductor, poles, and shield wire and substation work | [5 empty] | 48 | 48 |  |  |  |  | Includes redispatch requirements | 49623119 | 2011-03-27 | [39 empty] | 2015-06-01 | 2018-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5415523SP | TO->FROM | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | CP | WERE | WERE | NEAST | NEAST | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 | 23SP | 1076 | 1076 | 0 | 97.6 | 97.5765 | 102.5555 | [7 empty] | CATEGORYB | SINGLE | SWISSVALE - WEST GARDNER 345KV CKT 1 | 0 | 532774 | SWISVAL7 345.00 | 542965 | W.GRDNR7 345.00 | 0 |  | 1 |  | 1104 |  | WERE | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | Rebuild the JEC - Hoyt 345kV line as a single circuit with new conductor, poles, and shield wire and substation work | [5 empty] | 48 | 48 |  |  |  |  | Includes redispatch requirements | 49623119 | 2011-03-27 | [39 empty] | 2015-06-01 | 2018-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T27175523SP | TO->FROM | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | CP | WERE | WERE | NEAST | NEAST | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 | 23SP | 1076 | 1076 | 0 | 98.2 | 98.1657 | 102.4433 | [7 empty] | CATEGORYB | GENOUT | GEN542962 2-IATAN UNIT #2 | 0 | 0 |  | 0 |  | 0 |  |  |  | 1103 |  | WERE | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | Rebuild the JEC - Hoyt 345kV line as a single circuit with new conductor, poles, and shield wire and substation work | [5 empty] | 48 | 48 |  |  |  |  | Includes redispatch requirements | 49623119 | 2011-03-27 | [39 empty] | 2015-06-01 | 2018-06-01
GI | [10 empty] | LYONS - WHEATLAND 115KV CKT 1 #1 | U | WERE | WERE |  |  | 0 | 530620 | LYONS 3 115.00 | 533439 | WHEATLD3 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | WERE | LYONS - WHEATLAND 115KV CKT 1 #1 | Replace CTs | [53 empty] | 2012-10-01 | 2013-07-15
GI | [10 empty] | LYONS - WHEATLAND 115KV CKT 1 #2 | U | WERE | WERE |  |  | 0 | 530620 | LYONS 3 115.00 | 533439 | WHEATLD3 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | WERE | LYONS - WHEATLAND 115KV CKT 1 #2 | Rerate circuit to 1000 amps | [53 empty] | 2012-10-01 | 2013-07-15
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3265513WP | FROM->TO | MOUNDRIDGE (MOUND10X) 138/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE | WERE | SCENTRAL | WEST | 1 | 533429 | MOUNDRG3 115.00 | 533013 | MOUND 4 138.00 | 533096 | MOUNDRI1 13.800 | 1 | 13WP | 100 | 110 | 125 | 135.5 | 135.5249 | 130.9443 | [7 empty] | CATEGORYB | SINGLE | RENO COUNTY - WICHITA 345KV CKT 1 | 0 | 532771 | RENO 7 345.00 | 532796 | WICHITA7 345.00 | 0 |  | 1 |  | 145 |  | WERE | MOUNDRIDGE 138/115KV TRANSFORMER CKT 2 | Install second 138/115 kV transformer at Moundridge. Operate both 138/115 kV transformers normally closed. | 100 | 110 |  |  |  | 24 | 24 | [46 empty] | 2013-10-01 | 2014-12-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3305513WP | TO->FROM | MUND - PENTAGON 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533261 | PENTAGN3 115.00 | 533282 | MUND 3 115.00 | 0 |  | 1 | 13WP | 173 | 206 | 0 | 113.1 | 113.0738 | 113.478 | [7 empty] | CATEGORYB | SINGLE | 87th STREET - CRAIG 345KV CKT 1 | 0 | 532775 | 87TH 7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  | 234 |  | KACP | IATAN - NASHUA 345KV CKT 1 | Tap Nashua 345kV bus in Hawthorn - St. Joseph 345 kV line. Build new 345 kV line from Iatan to Nashua,Add Nashua 345/161 kV | [53 empty] | 2013-10-01 | 2015-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2365514WP | TO->FROM | MUND - PENTAGON 115KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 533261 | PENTAGN3 115.00 | 533282 | MUND 3 115.00 | 0 |  | 1 | 14WP | 173 | 206 | 0 | 113.9 | 113.8791 | 117.4078 | [7 empty] | CATEGORYB | SINGLE | 87th STREET - CRAIG 345KV CKT 1 | 0 | 532775 | 87TH 7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 |  | 242 |  | KACP | IATAN - NASHUA 345KV CKT 1 | Tap Nashua 345kV bus in Hawthorn - St. Joseph 345 kV line. Build new 345 kV line from Iatan to Nashua,Add Nashua 345/161 kV | [53 empty] | 2013-10-01 | 2015-06-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T7415514WP | FROM->TO | WICHITA (WICHT12X) 345/138/13.8KV TRANSFORMER CKT 1 | REL | WERE | WERE | SCENTRAL | SCENTRAL | 1 | 532796 | WICHITA7 345.00 | 533040 | EVANS N4 138.00 | 532830 | WICH12 1 13.800 | 1 | 14WP | 400 | 440 | 500 | 102.5 | 102.4595 | 105.6912 | [7 empty] | CATEGORYB | SINGLE | WICHITA (WICHT11X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532796 | WICHITA7 345.00 | 533040 | EVANS N4 138.00 | 532829 | WICH11 1 13.800 | 1 |  | 466 |  | WERE | Viola 345/138kV Transformer Ckt 1 | Install new 345/138 kV transformer at Viola substation | [5 empty] | 36 | 36 | [5 empty] | 15402744 | 2012-11-16 | [39 empty] | 2014-10-01 | 2018-06-01
2009-AGP1 | [10 empty] | ALTUS SW - NAVAJO 69KV CKT 1 | U | WFEC | WFEC | AEP-KP | AEP-KP | 0 | 521009 | NAVAJO 2 69.000 | 520805 | ALTUSSW2 69.000 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | WFEC | ALTUS SW - NAVAJO 69KV CKT 1 | Upgrade Terminal Equipment at Altus SW, 300-600A, new rating conductor 53/65MVA | [53 empty] | 2013-06-01 | 2013-06-01
2009-AGP1 | [10 empty] | BLUE CANYON - PARADISE 138KV CKT 1 | U | WFEC | WFEC | AEP-OP-I | AEP-KP | 0 | 521129 | BLUCAN5 4 | 521024 | PARADSE4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | WFEC | BLUE CANYON - PARADISE 138KV CKT 1 | Upgrade Paradise to Blue Canyon to 1113 | [53 empty] | 2010-06-01 | 2013-06-01
2009-AGP2 | AFS5 | [9 empty] | CANTON - TALOGA 69KV CKT 1 | U | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521064 | TALOGA 2 69.000 | 520843 | CANTON-2 69.000 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | WFEC | CANTON - TALOGA 69KV CKT 1 | UPGRADE CANTON TO TALOGA TO 336.4 | 106 | 132 |  |  | 9.7 | 24 | 24 |  | 0.04013 | 0.16101 | 0.00252 | [42 empty] | 2011-06-01 | 2013-06-01
2012-AG1 | AFS4-ADD | [5 empty] | 5 | 5 | 2012AG1AFS4ADD1T1985513WP | TO->FROM | ELK CITY - RHWIND4 138.00 138KV CKT 1 | EXP | WFEC | AEPW | WESTERN |  | 0 | 521116 | RHWIND4 138.00 | 511458 | ELKCTY-4 138.00 | 0 |  | 1 | 13WP | 144 | 179 | 179 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  |  | Priority Projects | [54 empty] | 2013-10-01 | 2015-01-01
2006-AG1 | 2006-AG1 | [9 empty] | FT SUPPLY 138/69KV TRANSFORMER CKT 1 | U | WFEC | WFEC |  |  | 1 | 520920 | FTSUPLY4 138 | 520919 | FTSUPLY269.0 | 521182 |  | 2 | [15 empty] | BASECASE | BASE CASE | [11 empty] | WFEC | FT SUPPLY 138/69KV TRANSFORMER CKT 1 | Install 2nd 70 MVA auto at Ft Supply | [53 empty] | 2006-12-01 | 2008-06-01
2012-AG1 | AFS4-ADD | [5 empty] | 5 | 5 | 2012AG1AFS4ADD1T685513WP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | EXP | WFEC | OKGE | ENID |  | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 13WP | 152 | 152 | 0 |  | 999 | 999 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  |  | Priority Projects | [54 empty] | 2013-10-01 | 2015-01-01
2012-AG1 | AFS4NC1 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS4NC11T45514SP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | EXP | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 14SP | 124 | 124 | 0 | 124.3 | 124.328 | 115.4257 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  | 144 |  |  | Priority Projects | [54 empty] | 2013-10-01 | 2015-01-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2405514SP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | EXP | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 14SP | 124 | 124 | 0 | 109.7 | 109.697 | 101.3805 | [7 empty] | CATEGORYB | SINGLE | KNOBHILL - MOORELAND 138KV CKT 1 | 0 | 514795 | KNOBHIL4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 |  | 126 |  |  | Priority Projects | [54 empty] | 2013-10-01 | 2015-01-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T12345514SP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | EXP | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 14SP | 124 | 124 | 0 | 109.7 | 109.6848 | 101.3699 | [7 empty] | CATEGORYB | SINGLE | KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 514794 | KNOBHIL2 69.000 | 514795 | KNOBHIL4 138.00 | 515732 | KNOBHIL1 13.200 | 1 |  | 126 |  |  | Priority Projects | [54 empty] | 2013-10-01 | 2015-01-01
GEN | [10 empty] | GRACMNT4 138.00 - WASHITA 138KV CKT 2 OKGE | U | WFEC | OKGE | AEP-CS | ARDMORE | 0 | 521089 | WASHITA4 138.00 | 515802 | GRACMNT4 138.00 | 0 |  | 2 | [15 empty] | BASECASE | BASE CASE | [11 empty] | OKGE | GRACMNT4 138.00 - WASHITA 138KV CKT 2 OKGE | Build 138kV Terminal. | [53 empty] | 2012-01-01 | 2012-01-01
GEN | [10 empty] | GRACMNT4 138.00 - WASHITA 138KV CKT 2 WFEC | U | WFEC | OKGE | AEP-CS | ARDMORE | 0 | 521089 | WASHITA4 138.00 | 515802 | GRACMNT4 138.00 | 0 |  | 2 | [15 empty] | BASECASE | BASE CASE | [11 empty] | WFEC | GRACMNT4 138.00 - WASHITA 138KV CKT 2 WFEC | Build approximately 6 miles of 138kV. | [53 empty] | 2012-01-01 | 2012-01-01
2005-AG2 | 2005-AG2 | [9 empty] | HUGO POWER PLANT - VALLIANT 138KV CKT 1 | U | WFEC | AEPW |  |  | 0 | 521157 | HUGO PP4 138 | 510911 | VALIANT4 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | AEPW | HUGO POWER PLANT - VALLIANT 345 KV AEPW | Vallient 345 KV line terminal | [53 empty] | 2012-07-01 | 2012-07-01
2005-AG2 | 2005-AG2 | [9 empty] | HUGO POWER PLANT - VALLIANT 345KV CKT 1 AEPW | U | WFEC | AEPW |  |  | 0 | 521157 | HUGO PP4 138 | 510911 | VALIANT4 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | AEPW | HUGO POWER PLANT - VALLIANT 345KV CKT 1 AEPW | Vallient 345 KV line terminal | [53 empty] | 2012-07-01 | 2012-07-01
2005-AG2 | 2005-AG2 | [9 empty] | HUGO POWER PLANT - VALLIANT 345KV CKT 1 WFEC | U | WFEC | AEPW |  |  | 0 | 521157 | HUGO PP4 138 | 510911 | VALIANT4 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | WFEC | HUGO POWER PLANT - VALLIANT 345KV CKT 1 WFEC | New 19 miles 345 KV | [53 empty] | 2012-07-01 | 2012-07-01
2005-AG2 | 2005-AG2 | [9 empty] | HUGO POWER PLANT 345/138KV TRANSFORMER CKT 1 | U | WFEC | AEPW |  |  | 1 | 521157 | HUGO PP4 138 | 520948 | HUGO PP4 138.00 | 521189 |  | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | WFEC | HUGO POWER PLANT 345/138KV TRANSFORMER CKT 1 | New 345/138 kv Auto | [53 empty] | 2012-07-01 | 2012-07-01
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3755523SP | TO->FROM | PAOLI - PAYNE 138.00 138KV CKT 1 | REL | WFEC | WFEC | AEP-IM-I | AEP-IM-I | 0 | 520888 | PAYNE 138.00 | 521023 | PAOLI 4 138.00 | 0 |  | 1 | 23SP | 132 | 143 | 143 | 103.9 | 103.9043 | 101.4416 | [7 empty] | CATEGORYB | SINGLE | ANADARKO - GEORGIA 138KV CKT 1 | 0 | 520814 | ANADARK4 138.00 | 520923 | GEORGIA4 138.00 | 0 |  | 1 |  | 146 |  | WFEC | PAOLI - PAYNE 138.00 138KV CKT 1 | Reset CT | [11 empty] | SPP Estimate | 225000 | 2010-01-01 | [39 empty] | 2019-06-01 | 2019-06-01
2009-AGP2 | AFS5 | [9 empty] | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | U | WFEC | WFEC | AEP-OP | AEP-OP | 2 | 521065 | TALOGA 4 138.00 | 521064 | TALOGA 2 69.000 | 521178 | TLGTERT 13.800 | 1 | [15 empty] | BASECASE | BASE CASE | [11 empty] | WFEC | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | Auto XFMR 56 to 112MVA | 112 | 112 | 112 | 112 |  | 24 | 24 | [46 empty] | 2010-10-01 | 2013-06-01

## tblAllFacilityLog < 100%
STUDYDES | STUDYDES2 | EVENTTYPE | AssessmentSOLUTIONTYPE | AssessmenFDNS-TERMINATION | SOLUTIONTYPE | FDNS-TERMINATION | GROUP | SCENARIO | FGName | DIRECTION | FacilityName | FacilityUpgradeCode | ModelArea1 | ModelArea2 | FZONENAME | TZONENAME | MONTFLAG | MONTFB | MONTFNAME | MONTTB1 | MONTTNAME1 | MONTTB2 | MONTTNAME2 | MONTCKT | Case | RATEA | RATEB | RATEC | Assessment Loading | BaseCaseLoading | TransferCaseLoading | NameOfBusWithMonitoredVoltage | Assessment Voltage | BaseCaseVoltage | TransferCaseVoltage | VINIT | VMIN | VMAX | CATEGORY | CONTTYPE | CONTNAME | CONTXFMRFLAG | CONTFB | CONTFNAME | CONTTB1 | CONTTNAME1 | CONTTB2 | CONTTNAME2 | CONTCKT | TransmissionProviderCommentsNotes | RequiredRateB | TransmissionOwnerComments | OwnerDesignation | UpgradeName | UpgradeComponentWithinFacility | NewSummerA | NewSummerB | NewOtherA | NewOtherB | DistToConstruct | TotalLead | ConstructionLeadOnly | NewOrConstructWhileEnergized | NewR | NewX | NewB | CommentsRegardingUpgradeRequirements | NewCost | EffDate | NetPlantDate | ReusableEx_GrossValue | ReusableEx_NetValue | Reusable_EndofDepr | SalvageValue | NewCostWhileExpediting | EffDateExpedited | StartDeprExpedited | EndDeprExpedited | NetPlantDateExpedited | ReusableEx_GrossExpedited | ReusableEx_NetExpedited | Reusable_EndofDeprExpedited | SalvageValueExpedited | Generation 1 Owner & Unit (Name) | Generation 1 Redispatch Cost ($) | Generation 1 Redispatch Date (M/D/Y) | Generation 2 Owner & Unit (Name) | Generation 2 Redispatch Cost ($) | Generation 2 Redispatch Date (M/D/Y) | Generation 3 Owner & Unit (Name) | Generation 3 Redispatch Cost ($) | Generation 3 Redispatch Date (M/D/Y) | ActualCompletion | ActualNewCost | ActualNetPlantDate | ActualReusableEx_GrossValue | ActualReusableEx_NetValue | ActualReusable_EndofDepr | ActualSalvageValue | Actual_NewCostWhileExpediting | Actual_StartDeprExp | Actual_EndDeprExp | Actual_NetPlantDateExpedited | ActualReusableEx_GrossExpedited | ActualReusableEx_NetExpedited | ActualReusable_EndofDeprExpedited | Actual_SalvageValueExpedited | SPPReliabilityDate | DUN | EOC | EarliestDate
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T21835518SP | TO->FROM | 7JASPER 345.00 - BLACKBERRY 345KV CKT 1 | E | AECI | AECI | KAMO | KAMO | 0 | 300739 | 7BLACKBERRY 345.00 | 300949 | 7JASPER 345.00 | 0 |  | 1 | 18SP | 870 | 870 | 0 |  | 86.3295 | 96.8 | [7 empty] | CATEGORYB | NONSINGLE | GRDA-OPGD-05 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 843
2012-AG1 | AFS4 | INVALID |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2085518SP | TO->FROM | 7JASPER 345.00 - BLACKBERRY 345KV CKT 1 | E | AECI | AECI | KAMO | KAMO | 0 | 300739 | 7BLACKBERRY 345.00 | 300949 | 7JASPER 345.00 | 0 |  | 1 | 18SP | 870 | 870 | 0 |  | 86.0929 | 96.4736 | [7 empty] | CATEGORYB | SINGLE | GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 | 0 | 512650 | GRDA1 7 345.00 | 512750 | TONECE7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 840
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T19455023SP | FROM->TO | 36TH & LEWIS - 52ND & DELAWARE TAP 138KV CKT 1 | E | AEPW | AEPW | PSO_TULSA | PSO_TULSA | 0 | 509800 | 36LEWIS4 138.00 | 509776 | 52DELTP4 138.00 | 0 |  | 1 | 23SP | 278 | 278 | 0 | 97.6 | 97.6475 | 97.6 | [7 empty] | CATEGORYB | NONSINGLE | SPP-AEPW-18 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 272
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T1735023SP | FROM->TO | 36TH & LEWIS - 52ND & DELAWARE TAP 138KV CKT 1 | E | AEPW | AEPW | PSO_TULSA | PSO_TULSA | 0 | 509800 | 36LEWIS4 138.00 | 509776 | 52DELTP4 138.00 | 0 |  | 1 | 23SP | 278 | 278 | 0 | 97.4 | 97.3894 | 97.4 | [7 empty] | CATEGORYB | SINGLE | ORU WEST TAP - SOUTHERN HILLS EAST TAP 138KV CKT 1 | 0 | 509813 | SHILETP4 138.00 | 509853 | ORU-WTP4 138.00 | 0 |  | 1 | Transfer Loading < 100% | 271
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 0 | 2012AG1AFS41T13965014SP | TO->FROM | 52ND & DELAWARE WEST TAP - RIVERSIDE STATION 138KV CKT 1 | E | AEPW | AEPW | PSO_TULSA | PSO_TULSA | 0 | 509783 | R.S.S.-4 138.00 | 509814 | 52DELWT4 138.00 | 0 |  | 1 | 14SP | 168 | 168 | 0 |  | 89.3365 | 98.4 | [7 empty] | CATEGORYB | NONSINGLE | SPP-AEPW-38 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 166
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T21745518SP | TO->FROM | 52ND & DELAWARE WEST TAP - RIVERSIDE STATION 138KV CKT 1 | E | AEPW | AEPW | PSO_TULSA | PSO_TULSA | 0 | 509783 | R.S.S.-4 138.00 | 509814 | 52DELWT4 138.00 | 0 |  | 1 | 18SP | 168 | 168 | 0 | 95.5 | 95.5057 | 99.2 | [7 empty] | CATEGORYB | NONSINGLE | SPP-AEPW-38 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 167
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T24585523SP | TO->FROM | 52ND & DELAWARE WEST TAP - RIVERSIDE STATION 138KV CKT 1 | E | AEPW | AEPW | PSO_TULSA | PSO_TULSA | 0 | 509783 | R.S.S.-4 138.00 | 509814 | 52DELWT4 138.00 | 0 |  | 1 | 23SP | 168 | 168 | 0 |  | 68.4423 | 95.5 | [7 empty] | CATEGORYB | NONSINGLE | SPP-AEPW-38 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 161
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T1715023SP | FROM->TO | 77TH & MEMORIAL WEST - EAST 61ST STREET 138KV CKT 1 | E | AEPW | AEPW | PSO_TULSA | PSO_TULSA | 0 | 509766 | 77MEM-W4 138.00 | 509831 | E.61ST-4 138.00 | 0 |  | 1 | 23SP | 191 | 191 | 0 | 96.3 | 96.284 | 97.2 | [7 empty] | CATEGORYB | SINGLE | 36TH & LEWIS - TULSA POWER STATION 138KV CKT 1 | 0 | 509788 | T.P.S.-4 138.00 | 509800 | 36LEWIS4 138.00 | 0 |  | 1 | Transfer Loading < 100% | 186
2012-AG1 | AFS4 | INVALID | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T1695023SP | FROM->TO | 77TH & MEMORIAL WEST - EAST 61ST STREET 138KV CKT 1 | E | AEPW | AEPW | PSO_TULSA | PSO_TULSA | 0 | 509766 | 77MEM-W4 138.00 | 509831 | E.61ST-4 138.00 | 0 |  | 1 | 23SP | 191 | 191 | 0 | 95.8 | 95.7868 | 97.0254 | [7 empty] | CATEGORYB | SINGLE | ORU WEST TAP - RIVERSIDE STATION 138KV CKT 1 | 0 | 509783 | R.S.S.-4 138.00 | 509853 | ORU-WTP4 138.00 | 0 |  | 1 | Transfer Loading < 100% | 186
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T1385013SP | TO->FROM | BLUEBELL - PRATTVILLE 138KV CKT 1 | E | AEPW | OKGE | PSO_TULSA | MUSKOGEE | 0 | 509758 | PRATTV-4 138.00 | 515242 | BLUEBEL4 138.00 | 0 |  | 1 | 13SP | 212 | 212 | 0 | 97.8 | 97.752 | 97.3 | [7 empty] | CATEGORYB | SINGLE | EXPGLNT4 138.00 - RIVERSIDE STATION 138KV CKT 1 | 0 | 509783 | R.S.S.-4 138.00 | 515473 | EXPGLNT4 138.00 | 0 |  | 1 | Transfer Loading < 100% | 207
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T1855013SP | TO->FROM | BLUEBELL - PRATTVILLE 138KV CKT 1 | E | AEPW | OKGE | PSO_TULSA | MUSKOGEE | 0 | 509758 | PRATTV-4 138.00 | 515242 | BLUEBEL4 138.00 | 0 |  | 1 | 13SP | 212 | 212 | 0 | 96.9 | 96.9363 | 96.4 | [7 empty] | CATEGORYB | SINGLE | BEELINE - EXPGLNT4 138.00 138KV CKT 1 | 0 | 515247 | BEELINE4 138.00 | 515473 | EXPGLNT4 138.00 | 0 |  | 1 | Transfer Loading < 100% | 205
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T945014SP | TO->FROM | BLUEBELL - PRATTVILLE 138KV CKT 1 | E | AEPW | OKGE | PSO_TULSA | MUSKOGEE | 0 | 509758 | PRATTV-4 138.00 | 515242 | BLUEBEL4 138.00 | 0 |  | 1 | 14SP | 212 | 212 | 0 | 97.4 | 97.3958 | 97.4 | [7 empty] | CATEGORYB | SINGLE | EXPGLNT4 138.00 - RIVERSIDE STATION 138KV CKT 1 | 0 | 509783 | R.S.S.-4 138.00 | 515473 | EXPGLNT4 138.00 | 0 |  | 1 | Transfer Loading < 100% | 207
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T1605014SP | TO->FROM | BLUEBELL - PRATTVILLE 138KV CKT 1 | E | AEPW | OKGE | PSO_TULSA | MUSKOGEE | 0 | 509758 | PRATTV-4 138.00 | 515242 | BLUEBEL4 138.00 | 0 |  | 1 | 14SP | 212 | 212 | 0 | 96.5 | 96.5479 | 96.6 | [7 empty] | CATEGORYB | SINGLE | BEELINE - EXPGLNT4 138.00 138KV CKT 1 | 0 | 515247 | BEELINE4 138.00 | 515473 | EXPGLNT4 138.00 | 0 |  | 1 | Transfer Loading < 100% | 205
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3335513SP | FROM->TO | BONANZA - HACKETT AECC 161KV CKT 1 | E | AEPW | AEPW | GREENWOOD | GREENWD AECC | 0 | 507182 | BONANZA5 161.00 | 504181 | HACKETT 5 161.00 | 0 |  | 1 | 13SP | 158 | 178 | 0 |  | 94.0331 | 95.8 | [7 empty] | CATEGORYB | SINGLE | AES - TARBY 161KV CKT 1 | 0 | 515262 | AES 5 161.00 | 515264 | TARBY 5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 171
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2725514SP | FROM->TO | BONANZA - HACKETT AECC 161KV CKT 1 | E | AEPW | AEPW | GREENWOOD | GREENWD AECC | 0 | 507182 | BONANZA5 161.00 | 504181 | HACKETT 5 161.00 | 0 |  | 1 | 14SP | 158 | 178 | 0 |  | 94.9766 | 97.3 | [7 empty] | CATEGORYB | SINGLE | AES - TARBY 161KV CKT 1 | 0 | 515262 | AES 5 161.00 | 515264 | TARBY 5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 174
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3555523SP | FROM->TO | BONANZA - HACKETT AECC 161KV CKT 1 | E | AEPW | AEPW | GREENWOOD | GREENWD AECC | 0 | 507182 | BONANZA5 161.00 | 504181 | HACKETT 5 161.00 | 0 |  | 1 | 23SP | 158 | 178 | 0 | 97.4 | 97.3781 | 98.3 | [7 empty] | CATEGORYB | SINGLE | AES - TARBY 161KV CKT 1 | 0 | 515262 | AES 5 161.00 | 515264 | TARBY 5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 175
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T855513SP | FROM->TO | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | E | AEPW | AEPW | FAYETTEVILLE | FAYETVL AECC | 0 | 506944 | CHAMSPR5 161.00 | 504020 | FARMNGTN 5 161.00 | 0 |  | 1 | 13SP | 294 | 317 | 0 | 99 | 99.03 | 99.1 | [7 empty] | CATEGORYB | SINGLE | FLINT CREEK - GENTRY REC 161KV CKT 1 | 0 | 504201 | GENTRY 5 161.00 | 506934 | FLINTCR5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 315
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T875513SP | FROM->TO | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | E | AEPW | AEPW | FAYETTEVILLE | FAYETVL AECC | 0 | 506944 | CHAMSPR5 161.00 | 504020 | FARMNGTN 5 161.00 | 0 |  | 1 | 13SP | 294 | 317 | 0 | 98.7 | 98.6776 | 98.7 | [7 empty] | CATEGORYB | SINGLE | BENTONVILLE 279TH STREET - GENTRY REC 161KV CKT 1 | 0 | 504201 | GENTRY 5 161.00 | 506960 | BEN279_5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 313
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1005513SP | FROM->TO | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | E | AEPW | AEPW | FAYETTEVILLE | FAYETVL AECC | 0 | 506944 | CHAMSPR5 161.00 | 504020 | FARMNGTN 5 161.00 | 0 |  | 1 | 13SP | 294 | 317 | 0 | 98.3 | 98.3266 | 98.4 | [7 empty] | CATEGORYB | SINGLE | BENTONVILLE 279TH STREET - EAST CENTERTON 161KV CKT 1 | 0 | 506929 | ECNTRTN5 161.00 | 506960 | BEN279_5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 312
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T975514SP | FROM->TO | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | E | AEPW | AEPW | FAYETTEVILLE | FAYETVL AECC | 0 | 506944 | CHAMSPR5 161.00 | 504020 | FARMNGTN 5 161.00 | 0 |  | 1 | 14SP | 294 | 317 | 0 | 98.3 | 98.2611 | 98.7 | [7 empty] | CATEGORYB | SINGLE | DYESS - SOUTH SPRINGDALE 161KV CKT 1 | 0 | 506927 | DYESS 5 161.00 | 506949 | SOSPRDL5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 313
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T785514SP | FROM->TO | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | E | AEPW | AEPW | FAYETTEVILLE | FAYETVL AECC | 0 | 506944 | CHAMSPR5 161.00 | 504020 | FARMNGTN 5 161.00 | 0 |  | 1 | 14SP | 294 | 317 | 0 | 97.3 | 97.3162 | 97.7 | [7 empty] | CATEGORYB | SINGLE | ELM SPRINGS REC - TONTITOWN 161KV CKT 1 | 0 | 504010 | ELMSPRGS 5 161.00 | 506957 | TONTITN5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 310
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T855514SP | FROM->TO | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | E | AEPW | AEPW | FAYETTEVILLE | FAYETVL AECC | 0 | 506944 | CHAMSPR5 161.00 | 504020 | FARMNGTN 5 161.00 | 0 |  | 1 | 14SP | 294 | 317 | 0 |  | 94.868 | 95.3 | [7 empty] | CATEGORYB | SINGLE | CARLY ROAD - DYESS 161KV CKT 1 | 0 | 504274 | CARLEYRD 5 161.00 | 506927 | DYESS 5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 303
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1075518SP | FROM->TO | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | E | AEPW | AEPW | FAYETTEVILLE | FAYETVL AECC | 0 | 506944 | CHAMSPR5 161.00 | 504020 | FARMNGTN 5 161.00 | 0 |  | 1 | 18SP | 294 | 360 | 0 |  | 86.0938 | 96.8 | [7 empty] | CATEGORYB | SINGLE | DYESS - SOUTH SPRINGDALE 161KV CKT 1 | 0 | 506927 | DYESS 5 161.00 | 506949 | SOSPRDL5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 349
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T935518SP | FROM->TO | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | E | AEPW | AEPW | FAYETTEVILLE | FAYETVL AECC | 0 | 506944 | CHAMSPR5 161.00 | 504020 | FARMNGTN 5 161.00 | 0 |  | 1 | 18SP | 294 | 360 | 0 |  | 85.8247 | 96.3 | [7 empty] | CATEGORYB | SINGLE | ELM SPRINGS REC - TONTITOWN 161KV CKT 1 | 0 | 504010 | ELMSPRGS 5 161.00 | 506957 | TONTITN5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 347
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1525523SP | FROM->TO | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | E | AEPW | AEPW | FAYETTEVILLE | FAYETVL AECC | 0 | 506944 | CHAMSPR5 161.00 | 504020 | FARMNGTN 5 161.00 | 0 |  | 1 | 23SP | 294 | 360 | 0 |  | 88.7644 | 98.9 | [7 empty] | CATEGORYB | SINGLE | OSBORNT5 161.00 - SOUTH SPRINGDALE 161KV CKT 1 | 0 | 506949 | SOSPRDL5 161.00 | 506984 | OSBORNT5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 357
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1175523SP | FROM->TO | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | E | AEPW | AEPW | FAYETTEVILLE | FAYETVL AECC | 0 | 506944 | CHAMSPR5 161.00 | 504020 | FARMNGTN 5 161.00 | 0 |  | 1 | 23SP | 294 | 360 | 0 |  | 87.9218 | 98.7 | [7 empty] | CATEGORYB | SINGLE | CARLY ROAD - DYESS 161KV CKT 1 | 0 | 504274 | CARLEYRD 5 161.00 | 506927 | DYESS 5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 356
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1325523SP | FROM->TO | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | E | AEPW | AEPW | FAYETTEVILLE | FAYETVL AECC | 0 | 506944 | CHAMSPR5 161.00 | 504020 | FARMNGTN 5 161.00 | 0 |  | 1 | 23SP | 294 | 360 | 0 |  | 88.3272 | 98.3 | [7 empty] | CATEGORYB | SINGLE | DYESS - TONTITOWN 161KV CKT 1 | 0 | 506927 | DYESS 5 161.00 | 506957 | TONTITN5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 354
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T935523WP | FROM->TO | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | E | AEPW | AEPW | FAYETTEVILLE | FAYETVL AECC | 0 | 506944 | CHAMSPR5 161.00 | 504020 | FARMNGTN 5 161.00 | 0 |  | 1 | 23WP | 294 | 360 | 0 | 95.1 | 95.1435 | 96.3 | [7 empty] | CATEGORYB | SINGLE | CHAMBER SPRINGS - TONTITOWN 345KV CKT 1 | 0 | 506945 | CHAMSPR7 345.00 | 506959 | TONTITN7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 347
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T8965523WP | FROM->TO | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | E | AEPW | AEPW | FAYETTEVILLE | FAYETVL AECC | 0 | 506944 | CHAMSPR5 161.00 | 504020 | FARMNGTN 5 161.00 | 0 |  | 1 | 23WP | 294 | 360 | 0 | 95.1 | 95.0971 | 96.2 | [7 empty] | CATEGORYB | SINGLE | TONTITOWN () 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 506957 | TONTITN5 161.00 | 506959 | TONTITN7 345.00 | 506958 | TONTITN1 13.800 | 1 | Transfer Loading < 100% | 347
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T15523WP | FROM->TO | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | E | AEPW | AEPW | FAYETTEVILLE | FAYETVL AECC | 0 | 506944 | CHAMSPR5 161.00 | 504020 | FARMNGTN 5 161.00 | 0 |  | 1 | 23WP | 294 | 360 | 0 |  | 94.2458 | 95 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 342
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T21085513SP | FROM->TO | DIANA - PERDUE 138KV CKT 1 | E | AEPW | AEPW | NWLA_NTEC | MT PLES NTEC | 0 | 508831 | DIANA 4 138.00 | 508351 | PERDUE 4 138.00 | 0 |  | 1 | 13SP | 246 | 272 | 0 | 99.9 | 99.8842 | 99.9 | [7 empty] | CATEGORYB | NONSINGLE | SPP-AEPW-27 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 272
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1975513SP | FROM->TO | DIANA - PERDUE 138KV CKT 1 | E | AEPW | AEPW | NWLA_NTEC | MT PLES NTEC | 0 | 508831 | DIANA 4 138.00 | 508351 | PERDUE 4 138.00 | 0 |  | 1 | 13SP | 246 | 272 | 0 | 99.6 | 99.6299 | 99.6 | [7 empty] | CATEGORYB | SINGLE | CROCKETT - LATEXO (ETEC) 138KV CKT 1 | 0 | 509240 | CROCKET4 138.00 | 509323 | LATEXO 4 138.00 | 0 |  | 1 | Transfer Loading < 100% | 271
2012-AG1 | AFS4 | SPP_FG-5287 - DIAPERDIAPIR | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1775513SP | FROM->TO | DIANA - PERDUE 138KV CKT 1 | E | AEPW | AEPW | NWLA_NTEC | MT PLES NTEC | 0 | 508831 | DIANA 4 138.00 | 508351 | PERDUE 4 138.00 | 0 |  | 1 | 13SP | 246 | 272 | 0 | 99.5 | 99.4851 | 99.4 | [7 empty] | CATEGORYB | SINGLE | DIANA - PIRKEY 345KV CKT 1 | 0 | 508563 | PIRKEY 7 345.00 | 508832 | DIANA 7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 271
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T865513SP | FROM->TO | EAST ROGERS - ROGERS WEST REC 161KV CKT 1 | E | AEPW | AEPW | FAYETTEVILLE | FAYETVL AECC | 0 | 506931 | EROGERS5 161.00 | 504200 | WROGERS 5 161.00 | 0 |  | 1 | 13SP | 288 | 339 | 0 | 95.2 | 95.2122 | 95.2 | [7 empty] | CATEGORYB | SINGLE | FLINT CREEK - GENTRY REC 161KV CKT 1 | 0 | 504201 | GENTRY 5 161.00 | 506934 | FLINTCR5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 323
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1435523SP | TO->FROM | FARMINGTON - FARMINGTON AECC 161KV CKT 1 | E | AEPW | AEPW | FAYETVL AECC | FAYETTEVILLE | 0 | 504020 | FARMNGTN 5 161.00 | 506956 | FARMING5 161.00 | 0 |  | 1 | 23SP | 294 | 317 | 0 | 100 | 100.0059 | 96.4 | [7 empty] | CATEGORYB | SINGLE | CHAMBER SPRINGS - TONTITOWN 345KV CKT 1 | 0 | 506945 | CHAMSPR7 345.00 | 506959 | TONTITN7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 306
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T15425523SP | TO->FROM | FARMINGTON - FARMINGTON AECC 161KV CKT 1 | E | AEPW | AEPW | FAYETVL AECC | FAYETTEVILLE | 0 | 504020 | FARMNGTN 5 161.00 | 506956 | FARMING5 161.00 | 0 |  | 1 | 23SP | 294 | 317 | 0 | 99.9 | 99.923 | 96.3 | [7 empty] | CATEGORYB | SINGLE | TONTITOWN () 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 506957 | TONTITN5 161.00 | 506959 | TONTITN7 345.00 | 506958 | TONTITN1 13.800 | 1 | Transfer Loading < 100% | 306
2012-AG1 | AFS4 | SPP_FG-5277 - FLITONCLACHA | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1075513SP | FROM->TO | FLINT CREEK - TONTITOWN 161KV CKT 1 | E | AEPW | AEPW | FAYETTEVILLE | FAYETTEVILLE | 0 | 506934 | FLINTCR5 161.00 | 506957 | TONTITN5 161.00 | 0 |  | 1 | 13SP | 314 | 348 | 0 | 95.8 | 95.7614 | 95.9 | [7 empty] | CATEGORYB | SINGLE | CHAMBER SPRINGS - CLARKSVILLE 345KV CKT 1 | 0 | 506945 | CHAMSPR7 345.00 | 509745 | CLARKSV7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 334
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1635523SP | FROM->TO | HUGHES SPRINGS - JENKINS REC T 69KV CKT 1 | E | AEPW | AEPW | MT. PLEASANT | MT. PLEASANT | 0 | 508291 | HUGHES 2 69.000 | 508293 | JENKNST2 69.000 | 0 |  | 1 | 23SP | 39 | 39 | 0 | 97.8 | 97.8165 | 98.8 | [7 empty] | CATEGORYB | SINGLE | LONE STAR POWER PLANT - LONE STAR SOUTH 69KV CKT 1 | 0 | 508296 | LSSOUTH2 69.000 | 508320 | LONSTAR2 69.000 | 0 |  | 1 | Transfer Loading < 100% | 39
2012-AG1 | AFS4 | SPP_FG- |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T15513WP | TO->FROM | OKLAUN - OKLAUNION 345KV CKT 1 | E | AEPW | ERCOT | PSO_WESTERN |  | 0 | 511456 | O.K.U.-7 345.00 | 599891 | OKLAUN 7 345.00 | 0 |  | 1 | 13WP | 250 | 250 | 0 |  | 5.158 | 98 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 245
2012-AG1 | AFS4 | SPP_FG- |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T25514SP | TO->FROM | OKLAUN - OKLAUNION 345KV CKT 1 | E | AEPW | ERCOT | PSO_WESTERN |  | 0 | 511456 | O.K.U.-7 345.00 | 599891 | OKLAUN 7 345.00 | 0 |  | 1 | 14SP | 250 | 250 | 0 |  | 5.1733 | 97.7 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 245
2012-AG1 | AFS4 | SPP_FG- |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T15514WP | TO->FROM | OKLAUN - OKLAUNION 345KV CKT 1 | E | AEPW | ERCOT | PSO_WESTERN |  | 0 | 511456 | O.K.U.-7 345.00 | 599891 | OKLAUN 7 345.00 | 0 |  | 1 | 14WP | 250 | 250 | 0 |  | 5.1912 | 97.4 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 244
2012-AG1 | AFS4 | SPP_FG- |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T45518SP | TO->FROM | OKLAUN - OKLAUNION 345KV CKT 1 | E | AEPW | ERCOT | PSO_WESTERN |  | 0 | 511456 | O.K.U.-7 345.00 | 599891 | OKLAUN 7 345.00 | 0 |  | 1 | 18SP | 250 | 250 | 0 |  | 5.2025 | 97.7 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 245
2012-AG1 | AFS4 | SPP_FG- |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T15518WP | TO->FROM | OKLAUN - OKLAUNION 345KV CKT 1 | E | AEPW | ERCOT | PSO_WESTERN |  | 0 | 511456 | O.K.U.-7 345.00 | 599891 | OKLAUN 7 345.00 | 0 |  | 1 | 18WP | 250 | 250 | 0 |  | 5.2094 | 97.7 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 245
2012-AG1 | AFS4 | SPP_FG- |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T45523SP | TO->FROM | OKLAUN - OKLAUNION 345KV CKT 1 | E | AEPW | ERCOT | PSO_WESTERN |  | 0 | 511456 | O.K.U.-7 345.00 | 599891 | OKLAUN 7 345.00 | 0 |  | 1 | 23SP | 250 | 250 | 0 |  | 5.211 | 97.7 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 245
2012-AG1 | AFS4 | SPP_FG- |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T25523WP | TO->FROM | OKLAUN - OKLAUNION 345KV CKT 1 | E | AEPW | ERCOT | PSO_WESTERN |  | 0 | 511456 | O.K.U.-7 345.00 | 599891 | OKLAUN 7 345.00 | 0 |  | 1 | 23WP | 250 | 250 | 0 |  | 5.2162 | 97.8 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 245
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 0 | 2012AG1AFS41T1205013SP | TO->FROM | ROCK HILL - SPRINGRIDGE PAN-HARR REC 138KV CKT 1 | E | AEPW | AEPW | SHREVE_NTEC | ROCKHILL | 0 | 507757 | SPRIDGE4 138.00 | 509083 | ROKHILL4 138.00 | 0 |  | 1 | 13SP | 136 | 136 | 0 |  | 82.2621 | 98.4 | [7 empty] | CATEGORYB | SINGLE | KEATCHIE REC - STONEWALL 138KV CKT 1 | 0 | 509050 | KEATCHI4 138.00 | 509052 | STONWAL4 138.00 | 0 |  | 1 | Transfer Loading < 100% | 134
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 0 | 2012AG1AFS41T1255013SP | TO->FROM | ROCK HILL - SPRINGRIDGE PAN-HARR REC 138KV CKT 1 | E | AEPW | AEPW | SHREVE_NTEC | ROCKHILL | 0 | 507757 | SPRIDGE4 138.00 | 509083 | ROKHILL4 138.00 | 0 |  | 1 | 13SP | 136 | 136 | 0 |  | 80.9638 | 97.1 | [7 empty] | CATEGORYB | SINGLE | GEORGIA-PACIFIC - LOGANSPORT 138KV CKT 1 | 0 | 509064 | GEORPAC4 138.00 | 509071 | LOGANSP4 138.00 | 0 |  | 1 | Transfer Loading < 100% | 133
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T18975514SP | TO->FROM | ROCK HILL - SPRINGRIDGE PAN-HARR REC 138KV CKT 1 | E | AEPW | AEPW | SHREVE_NTEC | ROCKHILL | 0 | 507757 | SPRIDGE4 138.00 | 509083 | ROKHILL4 138.00 | 0 |  | 1 | 14SP | 136 | 136 | 0 | 95.8 | 95.7864 | 96.3 | [7 empty] | CATEGORYB | NONSINGLE | SPP-AEPW-30 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 131
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T1725023SP | FROM->TO | SOUTH HUDSON - TULSA SOUTHEAST 138KV CKT 1 | E | AEPW | AEPW | PSO_TULSA | PSO_TULSA | 0 | 509833 | S.HUD.-4 138.00 | 509811 | T.S.E.-4 138.00 | 0 |  | 1 | 23SP | 168 | 168 | 0 | 96.4 | 96.3849 | 97.5 | [7 empty] | CATEGORYB | SINGLE | 36TH & LEWIS - TULSA POWER STATION 138KV CKT 1 | 0 | 509788 | T.P.S.-4 138.00 | 509800 | 36LEWIS4 138.00 | 0 |  | 1 | Transfer Loading < 100% | 164
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T815014SP | TO->FROM | WELSH REC - WILKES 138KV CKT 1 | E | AEPW | AEPW | NWLA-EAST TX | MT. PLEASANT | 0 | 508840 | WILKES 4 138.00 | 508355 | WELSHRE4 138.00 | 0 |  | 1 | 14SP | 239 | 272 | 0 | 97 | 97.0334 | 96.1 | [7 empty] | CATEGORYB | SINGLE | LONE STAR SOUTH - PITTSBURG 138KV CKT 1 | 0 | 508297 | LSSOUTH4 138.00 | 508313 | PITTSB_4 138.00 | 0 |  | 1 | Transfer Loading < 100% | 262
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T8345523WP | FROM->TO | NORTH SLIDELL - SLIDELL 230KV CKT 1 | E | CLEC | EES | CLE_EAST |  | 0 | 500640 | NSLID 6 230.00 | 336137 | 6SLIDEL! 230.00 | 0 |  | 1 | 23WP | 478 | 478 | 0 |  | 93.8253 | 97 | [7 empty] | CATEGORYB | SINGLE | FRONT STREET - MICHOUD 230KV CKT 1 | 0 | 500360 | FRONTST6 230.00 | 336462 | 6MICHO% 230.00 | 0 |  | 1 | Transfer Loading < 100% | 464
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T705513SP | FROM->TO | RODEMACHER 230/22.0KV TRANSFORMER CKT 1 | E | CLEC | CLEC | CLE_CENTRAL | CLE_CENTRAL | 0 | 501811 | G1NESBIT 22.000 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | 13SP | 476 | 476 | 0 | 98.9 | 98.8702 | 98.9 | [7 empty] | CATEGORYB | SINGLE | DOLET HILLS - SOUTHWEST SHREVEPORT 345KV CKT 1 | 0 | 500250 | DOLHILL7 345.00 | 507760 | SW SHV 7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 471
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T645513SP | FROM->TO | RODEMACHER 230/22.0KV TRANSFORMER CKT 1 | E | CLEC | CLEC | CLE_CENTRAL | CLE_CENTRAL | 0 | 501811 | G1NESBIT 22.000 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | 13SP | 476 | 476 | 0 | 98.1 | 98.1225 | 98.1 | [7 empty] | CATEGORYB | SINGLE | COLFAX - RODEMACHER 230KV CKT 1 | 0 | 500200 | COLFAX 6 230.00 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | Transfer Loading < 100% | 467
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T12615513SP | FROM->TO | RODEMACHER 230/22.0KV TRANSFORMER CKT 1 | E | CLEC | CLEC | CLE_CENTRAL | CLE_CENTRAL | 0 | 501811 | G1NESBIT 22.000 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | 13SP | 476 | 476 | 0 | 97.1 | 97.0571 | 97 | [7 empty] | CATEGORYB | SINGLE | COLFAX - MONTGOMERY 230KV CKT 1 | 0 | 500200 | COLFAX 6 230.00 | 337304 | 6MONTGOMERY!230.00 | 0 |  | 1 | Transfer Loading < 100% | 462
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T655013SP | FROM->TO | RODEMACHER 230/22.0KV TRANSFORMER CKT 1 | E | CLEC | CLEC | CLE_CENTRAL | CLE_CENTRAL | 0 | 501811 | G1NESBIT 22.000 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | 13SP | 476 | 476 | 0 | 96.3 | 96.3064 | 96.8 | [7 empty] | CATEGORYB | SINGLE | DOLET HILLS - SOUTHWEST SHREVEPORT 345KV CKT 1 | 0 | 500250 | DOLHILL7 345.00 | 507760 | SW SHV 7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 461
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T22005513SP | FROM->TO | RODEMACHER 230/22.0KV TRANSFORMER CKT 1 | E | CLEC | CLEC | CLE_CENTRAL | CLE_CENTRAL | 0 | 501811 | G1NESBIT 22.000 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | 13SP | 476 | 476 | 0 | 96.1 | 96.0935 | 96.1 | [7 empty] | CATEGORYB | GENOUT | GEN501812 1-RODEMACHER UNIT 2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 458
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T585013SP | FROM->TO | RODEMACHER 230/22.0KV TRANSFORMER CKT 1 | E | CLEC | CLEC | CLE_CENTRAL | CLE_CENTRAL | 0 | 501811 | G1NESBIT 22.000 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | 13SP | 476 | 476 | 0 | 95.6 | 95.5577 | 96 | [7 empty] | CATEGORYB | SINGLE | COLFAX - RODEMACHER 230KV CKT 1 | 0 | 500200 | COLFAX 6 230.00 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | Transfer Loading < 100% | 457
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T725513SP | FROM->TO | RODEMACHER 230/22.0KV TRANSFORMER CKT 1 | E | CLEC | CLEC | CLE_CENTRAL | CLE_CENTRAL | 0 | 501811 | G1NESBIT 22.000 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | 13SP | 476 | 476 | 0 | 95.5 | 95.5486 | 95.5 | [7 empty] | CATEGORYB | SINGLE | EAST LEESVILLE - RODEMACHER 230KV CKT 1 | 0 | 500280 | ELEESV 6 230.00 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | Transfer Loading < 100% | 455
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T4065523WP | TO->FROM | 4BENTWATER 138.00 - GRIMES 138KV CKT 1 | E | EES | EES | ISONE_ME_CMP | ISONE_ME_CMP | 0 | 334026 | 4GRIMES% 138.00 | 334039 | 4BENTWATER 138.00 | 0 |  | 1 | 23WP | 206 | 206 | 0 |  | 94.3138 | 96.6 | [7 empty] | CATEGORYB | SINGLE | GRIMES - MT. ZION 138KV CKT 1 | 0 | 334026 | 4GRIMES% 138.00 | 334060 | 4MT.ZION 138.00 | 0 |  | 1 | Transfer Loading < 100% | 199
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 0 | 2012AG1AFS41T3735018SP | TO->FROM | CHINA - SABINE 230KV CKT 1 | E | EES | EES | ISONE_NH_NGR | ISONE_NH_NGR | 0 | 334434 | 6SABINE% 230.00 | 334204 | 6CHINA% 230.00 | 0 |  | 1 | 18SP | 685 | 685 | 0 |  | 94.9104 | 95 | [7 empty] | CATEGORYB | SINGLE | AMELIA BULK - CHINA 230KV CKT 1 | 0 | 334204 | 6CHINA% 230.00 | 334327 | 6AMELIA! 230.00 | 0 |  | 1 | Transfer Loading < 100% | 651
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T4135523WP | FROM->TO | GRIMES - MT. ZION 138KV CKT 1 | E | EES | EES | ISONE_ME_CMP |  | 0 | 334026 | 4GRIMES% 138.00 | 334060 | 4MT.ZION 138.00 | 0 |  | 1 | 23WP | 206 | 206 | 0 | 96 | 95.9722 | 98.6 | [7 empty] | CATEGORYB | SINGLE | APRIL - WALDEN 138KV CKT 1 | 0 | 334040 | 4WALDEN 138.00 | 334041 | 4APRILTX 138.00 | 0 |  | 1 | Transfer Loading < 100% | 204
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3945523WP | FROM->TO | GRIMES - MT. ZION 138KV CKT 1 | E | EES | EES | ISONE_ME_CMP |  | 0 | 334026 | 4GRIMES% 138.00 | 334060 | 4MT.ZION 138.00 | 0 |  | 1 | 23WP | 206 | 206 | 0 |  | 93.9611 | 96.2 | [7 empty] | CATEGORYB | SINGLE | BRYAN - COLLEGE STATION TAP 138KV CKT 1 | 0 | 334020 | 4BRYAN! 138.00 | 334021 | 4COLSTTA! 138.00 | 0 |  | 1 | Transfer Loading < 100% | 199
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T4045523WP | TO->FROM | LINE 558 TAP - MT. ZION 138KV CKT 1 | E | EES | EES |  |  | 0 | 334060 | 4MT.ZION 138.00 | 334058 | 4L558T485 138.00 | 0 |  | 1 | 23WP | 206 | 206 | 0 |  | 93.6657 | 96.3 | [7 empty] | CATEGORYB | SINGLE | 4BENTWATER 138.00 - GRIMES 138KV CKT 1 | 0 | 334026 | 4GRIMES% 138.00 | 334039 | 4BENTWATER 138.00 | 0 |  | 1 | Transfer Loading < 100% | 199
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T10405518SP | FROM->TO | ARKANSAS NUCLEAR ONE - PLEASANT HILL 500KV CKT 1 | E | EES-EAI | EES-EAI | NYPA E | NYPA E | 0 | 337909 | 8ANO% 500.00 | 337922 | 8P.HILL% 500.00 | 0 |  | 1 | 18SP | 1732 | 1732 | 0 |  | 86.0263 | 95.8 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - MABELVALE 500 500KV CKT 1 | 0 | 337808 | 8MABELVALE% 500.00 | 337909 | 8ANO% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 1660
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T4725518WP | FROM->TO | ARKANSAS NUCLEAR ONE - PLEASANT HILL 500KV CKT 1 | E | EES-EAI | EES-EAI | NYPA E | NYPA E | 0 | 337909 | 8ANO% 500.00 | 337922 | 8P.HILL% 500.00 | 0 |  | 1 | 18WP | 1732 | 1732 | 0 |  | 93.1403 | 97.2 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - MABELVALE 500 500KV CKT 1 | 0 | 337808 | 8MABELVALE% 500.00 | 337909 | 8ANO% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 1684
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T7275523WP | FROM->TO | ARKANSAS NUCLEAR ONE - PLEASANT HILL 500KV CKT 1 | E | EES-EAI | EES-EAI | NYPA E | NYPA E | 0 | 337909 | 8ANO% 500.00 | 337922 | 8P.HILL% 500.00 | 0 |  | 1 | 23WP | 1732 | 1732 | 0 |  | 93.9191 | 97.5 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - MABELVALE 500 500KV CKT 1 | 0 | 337808 | 8MABELVALE% 500.00 | 337909 | 8ANO% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 1689
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T22095518SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | NYPA C | NYPA C | 0 | 337653 | 1WHT BLUF U226.000 | 337651 | 8WHT BLUFF% 500.00 | 0 |  | 1 | 18SP | 910 | 910 | 0 |  | 94.1253 | 95 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 865
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T15665518SP | FROM->TO | SUB 167 - RIVERTON 69/13.2KV TRANSFORMER CKT 1 | E | EMDE | EMDE | BAXTER | BAXTER | 0 | 547645 | R8G167 1 13.200 | 547541 | RIV167 2 69.000 | 0 |  | 1 | 18SP | 52 | 52 | 0 |  | 90.5556 | 95.4 | [7 empty] | CATEGORYB | SINGLE | BLACKBERRY - NEOSHO 345KV CKT 1 | 0 | 532793 | NEOSHO 7 345.00 | 300739 | 7BLACKBERRY 345.00 | 0 |  | 1 | Transfer Loading < 100% | 50
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2495518WP | FROM->TO | SUB 167 - RIVERTON 69/13.2KV TRANSFORMER CKT 1 | E | EMDE | EMDE | BAXTER | BAXTER | 0 | 547645 | R8G167 1 13.200 | 547541 | RIV167 2 69.000 | 0 |  | 1 | 18WP | 52 | 52 | 0 | 95 | 95.0246 | 95.2 | [7 empty] | CATEGORYB | SINGLE | SUB 368 - DADEVILLE EAST - SUB 431 - BOLIVAR SOUTH 161KV CKT 1 | 0 | 547478 | DAD368 5 161.00 | 547493 | BOL431 5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 50
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T24675523SP | FROM->TO | SUB 167 - RIVERTON 69/13.2KV TRANSFORMER CKT 1 | E | EMDE | EMDE | BAXTER | BAXTER | 0 | 547645 | R8G167 1 13.200 | 547541 | RIV167 2 69.000 | 0 |  | 1 | 23SP | 52 | 52 | 0 | 95.1 | 95.1251 | 96.9 | [7 empty] | CATEGORYB | NONSINGLE | GRDA-OPGD-05 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 51
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T17865523SP | FROM->TO | SUB 167 - RIVERTON 69/13.2KV TRANSFORMER CKT 1 | E | EMDE | EMDE | BAXTER | BAXTER | 0 | 547645 | R8G167 1 13.200 | 547541 | RIV167 2 69.000 | 0 |  | 1 | 23SP | 52 | 52 | 0 |  | 92.7169 | 95.2 | [7 empty] | CATEGORYB | SINGLE | BLACKBERRY - NEOSHO 345KV CKT 1 | 0 | 532793 | NEOSHO 7 345.00 | 300739 | 7BLACKBERRY 345.00 | 0 |  | 1 | Transfer Loading < 100% | 50
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T1785023WP | FROM->TO | SUB 167 - RIVERTON 69/13.2KV TRANSFORMER CKT 1 | E | EMDE | EMDE | BAXTER | BAXTER | 0 | 547645 | R8G167 1 13.200 | 547541 | RIV167 2 69.000 | 0 |  | 1 | 23WP | 52 | 52 | 0 | 97.8 | 97.8212 | 97.8 | [7 empty] | CATEGORYB | SINGLE | MT. VERNON CITY 348 - SUB 351 - MOUNT VERNON EAST 69KV CKT 1 | 0 | 547577 | MTV351 2 69.000 | 547620 | MTV348 2 69.000 | 0 |  | 1 | Transfer Loading < 100% | 51
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3135523WP | FROM->TO | SUB 167 - RIVERTON 69/13.2KV TRANSFORMER CKT 1 | E | EMDE | EMDE | BAXTER | BAXTER | 0 | 547645 | R8G167 1 13.200 | 547541 | RIV167 2 69.000 | 0 |  | 1 | 23WP | 52 | 52 | 0 | 98.3 | 98.2599 | 97.7 | [7 empty] | CATEGORYB | SINGLE | MT. VERNON CITY 348 - SUB 351 - MOUNT VERNON EAST 69KV CKT 1 | 0 | 547577 | MTV351 2 69.000 | 547620 | MTV348 2 69.000 | 0 |  | 1 | Transfer Loading < 100% | 51
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3125523WP | FROM->TO | SUB 167 - RIVERTON 69/13.2KV TRANSFORMER CKT 1 | E | EMDE | EMDE | BAXTER | BAXTER | 0 | 547645 | R8G167 1 13.200 | 547541 | RIV167 2 69.000 | 0 |  | 1 | 23WP | 52 | 52 | 0 | 96.1 | 96.1129 | 96.1 | [7 empty] | CATEGORYB | SINGLE | SUB 368 - DADEVILLE EAST - SUB 431 - BOLIVAR SOUTH 161KV CKT 1 | 0 | 547478 | DAD368 5 161.00 | 547493 | BOL431 5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 50
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T1775023WP | FROM->TO | SUB 167 - RIVERTON 69/13.2KV TRANSFORMER CKT 1 | E | EMDE | EMDE | BAXTER | BAXTER | 0 | 547645 | R8G167 1 13.200 | 547541 | RIV167 2 69.000 | 0 |  | 1 | 23WP | 52 | 52 | 0 | 95 | 95.0207 | 95.2 | [7 empty] | CATEGORYB | SINGLE | SUB 368 - DADEVILLE EAST - SUB 431 - BOLIVAR SOUTH 161KV CKT 1 | 0 | 547478 | DAD368 5 161.00 | 547493 | BOL431 5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 50
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T965523WP | FROM->TO | SUB 167 - RIVERTON 69/13.2KV TRANSFORMER CKT 1 | E | EMDE | EMDE | BAXTER | BAXTER | 0 | 547645 | R8G167 1 13.200 | 547541 | RIV167 2 69.000 | 0 |  | 1 | 23WP | 52 | 52 | 0 |  | 92.7936 | 95.1 | [7 empty] | CATEGORYB | SINGLE | KINGRIV7 345.00 - OSBOURNE 345KV CKT 1 | 0 | 506979 | SHIPERD7 345.00 | 506987 | KINGRIV7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 50
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T6695523SP | TO->FROM | SUB 389 - JOPLIN SOUTHWEST - SUB 439 - STATELINE 161KV CKT 1 | E | EMDE | EMDE | JOPLIN | JOPLIN | 0 | 547498 | STL439 5 161.00 | 547483 | JOP389 5 161.00 | 0 |  | 1 | 23SP | 418 | 418 | 0 |  | 94.0247 | 96 | [7 empty] | CATEGORYB | SINGLE | SUB 389 - JOPLIN SOUTHWEST - SUB 439 - STATELINE 161KV CKT 2 | 0 | 547483 | JOP389 5 161.00 | 547498 | STL439 5 161.00 | 0 |  | 2 | Transfer Loading < 100% | 402
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T14225514SP | FROM->TO | BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 | E | GMO | GMO |  |  | 0 | 541211 | BLSPS 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 | 14SP | 224 | 224 | 224 | 95.2 | 95.1937 | 96.4 | [7 empty] | CATEGORYB | SINGLE | CLINTON - MONTROSE 161KV CKT 1 | 0 | 542995 | MONTROS5 161.00 | 300071 | 5CLINTN 161.00 | 0 |  | 1 | Transfer Loading < 100% | 216
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T27085523SP | FROM->TO | BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 | E | GMO | GMO |  |  | 0 | 541211 | BLSPS 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 | 23SP | 224 | 224 | 224 | 96.4 | 96.442 | 98.9 | [7 empty] | CATEGORYB | GENOUT | GEN542951 5-HAWTHORN UNIT #5 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 222
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T6335523SP | FROM->TO | BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 | E | GMO | GMO |  |  | 0 | 541211 | BLSPS 5 161.00 | 541205 | BLSPE 5 161.00 | 0 |  | 1 | 23SP | 224 | 224 | 224 | 96.3 | 96.3489 | 98.8 | [7 empty] | CATEGORYB | SINGLE | MARTIN CITY - SOUTHTOWN 161KV CKT 1 | 0 | 541210 | MARTCTY5 161.00 | 542993 | STHTOWN5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 222
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5805518SP | TO->FROM | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 | E | GMO | GMO |  |  | 0 | 541206 | PRALEE 5 161.00 | 541211 | BLSPS 5 161.00 | 0 |  | 1 | 18SP | 228 | 259 | 259 |  | 92.2679 | 99.4 | [7 empty] | CATEGORYB | SINGLE | PLEASANT HILL - SIBLEY 345KV CKT 1 | 0 | 541200 | PHILL 7 345.00 | 541201 | SIBLEY 7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 258
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T265523SP | TO->FROM | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 | E | GMO | GMO |  |  | 0 | 541206 | PRALEE 5 161.00 | 541211 | BLSPS 5 161.00 | 0 |  | 1 | 23SP | 228 | 259 | 259 |  | 93.7203 | 96.1 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 249
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5705514SP | FROM->TO | LONGVIEW - WESTERN ELECTRIC 161KV CKT 1 | E | GMO | GMO |  |  | 0 | 541224 | LNGVW 5 161.00 | 541222 | WSTELEC5 161.00 | 0 |  | 1 | 14SP | 228 | 259 | 259 | 97.6 | 97.5597 | 98.2 | [7 empty] | CATEGORYB | SINGLE | GREENWOOD ENERGY CENTER - LEES SUMMIT EAST 161KV CKT 1 | 0 | 541218 | GRNWD 5 161.00 | 541233 | LEESUM 5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 255
2012-AG1 | AFS4 | INVALID |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1885514SP | FROM->TO | 412SUB - KANSAS TAP 161KV CKT 1 | E | GRDA | GRDA | GRDA-NEO | GRDA | 0 | 512637 | 412SUB 5 161.00 | 512714 | KANSATP5 161.00 | 0 |  | 1 | 14SP | 335 | 335 | 0 |  | 94.4912 | 95.1656 | [7 empty] | CATEGORYB | SINGLE | GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 | 0 | 512650 | GRDA1 7 345.00 | 512750 | TONECE7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 319
2012-AG1 | AFS4 | INVALID | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1875514SP | TO->FROM | 412SUB - KERR 161KV CKT 1 | E | GRDA | GRDA | GRDA | GRDA-NEO | 0 | 512635 | KERR GR5 161.00 | 512637 | 412SUB 5 161.00 | 0 |  | 1 | 14SP | 335 | 335 | 0 | 95.4 | 95.3516 | 96.0259 | [7 empty] | CATEGORYB | SINGLE | GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 | 0 | 512650 | GRDA1 7 345.00 | 512750 | TONECE7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 322
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T19025514SP | TO->FROM | 412SUB - KERR 161KV CKT 1 | E | GRDA | GRDA | GRDA | GRDA-NEO | 0 | 512635 | KERR GR5 161.00 | 512637 | 412SUB 5 161.00 | 0 |  | 1 | 14SP | 335 | 335 | 0 |  | 94.3945 | 95.1 | [7 empty] | CATEGORYB | NONSINGLE | GRDA-OPGD-05 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 319
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1465523SP | TO->FROM | 412SUB - KERR 161KV CKT 1 | E | GRDA | GRDA | GRDA | GRDA-NEO | 0 | 512635 | KERR GR5 161.00 | 512637 | 412SUB 5 161.00 | 0 |  | 1 | 23SP | 335 | 335 | 0 |  | 90.8907 | 95.4 | [7 empty] | CATEGORYB | SINGLE | CHAMBER SPRINGS - CLARKSVILLE 345KV CKT 1 | 0 | 506945 | CHAMSPR7 345.00 | 509745 | CLARKSV7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 320
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1445523SP | TO->FROM | FLINT CREEK - SILOAM SPRINGS TAP 345KV CKT 1 | E | GRDA | AEPW | GRDA-MUN | FAYETTEVILLE | 0 | 512750 | TONECE7 345.00 | 506935 | FLINTCR7 345.00 | 0 |  | 1 | 23SP | 1195 | 1195 | 0 |  | 91.9965 | 96.7 | [7 empty] | CATEGORYB | SINGLE | CHAMBER SPRINGS - CLARKSVILLE 345KV CKT 1 | 0 | 506945 | CHAMSPR7 345.00 | 509745 | CLARKSV7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 1156
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T6545518SP | FROM->TO | GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 | E | GRDA | GRDA | GRDA | GRDA-MUN | 0 | 512650 | GRDA1 7 345.00 | 512750 | TONECE7 345.00 | 0 |  | 1 | 18SP | 1064 | 1064 | 0 |  | 90.1411 | 97.1 | [7 empty] | CATEGORYB | SINGLE | 7JASPER 345.00 - BLACKBERRY 345KV CKT 1 | 0 | 300739 | 7BLACKBERRY 345.00 | 300949 | 7JASPER 345.00 | 0 |  | 1 | Transfer Loading < 100% | 1034
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T23135518SP | FROM->TO | GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 | E | GRDA | GRDA | GRDA | GRDA-MUN | 0 | 512650 | GRDA1 7 345.00 | 512750 | TONECE7 345.00 | 0 |  | 1 | 18SP | 1064 | 1064 | 0 |  | 91.1012 | 96.3 | [7 empty] | CATEGORYB | GENOUT | GEN509394 1-FLINT CREEK | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 1025
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2535523SP | FROM->TO | GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 | E | GRDA | GRDA | GRDA | GRDA-MUN | 0 | 512650 | GRDA1 7 345.00 | 512750 | TONECE7 345.00 | 0 |  | 1 | 23SP | 1064 | 1064 | 0 |  | 94.2358 | 97.8 | [7 empty] | CATEGORYB | SINGLE | 412SUB - KERR 161KV CKT 1 | 0 | 512635 | KERR GR5 161.00 | 512637 | 412SUB 5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 1041
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2615523SP | FROM->TO | GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 | E | GRDA | GRDA | GRDA | GRDA-MUN | 0 | 512650 | GRDA1 7 345.00 | 512750 | TONECE7 345.00 | 0 |  | 1 | 23SP | 1064 | 1064 | 0 |  | 94.0616 | 97.7 | [7 empty] | CATEGORYB | SINGLE | 412SUB - KANSAS TAP 161KV CKT 1 | 0 | 512637 | 412SUB 5 161.00 | 512714 | KANSATP5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 1040
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2685523SP | FROM->TO | GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 | E | GRDA | GRDA | GRDA | GRDA-MUN | 0 | 512650 | GRDA1 7 345.00 | 512750 | TONECE7 345.00 | 0 |  | 1 | 23SP | 1064 | 1064 | 0 |  | 92.3832 | 95.9 | [7 empty] | CATEGORYB | SINGLE | KANSAS TAP - WEST SILOAM SPRINGS 161KV CKT 1 | 0 | 512642 | SILSPWW5 161.00 | 512714 | KANSATP5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 1021
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3505523WP | FROM->TO | GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 | E | GRDA | GRDA | GRDA | GRDA-MUN | 0 | 512650 | GRDA1 7 345.00 | 512750 | TONECE7 345.00 | 0 |  | 1 | 23WP | 1064 | 1064 | 0 |  | 94.3125 | 96.8 | [7 empty] | CATEGORYB | SINGLE | 7JASPER 345.00 - BLACKBERRY 345KV CKT 1 | 0 | 300739 | 7BLACKBERRY 345.00 | 300949 | 7JASPER 345.00 | 0 |  | 1 | Transfer Loading < 100% | 1030
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T15775523WP | FROM->TO | GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 | E | GRDA | GRDA | GRDA | GRDA-MUN | 0 | 512650 | GRDA1 7 345.00 | 512750 | TONECE7 345.00 | 0 |  | 1 | 23WP | 1064 | 1064 | 0 |  | 94.5677 | 96.1 | [7 empty] | CATEGORYB | GENOUT | GEN509394 1-FLINT CREEK | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 1023
2012-AG1 | AFS4 | INVALID |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2045518SP | TO->FROM | SILOAM CITY - WEST SILOAM SPRINGS 161KV CKT 1 | E | GRDA | GRDA | GRDA-NEO | GRDA-MUN | 0 | 512642 | SILSPWW5 161.00 | 512643 | SILMCTY5 161.00 | 0 |  | 1 | 18SP | 307 | 335 | 0 |  | 91.2514 | 97.6459 | [7 empty] | CATEGORYB | SINGLE | GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 | 0 | 512650 | GRDA1 7 345.00 | 512750 | TONECE7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 328
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T21795518SP | TO->FROM | SILOAM CITY - WEST SILOAM SPRINGS 161KV CKT 1 | E | GRDA | GRDA | GRDA-NEO | GRDA-MUN | 0 | 512642 | SILSPWW5 161.00 | 512643 | SILMCTY5 161.00 | 0 |  | 1 | 18SP | 307 | 335 | 0 |  | 89.711 | 95.9 | [7 empty] | CATEGORYB | NONSINGLE | GRDA-OPGD-05 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 322
2012-AG1 | AFS4 | INVALID | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1555523WP | TO->FROM | SILOAM CITY - WEST SILOAM SPRINGS 161KV CKT 1 | E | GRDA | GRDA | GRDA-NEO | GRDA-MUN | 0 | 512642 | SILSPWW5 161.00 | 512643 | SILMCTY5 161.00 | 0 |  | 1 | 23WP | 307 | 335 | 0 | 95.5 | 95.4969 | 96.5486 | [7 empty] | CATEGORYB | SINGLE | GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 | 0 | 512650 | GRDA1 7 345.00 | 512750 | TONECE7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 324
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T19265523SP | TO->FROM | BIRMINGHAM - HAWTHORN 161KV CKT 1 | E | KCPL | KCPL | METRO | NORTH | 0 | 542973 | HAWTHRN5 161.00 | 543020 | BRMGHAM5 161.00 | 0 |  | 1 | 23SP | 187 | 211 | 0 |  | 91.031 | 95.3 | [7 empty] | CATEGORYB | SINGLE | ECKLES - MISSOURI CITY 161KV CKT 1 | 0 | 548808 | ECKLES-161 161.00 | 300098 | 5MOCITY 161.00 | 0 |  | 1 | Transfer Loading < 100% | 202
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T22495518SP | TO->FROM | CLINTON - MONTROSE 161KV CKT 1 | E | KCPL | AECI | METRO | KAMO | 0 | 542995 | MONTROS5 161.00 | 300071 | 5CLINTN 161.00 | 0 |  | 1 | 18SP | 495 | 495 | 0 |  | 88.8432 | 95 | [7 empty] | CATEGORYB | NONSINGLE | OVERTON-TRF | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 471
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T7165513SP | FROM->TO | CRAIG - LENEXA NORTH 161KV CKT 1 | E | KCPL | KCPL | JOCO | JOCO | 0 | 542978 | CRAIG 5 161.00 | 543039 | LENEXAN5 161.00 | 0 |  | 1 | 13SP | 293 | 334 | 0 | 95.9 | 95.8991 | 96.6 | [7 empty] | CATEGORYB | SINGLE | CRAIG - PFLUMM 161KV CKT 1 | 0 | 542978 | CRAIG 5 161.00 | 542979 | PFLUMM 5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 323
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T7175513SP | FROM->TO | CRAIG - LENEXA NORTH 161KV CKT 1 | E | KCPL | KCPL | JOCO | JOCO | 0 | 542978 | CRAIG 5 161.00 | 543039 | LENEXAN5 161.00 | 0 |  | 1 | 13SP | 293 | 334 | 0 |  | 94.8184 | 95.6 | [7 empty] | CATEGORYB | SINGLE | CEDAR CREEK - GREENWOOD 161KV CKT 1 | 0 | 543031 | SHWNMSN5 161.00 | 543049 | CEDRCRK5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 320
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T4135023SP | TO->FROM | CROSSTOWN - GRAND AVENUE WEST 161KV CKT 1 | E | KCPL | KCPL | DWNTWN | DWNTWN | 0 | 542988 | GRAND W5 161.00 | 542990 | CROSTWN5 161.00 | 0 |  | 1 | 23SP | 259 | 259 | 0 | 100.2 | 100.1957 | 98.5 | [7 empty] | CATEGORYB | SINGLE | CROSSTOWN - NORTHEAST 161KV CKT 1 | 0 | 542985 | NEAST 5 161.00 | 542990 | CROSTWN5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 256
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T4125023SP | TO->FROM | CROSSTOWN - NORTHEAST 161KV CKT 1 | E | KCPL | KCPL | DWNTWN | DWNTWN | 0 | 542985 | NEAST 5 161.00 | 542990 | CROSTWN5 161.00 | 0 |  | 1 | 23SP | 259 | 259 | 0 | 102.7 | 102.6972 | 99.8 | [7 empty] | CATEGORYB | SINGLE | NAVY - NORTHEAST 161KV CKT 1 | 0 | 542985 | NEAST 5 161.00 | 542989 | NAVY 5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 259
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5975514SP | TO->FROM | FOREST - SOUTHTOWN 161KV CKT 1 | E | KCPL | KCPL | METRO | METRO | 0 | 542993 | STHTOWN5 161.00 | 543001 | FOREST 5 161.00 | 0 |  | 1 | 14SP | 223 | 223 | 0 | 95.4 | 95.4004 | 96.4 | [7 empty] | CATEGORYB | SINGLE | MERRIAM - ROELAND PARK 161KV CKT 1 | 0 | 543032 | MERRIAM5 161.00 | 543040 | ROEPARK5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 215
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T20225514SP | TO->FROM | FOREST - SOUTHTOWN 161KV CKT 1 | E | KCPL | KCPL | METRO | METRO | 0 | 542993 | STHTOWN5 161.00 | 543001 | FOREST 5 161.00 | 0 |  | 1 | 14SP | 223 | 223 | 0 | 95.4 | 95.3951 | 95.8 | [7 empty] | CATEGORYB | GENOUT | GEN542951 5-HAWTHORN UNIT #5 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 214
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5965514SP | TO->FROM | GREENWOOD - LENEXA NORTH 161KV CKT 1 | E | KCPL | KCPL | JOCO | JOCO | 0 | 543039 | LENEXAN5 161.00 | 543031 | SHWNMSN5 161.00 | 0 |  | 1 | 14SP | 293 | 334 | 0 | 98.7 | 98.665 | 99.7 | [7 empty] | CATEGORYB | SINGLE | CEDAR CREEK - GREENWOOD 161KV CKT 1 | 0 | 543031 | SHWNMSN5 161.00 | 543049 | CEDRCRK5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 333
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T3215013SP | FROM->TO | IATAN - STRANGER CREEK 345KV CKT 1 | E | KCPL | WERE | KACP | NEAST | 0 | 542982 | IATAN 7 345.00 | 532772 | STRANGR7 345.00 | 0 |  | 1 | 13SP | 1099 | 1195 | 0 | 97.1 | 97.1394 | 97 | [7 empty] | CATEGORYB | SINGLE | EASTOWN7 345.00 - IATAN 345KV CKT 1 | 0 | 541400 | EASTOWN7 345.00 | 542982 | IATAN 7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 1160
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T4325513WP | FROM->TO | IATAN - STRANGER CREEK 345KV CKT 1 | E | KCPL | WERE | KACP | NEAST | 0 | 542982 | IATAN 7 345.00 | 532772 | STRANGR7 345.00 | 0 |  | 1 | 13WP | 1195 | 1195 | 0 | 95.9 | 95.8645 | 95.8 | [7 empty] | CATEGORYB | SINGLE | EASTOWN7 345.00 - IATAN 345KV CKT 1 | 0 | 541400 | EASTOWN7 345.00 | 542982 | IATAN 7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 1145
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T2935014SP | FROM->TO | IATAN - STRANGER CREEK 345KV CKT 1 | E | KCPL | WERE | KACP | NEAST | 0 | 542982 | IATAN 7 345.00 | 532772 | STRANGR7 345.00 | 0 |  | 1 | 14SP | 1099 | 1195 | 0 | 97.2 | 97.1873 | 97.1 | [7 empty] | CATEGORYB | SINGLE | EASTOWN7 345.00 - IATAN 345KV CKT 1 | 0 | 541400 | EASTOWN7 345.00 | 542982 | IATAN 7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 1161
2012-AG1 | AFS4 | CONT-LaCygne West Gardner 345kv | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T7125513SP | TO->FROM | STILWELL - WEST GARDNER 345KV CKT 1 | E | KCPL | KCPL | KACP | KACP | 0 | 542965 | W.GRDNR7 345.00 | 542968 | STILWEL7 345.00 | 0 |  | 1 | 13SP | 994 | 994 | 994 | 95.6 | 95.6288 | 96.7 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 962
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T4815013SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 13SP | 615 | 615 | 0 | 95.6 | 95.6183 | 95.8 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNIGHT% 500.00 | 335837 | 8COLY% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 590
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T8805513SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 13SP | 615 | 615 | 0 | 95.8 | 95.791 | 95.8 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNIGHT% 500.00 | 335837 | 8COLY% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 590
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T6515013SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 13SP | 615 | 615 | 0 | 95.6 | 95.6406 | 95.8 | [7 empty] | CATEGORYB | SINGLE | ELDORADO EHV - STERLINGTON 500KV CKT 1 | 0 | 337420 | 8STERLING% 500.00 | 337561 | 8EL DORADO% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 590
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T615013SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 13SP | 615 | 615 | 0 | 95.4 | 95.3742 | 95.5 | [7 empty] | CATEGORYB | SINGLE | COUGHLIN - PLAISANCE 138KV CKT 1 | 0 | 500230 | COUGH 4 138.00 | 500720 | PLAISAN4 138.00 | 0 |  | 1 | Transfer Loading < 100% | 588
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T665513SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 13SP | 615 | 615 | 0 | 95.5 | 95.5323 | 95.5 | [7 empty] | CATEGORYB | SINGLE | COUGHLIN - PLAISANCE 138KV CKT 1 | 0 | 500230 | COUGH 4 138.00 | 500720 | PLAISAN4 138.00 | 0 |  | 1 | Transfer Loading < 100% | 588
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T3495013SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 13SP | 615 | 615 | 0 | 95.2 | 95.2151 | 95.3 | [7 empty] | CATEGORYB | SINGLE | 8CAJUN2 - WEBRE 500KV CKT 1 | 0 | 303005 | 8BIG_CAJUN2%500.00 | 335500 | 8WEBRE% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 587
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T4725013SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 13SP | 615 | 615 | 0 | 95.2 | 95.1512 | 95.3 | [7 empty] | CATEGORYB | SINGLE | ENJAY - FANCY POINT 230KV CKT 1 | 0 | 335772 | 6ENJAY! 230.00 | 335825 | 6FANCY_PT% 230.00 | 0 |  | 1 | Transfer Loading < 100% | 587
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T4805013SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 13SP | 615 | 615 | 0 | 95.2 | 95.1893 | 95.3 | [7 empty] | CATEGORYB | SINGLE | FANCY POINT - MCKNIGHT 500KV CKT 1 | 0 | 335835 | 8FANCY_PT% 500.00 | 335836 | 8MCKNIGHT% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 587
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T7595513SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 13SP | 615 | 615 | 0 | 95.2 | 95.2394 | 95.2 | [7 empty] | CATEGORYB | SINGLE | 8CAJUN2 - WEBRE 500KV CKT 1 | 0 | 303005 | 8BIG_CAJUN2%500.00 | 335500 | 8WEBRE% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 586
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T8715513SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 13SP | 615 | 615 | 0 | 95.2 | 95.2355 | 95.2 | [7 empty] | CATEGORYB | SINGLE | ENJAY - FANCY POINT 230KV CKT 1 | 0 | 335772 | 6ENJAY! 230.00 | 335825 | 6FANCY_PT% 230.00 | 0 |  | 1 | Transfer Loading < 100% | 586
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T8795513SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 13SP | 615 | 615 | 0 | 95.2 | 95.2425 | 95.2 | [7 empty] | CATEGORYB | SINGLE | FANCY POINT - MCKNIGHT 500KV CKT 1 | 0 | 335835 | 8FANCY_PT% 500.00 | 335836 | 8MCKNIGHT% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 586
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T3525013SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 13SP | 615 | 615 | 0 | 95 | 95.0089 | 95.1 | [7 empty] | CATEGORYB | SINGLE | 8CAJUN2 - FANCY POINT 500KV CKT 1 | 0 | 303005 | 8BIG_CAJUN2%500.00 | 335835 | 8FANCY_PT% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 585
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T7615513SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 13SP | 615 | 615 | 0 | 95.1 | 95.1005 | 95.1 | [7 empty] | CATEGORYB | SINGLE | 8CAJUN2 - FANCY POINT 500KV CKT 1 | 0 | 303005 | 8BIG_CAJUN2%500.00 | 335835 | 8FANCY_PT% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 585
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2012AG1AFS41T5685013SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 13SP | 615 | 615 | 0 |  | 94.9873 | 95.1 | [7 empty] | CATEGORYB | SINGLE | BAXTER WILSON SES - GRAND GULF 500KV CKT 1 | 0 | 336820 | 8GGNS% 500.00 | 336830 | 8BXTRWILSON%500.00 | 0 |  | 1 | Transfer Loading < 100% | 585
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2012AG1AFS41T4405013SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 13SP | 615 | 615 | 0 |  | 94.9763 | 95.1 | [7 empty] | CATEGORYB | SINGLE | DYNEGY - PECAN GROVE 230KV CKT 1 | 0 | 335074 | 6CALCASIEU% 230.00 | 335077 | 6PECAN_GRV! 230.00 | 0 |  | 1 | Transfer Loading < 100% | 585
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T4685013SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 13SP | 615 | 615 | 0 | 95 | 95.0041 | 95.1 | [7 empty] | CATEGORYB | SINGLE | ENJAY - JAGUAR 230KV CKT 1 | 0 | 335770 | 6JAGUAR% 230.00 | 335772 | 6ENJAY! 230.00 | 0 |  | 1 | Transfer Loading < 100% | 585
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T8675513SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 13SP | 615 | 615 | 0 | 95.1 | 95.0845 | 95.1 | [7 empty] | CATEGORYB | SINGLE | ENJAY - JAGUAR 230KV CKT 1 | 0 | 335770 | 6JAGUAR% 230.00 | 335772 | 6ENJAY! 230.00 | 0 |  | 1 | Transfer Loading < 100% | 585
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2012AG1AFS41T15765013SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 13SP | 615 | 615 | 0 |  | 94.9598 | 95.1 | [7 empty] | CATEGORYB | GENOUT | GEN303008 1-1BC2 U3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 585
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T4615013SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 13SP | 615 | 615 | 0 | 95 | 95.0331 | 95.1 | [7 empty] | CATEGORYB | SINGLE | WATERFORD - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WILLOW_GL% 500.00 | 336150 | 8WATERFO 500.00 | 0 |  | 1 | Transfer Loading < 100% | 585
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T8615513SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 13SP | 615 | 615 | 0 | 95.1 | 95.1028 | 95.1 | [7 empty] | CATEGORYB | SINGLE | WATERFORD - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WILLOW_GL% 500.00 | 336150 | 8WATERFO 500.00 | 0 |  | 1 | Transfer Loading < 100% | 585
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2012AG1AFS41T4445013SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 13SP | 615 | 615 | 0 |  | 94.935 | 95.1 | [7 empty] | CATEGORYB | SINGLE | WEBRE - WELLS 500KV CKT 1 | 0 | 335368 | 8WELLS% 500.00 | 335500 | 8WEBRE% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 585
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2012AG1AFS41T5725013SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 13SP | 615 | 615 | 0 |  | 94.9203 | 95 | [7 empty] | CATEGORYB | SINGLE | BAXTER WILSON SES - RAY BRASWELL SES 500KV CKT 1 | 0 | 336830 | 8BXTRWILSON%500.00 | 336839 | 8R.BRASWELL%500.00 | 0 |  | 1 | Transfer Loading < 100% | 585
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T9705513SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 13SP | 615 | 615 | 0 | 95 | 95.0209 | 95 | [7 empty] | CATEGORYB | SINGLE | BAXTER WILSON SES - RAY BRASWELL SES 500KV CKT 1 | 0 | 336830 | 8BXTRWILSON%500.00 | 336839 | 8R.BRASWELL%500.00 | 0 |  | 1 | Transfer Loading < 100% | 585
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T8415513SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 13SP | 615 | 615 | 0 | 95 | 95.0248 | 95 | [7 empty] | CATEGORYB | SINGLE | DYNEGY - PECAN GROVE 230KV CKT 1 | 0 | 335074 | 6CALCASIEU% 230.00 | 335077 | 6PECAN_GRV! 230.00 | 0 |  | 1 | Transfer Loading < 100% | 585
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T10425513SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 13SP | 615 | 615 | 0 | 95 | 95.0109 | 95 | [7 empty] | CATEGORYB | SINGLE | ELDORADO EHV - STERLINGTON 500KV CKT 1 | 0 | 337420 | 8STERLING% 500.00 | 337561 | 8EL DORADO% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 585
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2012AG1AFS41T15725013SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 13SP | 615 | 615 | 0 |  | 94.9136 | 95 | [7 empty] | CATEGORYB | GENOUT | GEN303006 1-1BC2 U1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 585
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T21815513SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 13SP | 615 | 615 | 0 | 95 | 95.0329 | 95 | [7 empty] | CATEGORYB | GENOUT | GEN303008 1-1BC2 U3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 585
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2012AG1AFS41T15865013SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 13SP | 615 | 615 | 0 |  | 94.917 | 95 | [7 empty] | CATEGORYB | GENOUT | GEN336153 1-WATERFORD UNIT#3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 585
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5785513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 95.7 | 95.7433 | 95.7 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNIGHT% 500.00 | 335837 | 8COLY% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 589
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T1975013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 95.5 | 95.5348 | 95.5 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNIGHT% 500.00 | 335837 | 8COLY% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 588
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5775513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 95.3 | 95.2543 | 95.3 | [7 empty] | CATEGORYB | SINGLE | FANCY POINT - MCKNIGHT 500KV CKT 1 | 0 | 335835 | 8FANCY_PT% 500.00 | 335836 | 8MCKNIGHT% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 587
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T1965013WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 95.2 | 95.1806 | 95.2 | [7 empty] | CATEGORYB | SINGLE | FANCY POINT - MCKNIGHT 500KV CKT 1 | 0 | 335835 | 8FANCY_PT% 500.00 | 335836 | 8MCKNIGHT% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 586
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T4955513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 95.1 | 95.0577 | 95.1 | [7 empty] | CATEGORYB | SINGLE | 4VATCAN - SCOTT 138KV CKT 1 | 0 | 303133 | 4VATICAN 138.00 | 335379 | 4SCOTT_1! 138.00 | 0 |  | 1 | Transfer Loading < 100% | 585
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS-CHECK-TC-Blown Up |  | 5 | 5 | 2012AG1AFS41T12805513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 95.1 | 95.0752 | 95.1 | [7 empty] | CATEGORYB | GENOUT | GEN336153 1-WATERFORD UNIT#3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 585
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T4845513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 95 | 95.0193 | 95 | [7 empty] | CATEGORYB | SINGLE | 8CAJUN2 - FANCY POINT 500KV CKT 1 | 0 | 303005 | 8BIG_CAJUN2%500.00 | 335835 | 8FANCY_PT% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 585
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T385513WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 13WP | 615 | 615 | 0 | 95 | 95.0433 | 95 | [7 empty] | CATEGORYB | SINGLE | COUGHLIN - PLAISANCE 138KV CKT 1 | 0 | 500230 | COUGH 4 138.00 | 500720 | PLAISAN4 138.00 | 0 |  | 1 | Transfer Loading < 100% | 585
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T7625514SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 14SP | 615 | 615 | 0 | 95.2 | 95.2388 | 95.3 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNIGHT% 500.00 | 335837 | 8COLY% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 587
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T725514SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 14SP | 615 | 615 | 0 | 95 | 95.0092 | 95 | [7 empty] | CATEGORYB | SINGLE | COUGHLIN - PLAISANCE 138KV CKT 1 | 0 | 500230 | COUGH 4 138.00 | 500720 | PLAISAN4 138.00 | 0 |  | 1 | Transfer Loading < 100% | 585
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T4635514WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 14WP | 615 | 615 | 0 | 95.3 | 95.3428 | 95.3 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNIGHT% 500.00 | 335837 | 8COLY% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 587
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T2035014WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 14WP | 615 | 615 | 0 | 95.1 | 95.0933 | 95 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNIGHT% 500.00 | 335837 | 8COLY% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 585
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T8275518SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 18SP | 615 | 615 | 0 | 95.4 | 95.3514 | 95.4 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNIGHT% 500.00 | 335837 | 8COLY% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 587
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T845518SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 18SP | 615 | 615 | 0 | 95.4 | 95.3565 | 95.4 | [7 empty] | CATEGORYB | SINGLE | COUGHLIN - PLAISANCE 138KV CKT 1 | 0 | 500230 | COUGH 4 138.00 | 500720 | PLAISAN4 138.00 | 0 |  | 1 | Transfer Loading < 100% | 587
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T675018SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 18SP | 615 | 615 | 0 | 95.1 | 95.1136 | 95.1 | [7 empty] | CATEGORYB | SINGLE | COUGHLIN - PLAISANCE 138KV CKT 1 | 0 | 500230 | COUGH 4 138.00 | 500720 | PLAISAN4 138.00 | 0 |  | 1 | Transfer Loading < 100% | 585
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T8265518SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 18SP | 615 | 615 | 0 | 95.1 | 95.053 | 95.1 | [7 empty] | CATEGORYB | SINGLE | FANCY POINT - MCKNIGHT 500KV CKT 1 | 0 | 335835 | 8FANCY_PT% 500.00 | 335836 | 8MCKNIGHT% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 585
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2012AG1AFS41T4545018SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 18SP | 615 | 615 | 0 |  | 94.988 | 95 | [7 empty] | CATEGORYB | SINGLE | FANCY POINT - MCKNIGHT 500KV CKT 1 | 0 | 335835 | 8FANCY_PT% 500.00 | 335836 | 8MCKNIGHT% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 585
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2795518WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 18WP | 615 | 615 | 0 | 95.8 | 95.7972 | 95.9 | [7 empty] | CATEGORYB | SINGLE | 4VATCAN - SCOTT 138KV CKT 1 | 0 | 303133 | 4VATICAN 138.00 | 335379 | 4SCOTT_1! 138.00 | 0 |  | 1 | Transfer Loading < 100% | 590
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3765518WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 18WP | 615 | 615 | 0 | 95.7 | 95.6769 | 95.8 | [7 empty] | CATEGORYB | SINGLE | FANCY POINT - MCKNIGHT 500KV CKT 1 | 0 | 335835 | 8FANCY_PT% 500.00 | 335836 | 8MCKNIGHT% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 590
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T2235018WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 18WP | 615 | 615 | 0 | 95.4 | 95.4201 | 95.5 | [7 empty] | CATEGORYB | SINGLE | FANCY POINT - MCKNIGHT 500KV CKT 1 | 0 | 335835 | 8FANCY_PT% 500.00 | 335836 | 8MCKNIGHT% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 588
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T1475018WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 18WP | 615 | 615 | 0 | 95.4 | 95.3933 | 95.4 | [7 empty] | CATEGORYB | SINGLE | 4VATCAN - SCOTT 138KV CKT 1 | 0 | 303133 | 4VATICAN 138.00 | 335379 | 4SCOTT_1! 138.00 | 0 |  | 1 | Transfer Loading < 100% | 587
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3805518WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 18WP | 615 | 615 | 0 | 95.4 | 95.3787 | 95.4 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNIGHT% 500.00 | 335837 | 8COLY% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 587
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T425518WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 18WP | 615 | 615 | 0 | 95.3 | 95.3335 | 95.4 | [7 empty] | CATEGORYB | SINGLE | COUGHLIN - PLAISANCE 138KV CKT 1 | 0 | 500230 | COUGH 4 138.00 | 500720 | PLAISAN4 138.00 | 0 |  | 1 | Transfer Loading < 100% | 587
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2665518WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 18WP | 615 | 615 | 0 | 95.2 | 95.2027 | 95.3 | [7 empty] | CATEGORYB | SINGLE | 8CAJUN2 - FANCY POINT 500KV CKT 1 | 0 | 303005 | 8BIG_CAJUN2%500.00 | 335835 | 8FANCY_PT% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 587
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3665518WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 18WP | 615 | 615 | 0 | 95.2 | 95.1929 | 95.3 | [7 empty] | CATEGORYB | SINGLE | ENJAY - FANCY POINT 230KV CKT 1 | 0 | 335772 | 6ENJAY! 230.00 | 335825 | 6FANCY_PT% 230.00 | 0 |  | 1 | Transfer Loading < 100% | 587
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T8615518WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 18WP | 615 | 615 | 0 | 95.1 | 95.0695 | 95.2 | [7 empty] | CATEGORYB | SINGLE | 8DANIEL 500.00 - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNIGHT% 500.00 | 388700 | 8DANIEL 500.00 | 0 |  | 1 | Transfer Loading < 100% | 586
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T10435518WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 18WP | 615 | 615 | 0 | 95.1 | 95.08 | 95.2 | [7 empty] | CATEGORYB | GENOUT | GEN336153 1-WATERFORD UNIT#3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 586
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3555518WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 18WP | 615 | 615 | 0 | 95.1 | 95.0544 | 95.1 | [7 empty] | CATEGORYB | SINGLE | WATERFORD - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WILLOW_GL% 500.00 | 336150 | 8WATERFO 500.00 | 0 |  | 1 | Transfer Loading < 100% | 585
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T8995023SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23SP | 615 | 615 | 0 | 96 | 95.9622 | 95.8 | [7 empty] | CATEGORYB | SINGLE | ELDORADO EHV - STERLINGTON 500KV CKT 1 | 0 | 337420 | 8STERLING% 500.00 | 337561 | 8EL DORADO% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 590
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T9785523SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23SP | 615 | 615 | 0 | 95.7 | 95.7401 | 95.7 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNIGHT% 500.00 | 335837 | 8COLY% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 589
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1045523SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23SP | 615 | 615 | 0 | 95.7 | 95.6692 | 95.6 | [7 empty] | CATEGORYB | SINGLE | COUGHLIN - PLAISANCE 138KV CKT 1 | 0 | 500230 | COUGH 4 138.00 | 500720 | PLAISAN4 138.00 | 0 |  | 1 | Transfer Loading < 100% | 588
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T1015023SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23SP | 615 | 615 | 0 | 95.4 | 95.4125 | 95.4 | [7 empty] | CATEGORYB | SINGLE | COUGHLIN - PLAISANCE 138KV CKT 1 | 0 | 500230 | COUGH 4 138.00 | 500720 | PLAISAN4 138.00 | 0 |  | 1 | Transfer Loading < 100% | 587
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T7405023SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23SP | 615 | 615 | 0 | 95.4 | 95.4228 | 95.4 | [7 empty] | CATEGORYB | SINGLE | FANCY POINT - MCKNIGHT 500KV CKT 1 | 0 | 335835 | 8FANCY_PT% 500.00 | 335836 | 8MCKNIGHT% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 587
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T9765523SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23SP | 615 | 615 | 0 | 95.5 | 95.4573 | 95.4 | [7 empty] | CATEGORYB | SINGLE | FANCY POINT - MCKNIGHT 500KV CKT 1 | 0 | 335835 | 8FANCY_PT% 500.00 | 335836 | 8MCKNIGHT% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 587
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T9645523SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23SP | 615 | 615 | 0 | 95.3 | 95.3224 | 95.3 | [7 empty] | CATEGORYB | SINGLE | ENJAY - FANCY POINT 230KV CKT 1 | 0 | 335772 | 6ENJAY! 230.00 | 335825 | 6FANCY_PT% 230.00 | 0 |  | 1 | Transfer Loading < 100% | 587
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T7675523SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23SP | 615 | 615 | 0 | 95.2 | 95.2427 | 95.2 | [7 empty] | CATEGORYB | SINGLE | 8CAJUN2 - WEBRE 500KV CKT 1 | 0 | 303005 | 8BIG_CAJUN2%500.00 | 335500 | 8WEBRE% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 586
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T9295523SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23SP | 615 | 615 | 0 | 95.3 | 95.2763 | 95.2 | [7 empty] | CATEGORYB | SINGLE | DYNEGY - PECAN GROVE 230KV CKT 1 | 0 | 335074 | 6CALCASIEU% 230.00 | 335077 | 6PECAN_GRV! 230.00 | 0 |  | 1 | Transfer Loading < 100% | 586
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T25955523SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23SP | 615 | 615 | 0 | 95.3 | 95.2975 | 95.2 | [7 empty] | CATEGORYB | GENOUT | GEN335614 1-WILLOW GLENN UNIT#4 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 586
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T7875523SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23SP | 615 | 615 | 0 | 95.2 | 95.1878 | 95.1 | [7 empty] | CATEGORYB | SINGLE | 3MNDENLG - MINDEN 115KV CKT 1 | 0 | 303302 | 3MINDEN_LG 115.00 | 337361 | 3MINDEN_LA! 115.00 | 0 |  | 1 | Transfer Loading < 100% | 585
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T7415023SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23SP | 615 | 615 | 0 | 95.2 | 95.1608 | 95.1 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNIGHT% 500.00 | 335837 | 8COLY% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 585
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T9585523SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23SP | 615 | 615 | 0 | 95.2 | 95.1554 | 95.1 | [7 empty] | CATEGORYB | SINGLE | ENJAY - JAGUAR 230KV CKT 1 | 0 | 335770 | 6JAGUAR% 230.00 | 335772 | 6ENJAY! 230.00 | 0 |  | 1 | Transfer Loading < 100% | 585
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T11245523SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23SP | 615 | 615 | 0 | 95.1 | 95.0921 | 95.1 | [7 empty] | CATEGORYB | SINGLE | MINDEN - SAREPTA 115KV CKT 1 | 0 | 337361 | 3MINDEN_LA! 115.00 | 337363 | 3SAREPTA! 115.00 | 0 |  | 1 | Transfer Loading < 100% | 585
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T6965023SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23SP | 615 | 615 | 0 | 95.2 | 95.2474 | 95.1 | [7 empty] | CATEGORYB | SINGLE | WEBRE - WELLS 500KV CKT 1 | 0 | 335368 | 8WELLS% 500.00 | 335500 | 8WEBRE% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 585
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T9355523SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23SP | 615 | 615 | 0 | 95.2 | 95.1511 | 95.1 | [7 empty] | CATEGORYB | SINGLE | WEBRE - WELLS 500KV CKT 1 | 0 | 335368 | 8WELLS% 500.00 | 335500 | 8WEBRE% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 585
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T7275023SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23SP | 615 | 615 | 0 | 95.1 | 95.0623 | 95 | [7 empty] | CATEGORYB | SINGLE | ENJAY - FANCY POINT 230KV CKT 1 | 0 | 335772 | 6ENJAY! 230.00 | 335825 | 6FANCY_PT% 230.00 | 0 |  | 1 | Transfer Loading < 100% | 585
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1085523SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23SP | 615 | 615 | 0 | 95.1 | 95.0716 | 95 | [7 empty] | CATEGORYB | SINGLE | RICHARD - SELLRD 230KV CKT 1 | 0 | 500765 | RORK 6 230.00 | 500776 | SELLRD6 230.00 | 0 |  | 1 | Transfer Loading < 100% | 585
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T9505523SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23SP | 615 | 615 | 0 | 95.1 | 95.1046 | 95 | [7 empty] | CATEGORYB | SINGLE | WATERFORD - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WILLOW_GL% 500.00 | 336150 | 8WATERFO 500.00 | 0 |  | 1 | Transfer Loading < 100% | 585
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3875523WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23WP | 615 | 615 | 0 | 97.2 | 97.182 | 97.3 | [7 empty] | CATEGORYB | SINGLE | 4VATCAN - SCOTT 138KV CKT 1 | 0 | 303133 | 4VATICAN 138.00 | 335379 | 4SCOTT_1! 138.00 | 0 |  | 1 | Transfer Loading < 100% | 599
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T2185023WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23WP | 615 | 615 | 0 | 96.7 | 96.6699 | 96.7 | [7 empty] | CATEGORYB | SINGLE | 4VATCAN - SCOTT 138KV CKT 1 | 0 | 303133 | 4VATICAN 138.00 | 335379 | 4SCOTT_1! 138.00 | 0 |  | 1 | Transfer Loading < 100% | 595
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T675523WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23WP | 615 | 615 | 0 | 96.2 | 96.2072 | 96.3 | [7 empty] | CATEGORYB | SINGLE | COUGHLIN - PLAISANCE 138KV CKT 1 | 0 | 500230 | COUGH 4 138.00 | 500720 | PLAISAN4 138.00 | 0 |  | 1 | Transfer Loading < 100% | 593
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5795523WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23WP | 615 | 615 | 0 | 96.3 | 96.2752 | 96.3 | [7 empty] | CATEGORYB | SINGLE | FANCY POINT - MCKNIGHT 500KV CKT 1 | 0 | 335835 | 8FANCY_PT% 500.00 | 335836 | 8MCKNIGHT% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 593
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T3515023WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23WP | 615 | 615 | 0 | 96 | 95.9849 | 96 | [7 empty] | CATEGORYB | SINGLE | FANCY POINT - MCKNIGHT 500KV CKT 1 | 0 | 335835 | 8FANCY_PT% 500.00 | 335836 | 8MCKNIGHT% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 591
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T12295523WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23WP | 615 | 615 | 0 | 95.8 | 95.7954 | 95.9 | [7 empty] | CATEGORYB | SINGLE | 8DANIEL 500.00 - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNIGHT% 500.00 | 388700 | 8DANIEL 500.00 | 0 |  | 1 | Transfer Loading < 100% | 590
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5615523WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23WP | 615 | 615 | 0 | 95.9 | 95.8534 | 95.9 | [7 empty] | CATEGORYB | SINGLE | ENJAY - FANCY POINT 230KV CKT 1 | 0 | 335772 | 6ENJAY! 230.00 | 335825 | 6FANCY_PT% 230.00 | 0 |  | 1 | Transfer Loading < 100% | 590
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5855523WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23WP | 615 | 615 | 0 | 95.8 | 95.8104 | 95.8 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNIGHT% 500.00 | 335837 | 8COLY% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 590
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T15415523WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23WP | 615 | 615 | 0 | 95.7 | 95.6788 | 95.8 | [7 empty] | CATEGORYB | GENOUT | GEN336153 1-WATERFORD UNIT#3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 590
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5435523WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23WP | 615 | 615 | 0 | 95.7 | 95.7284 | 95.8 | [7 empty] | CATEGORYB | SINGLE | WATERFORD - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WILLOW_GL% 500.00 | 336150 | 8WATERFO 500.00 | 0 |  | 1 | Transfer Loading < 100% | 590
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3625523WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23WP | 615 | 615 | 0 | 95.6 | 95.62 | 95.7 | [7 empty] | CATEGORYB | SINGLE | 8CAJUN2 - FANCY POINT 500KV CKT 1 | 0 | 303005 | 8BIG_CAJUN2%500.00 | 335835 | 8FANCY_PT% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 589
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5525523WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23WP | 615 | 615 | 0 | 95.6 | 95.6368 | 95.7 | [7 empty] | CATEGORYB | SINGLE | ENJAY - JAGUAR 230KV CKT 1 | 0 | 335770 | 6JAGUAR% 230.00 | 335772 | 6ENJAY! 230.00 | 0 |  | 1 | Transfer Loading < 100% | 589
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T525023WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23WP | 615 | 615 | 0 | 95.5 | 95.5238 | 95.6 | [7 empty] | CATEGORYB | SINGLE | COUGHLIN - PLAISANCE 138KV CKT 1 | 0 | 500230 | COUGH 4 138.00 | 500720 | PLAISAN4 138.00 | 0 |  | 1 | Transfer Loading < 100% | 588
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T755523WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23WP | 615 | 615 | 0 | 95.6 | 95.5588 | 95.6 | [7 empty] | CATEGORYB | SINGLE | RICHARD - SELLRD 230KV CKT 1 | 0 | 500765 | RORK 6 230.00 | 500776 | SELLRD6 230.00 | 0 |  | 1 | Transfer Loading < 100% | 588
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T605523WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23WP | 615 | 615 | 0 | 95.4 | 95.3937 | 95.5 | [7 empty] | CATEGORYB | SINGLE | BAYOU SALE - WAXLAKE 138KV CKT 1 | 0 | 500050 | BSALES 4 138.00 | 500890 | WAXLAKE4 138.00 | 0 |  | 1 | Transfer Loading < 100% | 588
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T15305523WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23WP | 615 | 615 | 0 | 95.4 | 95.407 | 95.5 | [7 empty] | CATEGORYB | GENOUT | GEN335831 1-RIVERBEND UNIT#1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 588
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3925523WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23WP | 615 | 615 | 0 | 95.3 | 95.3481 | 95.4 | [7 empty] | CATEGORYB | SINGLE | 3MNDENLG - MINDEN 115KV CKT 1 | 0 | 303302 | 3MINDEN_LG 115.00 | 337361 | 3MINDEN_LA! 115.00 | 0 |  | 1 | Transfer Loading < 100% | 587
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T8465523WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23WP | 615 | 615 | 0 | 95.4 | 95.3926 | 95.4 | [7 empty] | CATEGORYB | SINGLE | 6MEAUX - SELLRD 230KV CKT 1 | 0 | 500776 | SELLRD6 230.00 | 335381 | 6MEAUX! 230.00 | 0 |  | 1 | Transfer Loading < 100% | 587
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5205523WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23WP | 615 | 615 | 0 | 95.4 | 95.3844 | 95.4 | [7 empty] | CATEGORYB | SINGLE | 6MEAUX 230/138KV TRANSFORMER CKT 1 | 0 | 335380 | 4MEAUX! 138.00 | 335381 | 6MEAUX! 230.00 | 0 |  | 1 | Transfer Loading < 100% | 587
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T1985023WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23WP | 615 | 615 | 0 | 95.3 | 95.2954 | 95.4 | [7 empty] | CATEGORYB | SINGLE | 8CAJUN2 - FANCY POINT 500KV CKT 1 | 0 | 303005 | 8BIG_CAJUN2%500.00 | 335835 | 8FANCY_PT% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 587
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3595523WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23WP | 615 | 615 | 0 | 95.3 | 95.3376 | 95.4 | [7 empty] | CATEGORYB | SINGLE | 8CAJUN2 - WEBRE 500KV CKT 1 | 0 | 303005 | 8BIG_CAJUN2%500.00 | 335500 | 8WEBRE% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 587
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T585523WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23WP | 615 | 615 | 0 | 95.3 | 95.348 | 95.4 | [7 empty] | CATEGORYB | SINGLE | BAYOU SALE - TECHE 138KV CKT 1 | 0 | 500050 | BSALES 4 138.00 | 500820 | TECHE 4 138.00 | 0 |  | 1 | Transfer Loading < 100% | 587
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5125523WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23WP | 615 | 615 | 0 | 95.4 | 95.3598 | 95.4 | [7 empty] | CATEGORYB | SINGLE | BOUDOIN - CARLYSS 230KV CKT 1 | 0 | 335070 | 6CARLYSS% 230.00 | 335073 | 6BOUDOIN% 230.00 | 0 |  | 1 | Transfer Loading < 100% | 587
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T14855523WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23WP | 615 | 615 | 0 | 95.3 | 95.3267 | 95.4 | [7 empty] | CATEGORYB | GENOUT | GEN303006 1-1BC2 U1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 587
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T14965523WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23WP | 615 | 615 | 0 | 95.4 | 95.3755 | 95.4 | [7 empty] | CATEGORYB | GENOUT | GEN303008 1-1BC2 U3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 587
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5465523WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23WP | 615 | 615 | 0 | 95.4 | 95.3524 | 95.4 | [7 empty] | CATEGORYB | SINGLE | JAGUAR - POINT ESSO TAP 230KV CKT 1 | 0 | 335641 | 6ESSO_TP 230.00 | 335770 | 6JAGUAR% 230.00 | 0 |  | 1 | Transfer Loading < 100% | 587
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T6125523WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23WP | 615 | 615 | 0 | 95.3 | 95.2559 | 95.3 | [7 empty] | CATEGORYB | SINGLE | BOGALUSA - FRANKLIN 500KV CKT 1 | 0 | 336130 | 8BOGALUS 500.00 | 336562 | 8FRANKLIN% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 587
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T735523WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23WP | 615 | 615 | 0 | 95.3 | 95.2901 | 95.3 | [7 empty] | CATEGORYB | SINGLE | EL PASO TAP - WAXLAKE 138KV CKT 1 | 0 | 500290 | ELPTAP 4 138.00 | 500890 | WAXLAKE4 138.00 | 0 |  | 1 | Transfer Loading < 100% | 587
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T3335023WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23WP | 615 | 615 | 0 | 95.3 | 95.2652 | 95.3 | [7 empty] | CATEGORYB | SINGLE | ENJAY - FANCY POINT 230KV CKT 1 | 0 | 335772 | 6ENJAY! 230.00 | 335825 | 6FANCY_PT% 230.00 | 0 |  | 1 | Transfer Loading < 100% | 587
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5135523WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23WP | 615 | 615 | 0 |  | 95.2324 | 95.3 | [7 empty] | CATEGORYB | SINGLE | NELSON - RICHARD 500KV CKT 1 | 0 | 335192 | 8NELSON% 500.00 | 335367 | 8RICHARD% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 587
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T785523WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23WP | 615 | 615 | 0 | 95.3 | 95.2904 | 95.3 | [7 empty] | CATEGORYB | SINGLE | SEGURA 230/138KV TRANSFORMER CKT 1 | 0 | 500773 | SEGURA 6 230.00 | 500774 | SEGURA4 138.00 | 0 |  | 1 | Transfer Loading < 100% | 587
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T6155523WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23WP | 615 | 615 | 0 | 95.3 | 95.2516 | 95.3 | [7 empty] | CATEGORYB | SINGLE | WATERFORD 500/230KV TRANSFORMER CKT 1 | 0 | 336150 | 8WATERFO 500.00 | 336154 | 6WATFRD% 230.00 | 0 |  | 1 | Transfer Loading < 100% | 587
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T8615023WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23WP | 615 | 615 | 0 | 95.1 | 95.1463 | 95.2 | [7 empty] | CATEGORYB | SINGLE | 8DANIEL 500.00 - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNIGHT% 500.00 | 388700 | 8DANIEL 500.00 | 0 |  | 1 | Transfer Loading < 100% | 586
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T3205023WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23WP | 615 | 615 | 0 | 95.1 | 95.1371 | 95.2 | [7 empty] | CATEGORYB | SINGLE | WATERFORD - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WILLOW_GL% 500.00 | 336150 | 8WATERFO 500.00 | 0 |  | 1 | Transfer Loading < 100% | 586
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2012AG1AFS41T3575023WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23WP | 615 | 615 | 0 |  | 94.9972 | 95.1 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNIGHT% 500.00 | 335837 | 8COLY% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 585
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T3285023WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23WP | 615 | 615 | 0 | 95.1 | 95.0673 | 95.1 | [7 empty] | CATEGORYB | SINGLE | ENJAY - JAGUAR 230KV CKT 1 | 0 | 335770 | 6JAGUAR% 230.00 | 335772 | 6ENJAY! 230.00 | 0 |  | 1 | Transfer Loading < 100% | 585
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T605023WP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | WECC | WECC | 0 | 303007 | 1BCAJUN2_U2%24.000 | 303005 | 8BIG_CAJUN2%500.00 | 0 |  | 1 | 23WP | 615 | 615 | 0 | 95 | 95.0053 | 95.1 | [7 empty] | CATEGORYB | SINGLE | RICHARD - SELLRD 230KV CKT 1 | 0 | 500765 | RORK 6 230.00 | 500776 | SELLRD6 230.00 | 0 |  | 1 | Transfer Loading < 100% | 585
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T11985513SP | FROM->TO | RAUN 345/22.0KV TRANSFORMER CKT 1 | E | MEC | MEC | MEC_679 | MEC_679 | 0 | 635213 | NEAL 3G 22.000 | 635200 | RAUN 3 345.00 | 0 |  | 1 | 13SP | 560 | 560 | 1282 | 95.1 | 95.0776 | 95.3 | [7 empty] | CATEGORYB | SINGLE | FALLOW 3 345.00 - GRIMES 345KV CKT 1 | 0 | 635590 | FALLOW 3 345.00 | 635600 | GRIMES 3 345.00 | 0 |  | 1 | Transfer Loading < 100% | 534
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T10445514SP | FROM->TO | RAUN 345/22.0KV TRANSFORMER CKT 1 | E | MEC | MEC | MEC_679 | MEC_679 | 0 | 635213 | NEAL 3G 22.000 | 635200 | RAUN 3 345.00 | 0 |  | 1 | 14SP | 560 | 560 | 1282 | 95 | 95.0374 | 95.3 | [7 empty] | CATEGORYB | SINGLE | FALLOW 3 345.00 - GRIMES 345KV CKT 1 | 0 | 635590 | FALLOW 3 345.00 | 635600 | GRIMES 3 345.00 | 0 |  | 1 | Transfer Loading < 100% | 534
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T4995513SP | TO->FROM | N HAYS3 115.00 - VINE STREET 115KV CKT 1 | E | MIDW | MIDW | REG E-IL | REG E-IL | 0 | 530591 | VINE 3 115.00 | 530581 | N HAYS3 115.00 | 0 |  | 1 | 13SP | 83 | 99 | 0 | 96 | 96.008 | 96.5 | [7 empty] | CATEGORYB | SINGLE | KNOLL 230 - POSTROCK6 230.00 230KV CKT 1 | 0 | 530558 | KNOLL 6 230.00 | 530584 | POSTROCK6 230.00 | 0 |  | 1 | Transfer Loading < 100% | 96
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5015513SP | FROM->TO | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | E | MIDW | WERE | REG E-IL | WEST | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 13SP | 319 | 319 | 0 | 98.1 | 98.1158 | 99.1 | [7 empty] | CATEGORYB | SINGLE | AXTELL - POST ROCK 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 640065 | AXTELL 3 345.00 | 0 |  | 1 | Transfer Loading < 100% | 317
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T13395513WP | FROM->TO | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | E | MIDW | WERE | REG E-IL | WEST | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 13WP | 319 | 319 | 0 | 99.8 | 99.6375 | 99.8 | [7 empty] | CATEGORYB | GENOUT | GEN532651 1-JEFFREY ENERGY CENTER UNIT 1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 319
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T4685513WP | FROM->TO | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | E | MIDW | WERE | REG E-IL | WEST | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 13WP | 319 | 319 | 0 | 99 | 98.9602 | 98.9 | [7 empty] | CATEGORYB | SINGLE | MOORE - PAULINE 345KV CKT 1 | 0 | 640277 | MOORE 3 345.00 | 640312 | PAULINE3 345.00 | 0 |  | 1 | Transfer Loading < 100% | 316
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2735513WP | FROM->TO | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | E | MIDW | WERE | REG E-IL | WEST | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 13WP | 319 | 319 | 0 | 97.6 | 97.5818 | 97.3 | [7 empty] | CATEGORYB | SINGLE | MULLERGREN - SOUTH HAYS 230KV CKT 1 | 0 | 530582 | S HAYS6 230.00 | 539679 | GRTBEND6 230.00 | 0 |  | 1 | Transfer Loading < 100% | 311
2012-AG1 | AFS4 | CONT-0402 - JEC - Summit 345kV | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3235513WP | FROM->TO | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | E | MIDW | WERE | REG E-IL | WEST | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 13WP | 319 | 319 | 0 | 96.6 | 96.5739 | 96.1 | [7 empty] | CATEGORYB | SINGLE | JEFFREY ENERGY CENTER - SUMMIT 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532773 | SUMMIT 7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 307
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3715514SP | FROM->TO | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | E | MIDW | WERE | REG E-IL | WEST | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | 14SP | 319 | 319 | 0 | 100.1 | 100.0814 | 99.1 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 | Transfer Loading < 100% | 317
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T475523WP | FROM->TO | MURRAY HYDRO - NORTH LITTLE ROCK (LEVY II) 115/6.9KV TRANSFORMER CKT 1 | E | NLR | EES-EAI |  | NYPA E | 0 | 338482 | 1M.HYD U1 6.9000 | 337935 | 3MURRAY HYD!115.00 | 0 |  | 1 | 23WP | 50 | 50 | 0 | 95.8 | 95.8254 | 95.9 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 48
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T375023WP | FROM->TO | MURRAY HYDRO - NORTH LITTLE ROCK (LEVY II) 115/6.9KV TRANSFORMER CKT 1 | E | NLR | EES-EAI |  | NYPA E | 0 | 338482 | 1M.HYD U1 6.9000 | 337935 | 3MURRAY HYD!115.00 | 0 |  | 1 | 23WP | 50 | 50 | 0 | 95.6 | 95.6029 | 95.6 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 48
2012-AG1 | AFS4NC1 |  |  |  | FDNS-CHECK-TC-Iteration Limit Exceeded. |  | 5 | 5 | 2012AG1AFS4NC11T145513WP | TO->FROM | AINSWORTH - AINSWORTH 115KV CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640050 | AINSWND7 115.00 | 640051 | AINSWRT7 115.00 | 0 |  | 1 | 13WP | 120 | 120 | 132 |  | -999 | 95.6 | [7 empty] | CATEGORYB | SINGLE | BONESTEEL - FT RANDAL 115KV CKT 1 | 0 | 652475 | BONESTL7 115.00 | 652510 | FTRANDL7 115.00 | 0 |  | 1 | Transfer Loading < 100% | 115
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T4625513WP | FROM->TO | BROKEN BOW - LOUP CITY 115KV CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640089 | BROKENB7 115.00 | 640259 | LOUPCTY7 115.00 | 0 |  | 1 | 13WP | 120 | 120 | 127 | 99.2 | 99.1504 | 99.6 | [7 empty] | CATEGORYB | SINGLE | CROOKED CREEK - RIVERDALE 230KV CKT 1 | 0 | 640093 | C.CREEK4 230.00 | 640330 | RIVERDL4 230.00 | 0 |  | 1 | Transfer Loading < 100% | 120
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T4645513WP | FROM->TO | BROKEN BOW - LOUP CITY 115KV CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640089 | BROKENB7 115.00 | 640259 | LOUPCTY7 115.00 | 0 |  | 1 | 13WP | 120 | 120 | 127 | 96 | 96.0141 | 96.5 | [7 empty] | CATEGORYB | SINGLE | GERALD GENTLEMAN STATION - SWEETWATER 345KV CKT 1 | 0 | 640183 | GENTLMN3 345.00 | 640374 | SWEET W3 345.00 | 0 |  | 1 | Transfer Loading < 100% | 116
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3255514WP | FROM->TO | BROKEN BOW - LOUP CITY 115KV CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640089 | BROKENB7 115.00 | 640259 | LOUPCTY7 115.00 | 0 |  | 1 | 14WP | 120 | 120 | 127 |  | 94.9638 | 97.7 | [7 empty] | CATEGORYB | SINGLE | BROKEN BOW - CROOKED CREEK 115KV CKT 1 | 0 | 640089 | BROKENB7 115.00 | 640094 | C.CREEK7 115.00 | 0 |  | 1 | Transfer Loading < 100% | 118
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3295514WP | FROM->TO | BROKEN BOW - LOUP CITY 115KV CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640089 | BROKENB7 115.00 | 640259 | LOUPCTY7 115.00 | 0 |  | 1 | 14WP | 120 | 120 | 127 |  | 93.4458 | 97.4 | [7 empty] | CATEGORYB | SINGLE | GERALD GENTLEMAN STATION - SWEETWATER 345KV CKT 1 | 0 | 640183 | GENTLMN3 345.00 | 640374 | SWEET W3 345.00 | 0 |  | 1 | Transfer Loading < 100% | 117
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T8435514WP | FROM->TO | BROKEN BOW - LOUP CITY 115KV CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640089 | BROKENB7 115.00 | 640259 | LOUPCTY7 115.00 | 0 |  | 1 | 14WP | 120 | 120 | 127 |  | 94.5128 | 97.3 | [7 empty] | CATEGORYB | SINGLE | CROOKED CREEK (CR.CREEK T1) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 640093 | C.CREEK4 230.00 | 640094 | C.CREEK7 115.00 | 643026 | CRKDCREEKT1913.800 | 1 | Transfer Loading < 100% | 117
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T4725513WP | TO->FROM | GRAND ISLAND - SWEETWATER 345KV CKT 1 | E | NPPD | NPPD | NPPD_686 | WAPA_1606 | 0 | 640374 | SWEET W3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 | 13WP | 717 | 717 | 789 | 95.4 | 95.3579 | 96.2 | [7 empty] | CATEGORYB | SINGLE | MOORE - PAULINE 345KV CKT 1 | 0 | 640277 | MOORE 3 345.00 | 640312 | PAULINE3 345.00 | 0 |  | 1 | Transfer Loading < 100% | 690
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T6105514SP | TO->FROM | GRAND ISLAND - SWEETWATER 345KV CKT 1 | E | NPPD | NPPD | NPPD_686 | WAPA_1606 | 0 | 640374 | SWEET W3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 | 14SP | 717 | 717 | 789 | 96.2 | 96.158 | 96.4 | [7 empty] | CATEGORYB | SINGLE | AXTELL - SWEETWATER 345KV CKT 1 | 0 | 640065 | AXTELL 3 345.00 | 640374 | SWEET W3 345.00 | 0 |  | 1 | Transfer Loading < 100% | 692
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3325514WP | TO->FROM | GRAND ISLAND - SWEETWATER 345KV CKT 1 | E | NPPD | NPPD | NPPD_686 | WAPA_1606 | 0 | 640374 | SWEET W3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 | 14WP | 717 | 717 | 789 |  | 89.4068 | 97.6 | [7 empty] | CATEGORYB | SINGLE | MOORE - PAULINE 345KV CKT 1 | 0 | 640277 | MOORE 3 345.00 | 640312 | PAULINE3 345.00 | 0 |  | 1 | Transfer Loading < 100% | 700
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T10955013SP | FROM->TO | SHELDON 115/13.8KV TRANSFORMER CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640020 | SHELDN2G 13.800 | 640278 | SHELDON7 115.00 | 0 |  | 1 | 13SP | 140 | 140 | 140 | 97.4 | 97.365 | 97.4 | [7 empty] | CATEGORYB | SINGLE | KEYSTONE - SIDNEY 345KV CKT 1 | 0 | 640252 | KEYSTON3 345.00 | 659133 | SIDNEY 3 345.00 | 0 |  | 1 | Transfer Loading < 100% | 137
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T10025014SP | FROM->TO | SHELDON 115/13.8KV TRANSFORMER CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640020 | SHELDN2G 13.800 | 640278 | SHELDON7 115.00 | 0 |  | 1 | 14SP | 140 | 140 | 140 | 96.2 | 96.2284 | 96.2 | [7 empty] | CATEGORYB | SINGLE | KEYSTONE - SIDNEY 345KV CKT 1 | 0 | 640252 | KEYSTON3 345.00 | 659133 | SIDNEY 3 345.00 | 0 |  | 1 | Transfer Loading < 100% | 135
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T2895018SP | FROM->TO | SHELDON 115/13.8KV TRANSFORMER CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640020 | SHELDN2G 13.800 | 640278 | SHELDON7 115.00 | 0 |  | 1 | 18SP | 140 | 140 | 140 | 101 | 100.9677 | 98.8 | [7 empty] | CATEGORYB | SINGLE | GERALD GENTLEMAN STATION - RED WILLOW 345KV CKT 1 | 0 | 640183 | GENTLMN3 345.00 | 640325 | REDWILO3 345.00 | 0 |  | 1 | Transfer Loading < 100% | 139
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T10755018SP | FROM->TO | SHELDON 115/13.8KV TRANSFORMER CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640020 | SHELDN2G 13.800 | 640278 | SHELDON7 115.00 | 0 |  | 1 | 18SP | 140 | 140 | 140 | 96.4 | 96.4238 | 96.1 | [7 empty] | CATEGORYB | SINGLE | KEYSTONE - SIDNEY 345KV CKT 1 | 0 | 640252 | KEYSTON3 345.00 | 659133 | SIDNEY 3 345.00 | 0 |  | 1 | Transfer Loading < 100% | 135
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2012AG1AFS41T2925018SP | FROM->TO | SHELDON 115/13.8KV TRANSFORMER CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640020 | SHELDN2G 13.800 | 640278 | SHELDON7 115.00 | 0 |  | 1 | 18SP | 140 | 140 | 140 |  | -999 | 95.3 | [7 empty] | CATEGORYB | SINGLE | MAXWELL - NORTH PLATTE 115KV CKT 1 | 0 | 640267 | MAXWELS7 115.00 | 640287 | N.PLATT7 115.00 | 0 |  | 1 | Transfer Loading < 100% | 134
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T7105523SP | FROM->TO | SHELDON 115/13.8KV TRANSFORMER CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640020 | SHELDN2G 13.800 | 640278 | SHELDON7 115.00 | 0 |  | 1 | 23SP | 140 | 140 | 140 |  | 94.3684 | 96.8 | [7 empty] | CATEGORYB | SINGLE | GRAND ISLAND - SWEETWATER 345KV CKT 1 | 0 | 640374 | SWEET W3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 | Transfer Loading < 100% | 136
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T6855523SP | FROM->TO | SHELDON 115/13.8KV TRANSFORMER CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640020 | SHELDN2G 13.800 | 640278 | SHELDON7 115.00 | 0 |  | 1 | 23SP | 140 | 140 | 140 | 95.7 | 95.6741 | 96.5 | [7 empty] | CATEGORYB | SINGLE | AINSWORTH - AINSWORTH 115KV CKT 1 | 0 | 640050 | AINSWND7 115.00 | 640051 | AINSWRT7 115.00 | 0 |  | 1 | Transfer Loading < 100% | 136
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T6985523SP | FROM->TO | SHELDON 115/13.8KV TRANSFORMER CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640020 | SHELDN2G 13.800 | 640278 | SHELDON7 115.00 | 0 |  | 1 | 23SP | 140 | 140 | 140 |  | 94.3911 | 96.2 | [7 empty] | CATEGORYB | SINGLE | CHERRYC3 345.00 - GERALD GENTLEMAN STATION 345KV CKT 1 | 0 | 640183 | GENTLMN3 345.00 | 640500 | CHERRYC3 345.00 | 0 |  | 1 | Transfer Loading < 100% | 135
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T7125523SP | FROM->TO | SHELDON 115/13.8KV TRANSFORMER CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640020 | SHELDN2G 13.800 | 640278 | SHELDON7 115.00 | 0 |  | 1 | 23SP | 140 | 140 | 140 |  | 93.5958 | 95.7 | [7 empty] | CATEGORYB | SINGLE | CHERRYC3 345.00 - HOLT.CO3 345.00 345KV CKT 1 | 0 | 640500 | CHERRYC3 345.00 | 640510 | HOLT.CO3 345.00 | 0 |  | 1 | Transfer Loading < 100% | 134
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T14875023SP | FROM->TO | SHELDON 115/13.8KV TRANSFORMER CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640020 | SHELDN2G 13.800 | 640278 | SHELDON7 115.00 | 0 |  | 1 | 23SP | 140 | 140 | 140 | 96.7 | 96.7383 | 95.6 | [7 empty] | CATEGORYB | SINGLE | KEYSTONE - SIDNEY 345KV CKT 1 | 0 | 640252 | KEYSTON3 345.00 | 659133 | SIDNEY 3 345.00 | 0 |  | 1 | Transfer Loading < 100% | 134
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T4495523SP | FROM->TO | SHELDON 115/13.8KV TRANSFORMER CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640020 | SHELDN2G 13.800 | 640278 | SHELDON7 115.00 | 0 |  | 1 | 23SP | 140 | 140 | 140 |  | 92.1227 | 95.4 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 | Transfer Loading < 100% | 134
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T7645523WP | FROM->TO | SHELDON 115/13.8KV TRANSFORMER CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640020 | SHELDN2G 13.800 | 640278 | SHELDON7 115.00 | 0 |  | 1 | 23WP | 140 | 140 | 140 | 99.9 | 99.8549 | 99.9 | [7 empty] | CATEGORYB | SINGLE | NUNDRWD - WAYSIDE 230KV CKT 1 | 0 | 640404 | WAYSIDE4 230.00 | 652484 | NUNDRWD4 230.00 | 0 |  | 1 | Transfer Loading < 100% | 140
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3385523WP | FROM->TO | SHELDON 115/13.8KV TRANSFORMER CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640020 | SHELDN2G 13.800 | 640278 | SHELDON7 115.00 | 0 |  | 1 | 23WP | 140 | 140 | 140 | 97.6 | 97.6046 | 98 | [7 empty] | CATEGORYB | SINGLE | GRAND ISLAND - SWEETWATER 345KV CKT 1 | 0 | 640374 | SWEET W3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 | Transfer Loading < 100% | 138
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T4925023WP | FROM->TO | SHELDON 115/13.8KV TRANSFORMER CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640020 | SHELDN2G 13.800 | 640278 | SHELDON7 115.00 | 0 |  | 1 | 23WP | 140 | 140 | 140 | 96.6 | 96.6223 | 97.8 | [7 empty] | CATEGORYB | SINGLE | STEGALL - WAYSIDE 230KV CKT 1 | 0 | 640404 | WAYSIDE4 230.00 | 652573 | STEGALL4 230.00 | 0 |  | 1 | Transfer Loading < 100% | 137
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2425523WP | FROM->TO | SHELDON 115/13.8KV TRANSFORMER CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640020 | SHELDN2G 13.800 | 640278 | SHELDON7 115.00 | 0 |  | 1 | 23WP | 140 | 140 | 140 | 96.1 | 96.0847 | 97.6 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 | Transfer Loading < 100% | 137
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T7235023WP | FROM->TO | SHELDON 115/13.8KV TRANSFORMER CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640020 | SHELDN2G 13.800 | 640278 | SHELDON7 115.00 | 0 |  | 1 | 23WP | 140 | 140 | 140 | 96.7 | 96.7115 | 95.7 | [7 empty] | CATEGORYB | SINGLE | KEYSTONE - SIDNEY 345KV CKT 1 | 0 | 640252 | KEYSTON3 345.00 | 659133 | SIDNEY 3 345.00 | 0 |  | 1 | Transfer Loading < 100% | 134
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3285523WP | FROM->TO | SHELDON 115/13.8KV TRANSFORMER CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640020 | SHELDN2G 13.800 | 640278 | SHELDON7 115.00 | 0 |  | 1 | 23WP | 140 | 140 | 140 | 96.5 | 96.5115 | 95.5 | [7 empty] | CATEGORYB | SINGLE | GERALD GENTLEMAN STATION - SWEETWATER 345KV CKT 1 | 0 | 640183 | GENTLMN3 345.00 | 640374 | SWEET W3 345.00 | 0 |  | 1 | Transfer Loading < 100% | 134
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3355523WP | FROM->TO | SHELDON 115/13.8KV TRANSFORMER CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640020 | SHELDN2G 13.800 | 640278 | SHELDON7 115.00 | 0 |  | 1 | 23WP | 140 | 140 | 140 | 95.1 | 95.1058 | 95.3 | [7 empty] | CATEGORYB | SINGLE | MOORE - PAULINE 345KV CKT 1 | 0 | 640277 | MOORE 3 345.00 | 640312 | PAULINE3 345.00 | 0 |  | 1 | Transfer Loading < 100% | 134
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3225513SP | FROM->TO | 5 TRIBES - HANCOCK 161KV CKT 1 | E | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515228 | 5TRIBES5 161.00 | 515250 | HANCOK-5 161.00 | 0 |  | 1 | 13SP | 223 | 223 | 0 | 99.7 | 99.6865 | 99.9 | [7 empty] | CATEGORYB | SINGLE | FT SMITH - MUSKOGEE 345KV CKT 1 | 0 | 515224 | MUSKOGE7 345.00 | 515302 | FTSMITH7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 223
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T14435518SP | FROM->TO | 5 TRIBES - HANCOCK 161KV CKT 1 | E | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515228 | 5TRIBES5 161.00 | 515250 | HANCOK-5 161.00 | 0 |  | 1 | 18SP | 223 | 223 | 0 |  | 84.5755 | 95.3 | [7 empty] | CATEGORYB | SINGLE | 5LOCSTGV - MAID 161KV CKT 1 | 0 | 512648 | MAID 5 161.00 | 300274 | 5LOCSTGV 161.00 | 0 |  | 1 | Transfer Loading < 100% | 213
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T6515518SP | FROM->TO | 5 TRIBES - HANCOCK 161KV CKT 1 | E | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515228 | 5TRIBES5 161.00 | 515250 | HANCOK-5 161.00 | 0 |  | 1 | 18SP | 223 | 223 | 0 |  | 84.3698 | 95.1 | [7 empty] | CATEGORYB | SINGLE | 5CDRCRST 161.00 - 5LOCSTGV 161KV CKT 1 | 0 | 300274 | 5LOCSTGV 161.00 | 301344 | 5CDRCRST 161.00 | 0 |  | 1 | Transfer Loading < 100% | 213
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2845523SP | FROM->TO | 5 TRIBES - HANCOCK 161KV CKT 1 | E | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515228 | 5TRIBES5 161.00 | 515250 | HANCOK-5 161.00 | 0 |  | 1 | 23SP | 223 | 223 | 0 |  | 91.3982 | 97.8 | [7 empty] | CATEGORYB | SINGLE | GRDA1 - WAGONER 161KV CKT 1 | 0 | 512656 | GRDA1 5 161.00 | 512700 | WAGNOR 5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 219
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1955523WP | FROM->TO | 5 TRIBES - HANCOCK 161KV CKT 1 | E | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515228 | 5TRIBES5 161.00 | 515250 | HANCOK-5 161.00 | 0 |  | 1 | 23WP | 223 | 223 | 0 |  | 90.0806 | 95.5 | [7 empty] | CATEGORYB | SINGLE | AGENCY - EUCLID 161KV CKT 1 | 0 | 515230 | AGENCY 5 161.00 | 515251 | EUCLID 5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 213
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3475523SP | TO->FROM | AGENCY - PECAN CREEK 161KV CKT 1 | E | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515234 | PECANCK5 161.00 | 515230 | AGENCY 5 161.00 | 0 |  | 1 | 23SP | 313 | 335 | 0 |  | 94.0912 | 99.8 | [7 empty] | CATEGORYB | SINGLE | 5 TRIBES - PECAN CREEK 161KV CKT 1 | 0 | 515228 | 5TRIBES5 161.00 | 515234 | PECANCK5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 335
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T24895523SP | TO->FROM | COUNCIL - MUSTANG 138KV CKT 1 | E | OKGE | OKGE |  |  | 0 | 514861 | MUSTANG4 138.00 | 514865 | COUNCIL4 138.00 | 0 |  | 1 | 23SP | 287 | 287 | 0 | 98.3 | 98.2504 | 98.5 | [7 empty] | CATEGORYB | NONSINGLE | OGE3TERM15 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 283
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3265523SP | TO->FROM | COUNCIL - MUSTANG 138KV CKT 1 | E | OKGE | OKGE |  |  | 0 | 514861 | MUSTANG4 138.00 | 514865 | COUNCIL4 138.00 | 0 |  | 1 | 23SP | 287 | 287 | 0 | 97.4 | 97.3664 | 97.5 | [7 empty] | CATEGORYB | SINGLE | CLASSEN - SW 5TAP 138KV CKT 1 | 0 | 514921 | SW 5TAP4 138.00 | 514922 | CLASSEN4 138.00 | 0 |  | 1 | Transfer Loading < 100% | 280
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1045518WP | FROM->TO | DIVISION AVE - MUSTANG 138KV CKT 1 | E | OKGE | OKGE |  |  | 0 | 514853 | DVISION4 138.00 | 514861 | MUSTANG4 138.00 | 0 |  | 1 | 18WP | 237 | 287 | 0 |  | 92.0233 | 95.5 | [7 empty] | CATEGORYB | SINGLE | CIMARRON - CZECH HALL 138KV CKT 1 | 0 | 514894 | CZECHAL4 138.00 | 514898 | CIMARON4 138.00 | 0 |  | 1 | Transfer Loading < 100% | 275
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T2645023SP | FROM->TO | DUNJEE - RENO 138KV CKT 1 | E | OKGE | OKGE |  |  | 0 | 514884 | DUNJEE 4 138.00 | 514973 | RENO 4 138.00 | 0 |  | 1 | 23SP | 287 | 287 | 0 | 97.5 | 97.5179 | 96.8 | [7 empty] | CATEGORYB | SINGLE | HORSESHOE LAKE - MIDWAY 138KV CKT 1 | 0 | 514941 | HSL 4 138.00 | 514966 | MIDWAY 4 138.00 | 0 |  | 1 | Transfer Loading < 100% | 278
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T21955513SP | TO->FROM | FT SMITH - MUSKOGEE 345KV CKT 1 | E | OKGE | OKGE | MUSKOGEE | FT SMITH | 0 | 515224 | MUSKOGE7 345.00 | 515302 | FTSMITH7 345.00 | 0 |  | 1 | 13SP | 717 | 717 | 0 | 97.1 | 97.1076 | 97.9 | [7 empty] | CATEGORYB | GENOUT | GEN337911 1-ARKANSAS NUCLEAR ONE UNIT #2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 702
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T18955514SP | TO->FROM | FT SMITH - MUSKOGEE 345KV CKT 1 | E | OKGE | OKGE | MUSKOGEE | FT SMITH | 0 | 515224 | MUSKOGE7 345.00 | 515302 | FTSMITH7 345.00 | 0 |  | 1 | 14SP | 717 | 717 | 0 |  | 89.7857 | 95.9 | [7 empty] | CATEGORYB | NONSINGLE | SPP-AEPW-01 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 688
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1505523SP | TO->FROM | FT SMITH - MUSKOGEE 345KV CKT 1 | E | OKGE | OKGE | MUSKOGEE | FT SMITH | 0 | 515224 | MUSKOGE7 345.00 | 515302 | FTSMITH7 345.00 | 0 |  | 1 | 23SP | 717 | 717 | 0 |  | 84.2384 | 96.6 | [7 empty] | CATEGORYB | SINGLE | CHAMBER SPRINGS - CLARKSVILLE 345KV CKT 1 | 0 | 506945 | CHAMSPR7 345.00 | 509745 | CLARKSV7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 693
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T26075523SP | TO->FROM | FT SMITH - MUSKOGEE 345KV CKT 1 | E | OKGE | OKGE | MUSKOGEE | FT SMITH | 0 | 515224 | MUSKOGE7 345.00 | 515302 | FTSMITH7 345.00 | 0 |  | 1 | 23SP | 717 | 717 | 0 |  | 84.5712 | 96 | [7 empty] | CATEGORYB | GENOUT | GEN336153 1-WATERFORD UNIT#3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 689
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T25985523SP | TO->FROM | FT SMITH - MUSKOGEE 345KV CKT 1 | E | OKGE | OKGE | MUSKOGEE | FT SMITH | 0 | 515224 | MUSKOGE7 345.00 | 515302 | FTSMITH7 345.00 | 0 |  | 1 | 23SP | 717 | 717 | 0 |  | 83.7051 | 95.1 | [7 empty] | CATEGORYB | GENOUT | GEN335831 1-RIVERBEND UNIT#1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 682
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T14745518SP | FROM->TO | FT SMITH (FTSMITH5) 345/161/13.8KV TRANSFORMER CKT 5 | E | OKGE | OKGE | FT SMITH | FT SMITH | 1 | 515302 | FTSMITH7 345.00 | 515301 | FTSMTHW5 161.00 | 515728 | FTSMTH51 13.800 | 5 | 18SP | 493 | 493 | 0 |  | 77.5045 | 98.3 | [7 empty] | CATEGORYB | SINGLE | FT SMITH (FTSMITH1) 500/345/13.8KV TRANSFORMER CKT 1 | 1 | 515302 | FTSMITH7 345.00 | 515305 | FTSMITH8 500.00 | 515726 | FTSMTH11 13.800 | 1 | Transfer Loading < 100% | 485
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3275513SP | FROM->TO | HANCOCK - MUSKOGEE 161KV CKT 1 | E | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515250 | HANCOK-5 161.00 | 515222 | MUSKOGE5 161.00 | 0 |  | 1 | 13SP | 223 | 223 | 0 | 95.8 | 95.8029 | 95.8 | [7 empty] | CATEGORYB | SINGLE | AGENCY - PECAN CREEK 161KV CKT 1 | 0 | 515230 | AGENCY 5 161.00 | 515234 | PECANCK5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 214
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2675514SP | FROM->TO | HANCOCK - MUSKOGEE 161KV CKT 1 | E | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515250 | HANCOK-5 161.00 | 515222 | MUSKOGE5 161.00 | 0 |  | 1 | 14SP | 223 | 223 | 0 | 96.1 | 96.1311 | 99.7 | [7 empty] | CATEGORYB | SINGLE | AGENCY - EUCLID 161KV CKT 1 | 0 | 515230 | AGENCY 5 161.00 | 515251 | EUCLID 5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 223
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2595518SP | FROM->TO | HANCOCK - MUSKOGEE 161KV CKT 1 | E | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515250 | HANCOK-5 161.00 | 515222 | MUSKOGE5 161.00 | 0 |  | 1 | 18SP | 223 | 223 | 0 |  | 84.6013 | 99.2 | [7 empty] | CATEGORYB | SINGLE | MUSKOGEE - MUSKOGEE PORT 161KV CKT 1 | 0 | 515222 | MUSKOGE5 161.00 | 515232 | MSKPTAP5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 222
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3425523SP | FROM->TO | HANCOCK - MUSKOGEE 161KV CKT 1 | E | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515250 | HANCOK-5 161.00 | 515222 | MUSKOGE5 161.00 | 0 |  | 1 | 23SP | 223 | 223 | 0 |  | 88.4695 | 98.3 | [7 empty] | CATEGORYB | SINGLE | FT SMITH - MUSKOGEE 345KV CKT 1 | 0 | 515224 | MUSKOGE7 345.00 | 515302 | FTSMITH7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 220
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3255513SP | TO->FROM | MUSKOGEE - MUSKOGEE PORT 161KV CKT 1 | E | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515232 | MSKPTAP5 161.00 | 515222 | MUSKOGE5 161.00 | 0 |  | 1 | 13SP | 223 | 223 | 0 | 99.2 | 99.2051 | 99.2 | [7 empty] | CATEGORYB | SINGLE | 5 TRIBES - PECAN CREEK 161KV CKT 1 | 0 | 515228 | 5TRIBES5 161.00 | 515234 | PECANCK5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 222
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3265513SP | TO->FROM | MUSKOGEE - MUSKOGEE PORT 161KV CKT 1 | E | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515232 | MSKPTAP5 161.00 | 515222 | MUSKOGE5 161.00 | 0 |  | 1 | 13SP | 223 | 223 | 0 | 97.5 | 97.5393 | 97.5 | [7 empty] | CATEGORYB | SINGLE | 5 TRIBES - HANCOCK 161KV CKT 1 | 0 | 515228 | 5TRIBES5 161.00 | 515250 | HANCOK-5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 218
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2615518SP | TO->FROM | MUSKOGEE - MUSKOGEE PORT 161KV CKT 1 | E | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515232 | MSKPTAP5 161.00 | 515222 | MUSKOGE5 161.00 | 0 |  | 1 | 18SP | 223 | 223 | 0 |  | 80.873 | 95.1 | [7 empty] | CATEGORYB | SINGLE | HANCOCK - MUSKOGEE 161KV CKT 1 | 0 | 515222 | MUSKOGE5 161.00 | 515250 | HANCOK-5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 213
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T16625523SP | FROM->TO | MUSKOGEE - ROSS LAKE 161KV CKT 1 | E | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515222 | MUSKOGE5 161.00 | 515252 | ROSSLAK5 161.00 | 0 |  | 1 | 23SP | 223 | 223 | 0 |  | 90.9788 | 96.5 | [7 empty] | CATEGORYB | SINGLE | 5LOCSTGV - MAID 161KV CKT 1 | 0 | 512648 | MAID 5 161.00 | 300274 | 5LOCSTGV 161.00 | 0 |  | 1 | Transfer Loading < 100% | 216
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T7395523SP | FROM->TO | MUSKOGEE - ROSS LAKE 161KV CKT 1 | E | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515222 | MUSKOGE5 161.00 | 515252 | ROSSLAK5 161.00 | 0 |  | 1 | 23SP | 223 | 223 | 0 |  | 90.3707 | 95.9 | [7 empty] | CATEGORYB | SINGLE | 5CDRCRST 161.00 - 5LOCSTGV 161KV CKT 1 | 0 | 300274 | 5LOCSTGV 161.00 | 301344 | 5CDRCRST 161.00 | 0 |  | 1 | Transfer Loading < 100% | 214
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3135513SP | FROM->TO | NORTHWEST (NORTWST2) 345/138/13.8KV TRANSFORMER CKT 1 | E | OKGE | OKGE |  |  | 2 | 514880 | NORTWST7 345.00 | 514879 | NORTWST4 138.00 | 515742 | NORTWS21 13.800 | 1 | 13SP | 493 | 493 | 0 | 95.9 | 95.8627 | 96.3 | [7 empty] | CATEGORYB | SINGLE | CIMARRON - NORTHWEST 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 514901 | CIMARON7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 475
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T7825513WP | FROM->TO | NORTHWEST (NORTWST3) 345/138/13.8KV TRANSFORMER CKT 1 | E | OKGE | OKGE |  |  | 2 | 514880 | NORTWST7 345.00 | 514879 | NORTWST4 138.00 | 515743 | NORTWS31 13.800 | 1 | 13WP | 493 | 493 | 0 | 97.9 | 97.8873 | 99.4 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST (NORTWST2) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514879 | NORTWST4 138.00 | 514880 | NORTWST7 345.00 | 515742 | NORTWS21 13.800 | 1 | Transfer Loading < 100% | 491
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2545518SP | TO->FROM | PARK LANE - SEMINOLE 138KV CKT 1 | E | OKGE | OKGE | SHAWNEE | ARDMORE | 0 | 515044 | SEMINOL4 138.00 | 515178 | PARKLN 4 138.00 | 0 |  | 1 | 18SP | 287 | 287 | 0 |  | 84.1412 | 95.1 | [7 empty] | CATEGORYB | SINGLE | SEMINOLE - VANOSS 138KV CKT 1 | 0 | 515044 | SEMINOL4 138.00 | 515174 | VANOSS 4 138.00 | 0 |  | 1 | Transfer Loading < 100% | 273
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T12465514SP | FROM->TO | PECAN CREEK (PECANCK1) 345/161/13.8KV TRANSFORMER CKT 1 | E | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 2 | 515235 | PECANCK7 345.00 | 515234 | PECANCK5 161.00 | 515749 | PECANC11 13.800 | 1 | 14SP | 370 | 370 | 0 |  | 93.5006 | 95.3 | [7 empty] | CATEGORYB | SINGLE | PECAN CREEK (PECANCK1) 345/161/13.8KV TRANSFORMER CKT 2 | 1 | 515234 | PECANCK5 161.00 | 515235 | PECANCK7 345.00 | 515759 | PECANC21 13.800 | 2 | Transfer Loading < 100% | 353
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T14735518SP | FROM->TO | PECAN CREEK (PECANCK1) 345/161/13.8KV TRANSFORMER CKT 1 | E | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 2 | 515235 | PECANCK7 345.00 | 515234 | PECANCK5 161.00 | 515749 | PECANC11 13.800 | 1 | 18SP | 370 | 370 | 0 |  | 89.002 | 96 | [7 empty] | CATEGORYB | SINGLE | PECAN CREEK (PECANCK1) 345/161/13.8KV TRANSFORMER CKT 2 | 1 | 515234 | PECANCK5 161.00 | 515235 | PECANCK7 345.00 | 515759 | PECANC21 13.800 | 2 | Transfer Loading < 100% | 356
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T7145523SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 23SP | 250 | 250 | 250 | 98.2 | 98.2389 | 98.3 | [7 empty] | CATEGORYB | SINGLE | SUB 3455 - SUB 3740 345KV CKT 1 | 0 | 645455 | S3455 3 345.00 | 645740 | S3740 3 345.00 | 0 |  | 1 | Transfer Loading < 100% | 246
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T4445023SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 23SP | 250 | 250 | 250 | 97.5 | 97.4612 | 97.6 | [7 empty] | CATEGORYB | SINGLE | SUB 3455 - SUB 3740 345KV CKT 1 | 0 | 645455 | S3455 3 345.00 | 645740 | S3740 3 345.00 | 0 |  | 1 | Transfer Loading < 100% | 244
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T13565523SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 23SP | 250 | 250 | 250 | 97 | 96.997 | 97.3 | [7 empty] | CATEGORYB | SINGLE | ATCHSNT3 345.00 - BOONEVILLE 345KV CKT 1 | 0 | 635017 | ATCHSNT3 345.00 | 635630 | BOONVIL3 345.00 | 0 |  | 1 | Transfer Loading < 100% | 244
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T19965523SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 23SP | 250 | 250 | 250 | 96.8 | 96.7563 | 97.1 | [7 empty] | CATEGORYB | SINGLE | ATCHSNT3 345.00 - COOPER 345KV CKT 1 | 0 | 640139 | COOPER 3 345.00 | 635017 | ATCHSNT3 345.00 | 0 |  | 1 | Transfer Loading < 100% | 243
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T24905523SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 23SP | 250 | 250 | 250 |  | 94.3752 | 96.9 | [7 empty] | CATEGORYB | SINGLE | NF | 0 | 0 | NF | 0 | NF | 0 |  |  | Transfer Loading < 100% | 243
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T20225523SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 23SP | 250 | 250 | 250 | 96.6 | 96.6311 | 96.6 | [7 empty] | CATEGORYB | SINGLE | SUB 3456 (S3456 T4) 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 645456 | S3456 3 345.00 | 646206 | S1206 5 161.00 | 648256 | S3456T49 13.800 | 1 | Transfer Loading < 100% | 242
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2012AG1AFS41T19645023SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 23SP | 250 | 250 | 250 |  | 94.0746 | 96.5 | [7 empty] | CATEGORYB | SINGLE | NF | 0 | 0 | NF | 0 | NF | 0 |  |  | Transfer Loading < 100% | 242
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T15065023SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 23SP | 250 | 250 | 250 | 96.4 | 96.4237 | 96.4 | [7 empty] | CATEGORYB | SINGLE | SUB 3456 (S3456 T4) 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 645456 | S3456 3 345.00 | 646206 | S1206 5 161.00 | 648256 | S3456T49 13.800 | 1 | Transfer Loading < 100% | 242
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2012AG1AFS41T19635023SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 23SP | 250 | 250 | 250 |  | 94.0746 | 96.3 | [7 empty] | CATEGORYB | SINGLE | NF | 0 | 0 | NF | 0 | NF | 0 |  |  | Transfer Loading < 100% | 241
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T7155523SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 23SP | 250 | 250 | 250 | 96.1 | 96.1061 | 96.2 | [7 empty] | CATEGORYB | SINGLE | SUB 3456 - SUB 3458 NEB CTY 345KV CKT 1 | 0 | 645456 | S3456 3 345.00 | 645458 | S3458 3 345.00 | 0 |  | 1 | Transfer Loading < 100% | 241
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T6925523SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 23SP | 250 | 250 | 250 | 96 | 96.0371 | 96.1 | [7 empty] | CATEGORYB | SINGLE | FIRTH - SHELDON 115KV CKT 1 | 0 | 640171 | FIRTH 7 115.00 | 640278 | SHELDON7 115.00 | 0 |  | 1 | Transfer Loading < 100% | 241
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T7205523SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 23SP | 250 | 250 | 250 | 95.8 | 95.8212 | 95.9 | [7 empty] | CATEGORYB | SINGLE | SUB 1214 - SUB 914 69KV CKT 1 | 0 | 647014 | S914A 8 69.000 | 647914 | S914 8 69.000 | 0 |  | 1 | Transfer Loading < 100% | 240
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T20385523SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 23SP | 250 | 250 | 250 | 95.7 | 95.7458 | 95.9 | [7 empty] | CATEGORYB | SINGLE | SUB 1214 (S1214 T1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 646214 | S1214 5 161.00 | 647014 | S914A 8 69.000 | 648214 | S1214T19 13.800 | 1 | Transfer Loading < 100% | 240
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T7165523SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 23SP | 250 | 250 | 250 | 95.7 | 95.7462 | 95.8 | [7 empty] | CATEGORYB | SINGLE | SUB 1206 - SUB 1216 161KV CKT 1 | 0 | 646206 | S1206 5 161.00 | 646216 | S1216 5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 240
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T15145023SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 23SP | 250 | 250 | 250 | 95.8 | 95.7858 | 95.8 | [7 empty] | CATEGORYB | SINGLE | SUB 3459 (S3459 T3) 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 645459 | S3459 3 345.00 | 646209 | S1209 5 161.00 | 648259 | S3459T39 13.800 | 1 | Transfer Loading < 100% | 240
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T4315023SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 23SP | 250 | 250 | 250 | 95.8 | 95.8171 | 95.7 | [7 empty] | CATEGORYB | SINGLE | COOPER - MOORE 345KV CKT 1 | 0 | 640139 | COOPER 3 345.00 | 640277 | MOORE 3 345.00 | 0 |  | 1 | Transfer Loading < 100% | 240
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T15055023SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 23SP | 250 | 250 | 250 | 95.5 | 95.4546 | 95.7 | [7 empty] | CATEGORYB | SINGLE | COUNCIL BLUFFS - SUB 3456 345KV CKT 1 | 0 | 645456 | S3456 3 345.00 | 635000 | CBLUFFS3 345.00 | 0 |  | 1 | Transfer Loading < 100% | 240
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T4325023SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 23SP | 250 | 250 | 250 | 95.6 | 95.6434 | 95.7 | [7 empty] | CATEGORYB | SINGLE | FIRTH - SHELDON 115KV CKT 1 | 0 | 640171 | FIRTH 7 115.00 | 640278 | SHELDON7 115.00 | 0 |  | 1 | Transfer Loading < 100% | 240
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T7185523SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 23SP | 250 | 250 | 250 | 95.6 | 95.6408 | 95.7 | [7 empty] | CATEGORYB | SINGLE | SUB 1233 - SUB 1255 161KV CKT 1 | 0 | 646233 | S1233 5 161.00 | 646255 | S1255 5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 240
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2012AG1AFS41T10325023SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 23SP | 250 | 250 | 250 |  | 95.2687 | 95.5 | [7 empty] | CATEGORYB | SINGLE | ATCHSNT3 345.00 - BOONEVILLE 345KV CKT 1 | 0 | 635017 | ATCHSNT3 345.00 | 635630 | BOONVIL3 345.00 | 0 |  | 1 | Transfer Loading < 100% | 239
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2012AG1AFS41T14815023SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 23SP | 250 | 250 | 250 |  | 95.1694 | 95.4 | [7 empty] | CATEGORYB | SINGLE | ATCHSNT3 345.00 - COOPER 345KV CKT 1 | 0 | 640139 | COOPER 3 345.00 | 635017 | ATCHSNT3 345.00 | 0 |  | 1 | Transfer Loading < 100% | 239
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T4465023SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 23SP | 250 | 250 | 250 | 95.4 | 95.4246 | 95.4 | [7 empty] | CATEGORYB | SINGLE | SUB 1206 - SUB 1216 161KV CKT 1 | 0 | 646206 | S1206 5 161.00 | 646216 | S1216 5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 239
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T4495023SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 23SP | 250 | 250 | 250 | 95.4 | 95.4071 | 95.4 | [7 empty] | CATEGORYB | SINGLE | SUB 1214 - SUB 914 69KV CKT 1 | 0 | 647014 | S914A 8 69.000 | 647914 | S914 8 69.000 | 0 |  | 1 | Transfer Loading < 100% | 239
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T15235023SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 23SP | 250 | 250 | 250 | 95.4 | 95.3515 | 95.4 | [7 empty] | CATEGORYB | SINGLE | SUB 1214 (S1214 T1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 646214 | S1214 5 161.00 | 647014 | S914A 8 69.000 | 648214 | S1214T19 13.800 | 1 | Transfer Loading < 100% | 239
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T4515023SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 23SP | 250 | 250 | 250 | 95.4 | 95.4091 | 95.4 | [7 empty] | CATEGORYB | SINGLE | SUB 904 - SUB 906 SOUTH 69KV CKT 1 | 0 | 647904 | S904 8 69.000 | 647906 | S906 S 8 69.000 | 0 |  | 1 | Transfer Loading < 100% | 239
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T4475023SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 23SP | 250 | 250 | 250 | 95.3 | 95.3071 | 95.3 | [7 empty] | CATEGORYB | SINGLE | SUB 1233 - SUB 1255 161KV CKT 1 | 0 | 646233 | S1233 5 161.00 | 646255 | S1255 5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 239
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2012AG1AFS41T4455023SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 23SP | 250 | 250 | 250 |  | 95.2456 | 95.3 | [7 empty] | CATEGORYB | SINGLE | SUB 3456 - SUB 3458 NEB CTY 345KV CKT 1 | 0 | 645456 | S3456 3 345.00 | 645458 | S3458 3 345.00 | 0 |  | 1 | Transfer Loading < 100% | 239
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T2325018SP | TO->FROM | ALLEN SUB - LUBBOCK SOUTH INTERCHANGE 115KV CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 0 | 526268 | LUBBCK_STH 3115.00 | 526213 | ALLEN 3115.00 | 0 |  | 1 | 18SP | 159 | 160 | 0 | 97.8 | 97.8276 | 97.1 | [7 empty] | CATEGORYB | SINGLE | LUBBOCK SOUTH INTERCHANGE - WOLFFORTH INTERCHANGE 230KV CKT 1 | 0 | 526269 | LUBBCK_STH 6230.00 | 526525 | WOLFFORTH 6230.00 | 0 |  | 1 | Transfer Loading < 100% | 156
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T13305513WP | FROM->TO | AMARILLO SOUTH INTERCHANGE - SWISHER COUNTY INTERCHANGE 230KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-CNPL | 0 | 524415 | AMA_SOUTH 6230.00 | 525213 | SWISHER 6230.00 | 0 |  | 1 | 13WP | 329 | 361 | 0 |  | 93.422 | 99.5 | [7 empty] | CATEGORYB | GENOUT | GEN527166 1-MUSTANG_6 18.000 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 360
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T13325513WP | FROM->TO | AMARILLO SOUTH INTERCHANGE - SWISHER COUNTY INTERCHANGE 230KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-CNPL | 0 | 524415 | AMA_SOUTH 6230.00 | 525213 | SWISHER 6230.00 | 0 |  | 1 | 13WP | 329 | 361 | 0 |  | 93.3258 | 99.4 | [7 empty] | CATEGORYB | GENOUT | GEN527882 1-CUNNINGHAM GEN #2 20 KV | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 359
2012-AG1 | AFS4 | ISLAND-LOAD |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T8065513WP | FROM->TO | AMARILLO SOUTH INTERCHANGE - SWISHER COUNTY INTERCHANGE 230KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-CNPL | 0 | 524415 | AMA_SOUTH 6230.00 | 525213 | SWISHER 6230.00 | 0 |  | 1 | 13WP | 329 | 361 | 0 |  | 90.0625 | 96.1 | [7 empty] | CATEGORYB | SINGLE | STATELINE INTERCHANGE (H TP80154301) 230/115/13.2KV TRANSFORMER CKT 1 | 1 | 523776 | WHEELER 3115.00 | 523777 | WHEELER 6230.00 | 523774 | WHEELER_TR1113.200 | 1 | Transfer Loading < 100% | 347
2012-AG1 | AFS4 | INVALID |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2325513WP | FROM->TO | AMARILLO SOUTH INTERCHANGE - SWISHER COUNTY INTERCHANGE 230KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-CNPL | 0 | 524415 | AMA_SOUTH 6230.00 | 525213 | SWISHER 6230.00 | 0 |  | 1 | 13WP | 329 | 361 | 0 |  | 89.7457 | 95.8731 | [7 empty] | CATEGORYB | SINGLE | DEAF SMITH COUNTY INTERCHANGE - DEAF SMITH REC-#21 115KV CKT 1 | 0 | 524622 | DEAFSMITH 3115.00 | 524734 | DS-#21 3115.00 | 0 |  | 1 | Transfer Loading < 100% | 347
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1835514WP | FROM->TO | AMARILLO SOUTH INTERCHANGE - SWISHER COUNTY INTERCHANGE 230KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-CNPL | 0 | 524415 | AMA_SOUTH 6230.00 | 525213 | SWISHER 6230.00 | 0 |  | 1 | 14WP | 329 | 361 | 0 |  | 88.0754 | 95.5 | [7 empty] | CATEGORYB | SINGLE | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | Transfer Loading < 100% | 345
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T2575013SP | TO->FROM | BAILEY COUNTY REC-EARTH INTERCHANGE - PLANT X STATION 115KV CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CLHF | 0 | 525480 | PLANT_X 3115.00 | 525056 | BC-EARTH 3115.00 | 0 |  | 1 | 13SP | 159 | 160 | 0 | 97.9 | 97.888 | 96.3 | [7 empty] | CATEGORYB | SINGLE | DEAF SMITH COUNTY INTERCHANGE - PLANT X STATION 230KV CKT 1 | 0 | 524623 | DEAFSMITH 6230.00 | 525481 | PLANT_X 6230.00 | 0 |  | 1 | Transfer Loading < 100% | 155
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T2335014SP | TO->FROM | BAILEY COUNTY REC-EARTH INTERCHANGE - PLANT X STATION 115KV CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CLHF | 0 | 525480 | PLANT_X 3115.00 | 525056 | BC-EARTH 3115.00 | 0 |  | 1 | 14SP | 159 | 160 | 0 | 100.9 | 100.9076 | 98.1 | [7 empty] | CATEGORYB | SINGLE | DEAF SMITH COUNTY INTERCHANGE - PLANT X STATION 230KV CKT 1 | 0 | 524623 | DEAFSMITH 6230.00 | 525481 | PLANT_X 6230.00 | 0 |  | 1 | Transfer Loading < 100% | 157
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T22195513SP | FROM->TO | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | 13SP | 319 | 351 | 0 |  | 94.104 | 96.1 | [7 empty] | CATEGORYB | GENOUT | GEN525561 1-TOLK GEN #1 24 KV | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 338
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T12505513WP | FROM->TO | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | 13WP | 329 | 360 | 0 |  | 94.3899 | 99.8 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-V05 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 360
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T13355513WP | FROM->TO | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | 13WP | 329 | 360 | 0 |  | 94.3899 | 99.3 | [7 empty] | CATEGORYB | GENOUT | GEN527902 1-HOBBS PLANT #2 (CT) | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 358
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T13335513WP | FROM->TO | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | 13WP | 329 | 360 | 0 |  | 94.3284 | 99.2 | [7 empty] | CATEGORYB | GENOUT | GEN527901 1-HOBBS PLANT #1 (CT) | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 358
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T65513WP | FROM->TO | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | 13WP | 329 | 360 | 0 |  | 93.406 | 98.6 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 355
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T20015514SP | FROM->TO | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | 14SP | 319 | 351 | 0 |  | 93.2706 | 96.5 | [7 empty] | CATEGORYB | GENOUT | GEN525561 1-TOLK GEN #1 24 KV | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 339
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1315514WP | FROM->TO | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | 14WP | 329 | 360 | 0 |  | 92.6147 | 98.7 | [7 empty] | CATEGORYB | SINGLE | BORDER 7345.00 - TUCO INTERCHANGE 345KV CKT 1 | 0 | 515458 | BORDER 7345.00 | 525832 | TUCO_INT 7345.00 | 0 |  | 1 | Transfer Loading < 100% | 356
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T12055514WP | FROM->TO | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | 14WP | 329 | 360 | 0 |  | 92.353 | 98.6 | [7 empty] | CATEGORYB | GENOUT | GEN527903 1-HOBBS PLANT #3 (ST) | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 355
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1565518WP | FROM->TO | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | 18WP | 329 | 360 | 0 |  | 89.9607 | 96 | [7 empty] | CATEGORYB | SINGLE | NEWHART 230 - POTTER COUNTY INTERCHANGE 230KV CKT 1 | 0 | 523959 | POTTER_CO 6230.00 | 525461 | NEWHART 6230.00 | 0 |  | 1 | Transfer Loading < 100% | 346
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T4605513SP | FROM->TO | CANYON EAST SUB - CANYON WEST SUB 115KV CKT 1 | E | SPS | SPS | SPS-CLHF | SPS-CLHF | 0 | 524523 | CANYON_EAST3115.00 | 524516 | CANYON_WEST3115.00 | 0 |  | 1 | 13SP | 96 | 96 | 0 | 95.2 | 95.2289 | 98.9 | [7 empty] | CATEGORYB | SINGLE | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | Transfer Loading < 100% | 95
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 0 | 2012AG1AFS41T3465023SP | TO->FROM | CANYON EAST SUB - RANDALL COUNTY INTERCHANGE 115KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-CLHF | 0 | 524364 | RANDALL 3115.00 | 524523 | CANYON_EAST3115.00 | 0 |  | 1 | 23SP | 96 | 96 | 0 |  | 90.6031 | 96.7 | [7 empty] | CATEGORYB | SINGLE | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | Transfer Loading < 100% | 93
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1855514WP | FROM->TO | CANYON WEST SUB - DAWN SUB 115KV CKT 1 | E | SPS | SPS | SPS-CLHF | SPS-CLHF | 0 | 524516 | CANYON_WEST3115.00 | 524590 | DAWN 3115.00 | 0 |  | 1 | 14WP | 106 | 106 | 0 |  | 91.7075 | 99.6 | [7 empty] | CATEGORYB | SINGLE | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | Transfer Loading < 100% | 106
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1865514WP | FROM->TO | DAWN SUB - Panda Energy Substation Hereford 115KV CKT 1 | E | SPS | SPS | SPS-CLHF | SPS-CLHF | 0 | 524590 | DAWN 3115.00 | 524597 | PANDAHFD 3115.00 | 0 |  | 1 | 14WP | 106 | 106 | 0 |  | 88.2956 | 96.1 | [7 empty] | CATEGORYB | SINGLE | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | Transfer Loading < 100% | 102
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T2315018SP | FROM->TO | Jones Station Bus#2 - LUBBOCK SOUTH INTERCHANGE 230KV CKT 2 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 0 | 526338 | JONES_BUS2 6230.00 | 526269 | LUBBCK_STH 6230.00 | 0 |  | 2 | 18SP | 478 | 478 | 0 | 95.9 | 95.9177 | 95.1 | [7 empty] | CATEGORYB | SINGLE | JONES STATION - LUBBOCK SOUTH INTERCHANGE 230KV CKT 1 | 0 | 526269 | LUBBCK_STH 6230.00 | 526337 | JONES_BUS1 6230.00 | 0 |  | 1 | Transfer Loading < 100% | 455
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T2455018SP | FROM->TO | MADDOX STATION - SANGER SWITCHING STATION 115KV CKT 1 | E | SPS | SPS | SPS-HOBB | SPS-HOBB | 0 | 528355 | MADDOX 3115.00 | 528463 | SANGER_SW 3115.00 | 0 |  | 1 | 18SP | 141 | 141 | 0 | 99.7 | 99.7327 | 99.8 | [7 empty] | CATEGORYB | SINGLE | HOBBS INTERCHANGE - MILLEN SUB 115KV CKT 1 | 0 | 527891 | HOBBS_INT 3115.00 | 528435 | MILLEN 3115.00 | 0 |  | 1 | Transfer Loading < 100% | 141
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T3775023SP | FROM->TO | MADDOX STATION - SANGER SWITCHING STATION 115KV CKT 1 | E | SPS | SPS | SPS-HOBB | SPS-HOBB | 0 | 528355 | MADDOX 3115.00 | 528463 | SANGER_SW 3115.00 | 0 |  | 1 | 23SP | 146 | 161 | 0 | 97.7 | 97.7198 | 97.8 | [7 empty] | CATEGORYB | SINGLE | MADDOX STATION - MONUMENT SUB 115KV CKT 1 | 0 | 528355 | MADDOX 3115.00 | 528491 | MONUMENT 3115.00 | 0 |  | 1 | Transfer Loading < 100% | 158
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T19735023SP | FROM->TO | MADDOX STATION - SANGER SWITCHING STATION 115KV CKT 1 | E | SPS | SPS | SPS-HOBB | SPS-HOBB | 0 | 528355 | MADDOX 3115.00 | 528463 | SANGER_SW 3115.00 | 0 |  | 1 | 23SP | 146 | 161 | 0 | 96.3 | 96.2914 | 96.3 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-T42 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 156
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T3805023SP | FROM->TO | MADDOX STATION - SANGER SWITCHING STATION 115KV CKT 1 | E | SPS | SPS | SPS-HOBB | SPS-HOBB | 0 | 528355 | MADDOX 3115.00 | 528463 | SANGER_SW 3115.00 | 0 |  | 1 | 23SP | 146 | 161 | 0 | 95.8 | 95.7855 | 95.8 | [7 empty] | CATEGORYB | SINGLE | MONUMENT SUB - WEST HOBBS SWITCHING STATION 115KV CKT 1 | 0 | 528491 | MONUMENT 3115.00 | 528498 | W_HOBBS 3115.00 | 0 |  | 1 | Transfer Loading < 100% | 155
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T145513SP | FROM->TO | MAJESTIC WIND - MARTIN SUB 115KV CKT 1 | E | SPS | SPS | SPS-OKLA | SPS-OKLA | 0 | 523926 | MAJESTC_WND3115.00 | 523928 | MARTIN 3115.00 | 0 |  | 1 | 13SP | 160.5 | 160.5 | 0 |  | 49.4317 | 98.5 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 159
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T55513WP | FROM->TO | MAJESTIC WIND - MARTIN SUB 115KV CKT 1 | E | SPS | SPS | SPS-OKLA | SPS-OKLA | 0 | 523926 | MAJESTC_WND3115.00 | 523928 | MARTIN 3115.00 | 0 |  | 1 | 13WP | 160.5 | 160.5 | 0 |  | 49.1923 | 98.2 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 158
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T155514SP | FROM->TO | MAJESTIC WIND - MARTIN SUB 115KV CKT 1 | E | SPS | SPS | SPS-OKLA | SPS-OKLA | 0 | 523926 | MAJESTC_WND3115.00 | 523928 | MARTIN 3115.00 | 0 |  | 1 | 14SP | 160.5 | 160.5 | 0 |  | 48.8637 | 97.3 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 157
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T65514WP | FROM->TO | MAJESTIC WIND - MARTIN SUB 115KV CKT 1 | E | SPS | SPS | SPS-OKLA | SPS-OKLA | 0 | 523926 | MAJESTC_WND3115.00 | 523928 | MARTIN 3115.00 | 0 |  | 1 | 14WP | 160.5 | 160.5 | 0 |  | 49.0449 | 97.7 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 157
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T145518SP | FROM->TO | MAJESTIC WIND - MARTIN SUB 115KV CKT 1 | E | SPS | SPS | SPS-OKLA | SPS-OKLA | 0 | 523926 | MAJESTC_WND3115.00 | 523928 | MARTIN 3115.00 | 0 |  | 1 | 18SP | 160.5 | 160.5 | 0 |  | 49.415 | 98.4 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 158
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T65518WP | FROM->TO | MAJESTIC WIND - MARTIN SUB 115KV CKT 1 | E | SPS | SPS | SPS-OKLA | SPS-OKLA | 0 | 523926 | MAJESTC_WND3115.00 | 523928 | MARTIN 3115.00 | 0 |  | 1 | 18WP | 160.5 | 160.5 | 0 |  | 49.3004 | 98.3 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 158
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T155523SP | FROM->TO | MAJESTIC WIND - MARTIN SUB 115KV CKT 1 | E | SPS | SPS | SPS-OKLA | SPS-OKLA | 0 | 523926 | MAJESTC_WND3115.00 | 523928 | MARTIN 3115.00 | 0 |  | 1 | 23SP | 160.5 | 160.5 | 0 |  | 48.847 | 97.3 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 157
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T95523WP | FROM->TO | MAJESTIC WIND - MARTIN SUB 115KV CKT 1 | E | SPS | SPS | SPS-OKLA | SPS-OKLA | 0 | 523926 | MAJESTC_WND3115.00 | 523928 | MARTIN 3115.00 | 0 |  | 1 | 23WP | 160.5 | 160.5 | 0 |  | 48.6963 | 97 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 156
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3865514SP | FROM->TO | MANHATTAN TAP - OSAGE SWITCHING STATION 115KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524354 | MANHATN_TP 3115.00 | 524345 | OSAGE 3115.00 | 0 |  | 1 | 14SP | 160 | 160 | 0 |  | 91.1938 | 95 | [7 empty] | CATEGORYB | SINGLE | EAST PLANT INTERCHANGE - PIERCE STREET TAP 115KV CKT 1 | 0 | 524162 | EAST_PLANT 3115.00 | 524185 | PIERCE_TP 3115.00 | 0 |  | 1 | Transfer Loading < 100% | 152
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2045513WP | FROM->TO | SWISHER COUNTY INTERCHANGE - TUCO INTERCHANGE 230KV CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 0 | 525213 | SWISHER 6230.00 | 525830 | TUCO_INT 6230.00 | 0 |  | 1 | 13WP | 329 | 361 | 0 |  | 90.0397 | 97.5 | [7 empty] | CATEGORYB | SINGLE | PLANT X STATION - POTTER COUNTY INTERCHANGE 230KV CKT 1 | 0 | 523959 | POTTER_CO 6230.00 | 525481 | PLANT_X 6230.00 | 0 |  | 1 | Transfer Loading < 100% | 352
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2435513WP | FROM->TO | SWISHER COUNTY INTERCHANGE - TUCO INTERCHANGE 230KV CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 0 | 525213 | SWISHER 6230.00 | 525830 | TUCO_INT 6230.00 | 0 |  | 1 | 13WP | 329 | 361 | 0 |  | 89.2249 | 96.7 | [7 empty] | CATEGORYB | SINGLE | HALE CO INTERCHANGE - KRESS INTERCHANGE 115KV CKT 1 | 0 | 525192 | KRESS_INT 3115.00 | 525454 | HALE_CNTY 3115.00 | 0 |  | 1 | Transfer Loading < 100% | 350
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T2685013SP | FROM->TO | WOLFFORTH INTERCHANGE - YUMA INTERCHANGE 115KV CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 0 | 526524 | WOLFFORTH 3115.00 | 526475 | YUMA_INT 3115.00 | 0 |  | 1 | 13SP | 120 | 154 | 0 | 97.1 | 97.1112 | 98 | [7 empty] | CATEGORYB | SINGLE | ALLEN SUB - LUBBOCK SOUTH INTERCHANGE 115KV CKT 1 | 0 | 526213 | ALLEN 3115.00 | 526268 | LUBBCK_STH 3115.00 | 0 |  | 1 | Transfer Loading < 100% | 151
2012-AG1 | AFS4LAMAR |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS4LAMAR1T1715518WP | TO->FROM | CIMARRON RIVER TAP - KISMET 3 115.00 115KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539646 | KISMET 3 115.00 | 539652 | CMRIVTP3 115.00 | 0 |  | 1 | 18WP | 120.7 | 129.5 | 0.0 |  | 67.3447 | 99.6 | [7 empty] | CATEGORYB | SINGLE | BUCKNER7 345.00 - HOLCOMB 345KV CKT 1 | 0 | 531449 | HOLCOMB7 345.00 | 531501 | BUCKNER7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 129
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T6485513SP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | E | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13SP | 110 | 110 | 0 | 98.8 | 98.7571 | 99.4 | [7 empty] | CATEGORYB | SINGLE | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 | Transfer Loading < 100% | 110
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T13925513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | E | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 100.4 | 99.6535 | 99.9 | [7 empty] | CATEGORYB | GENOUT | GEN640011 2-GERALD GENTLEMAN STATION UNIT 2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 110
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T4125513WP | TO->FROM | CLEARWATER - MILAN TAP 138KV CKT 1 | E | SUNC | WERE | GREAT PL | SCENTRAL | 0 | 539675 | MILANTP4 138.00 | 533036 | CLEARWT4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 99 | 98.9558 | 98.7 | [7 empty] | CATEGORYB | SINGLE | JUDSON LARGE - NORTH JUDSON LARGE SUB 115KV CKT 1 | 0 | 539671 | FTDODGE3 115.00 | 539771 | NFTDODG3 115.00 | 0 |  | 1 | Transfer Loading < 100% | 109
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5155513SP | TO->FROM | CUDAHY - CROOKED CREEK 115.00 115KV CKT 1 | E | SUNC | SUNC | BEPC_1630 | GREAT PL | 0 | 560229 | CROOKED CREEK 115.00 | 539659 | CUDAHY 3 115.00 | 0 |  | 1 | 13SP | 120.7 | 129.5 | 0 | 100.1 | 100.1195 | 98.9 | [7 empty] | CATEGORYB | SINGLE | BUCKNER7 345.00 - HOLCOMB 345KV CKT 1 | 0 | 531449 | HOLCOMB7 345.00 | 531501 | BUCKNER7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 129
2012-AG1 | AFS4LAMAR |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS4LAMAR1T4105514SP | TO->FROM | CUDAHY - CROOKED CREEK 115.00 115KV CKT 1 | E | SUNC | SUNC | BEPC_1630 | GREAT PL | 0 | 560229 | CROOKED CREEK 115.00 | 539659 | CUDAHY 3 115.00 | 0 |  | 1 | 14SP | 120.7 | 129.5 | 0.0 |  | 82.5543 | 95.6 | [7 empty] | CATEGORYB | SINGLE | BUCKNER7 345.00 - HOLCOMB 345KV CKT 1 | 0 | 531449 | HOLCOMB7 345.00 | 531501 | BUCKNER7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 124
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T4615518SP | TO->FROM | CUDAHY - CROOKED CREEK 115.00 115KV CKT 1 | E | SUNC | SUNC | BEPC_1630 | GREAT PL | 0 | 560229 | CROOKED CREEK 115.00 | 539659 | CUDAHY 3 115.00 | 0 |  | 1 | 18SP | 120.7 | 129.5 | 0 |  | 89.5503 | 98 | [7 empty] | CATEGORYB | SINGLE | BUCKNER7 345.00 - HOLCOMB 345KV CKT 1 | 0 | 531449 | HOLCOMB7 345.00 | 531501 | BUCKNER7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 127
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5145523SP | TO->FROM | CUDAHY - CROOKED CREEK 115.00 115KV CKT 1 | E | SUNC | SUNC | BEPC_1630 | GREAT PL | 0 | 560229 | CROOKED CREEK 115.00 | 539659 | CUDAHY 3 115.00 | 0 |  | 1 | 23SP | 120.7 | 129.5 | 0 |  | 92.6256 | 99.8 | [7 empty] | CATEGORYB | SINGLE | BUCKNER7 345.00 - HOLCOMB 345KV CKT 1 | 0 | 531449 | HOLCOMB7 345.00 | 531501 | BUCKNER7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 130
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T22405513SP | FROM->TO | FLATRDG3 - HARPER 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 98.1 | 98.0552 | 98.8 | [7 empty] | CATEGORYB | GENOUT | GEN539767 1-GRAY COUNTY WIND FARM | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 95
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T22605513SP | FROM->TO | FLATRDG3 - HARPER 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 97.6 | 97.5729 | 98.4 | [7 empty] | CATEGORYB | GENOUT | GEN640011 2-GERALD GENTLEMAN STATION UNIT 2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 95
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T22595513SP | FROM->TO | FLATRDG3 - HARPER 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 97.6 | 97.5462 | 98.3 | [7 empty] | CATEGORYB | GENOUT | GEN640010 1-GERALD GENTLEMAN STATION UNIT 1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 94
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T22355513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 97.7 | 97.8146 | 98.5 | [7 empty] | CATEGORYB | GENOUT | GEN532751 1-WOLF CREEK GENERATING STATION UNIT 1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 95
2012-AG1 | AFS4 | INVALID | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5125513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 102 | 102.0003 | 98.2328 | [7 empty] | CATEGORYB | SINGLE | ST JOHN - ST_JOHN 115KV CKT 1 | 0 | 530624 | ST JOHN3 115.00 | 539696 | ST-JOHN3 115.00 | 0 |  | 1 | Transfer Loading < 100% | 94
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T6835513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 101.4 | 101.3768 | 97.6 | [7 empty] | CATEGORYB | SINGLE | NORTH JUDSON LARGE SUB - SPEARVILLE 115KV CKT 1 | 0 | 539694 | SPEARVL3 115.00 | 539771 | NFTDODG3 115.00 | 0 |  | 1 | Transfer Loading < 100% | 94
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5615513SP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13SP | 95.6 | 95.6 | 0 | 96.8 | 96.7743 | 97.3 | [7 empty] | CATEGORYB | SINGLE | RENO COUNTY - WICHITA 345KV CKT 1 | 0 | 532771 | RENO 7 345.00 | 532796 | WICHITA7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 94
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T13535513WP | FROM->TO | HARPER - MILAN TAP 138KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539668 | HARPER 4 138.00 | 539675 | MILANTP4 138.00 | 0 |  | 1 | 13WP | 110 | 110 | 0 | 97.1 | 96.9855 | 96.6 | [7 empty] | CATEGORYB | GENOUT | GEN539762 1-SSWIND 1 34.500 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 107
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T4445518SP | TO->FROM | MULLERGREN - SPEARVILLE 230KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539695 | SPEARVL6 230.00 | 539679 | GRTBEND6 230.00 | 0 |  | 1 | 18SP | 330.3 | 355.3 | 0 |  | 79.2132 | 98 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 349
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T4925523SP | TO->FROM | MULLERGREN - SPEARVILLE 230KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539695 | SPEARVL6 230.00 | 539679 | GRTBEND6 230.00 | 0 |  | 1 | 23SP | 330.3 | 355.3 | 0 |  | 80.0993 | 97.9 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 348
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T18945514SP | FROM->TO | BEAVER - EUREKA SPRINGS 161KV CKT 1 | E | SWPA | AEPW | EMINTH | FAYETTEVILLE | 0 | 505480 | BEAVER 5 161.00 | 506932 | EUREKA 5 161.00 | 0 |  | 1 | 14SP | 236 | 247 | 0 | 95.4 | 95.3668 | 98.7 | [7 empty] | CATEGORYB | NONSINGLE | SPP-AEPW-01 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 244
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3235513SP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 13SP | 68 | 68 | 0 | 95.6 | 95.6046 | 96 | [7 empty] | CATEGORYB | SINGLE | FT SMITH - MUSKOGEE 345KV CKT 1 | 0 | 515224 | MUSKOGE7 345.00 | 515302 | FTSMITH7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 66
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T10155514SP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 14SP | 68 | 68 | 0 | 97.9 | 97.93 | 99.8 | [7 empty] | CATEGORYB | SINGLE | CASH - NEWPORT AB 161KV CKT 1 | 0 | 338171 | 5CASH 161.00 | 338172 | 5NEWPORT AB 161.00 | 0 |  | 1 | Transfer Loading < 100% | 68
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T10145514SP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 14SP | 68 | 68 | 0 | 97 | 97.0026 | 99 | [7 empty] | CATEGORYB | SINGLE | CASH - JONESBORO 161KV CKT 1 | 0 | 338170 | 5JONESBORO! 161.00 | 338171 | 5CASH 161.00 | 0 |  | 1 | Transfer Loading < 100% | 68
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T10105514SP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 14SP | 68 | 68 | 0 | 96.7 | 96.7321 | 98.7 | [7 empty] | CATEGORYB | SINGLE | HARISBURG TAP - MARKED TREE 161KV CKT 1 | 0 | 338165 | 5MARKEDTREE!161.00 | 338167 | 5HARRISBURG+161.00 | 0 |  | 1 | Transfer Loading < 100% | 68
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T10085514SP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 14SP | 68 | 68 | 0 | 95 | 95.0065 | 96.4 | [7 empty] | CATEGORYB | SINGLE | WEST MEMPHIS 500 500/161KV TRANSFORMER CKT 1 | 0 | 338161 | 5W.MEMPHIS! 161.00 | 338162 | 8W.MEMPHIS% 500.00 | 0 |  | 1 | Transfer Loading < 100% | 66
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T10025514SP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 14SP | 68 | 68 | 0 |  | 94.2636 | 96.2 | [7 empty] | CATEGORYB | SINGLE | INDEPENDENCE - MOOREFIELD 161KV CKT 1 | 0 | 338138 | 5MOOREFIELD 161.00 | 338142 | 5ISES-1! 161.00 | 0 |  | 1 | Transfer Loading < 100% | 66
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T10125514SP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 14SP | 68 | 68 | 0 |  | 93.538 | 95.5 | [7 empty] | CATEGORYB | SINGLE | HARISBURG TAP - TRUMANN 161KV CKT 1 | 0 | 338167 | 5HARRISBURG+161.00 | 338169 | 5TRUMANN 161.00 | 0 |  | 1 | Transfer Loading < 100% | 65
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T10205514SP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 14SP | 68 | 68 | 0 |  | 93.1852 | 95.2 | [7 empty] | CATEGORYB | SINGLE | PARAGOULD 161 - PARAGOULD SOUTH (AECC) 161KV CKT 1 | 0 | 338204 | 5PARAGOULD% 161.00 | 338706 | 5PARGOULD.S#161.00 | 0 |  | 1 | Transfer Loading < 100% | 65
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T11405518SP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 18SP | 68 | 68 | 0 |  | 90.8266 | 97.4 | [7 empty] | CATEGORYB | SINGLE | NEWPORT - NEWPORT INDUSTRIAL 161KV CKT 1 | 0 | 338151 | 5NEWPORT! 161.00 | 338173 | 5NEWPORT IND161.00 | 0 |  | 1 | Transfer Loading < 100% | 67
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T11505518SP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 18SP | 68 | 68 | 0 |  | 89.686 | 97.4 | [7 empty] | CATEGORYB | SINGLE | NEWPORT AB - NEWPORT INDUSTRIAL 161KV CKT 1 | 0 | 338172 | 5NEWPORT AB 161.00 | 338173 | 5NEWPORT IND161.00 | 0 |  | 1 | Transfer Loading < 100% | 67
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T11485518SP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 18SP | 68 | 68 | 0 |  | 88.5079 | 95.9 | [7 empty] | CATEGORYB | SINGLE | CASH - NEWPORT AB 161KV CKT 1 | 0 | 338171 | 5CASH 161.00 | 338172 | 5NEWPORT AB 161.00 | 0 |  | 1 | Transfer Loading < 100% | 66
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T12895518SP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 18SP | 68 | 68 | 0 |  | 89.1441 | 95.8 | [7 empty] | CATEGORYB | SINGLE | JONESBORO - JONESBORO 161KV CKT 1 | 0 | 505418 | JONESBO5 161.00 | 338170 | 5JONESBORO! 161.00 | 0 |  | 1 | Transfer Loading < 100% | 66
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T13055523SP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 23SP | 68 | 68 | 0 |  | 94.3788 | 98.8 | [7 empty] | CATEGORYB | SINGLE | CASH - NEWPORT AB 161KV CKT 1 | 0 | 338171 | 5CASH 161.00 | 338172 | 5NEWPORT AB 161.00 | 0 |  | 1 | Transfer Loading < 100% | 68
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T14595523SP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 23SP | 68 | 68 | 0 |  | 94.3746 | 98.7 | [7 empty] | CATEGORYB | SINGLE | JONESBORO - JONESBORO 161KV CKT 1 | 0 | 505418 | JONESBO5 161.00 | 338170 | 5JONESBORO! 161.00 | 0 |  | 1 | Transfer Loading < 100% | 68
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T12975523SP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 23SP | 68 | 68 | 0 |  | 93.5289 | 98 | [7 empty] | CATEGORYB | SINGLE | HARISBURG TAP - MARKED TREE 161KV CKT 1 | 0 | 338165 | 5MARKEDTREE!161.00 | 338167 | 5HARRISBURG+161.00 | 0 |  | 1 | Transfer Loading < 100% | 67
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T13025523SP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 23SP | 68 | 68 | 0 |  | 93.226 | 97.9 | [7 empty] | CATEGORYB | SINGLE | CASH - JONESBORO 161KV CKT 1 | 0 | 338170 | 5JONESBORO! 161.00 | 338171 | 5CASH 161.00 | 0 |  | 1 | Transfer Loading < 100% | 67
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T12995523SP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 23SP | 68 | 68 | 0 |  | 92.2851 | 96.9 | [7 empty] | CATEGORYB | SINGLE | HARISBURG TAP - TRUMANN 161KV CKT 1 | 0 | 338167 | 5HARRISBURG+161.00 | 338169 | 5TRUMANN 161.00 | 0 |  | 1 | Transfer Loading < 100% | 66
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T13015523SP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 23SP | 68 | 68 | 0 |  | 91.9129 | 96.3 | [7 empty] | CATEGORYB | SINGLE | TRUMANN - TRUMANN WEST AECC 161KV CKT 1 | 0 | 338169 | 5TRUMANN 161.00 | 338707 | 5TRUMANN.W# 161.00 | 0 |  | 1 | Transfer Loading < 100% | 66
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T12815523SP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 23SP | 68 | 68 | 0 |  | 91.7988 | 95.9 | [7 empty] | CATEGORYB | SINGLE | INDEPENDENCE - MOOREFIELD 161KV CKT 1 | 0 | 338138 | 5MOOREFIELD 161.00 | 338142 | 5ISES-1! 161.00 | 0 |  | 1 | Transfer Loading < 100% | 66
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T14955523SP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 23SP | 68 | 68 | 0 |  | 89.368 | 95.4 | [7 empty] | CATEGORYB | SINGLE | BULL SHOALS - MIDWAY (YVEPA) 161KV CKT 1 | 0 | 505460 | BULL SH5 161.00 | 338813 | 5MIDWY JRDN#161.00 | 0 |  | 1 | Transfer Loading < 100% | 65
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1945523WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 23WP | 68 | 68 | 0 |  | 90.205 | 96.3 | [7 empty] | CATEGORYB | SINGLE | FT SMITH - MUSKOGEE 345KV CKT 1 | 0 | 515224 | MUSKOGE7 345.00 | 515302 | FTSMITH7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 66
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T455518WP | FROM->TO | BULL SHOALS - MIDWAY (YVEPA) 161KV CKT 1 | E | SWPA | EES-EAI | EMINTH |  | 0 | 505460 | BULL SH5 161.00 | 338813 | 5MIDWY JRDN#161.00 | 0 |  | 1 | 18WP | 162 | 162 | 0 |  | 90.1032 | 99.7 | [7 empty] | CATEGORYB | SINGLE | BUFORD 5 161.00 - NORFORK 161KV CKT 1 | 0 | 504440 | BUFORD 5 161.00 | 505448 | NORFORK5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 162
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T935514SP | TO->FROM | FITZHUGH - OZARK 161KV CKT 1 | E | SWPA | AEPW | EMINTH | GREENWD AECC | 0 | 505516 | OZARK H5 161.00 | 503902 | FITZHUGH 5 161.00 | 0 |  | 1 | 14SP | 88.84 | 103.07 | 0 |  | 81.5172 | 99.1 | [7 empty] | CATEGORYB | SINGLE | VAN BUREN - VBI 161KV CKT 1 | 0 | 505522 | VAN BUR5 161.00 | 515339 | VBI 5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 103
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T495518WP | TO->FROM | FITZHUGH - OZARK 161KV CKT 1 | E | SWPA | AEPW | EMINTH | GREENWD AECC | 0 | 505516 | OZARK H5 161.00 | 503902 | FITZHUGH 5 161.00 | 0 |  | 1 | 18WP | 88.84 | 103.07 | 0 |  | 82.4759 | 95.3 | [7 empty] | CATEGORYB | SINGLE | CLARKSVILLE - OZARK 161KV CKT 1 | 0 | 505514 | CLARKSV5 161.00 | 505516 | OZARK H5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 99
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3215513SP | TO->FROM | GORE - MUSKOGEE TAP 161KV CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505558 | MUSKTAP5 161.00 | 505552 | GORE 5 161.00 | 0 |  | 1 | 13SP | 171 | 206 | 0 |  | 93.2361 | 95.5 | [7 empty] | CATEGORYB | SINGLE | FT SMITH - MUSKOGEE 345KV CKT 1 | 0 | 515224 | MUSKOGE7 345.00 | 515302 | FTSMITH7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 197
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2635518SP | TO->FROM | GORE - MUSKOGEE TAP 161KV CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505558 | MUSKTAP5 161.00 | 505552 | GORE 5 161.00 | 0 |  | 1 | 18SP | 171 | 206 | 0 |  | 74.3501 | 99.2 | [7 empty] | CATEGORYB | SINGLE | FT SMITH - MUSKOGEE 345KV CKT 1 | 0 | 515224 | MUSKOGE7 345.00 | 515302 | FTSMITH7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 205
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3405523SP | FROM->TO | GORE - SALLISAW 161KV CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505552 | GORE 5 161.00 | 505550 | SALISAW5 161.00 | 0 |  | 1 | 23SP | 189 | 189 | 0 |  | 87.3808 | 97.8 | [7 empty] | CATEGORYB | SINGLE | FT SMITH - MUSKOGEE 345KV CKT 1 | 0 | 515224 | MUSKOGE7 345.00 | 515302 | FTSMITH7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 185
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T6955513SP | TO->FROM | NORTH WARSAW - TRUMAN 161KV CKT 1 | E | SWPA | GMO | EMINTH |  | 0 | 505502 | TRUMAN 5 161.00 | 541314 | NWARSAW5 161.00 | 0 |  | 1 | 13SP | 223 | 223 | 223 | 96.7 | 96.6959 | 97.6 | [7 empty] | CATEGORYB | SINGLE | CLINTON - WINDSOR 161KV CKT 1 | 0 | 541217 | WINDSR 5 161.00 | 541242 | CLINTON5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 218
2012-AG1 | AFS4 |  | FDNS |  | FNSL | FDNS-Iteration limit exceeded | 5 | 5 | 2012AG1AFS42T125513SP | TO->FROM | NORTH WARSAW - TRUMAN 161KV CKT 1 | E | SWPA | GMO | EMINTH |  | 0 | 505502 | TRUMAN 5 161.00 | 541314 | NWARSAW5 161.00 | 0 |  | 1 | 13SP | 223 | 223 | 223 | 96 | 96.036 | 97.2 | [7 empty] | CATEGORYB | NONSINGLE | OVERTON-TRF | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 217
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T15785513SP | TO->FROM | NORTH WARSAW - TRUMAN 161KV CKT 1 | E | SWPA | GMO | EMINTH |  | 0 | 505502 | TRUMAN 5 161.00 | 541314 | NWARSAW5 161.00 | 0 |  | 1 | 13SP | 223 | 223 | 223 | 96.2 | 96.1648 | 97.1 | [7 empty] | CATEGORYB | SINGLE | 5SEDALATAP 161.00 - WINDSOR 161KV CKT 1 | 0 | 541217 | WINDSR 5 161.00 | 300457 | 5SEDALATAP 161.00 | 0 |  | 1 | Transfer Loading < 100% | 217
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5665514SP | TO->FROM | NORTH WARSAW - TRUMAN 161KV CKT 1 | E | SWPA | GMO | EMINTH |  | 0 | 505502 | TRUMAN 5 161.00 | 541314 | NWARSAW5 161.00 | 0 |  | 1 | 14SP | 223 | 223 | 223 | 96.5 | 96.4812 | 97.7 | [7 empty] | CATEGORYB | SINGLE | CLINTON - WINDSOR 161KV CKT 1 | 0 | 541217 | WINDSR 5 161.00 | 541242 | CLINTON5 161.00 | 0 |  | 1 | Transfer Loading < 100% | 218
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T14045514SP | TO->FROM | NORTH WARSAW - TRUMAN 161KV CKT 1 | E | SWPA | GMO | EMINTH |  | 0 | 505502 | TRUMAN 5 161.00 | 541314 | NWARSAW5 161.00 | 0 |  | 1 | 14SP | 223 | 223 | 223 | 95.9 | 95.9285 | 97.2 | [7 empty] | CATEGORYB | SINGLE | 5SEDALATAP 161.00 - WINDSOR 161KV CKT 1 | 0 | 541217 | WINDSR 5 161.00 | 300457 | 5SEDALATAP 161.00 | 0 |  | 1 | Transfer Loading < 100% | 217
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T19465514SP | TO->FROM | NORTH WARSAW - TRUMAN 161KV CKT 1 | E | SWPA | GMO | EMINTH |  | 0 | 505502 | TRUMAN 5 161.00 | 541314 | NWARSAW5 161.00 | 0 |  | 1 | 14SP | 223 | 223 | 223 | 95.7 | 95.7029 | 97 | [7 empty] | CATEGORYB | NONSINGLE | AI03 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 217
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T13445523SP | TO->FROM | NORTH WARSAW - TRUMAN 161KV CKT 1 | E | SWPA | GMO | EMINTH |  | 0 | 505502 | TRUMAN 5 161.00 | 541314 | NWARSAW5 161.00 | 0 |  | 1 | 23SP | 223 | 223 | 223 |  | 95.9627 | 99.8 | [7 empty] | CATEGORYB | SINGLE | 5ELDON 161/138KV TRANSFORMER CKT 1 | 0 | 344532 | 5ELDON 161.00 | 345400 | 4OSAGE 138.00 | 0 |  | 1 | Transfer Loading < 100% | 223
2012-AG1 | AFS4 | CONT-0803 - Hoyt - Stranger 345kV |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5315523SP | TO->FROM | NORTH WARSAW - TRUMAN 161KV CKT 1 | E | SWPA | GMO | EMINTH |  | 0 | 505502 | TRUMAN 5 161.00 | 541314 | NWARSAW5 161.00 | 0 |  | 1 | 23SP | 223 | 223 | 223 |  | 94.9162 | 99 | [7 empty] | CATEGORYB | SINGLE | HOYT - STRANGER CREEK 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532772 | STRANGR7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 221
2012-AG1 | AFS4 | CONT-0400 - JEC - Hoyt 345kV |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5255523SP | TO->FROM | NORTH WARSAW - TRUMAN 161KV CKT 1 | E | SWPA | GMO | EMINTH |  | 0 | 505502 | TRUMAN 5 161.00 | 541314 | NWARSAW5 161.00 | 0 |  | 1 | 23SP | 223 | 223 | 223 |  | 94.5823 | 98.7 | [7 empty] | CATEGORYB | SINGLE | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 221
2012-AG1 | AFS4 | CONT-0302 - Lacygne - Wolf Creek 345kV |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5485523SP | TO->FROM | NORTH WARSAW - TRUMAN 161KV CKT 1 | E | SWPA | GMO | EMINTH |  | 0 | 505502 | TRUMAN 5 161.00 | 541314 | NWARSAW5 161.00 | 0 |  | 1 | 23SP | 223 | 223 | 223 |  | 93.2743 | 97.3 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - WOLF CREEK 345KV CKT 1 | 0 | 532797 | WOLFCRK7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 217
2012-AG1 | AFS4 | CONT-LaCygne West Gardner 345kv |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T6535523SP | TO->FROM | NORTH WARSAW - TRUMAN 161KV CKT 1 | E | SWPA | GMO | EMINTH |  | 0 | 505502 | TRUMAN 5 161.00 | 541314 | NWARSAW5 161.00 | 0 |  | 1 | 23SP | 223 | 223 | 223 |  | 92.4939 | 96.6 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 216
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3485523WP | TO->FROM | NORTH WARSAW - TRUMAN 161KV CKT 1 | E | SWPA | GMO | EMINTH |  | 0 | 505502 | TRUMAN 5 161.00 | 541314 | NWARSAW5 161.00 | 0 |  | 1 | 23WP | 234 | 234 | 234 |  | 94.2671 | 99.5 | [7 empty] | CATEGORYB | SINGLE | 7JASPER 345.00 - BLACKBERRY 345KV CKT 1 | 0 | 300739 | 7BLACKBERRY 345.00 | 300949 | 7JASPER 345.00 | 0 |  | 1 | Transfer Loading < 100% | 233
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T15265523WP | TO->FROM | NORTH WARSAW - TRUMAN 161KV CKT 1 | E | SWPA | GMO | EMINTH |  | 0 | 505502 | TRUMAN 5 161.00 | 541314 | NWARSAW5 161.00 | 0 |  | 1 | 23WP | 234 | 234 | 234 |  | 94.2048 | 99.4 | [7 empty] | CATEGORYB | GENOUT | GEN335831 1-RIVERBEND UNIT#1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 233
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T14825523WP | TO->FROM | NORTH WARSAW - TRUMAN 161KV CKT 1 | E | SWPA | GMO | EMINTH |  | 0 | 505502 | TRUMAN 5 161.00 | 541314 | NWARSAW5 161.00 | 0 |  | 1 | 23WP | 234 | 234 | 234 |  | 93.3714 | 98.5 | [7 empty] | CATEGORYB | GENOUT | GEN300007 1-NEW MADRID UNIT 2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 231
2012-AG1 | AFS4 | CONT-LaCygne Neosho 345kv |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2825523WP | TO->FROM | NORTH WARSAW - TRUMAN 161KV CKT 1 | E | SWPA | GMO | EMINTH |  | 0 | 505502 | TRUMAN 5 161.00 | 541314 | NWARSAW5 161.00 | 0 |  | 1 | 23WP | 234 | 234 | 234 |  | 93.1263 | 98.2 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - NEOSHO 345KV CKT 1 | 0 | 532793 | NEOSHO 7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 230
2012-AG1 | AFS4 | ISLAND-LOAD |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T7605523WP | TO->FROM | NORTH WARSAW - TRUMAN 161KV CKT 1 | E | SWPA | GMO | EMINTH |  | 0 | 505502 | TRUMAN 5 161.00 | 541314 | NWARSAW5 161.00 | 0 |  | 1 | 23WP | 234 | 234 | 234 |  | 92.6855 | 97.6 | [7 empty] | CATEGORYB | SINGLE | 5TRAIL TR 161.00 - 5WEDK 1 161.00 161KV CKT 1 | 0 | 345823 | 5TRAIL TR 161.00 | 345975 | 5WEDK 1 161.00 | 0 |  | 1 | Transfer Loading < 100% | 229
2012-AG1 | AFS4 | CONT-Thomas Hill Operating Guide |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T8085523WP | TO->FROM | NORTH WARSAW - TRUMAN 161KV CKT 1 | E | SWPA | GMO | EMINTH |  | 0 | 505502 | TRUMAN 5 161.00 | 541314 | NWARSAW5 161.00 | 0 |  | 1 | 23WP | 234 | 234 | 234 |  | 91.8473 | 96.9 | [7 empty] | CATEGORYB | SINGLE | MCCREDIE - THOMAS HILL 345KV CKT 1 | 0 | 300044 | 7MCCRED 345.00 | 300049 | 7THOMHL 345.00 | 0 |  | 1 | Transfer Loading < 100% | 227
2012-AG1 | AFS4 | INVALID |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1515523WP | TO->FROM | NORTH WARSAW - TRUMAN 161KV CKT 1 | E | SWPA | GMO | EMINTH |  | 0 | 505502 | TRUMAN 5 161.00 | 541314 | NWARSAW5 161.00 | 0 |  | 1 | 23WP | 234 | 234 | 234 |  | 91.7161 | 96.7628 | [7 empty] | CATEGORYB | SINGLE | GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 | 0 | 512650 | GRDA1 7 345.00 | 512750 | TONECE7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 227
2012-AG1 | AFS4 | CONT-Maries 161/138kV Transformer Overload |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T13265523WP | TO->FROM | NORTH WARSAW - TRUMAN 161KV CKT 1 | E | SWPA | GMO | EMINTH |  | 0 | 505502 | TRUMAN 5 161.00 | 541314 | NWARSAW5 161.00 | 0 |  | 1 | 23WP | 234 | 234 | 234 |  | 91.5768 | 96.5 | [7 empty] | CATEGORYB | SINGLE | 7BLAND 345.00 - FRANKS 345KV CKT 1 | 0 | 344154 | 7BLAND 345.00 | 300041 | 7FRANKS 345.00 | 0 |  | 1 | Transfer Loading < 100% | 226
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T7915013SP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 13SP | 103 | 129 | 0 | 97.4 | 97.3854 | 99.1 | [7 empty] | CATEGORYB | SINGLE | ANTELOPE VALLEY - CHARLIE CREEK 345KV CKT 1 | 0 | 659101 | ANTELOP3 345.00 | 659183 | CHAR.CK3 345.00 | 0 |  | 1 | Transfer Loading < 100% | 128
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T315513WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 13WP | 103 | 129 | 0 | 97.3 | 97.3144 | 97.5 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 126
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T6765513WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 13WP | 103 | 129 | 0 | 95.6 | 95.6254 | 97.1 | [7 empty] | CATEGORYB | SINGLE | ANTELOPE VALLEY - CHARLIE CREEK 345KV CKT 1 | 0 | 659101 | ANTELOP3 345.00 | 659183 | CHAR.CK3 345.00 | 0 |  | 1 | Transfer Loading < 100% | 126
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T10555514SP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 14SP | 103 | 129 | 0 | 98 | 98.0208 | 98.2 | [7 empty] | CATEGORYB | SINGLE | ANTELOPE VALLEY - CHARLIE CREEK 345KV CKT 1 | 0 | 659101 | ANTELOP3 345.00 | 659183 | CHAR.CK3 345.00 | 0 |  | 1 | Transfer Loading < 100% | 127
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T565014SP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 14SP | 103 | 129 | 0 | 98.2 | 98.2448 | 98.1 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 127
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5925514WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 14WP | 103 | 129 | 0 |  | 94.7272 | 98.7 | [7 empty] | CATEGORYB | SINGLE | ANTELOPE VALLEY - CHARLIE CREEK 345KV CKT 1 | 0 | 659101 | ANTELOP3 345.00 | 659183 | CHAR.CK3 345.00 | 0 |  | 1 | Transfer Loading < 100% | 128
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T455023WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 23WP | 103 | 129 | 0 | 98.3 | 98.2592 | 99.7 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 129
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T7695523WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 23WP | 103 | 129 | 0 | 96 | 95.9875 | 99 | [7 empty] | CATEGORYB | SINGLE | CHAR.CK4 230.00 - WATFORD 230KV CKT 1 | 0 | 652216 | WATFORD4 230.00 | 659302 | CHAR.CK4 230.00 | 0 |  | 1 | Transfer Loading < 100% | 128
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T7915523WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 23WP | 103 | 129 | 0 | 95.8 | 95.8161 | 98.8 | [7 empty] | CATEGORYB | SINGLE | CHARLIE CREEK 345/230KV TRANSFORMER CKT 1 | 0 | 659183 | CHAR.CK3 345.00 | 659302 | CHAR.CK4 230.00 | 0 |  | 1 | Transfer Loading < 100% | 128
2012-AG1 | AFS4NC2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2012AG1AFS4NC21T345523WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 23WP | 103 | 129 | 0 |  | 94.035 | 98.4 | [7 empty] | CATEGORYB | SINGLE | BISON - MAURINE 230KV CKT 1 | 0 | 652470 | BISON 4 230.00 | 652497 | MAURINE4 230.00 | 0 |  | 1 | Transfer Loading < 100% | 127
2012-AG1 | AFS4NC1 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2012AG1AFS4NC11T345523WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 23WP | 103 | 129 | 0 |  | 94.712 | 98.3 | [7 empty] | CATEGORYB | SINGLE | BISON - MAURINE 230KV CKT 1 | 0 | 652470 | BISON 4 230.00 | 652497 | MAURINE4 230.00 | 0 |  | 1 | Transfer Loading < 100% | 127
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T7725523WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 23WP | 103 | 129 | 0 | 95.4 | 95.4116 | 98.2 | [7 empty] | CATEGORYB | SINGLE | BELFIELD - CHARLIE CREEK 345KV CKT 1 | 0 | 652424 | BELFELD3 345.00 | 659183 | CHAR.CK3 345.00 | 0 |  | 1 | Transfer Loading < 100% | 127
2012-AG1 | AFS4 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T13725523WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 23WP | 103 | 129 | 0 | 95.7 | 95.6981 | 98 | [7 empty] | CATEGORYB | SINGLE | BELFIELD (BEF KU1A) 345/230/13.8KV TRANSFORMER CKT 1 | 1 | 652424 | BELFELD3 345.00 | 652425 | BELFELD4 230.00 | 652221 | BELFELD9 13.800 | 1 | Transfer Loading < 100% | 127
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T10805523WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 23WP | 103 | 129 | 0 |  | 92.3233 | 96.7 | [7 empty] | CATEGORYB | SINGLE | KEYSTONE - SIDNEY 345KV CKT 1 | 0 | 640252 | KEYSTON3 345.00 | 659133 | SIDNEY 3 345.00 | 0 |  | 1 | Transfer Loading < 100% | 125
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T7615523WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 23WP | 103 | 129 | 0 |  | 93.4175 | 96.3 | [7 empty] | CATEGORYB | SINGLE | MALLARD - NELSON 7 115.00 115KV CKT 1 | 0 | 603023 | MALLARD7 115.00 | 652440 | NELSON 7 115.00 | 0 |  | 1 | Transfer Loading < 100% | 125
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T7855523WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 23WP | 103 | 129 | 0 |  | 92.8524 | 96 | [7 empty] | CATEGORYB | SINGLE | STORLA - WESSINGTON 230KV CKT 1 | 0 | 652607 | WESSINGTON 4230.00 | 659122 | STORLA 4 230.00 | 0 |  | 1 | Transfer Loading < 100% | 124
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T7685523WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 23WP | 103 | 129 | 0 |  | 92.8487 | 95.7 | [7 empty] | CATEGORYB | SINGLE | WATFORD - WILLISTON 230KV CKT 1 | 0 | 652216 | WATFORD4 230.00 | 652400 | WILISTN4 230.00 | 0 |  | 1 | Transfer Loading < 100% | 124
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T14775523WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 23WP | 103 | 129 | 0 |  | 92.4975 | 95.6 | [7 empty] | CATEGORYB | NONSINGLE | DAK01WAPAB2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 124
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T7885523WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 23WP | 103 | 129 | 0 |  | 93.074 | 95.6 | [7 empty] | CATEGORYB | SINGLE | LELAND OLDS - LOGAN 230KV CKT 1 | 0 | 659106 | LELANDO4 230.00 | 659108 | LOGAN 4 230.00 | 0 |  | 1 | Transfer Loading < 100% | 124
2012-AG1 | AFS4 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T7715523WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 23WP | 103 | 129 | 0 |  | 91.1223 | 95.2 | [7 empty] | CATEGORYB | SINGLE | BELFIELD - MEDORA 230KV CKT 1 | 0 | 652413 | MEDORA 4 230.00 | 652425 | BELFELD4 230.00 | 0 |  | 1 | Transfer Loading < 100% | 123
2012-AG1 | AFS4NC1 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2012AG1AFS4NC11T445523WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 23WP | 103 | 129 | 0 |  | 91.4929 | 95.2 | [7 empty] | CATEGORYB | GENOUT | GEN659118 1-LARAMIE RIVER UNIT1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 123
2012-AG1 | AFS4NC2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2012AG1AFS4NC21T355523WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 23WP | 103 | 129 | 0 |  | 91.5737 | 95 | [7 empty] | CATEGORYB | SINGLE | BISON - HETINGER 230KV CKT 1 | 0 | 652470 | BISON 4 230.00 | 661047 | HETINGR4 230.00 | 0 |  | 1 | Transfer Loading < 100% | 123
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5625513SP | TO->FROM | 166TH STREET - JARBALO JUNCTION SWITCHING STATION 115KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 533244 | JARBALO3 115.00 | 533233 | 166TH 3 115.00 | 0 |  | 1 | 13SP | 239 | 239 | 0 | 96.7 | 96.6606 | 97 | [7 empty] | CATEGORYB | SINGLE | 87th STREET - STRANGER CREEK 345KV CKT 1 | 0 | 532772 | STRANGR7 345.00 | 532775 | 87TH 7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 232
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T4815514SP | TO->FROM | 166TH STREET - JARBALO JUNCTION SWITCHING STATION 115KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 533244 | JARBALO3 115.00 | 533233 | 166TH 3 115.00 | 0 |  | 1 | 14SP | 239 | 239 | 0 | 97.3 | 97.2913 | 97.1 | [7 empty] | CATEGORYB | SINGLE | 87th STREET - STRANGER CREEK 345KV CKT 1 | 0 | 532772 | STRANGR7 345.00 | 532775 | 87TH 7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 233
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T7015513SP | TO->FROM | 87th STREET - STRANGER CREEK 345KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532772 | STRANGR7 345.00 | 532775 | 87TH 7 345.00 | 0 |  | 1 | 13SP | 1099 | 1195 | 0 |  | 94.512 | 95.1 | [7 empty] | CATEGORYB | SINGLE | EASTOWN7 345.00 - IATAN 345KV CKT 1 | 0 | 541400 | EASTOWN7 345.00 | 542982 | IATAN 7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 1137
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T4315513WP | TO->FROM | 87th STREET - STRANGER CREEK 345KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532772 | STRANGR7 345.00 | 532775 | 87TH 7 345.00 | 0 |  | 1 | 13WP | 1195 | 1195 | 0 | 96.7 | 96.6515 | 96.9 | [7 empty] | CATEGORYB | SINGLE | EASTOWN7 345.00 - IATAN 345KV CKT 1 | 0 | 541400 | EASTOWN7 345.00 | 542982 | IATAN 7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 1158
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2345514WP | TO->FROM | 95WAJ 3 115.00 - CAPTAIN JUNCTION 115KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 533235 | CAPTAIN3 115.00 | 533284 | 95WAJ 3 115.00 | 0 |  | 1 | 14WP | 117 | 117 | 0 |  | 89.1128 | 95 | [7 empty] | CATEGORYB | SINGLE | SWISSVALE - WEST GARDNER 345KV CKT 1 | 0 | 532774 | SWISVAL7 345.00 | 542965 | W.GRDNR7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 112
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T525518SP | FROM->TO | ALTOONA (ALTOON1X) 138/69/13.2KV TRANSFORMER CKT 1 | E | WERE | WERE | SEAST | SEAST | 2 | 533001 | ALTOONA4 138.00 | 533674 | ALTOO W2 69.000 | 533086 | ALTOO1 1 13.200 | 1 | 18SP | 33 | 36.3 | 41.3 | 99.7 | 99.6713 | 99.7 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 37
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T225523SP | FROM->TO | ALTOONA WEST - CONSOLIDATED 69KV CKT 1 | E | WERE | WERE | SEAST | SEAST | 0 | 533674 | ALTOO W2 69.000 | 533684 | CONSOL 2 69.000 | 0 |  | 1 | 23SP | 32 | 32 | 0 | 98.1 | 98.1389 | 98.2 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 32
2012-AG1 | AFS4 | 0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3205513WP | TO->FROM | AUBURN ROAD - JEFFREY ENERGY CENTER 230KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532852 | JEC 6 230.00 | 532851 | AUBURN 6 230.00 | 0 |  | 1 | 13WP | 565 | 565 | 0 | 98.3 | 98.2906 | 98.4 | [7 empty] | CATEGORYB | SINGLE | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 556
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T12645513WP | TO->FROM | AUBURN ROAD - JEFFREY ENERGY CENTER 230KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532852 | JEC 6 230.00 | 532851 | AUBURN 6 230.00 | 0 |  | 1 | 13WP | 565 | 565 | 0 | 95.5 | 95.4747 | 95.6 | [7 empty] | CATEGORYB | NONSINGLE | WRTOD400 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 541
2012-AG1 | AFS4 | CONT-0400 - JEC - Hoyt 345kV |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5275523SP | FROM->TO | AUBURN ROAD - SHERWOD 115KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 533151 | AUBURN 3 115.00 | 533194 | SHERWOD3 115.00 | 0 |  | 1 | 23SP | 223 | 240 | 0 |  | 92.1504 | 95.9 | [7 empty] | CATEGORYB | SINGLE | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 231
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T19435514SP | FROM->TO | AUBURN ROAD - SWISSVALE 230KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532851 | AUBURN 6 230.00 | 532856 | SWISVAL6 230.00 | 0 |  | 1 | 14SP | 319 | 319 | 0 | 95 | 95.0045 | 95.1 | [7 empty] | CATEGORYB | NONSINGLE | WRTOD400 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 304
2012-AG1 | AFS4 | 0400 - JEC - Hoyt 345kV |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2315514WP | FROM->TO | AUBURN ROAD - SWISSVALE 230KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532851 | AUBURN 6 230.00 | 532856 | SWISVAL6 230.00 | 0 |  | 1 | 14WP | 319 | 319 | 0 |  | 93.1729 | 95.6 | [7 empty] | CATEGORYB | SINGLE | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 305
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5815513SP | FROM->TO | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | E | WERE | WERE | NEAST | NEAST | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 13SP | 280 | 308 | 350 | 97.1 | 97.0853 | 97.3 | [7 empty] | CATEGORYB | SINGLE | AUBURN ROAD - SWISSVALE 230KV CKT 1 | 0 | 532851 | AUBURN 6 230.00 | 532856 | SWISVAL6 230.00 | 0 |  | 1 | Transfer Loading < 100% | 300
2012-AG1 | AFS4 | 0623 - Hoyt 345-115kV Xfmr | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T14875513SP | FROM->TO | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | E | WERE | WERE | NEAST | NEAST | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | 13SP | 280 | 308 | 350 | 95.3 | 95.3498 | 95.5 | [7 empty] | CATEGORYB | SINGLE | HOYT (HOYT 44X) 345/115/14.4KV TRANSFORMER CKT 1 | 1 | 532765 | HOYT 7 345.00 | 533163 | HOYT 3 115.00 | 532804 | HOYT 1 14.400 | 1 | Transfer Loading < 100% | 295
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5225518SP | FROM->TO | BENTON - MIDIAN 138KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 532986 | BENTON 4 138.00 | 532990 | MIDIAN 4 138.00 | 0 |  | 1 | 18SP | 202 | 202 | 0 |  | 93.3092 | 95.6 | [7 empty] | CATEGORYB | SINGLE | BUTLER - WEAVER 138KV CKT 1 | 0 | 532987 | BUTLER 4 138.00 | 532991 | WEAVER 4 138.00 | 0 |  | 1 | Transfer Loading < 100% | 194
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5625523SP | FROM->TO | BENTON - MIDIAN 138KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 532986 | BENTON 4 138.00 | 532990 | MIDIAN 4 138.00 | 0 |  | 1 | 23SP | 202 | 202 | 0 | 95.5 | 95.4763 | 97.7 | [7 empty] | CATEGORYB | SINGLE | BUTLER - WEAVER 138KV CKT 1 | 0 | 532987 | BUTLER 4 138.00 | 532991 | WEAVER 4 138.00 | 0 |  | 1 | Transfer Loading < 100% | 198
2012-AG1 | AFS4 | CONT-1211 - Mockingbird Hill - SW Lawrence 115kV | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T6115513SP | FROM->TO | BISMARK JUNCTION SWITCHING STATION - FARMERS CONSUMER CO-OP 115KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 533234 | BISMARK3 115.00 | 533236 | COOP 3 115.00 | 0 |  | 1 | 13SP | 118 | 118 | 0 | 95.7 | 95.7055 | 96.1 | [7 empty] | CATEGORYB | SINGLE | MOCKINGBIRD HILL SWITCHING STATION - SOUTHWEST LAWRENCE 115KV CKT 1 | 0 | 533253 | MOCKBRD3 115.00 | 533271 | SWLWRNC3 115.00 | 0 |  | 1 | Transfer Loading < 100% | 114
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T21605513SP | FROM->TO | BISMARK JUNCTION SWITCHING STATION - FARMERS CONSUMER CO-OP 115KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 533234 | BISMARK3 115.00 | 533236 | COOP 3 115.00 | 0 |  | 1 | 13SP | 118 | 118 | 0 | 95.3 | 95.2927 | 95.7 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-56 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 113
2012-AG1 | AFS4 | CONT-1211 - Mockingbird Hill - SW Lawrence 115kV | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5135514SP | FROM->TO | BISMARK JUNCTION SWITCHING STATION - FARMERS CONSUMER CO-OP 115KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 533234 | BISMARK3 115.00 | 533236 | COOP 3 115.00 | 0 |  | 1 | 14SP | 118 | 118 | 0 | 96.4 | 96.4372 | 96.7 | [7 empty] | CATEGORYB | SINGLE | MOCKINGBIRD HILL SWITCHING STATION - SOUTHWEST LAWRENCE 115KV CKT 1 | 0 | 533253 | MOCKBRD3 115.00 | 533271 | SWLWRNC3 115.00 | 0 |  | 1 | Transfer Loading < 100% | 115
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T19415514SP | FROM->TO | BISMARK JUNCTION SWITCHING STATION - FARMERS CONSUMER CO-OP 115KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 533234 | BISMARK3 115.00 | 533236 | COOP 3 115.00 | 0 |  | 1 | 14SP | 118 | 118 | 0 | 96 | 96.041 | 96.3 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-56 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 114
2012-AG1 | AFS4 | CONT-1211 - Mockingbird Hill - SW Lawrence 115kV |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5295518SP | FROM->TO | BISMARK JUNCTION SWITCHING STATION - FARMERS CONSUMER CO-OP 115KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 533234 | BISMARK3 115.00 | 533236 | COOP 3 115.00 | 0 |  | 1 | 18SP | 118 | 118 | 0 |  | 93.6413 | 95.8 | [7 empty] | CATEGORYB | SINGLE | MOCKINGBIRD HILL SWITCHING STATION - SOUTHWEST LAWRENCE 115KV CKT 1 | 0 | 533253 | MOCKBRD3 115.00 | 533271 | SWLWRNC3 115.00 | 0 |  | 1 | Transfer Loading < 100% | 114
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T22205518SP | FROM->TO | BISMARK JUNCTION SWITCHING STATION - FARMERS CONSUMER CO-OP 115KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 533234 | BISMARK3 115.00 | 533236 | COOP 3 115.00 | 0 |  | 1 | 18SP | 118 | 118 | 0 |  | 93.2691 | 95.4 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-56 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 113
2012-AG1 | AFS4 | CONT-1211 - Mockingbird Hill - SW Lawrence 115kV | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5725523SP | FROM->TO | BISMARK JUNCTION SWITCHING STATION - FARMERS CONSUMER CO-OP 115KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 533234 | BISMARK3 115.00 | 533236 | COOP 3 115.00 | 0 |  | 1 | 23SP | 118 | 118 | 0 | 95.7 | 95.6513 | 97.3 | [7 empty] | CATEGORYB | SINGLE | MOCKINGBIRD HILL SWITCHING STATION - SOUTHWEST LAWRENCE 115KV CKT 1 | 0 | 533253 | MOCKBRD3 115.00 | 533271 | SWLWRNC3 115.00 | 0 |  | 1 | Transfer Loading < 100% | 115
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T25145523SP | FROM->TO | BISMARK JUNCTION SWITCHING STATION - FARMERS CONSUMER CO-OP 115KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 533234 | BISMARK3 115.00 | 533236 | COOP 3 115.00 | 0 |  | 1 | 23SP | 118 | 118 | 0 | 95.2 | 95.2486 | 96.8 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WERE-56 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 115
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5035514SP | TO->FROM | BUTLER - WEAVER 138KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 532991 | WEAVER 4 138.00 | 532987 | BUTLER 4 138.00 | 0 |  | 1 | 14SP | 160 | 160 | 0 | 97.9 | 97.8586 | 98.7 | [7 empty] | CATEGORYB | SINGLE | BENTON - MIDIAN 138KV CKT 1 | 0 | 532986 | BENTON 4 138.00 | 532990 | MIDIAN 4 138.00 | 0 |  | 1 | Transfer Loading < 100% | 158
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5025518SP | TO->FROM | CHISHOLM - MAIZEE 4 138.00 138KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533391 | MAIZEE 4 138.00 | 533035 | CHISHLM4 138.00 | 0 |  | 1 | 18SP | 382 | 382 | 0 |  | 89.9081 | 97.6 | [7 empty] | CATEGORYB | SINGLE | BENTON - WICHITA 345KV CKT 1 | 0 | 532791 | BENTON 7 345.00 | 532796 | WICHITA7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 373
2012-AG1 | AFS4 | 0803 - Hoyt - Stranger 345kV |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T4825518SP | FROM->TO | CIRCLEVILLE - KING HILL N.M. COOP (NEMAHA MARSHALL R.E.C. 115KV CKT 1 | E | WERE | WERE | NEAST | NCENTRAL | 0 | 533152 | CIRCLVL3 115.00 | 533331 | KING HL3 115.00 | 0 |  | 1 | 18SP | 86 | 92 | 0 |  | 89.9755 | 96.7 | [7 empty] | CATEGORYB | SINGLE | HOYT - STRANGER CREEK 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532772 | STRANGR7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 89
2012-AG1 | AFS4 | 0803 - Hoyt - Stranger 345kV |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5325523SP | FROM->TO | CIRCLEVILLE - KING HILL N.M. COOP (NEMAHA MARSHALL R.E.C. 115KV CKT 1 | E | WERE | WERE | NEAST | NCENTRAL | 0 | 533152 | CIRCLVL3 115.00 | 533331 | KING HL3 115.00 | 0 |  | 1 | 23SP | 86 | 92 | 0 |  | 91.7878 | 97.2 | [7 empty] | CATEGORYB | SINGLE | HOYT - STRANGER CREEK 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532772 | STRANGR7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 90
2012-AG1 | AFS4 | CONT-0803 - Hoyt - Stranger 345kV |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5355523SP | FROM->TO | COUNTY LINE - ROCK CREEK 69KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 533456 | COLINE 2 69.000 | 533458 | ROCKCRK2 69.000 | 0 |  | 1 | 23SP | 41 | 41 | 0 |  | 92.2375 | 95.4 | [7 empty] | CATEGORYB | SINGLE | HOYT - STRANGER CREEK 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532772 | STRANGR7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 40
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T2625018SP | TO->FROM | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | E | WERE | WERE | NEAST | NCENTRAL | 0 | 532852 | JEC 6 230.00 | 532861 | EMANHAT6 230.00 | 0 |  | 1 | 18SP | 446 | 446 | 0 | 101.8 | 101.8148 | 98.1 | [7 empty] | CATEGORYB | SINGLE | GEARY 7 345.00 - JEFFREY ENERGY CENTER 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532767 | GEARY 7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 438
2012-AG1 | AFS4 | CONT-0633 - East Manhattan 230-115kV XFMR | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T10095013SP | FROM->TO | EAST MANHATTAN - NORTHWEST MANHATTAN 230KV CKT 1 | E | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 532861 | EMANHAT6 230.00 | 532865 | NMANHT6 230.00 | 0 |  | 1 | 13SP | 319 | 319 | 0 | 95.4 | 95.4334 | 95.2 | [7 empty] | CATEGORYB | SINGLE | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | Transfer Loading < 100% | 304
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T3025013SP | FROM->TO | EAST MANHATTAN (EMANHT3X) 230/115/18.0KV TRANSFORMER CKT 1 | E | WERE | WERE | NCENTRAL | NCENTRAL | 1 | 532861 | EMANHAT6 230.00 | 533326 | EMANHAT3 115.00 | 532888 | EMANHAT1 18.000 | 1 | 13SP | 280 | 308 | 350 | 96.2 | 96.1672 | 95.9 | [7 empty] | CATEGORYB | SINGLE | EAST MANHATTAN - NORTHWEST MANHATTAN 230KV CKT 1 | 0 | 532861 | EMANHAT6 230.00 | 532865 | NMANHT6 230.00 | 0 |  | 1 | Transfer Loading < 100% | 296
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5995513SP | FROM->TO | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 | 13SP | 382 | 413 | 0 |  | 93.5067 | 95.5 | [7 empty] | CATEGORYB | SINGLE | 45TH ST4 138.00 - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533074 | 45TH ST4 138.00 | 0 |  | 1 | Transfer Loading < 100% | 395
2012-AG1 | AFS4 | CONT-0803 - Hoyt - Stranger 345kV |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2325514WP | TO->FROM | GOODYEAR JUNCTION - NORTHLAND 115KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 533169 | NTHLAND3 115.00 | 533162 | GOODYR 3 115.00 | 0 |  | 1 | 14WP | 159 | 159 | 0 |  | 94.929 | 97.9 | [7 empty] | CATEGORYB | SINGLE | HOYT - STRANGER CREEK 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532772 | STRANGR7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 156
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T6045513SP | FROM->TO | HOOVER NORTH (HOOVER3X) 138/69/13.2KV TRANSFORMER CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 1 | 533049 | HOOVERN4 138.00 | 533805 | HOOVERN2 69.000 | 533109 | HOOVR3 1 13.200 | 1 | 13SP | 150 | 165 | 187.5 | 96.1 | 96.1221 | 98.2 | [7 empty] | CATEGORYB | SINGLE | HOOVER NORTH - HOOVERS4 138.00 138KV CKT 1 | 0 | 533049 | HOOVERN4 138.00 | 533050 | HOOVERS4 138.00 | 0 |  | 1 | Transfer Loading < 100% | 163
2012-AG1 | AFS4 | CONT-0803 - Hoyt - Stranger 345kV | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5525513SP | FROM->TO | HOYT - HOYTJS 3 115.00 115KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 533163 | HOYT 3 115.00 | 533198 | HOYTJS 3 115.00 | 0 |  | 1 | 13SP | 179 | 179 | 0 | 95.5 | 95.4936 | 96.2 | [7 empty] | CATEGORYB | SINGLE | HOYT - STRANGER CREEK 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532772 | STRANGR7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 173
2012-AG1 | AFS4 | CONT-0803 - Hoyt - Stranger 345kV | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T4715514SP | FROM->TO | HOYT - HOYTJS 3 115.00 115KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 533163 | HOYT 3 115.00 | 533198 | HOYTJS 3 115.00 | 0 |  | 1 | 14SP | 179 | 179 | 0 | 97.1 | 97.0737 | 97.6 | [7 empty] | CATEGORYB | SINGLE | HOYT - STRANGER CREEK 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532772 | STRANGR7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 175
2012-AG1 | AFS4 | CONT-0803 - Hoyt - Stranger 345kV |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T4845518SP | FROM->TO | HOYT - HOYTJS 3 115.00 115KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 533163 | HOYT 3 115.00 | 533198 | HOYTJS 3 115.00 | 0 |  | 1 | 18SP | 179 | 179 | 0 |  | 92.4655 | 96.2 | [7 empty] | CATEGORYB | SINGLE | HOYT - STRANGER CREEK 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532772 | STRANGR7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 173
2012-AG1 | AFS4 | CONT-0803 - Hoyt - Stranger 345kV | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5345523SP | FROM->TO | HOYT - HOYTJS 3 115.00 115KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 533163 | HOYT 3 115.00 | 533198 | HOYTJS 3 115.00 | 0 |  | 1 | 23SP | 179 | 179 | 0 | 95.1 | 95.0975 | 98.3 | [7 empty] | CATEGORYB | SINGLE | HOYT - STRANGER CREEK 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532772 | STRANGR7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 176
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5555513SP | TO->FROM | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 | 13SP | 1076 | 1076 | 0 | 97.5 | 97.5463 | 98.3 | [7 empty] | CATEGORYB | SINGLE | JEFFREY ENERGY CENTER - MORRIS COUNTY 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532770 | MORRIS 7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 1058
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5785513SP | TO->FROM | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 | 13SP | 1076 | 1076 | 0 | 96.8 | 96.8212 | 97.7 | [7 empty] | CATEGORYB | SINGLE | AUBURN ROAD - JEFFREY ENERGY CENTER 230KV CKT 1 | 0 | 532851 | AUBURN 6 230.00 | 532852 | JEC 6 230.00 | 0 |  | 1 | Transfer Loading < 100% | 1052
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T4745514SP | TO->FROM | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 | 14SP | 1076 | 1076 | 0 | 98.7 | 98.6566 | 99.4 | [7 empty] | CATEGORYB | SINGLE | JEFFREY ENERGY CENTER - MORRIS COUNTY 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532770 | MORRIS 7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 1070
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T4965514SP | TO->FROM | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 | 14SP | 1076 | 1076 | 0 | 98.5 | 98.4509 | 99.2 | [7 empty] | CATEGORYB | SINGLE | AUBURN ROAD - JEFFREY ENERGY CENTER 230KV CKT 1 | 0 | 532851 | AUBURN 6 230.00 | 532852 | JEC 6 230.00 | 0 |  | 1 | Transfer Loading < 100% | 1068
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T20305514SP | TO->FROM | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 | 14SP | 1076 | 1076 | 0 |  | 94.6637 | 95.5 | [7 empty] | CATEGORYB | GENOUT | GEN542962 2-IATAN UNIT #2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 1028
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2335514WP | TO->FROM | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 | 14WP | 1076 | 1076 | 0 |  | 91.4246 | 95.2 | [7 empty] | CATEGORYB | SINGLE | JEFFREY ENERGY CENTER - MORRIS COUNTY 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532770 | MORRIS 7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 1025
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T23855518SP | TO->FROM | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 | 18SP | 1076 | 1076 | 0 |  | 93.7978 | 99 | [7 empty] | CATEGORYB | GENOUT | GEN542957 1-IATAN UNIT #1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 1066
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T4935518SP | TO->FROM | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 | 18SP | 1076 | 1076 | 0 |  | 92.8677 | 98.9 | [7 empty] | CATEGORYB | SINGLE | EMPORIA ENERGY CENTER - SWISSVALE 345KV CKT 1 | 0 | 532768 | EMPEC 7 345.00 | 532774 | SWISVAL7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 1065
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T4875518SP | TO->FROM | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 | 18SP | 1076 | 1076 | 0 |  | 94.7591 | 98.7 | [7 empty] | CATEGORYB | SINGLE | GEARY 7 345.00 - JEFFREY ENERGY CENTER 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532767 | GEARY 7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 1063
2012-AG1 | AFS4 | CONT-0302 - Lacygne - Wolf Creek 345kV |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5075518SP | TO->FROM | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 | 18SP | 1076 | 1076 | 0 |  | 90.093 | 95.8 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - WOLF CREEK 345KV CKT 1 | 0 | 532797 | WOLFCRK7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 1031
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T6485523SP | TO->FROM | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 | 23SP | 1076 | 1076 | 0 |  | 92.9954 | 97.3 | [7 empty] | CATEGORYB | SINGLE | CRAIG - WEST GARDNER 345KV CKT 1 | 0 | 542965 | W.GRDNR7 345.00 | 542977 | CRAIG 7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 1047
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T27325523SP | TO->FROM | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 | 23SP | 1076 | 1076 | 0 |  | 92.3732 | 96.6 | [7 empty] | CATEGORYB | GENOUT | GEN640009 1-COOPER NUCLEAR STATION | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 1040
2012-AG1 | AFS4 | CONT-0302 - Lacygne - Wolf Creek 345kV |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5495523SP | TO->FROM | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 | 23SP | 1076 | 1076 | 0 |  | 92.0593 | 96.6 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - WOLF CREEK 345KV CKT 1 | 0 | 532797 | WOLFCRK7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 1040
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T27075523SP | TO->FROM | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 | 23SP | 1076 | 1076 | 0 |  | 91.5823 | 95.8 | [7 empty] | CATEGORYB | GENOUT | GEN542951 5-HAWTHORN UNIT #5 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 1031
2012-AG1 | AFS4 | CONT-0618 - Auburn Road 230-115kV XFMR |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T17895523SP | TO->FROM | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 | 23SP | 1076 | 1076 | 0 |  | 91.4433 | 95.6 | [7 empty] | CATEGORYB | SINGLE | AUBURN ROAD (AUBRN77X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532851 | AUBURN 6 230.00 | 533151 | AUBURN 3 115.00 | 532880 | AUBURN 1 13.800 | 1 | Transfer Loading < 100% | 1029
2012-AG1 | AFS4 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T14965513SP | FROM->TO | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | E | WERE | WERE | NEAST | NEAST | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 13SP | 280 | 308 | 350 | 96.6 | 96.6174 | 97 | [7 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 | Transfer Loading < 100% | 299
2012-AG1 | AFS4 | 0901 - Lawrence Hill - Midland Junction 230kV | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T4995514SP | FROM->TO | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | E | WERE | WERE | NEAST | NEAST | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 14SP | 280 | 308 | 350 | 99.3 | 99.2952 | 99.6 | [7 empty] | CATEGORYB | SINGLE | LAWRENCE HILL - MIDLAND JUNCTION 230KV CKT 1 | 0 | 532853 | LAWHILL6 230.00 | 532855 | MIDLAND6 230.00 | 0 |  | 1 | Transfer Loading < 100% | 307
2012-AG1 | AFS4 | 0615 - Midland Junction 230-115kV | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T13505514SP | FROM->TO | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | E | WERE | WERE | NEAST | NEAST | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 14SP | 280 | 308 | 350 | 99.2 | 99.2397 | 99.5 | [7 empty] | CATEGORYB | SINGLE | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 | Transfer Loading < 100% | 307
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T19675514SP | FROM->TO | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | E | WERE | WERE | NEAST | NEAST | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | 14SP | 280 | 308 | 350 | 96.8 | 96.8438 | 97.1 | [7 empty] | CATEGORYB | NONSINGLE | WR-TOD-0615 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 300
2012-AG1 | AFS4 | 0631 - Lawrence Hill 230-115kV |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T15715518SP | FROM->TO | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | E | WERE | WERE | NEAST | NEAST | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 | 18SP | 280 | 308 | 350 |  | 93.6728 | 96.4 | [7 empty] | CATEGORYB | SINGLE | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | Transfer Loading < 100% | 297
2012-AG1 | AFS4 | 0631 - Lawrence Hill 230-115kV | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T17925523SP | FROM->TO | MIDLAND JUNCTION (MIDJ126X) 230/115/18.0KV TRANSFORMER CKT 1 | E | WERE | WERE | NEAST | NEAST | 1 | 532855 | MIDLAND6 230.00 | 533252 | MIDLAND3 115.00 | 532884 | MIDLAND1 18.000 | 1 | 23SP | 280 | 308 | 350 | 97.4 | 97.4059 | 99.4 | [7 empty] | CATEGORYB | SINGLE | LAWRENCE HILL (LAWHL29X) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532853 | LAWHILL6 230.00 | 533250 | LWRNCHL3 115.00 | 532882 | LAWHILL1 13.800 | 1 | Transfer Loading < 100% | 307
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T8475513WP | FROM->TO | MOUNDRIDGE (MOUND10X) 138/115/13.8KV TRANSFORMER CKT 1 | E | WERE | WERE | WEST | SCENTRAL | 2 | 533429 | MOUNDRG3 115.00 | 533013 | MOUND 4 138.00 | 533096 | MOUNDRI1 13.800 | 1 | 13WP | 100 | 110 | 125 | 97.7 | 97.7193 | 96.6 | [7 empty] | CATEGORYB | SINGLE | WICHITA (WICHT12X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532796 | WICHITA7 345.00 | 533040 | EVANS N4 138.00 | 532830 | WICH12 1 13.800 | 1 | Transfer Loading < 100% | 107
2012-AG1 | AFS4 | INVALID | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T2755018SP | TO->FROM | NORTH STREET - NORTHVIEW 115KV CKT 1 | E | WERE | WERE | WEST | WEST | 0 | 533371 | NORTHVW3 115.00 | 533370 | NORTHST3 115.00 | 0 |  | 1 | 18SP | 68 | 68 | 0 | 96.3 | 96.3006 | 96.293 | [7 empty] | CATEGORYB | SINGLE | NORTH STREET - NORTHVIEW 115KV CKT 2 | 0 | 533370 | NORTHST3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 2 | Transfer Loading < 100% | 66
2012-AG1 | AFS4 | INVALID | FDNS |  | FDNS |  | 5 | 0 | 2012AG1AFS41T2745018SP | TO->FROM | NORTH STREET - NORTHVIEW 115KV CKT 2 | E | WERE | WERE | WEST | WEST | 0 | 533371 | NORTHVW3 115.00 | 533370 | NORTHST3 115.00 | 0 |  | 2 | 18SP | 68 | 68 | 0 | 96.3 | 96.3006 | 96.293 | [7 empty] | CATEGORYB | SINGLE | NORTH STREET - NORTHVIEW 115KV CKT 1 | 0 | 533370 | NORTHST3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | Transfer Loading < 100% | 66
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T5565523SP | TO->FROM | SMAN_E_3 115.00 - SOUTH MANHATTAN 115KV CKT 1 | E | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533340 | SMANHAT3 115.00 | 533351 | SMAN_E_3 115.00 | 0 |  | 1 | 23SP | 86 | 102 | 0 |  | 90.3454 | 97.3 | [7 empty] | CATEGORYB | SINGLE | AUBURN ROAD - JEFFREY ENERGY CENTER 230KV CKT 1 | 0 | 532851 | AUBURN 6 230.00 | 532852 | JEC 6 230.00 | 0 |  | 1 | Transfer Loading < 100% | 100
2012-AG1 | AFS4 | CONT-0400 - JEC - Hoyt 345kV |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2785523WP | FROM->TO | SMAN_W_3 115.00 - SOUTH MANHATTAN 115KV CKT 1 | E | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533350 | SMAN_W_3 115.00 | 533340 | SMANHAT3 115.00 | 0 |  | 1 | 23WP | 86 | 102 | 0 |  | 87.268 | 96.2 | [7 empty] | CATEGORYB | SINGLE | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 99
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T7455514WP | FROM->TO | WICHITA (WICHT11X) 345/138/13.8KV TRANSFORMER CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 1 | 532796 | WICHITA7 345.00 | 533040 | EVANS N4 138.00 | 532829 | WICH11 1 13.800 | 1 | 14WP | 400 | 440 | 500 | 96.4 | 96.3766 | 99.4 | [7 empty] | CATEGORYB | SINGLE | WICHITA (WICHT12X) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532796 | WICHITA7 345.00 | 533040 | EVANS N4 138.00 | 532830 | WICH12 1 13.800 | 1 | Transfer Loading < 100% | 438
2012-AG1 | AFS4 | CONT-0302 - Lacygne - Wolf Creek 345kV |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2075518WP | FROM->TO | WOLF CREEK 345/69KV TRANSFORMER CKT 1 | E | WERE | WERE | SEAST | SEAST | 0 | 532797 | WOLFCRK7 345.00 | 533653 | WOLFCRK2 69.000 | 0 |  | 1 | 18WP | 100 | 110 | 0 |  | 94.8023 | 99.7 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - WOLF CREEK 345KV CKT 1 | 0 | 532797 | WOLFCRK7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 110
2012-AG1 | AFS4 | CONT-0302 - Lacygne - Wolf Creek 345kV |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2835523WP | FROM->TO | WOLF CREEK 345/69KV TRANSFORMER CKT 1 | E | WERE | WERE | SEAST | SEAST | 0 | 532797 | WOLFCRK7 345.00 | 533653 | WOLFCRK2 69.000 | 0 |  | 1 | 23WP | 100 | 110 | 0 |  | 91.4528 | 95.3 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - WOLF CREEK 345KV CKT 1 | 0 | 532797 | WOLFCRK7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 105
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T12295514SP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | E | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 14SP | 124 | 124 | 0 | 104 | 103.9931 | 96.5 | [7 empty] | CATEGORYB | SINGLE | WOODRING (WOODRNG2) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514714 | WOODRNG4 138.00 | 514715 | WOODRNG7 345.00 | 515770 | WOODRNG1 13.800 | 1 | Transfer Loading < 100% | 120
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2305514SP | TO->FROM | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | E | WFEC | OKGE | AEP-OP | ENID | 0 | 520999 | MOORLND4 138.00 | 514788 | GLASMTN4 138.00 | 0 |  | 1 | 14SP | 124 | 124 | 0 | 103.4 | 103.4393 | 95.7 | [7 empty] | CATEGORYB | SINGLE | ALVA - KNOBHILL 69KV CKT 1 | 0 | 514792 | ALVAOGE2 69.000 | 514794 | KNOBHIL2 69.000 | 0 |  | 1 | Transfer Loading < 100% | 119
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T2965518SP | TO->FROM | PAOLI - PAYNE 138.00 138KV CKT 1 | E | WFEC | WFEC | AEP-IM-I | AEP-IM-I | 0 | 520888 | PAYNE 138.00 | 521023 | PAOLI 4 138.00 | 0 |  | 1 | 18SP | 132 | 143 | 143 |  | 92.8211 | 98.3 | [7 empty] | CATEGORYB | SINGLE | ANADARKO - GEORGIA 138KV CKT 1 | 0 | 520814 | ANADARK4 138.00 | 520923 | GEORGIA4 138.00 | 0 |  | 1 | Transfer Loading < 100% | 141
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3195518SP | TO->FROM | PAOLI - PAYNE 138.00 138KV CKT 1 | E | WFEC | WFEC | AEP-IM-I | AEP-IM-I | 0 | 520888 | PAYNE 138.00 | 521023 | PAOLI 4 138.00 | 0 |  | 1 | 18SP | 132 | 143 | 143 |  | 90.7369 | 96.3 | [7 empty] | CATEGORYB | SINGLE | FLETCHER - GEORGIA 138KV CKT 1 | 0 | 520912 | FLETCH-4 138.00 | 520923 | GEORGIA4 138.00 | 0 |  | 1 | Transfer Loading < 100% | 138
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T4105523SP | TO->FROM | PAOLI - PAYNE 138.00 138KV CKT 1 | E | WFEC | WFEC | AEP-IM-I | AEP-IM-I | 0 | 520888 | PAYNE 138.00 | 521023 | PAOLI 4 138.00 | 0 |  | 1 | 23SP | 132 | 143 | 143 | 101.6 | 101.6295 | 99.2 | [7 empty] | CATEGORYB | SINGLE | FLETCHER - GEORGIA 138KV CKT 1 | 0 | 520912 | FLETCH-4 138.00 | 520923 | GEORGIA4 138.00 | 0 |  | 1 | Transfer Loading < 100% | 142
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3985523SP | TO->FROM | PAOLI - PAYNE 138.00 138KV CKT 1 | E | WFEC | WFEC | AEP-IM-I | AEP-IM-I | 0 | 520888 | PAYNE 138.00 | 521023 | PAOLI 4 138.00 | 0 |  | 1 | 23SP | 132 | 143 | 143 | 100.2 | 100.1631 | 97.1 | [7 empty] | CATEGORYB | SINGLE | EMPIRE - FLETCHER 138KV CKT 1 | 0 | 520900 | EMPIRE 4 138.00 | 520912 | FLETCH-4 138.00 | 0 |  | 1 | Transfer Loading < 100% | 139
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T3925523SP | TO->FROM | PAOLI - PAYNE 138.00 138KV CKT 1 | E | WFEC | WFEC | AEP-IM-I | AEP-IM-I | 0 | 520888 | PAYNE 138.00 | 521023 | PAOLI 4 138.00 | 0 |  | 1 | 23SP | 132 | 143 | 143 | 99.7 | 99.7099 | 96.1 | [7 empty] | CATEGORYB | SINGLE | COMANCHE - LOCO 138KV CKT 1 | 0 | 520864 | COMANCH4 138.00 | 520981 | LOCO 4 138.00 | 0 |  | 1 | Transfer Loading < 100% | 138
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T655513WP | TO->FROM | SOUTHWESTERN STATION - WASHITA 138KV CKT 1 | E | WFEC | AEPW | AEP-CS | PSO_WESTERN | 0 | 521089 | WASHITA4 138.00 | 511477 | S.W.S.-4 138.00 | 0 |  | 1 | 13WP | 262 | 329 | 0 |  | 89.9448 | 97 | [7 empty] | CATEGORYB | SINGLE | GRACEMONT - LAWTON EASTSIDE 345KV CKT 1 | 0 | 511468 | L.E.S.-7 345.00 | 515800 | GRACMNT7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 320
2012-AG1 | AFS4 |  |  |  | FDNS |  | 5 | 5 | 2012AG1AFS41T785514WP | TO->FROM | SOUTHWESTERN STATION - WASHITA 138KV CKT 1 | E | WFEC | AEPW | AEP-CS | PSO_WESTERN | 0 | 521089 | WASHITA4 138.00 | 511477 | S.W.S.-4 138.00 | 0 |  | 1 | 14WP | 262 | 329 | 0 |  | 85.6895 | 99.4 | [7 empty] | CATEGORYB | SINGLE | GRACEMONT - LAWTON EASTSIDE 345KV CKT 1 | 0 | 511468 | L.E.S.-7 345.00 | 515800 | GRACMNT7 345.00 | 0 |  | 1 | Transfer Loading < 100% | 328
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T605513SP | FROM->TO | LAMAR_E_W | E |  |  |  |  | LAMAR_E_W | 0 |  | 0 |  | 0 |  |  | 13SP | 210 | 210 | 210 | 99 | -99.0479 | 99 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 208
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T355513WP | FROM->TO | LAMAR_E_W | E |  |  |  |  | LAMAR_E_W | 0 |  | 0 |  | 0 |  |  | 13WP | 210 | 210 | 210 | 99 | -99.0468 | 99 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 208
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T655514SP | FROM->TO | LAMAR_E_W | E |  |  |  |  | LAMAR_E_W | 0 |  | 0 |  | 0 |  |  | 14SP | 210 | 210 | 210 | 99 | -99.0478 | 99 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 208
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T385514WP | FROM->TO | LAMAR_E_W | E |  |  |  |  | LAMAR_E_W | 0 |  | 0 |  | 0 |  |  | 14WP | 210 | 210 | 210 | 99.1 | -99.0502 | 99 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 208
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T825518SP | FROM->TO | LAMAR_E_W | E |  |  |  |  | LAMAR_E_W | 0 |  | 0 |  | 0 |  |  | 18SP | 210 | 210 | 210 | 99 | -99.0482 | 99 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 208
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T395518WP | FROM->TO | LAMAR_E_W | E |  |  |  |  | LAMAR_E_W | 0 |  | 0 |  | 0 |  |  | 18WP | 210 | 210 | 210 | 99 | -99.0433 | 99 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 208
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T1025523SP | FROM->TO | LAMAR_E_W | E |  |  |  |  | LAMAR_E_W | 0 |  | 0 |  | 0 |  |  | 23SP | 210 | 210 | 210 | 99 | -99.0475 | 99 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 208
2012-AG1 | AFS4 |  | FDNS |  | FDNS |  | 5 | 5 | 2012AG1AFS41T565523WP | FROM->TO | LAMAR_E_W | E |  |  |  |  | LAMAR_E_W | 0 |  | 0 |  | 0 |  |  | 23WP | 210 | 210 | 210 | 98 | -97.9941 | 98 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | 206