## Table1
Customer | Study Number | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date without interim redispatch | Deferred Stop Date without interim redispatch | Start Date with interim redispatch | Stop Date with interim redispatch | Minimum Allocated ATC (MW) within reservation period | Season of Minimum Allocated ATC within reservation period
BPAE | 2012-AG3-070 | 77387381 | WR | KCPL | 50 | 2014-10-01 | 2019-10-01 | 2019-06-01 | 2024-06-01 | 2019-06-01 | 2024-06-01 | 0 | 18SP
BPAE | 2012-AG3-071 | 77387397 | WR | KCPL | 50 | 2014-10-01 | 2019-10-01 | 2019-06-01 | 2024-06-01 | 2019-06-01 | 2024-06-01 | 0 | 18SP
BPAE | 2012-AG3-072 | 77387401 | WR | KCPL | 30 | 2014-10-01 | 2019-10-01 | 2019-06-01 | 2024-06-01 | 2019-06-01 | 2024-06-01 | 0 | 18SP
BPAE | 2012-AG3-073 | 77387415 | SPS | AMRN | 100 | 2014-10-01 | 2019-10-01 | 2019-06-01 | 2024-06-01 | 2019-06-01 | 2024-06-01 | 0 | 18SP
BPAE | 2012-AG3-074 | 77387419 | SPS | AMRN | 100 | 2014-10-01 | 2019-10-01 | 2019-06-01 | 2024-06-01 | 2019-06-01 | 2024-06-01 | 0 | 18SP
BPAE | 2012-AG3-075 | 77387426 | SPS | EES | 100 | 2014-10-01 | 2019-10-01 | 2019-06-01 | 2024-06-01 | 2019-06-01 | 2024-06-01 | 0 | 18SP
BPAE | 2012-AG3-076 | 77387430 | SPS | EES | 100 | 2014-10-01 | 2019-10-01 | 2019-06-01 | 2024-06-01 | 2019-06-01 | 2024-06-01 | 0 | 18SP
BPAE | 2012-AG3-077 | 77387435 | SPS | EES | 100 | 2014-10-01 | 2019-10-01 | 2019-06-01 | 2024-06-01 | 2019-06-01 | 2024-06-01 | 0 | 18SP
BPAE | 2012-AG3-078 | 77387437 | SPS | EES | 100 | 2014-10-01 | 2019-10-01 | 2019-06-01 | 2024-06-01 | 2019-06-01 | 2024-06-01 | 0 | 18SP
CCG | 2012-AG3-056 | 76979606 | CSWS | ERCOTN | 198 | 2013-06-01 | 2018-06-01 | 2019-06-01 | 2024-06-01 | 2019-06-01 | 2024-06-01 | 0 | 13SP
CCG | 2012-AG3-057 | 76979671 | ERCOTN | ERCOTN | 198 | 2014-05-01 | 2019-05-01 | 2014-05-01 | 2019-05-01 | 2014-05-01 | 2019-05-01 | 0 | 14SP
CCG | 2012-AG3-058 | 76979772 | ERCOTN | ERCOTN | 198 | 2015-05-01 | 2020-05-01 | 2015-05-01 | 2020-05-01 | 2015-05-01 | 2020-05-01 | 0 | 18SP
CRGL | 2012-AG3-047 | 77029025 | WFEC | ERCOTN | 207 | 2014-01-01 | 2020-01-01 | 2019-06-01 | 2025-06-01 | 2019-06-01 | 2025-06-01 | 0 | 14SP
CRGL | 2012-AG3-048 | 77029027 | SPS | ERCOTN | 207 | 2014-01-01 | 2020-01-01 | 2019-06-01 | 2025-06-01 | 2019-06-01 | 2025-06-01 | 0 | 14SP
CRGL | 2012-AG3-049 | 77410128 | WR | EES | 200 | 2014-01-01 | 2019-01-01 | 2019-06-01 | 2024-06-01 | 2019-06-01 | 2024-06-01 | 0 | 14SP
CRGL | 2012-AG3-050 | 77410129 | SECI | EES | 101 | 2014-01-01 | 2019-01-01 | 2019-06-01 | 2024-06-01 | 2019-06-01 | 2024-06-01 | 0 | 14SP
CRGL | 2012-AG3-051 | 77410131 | SECI | EES | 100 | 2014-01-01 | 2019-01-01 | 2019-06-01 | 2024-06-01 | 2019-06-01 | 2024-06-01 | 0 | 14SP
CRGL | 2012-AG3-052 | 77410135 | WFEC | EES | 75 | 2014-01-01 | 2019-01-01 | 2019-06-01 | 2024-06-01 | 2019-06-01 | 2024-06-01 | 0 | 14SP
CRGL | 2012-AG3-054 | 77410157 | CSWS | EES | 150 | 2014-01-01 | 2019-01-01 | 2019-06-01 | 2024-06-01 | 2019-06-01 | 2024-06-01 | 0 | 14SP
ETEC | 2012-AG3-038 | 77410319 | CSWS | CSWS | 1171 | 2015-01-01 | 2040-01-01 | 2015-01-01 | 2040-01-01 | 2015-01-01 | 2040-01-01 | 0 | 18SP
ETEC | 2012-AG3-039 | 77410327 | CSWS | CSWS | 79 | 2015-01-01 | 2040-01-01 | 2015-01-01 | 2040-01-01 | 2015-01-01 | 2040-01-01 | 0 | 18SP
ETEC | 2012-AG3-040 | 77410336 | CSWS | CSWS | 500 | 2015-01-01 | 2040-01-01 | 2015-01-01 | 2040-01-01 | 2015-01-01 | 2040-01-01 | 0 | 18SP
ETEC | 2012-AG3-041 | 77410342 | EES | CSWS | 30 | 2015-01-01 | 2040-01-01 | 2015-01-01 | 2040-01-01 | 2015-01-01 | 2040-01-01 | 0 | 18SP
ETEC | 2012-AG3-042 | 77410350 | CSWS | CSWS | 406 | 2015-01-01 | 2040-01-01 | 2017-06-01 | 2042-06-01 | 2015-01-01 | 2040-01-01 | 0 | 18SP
ETEC | 2012-AG3-043 | 77410353 | CLEC | CSWS | 38 | 2015-01-01 | 2040-01-01 | 2015-01-01 | 2040-01-01 | 2015-01-01 | 2040-01-01 | 0 | 18SP
ETEC | 2012-AG3-044 | 77410357 | SPA | CSWS | 128 | 2015-01-01 | 2040-01-01 | 2015-01-01 | 2040-01-01 | 2015-01-01 | 2040-01-01 | 0 | 18SP
ETEC | 2012-AG3-045 | 77410360 | SPA | CSWS | 1 | 2015-01-01 | 2040-01-01 | 2015-01-01 | 2040-01-01 | 2015-01-01 | 2040-01-01 | 0 | 18SP
ETEC | 2012-AG3-046 | 77410382 | CSWS | CSWS | 52 | 2015-01-01 | 2040-01-01 | 2015-01-01 | 2040-01-01 | 2015-01-01 | 2040-01-01 | 0 | 18SP
GSECGS | 2012-AG3-032 | 77401449 | SPS | SPS | 7 | 2013-06-01 | 2039-01-01 | 2020-01-01 | 2045-08-01 | 2020-01-01 | 2045-08-01 | 0 | 13SP
GSECGS | 2012-AG3-033 | 77401452 | SPS | SPS | 7 | 2013-06-01 | 2039-01-01 | 2020-01-01 | 2045-08-01 | 2020-01-01 | 2045-08-01 | 0 | 13SP
GSECGS | 2012-AG3-034 | 77401453 | SPS | SPS | 7 | 2013-06-01 | 2039-01-01 | 2020-01-01 | 2045-08-01 | 2020-01-01 | 2045-08-01 | 0 | 13SP
GSECGS | 2012-AG3-035 | 77402179 | SPS | SPS | 203 | 2015-01-01 | 2041-01-01 | 2020-01-01 | 2046-01-01 | 2020-01-01 | 2046-01-01 | 0 | 18SP
GSECGS | 2012-AG3-036 | 77402184 | SPS | SPS | 203 | 2015-01-01 | 2041-01-01 | 2020-01-01 | 2046-01-01 | 2020-01-01 | 2046-01-01 | 0 | 18SP
INF | 2012-AG3-030 | 77409954 | SECI | EES | 200 | 2015-01-01 | 2020-01-01 | 2019-06-01 | 2024-06-01 | Note 4 | Note 4 | 0 | 18SP
INF | 2012-AG3-031 | 77409979 | SECI | EES | 200 | 2015-01-01 | 2020-01-01 | 2019-06-01 | 2024-06-01 | Note 4 | Note 4 | 0 | 18SP
KBPU | 2012-AG3-029 | 77155691 | WR | KACY | 2 | 2013-04-01 | 2030-08-01 | 2019-06-01 | 2036-10-01 | 2019-06-01 | 2036-10-01 | 0 | 13SP
KPP | 2012-AG3-024 | 77398979 | WR | WR | 15 | 2013-06-01 | 2023-06-01 | 2019-06-01 | 2029-06-01 | 2019-06-01 | 2029-06-01 | 0 | 13SP
KPP | 2012-AG3-025 | 77405406 | SPA | WR | 1 | 2013-06-01 | 2023-06-01 | 2013-12-01 | 2023-12-01 | 2013-12-01 | 2023-12-01 | 0 | 13SP
KPP | 2012-AG3-026 | 77405413 | KACY | WR | 3 | 2013-06-01 | 2023-06-01 | 2013-12-01 | 2023-12-01 | 2013-12-01 | 2023-12-01 | 0 | 13SP
KPP | 2012-AG3-027 | 77405416 | WR | WR | 9 | 2013-06-01 | 2023-06-01 | 2019-06-01 | 2029-06-01 | 2019-06-01 | 2029-06-01 | 0 | 13SP
KPP | 2012-AG3-028 | 77405426 | WR | WR | 4 | 2013-06-01 | 2015-01-01 | 2019-06-01 | 2021-01-01 | 2019-06-01 | 2021-01-01 | 0 | 13SP
MIDW | 2012-AG3-013 | 77410531 | WR | WR | 28 | 2015-06-01 | 2038-06-01 | 2019-06-01 | 2042-06-01 | 2019-06-01 | 2042-06-01 | 0 | 18SP
NPPM | 2012-AG3-012 | 77407262 | NPPD | NPPD | 115 | 2018-09-01 | 2028-09-01 | 2018-09-01 | 2028-09-01 | Note 4 | Note 4 | 0 | 23SP
SPSM | 2012-AG3-009 | 77341873 | WFEC | SPS | 36 | 2017-06-01 | 2047-06-01 | 2020-01-01 | 2050-01-01 | 2020-01-01 | 2050-01-01 | 0 | 23SP
SPSM | 2012-AG3-010 | 77341881 | WFEC | SPS | 44 | 2017-06-01 | 2047-06-01 | 2020-01-01 | 2050-01-01 | 2020-01-01 | 2050-01-01 | 0 | 23SP
WFEC | 2012-AG3-008 | 77193289 | WFEC | WFEC | 320 | 2017-03-01 | 2042-03-01 | 2019-06-01 | 2044-06-01 | 2019-06-01 | 2044-06-01 | 0 | 23SP
WRGS | 2012-AG3-002 | 77379445 | WR | EES | 50 | 2014-01-01 | 2019-01-01 | 6/1/2019 (Note 3) | 6/1/2024 (Note 3) | 2019-06-01 | 2024-06-01 | 0 | 14SP
WRGS | 2012-AG3-005 | 77409901 | WR | EES | 106 | 2014-01-01 | 2019-01-01 | 6/1/2019 (Note 3) | 6/1/2024 (Note 3) | 2019-06-01 | 2024-06-01 | 0 | 14SP
WRGS | 2012-AG3-006 | 77409994 | SPS | EES | 106 | 2014-01-01 | 2019-01-01 | 6/1/2019 (Note 3) | 6/1/2024 (Note 3) | 2019-06-01 | 2024-06-01 | 0 | 14SP
6435
Note 1: Start and Stop Dates with interim redispatch are determined based on customers choosing option to pursue redispatch to start service at Requested Start and Stop Dates or earliest date possible.
Note 2: Start dates with and without redispatch are based on the assumed completion dates of previous Aggregate Transmission Service Studies currently being conducted. Actual start dates may differ from the potential start dates upon completion of the previous studies.
Note 3: Request is unable to be deferred due to fixed stop dates.
Note 4: Transmission customer did not select “remain in the study using interim redispatch” option.

## Table2
Customer | Study Number | Reservation | Engineering and Construction Cost of Upgrades Allocated to Customer for Revenue Requirements | 1Letter of Credit Amount Required | 2Potential Base Plan Engineering and Construction Funding Allowable | Notes | 4Additional Engineering and Construction Cost for 3rd Party Upgrades | 3 5Total Revenue Requirements for Assigned Upgrades Over Term of Reservation WITH Potential Base Plan Funding Allocation | Point-to-Point Base Rate Over Reservation Period | 4Total Cost of Reservation Assignable to Customer Contingent Upon Base Plan Funding
BPAE | 2012-AG3-070 | 77387381 | 2029377 | 2029377 | 0 |  | Indeterminate | 5458708 | 2631000 | 5458708
BPAE | 2012-AG3-071 | 77387397 | 2029377 | 2029377 | 0 |  | Indeterminate | 5458708 | 2631000 | 5458708
BPAE | 2012-AG3-072 | 77387401 | 1217626 | 1217626 | 0 |  | Indeterminate | 3275224 | 1578600 | 3275224
BPAE | 2012-AG3-073 | 77387415 | 9747137 | 9747137 | 0 | 6,12 | Indeterminate | 28661670 | 5262000 | 28661670
BPAE | 2012-AG3-074 | 77387419 | 9747137 | 9747137 | 0 | 7,12 | Indeterminate | 28661670 | 5262000 | 28661670
BPAE | 2012-AG3-075 | 77387426 | 9747137 | 9747137 | 0 | 6,12 | Indeterminate | 28661670 | 7680000 | 28661670
BPAE | 2012-AG3-076 | 77387430 | 9747137 | 9747137 | 0 | 7,12 | Indeterminate | 28661670 | 7680000 | 28661670
BPAE | 2012-AG3-077 | 77387435 | 9735026 | 9735026 | 0 | 6,12 | Indeterminate | 28653980 | 7680000 | 28653980
BPAE | 2012-AG3-078 | 77387437 | 9735026 | 9735026 | 0 | 7,12 | Indeterminate | 28653980 | 7680000 | 28653980
CCG | 2012-AG3-056 | 76979606 | 4151299 | 4151299 | 0 | 9,12 | Indeterminate | 13729780 | 18731671 | 18731670
CCG | 2012-AG3-057 | 76979671 | 0 | 0 | 0 | 9,12 | 0 | 0 | 18731671 | 18731670
CCG | 2012-AG3-058 | 76979772 | 0 | 0 | 0 | 9,12 | 0 | 0 | 18731671 | 18731670
CRGL | 2012-AG3-047 | 77029025 | 35348462 | 35348462 | 0 | 11,12 | 0 | 116855826.8518 | 23499733 | 116855826.8518
CRGL | 2012-AG3-048 | 77029027 | 45888723 | 45888723 | 0 | 11,12 | 0 | 151327490.527 | 23499733 | 151327490.527
CRGL | 2012-AG3-049 | 77410128 | 44082561 | 44082560 | 0 |  | Indeterminate | 120643300 | 15360000 | 120643300
CRGL | 2012-AG3-050 | 77410129 | 17846525 | 17846520 | 0 |  | Indeterminate | 48745710 | 7756800 | 48745710
CRGL | 2012-AG3-051 | 77410131 | 18665471 | 18665470 | 0 |  | Indeterminate | 50845520 | 7680000 | 50845520
CRGL | 2012-AG3-052 | 77410135 | 3192634 | 3192634 | 0 |  | Indeterminate | 8296409 | 5760000 | 8296409
CRGL | 2012-AG3-054 | 77410157 | 9332613 | 9332613 | 0 |  | Indeterminate | 23572980 | 11520000 | 23572980
ETEC | 2012-AG3-038 | 77410319 | 0 | 0 | 0 |  | 0 | 0 | 0 | Schedule 9 & 11 Charges
ETEC | 2012-AG3-039 | 77410327 | 0 | 0 | 0 |  | 0 | 0 | 0 | Schedule 9 & 11 Charges
ETEC | 2012-AG3-040 | 77410336 | 0 | 0 | 0 |  | 0 | 0 | 0 | Schedule 9 & 11 Charges
ETEC | 2012-AG3-041 | 77410342 | 0 | 0 | 0 |  | 0 | 0 | 0 | Schedule 9 & 11 Charges
ETEC | 2012-AG3-042 | 77410350 | 0 | 0 | 0 |  | 0 | 0 | 0 | Schedule 9 & 11 Charges
ETEC | 2012-AG3-043 | 77410353 | 0 | 0 | 0 |  | 0 | 0 | 0 | Schedule 9 & 11 Charges
ETEC | 2012-AG3-044 | 77410357 | 0 | 0 | 0 |  | Indeterminate | 0 | 0 | Schedule 9 & 11 Charges
ETEC | 2012-AG3-045 | 77410360 | 0 | 0 | 0 |  | 0 | 0 | 0 | Schedule 9 & 11 Charges
ETEC | 2012-AG3-046 | 77410382 | 0 | 0 | 0 |  | 0 | 0 | 0 | Schedule 9 & 11 Charges
GSECGS | 2012-AG3-032 | 77401449 | 21061 | 0 | 21061 |  | 0 | 0 | 0 | Schedule 9 & 11 Charges
GSECGS | 2012-AG3-033 | 77401452 | 21061 | 0 | 21061 |  | 0 | 0 | 0 | Schedule 9 & 11 Charges
GSECGS | 2012-AG3-034 | 77401453 | 21061 | 0 | 21061 |  | 0 | 0 | 0 | Schedule 9 & 11 Charges
GSECGS | 2012-AG3-035 | 77402179 | 1796485 | 1796485 | 0 |  | 0 | 11889820 | 0 | 11889820
GSECGS | 2012-AG3-036 | 77402184 | 1874795 | 1874795 | 0 |  | 0 | 11971120 | 0 | 11971120
INF | 2012-AG3-030 | 77409954 | 8936649 | 8936649 | 0 | 8,12 | Indeterminate | 23985450 | 15360000 | 23985450
INF | 2012-AG3-031 | 77409979 | 8995376 | 8995376 | 0 | 8,12 | Indeterminate | 24136380 | 15360000 | 24136380
KBPU | 2012-AG3-029 | 77155691 | 49477 | 49477 | 0 |  | Indeterminate | 197128 | 364832 | 364832
KPP | 2012-AG3-024 | 77398979 | 3173666 | 707666 | 2466000 |  | Indeterminate | 2114545.9438 | 0 | 2114545.9438
KPP | 2012-AG3-025 | 77405406 | 0 | 0 | 0 |  | 0 | 0 | 0 | Schedule 9 & 11 Charges
KPP | 2012-AG3-026 | 77405413 | 1178583 | 638583 | 540000 |  | 0 | 1301434 | 0 | 1301434
KPP | 2012-AG3-027 | 77405416 | 3337224 | 1861224 | 1476000 |  | 0 | 5667910 | 0 | 5667910
KPP | 2012-AG3-028 | 77405426 | 0 | 0 | 0 |  | 0 | 0 | 0 | Schedule 9 & 11 Charges
MIDW | 2012-AG3-013 | 77410531 | 6946657 | 1906657 | 5040000 |  | Indeterminate | 9323506 | 0 | 9323506
NPPM | 2012-AG3-012 | 77407262 | 1420998 | 0 | 1420998 |  | 0 | 0 | 0 | Schedule 9 & 11 Charges
SPSM | 2012-AG3-009 | 77341873 | 146243 | 0 | 146243 |  | 0 | 0 | 0 | Schedule 9 & 11 Charges
SPSM | 2012-AG3-010 | 77341881 | 96906 | 0 | 96906 |  | 0 | 0 | 0 | Schedule 9 & 11 Charges
WFEC | 2012-AG3-008 | 77193289 | 22059704 | 0 | 22059704 |  | Indeterminate | 0 | 0 | Schedule 9 & 11 Charges
WRGS | 2012-AG3-002 | 77379445 | 6440976 | 6440976 | 0 | 10,12 | Indeterminate | 17694850 | 3840000 | 17694850
WRGS | 2012-AG3-005 | 77409901 | 7457000 | 7457000 | 0 | 10,12 | Indeterminate | 21124740 | 8140800 | 21124740
WRGS | 2012-AG3-006 | 77409994 | 13495436 | 13495440 | 0 | 10,12 | Indeterminate | 37028260 | 8140800 | 37028260
Grand Total |  |  | 329712626 |  | 33309034 |  |  | 886599440.3226
Note 1: Letter of Credit required for financial security for transmission owner for network upgrades is determined by allocated engineering and construction costs less engineering and construction costs for upgrades when network customer is the transmission owner less the E & C allocation of expedited projects. Letter of Credit is required for upgrades assigned to PTP requests. The amount of the letter of credit will be adjusted down on an annual basis to reflect cost recovery based on revenue allocation. This letter of credit is not required for those facilities that are fully base plan funded. The Letter Of Credit Amount listed is based on meeting OATT Attachment J requirements for base plan funding.
Note 2: If potential base plan funding is applicable, this value is the lesser of the Engineering and Construction costs of assignable upgrades or the value of base plan funding calculated pursuant to Attachment J, Section III B criteria. Allocation of base plan funding is contingent upon verification of customer agreements meeting Attachment J, Section II B criteria. Not applicable if Point-to-Point base rate exceeds revenue requirements.
Note 3: Revenue Requirements (RR) are based upon deferred end dates if applicable. Deferred dates are based upon customer's choice to pursue redispatch. Achievable Base Plan Avoided RR in the case of a Base Plan upgrade being displaced or deferred by an earlier in service date for a Requested Upgrade shall be determined per Attachment J, Section VII.C methodology. Assumption of a 40 year service life is utilized for Base Plan funded projects. A present worth analysis of RR on a common year basis between the Base Plan and Requested Upgrades was performed to determine avoided Base Plan RR due to the displacement or deferral of the Base Plan upgrade by the Requested Upgrade. The incremental increase in present worth of a Requested Upgrade on a common year basis as a Base Plan upgrade is assigned to the transmission requests impacting the upgrade based on the displacement or deferral. If the displacement analysis results in lower RR due to the shorter amortization period of the requested upgrade when compared to a base plan amortization period, then no direct assignment of the upgrade cost is made due to the displacement to an earlier start date.
Note 4: For Point-to-Point requests, total cost is based on the higher of the base rate or assigned upgrade revenue requirements. For Network requests, the total cost is based on the assigned upgrade revenue requirement. Allocation of base plan funding will be determined after verification of designated resource meeting Attachment J, Section II B Criteria. Additionally E & C of 3rd Party upgrades is assignable to Customer. This includes prepayments required for any SWPA upgrades. Revenue requirements for 3rd Party facilities are not calculated. Total cost to customer is based on assumption of Revenue Requirements with confirmation of base plan funding. Customer is responsible for negotiating redispatch costs if applicable. Customer is also responsible to pay credits for previously assigned upgrades that are impacted by their request. Credits can be paid from base plan funding if applicable.
Note 5: RR with base plan funding may increase or decrease even if no base plan funding is applicable to a particular request if another request that shares the upgrade is now full base plan funded resulting in a different amortization period for the upgrade and thus different RR.
Note 6: Mutually exclusive with 77387415, 77387426, and 77387435. System impacts were identified by only modeling mutually exclusive request 77387435.
Note 7: Mutually exclusive with77387419, 77387430, and 77387437. System impacts were identified by only modeling mutually exclusive request 77387437.
Note 8: Mutually exclusive with 77409954 and 77409979. System impacts were identified by only modeling mutually exclusive request 77409954.
Note 9: Mutually exclusive with 76979606, 76979671, and 76979772. System impacts were identified by only modeling mutually exclusive request 76979606.
Note 10: Mutually exclusive with 77379445, 77409901, and 77409994. System impacts were identified by only modeling mutually exclusive request 77379445.
Note 11: Mutually exclusive with 77029025 and 77029027. System impacts were identified by only modeling mutually exclusive request 77029025.
Note 12: ATSS cost allocation includes all customers’ mutually exclusive requests in SPP-2012-AG3.

## Table3
Customer | Study Number
BPAE | 2012-AG3-070
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
BPAE | 77387381 | WR | KCPL | 50 | 2014-10-01 | 2019-10-01 | 2019-06-01 | 2024-06-01 | 0 | 2631000 | 2029377 | 5458707.54
[9 empty] | 0 | 2631000 | 2029377 | 5458707.54
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77387381 | 59TH ST - EL PASO 138KV CKT 1 | 2015-06-01 | 2017-06-01 |  | No | 132339 | 5693300 | 409391.25
| 59TH ST - GILL ENERGY CENTER SOUTH 138KV CKT 1 | 2015-06-01 | 2017-06-01 |  | No | 117227 | 5043200 | 362642.226
| GRAND ISLAND - SWEETWATER 345KV CKT 2 | 2013-12-01 | 2019-06-01 |  | No | 1322987 | 96288750 | 3488031.678
| HOLT - NELIGH 345KV CKT 1 | 2013-12-01 | 2019-06-01 |  | No | 348683 | 30656000 | 865348.986
| OKLAUNION 345KV SVC | 2014-10-01 | 2019-06-01 |  | No | 10193 | 18500000 | 32465.85
| SMAN_W_3 115.00 - SOUTH MANHATTAN 115KV CKT 1 | 2015-06-01 | 2016-06-01 |  | No | 97948 | 790000 | 300827.55
[5 empty] | Total | 2029377 | 156971250 | 5458707.54
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77387381 | IATAN - NASHUA 345KV CKT 1 | 2013-12-01 | 2015-06-01 |  | No
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77387381 | Cherry Co - Gentleman 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co - Holt Co 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co 345 kV Terminal Upgrades | 2013-12-01 | 2018-01-01 |  | No
| Neligh - Hoskins 345 kV Ckt1 | 2013-12-01 | 2019-03-01 |  | No
| Neligh 345/115 kV Transformer | 2013-12-01 | 2019-03-01 |  | No
| Viola - Clearwater 138kV Ckt1 | 2014-10-01 | 2018-06-01 |  | No
| Viola - Gill 138kV Ckt1 | 2014-10-01 | 2018-06-01 |  | No
| Viola 345/138kV Transformer Ckt 1 | 2014-10-01 | 2018-06-01 |  | No
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77387381 | BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #1 Accelerate | 2014-06-01 | 2015-06-01
| BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #2 Accelerate | 2014-06-01 | 2017-06-01 |  | No
| BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #1 Accelerate | 2014-06-01 | 2015-06-01
| BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #2 Accelerate | 2014-06-01 | 2016-06-01 |  | No
| CHISHOLM - MAIZE 138KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| CHISHOLM - MAIZE 138KV CKT 1 #2 | 2015-06-01 | 2017-06-01 |  | No
| CIMARRON - DRAPER LAKE 345KV CKT 1 | 2019-10-01 | 2019-10-01
| EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 #2 | 2015-06-01 | 2017-06-01 |  | No
| FLINT CREEK - SILOAM SPRINGS TAP 345KV CKT 1 AEPW | 2019-06-01 | 2019-06-01
| FT SMITH - MUSKOGEE 345KV CKT 1 | 2014-06-01 | 2016-06-01 |  | No
| FT SMITH (FTSMITH1) 500/345/13.8KV TRANSFORMER CKT 1 | 2014-06-01 | 2018-06-01 |  | No
| GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #2 | 2015-06-01 | 2016-06-01 |  | No
| HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 2013-12-01 | 2017-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV KACP | 2013-12-01 | 2019-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV WERE | 2013-12-01 | 2019-06-01 |  | No
| Lacygne - Mariosa 345KV KACP | 2013-12-01 | 2019-06-01 |  | No
| Muskogee - VBI 345 kV with 345/161 kV bus tie near VBI | 2014-06-01 | 2019-06-01 |  | No
| VBI - Arkansas Nuclear One 345kV OKGE | 2014-06-01 | 2019-06-01 |  | No
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77387381 | CIMARRON - DRAPER LAKE 345KV CKT 1 | 2014-10-01 | 2016-06-01
| LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01
Third Party Limitations.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | *Allocated E & C Cost | *Total E & C Cost
77387381 | 7JASPER 345.00 - BLACKBERRY 345KV CKT 1 #1 | 2015-06-01 | 2015-06-01 |  |  | 1966 | 100000
| ARKANSAS NUCLEAR ONE - PLEASANT HILL 500KV CKT 1 | 2014-10-01 | 2014-10-01 |  |  | 0.7769% | 100%
| Arkansas Nuclear One 500/345 Transformer | 2014-06-01 | 2019-06-01 |  | No | 94174 | 12000000
| Lacygne - Mariosa 345KV AMRN | 2013-12-01 | 2019-06-01 |  | No | 3.262% | 100%
| VBI - Arkansas Nuclear One 345kV EES | 2014-06-01 | 2019-06-01 |  | No | 0.7848% | 100%
[5 empty] | Total | 96140 | 12100000
*Estimated cost allocation as a percentage of total cost is shown for third-party limitations when costs have not yet been established by the third-party.
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
BPAE | 2012-AG3-071
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
BPAE | 77387397 | WR | KCPL | 50 | 2014-10-01 | 2019-10-01 | 2019-06-01 | 2024-06-01 | 0 | 2631000 | 2029377 | 5458707.54
[9 empty] | 0 | 2631000 | 2029377 | 5458707.54
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77387397 | 59TH ST - EL PASO 138KV CKT 1 | 2015-06-01 | 2017-06-01 |  | No | 132339 | 5693300 | 409391.25
| 59TH ST - GILL ENERGY CENTER SOUTH 138KV CKT 1 | 2015-06-01 | 2017-06-01 |  | No | 117227 | 5043200 | 362642.226
| GRAND ISLAND - SWEETWATER 345KV CKT 2 | 2013-12-01 | 2019-06-01 |  | No | 1322987 | 96288750 | 3488031.678
| HOLT - NELIGH 345KV CKT 1 | 2013-12-01 | 2019-06-01 |  | No | 348683 | 30656000 | 865348.986
| OKLAUNION 345KV SVC | 2014-10-01 | 2019-06-01 |  | No | 10193 | 18500000 | 32465.85
| SMAN_W_3 115.00 - SOUTH MANHATTAN 115KV CKT 1 | 2015-06-01 | 2016-06-01 |  | No | 97948 | 790000 | 300827.55
[5 empty] | Total | 2029377 | 156971250 | 5458707.54
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77387397 | IATAN - NASHUA 345KV CKT 1 | 2013-12-01 | 2015-06-01 |  | No
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77387397 | Cherry Co - Gentleman 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co - Holt Co 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co 345 kV Terminal Upgrades | 2013-12-01 | 2018-01-01 |  | No
| Neligh - Hoskins 345 kV Ckt1 | 2013-12-01 | 2019-03-01 |  | No
| Neligh 345/115 kV Transformer | 2013-12-01 | 2019-03-01 |  | No
| Viola - Clearwater 138kV Ckt1 | 2014-10-01 | 2018-06-01 |  | No
| Viola - Gill 138kV Ckt1 | 2014-10-01 | 2018-06-01 |  | No
| Viola 345/138kV Transformer Ckt 1 | 2014-10-01 | 2018-06-01 |  | No
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77387397 | BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #1 Accelerate | 2014-06-01 | 2015-06-01
| BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #2 Accelerate | 2014-06-01 | 2017-06-01 |  | No
| BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #1 Accelerate | 2014-06-01 | 2015-06-01
| BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #2 Accelerate | 2014-06-01 | 2016-06-01 |  | No
| CHISHOLM - MAIZE 138KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| CHISHOLM - MAIZE 138KV CKT 1 #2 | 2015-06-01 | 2017-06-01 |  | No
| CIMARRON - DRAPER LAKE 345KV CKT 1 | 2019-10-01 | 2019-10-01
| EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 #2 | 2015-06-01 | 2017-06-01 |  | No
| FLINT CREEK - SILOAM SPRINGS TAP 345KV CKT 1 AEPW | 2019-06-01 | 2019-06-01
| FT SMITH - MUSKOGEE 345KV CKT 1 | 2014-06-01 | 2016-06-01 |  | No
| FT SMITH (FTSMITH1) 500/345/13.8KV TRANSFORMER CKT 1 | 2014-06-01 | 2018-06-01 |  | No
| GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #2 | 2015-06-01 | 2016-06-01 |  | No
| HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 2013-12-01 | 2017-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV KACP | 2013-12-01 | 2019-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV WERE | 2013-12-01 | 2019-06-01 |  | No
| Lacygne - Mariosa 345KV KACP | 2013-12-01 | 2019-06-01 |  | No
| Muskogee - VBI 345 kV with 345/161 kV bus tie near VBI | 2014-06-01 | 2019-06-01 |  | No
| VBI - Arkansas Nuclear One 345kV OKGE | 2014-06-01 | 2019-06-01 |  | No
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77387397 | CIMARRON - DRAPER LAKE 345KV CKT 1 | 2014-10-01 | 2016-06-01
| LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01
Third Party Limitations.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | *Allocated E & C Cost | *Total E & C Cost
77387397 | 7JASPER 345.00 - BLACKBERRY 345KV CKT 1 #1 | 2015-06-01 | 2015-06-01 |  |  | 1966 | 100000
| ARKANSAS NUCLEAR ONE - PLEASANT HILL 500KV CKT 1 | 2014-10-01 | 2014-10-01 |  |  | 0.7769% | 100%
| Arkansas Nuclear One 500/345 Transformer | 2014-06-01 | 2019-06-01 |  | No | 94174 | 12000000
| Lacygne - Mariosa 345KV AMRN | 2013-12-01 | 2019-06-01 |  | No | 3.262% | 100%
| VBI - Arkansas Nuclear One 345kV EES | 2014-06-01 | 2019-06-01 |  | No | 0.7848% | 100%
[5 empty] | Total | 96140 | 12100000
*Estimated cost allocation as a percentage of total cost is shown for third-party limitations when costs have not yet been established by the third-party.
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
BPAE | 2012-AG3-072
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
BPAE | 77387401 | WR | KCPL | 30 | 2014-10-01 | 2019-10-01 | 2019-06-01 | 2024-06-01 | 0 | 1578600 | 1217626 | 3275223.9
[9 empty] | 0 | 1578600 | 1217626 | 3275223.9
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77387401 | 59TH ST - EL PASO 138KV CKT 1 | 2015-06-01 | 2017-06-01 |  | No | 79403 | 5693300 | 245633.526
| 59TH ST - GILL ENERGY CENTER SOUTH 138KV CKT 1 | 2015-06-01 | 2017-06-01 |  | No | 70336 | 5043200 | 217584.72
| GRAND ISLAND - SWEETWATER 345KV CKT 2 | 2013-12-01 | 2019-06-01 |  | No | 793792 | 96288750 | 2092818.474
| HOLT - NELIGH 345KV CKT 1 | 2013-12-01 | 2019-06-01 |  | No | 209210 | 30656000 | 519209.886
| OKLAUNION 345KV SVC | 2014-10-01 | 2019-06-01 |  | No | 6116 | 18500000 | 19480.152
| SMAN_W_3 115.00 - SOUTH MANHATTAN 115KV CKT 1 | 2015-06-01 | 2016-06-01 |  | No | 58769 | 790000 | 180497.142
[5 empty] | Total | 1217626 | 156971250 | 3275223.9
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77387401 | IATAN - NASHUA 345KV CKT 1 | 2013-12-01 | 2015-06-01 |  | No
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77387401 | Cherry Co - Gentleman 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co - Holt Co 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co 345 kV Terminal Upgrades | 2013-12-01 | 2018-01-01 |  | No
| Neligh - Hoskins 345 kV Ckt1 | 2013-12-01 | 2019-03-01 |  | No
| Neligh 345/115 kV Transformer | 2013-12-01 | 2019-03-01 |  | No
| Viola - Clearwater 138kV Ckt1 | 2014-10-01 | 2018-06-01 |  | No
| Viola - Gill 138kV Ckt1 | 2014-10-01 | 2018-06-01 |  | No
| Viola 345/138kV Transformer Ckt 1 | 2014-10-01 | 2018-06-01 |  | No
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77387401 | BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #1 Accelerate | 2014-06-01 | 2015-06-01
| BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #2 Accelerate | 2014-06-01 | 2017-06-01 |  | No
| BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #1 Accelerate | 2014-06-01 | 2015-06-01
| BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #2 Accelerate | 2014-06-01 | 2016-06-01 |  | No
| CHISHOLM - MAIZE 138KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| CHISHOLM - MAIZE 138KV CKT 1 #2 | 2015-06-01 | 2017-06-01 |  | No
| CIMARRON - DRAPER LAKE 345KV CKT 1 | 2019-10-01 | 2019-10-01
| EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 #2 | 2015-06-01 | 2017-06-01 |  | No
| FLINT CREEK - SILOAM SPRINGS TAP 345KV CKT 1 AEPW | 2019-06-01 | 2019-06-01
| FT SMITH - MUSKOGEE 345KV CKT 1 | 2014-06-01 | 2016-06-01 |  | No
| FT SMITH (FTSMITH1) 500/345/13.8KV TRANSFORMER CKT 1 | 2014-06-01 | 2018-06-01 |  | No
| GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #2 | 2015-06-01 | 2016-06-01 |  | No
| HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 2013-12-01 | 2017-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV KACP | 2013-12-01 | 2019-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV WERE | 2013-12-01 | 2019-06-01 |  | No
| Lacygne - Mariosa 345KV KACP | 2013-12-01 | 2019-06-01 |  | No
| Muskogee - VBI 345 kV with 345/161 kV bus tie near VBI | 2014-06-01 | 2019-06-01 |  | No
| VBI - Arkansas Nuclear One 345kV OKGE | 2014-06-01 | 2019-06-01 |  | No
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77387401 | CIMARRON - DRAPER LAKE 345KV CKT 1 | 2014-10-01 | 2016-06-01
| LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01
Third Party Limitations.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | *Allocated E & C Cost | *Total E & C Cost
77387401 | 7JASPER 345.00 - BLACKBERRY 345KV CKT 1 #1 | 2015-06-01 | 2015-06-01 |  |  | 1180 | 100000
| ARKANSAS NUCLEAR ONE - PLEASANT HILL 500KV CKT 1 | 2014-10-01 | 2014-10-01 |  |  | 0.4661% | 100%
| Arkansas Nuclear One 500/345 Transformer | 2014-06-01 | 2019-06-01 |  | No | 56504 | 12000000
| Lacygne - Mariosa 345KV AMRN | 2013-12-01 | 2019-06-01 |  | No | 1.957% | 100%
| VBI - Arkansas Nuclear One 345kV EES | 2014-06-01 | 2019-06-01 |  | No | 0.4709% | 100%
[5 empty] | Total | 57684 | 12100000
*Estimated cost allocation as a percentage of total cost is shown for third-party limitations when costs have not yet been established by the third-party.
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
BPAE | 2012-AG3-073
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
BPAE | 77387415 | SPS | AMRN | 100 | 2014-10-01 | 2019-10-01 | 2019-06-01 | 2024-06-01 | 0 | 5262000 | 9747137 | 28661665.74
[9 empty] | 0 | 5262000 | 9747137 | 28661665.74
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77387415 | 59TH ST - EL PASO 138KV CKT 1 | 2015-06-01 | 2017-06-01 |  | No | 266366 | 5693300 | 824004.354
| 59TH ST - GILL ENERGY CENTER SOUTH 138KV CKT 1 | 2015-06-01 | 2017-06-01 |  | No | 235951 | 5043200 | 729915.426
| Cimarron - Mathewson 345 kV Ckt 1 Accelerate | 2013-12-01 | 2015-06-01 |  | No | 532898 | 10704894 | 1898996.25
| GRAND ISLAND - SWEETWATER 345KV CKT 2 | 2013-12-01 | 2019-06-01 |  | No | 3811385 | 96288750 | 10048648.716
| HOLT - NELIGH 345KV CKT 1 | 2013-12-01 | 2019-06-01 |  | No | 1309918 | 30656000 | 3250907.586
| Mathewson - Tatonga 345 kV Ckt 2 Accelerate | 2013-12-01 | 2015-06-01 |  | No | 1971951 | 26823745 | 7027099.986
| Mathewson 345 kV Accelerate | 2013-12-01 | 2015-06-01 |  | No | 327887 | 6586619 | 1168434.072
| OKLAUNION 345KV SVC | 2014-10-01 | 2019-06-01 |  | No | 384522 | 18500000 | 1224745.824
| SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 MIDW | 2013-12-01 | 2018-06-01 |  | No | 262172 | 13864500 | 613501.506
| SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 WERE | 2013-12-01 | 2018-06-01 |  | No | 644087 | 34061343.75 | 1875412.02
[5 empty] | Total | 9747137 | 248222351.75 | 28661665.74
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77387415 | 5 TRIBES - PECAN CREEK 161KV CKT 1 | 2014-06-01 | 2014-06-01
| HARPER - MILAN TAP 138KV CKT 1 #1 | 2013-12-01 | 2014-12-01 |  | No
| IATAN - NASHUA 345KV CKT 1 | 2013-12-01 | 2015-06-01 |  | No
| Line - Clark County - Thistle 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2014-07-01
| Line - Hitchland - Woodward 345 kV dbl Ckt SPS | 2013-12-01 | 2014-07-01
| Line - Spearville - Clark County 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt WERE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Tuco - Woodward 345 kV line OKGE | 2013-12-01 | 2014-06-01
| Line - Tuco - Woodward 345 kV line SPS | 2013-12-01 | 2014-06-01
| XFR - Thistle 345/138 kV | 2013-12-01 | 2015-01-01 |  | No
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77387415 | Cherry Co - Gentleman 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co - Holt Co 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co 345 kV Terminal Upgrades | 2013-12-01 | 2018-01-01 |  | No
| Elk City 345/230 kV | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV AEPW | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV OKGE | 2013-12-01 | 2018-03-01 |  | No
| HITCHLAND INTERCHANGE () 230/115/13.2KV TRANSFORMER CKT 2 | 2015-06-01 | 2017-06-01 |  | No
| Multi - Centerton - Osage Creek 345 kV | 2014-06-01 | 2016-06-01 |  | No
| Multi - Flint Creek – Centerton 345 kV and Centerton- East Centerton 161 kV | 2014-06-01 | 2014-06-01
| Neligh - Hoskins 345 kV Ckt1 | 2013-12-01 | 2019-03-01 |  | No
| Neligh 345/115 kV Transformer | 2013-12-01 | 2019-03-01 |  | No
| Viola - Clearwater 138kV Ckt1 | 2014-10-01 | 2018-06-01 |  | No
| Viola - Gill 138kV Ckt1 | 2014-10-01 | 2018-06-01 |  | No
| Viola 345/138kV Transformer Ckt 1 | 2014-10-01 | 2018-06-01 |  | No
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77387415 | ADABELL - VBI 161KV CKT 1 | 2014-06-01 | 2016-06-01 |  | No
| BEAVER - EUREKA SPRINGS 161KV CKT 1 AEPW | 2014-06-01 | 2015-06-01 |  | No
| BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #1 Accelerate | 2014-06-01 | 2015-06-01 |  | No
| BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #2 Accelerate | 2014-06-01 | 2017-06-01 |  | No
| BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #1 Accelerate | 2014-06-01 | 2015-06-01 |  | No
| BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #2 Accelerate | 2014-06-01 | 2016-06-01 |  | No
| CHISHOLM - MAIZE 138KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| CHISHOLM - MAIZE 138KV CKT 1 #2 | 2015-06-01 | 2017-06-01 |  | No
| CIMARRON - DRAPER LAKE 345KV CKT 1 | 2019-10-01 | 2019-10-01
| CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | 2013-12-01 | 2017-06-01 |  | No
| CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | 2013-12-01 | 2017-06-01 |  | No
| EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 #2 | 2015-06-01 | 2017-06-01 |  | No
| FLINT CREEK - SILOAM SPRINGS TAP 345KV CKT 1 AEPW | 2019-06-01 | 2019-06-01
| FT SMITH - MUSKOGEE 345KV CKT 1 | 2014-06-01 | 2016-06-01 |  | No
| FT SMITH (FTSMITH1) 500/345/13.8KV TRANSFORMER CKT 1 | 2014-06-01 | 2018-06-01 |  | No
| GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | 2014-01-01 | 2016-06-01 |  | No
| GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #2 | 2015-06-01 | 2016-06-01 |  | No
| HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | 2013-12-01 | 2017-06-01 |  | No
| HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 2013-12-01 | 2017-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV KACP | 2013-12-01 | 2019-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV WERE | 2013-12-01 | 2019-06-01 |  | No
| Lacygne - Mariosa 345KV KACP | 2013-12-01 | 2019-06-01 |  | No
| Muskogee - VBI 345 kV with 345/161 kV bus tie near VBI | 2014-06-01 | 2019-06-01 |  | No
| Potter to Tolk 345 kV | 2013-12-01 | 2019-06-01 |  | No
| VBI - Arkansas Nuclear One 345kV OKGE | 2014-06-01 | 2019-06-01 |  | No
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77387415 | CIMARRON - DRAPER LAKE 345KV CKT 1 | 2014-10-01 | 2016-06-01
| HUGO POWER PLANT - VALLIANT 345 KV AEPW | 2012-07-01 | 2012-07-01
| HUGO POWER PLANT - VALLIANT 345KV CKT 1 WFEC | 2012-07-01 | 2012-07-01
| Mullergren - Reno 345kV Dbl CKT MKEC | 2013-10-01 | 2019-06-01
| Mullergren - Reno 345kV Dbl CKT WERE | 2013-10-01 | 2019-06-01
| NORTHWEST - TATONGA 345KV CKT 1 | 2010-01-01 | 2010-01-01
| Spearville - Mullergren 345kV Dbl CKT | 2013-10-01 | 2019-06-01
| TATONGA - WOODWARD 345KV CKT 1 | 2010-01-01 | 2010-01-01
| WOODWARD - WOODWARD EHV 138KV CKT 1 | 2010-01-01 | 2010-01-01
| WOODWARD 345/138KV TRANSFORMER CKT 1 | 2010-01-01 | 2010-01-01
Third Party Limitations.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | *Allocated E & C Cost | *Total E & C Cost
77387415 | 7JASPER 345.00 - BLACKBERRY 345KV CKT 1 #1 | 2015-06-01 | 2015-06-01 |  |  | 5881 | 100000
| 7OVERTON 345.00 () 345/161/13.8KV TRANSFORMER CKT 1 | 2014-01-01 | 2014-06-01 |  |  | 5.329% | 100%
| ARKANSAS NUCLEAR ONE - PLEASANT HILL 500KV CKT 1 | 2014-10-01 | 2014-10-01 |  |  | 5.944% | 100%
| Arkansas Nuclear One 500/345 Transformer | 2014-06-01 | 2019-06-01 |  | No | 713101 | 12000000
| BEAVER - EUREKA SPRINGS 161KV CKT 1 SWPA | 2014-06-01 | 2015-06-01 |  | No | 0 | 0
| BUFORD 5 161.00 - BULL SHOALS 161KV CKT 1 | 2014-06-01 | 2017-06-01 |  | No | 0 | 0
| BUFORD 5 161.00 - NORFORK 161KV CKT 1 | 2014-06-01 | 2017-06-01 |  | No | 0 | 0
| CLINTON - MONTROSE 161KV CKT 1 AECI | 2015-06-01 | 2016-06-01 |  | No | 10665 | 180000
| Lacygne - Mariosa 345KV AMRN | 2013-12-01 | 2019-06-01 |  | No | 3.604% | 100%
| VBI - Arkansas Nuclear One 345kV EES | 2014-06-01 | 2019-06-01 |  | No | 5.943% | 100%
[5 empty] | Total | 729647 | 12280000
*Estimated cost allocation as a percentage of total cost is shown for third-party limitations when costs have not yet been established by the third-party.
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
BPAE | 2012-AG3-074
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
BPAE | 77387419 | SPS | AMRN | 100 | 2014-10-01 | 2019-10-01 | 2019-06-01 | 2024-06-01 | 0 | 5262000 | 9747137 | 28661665.74
[9 empty] | 0 | 5262000 | 9747137 | 28661665.74
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77387419 | 59TH ST - EL PASO 138KV CKT 1 | 2015-06-01 | 2017-06-01 |  | No | 266366 | 5693300 | 824004.354
| 59TH ST - GILL ENERGY CENTER SOUTH 138KV CKT 1 | 2015-06-01 | 2017-06-01 |  | No | 235951 | 5043200 | 729915.426
| Cimarron - Mathewson 345 kV Ckt 1 Accelerate | 2013-12-01 | 2015-06-01 |  | No | 532898 | 10704894 | 1898996.25
| GRAND ISLAND - SWEETWATER 345KV CKT 2 | 2013-12-01 | 2019-06-01 |  | No | 3811385 | 96288750 | 10048648.716
| HOLT - NELIGH 345KV CKT 1 | 2013-12-01 | 2019-06-01 |  | No | 1309918 | 30656000 | 3250907.586
| Mathewson - Tatonga 345 kV Ckt 2 Accelerate | 2013-12-01 | 2015-06-01 |  | No | 1971951 | 26823745 | 7027099.986
| Mathewson 345 kV Accelerate | 2013-12-01 | 2015-06-01 |  | No | 327887 | 6586619 | 1168434.072
| OKLAUNION 345KV SVC | 2014-10-01 | 2019-06-01 |  | No | 384522 | 18500000 | 1224745.824
| SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 MIDW | 2013-12-01 | 2018-06-01 |  | No | 262172 | 13864500 | 613501.506
| SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 WERE | 2013-12-01 | 2018-06-01 |  | No | 644087 | 34061343.75 | 1875412.02
[5 empty] | Total | 9747137 | 248222351.75 | 28661665.74
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77387419 | 5 TRIBES - PECAN CREEK 161KV CKT 1 | 2014-06-01 | 2014-06-01
| HARPER - MILAN TAP 138KV CKT 1 #1 | 2013-12-01 | 2014-12-01 |  | No
| IATAN - NASHUA 345KV CKT 1 | 2013-12-01 | 2015-06-01 |  | No
| Line - Clark County - Thistle 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2014-07-01
| Line - Hitchland - Woodward 345 kV dbl Ckt SPS | 2013-12-01 | 2014-07-01
| Line - Spearville - Clark County 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt WERE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Tuco - Woodward 345 kV line OKGE | 2013-12-01 | 2014-06-01
| Line - Tuco - Woodward 345 kV line SPS | 2013-12-01 | 2014-06-01
| XFR - Thistle 345/138 kV | 2013-12-01 | 2015-01-01 |  | No
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77387419 | Cherry Co - Gentleman 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co - Holt Co 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co 345 kV Terminal Upgrades | 2013-12-01 | 2018-01-01 |  | No
| Elk City 345/230 kV | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV AEPW | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV OKGE | 2013-12-01 | 2018-03-01 |  | No
| HITCHLAND INTERCHANGE () 230/115/13.2KV TRANSFORMER CKT 2 | 2015-06-01 | 2017-06-01 |  | No
| Multi - Centerton - Osage Creek 345 kV | 2014-06-01 | 2016-06-01 |  | No
| Multi - Flint Creek – Centerton 345 kV and Centerton- East Centerton 161 kV | 2014-06-01 | 2014-06-01
| Neligh - Hoskins 345 kV Ckt1 | 2013-12-01 | 2019-03-01 |  | No
| Neligh 345/115 kV Transformer | 2013-12-01 | 2019-03-01 |  | No
| Viola - Clearwater 138kV Ckt1 | 2014-10-01 | 2018-06-01 |  | No
| Viola - Gill 138kV Ckt1 | 2014-10-01 | 2018-06-01 |  | No
| Viola 345/138kV Transformer Ckt 1 | 2014-10-01 | 2018-06-01 |  | No
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77387419 | ADABELL - VBI 161KV CKT 1 | 2014-06-01 | 2016-06-01 |  | No
| BEAVER - EUREKA SPRINGS 161KV CKT 1 AEPW | 2014-06-01 | 2015-06-01 |  | No
| BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #1 Accelerate | 2014-06-01 | 2015-06-01 |  | No
| BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #2 Accelerate | 2014-06-01 | 2017-06-01 |  | No
| BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #1 Accelerate | 2014-06-01 | 2015-06-01 |  | No
| BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #2 Accelerate | 2014-06-01 | 2016-06-01 |  | No
| CHISHOLM - MAIZE 138KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| CHISHOLM - MAIZE 138KV CKT 1 #2 | 2015-06-01 | 2017-06-01 |  | No
| CIMARRON - DRAPER LAKE 345KV CKT 1 | 2019-10-01 | 2019-10-01
| CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | 2013-12-01 | 2017-06-01 |  | No
| CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | 2013-12-01 | 2017-06-01 |  | No
| EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 #2 | 2015-06-01 | 2017-06-01 |  | No
| FLINT CREEK - SILOAM SPRINGS TAP 345KV CKT 1 AEPW | 2019-06-01 | 2019-06-01
| FT SMITH - MUSKOGEE 345KV CKT 1 | 2014-06-01 | 2016-06-01 |  | No
| FT SMITH (FTSMITH1) 500/345/13.8KV TRANSFORMER CKT 1 | 2014-06-01 | 2018-06-01 |  | No
| GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | 2014-01-01 | 2016-06-01 |  | No
| GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #2 | 2015-06-01 | 2016-06-01 |  | No
| HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | 2013-12-01 | 2017-06-01 |  | No
| HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 2013-12-01 | 2017-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV KACP | 2013-12-01 | 2019-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV WERE | 2013-12-01 | 2019-06-01 |  | No
| Lacygne - Mariosa 345KV KACP | 2013-12-01 | 2019-06-01 |  | No
| Muskogee - VBI 345 kV with 345/161 kV bus tie near VBI | 2014-06-01 | 2019-06-01 |  | No
| Potter to Tolk 345 kV | 2013-12-01 | 2019-06-01 |  | No
| VBI - Arkansas Nuclear One 345kV OKGE | 2014-06-01 | 2019-06-01 |  | No
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77387419 | CIMARRON - DRAPER LAKE 345KV CKT 1 | 2014-10-01 | 2016-06-01
| HUGO POWER PLANT - VALLIANT 345 KV AEPW | 2012-07-01 | 2012-07-01
| HUGO POWER PLANT - VALLIANT 345KV CKT 1 WFEC | 2012-07-01 | 2012-07-01
| Mullergren - Reno 345kV Dbl CKT MKEC | 2013-10-01 | 2019-06-01
| Mullergren - Reno 345kV Dbl CKT WERE | 2013-10-01 | 2019-06-01
| NORTHWEST - TATONGA 345KV CKT 1 | 2010-01-01 | 2010-01-01
| Spearville - Mullergren 345kV Dbl CKT | 2013-10-01 | 2019-06-01
| TATONGA - WOODWARD 345KV CKT 1 | 2010-01-01 | 2010-01-01
| WOODWARD - WOODWARD EHV 138KV CKT 1 | 2010-01-01 | 2010-01-01
| WOODWARD 345/138KV TRANSFORMER CKT 1 | 2010-01-01 | 2010-01-01
Third Party Limitations.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | *Allocated E & C Cost | *Total E & C Cost
77387419 | 7JASPER 345.00 - BLACKBERRY 345KV CKT 1 #1 | 2015-06-01 | 2015-06-01 |  |  | 5881 | 100000
| 7OVERTON 345.00 () 345/161/13.8KV TRANSFORMER CKT 1 | 2014-01-01 | 2014-06-01 |  |  | 5.329% | 100%
| ARKANSAS NUCLEAR ONE - PLEASANT HILL 500KV CKT 1 | 2014-10-01 | 2014-10-01 |  |  | 5.944% | 100%
| Arkansas Nuclear One 500/345 Transformer | 2014-06-01 | 2019-06-01 |  | No | 713101 | 12000000
| BEAVER - EUREKA SPRINGS 161KV CKT 1 SWPA | 2014-06-01 | 2015-06-01 |  | No | 0 | 0
| BUFORD 5 161.00 - BULL SHOALS 161KV CKT 1 | 2014-06-01 | 2017-06-01 |  | No | 0 | 0
| BUFORD 5 161.00 - NORFORK 161KV CKT 1 | 2014-06-01 | 2017-06-01 |  | No | 0 | 0
| CLINTON - MONTROSE 161KV CKT 1 AECI | 2015-06-01 | 2016-06-01 |  | No | 10665 | 180000
| Lacygne - Mariosa 345KV AMRN | 2013-12-01 | 2019-06-01 |  | No | 3.604% | 100%
| VBI - Arkansas Nuclear One 345kV EES | 2014-06-01 | 2019-06-01 |  | No | 5.943% | 100%
[5 empty] | Total | 729647 | 12280000
*Estimated cost allocation as a percentage of total cost is shown for third-party limitations when costs have not yet been established by the third-party.
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
BPAE | 2012-AG3-075
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
BPAE | 77387426 | SPS | EES | 100 | 2014-10-01 | 2019-10-01 | 2019-06-01 | 2024-06-01 | 0 | 7680000 | 9747137 | 28661665.74
[9 empty] | 0 | 7680000 | 9747137 | 28661665.74
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77387426 | 59TH ST - EL PASO 138KV CKT 1 | 2015-06-01 | 2017-06-01 |  | No | 266366 | 5693300 | 824004.354
| 59TH ST - GILL ENERGY CENTER SOUTH 138KV CKT 1 | 2015-06-01 | 2017-06-01 |  | No | 235951 | 5043200 | 729915.426
| Cimarron - Mathewson 345 kV Ckt 1 Accelerate | 2013-12-01 | 2015-06-01 |  | No | 532898 | 10704894 | 1898996.25
| GRAND ISLAND - SWEETWATER 345KV CKT 2 | 2013-12-01 | 2019-06-01 |  | No | 3811385 | 96288750 | 10048648.716
| HOLT - NELIGH 345KV CKT 1 | 2013-12-01 | 2019-06-01 |  | No | 1309918 | 30656000 | 3250907.586
| Mathewson - Tatonga 345 kV Ckt 2 Accelerate | 2013-12-01 | 2015-06-01 |  | No | 1971951 | 26823745 | 7027099.986
| Mathewson 345 kV Accelerate | 2013-12-01 | 2015-06-01 |  | No | 327887 | 6586619 | 1168434.072
| OKLAUNION 345KV SVC | 2014-10-01 | 2019-06-01 |  | No | 384522 | 18500000 | 1224745.824
| SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 MIDW | 2013-12-01 | 2018-06-01 |  | No | 262172 | 13864500 | 613501.506
| SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 WERE | 2013-12-01 | 2018-06-01 |  | No | 644087 | 34061343.75 | 1875412.02
[5 empty] | Total | 9747137 | 248222351.75 | 28661665.74
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77387426 | 5 TRIBES - PECAN CREEK 161KV CKT 1 | 2014-06-01 | 2014-06-01
| HARPER - MILAN TAP 138KV CKT 1 #1 | 2013-12-01 | 2014-12-01 |  | No
| IATAN - NASHUA 345KV CKT 1 | 2013-12-01 | 2015-06-01 |  | No
| Line - Clark County - Thistle 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2014-07-01
| Line - Hitchland - Woodward 345 kV dbl Ckt SPS | 2013-12-01 | 2014-07-01
| Line - Spearville - Clark County 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt WERE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Tuco - Woodward 345 kV line OKGE | 2013-12-01 | 2014-06-01
| Line - Tuco - Woodward 345 kV line SPS | 2013-12-01 | 2014-06-01
| XFR - Thistle 345/138 kV | 2013-12-01 | 2015-01-01 |  | No
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77387426 | Cherry Co - Gentleman 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co - Holt Co 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co 345 kV Terminal Upgrades | 2013-12-01 | 2018-01-01 |  | No
| Elk City 345/230 kV | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV AEPW | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV OKGE | 2013-12-01 | 2018-03-01 |  | No
| HITCHLAND INTERCHANGE () 230/115/13.2KV TRANSFORMER CKT 2 | 2015-06-01 | 2017-06-01 |  | No
| Multi - Centerton - Osage Creek 345 kV | 2014-06-01 | 2016-06-01 |  | No
| Multi - Flint Creek – Centerton 345 kV and Centerton- East Centerton 161 kV | 2014-06-01 | 2014-06-01
| Neligh - Hoskins 345 kV Ckt1 | 2013-12-01 | 2019-03-01 |  | No
| Neligh 345/115 kV Transformer | 2013-12-01 | 2019-03-01 |  | No
| Viola - Clearwater 138kV Ckt1 | 2014-10-01 | 2018-06-01 |  | No
| Viola - Gill 138kV Ckt1 | 2014-10-01 | 2018-06-01 |  | No
| Viola 345/138kV Transformer Ckt 1 | 2014-10-01 | 2018-06-01 |  | No
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77387426 | ADABELL - VBI 161KV CKT 1 | 2014-06-01 | 2016-06-01 |  | No
| BEAVER - EUREKA SPRINGS 161KV CKT 1 AEPW | 2014-06-01 | 2015-06-01 |  | No
| BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #1 Accelerate | 2014-06-01 | 2015-06-01 |  | No
| BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #2 Accelerate | 2014-06-01 | 2017-06-01 |  | No
| BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #1 Accelerate | 2014-06-01 | 2015-06-01 |  | No
| BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #2 Accelerate | 2014-06-01 | 2016-06-01 |  | No
| CHISHOLM - MAIZE 138KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| CHISHOLM - MAIZE 138KV CKT 1 #2 | 2015-06-01 | 2017-06-01 |  | No
| CIMARRON - DRAPER LAKE 345KV CKT 1 | 2019-10-01 | 2019-10-01
| CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | 2013-12-01 | 2017-06-01 |  | No
| CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | 2013-12-01 | 2017-06-01 |  | No
| EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 #2 | 2015-06-01 | 2017-06-01 |  | No
| FLINT CREEK - SILOAM SPRINGS TAP 345KV CKT 1 AEPW | 2019-06-01 | 2019-06-01
| FT SMITH - MUSKOGEE 345KV CKT 1 | 2014-06-01 | 2016-06-01 |  | No
| FT SMITH (FTSMITH1) 500/345/13.8KV TRANSFORMER CKT 1 | 2014-06-01 | 2018-06-01 |  | No
| GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | 2014-01-01 | 2016-06-01 |  | No
| GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #2 | 2015-06-01 | 2016-06-01 |  | No
| HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | 2013-12-01 | 2017-06-01 |  | No
| HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 2013-12-01 | 2017-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV KACP | 2013-12-01 | 2019-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV WERE | 2013-12-01 | 2019-06-01 |  | No
| Lacygne - Mariosa 345KV KACP | 2013-12-01 | 2019-06-01 |  | No
| Muskogee - VBI 345 kV with 345/161 kV bus tie near VBI | 2014-06-01 | 2019-06-01 |  | No
| Potter to Tolk 345 kV | 2013-12-01 | 2019-06-01 |  | No
| VBI - Arkansas Nuclear One 345kV OKGE | 2014-06-01 | 2019-06-01 |  | No
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77387426 | CIMARRON - DRAPER LAKE 345KV CKT 1 | 2014-10-01 | 2016-06-01
| HUGO POWER PLANT - VALLIANT 345 KV AEPW | 2012-07-01 | 2012-07-01
| HUGO POWER PLANT - VALLIANT 345KV CKT 1 WFEC | 2012-07-01 | 2012-07-01
| Mullergren - Reno 345kV Dbl CKT MKEC | 2013-10-01 | 2019-06-01
| Mullergren - Reno 345kV Dbl CKT WERE | 2013-10-01 | 2019-06-01
| NORTHWEST - TATONGA 345KV CKT 1 | 2010-01-01 | 2010-01-01
| Spearville - Mullergren 345kV Dbl CKT | 2013-10-01 | 2019-06-01
| TATONGA - WOODWARD 345KV CKT 1 | 2010-01-01 | 2010-01-01
| WOODWARD - WOODWARD EHV 138KV CKT 1 | 2010-01-01 | 2010-01-01
| WOODWARD 345/138KV TRANSFORMER CKT 1 | 2010-01-01 | 2010-01-01
Third Party Limitations.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | *Allocated E & C Cost | *Total E & C Cost
77387426 | 7JASPER 345.00 - BLACKBERRY 345KV CKT 1 #1 | 2015-06-01 | 2015-06-01 |  |  | 5881 | 100000
| 7OVERTON 345.00 () 345/161/13.8KV TRANSFORMER CKT 1 | 2014-01-01 | 2014-06-01 |  |  | 5.329% | 100%
| ARKANSAS NUCLEAR ONE - PLEASANT HILL 500KV CKT 1 | 2014-10-01 | 2014-10-01 |  |  | 5.944% | 100%
| Arkansas Nuclear One 500/345 Transformer | 2014-06-01 | 2019-06-01 |  | No | 713101 | 12000000
| BEAVER - EUREKA SPRINGS 161KV CKT 1 SWPA | 2014-06-01 | 2015-06-01 |  | No | 0 | 0
| BUFORD 5 161.00 - BULL SHOALS 161KV CKT 1 | 2014-06-01 | 2017-06-01 |  | No | 0 | 0
| BUFORD 5 161.00 - NORFORK 161KV CKT 1 | 2014-06-01 | 2017-06-01 |  | No | 0 | 0
| CLINTON - MONTROSE 161KV CKT 1 AECI | 2015-06-01 | 2016-06-01 |  | No | 10665 | 180000
| Lacygne - Mariosa 345KV AMRN | 2013-12-01 | 2019-06-01 |  | No | 3.604% | 100%
| VBI - Arkansas Nuclear One 345kV EES | 2014-06-01 | 2019-06-01 |  | No | 5.943% | 100%
[5 empty] | Total | 729647 | 12280000
*Estimated cost allocation as a percentage of total cost is shown for third-party limitations when costs have not yet been established by the third-party.
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
BPAE | 2012-AG3-076
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
BPAE | 77387430 | SPS | EES | 100 | 2014-10-01 | 2019-10-01 | 2019-06-01 | 2024-06-01 | 0 | 7680000 | 9747137 | 28661665.74
[9 empty] | 0 | 7680000 | 9747137 | 28661665.74
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77387430 | 59TH ST - EL PASO 138KV CKT 1 | 2015-06-01 | 2017-06-01 |  | No | 266366 | 5693300 | 824004.354
| 59TH ST - GILL ENERGY CENTER SOUTH 138KV CKT 1 | 2015-06-01 | 2017-06-01 |  | No | 235951 | 5043200 | 729915.426
| Cimarron - Mathewson 345 kV Ckt 1 Accelerate | 2013-12-01 | 2015-06-01 |  | No | 532898 | 10704894 | 1898996.25
| GRAND ISLAND - SWEETWATER 345KV CKT 2 | 2013-12-01 | 2019-06-01 |  | No | 3811385 | 96288750 | 10048648.716
| HOLT - NELIGH 345KV CKT 1 | 2013-12-01 | 2019-06-01 |  | No | 1309918 | 30656000 | 3250907.586
| Mathewson - Tatonga 345 kV Ckt 2 Accelerate | 2013-12-01 | 2015-06-01 |  | No | 1971951 | 26823745 | 7027099.986
| Mathewson 345 kV Accelerate | 2013-12-01 | 2015-06-01 |  | No | 327887 | 6586619 | 1168434.072
| OKLAUNION 345KV SVC | 2014-10-01 | 2019-06-01 |  | No | 384522 | 18500000 | 1224745.824
| SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 MIDW | 2013-12-01 | 2018-06-01 |  | No | 262172 | 13864500 | 613501.506
| SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 WERE | 2013-12-01 | 2018-06-01 |  | No | 644087 | 34061343.75 | 1875412.02
[5 empty] | Total | 9747137 | 248222351.75 | 28661665.74
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77387430 | 5 TRIBES - PECAN CREEK 161KV CKT 1 | 2014-06-01 | 2014-06-01
| HARPER - MILAN TAP 138KV CKT 1 #1 | 2013-12-01 | 2014-12-01 |  | No
| IATAN - NASHUA 345KV CKT 1 | 2013-12-01 | 2015-06-01 |  | No
| Line - Clark County - Thistle 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2014-07-01
| Line - Hitchland - Woodward 345 kV dbl Ckt SPS | 2013-12-01 | 2014-07-01
| Line - Spearville - Clark County 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt WERE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Tuco - Woodward 345 kV line OKGE | 2013-12-01 | 2014-06-01
| Line - Tuco - Woodward 345 kV line SPS | 2013-12-01 | 2014-06-01
| XFR - Thistle 345/138 kV | 2013-12-01 | 2015-01-01 |  | No
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77387430 | Cherry Co - Gentleman 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co - Holt Co 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co 345 kV Terminal Upgrades | 2013-12-01 | 2018-01-01 |  | No
| Elk City 345/230 kV | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV AEPW | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV OKGE | 2013-12-01 | 2018-03-01 |  | No
| HITCHLAND INTERCHANGE () 230/115/13.2KV TRANSFORMER CKT 2 | 2015-06-01 | 2017-06-01 |  | No
| Multi - Centerton - Osage Creek 345 kV | 2014-06-01 | 2016-06-01 |  | No
| Multi - Flint Creek – Centerton 345 kV and Centerton- East Centerton 161 kV | 2014-06-01 | 2014-06-01
| Neligh - Hoskins 345 kV Ckt1 | 2013-12-01 | 2019-03-01 |  | No
| Neligh 345/115 kV Transformer | 2013-12-01 | 2019-03-01 |  | No
| Viola - Clearwater 138kV Ckt1 | 2014-10-01 | 2018-06-01 |  | No
| Viola - Gill 138kV Ckt1 | 2014-10-01 | 2018-06-01 |  | No
| Viola 345/138kV Transformer Ckt 1 | 2014-10-01 | 2018-06-01 |  | No
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77387430 | ADABELL - VBI 161KV CKT 1 | 2014-06-01 | 2016-06-01 |  | No
| BEAVER - EUREKA SPRINGS 161KV CKT 1 AEPW | 2014-06-01 | 2015-06-01 |  | No
| BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #1 Accelerate | 2014-06-01 | 2015-06-01 |  | No
| BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #2 Accelerate | 2014-06-01 | 2017-06-01 |  | No
| BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #1 Accelerate | 2014-06-01 | 2015-06-01 |  | No
| BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #2 Accelerate | 2014-06-01 | 2016-06-01 |  | No
| CHISHOLM - MAIZE 138KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| CHISHOLM - MAIZE 138KV CKT 1 #2 | 2015-06-01 | 2017-06-01 |  | No
| CIMARRON - DRAPER LAKE 345KV CKT 1 | 2019-10-01 | 2019-10-01
| CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | 2013-12-01 | 2017-06-01 |  | No
| CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | 2013-12-01 | 2017-06-01 |  | No
| EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 #2 | 2015-06-01 | 2017-06-01 |  | No
| FLINT CREEK - SILOAM SPRINGS TAP 345KV CKT 1 AEPW | 2019-06-01 | 2019-06-01
| FT SMITH - MUSKOGEE 345KV CKT 1 | 2014-06-01 | 2016-06-01 |  | No
| FT SMITH (FTSMITH1) 500/345/13.8KV TRANSFORMER CKT 1 | 2014-06-01 | 2018-06-01 |  | No
| GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | 2014-01-01 | 2016-06-01 |  | No
| GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #2 | 2015-06-01 | 2016-06-01 |  | No
| HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | 2013-12-01 | 2017-06-01 |  | No
| HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 2013-12-01 | 2017-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV KACP | 2013-12-01 | 2019-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV WERE | 2013-12-01 | 2019-06-01 |  | No
| Lacygne - Mariosa 345KV KACP | 2013-12-01 | 2019-06-01 |  | No
| Muskogee - VBI 345 kV with 345/161 kV bus tie near VBI | 2014-06-01 | 2019-06-01 |  | No
| Potter to Tolk 345 kV | 2013-12-01 | 2019-06-01 |  | No
| VBI - Arkansas Nuclear One 345kV OKGE | 2014-06-01 | 2019-06-01 |  | No
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77387430 | CIMARRON - DRAPER LAKE 345KV CKT 1 | 2014-10-01 | 2016-06-01
| HUGO POWER PLANT - VALLIANT 345 KV AEPW | 2012-07-01 | 2012-07-01
| HUGO POWER PLANT - VALLIANT 345KV CKT 1 WFEC | 2012-07-01 | 2012-07-01
| Mullergren - Reno 345kV Dbl CKT MKEC | 2013-10-01 | 2019-06-01
| Mullergren - Reno 345kV Dbl CKT WERE | 2013-10-01 | 2019-06-01
| NORTHWEST - TATONGA 345KV CKT 1 | 2010-01-01 | 2010-01-01
| Spearville - Mullergren 345kV Dbl CKT | 2013-10-01 | 2019-06-01
| TATONGA - WOODWARD 345KV CKT 1 | 2010-01-01 | 2010-01-01
| WOODWARD - WOODWARD EHV 138KV CKT 1 | 2010-01-01 | 2010-01-01
| WOODWARD 345/138KV TRANSFORMER CKT 1 | 2010-01-01 | 2010-01-01
Third Party Limitations.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | *Allocated E & C Cost | *Total E & C Cost
77387430 | 7JASPER 345.00 - BLACKBERRY 345KV CKT 1 #1 | 2015-06-01 | 2015-06-01 |  |  | 5881 | 100000
| 7OVERTON 345.00 () 345/161/13.8KV TRANSFORMER CKT 1 | 2014-01-01 | 2014-06-01 |  |  | 5.329% | 100%
| ARKANSAS NUCLEAR ONE - PLEASANT HILL 500KV CKT 1 | 2014-10-01 | 2014-10-01 |  |  | 5.944% | 100%
| Arkansas Nuclear One 500/345 Transformer | 2014-06-01 | 2019-06-01 |  | No | 713101 | 12000000
| BEAVER - EUREKA SPRINGS 161KV CKT 1 SWPA | 2014-06-01 | 2015-06-01 |  | No | 0 | 0
| BUFORD 5 161.00 - BULL SHOALS 161KV CKT 1 | 2014-06-01 | 2017-06-01 |  | No | 0 | 0
| BUFORD 5 161.00 - NORFORK 161KV CKT 1 | 2014-06-01 | 2017-06-01 |  | No | 0 | 0
| CLINTON - MONTROSE 161KV CKT 1 AECI | 2015-06-01 | 2016-06-01 |  | No | 10665 | 180000
| Lacygne - Mariosa 345KV AMRN | 2013-12-01 | 2019-06-01 |  | No | 3.604% | 100%
| VBI - Arkansas Nuclear One 345kV EES | 2014-06-01 | 2019-06-01 |  | No | 5.943% | 100%
[5 empty] | Total | 729647 | 12280000
*Estimated cost allocation as a percentage of total cost is shown for third-party limitations when costs have not yet been established by the third-party.
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
BPAE | 2012-AG3-077
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
BPAE | 77387435 | SPS | EES | 100 | 2014-10-01 | 2019-10-01 | 2019-06-01 | 2024-06-01 | 0 | 7680000 | 9735026 | 28653981.51
[9 empty] | 0 | 7680000 | 9735026 | 28653981.51
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77387435 | 59TH ST - EL PASO 138KV CKT 1 | 2015-06-01 | 2017-06-01 |  | No | 266085 | 5693300 | 823135.08
| 59TH ST - GILL ENERGY CENTER SOUTH 138KV CKT 1 | 2015-06-01 | 2017-06-01 |  | No | 235701 | 5043200 | 729142.056
| Cimarron - Mathewson 345 kV Ckt 1 Accelerate | 2013-12-01 | 2015-06-01 |  | No | 542581 | 10704894 | 1933501.866
| GRAND ISLAND - SWEETWATER 345KV CKT 2 | 2013-12-01 | 2019-06-01 |  | No | 3787356 | 96288750 | 9985296.69
| HOLT - NELIGH 345KV CKT 1 | 2013-12-01 | 2019-06-01 |  | No | 1303321 | 30656000 | 3234535.404
| Mathewson - Tatonga 345 kV Ckt 2 Accelerate | 2013-12-01 | 2015-06-01 |  | No | 1980562 | 26823745 | 7057785.522
| Mathewson 345 kV Accelerate | 2013-12-01 | 2015-06-01 |  | No | 333845 | 6586619 | 1189665.552
| OKLAUNION 345KV SVC | 2014-10-01 | 2019-06-01 |  | No | 388072 | 18500000 | 1236052.968
| SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 MIDW | 2013-12-01 | 2018-06-01 |  | No | 259639 | 13864500 | 607574.106
| SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 WERE | 2013-12-01 | 2018-06-01 |  | No | 637864 | 34061343.75 | 1857292.266
[5 empty] | Total | 9735026 | 248222351.75 | 28653981.51
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77387435 | 5 TRIBES - PECAN CREEK 161KV CKT 1 | 2014-06-01 | 2014-06-01
| HARPER - MILAN TAP 138KV CKT 1 #1 | 2013-12-01 | 2014-12-01 |  | No
| IATAN - NASHUA 345KV CKT 1 | 2013-12-01 | 2015-06-01 |  | No
| Line - Clark County - Thistle 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2014-07-01
| Line - Hitchland - Woodward 345 kV dbl Ckt SPS | 2013-12-01 | 2014-07-01
| Line - Spearville - Clark County 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt WERE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Tuco - Woodward 345 kV line OKGE | 2013-12-01 | 2014-06-01
| Line - Tuco - Woodward 345 kV line SPS | 2013-12-01 | 2014-06-01
| XFR - Thistle 345/138 kV | 2013-12-01 | 2015-01-01 |  | No
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77387435 | Cherry Co - Gentleman 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co - Holt Co 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co 345 kV Terminal Upgrades | 2013-12-01 | 2018-01-01 |  | No
| Elk City 345/230 kV | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV AEPW | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV OKGE | 2013-12-01 | 2018-03-01 |  | No
| HITCHLAND INTERCHANGE () 230/115/13.2KV TRANSFORMER CKT 2 | 2015-06-01 | 2017-06-01 |  | No
| Multi - Centerton - Osage Creek 345 kV | 2014-06-01 | 2016-06-01 |  | No
| Multi - Flint Creek – Centerton 345 kV and Centerton- East Centerton 161 kV | 2014-06-01 | 2014-06-01
| Neligh - Hoskins 345 kV Ckt1 | 2013-12-01 | 2019-03-01 |  | No
| Neligh 345/115 kV Transformer | 2013-12-01 | 2019-03-01 |  | No
| Viola - Clearwater 138kV Ckt1 | 2014-10-01 | 2018-06-01 |  | No
| Viola - Gill 138kV Ckt1 | 2014-10-01 | 2018-06-01 |  | No
| Viola 345/138kV Transformer Ckt 1 | 2014-10-01 | 2018-06-01 |  | No
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77387435 | ADABELL - VBI 161KV CKT 1 | 2014-06-01 | 2016-06-01 |  | No
| BEAVER - EUREKA SPRINGS 161KV CKT 1 AEPW | 2014-06-01 | 2015-06-01 |  | No
| BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #1 Accelerate | 2014-06-01 | 2015-06-01 |  | No
| BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #2 Accelerate | 2014-06-01 | 2017-06-01 |  | No
| BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #1 Accelerate | 2014-06-01 | 2015-06-01 |  | No
| BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #2 Accelerate | 2014-06-01 | 2016-06-01 |  | No
| CHISHOLM - MAIZE 138KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| CHISHOLM - MAIZE 138KV CKT 1 #2 | 2015-06-01 | 2017-06-01 |  | No
| CIMARRON - DRAPER LAKE 345KV CKT 1 | 2019-10-01 | 2019-10-01
| CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | 2013-12-01 | 2017-06-01 |  | No
| CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | 2013-12-01 | 2017-06-01 |  | No
| EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 #2 | 2015-06-01 | 2017-06-01 |  | No
| FLINT CREEK - SILOAM SPRINGS TAP 345KV CKT 1 AEPW | 2019-06-01 | 2019-06-01
| FT SMITH - MUSKOGEE 345KV CKT 1 | 2014-06-01 | 2016-06-01 |  | No
| FT SMITH (FTSMITH1) 500/345/13.8KV TRANSFORMER CKT 1 | 2014-06-01 | 2018-06-01 |  | No
| GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | 2014-01-01 | 2016-06-01 |  | No
| GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #2 | 2015-06-01 | 2016-06-01 |  | No
| HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | 2013-12-01 | 2017-06-01 |  | No
| HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 2013-12-01 | 2017-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV KACP | 2013-12-01 | 2019-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV WERE | 2013-12-01 | 2019-06-01 |  | No
| Lacygne - Mariosa 345KV KACP | 2013-12-01 | 2019-06-01 |  | No
| Muskogee - VBI 345 kV with 345/161 kV bus tie near VBI | 2014-06-01 | 2019-06-01 |  | No
| Potter to Tolk 345 kV | 2013-12-01 | 2019-06-01 |  | No
| VBI - Arkansas Nuclear One 345kV OKGE | 2014-06-01 | 2019-06-01 |  | No
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77387435 | CIMARRON - DRAPER LAKE 345KV CKT 1 | 2014-10-01 | 2016-06-01
| HUGO POWER PLANT - VALLIANT 345 KV AEPW | 2012-07-01 | 2012-07-01
| HUGO POWER PLANT - VALLIANT 345KV CKT 1 WFEC | 2012-07-01 | 2012-07-01
| Mullergren - Reno 345kV Dbl CKT MKEC | 2013-10-01 | 2019-06-01
| Mullergren - Reno 345kV Dbl CKT WERE | 2013-10-01 | 2019-06-01
| NORTHWEST - TATONGA 345KV CKT 1 | 2010-01-01 | 2010-01-01
| Spearville - Mullergren 345kV Dbl CKT | 2013-10-01 | 2019-06-01
| TATONGA - WOODWARD 345KV CKT 1 | 2010-01-01 | 2010-01-01
| WOODWARD - WOODWARD EHV 138KV CKT 1 | 2010-01-01 | 2010-01-01
| WOODWARD 345/138KV TRANSFORMER CKT 1 | 2010-01-01 | 2010-01-01
Third Party Limitations.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | *Allocated E & C Cost | *Total E & C Cost
77387435 | 7JASPER 345.00 - BLACKBERRY 345KV CKT 1 #1 | 2015-06-01 | 2015-06-01 |  |  | 5630 | 100000
| 7OVERTON 345.00 () 345/161/13.8KV TRANSFORMER CKT 1 | 2014-01-01 | 2014-06-01 |  |  | 5.126% | 100%
| ARKANSAS NUCLEAR ONE - PLEASANT HILL 500KV CKT 1 | 2014-10-01 | 2014-10-01 |  |  | 5.945% | 100%
| Arkansas Nuclear One 500/345 Transformer | 2014-06-01 | 2019-06-01 |  | No | 715830 | 12000000
| BEAVER - EUREKA SPRINGS 161KV CKT 1 SWPA | 2014-06-01 | 2015-06-01 |  | No | 0 | 0
| BUFORD 5 161.00 - BULL SHOALS 161KV CKT 1 | 2014-06-01 | 2017-06-01 |  | No | 0 | 0
| BUFORD 5 161.00 - NORFORK 161KV CKT 1 | 2014-06-01 | 2017-06-01 |  | No | 0 | 0
| CLINTON - MONTROSE 161KV CKT 1 AECI | 2015-06-01 | 2016-06-01 |  | No | 10309 | 180000
| Lacygne - Mariosa 345KV AMRN | 2013-12-01 | 2019-06-01 |  | No | 3.553% | 100%
| NORTH SLIDELL - SLIDELL 230KV CKT 1 CELE | 2015-10-01 | 2015-10-01 |  |  | 9.879% | 100%
| NORTH SLIDELL - SLIDELL 230KV CKT 1 EES | 2015-10-01 | 2015-10-01 |  |  | 9.879% | 100%
| VBI - Arkansas Nuclear One 345kV EES | 2014-06-01 | 2019-06-01 |  | No | 5.965% | 100%
[5 empty] | Total | 731769 | 12280000
*Estimated cost allocation as a percentage of total cost is shown for third-party limitations when costs have not yet been established by the third-party.
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
BPAE | 2012-AG3-078
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
BPAE | 77387437 | SPS | EES | 100 | 2014-10-01 | 2019-10-01 | 2019-06-01 | 2024-06-01 | 0 | 7680000 | 9735026 | 28653981.51
[9 empty] | 0 | 7680000 | 9735026 | 28653981.51
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77387437 | 59TH ST - EL PASO 138KV CKT 1 | 2015-06-01 | 2017-06-01 |  | No | 266085 | 5693300 | 823135.08
| 59TH ST - GILL ENERGY CENTER SOUTH 138KV CKT 1 | 2015-06-01 | 2017-06-01 |  | No | 235701 | 5043200 | 729142.056
| Cimarron - Mathewson 345 kV Ckt 1 Accelerate | 2013-12-01 | 2015-06-01 |  | No | 542581 | 10704894 | 1933501.866
| GRAND ISLAND - SWEETWATER 345KV CKT 2 | 2013-12-01 | 2019-06-01 |  | No | 3787356 | 96288750 | 9985296.69
| HOLT - NELIGH 345KV CKT 1 | 2013-12-01 | 2019-06-01 |  | No | 1303321 | 30656000 | 3234535.404
| Mathewson - Tatonga 345 kV Ckt 2 Accelerate | 2013-12-01 | 2015-06-01 |  | No | 1980562 | 26823745 | 7057785.522
| Mathewson 345 kV Accelerate | 2013-12-01 | 2015-06-01 |  | No | 333845 | 6586619 | 1189665.552
| OKLAUNION 345KV SVC | 2014-10-01 | 2019-06-01 |  | No | 388072 | 18500000 | 1236052.968
| SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 MIDW | 2013-12-01 | 2018-06-01 |  | No | 259639 | 13864500 | 607574.106
| SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 WERE | 2013-12-01 | 2018-06-01 |  | No | 637864 | 34061343.75 | 1857292.266
[5 empty] | Total | 9735026 | 248222351.75 | 28653981.51
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77387437 | 5 TRIBES - PECAN CREEK 161KV CKT 1 | 2014-06-01 | 2014-06-01
| HARPER - MILAN TAP 138KV CKT 1 #1 | 2013-12-01 | 2014-12-01 |  | No
| IATAN - NASHUA 345KV CKT 1 | 2013-12-01 | 2015-06-01 |  | No
| Line - Clark County - Thistle 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2014-07-01
| Line - Hitchland - Woodward 345 kV dbl Ckt SPS | 2013-12-01 | 2014-07-01
| Line - Spearville - Clark County 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt WERE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Tuco - Woodward 345 kV line OKGE | 2013-12-01 | 2014-06-01
| Line - Tuco - Woodward 345 kV line SPS | 2013-12-01 | 2014-06-01
| XFR - Thistle 345/138 kV | 2013-12-01 | 2015-01-01 |  | No
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77387437 | Cherry Co - Gentleman 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co - Holt Co 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co 345 kV Terminal Upgrades | 2013-12-01 | 2018-01-01 |  | No
| Elk City 345/230 kV | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV AEPW | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV OKGE | 2013-12-01 | 2018-03-01 |  | No
| HITCHLAND INTERCHANGE () 230/115/13.2KV TRANSFORMER CKT 2 | 2015-06-01 | 2017-06-01 |  | No
| Multi - Centerton - Osage Creek 345 kV | 2014-06-01 | 2016-06-01 |  | No
| Multi - Flint Creek – Centerton 345 kV and Centerton- East Centerton 161 kV | 2014-06-01 | 2014-06-01
| Neligh - Hoskins 345 kV Ckt1 | 2013-12-01 | 2019-03-01 |  | No
| Neligh 345/115 kV Transformer | 2013-12-01 | 2019-03-01 |  | No
| Viola - Clearwater 138kV Ckt1 | 2014-10-01 | 2018-06-01 |  | No
| Viola - Gill 138kV Ckt1 | 2014-10-01 | 2018-06-01 |  | No
| Viola 345/138kV Transformer Ckt 1 | 2014-10-01 | 2018-06-01 |  | No
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77387437 | ADABELL - VBI 161KV CKT 1 | 2014-06-01 | 2016-06-01 |  | No
| BEAVER - EUREKA SPRINGS 161KV CKT 1 AEPW | 2014-06-01 | 2015-06-01 |  | No
| BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #1 Accelerate | 2014-06-01 | 2015-06-01 |  | No
| BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #2 Accelerate | 2014-06-01 | 2017-06-01 |  | No
| BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #1 Accelerate | 2014-06-01 | 2015-06-01 |  | No
| BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #2 Accelerate | 2014-06-01 | 2016-06-01 |  | No
| CHISHOLM - MAIZE 138KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| CHISHOLM - MAIZE 138KV CKT 1 #2 | 2015-06-01 | 2017-06-01 |  | No
| CIMARRON - DRAPER LAKE 345KV CKT 1 | 2019-10-01 | 2019-10-01
| CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | 2013-12-01 | 2017-06-01 |  | No
| CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | 2013-12-01 | 2017-06-01 |  | No
| EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 #2 | 2015-06-01 | 2017-06-01 |  | No
| FLINT CREEK - SILOAM SPRINGS TAP 345KV CKT 1 AEPW | 2019-06-01 | 2019-06-01
| FT SMITH - MUSKOGEE 345KV CKT 1 | 2014-06-01 | 2016-06-01 |  | No
| FT SMITH (FTSMITH1) 500/345/13.8KV TRANSFORMER CKT 1 | 2014-06-01 | 2018-06-01 |  | No
| GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | 2014-01-01 | 2016-06-01 |  | No
| GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #2 | 2015-06-01 | 2016-06-01 |  | No
| HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | 2013-12-01 | 2017-06-01 |  | No
| HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 2013-12-01 | 2017-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV KACP | 2013-12-01 | 2019-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV WERE | 2013-12-01 | 2019-06-01 |  | No
| Lacygne - Mariosa 345KV KACP | 2013-12-01 | 2019-06-01 |  | No
| Muskogee - VBI 345 kV with 345/161 kV bus tie near VBI | 2014-06-01 | 2019-06-01 |  | No
| Potter to Tolk 345 kV | 2013-12-01 | 2019-06-01 |  | No
| VBI - Arkansas Nuclear One 345kV OKGE | 2014-06-01 | 2019-06-01 |  | No
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77387437 | CIMARRON - DRAPER LAKE 345KV CKT 1 | 2014-10-01 | 2016-06-01
| HUGO POWER PLANT - VALLIANT 345 KV AEPW | 2012-07-01 | 2012-07-01
| HUGO POWER PLANT - VALLIANT 345KV CKT 1 WFEC | 2012-07-01 | 2012-07-01
| Mullergren - Reno 345kV Dbl CKT MKEC | 2013-10-01 | 2019-06-01
| Mullergren - Reno 345kV Dbl CKT WERE | 2013-10-01 | 2019-06-01
| NORTHWEST - TATONGA 345KV CKT 1 | 2010-01-01 | 2010-01-01
| Spearville - Mullergren 345kV Dbl CKT | 2013-10-01 | 2019-06-01
| TATONGA - WOODWARD 345KV CKT 1 | 2010-01-01 | 2010-01-01
| WOODWARD - WOODWARD EHV 138KV CKT 1 | 2010-01-01 | 2010-01-01
| WOODWARD 345/138KV TRANSFORMER CKT 1 | 2010-01-01 | 2010-01-01
Third Party Limitations.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | *Allocated E & C Cost | *Total E & C Cost
77387437 | 7JASPER 345.00 - BLACKBERRY 345KV CKT 1 #1 | 2015-06-01 | 2015-06-01 |  |  | 5630 | 100000
| 7OVERTON 345.00 () 345/161/13.8KV TRANSFORMER CKT 1 | 2014-01-01 | 2014-06-01 |  |  | 5.126% | 100%
| ARKANSAS NUCLEAR ONE - PLEASANT HILL 500KV CKT 1 | 2014-10-01 | 2014-10-01 |  |  | 5.945% | 100%
| Arkansas Nuclear One 500/345 Transformer | 2014-06-01 | 2019-06-01 |  | No | 715830 | 12000000
| BEAVER - EUREKA SPRINGS 161KV CKT 1 SWPA | 2014-06-01 | 2015-06-01 |  | No | 0 | 0
| BUFORD 5 161.00 - BULL SHOALS 161KV CKT 1 | 2014-06-01 | 2017-06-01 |  | No | 0 | 0
| BUFORD 5 161.00 - NORFORK 161KV CKT 1 | 2014-06-01 | 2017-06-01 |  | No | 0 | 0
| CLINTON - MONTROSE 161KV CKT 1 AECI | 2015-06-01 | 2016-06-01 |  | No | 10309 | 180000
| Lacygne - Mariosa 345KV AMRN | 2013-12-01 | 2019-06-01 |  | No | 3.553% | 100%
| NORTH SLIDELL - SLIDELL 230KV CKT 1 CELE | 2015-10-01 | 2015-10-01 |  |  | 9.879% | 100%
| NORTH SLIDELL - SLIDELL 230KV CKT 1 EES | 2015-10-01 | 2015-10-01 |  |  | 9.879% | 100%
| VBI - Arkansas Nuclear One 345kV EES | 2014-06-01 | 2019-06-01 |  | No | 5.965% | 100%
[5 empty] | Total | 731769 | 12280000
*Estimated cost allocation as a percentage of total cost is shown for third-party limitations when costs have not yet been established by the third-party.
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
CCG | 2012-AG3-056
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
CCG | 76979606 | CSWS | ERCOTN | 198 | 2013-06-01 | 2018-06-01 | 2019-06-01 | 2024-06-01 | 0 | 18731671 | 4151299 | 13729780.08
[9 empty] | 0 | 18731671 | 4151299 | 13729780.08
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
76979606 | Cimarron - Mathewson 345 kV Ckt 1 Accelerate | 2013-12-01 | 2015-06-01 |  | No | 830146 | 10704894 | 2958247.416
| Mathewson 345 kV Accelerate | 2013-12-01 | 2015-06-01 |  | No | 510781 | 6586619 | 1820181.732
| OKLAUNION 345KV SVC | 2014-10-01 | 2019-06-01 |  | No | 2810372 | 18500000 | 8951350.932
[5 empty] | Total | 4151299 | 35791513 | 13729780.08
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
76979606 | Arcadia 345 kV Terminal Upgrades | 2013-12-01 | 2013-12-01
| Line - Clark County - Thistle 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2014-07-01 |  | No
| Line - Hitchland - Woodward 345 kV dbl Ckt SPS | 2013-12-01 | 2014-07-01 |  | No
| Line - Spearville - Clark County 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt WERE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Tuco - Woodward 345 kV line OKGE | 2013-12-01 | 2014-06-01 |  | No
| Line - Tuco - Woodward 345 kV line SPS | 2013-12-01 | 2014-06-01 |  | No
| XFR - Thistle 345/138 kV | 2013-12-01 | 2015-01-01 |  | No
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
76979606 | BLUEBELL - PRATTVILLE 138KV CKT 1 | 2013-12-01 | 2015-06-01 |  | No
| Cherry Co - Gentleman 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co - Holt Co 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co 345 kV Terminal Upgrades | 2013-12-01 | 2018-01-01 |  | No
| Elk City 345/230 kV | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV AEPW | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV OKGE | 2013-12-01 | 2018-03-01 |  | No
| HITCHLAND INTERCHANGE () 230/115/13.2KV TRANSFORMER CKT 2 | 2015-06-01 | 2017-06-01 |  | No
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
76979606 | ADABELL - VBI 161KV CKT 1 | 2014-06-01 | 2016-06-01 |  | No
| FLINT CREEK - SILOAM SPRINGS TAP 345KV CKT 1 AEPW | 2019-06-01 | 2019-06-01
| FT SMITH - MUSKOGEE 345KV CKT 1 | 2014-06-01 | 2016-06-01 |  | No
| FT SMITH (FTSMITH1) 500/345/13.8KV TRANSFORMER CKT 1 | 2014-06-01 | 2018-06-01 |  | No
| GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #2 | 2015-06-01 | 2016-06-01 |  | No
| Muskogee - VBI 345 kV with 345/161 kV bus tie near VBI | 2014-06-01 | 2019-06-01 |  | No
| Potter to Tolk 345 kV | 2013-12-01 | 2019-06-01 |  | No
| SOUTHWESTERN STATION - WASHITA 138KV CKT 2 | 2013-12-01 | 2017-06-01 |  | No
| VBI - Arkansas Nuclear One 345kV OKGE | 2014-06-01 | 2019-06-01 |  | No
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
76979606 | BEELINE - EXPLORER GLENPOOL TAP 138KV CKT 1 | 2009-06-01 | 2009-06-01
| CIMARRON - DRAPER LAKE 345KV CKT 1 | 2014-10-01 | 2016-06-01
| EXPLORER GLENPOOL TAP - RIVERSIDE STATION 138KV CKT 1 AEPW | 2009-06-01 | 2009-06-01
| EXPLORER GLENPOOL TAP - RIVERSIDE STATION 138KV CKT 1 OKGE | 2009-06-01 | 2009-06-01
| HUGO POWER PLANT - VALLIANT 345 KV AEPW | 2012-07-01 | 2012-07-01
| HUGO POWER PLANT - VALLIANT 345KV CKT 1 WFEC | 2012-07-01 | 2012-07-01
| NORTHWEST - TATONGA 345KV CKT 1 | 2010-01-01 | 2010-01-01
| TATONGA - WOODWARD 345KV CKT 1 | 2010-01-01 | 2010-01-01
Potential reservation deferral and redispatch requirement on the following upgrades due to positive MW Impact on limitations that require upgrade. No cost assignment due to negative MW impact on defined upgrade.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
76979606 | Mathewson - Tatonga 345 kV Ckt 2 Accelerate | 2013-12-01 | 2015-06-01 |  | No
Third Party Limitations.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | *Allocated E & C Cost | *Total E & C Cost
76979606 | 7JASPER 345.00 - BLACKBERRY 345KV CKT 1 #1 | 2015-06-01 | 2015-06-01 |  |  | 2018 | 100000
| ARKANSAS NUCLEAR ONE - PLEASANT HILL 500KV CKT 1 | 2014-10-01 | 2014-10-01 |  |  | 3.155% | 100%
| Arkansas Nuclear One 500/345 Transformer | 2014-06-01 | 2019-06-01 |  | No | 403360 | 12000000
| VBI - Arkansas Nuclear One 345kV EES | 2014-06-01 | 2019-06-01 |  | No | 3.361% | 100%
[5 empty] | Total | 405378 | 12100000
*Estimated cost allocation as a percentage of total cost is shown for third-party limitations when costs have not yet been established by the third-party.
*Credits may be required for applicable generation interconnection network upgrades.
*The North DC Tie is derated to 210mw indefinately.
*The NORTH DC tie is scheduled for an outage beginning 12/1/2013 until 3/31/2014 to refurbish the facility.
*198 MW of available ERCOT North to South capacity without consideration of prior queued STUDY requests in active Aggregate Transmission Service Studies.
Available capacity will be allocated on a first come first served basis in accordance with Attachment Z1 III.b. of SPP OATT.
Customer | Study Number
CCG | 2012-AG3-057
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
CCG | 76979671 | ERCOTN | ERCOTN | 198 | 2014-05-01 | 2019-05-01 |  |  | 0 | 18731671 | 0 | 0
[9 empty] | 0 | 18731671 | 0 | 0
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
76979671 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
*Credits may be required for applicable generation interconnection network upgrades.
*The North DC Tie is derated to 210mw indefinately.
*The NORTH DC tie is scheduled for an outage beginning 12/1/2013 until 3/31/2014 to refurbish the facility.
*198 MW of available ERCOT North to South capacity without consideration of prior queued STUDY requests in active Aggregate Transmission Service Studies.
Available capacity will be allocated on a first come first served basis in accordance with Attachment Z1 III.b. of SPP OATT.
Customer | Study Number
CCG | 2012-AG3-058
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
CCG | 76979772 | ERCOTN | ERCOTN | 198 | 2015-05-01 | 2020-05-01 |  |  | 0 | 18731671 | 0 | 0
[9 empty] | 0 | 18731671 | 0 | 0
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
76979772 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
*Credits may be required for applicable generation interconnection network upgrades.
*The North DC Tie is derated to 210mw indefinately.
*The NORTH DC tie is scheduled for an outage beginning 12/1/2013 until 3/31/2014 to refurbish the facility.
*198 MW of available ERCOT North to South capacity without consideration of prior queued STUDY requests in active Aggregate Transmission Service Studies.
Available capacity will be allocated on a first come first served basis in accordance with Attachment Z1 III.b. of SPP OATT.
Customer | Study Number
CRGL | 2012-AG3-047
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
CRGL | 77029025 | WFEC | ERCOTN | 207 | 2014-01-01 | 2020-01-01 | 2019-06-01 | 2025-06-01 | 0 | 23499733 | 35348462 | 116855826.8518
[9 empty] | 0 | 23499733 | 35348462 | 116855826.8518
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77029025 | Cimarron - Mathewson 345 kV Ckt 1 Accelerate | 2013-12-01 | 2015-06-01 |  | No | 18248 | 10704894 | 67903.4376
| ERCOT North HVDC Tie Expansion | 2014-01-01 | 2019-06-01 |  | No | 32500000 | 65000000 | 107501958.1558
| FLETCHER - MARLOW JCT 69KV CKT 1 | 2019-06-01 | 2019-06-01 |  |  | 92302 | 225000 | 224988.264
| Mathewson 345 kV Accelerate | 2013-12-01 | 2015-06-01 |  | No | 11228 | 6586619 | 41781.0168
| OKLAUNION 345KV SVC | 2014-10-01 | 2019-06-01 |  | No | 2726684 | 18500000 | 9019195.9776
[5 empty] | Total | 35348462 | 101016513 | 116855826.8518
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77029025 | Line - Clark County - Thistle 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2014-07-01 |  | No
| Line - Hitchland - Woodward 345 kV dbl Ckt SPS | 2013-12-01 | 2014-07-01 |  | No
| Line - Spearville - Clark County 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt WERE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Tuco - Woodward 345 kV line OKGE | 2013-12-01 | 2014-06-01 |  | No
| Line - Tuco - Woodward 345 kV line SPS | 2013-12-01 | 2014-06-01 |  | No
| XFR - Thistle 345/138 kV | 2013-12-01 | 2015-01-01 |  | No
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77029025 | Cherry Co - Gentleman 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co - Holt Co 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co 345 kV Terminal Upgrades | 2013-12-01 | 2018-01-01 |  | No
| Elk City 345/230 kV | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV AEPW | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV OKGE | 2013-12-01 | 2018-03-01 |  | No
| HITCHLAND INTERCHANGE () 230/115/13.2KV TRANSFORMER CKT 2 | 2015-06-01 | 2017-06-01 |  | No
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77029025 | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | 2014-01-01 | 2016-06-01 |  | No
| Potter to Tolk 345 kV | 2013-12-01 | 2019-06-01 |  | No
| SOUTHWESTERN STATION - WASHITA 138KV CKT 2 | 2013-12-01 | 2017-06-01 |  | No
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77029025 | APACHE CO 138.00 - PARADISE 138KV CKT 1 | 2010-06-01 | 2013-06-01
| NORTHWEST - TATONGA 345KV CKT 1 | 2010-01-01 | 2010-01-01
| TATONGA - WOODWARD 345KV CKT 1 | 2010-01-01 | 2010-01-01
| WOODWARD - WOODWARD EHV 138KV CKT 1 | 2010-01-01 | 2010-01-01
| WOODWARD - WOODWARD EHV 138KV CKT 2 | 2010-01-01 | 2010-01-01
| WOODWARD 345/138KV TRANSFORMER CKT 1 | 2010-01-01 | 2010-01-01
Potential reservation deferral and redispatch requirement on the following upgrades due to positive MW Impact on limitations that require upgrade. No cost assignment due to negative MW impact on defined upgrade.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77029025 | Mathewson - Tatonga 345 kV Ckt 2 Accelerate | 2013-12-01 | 2015-06-01 |  | No
*Credits may be required for applicable generation interconnection network upgrades.
*The North DC Tie is derated to 210mw indefinately.
*The NORTH DC tie is scheduled for an outage beginning 12/1/2013 until 3/31/2014 to refurbish the facility.
*198 MW of available ERCOT North to South capacity without consideration of prior queued STUDY requests in active Aggregate Transmission Service Studies.
Available capacity will be allocated on a first come first served basis in accordance with Attachment Z1 III.b. of SPP OATT.
Customer | Study Number
CRGL | 2012-AG3-048
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
CRGL | 77029027 | SPS | ERCOTN | 207 | 2014-01-01 | 2020-01-01 | 2019-06-01 | 2025-06-01 | 0 | 23499733 | 45888723 | 151327490.527
[9 empty] | 0 | 23499733 | 45888723 | 151327490.527
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77029027 | Cimarron - Mathewson 345 kV Ckt 1 Accelerate | 2013-12-01 | 2015-06-01 |  |  | 1224085 | 10704894 | 4554996.7968
| ERCOT North HVDC Tie Expansion | 2014-01-01 | 2019-06-01 |  | No | 32500000 | 65000000 | 107501958.1558
| GRAND ISLAND - SWEETWATER 345KV CKT 2 | 2013-12-01 | 2019-06-01 |  | No | 2068046 | 96288750 | 5620755.7008
| HOLT - NELIGH 345KV CKT 1 | 2013-12-01 | 2019-06-01 |  | No | 688611 | 30656000 | 1761749.4312
| Mathewson - Tatonga 345 kV Ckt 2 Accelerate | 2013-12-01 | 2015-06-01 |  |  | 2201663 | 26823745 | 8192705.4936
| Mathewson 345 kV Accelerate | 2013-12-01 | 2015-06-01 |  |  | 753168 | 6586619 | 2802646.7424
| OKLAUNION 345KV SVC | 2014-10-01 | 2019-06-01 |  | No | 5473631 | 18500000 | 18105416.9352
| SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 MIDW | 2013-12-01 | 2018-06-01 |  | No | 283366 | 13864500 | 684870.3432
| SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 WERE | 2013-12-01 | 2018-06-01 |  | No | 696153 | 34061343.75 | 2102390.928
[5 empty] | Total | 45888723 | 302485851.75 | 151327490.527
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77029027 | Line - Clark County - Thistle 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2014-07-01 |  | No
| Line - Hitchland - Woodward 345 kV dbl Ckt SPS | 2013-12-01 | 2014-07-01 |  | No
| Line - Spearville - Clark County 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt WERE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Tuco - Woodward 345 kV line OKGE | 2013-12-01 | 2014-06-01 |  | No
| Line - Tuco - Woodward 345 kV line SPS | 2013-12-01 | 2014-06-01 |  | No
| LUBBOCK SOUTH INTERCHANGE 230/115/13.2KV TRANSFORMER CKT 2 | 2013-12-01 | 2014-12-31
| XFR - Thistle 345/138 kV | 2013-12-01 | 2015-01-01 |  | No
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77029027 | Cherry Co - Gentleman 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co - Holt Co 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co 345 kV Terminal Upgrades | 2013-12-01 | 2018-01-01 |  | No
| Elk City 345/230 kV | 2013-12-01 | 2018-03-01
| Elk City to Gracemont 345kV AEPW | 2013-12-01 | 2018-03-01
| Elk City to Gracemont 345kV OKGE | 2013-12-01 | 2018-03-01
| Neligh - Hoskins 345 kV Ckt1 | 2013-12-01 | 2019-03-01 |  | No
| Neligh 345/115 kV Transformer | 2013-12-01 | 2019-03-01 |  | No
| OXY PERMIAN SUB - SANGER SWITCHING STATION 115KV CKT 1 | 2015-06-01 | 2015-06-01
| Viola - Clearwater 138kV Ckt1 | 2014-10-01 | 2018-06-01 |  | No
| Viola - Gill 138kV Ckt1 | 2014-10-01 | 2018-06-01 |  | No
| Viola 345/138kV Transformer Ckt 1 | 2014-10-01 | 2018-06-01 |  | No
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77029027 | CIMARRON - DRAPER LAKE 345KV CKT 1 | 2019-10-01 | 2019-10-01
| Potter to Tolk 345 kV | 2013-12-01 | 2019-06-01
| SOUTHWESTERN STATION - WASHITA 138KV CKT 2 | 2013-12-01 | 2017-06-01 |  | No
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77029027 | CHERRY6 230.00 - Harrington Station East Bus 230KV CKT 1 | 2015-06-01 | 2015-06-01
| HUGO POWER PLANT - VALLIANT 345 KV AEPW | 2012-07-01 | 2012-07-01
| HUGO POWER PLANT - VALLIANT 345KV CKT 1 WFEC | 2012-07-01 | 2012-07-01
| NORTHWEST - TATONGA 345KV CKT 1 | 2010-01-01 | 2010-01-01
| TATONGA - WOODWARD 345KV CKT 1 | 2010-01-01 | 2010-01-01
| WOODWARD - WOODWARD EHV 138KV CKT 1 | 2010-01-01 | 2010-01-01
| WOODWARD 345/138KV TRANSFORMER CKT 1 | 2010-01-01 | 2010-01-01
*Credits may be required for applicable generation interconnection network upgrades.
*The North DC Tie is derated to 210mw indefinately.
*The NORTH DC tie is scheduled for an outage beginning 12/1/2013 until 3/31/2014 to refurbish the facility.
*198 MW of available ERCOT North to South capacity without consideration of prior queued STUDY requests in active Aggregate Transmission Service Studies.
Available capacity will be allocated on a first come first served basis in accordance with Attachment Z1 III.b. of SPP OATT.
Customer | Study Number
CRGL | 2012-AG3-049
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
CRGL | 77410128 | WR | EES | 200 | 2014-01-01 | 2019-01-01 | 2019-06-01 | 2024-06-01 | 0 | 15360000 | 44082561 | 120643335.534
[9 empty] | 0 | 15360000 | 44082561 | 120643335.534
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77410128 | 59TH ST - EL PASO 138KV CKT 1 | 2015-06-01 | 2017-06-01 |  | No | 703117 | 5693300 | 2175095.43
| 59TH ST - GILL ENERGY CENTER SOUTH 138KV CKT 1 | 2015-06-01 | 2017-06-01 |  | No | 622830 | 5043200 | 1926727.254
| Cimarron - Mathewson 345 kV Ckt 1 Accelerate | 2013-12-01 | 2015-06-01 |  | No | 648196 | 10704894 | 2309863.74
| GRAND ISLAND - SWEETWATER 345KV CKT 2 | 2013-12-01 | 2019-06-01 |  | No | 17463612 | 96288750 | 46042502.226
| HOLT - NELIGH 345KV CKT 1 | 2013-12-01 | 2019-06-01 |  | No | 4735493 | 30656000 | 11752376.976
| Mathewson - Tatonga 345 kV Ckt 2 Accelerate | 2013-12-01 | 2015-06-01 |  | No | 1502496 | 26823745 | 5354184.582
| Mathewson 345 kV Accelerate | 2013-12-01 | 2015-06-01 |  | No | 398829 | 6586619 | 1421237.79
| OKLAUNION 345KV SVC | 2014-10-01 | 2019-06-01 |  | No | 302712 | 18500000 | 964171.776
| SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 MIDW | 2013-12-01 | 2018-06-01 |  | No | 5082808 | 13864500 | 11894139.576
| SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 WERE | 2013-12-01 | 2018-06-01 |  | No | 12487091 | 34061343.75 | 36359126.034
| ST JOHN - ST_JOHN 115KV CKT 1 MIDW | 2013-12-01 | 2016-06-01 |  | No | 60168 | 450000 | 145529.688
| ST JOHN - ST_JOHN 115KV CKT 1 MKEC | 2013-12-01 | 2016-06-01 |  | No | 75209 | 562500 | 298380.462
[5 empty] | Total | 44082561 | 249234851.75 | 120643335.534
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77410128 | HARPER - MILAN TAP 138KV CKT 1 #1 | 2013-12-01 | 2014-12-01 |  | No
| HAYS PLANT - SOUTH HAYS 115KV CKT 1 #2 | 2014-01-01 | 2015-06-01 |  | No
| IATAN - NASHUA 345KV CKT 1 | 2013-12-01 | 2015-06-01 |  | No
| Line - Clark County - Thistle 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2014-07-01 |  | No
| Line - Hitchland - Woodward 345 kV dbl Ckt SPS | 2013-12-01 | 2014-07-01 |  | No
| Line - Spearville - Clark County 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt WERE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Tuco - Woodward 345 kV line OKGE | 2013-12-01 | 2014-06-01 |  | No
| Line - Tuco - Woodward 345 kV line SPS | 2013-12-01 | 2014-06-01 |  | No
| MOUNDRIDGE 138/115KV TRANSFORMER CKT 2 | 2013-12-01 | 2014-12-01 |  | No
| NORTHWEST TEXARKANA - VALLIANT 345KV CKT 1 | 2014-06-01 | 2015-05-01 |  | No
| XFR - Thistle 345/138 kV | 2013-12-01 | 2015-01-01 |  | No
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77410128 | Cherry Co - Gentleman 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co - Holt Co 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co 345 kV Terminal Upgrades | 2013-12-01 | 2018-01-01 |  | No
| Elk City 345/230 kV | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV AEPW | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV OKGE | 2013-12-01 | 2018-03-01 |  | No
| Multi - Centerton - Osage Creek 345 kV | 2014-06-01 | 2016-06-01 |  | No
| Multi - Flint Creek – Centerton 345 kV and Centerton- East Centerton 161 kV | 2014-06-01 | 2014-06-01
| Neligh - Hoskins 345 kV Ckt1 | 2013-12-01 | 2019-03-01 |  | No
| Neligh 345/115 kV Transformer | 2013-12-01 | 2019-03-01 |  | No
| Viola - Clearwater 138kV Ckt1 | 2014-10-01 | 2018-06-01 |  | No
| Viola - Gill 138kV Ckt1 | 2014-10-01 | 2018-06-01 |  | No
| Viola 345/138kV Transformer Ckt 1 | 2014-10-01 | 2018-06-01 |  | No
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77410128 | ADABELL - VBI 161KV CKT 1 | 2014-06-01 | 2016-06-01 |  | No
| BEAVER - EUREKA SPRINGS 161KV CKT 1 AEPW | 2014-06-01 | 2015-06-01 |  | No
| CHISHOLM - MAIZE 138KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| CHISHOLM - MAIZE 138KV CKT 1 #2 | 2015-06-01 | 2017-06-01 |  | No
| CIMARRON - DRAPER LAKE 345KV CKT 1 | 2019-10-01 | 2019-10-01
| CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | 2013-12-01 | 2017-06-01 |  | No
| CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | 2013-12-01 | 2017-06-01 |  | No
| EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 #2 | 2015-06-01 | 2017-06-01 |  | No
| FLINT CREEK - SILOAM SPRINGS TAP 345KV CKT 1 AEPW | 2019-06-01 | 2019-06-01
| FT SMITH - MUSKOGEE 345KV CKT 1 | 2014-06-01 | 2016-06-01 |  | No
| FT SMITH (FTSMITH1) 500/345/13.8KV TRANSFORMER CKT 1 | 2014-06-01 | 2018-06-01 |  | No
| GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #2 | 2015-06-01 | 2016-06-01 |  | No
| HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | 2013-12-01 | 2017-06-01 |  | No
| HAYS PLANT - VINE STREET 115KV CKT 1 | 2014-01-01 | 2017-06-01 |  | No
| HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 2013-12-01 | 2017-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV KACP | 2013-12-01 | 2019-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV WERE | 2013-12-01 | 2019-06-01 |  | No
| Lacygne - Mariosa 345KV KACP | 2013-12-01 | 2019-06-01 |  | No
| MEDICINE LODGE - PRATT 115KV CKT 1 | 2014-01-01 | 2014-06-15 |  | No
| Mullergren - Reno 345kV Dbl CKT MKEC | 2014-01-01 | 2019-06-01 |  | No
| Mullergren - Reno 345kV Dbl CKT WERE | 2014-01-01 | 2019-06-01 |  | No
| Muskogee - VBI 345 kV with 345/161 kV bus tie near VBI | 2014-06-01 | 2019-06-01 |  | No
| Potter to Tolk 345 kV | 2013-12-01 | 2019-06-01 |  | No
| Spearville - Mullergren 345kV Dbl CKT | 2014-01-01 | 2019-06-01 |  | No
| VBI - Arkansas Nuclear One 345kV OKGE | 2014-06-01 | 2019-06-01 |  | No
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77410128 | BARBER (BARBER 4) 138/115/2.72KV TRANSFORMER CKT 1 | 2009-12-01 | 2013-06-01
| CIMARRON - DRAPER LAKE 345KV CKT 1 | 2014-10-01 | 2016-06-01
| FLATRDG3 138.00 - MEDICINE LODGE 138KV CKT 1 | 2009-12-01 | 2013-06-01
| FLATRDG3 138.00 - HARPER 138KV CKT 1 | 2009-12-01 | 2013-06-01
| HUGO POWER PLANT - VALLIANT 345 KV AEPW | 2012-07-01 | 2012-07-01
| HUGO POWER PLANT - VALLIANT 345KV CKT 1 WFEC | 2012-07-01 | 2012-07-01
| LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01
| Mullergren - Reno 345kV Dbl CKT MKEC | 2013-10-01 | 2019-06-01
| Mullergren - Reno 345kV Dbl CKT WERE | 2013-10-01 | 2019-06-01
| NORTHWEST - TATONGA 345KV CKT 1 | 2010-01-01 | 2010-01-01
| Spearville - Mullergren 345kV Dbl CKT | 2013-10-01 | 2019-06-01
| TATONGA - WOODWARD 345KV CKT 1 | 2010-01-01 | 2010-01-01
Third Party Limitations.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | *Allocated E & C Cost | *Total E & C Cost
77410128 | 7JASPER 345.00 - BLACKBERRY 345KV CKT 1 #1 | 2015-06-01 | 2015-06-01 |  |  | 8584 | 100000
| 7OVERTON 345.00 () 345/161/13.8KV TRANSFORMER CKT 1 | 2014-01-01 | 2014-06-01 |  | No | 17.81% | 100%
| ARKANSAS NUCLEAR ONE - PLEASANT HILL 500KV CKT 1 | 2014-10-01 | 2014-10-01 |  |  | 9.827% | 100%
| Arkansas Nuclear One 500/345 Transformer | 2014-06-01 | 2019-06-01 |  | No | 1169009 | 12000000
| BEAVER - EUREKA SPRINGS 161KV CKT 1 SWPA | 2014-06-01 | 2015-06-01 |  | No | 0 | 0
| BUFORD 5 161.00 - BULL SHOALS 161KV CKT 1 | 2014-06-01 | 2017-06-01 |  | No | 0 | 0
| BUFORD 5 161.00 - NORFORK 161KV CKT 1 | 2014-06-01 | 2017-06-01 |  | No | 0 | 0
| CLINTON - MONTROSE 161KV CKT 1 AECI | 2015-06-01 | 2016-06-01 |  | No | 26336 | 180000
| Lacygne - Mariosa 345KV AMRN | 2013-12-01 | 2019-06-01 |  | No | 12.11% | 100%
| NORTH SLIDELL - SLIDELL 230KV CKT 1 CELE | 2015-10-01 | 2015-10-01 |  |  | 18.93% | 100%
| NORTH SLIDELL - SLIDELL 230KV CKT 1 EES | 2015-10-01 | 2015-10-01 |  |  | 18.93% | 100%
| VBI - Arkansas Nuclear One 345kV EES | 2014-06-01 | 2019-06-01 |  | No | 9.742% | 100%
[5 empty] | Total | 1203929 | 12280000
*Estimated cost allocation as a percentage of total cost is shown for third-party limitations when costs have not yet been established by the third-party.
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
CRGL | 2012-AG3-050
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
CRGL | 77410129 | SECI | EES | 101 | 2014-01-01 | 2019-01-01 | 2019-06-01 | 2024-06-01 | 0 | 7756800 | 17846525 | 48745707.354
[9 empty] | 0 | 7756800 | 17846525 | 48745707.354
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77410129 | 59TH ST - EL PASO 138KV CKT 1 | 2015-06-01 | 2017-06-01 |  | No | 327783 | 5693300 | 1013998.11
| 59TH ST - GILL ENERGY CENTER SOUTH 138KV CKT 1 | 2015-06-01 | 2017-06-01 |  | No | 290355 | 5043200 | 898214.43
| Cimarron - Mathewson 345 kV Ckt 1 Accelerate | 2013-12-01 | 2015-06-01 |  | No | 339503 | 10704894 | 1209827.994
| GRAND ISLAND - SWEETWATER 345KV CKT 2 | 2013-12-01 | 2019-06-01 |  | No | 8843393 | 96288750 | 23315448.258
| HOLT - NELIGH 345KV CKT 1 | 2013-12-01 | 2019-06-01 |  | No | 3135264 | 30656000 | 7780985.94
| Mathewson - Tatonga 345 kV Ckt 2 Accelerate | 2013-12-01 | 2015-06-01 |  | No | 905481 | 26823745 | 3226705.704
| Mathewson 345 kV Accelerate | 2013-12-01 | 2015-06-01 |  | No | 208893 | 6586619 | 744395.772
| OKLAUNION 345KV SVC | 2014-10-01 | 2019-06-01 |  | No | 206923 | 18500000 | 659073.03
| SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 MIDW | 2013-12-01 | 2018-06-01 |  | No | 1016215 | 13864500 | 2378016.846
| SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 WERE | 2013-12-01 | 2018-06-01 |  | No | 2496568 | 34061343.75 | 7269349.656
| ST JOHN - ST_JOHN 115KV CKT 1 MIDW | 2013-12-01 | 2016-06-01 |  | No | 33843 | 450000 | 81856.818
| ST JOHN - ST_JOHN 115KV CKT 1 MKEC | 2013-12-01 | 2016-06-01 |  | No | 42304 | 562500 | 167834.796
[5 empty] | Total | 17846525 | 249234851.75 | 48745707.354
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77410129 | 5 TRIBES - PECAN CREEK 161KV CKT 1 | 2014-06-01 | 2014-06-01
| HARPER - MILAN TAP 138KV CKT 1 #1 | 2013-12-01 | 2014-12-01 |  | No
| IATAN - NASHUA 345KV CKT 1 | 2013-12-01 | 2015-06-01 |  | No
| Line - Clark County - Thistle 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2014-07-01 |  | No
| Line - Hitchland - Woodward 345 kV dbl Ckt SPS | 2013-12-01 | 2014-07-01 |  | No
| Line - Spearville - Clark County 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt WERE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Tuco - Woodward 345 kV line OKGE | 2013-12-01 | 2014-06-01 |  | No
| Line - Tuco - Woodward 345 kV line SPS | 2013-12-01 | 2014-06-01 |  | No
| MOUNDRIDGE 138/115KV TRANSFORMER CKT 2 | 2013-12-01 | 2014-12-01 |  | No
| NORTHWEST TEXARKANA - VALLIANT 345KV CKT 1 | 2014-06-01 | 2015-05-01 |  | No
| XFR - Thistle 345/138 kV | 2013-12-01 | 2015-01-01 |  | No
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77410129 | Cherry Co - Gentleman 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co - Holt Co 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co 345 kV Terminal Upgrades | 2013-12-01 | 2018-01-01 |  | No
| Elk City 345/230 kV | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV AEPW | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV OKGE | 2013-12-01 | 2018-03-01 |  | No
| Multi - Centerton - Osage Creek 345 kV | 2014-06-01 | 2016-06-01 |  | No
| Multi - Flint Creek – Centerton 345 kV and Centerton- East Centerton 161 kV | 2014-06-01 | 2014-06-01
| Neligh - Hoskins 345 kV Ckt1 | 2013-12-01 | 2019-03-01 |  | No
| Neligh 345/115 kV Transformer | 2013-12-01 | 2019-03-01 |  | No
| Viola - Clearwater 138kV Ckt1 | 2014-10-01 | 2018-06-01 |  | No
| Viola - Gill 138kV Ckt1 | 2014-10-01 | 2018-06-01 |  | No
| Viola 345/138kV Transformer Ckt 1 | 2014-10-01 | 2018-06-01 |  | No
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77410129 | ADABELL - VBI 161KV CKT 1 | 2014-06-01 | 2016-06-01 |  | No
| BEAVER - EUREKA SPRINGS 161KV CKT 1 AEPW | 2014-06-01 | 2015-06-01 |  | No
| CHISHOLM - MAIZE 138KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| CHISHOLM - MAIZE 138KV CKT 1 #2 | 2015-06-01 | 2017-06-01 |  | No
| CIMARRON - DRAPER LAKE 345KV CKT 1 | 2019-10-01 | 2019-10-01
| CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | 2013-12-01 | 2017-06-01 |  | No
| CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | 2013-12-01 | 2017-06-01 |  | No
| EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 #2 | 2015-06-01 | 2017-06-01 |  | No
| FLINT CREEK - SILOAM SPRINGS TAP 345KV CKT 1 AEPW | 2019-06-01 | 2019-06-01
| FT SMITH - MUSKOGEE 345KV CKT 1 | 2014-06-01 | 2016-06-01 |  | No
| FT SMITH (FTSMITH1) 500/345/13.8KV TRANSFORMER CKT 1 | 2014-06-01 | 2018-06-01 |  | No
| GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #2 | 2015-06-01 | 2016-06-01 |  | No
| HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | 2013-12-01 | 2017-06-01 |  | No
| HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 2013-12-01 | 2017-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV KACP | 2013-12-01 | 2019-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV WERE | 2013-12-01 | 2019-06-01 |  | No
| Lacygne - Mariosa 345KV KACP | 2013-12-01 | 2019-06-01 |  | No
| MEDICINE LODGE - PRATT 115KV CKT 1 | 2014-01-01 | 2014-06-15 |  | No
| Mullergren - Reno 345kV Dbl CKT MKEC | 2014-01-01 | 2019-06-01 |  | No
| Mullergren - Reno 345kV Dbl CKT WERE | 2014-01-01 | 2019-06-01 |  | No
| Muskogee - VBI 345 kV with 345/161 kV bus tie near VBI | 2014-06-01 | 2019-06-01 |  | No
| Potter to Tolk 345 kV | 2013-12-01 | 2019-06-01 |  | No
| Spearville - Mullergren 345kV Dbl CKT | 2014-01-01 | 2019-06-01 |  | No
| VBI - Arkansas Nuclear One 345kV OKGE | 2014-06-01 | 2019-06-01 |  | No
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77410129 | BARBER (BARBER 4) 138/115/2.72KV TRANSFORMER CKT 1 | 2009-12-01 | 2013-06-01
| CIMARRON - DRAPER LAKE 345KV CKT 1 | 2014-10-01 | 2016-06-01
| FLATRDG3 138.00 - MEDICINE LODGE 138KV CKT 1 | 2009-12-01 | 2013-06-01
| FLATRDG3 138.00 - HARPER 138KV CKT 1 | 2009-12-01 | 2013-06-01
| HUGO POWER PLANT - VALLIANT 345 KV AEPW | 2012-07-01 | 2012-07-01
| HUGO POWER PLANT - VALLIANT 345KV CKT 1 WFEC | 2012-07-01 | 2012-07-01
| Mullergren - Reno 345kV Dbl CKT MKEC | 2013-10-01 | 2019-06-01
| Mullergren - Reno 345kV Dbl CKT WERE | 2013-10-01 | 2019-06-01
| NORTHWEST - TATONGA 345KV CKT 1 | 2010-01-01 | 2010-01-01
| Spearville - Mullergren 345kV Dbl CKT | 2013-10-01 | 2019-06-01
| TATONGA - WOODWARD 345KV CKT 1 | 2010-01-01 | 2010-01-01
Third Party Limitations.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | *Allocated E & C Cost | *Total E & C Cost
77410129 | 7JASPER 345.00 - BLACKBERRY 345KV CKT 1 #1 | 2015-06-01 | 2015-06-01 |  |  | 4365 | 100000
| 7OVERTON 345.00 () 345/161/13.8KV TRANSFORMER CKT 1 | 2014-01-01 | 2014-06-01 |  | No | 8.453% | 100%
| ARKANSAS NUCLEAR ONE - PLEASANT HILL 500KV CKT 1 | 2014-10-01 | 2014-10-01 |  |  | 5.033% | 100%
| Arkansas Nuclear One 500/345 Transformer | 2014-06-01 | 2019-06-01 |  | No | 599076 | 12000000
| BEAVER - EUREKA SPRINGS 161KV CKT 1 SWPA | 2014-06-01 | 2015-06-01 |  | No | 0 | 0
| BUFORD 5 161.00 - BULL SHOALS 161KV CKT 1 | 2014-06-01 | 2017-06-01 |  | No | 0 | 0
| BUFORD 5 161.00 - NORFORK 161KV CKT 1 | 2014-06-01 | 2017-06-01 |  | No | 0 | 0
| CLINTON - MONTROSE 161KV CKT 1 AECI | 2015-06-01 | 2016-06-01 |  | No | 12515 | 180000
| Lacygne - Mariosa 345KV AMRN | 2013-12-01 | 2019-06-01 |  | No | 4.888% | 100%
| NORTH SLIDELL - SLIDELL 230KV CKT 1 CELE | 2015-10-01 | 2015-10-01 |  |  | 9.591% | 100%
| NORTH SLIDELL - SLIDELL 230KV CKT 1 EES | 2015-10-01 | 2015-10-01 |  |  | 9.591% | 100%
| VBI - Arkansas Nuclear One 345kV EES | 2014-06-01 | 2019-06-01 |  | No | 4.992% | 100%
[5 empty] | Total | 615956 | 12280000
*Estimated cost allocation as a percentage of total cost is shown for third-party limitations when costs have not yet been established by the third-party.
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
CRGL | 2012-AG3-051
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
CRGL | 77410131 | SECI | EES | 100 | 2014-01-01 | 2019-01-01 | 2019-06-01 | 2024-06-01 | 0 | 7680000 | 18665471 | 50845516.086
[9 empty] | 0 | 7680000 | 18665471 | 50845516.086
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77410131 | 59TH ST - EL PASO 138KV CKT 1 | 2015-06-01 | 2017-06-01 |  | No | 317406 | 5693300 | 981896.808
| 59TH ST - GILL ENERGY CENTER SOUTH 138KV CKT 1 | 2015-06-01 | 2017-06-01 |  | No | 281163 | 5043200 | 869778.942
| Cimarron - Mathewson 345 kV Ckt 1 Accelerate | 2013-12-01 | 2015-06-01 |  | No | 326146 | 10704894 | 1162229.976
| GRAND ISLAND - SWEETWATER 345KV CKT 2 | 2013-12-01 | 2019-06-01 |  | No | 9179117 | 96288750 | 24200578.602
| HOLT - NELIGH 345KV CKT 1 | 2013-12-01 | 2019-06-01 |  | No | 3248407 | 30656000 | 8061780.174
| Mathewson - Tatonga 345 kV Ckt 2 Accelerate | 2013-12-01 | 2015-06-01 |  | No | 844127 | 26823745 | 3008069.076
| Mathewson 345 kV Accelerate | 2013-12-01 | 2015-06-01 |  | No | 200674 | 6586619 | 715107.156
| OKLAUNION 345KV SVC | 2014-10-01 | 2019-06-01 |  | No | 191212 | 18500000 | 609031.722
| SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 MIDW | 2013-12-01 | 2018-06-01 |  | No | 1158033 | 13864500 | 2709881.256
| SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 WERE | 2013-12-01 | 2018-06-01 |  | No | 2844976 | 34061343.75 | 8283822.15
| ST JOHN - ST_JOHN 115KV CKT 1 MIDW | 2013-12-01 | 2016-06-01 |  | No | 32982 | 450000 | 79774.302
| ST JOHN - ST_JOHN 115KV CKT 1 MKEC | 2013-12-01 | 2016-06-01 |  | No | 41228 | 562500 | 163565.922
[5 empty] | Total | 18665471 | 249234851.75 | 50845516.086
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77410131 | 5 TRIBES - PECAN CREEK 161KV CKT 1 | 2014-06-01 | 2014-06-01
| HARPER - MILAN TAP 138KV CKT 1 #1 | 2013-12-01 | 2014-12-01 |  | No
| IATAN - NASHUA 345KV CKT 1 | 2013-12-01 | 2015-06-01 |  | No
| Line - Clark County - Thistle 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2014-07-01 |  | No
| Line - Hitchland - Woodward 345 kV dbl Ckt SPS | 2013-12-01 | 2014-07-01 |  | No
| Line - Spearville - Clark County 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt WERE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Tuco - Woodward 345 kV line OKGE | 2013-12-01 | 2014-06-01 |  | No
| Line - Tuco - Woodward 345 kV line SPS | 2013-12-01 | 2014-06-01 |  | No
| MOUNDRIDGE 138/115KV TRANSFORMER CKT 2 | 2013-12-01 | 2014-12-01 |  | No
| NORTHWEST TEXARKANA - VALLIANT 345KV CKT 1 | 2014-06-01 | 2015-05-01 |  | No
| XFR - Thistle 345/138 kV | 2013-12-01 | 2015-01-01 |  | No
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77410131 | Cherry Co - Gentleman 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co - Holt Co 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co 345 kV Terminal Upgrades | 2013-12-01 | 2018-01-01 |  | No
| Elk City 345/230 kV | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV AEPW | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV OKGE | 2013-12-01 | 2018-03-01 |  | No
| Multi - Centerton - Osage Creek 345 kV | 2014-06-01 | 2016-06-01 |  | No
| Multi - Flint Creek – Centerton 345 kV and Centerton- East Centerton 161 kV | 2014-06-01 | 2014-06-01
| Neligh - Hoskins 345 kV Ckt1 | 2013-12-01 | 2019-03-01 |  | No
| Neligh 345/115 kV Transformer | 2013-12-01 | 2019-03-01 |  | No
| Viola - Clearwater 138kV Ckt1 | 2014-10-01 | 2018-06-01 |  | No
| Viola - Gill 138kV Ckt1 | 2014-10-01 | 2018-06-01 |  | No
| Viola 345/138kV Transformer Ckt 1 | 2014-10-01 | 2018-06-01 |  | No
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77410131 | ADABELL - VBI 161KV CKT 1 | 2014-06-01 | 2016-06-01 |  | No
| BEAVER - EUREKA SPRINGS 161KV CKT 1 AEPW | 2014-06-01 | 2015-06-01 |  | No
| CHISHOLM - MAIZE 138KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| CHISHOLM - MAIZE 138KV CKT 1 #2 | 2015-06-01 | 2017-06-01 |  | No
| CIMARRON - DRAPER LAKE 345KV CKT 1 | 2019-10-01 | 2019-10-01
| CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | 2013-12-01 | 2017-06-01 |  | No
| CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | 2013-12-01 | 2017-06-01 |  | No
| EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 #2 | 2015-06-01 | 2017-06-01 |  | No
| FLINT CREEK - SILOAM SPRINGS TAP 345KV CKT 1 AEPW | 2019-06-01 | 2019-06-01
| FT SMITH - MUSKOGEE 345KV CKT 1 | 2014-06-01 | 2016-06-01 |  | No
| FT SMITH (FTSMITH1) 500/345/13.8KV TRANSFORMER CKT 1 | 2014-06-01 | 2018-06-01 |  | No
| GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #2 | 2015-06-01 | 2016-06-01 |  | No
| HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | 2013-12-01 | 2017-06-01 |  | No
| HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 2013-12-01 | 2017-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV KACP | 2013-12-01 | 2019-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV WERE | 2013-12-01 | 2019-06-01 |  | No
| Lacygne - Mariosa 345KV KACP | 2013-12-01 | 2019-06-01 |  | No
| MEDICINE LODGE - PRATT 115KV CKT 1 | 2014-01-01 | 2014-06-15 |  | No
| Mullergren - Reno 345kV Dbl CKT MKEC | 2014-01-01 | 2019-06-01 |  | No
| Mullergren - Reno 345kV Dbl CKT WERE | 2014-01-01 | 2019-06-01 |  | No
| Muskogee - VBI 345 kV with 345/161 kV bus tie near VBI | 2014-06-01 | 2019-06-01 |  | No
| Potter to Tolk 345 kV | 2013-12-01 | 2019-06-01 |  | No
| Spearville - Mullergren 345kV Dbl CKT | 2014-01-01 | 2019-06-01 |  | No
| VBI - Arkansas Nuclear One 345kV OKGE | 2014-06-01 | 2019-06-01 |  | No
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77410131 | CIMARRON - DRAPER LAKE 345KV CKT 1 | 2014-10-01 | 2016-06-01
| HUGO POWER PLANT - VALLIANT 345 KV AEPW | 2012-07-01 | 2012-07-01
| HUGO POWER PLANT - VALLIANT 345KV CKT 1 WFEC | 2012-07-01 | 2012-07-01
| LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01
| Mullergren - Reno 345kV Dbl CKT MKEC | 2013-10-01 | 2019-06-01
| Mullergren - Reno 345kV Dbl CKT WERE | 2013-10-01 | 2019-06-01
| NORTHWEST - TATONGA 345KV CKT 1 | 2010-01-01 | 2010-01-01
| Spearville - Mullergren 345kV Dbl CKT | 2013-10-01 | 2019-06-01
| TATONGA - WOODWARD 345KV CKT 1 | 2010-01-01 | 2010-01-01
Third Party Limitations.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | *Allocated E & C Cost | *Total E & C Cost
77410131 | 7JASPER 345.00 - BLACKBERRY 345KV CKT 1 #1 | 2015-06-01 | 2015-06-01 |  |  | 4202 | 100000
| 7OVERTON 345.00 () 345/161/13.8KV TRANSFORMER CKT 1 | 2014-01-01 | 2014-06-01 |  | No | 8.527% | 100%
| ARKANSAS NUCLEAR ONE - PLEASANT HILL 500KV CKT 1 | 2014-10-01 | 2014-10-01 |  |  | 4.909% | 100%
| Arkansas Nuclear One 500/345 Transformer | 2014-06-01 | 2019-06-01 |  | No | 583868 | 12000000
| BEAVER - EUREKA SPRINGS 161KV CKT 1 SWPA | 2014-06-01 | 2015-06-01 |  | No | 0 | 0
| BUFORD 5 161.00 - BULL SHOALS 161KV CKT 1 | 2014-06-01 | 2017-06-01 |  | No | 0 | 0
| BUFORD 5 161.00 - NORFORK 161KV CKT 1 | 2014-06-01 | 2017-06-01 |  | No | 0 | 0
| CLINTON - MONTROSE 161KV CKT 1 AECI | 2015-06-01 | 2016-06-01 |  | No | 12535 | 180000
| Lacygne - Mariosa 345KV AMRN | 2013-12-01 | 2019-06-01 |  | No | 5.008% | 100%
| NORTH SLIDELL - SLIDELL 230KV CKT 1 CELE | 2015-10-01 | 2015-10-01 |  |  | 9.465% | 100%
| NORTH SLIDELL - SLIDELL 230KV CKT 1 EES | 2015-10-01 | 2015-10-01 |  |  | 9.465% | 100%
| VBI - Arkansas Nuclear One 345kV EES | 2014-06-01 | 2019-06-01 |  | No | 4.866% | 100%
[5 empty] | Total | 600605 | 12280000
*Estimated cost allocation as a percentage of total cost is shown for third-party limitations when costs have not yet been established by the third-party.
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
CRGL | 2012-AG3-052
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
CRGL | 77410135 | WFEC | EES | 75 | 2014-01-01 | 2019-01-01 | 2019-06-01 | 2024-06-01 | 0 | 5760000 | 3192634 | 8296409.184
[9 empty] | 0 | 5760000 | 3192634 | 8296409.184
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77410135 | AVOCA - EAST ROGERS 161KV CKT 1 Accelerate | 2014-06-01 | 2017-06-01 |  | No | 260617 | 822521 | 641519.49
| CORN TAP - PAOLI 138KV CKT 1 | 2019-06-01 | 2019-06-01 |  |  | 35828 | 225000 | 82339.488
| GRAND ISLAND - SWEETWATER 345KV CKT 2 | 2013-12-01 | 2019-06-01 |  | No | 1929029 | 96288750 | 5085850.626
| HOLT - NELIGH 345KV CKT 1 | 2013-12-01 | 2019-06-01 |  | No | 677812 | 30656000 | 1682169.546
| LAKE CREEK - LONEWOLF 69KV CKT 1 | 2014-01-01 | 2016-06-01 |  | No | 217519 | 225000 | 548565.48
| Mathewson - Tatonga 345 kV Ckt 2 Accelerate | 2013-12-01 | 2015-06-01 |  | No | 71829 | 26823745 | 255964.554
[5 empty] | Total | 3192634 | 155041016 | 8296409.18
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77410135 | 5 TRIBES - PECAN CREEK 161KV CKT 1 | 2014-06-01 | 2014-06-01
| IATAN - NASHUA 345KV CKT 1 | 2013-12-01 | 2015-06-01 |  | No
| Line - Clark County - Thistle 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2014-07-01 |  | No
| Line - Hitchland - Woodward 345 kV dbl Ckt SPS | 2013-12-01 | 2014-07-01 |  | No
| Line - Spearville - Clark County 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt WERE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Tuco - Woodward 345 kV line OKGE | 2013-12-01 | 2014-06-01 |  | No
| Line - Tuco - Woodward 345 kV line SPS | 2013-12-01 | 2014-06-01 |  | No
| NORTHWEST TEXARKANA - VALLIANT 345KV CKT 1 | 2014-06-01 | 2015-05-01 |  | No
| XFR - Thistle 345/138 kV | 2013-12-01 | 2015-01-01 |  | No
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77410135 | Cherry Co - Gentleman 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co - Holt Co 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co 345 kV Terminal Upgrades | 2013-12-01 | 2018-01-01 |  | No
| Multi - Centerton - Osage Creek 345 kV | 2014-06-01 | 2016-06-01 |  | No
| Multi - Flint Creek – Centerton 345 kV and Centerton- East Centerton 161 kV | 2014-06-01 | 2014-06-01
| Neligh - Hoskins 345 kV Ckt1 | 2013-12-01 | 2019-03-01 |  | No
| Neligh 345/115 kV Transformer | 2013-12-01 | 2019-03-01 |  | No
| Viola - Clearwater 138kV Ckt1 | 2014-10-01 | 2018-06-01 |  | No
| Viola - Gill 138kV Ckt1 | 2014-10-01 | 2018-06-01 |  | No
| Viola 345/138kV Transformer Ckt 1 | 2014-10-01 | 2018-06-01 |  | No
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77410135 | ADABELL - VBI 161KV CKT 1 | 2014-06-01 | 2016-06-01 |  | No
| BEAVER - EUREKA SPRINGS 161KV CKT 1 AEPW | 2014-06-01 | 2015-06-01 |  | No
| BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #1 Accelerate | 2014-06-01 | 2015-06-01 |  | No
| BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #2 Accelerate | 2014-06-01 | 2017-06-01 |  | No
| BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #1 Accelerate | 2014-06-01 | 2015-06-01 |  | No
| BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #2 Accelerate | 2014-06-01 | 2016-06-01 |  | No
| CIMARRON - DRAPER LAKE 345KV CKT 1 | 2019-10-01 | 2019-10-01
| FLINT CREEK - SILOAM SPRINGS TAP 345KV CKT 1 AEPW | 2019-06-01 | 2019-06-01
| FT SMITH - MUSKOGEE 345KV CKT 1 | 2014-06-01 | 2016-06-01 |  | No
| FT SMITH (FTSMITH1) 500/345/13.8KV TRANSFORMER CKT 1 | 2014-06-01 | 2018-06-01 |  | No
| GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | 2014-01-01 | 2016-06-01 |  | No
| GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #2 | 2015-06-01 | 2016-06-01 |  | No
| HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 2013-12-01 | 2017-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV KACP | 2013-12-01 | 2019-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV WERE | 2013-12-01 | 2019-06-01 |  | No
| Lacygne - Mariosa 345KV KACP | 2013-12-01 | 2019-06-01 |  | No
| Muskogee - VBI 345 kV with 345/161 kV bus tie near VBI | 2014-06-01 | 2019-06-01 |  | No
| SOUTHWESTERN STATION - WASHITA 138KV CKT 2 | 2013-12-01 | 2017-06-01 |  | No
| VBI - Arkansas Nuclear One 345kV OKGE | 2014-06-01 | 2019-06-01 |  | No
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77410135 | ALTUS SW - NAVAJO 69KV CKT 1 | 2013-06-01 | 2013-06-01
| CANTON - TALOGA 69KV CKT 1 | 2011-06-01 | 2013-06-01
| CIMARRON - DRAPER LAKE 345KV CKT 1 | 2014-10-01 | 2016-06-01
| GRACMNT4 138.00 - WASHITA 138KV CKT 2 OKGE | 2012-01-01 | 2012-01-01
| GRACMNT4 138.00 - WASHITA 138KV CKT 2 WFEC | 2012-01-01 | 2012-01-01
| HUGO POWER PLANT - VALLIANT 345 KV AEPW | 2012-07-01 | 2012-07-01
| HUGO POWER PLANT - VALLIANT 345KV CKT 1 WFEC | 2012-07-01 | 2012-07-01
| LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01
| NORTHWEST - TATONGA 345KV CKT 1 | 2010-01-01 | 2010-01-01
| TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | 2010-10-01 | 2013-06-01
| TATONGA - WOODWARD 345KV CKT 1 | 2010-01-01 | 2010-01-01
| WOODWARD - IODINE 138KV CKT 1 | 2010-01-01 | 2010-01-01
| WOODWARD - WOODWARD EHV 138KV CKT 1 | 2010-01-01 | 2010-01-01
| WOODWARD 345/138KV TRANSFORMER CKT 1 | 2010-01-01 | 2010-01-01
Potential reservation deferral and redispatch requirement on the following upgrades due to positive MW Impact on limitations that require upgrade. No cost assignment due to negative MW impact on defined upgrade.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77410135 | Cimarron - Mathewson 345 kV Ckt 1 Accelerate | 2013-12-01 | 2015-06-01 |  | No
| Mathewson 345 kV Accelerate | 2013-12-01 | 2015-06-01 |  | No
| OKLAUNION 345KV SVC | 2014-10-01 | 2019-06-01 |  | No
Third Party Limitations.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | *Allocated E & C Cost | *Total E & C Cost
77410135 | 7JASPER 345.00 - BLACKBERRY 345KV CKT 1 #1 | 2015-06-01 | 2015-06-01 |  |  | 4367 | 100000
| 7OVERTON 345.00 () 345/161/13.8KV TRANSFORMER CKT 1 | 2014-01-01 | 2014-06-01 |  | No | 3.64% | 100%
| ARKANSAS NUCLEAR ONE - PLEASANT HILL 500KV CKT 1 | 2014-10-01 | 2014-10-01 |  |  | 4.798% | 100%
| Arkansas Nuclear One 500/345 Transformer | 2014-06-01 | 2019-06-01 |  | No | 576911 | 12000000
| BEAVER - EUREKA SPRINGS 161KV CKT 1 SWPA | 2014-06-01 | 2015-06-01 |  | No | 0 | 0
| BUFORD 5 161.00 - BULL SHOALS 161KV CKT 1 | 2014-06-01 | 2017-06-01 |  | No | 0 | 0
| BUFORD 5 161.00 - NORFORK 161KV CKT 1 | 2014-06-01 | 2017-06-01 |  | No | 0 | 0
| CLINTON - MONTROSE 161KV CKT 1 AECI | 2015-06-01 | 2016-06-01 |  | No | 5946 | 180000
| Lacygne - Mariosa 345KV AMRN | 2013-12-01 | 2019-06-01 |  | No | 1.891% | 100%
| NORTH SLIDELL - SLIDELL 230KV CKT 1 CELE | 2015-10-01 | 2015-10-01 |  |  | 7.597% | 100%
| NORTH SLIDELL - SLIDELL 230KV CKT 1 EES | 2015-10-01 | 2015-10-01 |  |  | 7.597% | 100%
| VBI - Arkansas Nuclear One 345kV EES | 2014-06-01 | 2019-06-01 |  | No | 4.808% | 100%
[5 empty] | Total | 587224 | 12280000
*Estimated cost allocation as a percentage of total cost is shown for third-party limitations when costs have not yet been established by the third-party.
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
CRGL | 2012-AG3-054
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
CRGL | 77410157 | CSWS | EES | 150 | 2014-01-01 | 2019-01-01 | 2019-06-01 | 2024-06-01 | 0 | 11520000 | 9332613 | 23572983.876
[9 empty] | 0 | 11520000 | 9332613 | 23572983.876
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77410157 | AVOCA - EAST ROGERS 161KV CKT 1 Accelerate | 2014-06-01 | 2017-06-01 |  | No | 561904 | 822521 | 1383149.868
| BARTLESVILLE COMANCHE - MOUND ROAD 138KV CKT 1 | 2014-01-01 | 2017-06-01 |  | No | 4750000 | 4750000 | 11752229.034
| GRAND ISLAND - SWEETWATER 345KV CKT 2 | 2013-12-01 | 2019-06-01 |  | No | 2943103 | 96288750 | 7759438.68
| HOLT - NELIGH 345KV CKT 1 | 2013-12-01 | 2019-06-01 |  | No | 1072200 | 30656000 | 2660947.572
| OKLAUNION 345KV SVC | 2014-10-01 | 2019-06-01 |  | No | 5406 | 18500000 | 17218.722
[5 empty] | Total | 9332613 | 151017271 | 23572983.88
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77410157 | 5 TRIBES - PECAN CREEK 161KV CKT 1 | 2014-06-01 | 2014-06-01
| IATAN - NASHUA 345KV CKT 1 | 2013-12-01 | 2015-06-01 |  | No
| Line - Clark County - Thistle 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2014-07-01 |  | No
| Line - Hitchland - Woodward 345 kV dbl Ckt SPS | 2013-12-01 | 2014-07-01 |  | No
| Line - Spearville - Clark County 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt WERE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Tuco - Woodward 345 kV line OKGE | 2013-12-01 | 2014-06-01 |  | No
| Line - Tuco - Woodward 345 kV line SPS | 2013-12-01 | 2014-06-01 |  | No
| NORTHWEST TEXARKANA - VALLIANT 345KV CKT 1 | 2014-06-01 | 2015-05-01 |  | No
| XFR - Thistle 345/138 kV | 2013-12-01 | 2015-01-01 |  | No
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77410157 | Cherry Co - Gentleman 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co - Holt Co 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co 345 kV Terminal Upgrades | 2013-12-01 | 2018-01-01 |  | No
| Multi - Centerton - Osage Creek 345 kV | 2014-06-01 | 2016-06-01 |  | No
| Multi - Flint Creek – Centerton 345 kV and Centerton- East Centerton 161 kV | 2014-06-01 | 2014-06-01
| Neligh - Hoskins 345 kV Ckt1 | 2013-12-01 | 2019-03-01 |  | No
| Neligh 345/115 kV Transformer | 2013-12-01 | 2019-03-01 |  | No
| TERRA NITROGEN TAP - VERDIGRIS 138KV CKT 1 | 2014-06-01 | 2017-06-01 |  | No
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77410157 | ADABELL - VBI 161KV CKT 1 | 2014-06-01 | 2016-06-01 |  | No
| BEAVER - EUREKA SPRINGS 161KV CKT 1 AEPW | 2014-06-01 | 2015-06-01 |  | No
| BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #1 Accelerate | 2014-06-01 | 2015-06-01 |  | No
| BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #2 Accelerate | 2014-06-01 | 2017-06-01 |  | No
| BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #1 Accelerate | 2014-06-01 | 2015-06-01 |  | No
| BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #2 Accelerate | 2014-06-01 | 2016-06-01 |  | No
| CIMARRON - DRAPER LAKE 345KV CKT 1 | 2019-10-01 | 2019-10-01
| FLINT CREEK - SILOAM SPRINGS TAP 345KV CKT 1 AEPW | 2019-06-01 | 2019-06-01
| FT SMITH - MUSKOGEE 345KV CKT 1 | 2014-06-01 | 2016-06-01 |  | No
| FT SMITH (FTSMITH1) 500/345/13.8KV TRANSFORMER CKT 1 | 2014-06-01 | 2018-06-01 |  | No
| GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #2 | 2015-06-01 | 2016-06-01 |  | No
| HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 2013-12-01 | 2017-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV KACP | 2013-12-01 | 2019-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV WERE | 2013-12-01 | 2019-06-01 |  | No
| Lacygne - Mariosa 345KV KACP | 2013-12-01 | 2019-06-01 |  | No
| Muskogee - VBI 345 kV with 345/161 kV bus tie near VBI | 2014-06-01 | 2019-06-01 |  | No
| VBI - Arkansas Nuclear One 345kV OKGE | 2014-06-01 | 2019-06-01 |  | No
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77410157 | CIMARRON - DRAPER LAKE 345KV CKT 1 | 2014-10-01 | 2016-06-01
| HUGO POWER PLANT - VALLIANT 345 KV AEPW | 2012-07-01 | 2012-07-01
| HUGO POWER PLANT - VALLIANT 345KV CKT 1 WFEC | 2012-07-01 | 2012-07-01
| LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01
| TATONGA - WOODWARD 345KV CKT 1 | 2010-01-01 | 2010-01-01
Third Party Limitations.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | *Allocated E & C Cost | *Total E & C Cost
77410157 | 7JASPER 345.00 - BLACKBERRY 345KV CKT 1 #1 | 2015-06-01 | 2015-06-01 |  |  | 10722 | 100000
| 7OVERTON 345.00 () 345/161/13.8KV TRANSFORMER CKT 1 | 2014-01-01 | 2014-06-01 |  | No | 6.673% | 100%
| ARKANSAS NUCLEAR ONE - PLEASANT HILL 500KV CKT 1 | 2014-10-01 | 2014-10-01 |  |  | 10.21% | 100%
| Arkansas Nuclear One 500/345 Transformer | 2014-06-01 | 2019-06-01 |  | No | 1228442 | 12000000
| BEAVER - EUREKA SPRINGS 161KV CKT 1 SWPA | 2014-06-01 | 2015-06-01 |  | No | 0 | 0
| BUFORD 5 161.00 - BULL SHOALS 161KV CKT 1 | 2014-06-01 | 2017-06-01 |  | No | 0 | 0
| BUFORD 5 161.00 - NORFORK 161KV CKT 1 | 2014-06-01 | 2017-06-01 |  | No | 0 | 0
| CLINTON - MONTROSE 161KV CKT 1 AECI | 2015-06-01 | 2016-06-01 |  | No | 10411 | 180000
| FAIRFAX 138/69KV TRANSFORMER CKT 1 | 2015-06-01 | 2017-06-01 |  | No | 2000000 | 2000000
| Lacygne - Mariosa 345KV AMRN | 2013-12-01 | 2019-06-01 |  | No | 2.757% | 100%
| NORTH SLIDELL - SLIDELL 230KV CKT 1 CELE | 2015-10-01 | 2015-10-01 |  |  | 15.04% | 100%
| NORTH SLIDELL - SLIDELL 230KV CKT 1 EES | 2015-10-01 | 2015-10-01 |  |  | 15.04% | 100%
| VBI - Arkansas Nuclear One 345kV EES | 2014-06-01 | 2019-06-01 |  | No | 10.24% | 100%
[5 empty] | Total | 3249575 | 14280000
*Estimated cost allocation as a percentage of total cost is shown for third-party limitations when costs have not yet been established by the third-party.
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
ETEC | 2012-AG3-038
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
ETEC | 77410319 | CSWS | CSWS | 1171 | 2015-01-01 | 2040-01-01 |  |  | 0 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0 | 0
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77410319 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
ETEC | 2012-AG3-039
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
ETEC | 77410327 | CSWS | CSWS | 79 | 2015-01-01 | 2040-01-01 |  |  | 0 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0 | 0
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77410327 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
ETEC | 2012-AG3-040
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
ETEC | 77410336 | CSWS | CSWS | 500 | 2015-01-01 | 2040-01-01 |  |  | 0 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0 | 0
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77410336 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77410336 | HUGO POWER PLANT - VALLIANT 345 KV AEPW | 2012-07-01 | 2012-07-01
| HUGO POWER PLANT - VALLIANT 345KV CKT 1 WFEC | 2012-07-01 | 2012-07-01
| HUGO POWER PLANT 345/138KV TRANSFORMER CKT 1 | 2012-07-01 | 2012-07-01
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
ETEC | 2012-AG3-041
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
ETEC | 77410342 | EES | CSWS | 30 | 2015-01-01 | 2040-01-01 |  |  | 0 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0 | 0
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77410342 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
ETEC | 2012-AG3-042
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
ETEC | 77410350 | CSWS | CSWS | 406 | 2015-01-01 | 2040-01-01 | 2017-06-01 | 2042-06-01 | 0 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0 | 0
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77410350 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77410350 | Arcadia 345 kV Terminal Upgrades | 2013-12-01 | 2013-12-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77410350 | ADABELL - VBI 161KV CKT 1 | 2014-06-01 | 2016-06-01
| CIMARRON - DRAPER LAKE 345KV CKT 1 | 2019-10-01 | 2019-10-01
| Lacygne - Mariosa 345KV KACP | 2013-12-01 | 2019-06-01
| Muskogee - VBI 345 kV with 345/161 kV bus tie near VBI | 2014-06-01 | 2019-06-01
| NORTH NEW BOSTON - NW TEXARKANA-BANN T 138KV CKT 1 | 2015-06-01 | 2017-06-01 |  | Yes
| VBI - Arkansas Nuclear One 345kV OKGE | 2014-06-01 | 2019-06-01
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77410350 | ALUMAX TAP - BANN 138KV CKT 1 | 2008-06-01 | 2008-06-01
| ASHDOWN REC (MILLWOOD) - OKAY 138KV CKT 1 | 2012-07-01 | 2012-07-01
| ASHDOWN REC (MILLWOOD) - PATTERSON 138KV CKT 1 | 2012-07-01 | 2012-07-01
| BANN - RED SPRINGS REC 138KV CKT 1 | 2012-07-01 | 2012-07-01
| BEELINE - EXPLORER GLENPOOL TAP 138KV CKT 1 | 2009-06-01 | 2009-06-01
| CIMARRON - DRAPER LAKE 345KV CKT 1 | 2014-10-01 | 2016-06-01
| EXPLORER GLENPOOL TAP - RIVERSIDE STATION 138KV CKT 1 AEPW | 2009-06-01 | 2009-06-01
| EXPLORER GLENPOOL TAP - RIVERSIDE STATION 138KV CKT 1 OKGE | 2009-06-01 | 2009-06-01
| HUGO POWER PLANT - VALLIANT 345 KV AEPW | 2012-07-01 | 2012-07-01
| HUGO POWER PLANT - VALLIANT 345KV CKT 1 WFEC | 2012-07-01 | 2012-07-01
| MANDEVILTP4 - SE TEXARKANA 138KV CKT 1 | 2012-07-01 | 2012-07-01
| MANDEVILTP4 - TURK 138KV CKT 1 | 2012-07-01 | 2012-07-01
| MCNAB REC - TURK 115KV CKT 1 | 2012-07-01 | 2012-07-01
| NORTHWEST - TATONGA 345KV CKT 1 | 2010-01-01 | 2010-01-01
| SUGAR HILL - TURK 138KV CKT 1 | 2012-07-01 | 2012-07-01
| TATONGA - WOODWARD 345KV CKT 1 | 2010-01-01 | 2010-01-01
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
ETEC | 2012-AG3-043
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
ETEC | 77410353 | CLEC | CSWS | 38 | 2015-01-01 | 2040-01-01 |  |  | 0 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0 | 0
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77410353 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
ETEC | 2012-AG3-044
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
ETEC | 77410357 | SPA | CSWS | 128 | 2015-01-01 | 2040-01-01 |  |  | 0 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0 | 0
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77410357 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Third Party Limitations.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | *Allocated E & C Cost | *Total E & C Cost
77410357 | ARKANSAS NUCLEAR ONE - PLEASANT HILL 500KV CKT 1 | 2014-10-01 | 2014-10-01 |  |  | 0.08092% | 100%
[5 empty] | Total | 0 | 0
*Estimated cost allocation as a percentage of total cost is shown for third-party limitations when costs have not yet been established by the third-party.
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
ETEC | 2012-AG3-045
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
ETEC | 77410360 | SPA | CSWS | 1 | 2015-01-01 | 2040-01-01 |  |  | 0 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0 | 0
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77410360 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
ETEC | 2012-AG3-046
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
ETEC | 77410382 | CSWS | CSWS | 52 | 2015-01-01 | 2040-01-01 |  |  | 0 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0 | 0
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77410382 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77410382 | MCNAB REC - TURK 115KV CKT 1 | 2012-07-01 | 2012-07-01
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
GSECGS | 2012-AG3-032
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
GSECGS | 77401449 | SPS | SPS | 7 | 2013-06-01 | 2039-01-01 | 2020-01-01 | 2045-08-01 | 21061 | 0 | 21061 | 141300.9559
[9 empty] | 21061 | 0 | 21061 | 141300.9559
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77401449 | Cimarron - Mathewson 345 kV Ckt 1 Accelerate | 2013-12-01 | 2015-06-01 |  | No | 777 | 10704894 | 6108.6553
| Mathewson - Tatonga 345 kV Ckt 2 Accelerate | 2013-12-01 | 2015-06-01 |  | No | 1255 | 26823745 | 9866.5809
| Mathewson 345 kV Accelerate | 2013-12-01 | 2015-06-01 |  | No | 478 | 6586619 | 3757.987
| OKLAUNION 345KV SVC | 2014-10-01 | 2019-06-01 |  | No | 18551 | 18500000 | 121567.7327
[5 empty] | Total | 21061 | 62615258 | 141300.96
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77401449 | BAILEY COUNTY INTERCHANGE - CURRY COUNTY INTERCHANGE 115KV CKT 1 | 2014-06-01 | 2015-06-01 |  | No
| Deaf Smith County Interchange 230/115 kV Transformer Ckt 1 #2 | 2013-12-01 | 2015-03-01 |  | No
| Deaf Smith County Interchange 230/115 kV Transformer Ckt 2 | 2013-12-01 | 2015-03-01 |  | No
| Line - Clark County - Thistle 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2014-07-01 |  | No
| Line - Hitchland - Woodward 345 kV dbl Ckt SPS | 2013-12-01 | 2014-07-01 |  | No
| Line - Spearville - Clark County 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt WERE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Tuco - Woodward 345 kV line OKGE | 2013-12-01 | 2014-06-01 |  | No
| Line - Tuco - Woodward 345 kV line SPS | 2013-12-01 | 2014-06-01 |  | No
| LUBBOCK SOUTH INTERCHANGE 230/115/13.2KV TRANSFORMER CKT 2 | 2013-12-01 | 2014-12-31 |  | No
| NEWHART INTERCHANGE PROJECT | 2014-06-01 | 2015-04-30 |  | No
| XFR - Thistle 345/138 kV | 2013-12-01 | 2015-01-01 |  | No
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77401449 | Amoco - Tuco 345 kV Ckt 1 | 2014-10-01 | 2020-01-01 |  | No
| Amoco 345/230 kV Transformer Ckt 1 | 2014-10-01 | 2020-01-01 |  | No
| Cherry Co - Gentleman 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co - Holt Co 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co 345 kV Terminal Upgrades | 2013-12-01 | 2018-01-01 |  | No
| Elk City 345/230 kV | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV AEPW | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV OKGE | 2013-12-01 | 2018-03-01 |  | No
| HITCHLAND INTERCHANGE () 230/115/13.2KV TRANSFORMER CKT 2 | 2015-06-01 | 2017-06-01 |  | No
| MULTI - Tuco-New Deal 345 kV | 2014-10-01 | 2018-06-01 |  | No
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77401449 | DENVER CITY INTERCHANGE N. - MUSTANG STATION N. 115KV CKT 1 | 2019-06-01 | 2019-06-01
| DENVER CITY INTERCHANGE S. - MUSTANG STATION N. 115KV CKT 2 | 2019-06-01 | 2019-06-01
| Potter to Tolk 345 kV | 2013-12-01 | 2019-06-01 |  | No
| YOAKUM COUNTY INTERCHANGE () 230/115/13.2KV TRANSFORMER CKT 1 | 2019-06-01 | 2019-06-01
| YOAKUM COUNTY INTERCHANGE () 230/115/13.2KV TRANSFORMER CKT 2 | 2019-06-01 | 2019-06-01
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77401449 | CHERRY6 230.00 - Harrington Station East Bus 230KV CKT 1 | 2015-06-01 | 2015-06-01
Potential reservation deferral and redispatch requirement on the following upgrades due to positive MW Impact on limitations that require upgrade. No cost assignment due to negative MW impact on defined upgrade.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77401449 | CHAVES COUNTY INTERCHANGE - SAN JUAN MESA TAP 230KV CKT 1 | 2015-10-01 | 2016-06-01 |  | No
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
GSECGS | 2012-AG3-033
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
GSECGS | 77401452 | SPS | SPS | 7 | 2013-06-01 | 2039-01-01 | 2020-01-01 | 2045-08-01 | 21061 | 0 | 21061 | 141300.9559
[9 empty] | 21061 | 0 | 21061 | 141300.9559
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77401452 | Cimarron - Mathewson 345 kV Ckt 1 Accelerate | 2013-12-01 | 2015-06-01 |  | No | 777 | 10704894 | 6108.6553
| Mathewson - Tatonga 345 kV Ckt 2 Accelerate | 2013-12-01 | 2015-06-01 |  | No | 1255 | 26823745 | 9866.5809
| Mathewson 345 kV Accelerate | 2013-12-01 | 2015-06-01 |  | No | 478 | 6586619 | 3757.987
| OKLAUNION 345KV SVC | 2014-10-01 | 2019-06-01 |  | No | 18551 | 18500000 | 121567.7327
[5 empty] | Total | 21061 | 62615258 | 141300.96
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77401452 | BAILEY COUNTY INTERCHANGE - CURRY COUNTY INTERCHANGE 115KV CKT 1 | 2014-06-01 | 2015-06-01 |  | No
| Deaf Smith County Interchange 230/115 kV Transformer Ckt 1 #2 | 2013-12-01 | 2015-03-01 |  | No
| Deaf Smith County Interchange 230/115 kV Transformer Ckt 2 | 2013-12-01 | 2015-03-01 |  | No
| Line - Clark County - Thistle 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2014-07-01 |  | No
| Line - Hitchland - Woodward 345 kV dbl Ckt SPS | 2013-12-01 | 2014-07-01 |  | No
| Line - Spearville - Clark County 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt WERE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Tuco - Woodward 345 kV line OKGE | 2013-12-01 | 2014-06-01 |  | No
| Line - Tuco - Woodward 345 kV line SPS | 2013-12-01 | 2014-06-01 |  | No
| LUBBOCK SOUTH INTERCHANGE 230/115/13.2KV TRANSFORMER CKT 2 | 2013-12-01 | 2014-12-31 |  | No
| NEWHART INTERCHANGE PROJECT | 2014-06-01 | 2015-04-30 |  | No
| XFR - Thistle 345/138 kV | 2013-12-01 | 2015-01-01 |  | No
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77401452 | Amoco - Tuco 345 kV Ckt 1 | 2014-10-01 | 2020-01-01 |  | No
| Amoco 345/230 kV Transformer Ckt 1 | 2014-10-01 | 2020-01-01 |  | No
| Cherry Co - Gentleman 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co - Holt Co 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co 345 kV Terminal Upgrades | 2013-12-01 | 2018-01-01 |  | No
| Elk City 345/230 kV | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV AEPW | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV OKGE | 2013-12-01 | 2018-03-01 |  | No
| HITCHLAND INTERCHANGE () 230/115/13.2KV TRANSFORMER CKT 2 | 2015-06-01 | 2017-06-01 |  | No
| MULTI - Tuco-New Deal 345 kV | 2014-10-01 | 2018-06-01 |  | No
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77401452 | DENVER CITY INTERCHANGE N. - MUSTANG STATION N. 115KV CKT 1 | 2019-06-01 | 2019-06-01
| DENVER CITY INTERCHANGE S. - MUSTANG STATION N. 115KV CKT 2 | 2019-06-01 | 2019-06-01
| Potter to Tolk 345 kV | 2013-12-01 | 2019-06-01 |  | No
| YOAKUM COUNTY INTERCHANGE () 230/115/13.2KV TRANSFORMER CKT 1 | 2019-06-01 | 2019-06-01
| YOAKUM COUNTY INTERCHANGE () 230/115/13.2KV TRANSFORMER CKT 2 | 2019-06-01 | 2019-06-01
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77401452 | CHERRY6 230.00 - Harrington Station East Bus 230KV CKT 1 | 2015-06-01 | 2015-06-01
Potential reservation deferral and redispatch requirement on the following upgrades due to positive MW Impact on limitations that require upgrade. No cost assignment due to negative MW impact on defined upgrade.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77401452 | CHAVES COUNTY INTERCHANGE - SAN JUAN MESA TAP 230KV CKT 1 | 2015-10-01 | 2016-06-01 |  | No
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
GSECGS | 2012-AG3-034
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
GSECGS | 77401453 | SPS | SPS | 7 | 2013-06-01 | 2039-01-01 | 2020-01-01 | 2045-08-01 | 21061 | 0 | 21061 | 141300.9559
[9 empty] | 21061 | 0 | 21061 | 141300.9559
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77401453 | Cimarron - Mathewson 345 kV Ckt 1 Accelerate | 2013-12-01 | 2015-06-01 |  | No | 777 | 10704894 | 6108.6553
| Mathewson - Tatonga 345 kV Ckt 2 Accelerate | 2013-12-01 | 2015-06-01 |  | No | 1255 | 26823745 | 9866.5809
| Mathewson 345 kV Accelerate | 2013-12-01 | 2015-06-01 |  | No | 478 | 6586619 | 3757.987
| OKLAUNION 345KV SVC | 2014-10-01 | 2019-06-01 |  | No | 18551 | 18500000 | 121567.7327
[5 empty] | Total | 21061 | 62615258 | 141300.96
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77401453 | BAILEY COUNTY INTERCHANGE - CURRY COUNTY INTERCHANGE 115KV CKT 1 | 2014-06-01 | 2015-06-01 |  | No
| Deaf Smith County Interchange 230/115 kV Transformer Ckt 1 #2 | 2013-12-01 | 2015-03-01 |  | No
| Deaf Smith County Interchange 230/115 kV Transformer Ckt 2 | 2013-12-01 | 2015-03-01 |  | No
| Line - Clark County - Thistle 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2014-07-01 |  | No
| Line - Hitchland - Woodward 345 kV dbl Ckt SPS | 2013-12-01 | 2014-07-01 |  | No
| Line - Spearville - Clark County 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt WERE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Tuco - Woodward 345 kV line OKGE | 2013-12-01 | 2014-06-01 |  | No
| Line - Tuco - Woodward 345 kV line SPS | 2013-12-01 | 2014-06-01 |  | No
| LUBBOCK SOUTH INTERCHANGE 230/115/13.2KV TRANSFORMER CKT 2 | 2013-12-01 | 2014-12-31 |  | No
| NEWHART INTERCHANGE PROJECT | 2014-06-01 | 2015-04-30 |  | No
| XFR - Thistle 345/138 kV | 2013-12-01 | 2015-01-01 |  | No
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77401453 | Amoco - Tuco 345 kV Ckt 1 | 2014-10-01 | 2020-01-01 |  | No
| Amoco 345/230 kV Transformer Ckt 1 | 2014-10-01 | 2020-01-01 |  | No
| Cherry Co - Gentleman 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co - Holt Co 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co 345 kV Terminal Upgrades | 2013-12-01 | 2018-01-01 |  | No
| Elk City 345/230 kV | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV AEPW | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV OKGE | 2013-12-01 | 2018-03-01 |  | No
| HITCHLAND INTERCHANGE () 230/115/13.2KV TRANSFORMER CKT 2 | 2015-06-01 | 2017-06-01 |  | No
| MULTI - Tuco-New Deal 345 kV | 2014-10-01 | 2018-06-01 |  | No
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77401453 | DENVER CITY INTERCHANGE N. - MUSTANG STATION N. 115KV CKT 1 | 2019-06-01 | 2019-06-01
| DENVER CITY INTERCHANGE S. - MUSTANG STATION N. 115KV CKT 2 | 2019-06-01 | 2019-06-01
| Potter to Tolk 345 kV | 2013-12-01 | 2019-06-01 |  | No
| YOAKUM COUNTY INTERCHANGE () 230/115/13.2KV TRANSFORMER CKT 1 | 2019-06-01 | 2019-06-01
| YOAKUM COUNTY INTERCHANGE () 230/115/13.2KV TRANSFORMER CKT 2 | 2019-06-01 | 2019-06-01
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77401453 | CHERRY6 230.00 - Harrington Station East Bus 230KV CKT 1 | 2015-06-01 | 2015-06-01
Potential reservation deferral and redispatch requirement on the following upgrades due to positive MW Impact on limitations that require upgrade. No cost assignment due to negative MW impact on defined upgrade.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77401453 | CHAVES COUNTY INTERCHANGE - SAN JUAN MESA TAP 230KV CKT 1 | 2015-10-01 | 2016-06-01 |  | No
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
GSECGS | 2012-AG3-035
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
GSECGS | 77402179 | SPS | SPS | 203 | 2015-01-01 | 2041-01-01 | 2020-01-01 | 2046-01-01 | 0 | 0 | 1796485 | 11889819.4272
[9 empty] | 0 | 0 | 1796485 | 11889819.4272
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77402179 | AMOCO SWITCHING STATION - SUNDOWN INTERCHANGE 230KV CKT 1 | 2015-10-01 | 2016-06-01 |  | No | 201748 | 480000 | 1198423.356
| CARLISLE INTERCHANGE - TUCO INTERCHANGE 230KV CKT 1 | 2015-10-01 | 2016-06-01 |  | No | 101747 | 240000 | 604397.4768
| CHAVES COUNTY INTERCHANGE - SAN JUAN MESA TAP 230KV CKT 1 | 2015-10-01 | 2016-06-01 |  | No | 92381 | 240000 | 548761.5432
| Cimarron - Mathewson 345 kV Ckt 1 Accelerate | 2013-12-01 | 2015-06-01 |  | No | 77006 | 10704894 | 608028.9696
| JONES STATION - TUCO INTERCHANGE 230KV CKT 1 | 2015-01-01 | 2016-06-01 |  | No | 99055 | 236250 | 552933.9504
| Mathewson - Tatonga 345 kV Ckt 2 Accelerate | 2013-12-01 | 2015-06-01 |  | No | 199693 | 26823745 | 1576748.9712
| Mathewson 345 kV Accelerate | 2013-12-01 | 2015-06-01 |  | No | 47381 | 6586619 | 374113.9896
| OKLAUNION 345KV SVC | 2014-10-01 | 2019-06-01 |  | No | 977474 | 18500000 | 6426411.1704
[5 empty] | Total | 1796485 | 63811508 | 11889819.4272
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77402179 | Deaf Smith County Interchange 230/115 kV Transformer Ckt 1 #2 | 2013-12-01 | 2015-03-01
| Deaf Smith County Interchange 230/115 kV Transformer Ckt 2 | 2013-12-01 | 2015-03-01
| Line - Clark County - Thistle 345 kV dbl Ckt | 2013-12-01 | 2015-01-01
| Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2014-07-01
| Line - Hitchland - Woodward 345 kV dbl Ckt SPS | 2013-12-01 | 2014-07-01
| Line - Spearville - Clark County 345 kV dbl Ckt | 2013-12-01 | 2015-01-01
| Line - Thistle - Wichita 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01
| Line - Thistle - Wichita 345 kV dbl Ckt WERE | 2013-12-01 | 2015-01-01
| Line - Thistle - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2015-01-01
| Line - Thistle - Woodward 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01
| Line - Tuco - Woodward 345 kV line OKGE | 2013-12-01 | 2014-06-01
| Line - Tuco - Woodward 345 kV line SPS | 2013-12-01 | 2014-06-01
| LUBBOCK SOUTH INTERCHANGE 230/115/13.2KV TRANSFORMER CKT 2 | 2013-12-01 | 2014-12-31
| XFR - Thistle 345/138 kV | 2013-12-01 | 2015-01-01
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77402179 | Amoco - Tuco 345 kV Ckt 1 | 2014-10-01 | 2020-01-01 |  | No
| Amoco 345/230 kV Transformer Ckt 1 | 2014-10-01 | 2020-01-01 |  | No
| Carlisle Interchange - Wolfforth Interchange 230 kV Ckt 1 | 2019-06-01 | 2019-06-01
| Cherry Co - Gentleman 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co - Holt Co 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co 345 kV Terminal Upgrades | 2013-12-01 | 2018-01-01 |  | No
| Elk City 345/230 kV | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV AEPW | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV OKGE | 2013-12-01 | 2018-03-01 |  | No
| HITCHLAND INTERCHANGE () 230/115/13.2KV TRANSFORMER CKT 2 | 2015-06-01 | 2017-06-01 |  | No
| MULTI - Tuco-New Deal 345 kV | 2014-10-01 | 2018-06-01 |  | No
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77402179 | DENVER CITY INTERCHANGE N. - MUSTANG STATION N. 115KV CKT 1 | 2019-06-01 | 2019-06-01
| DENVER CITY INTERCHANGE S. - MUSTANG STATION N. 115KV CKT 2 | 2019-06-01 | 2019-06-01
| Potter to Tolk 345 kV | 2013-12-01 | 2019-06-01 |  | No
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77402179 | CHERRY6 230.00 - Harrington Station East Bus 230KV CKT 1 | 2015-06-01 | 2015-06-01
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
GSECGS | 2012-AG3-036
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
GSECGS | 77402184 | SPS | SPS | 203 | 2015-01-01 | 2041-01-01 | 2020-01-01 | 2046-01-01 | 0 | 0 | 1874795 | 11971119.3264
[9 empty] | 0 | 0 | 1874795 | 11971119.3264
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77402184 | AMOCO SWITCHING STATION - SUNDOWN INTERCHANGE 230KV CKT 1 | 2015-10-01 | 2016-06-01 |  | No | 203697 | 480000 | 1210000.8024
| CARLISLE INTERCHANGE - TUCO INTERCHANGE 230KV CKT 1 | 2015-10-01 | 2016-06-01 |  | No | 105293 | 240000 | 625461.408
| CHAVES COUNTY INTERCHANGE - SAN JUAN MESA TAP 230KV CKT 1 | 2015-10-01 | 2016-06-01 |  | No | 91283 | 240000 | 542239.2456
| JONES STATION - TUCO INTERCHANGE 230KV CKT 1 | 2015-01-01 | 2016-06-01 |  | No | 101610 | 236250 | 567196.188
| OKLAUNION 345KV SVC | 2014-10-01 | 2019-06-01 |  | No | 1372912 | 18500000 | 9026221.6824
[5 empty] | Total | 1874795 | 19696250 | 11971119.33
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77402184 | Deaf Smith County Interchange 230/115 kV Transformer Ckt 1 #2 | 2013-12-01 | 2015-03-01
| Deaf Smith County Interchange 230/115 kV Transformer Ckt 2 | 2013-12-01 | 2015-03-01
| Line - Clark County - Thistle 345 kV dbl Ckt | 2013-12-01 | 2015-01-01
| Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2014-07-01
| Line - Hitchland - Woodward 345 kV dbl Ckt SPS | 2013-12-01 | 2014-07-01
| Line - Spearville - Clark County 345 kV dbl Ckt | 2013-12-01 | 2015-01-01
| Line - Thistle - Wichita 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01
| Line - Thistle - Wichita 345 kV dbl Ckt WERE | 2013-12-01 | 2015-01-01
| Line - Thistle - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2015-01-01
| Line - Thistle - Woodward 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01
| Line - Tuco - Woodward 345 kV line OKGE | 2013-12-01 | 2014-06-01
| Line - Tuco - Woodward 345 kV line SPS | 2013-12-01 | 2014-06-01
| LUBBOCK SOUTH INTERCHANGE 230/115/13.2KV TRANSFORMER CKT 2 | 2013-12-01 | 2014-12-31
| XFR - Thistle 345/138 kV | 2013-12-01 | 2015-01-01
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77402184 | Amoco - Tuco 345 kV Ckt 1 | 2014-10-01 | 2020-01-01 |  | No
| Amoco 345/230 kV Transformer Ckt 1 | 2014-10-01 | 2020-01-01 |  | No
| Carlisle Interchange - Wolfforth Interchange 230 kV Ckt 1 | 2019-06-01 | 2019-06-01
| Cherry Co - Gentleman 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co - Holt Co 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co 345 kV Terminal Upgrades | 2013-12-01 | 2018-01-01 |  | No
| Elk City 345/230 kV | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV AEPW | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV OKGE | 2013-12-01 | 2018-03-01 |  | No
| HITCHLAND INTERCHANGE () 230/115/13.2KV TRANSFORMER CKT 2 | 2015-06-01 | 2017-06-01 |  | No
| MULTI - Tuco-New Deal 345 kV | 2014-10-01 | 2018-06-01 |  | No
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77402184 | DENVER CITY INTERCHANGE N. - MUSTANG STATION N. 115KV CKT 1 | 2019-06-01 | 2019-06-01
| DENVER CITY INTERCHANGE S. - MUSTANG STATION N. 115KV CKT 2 | 2019-06-01 | 2019-06-01
| Potter to Tolk 345 kV | 2013-12-01 | 2019-06-01 |  | No
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77402184 | CHERRY6 230.00 - Harrington Station East Bus 230KV CKT 1 | 2015-06-01 | 2015-06-01
Potential reservation deferral and redispatch requirement on the following upgrades due to positive MW Impact on limitations that require upgrade. No cost assignment due to negative MW impact on defined upgrade.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77402184 | Cimarron - Mathewson 345 kV Ckt 1 Accelerate | 2013-12-01 | 2015-06-01 |  | No
| Mathewson - Tatonga 345 kV Ckt 2 Accelerate | 2013-12-01 | 2015-06-01 |  | No
| Mathewson 345 kV Accelerate | 2013-12-01 | 2015-06-01 |  | No
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
INF | 2012-AG3-030
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
INF | 77409954 | SECI | EES | 200 | 2015-01-01 | 2020-01-01 | 2019-06-01 | 2024-06-01 | 0 | 15360000 | 8936649 | 23985454.05
[9 empty] | 0 | 15360000 | 8936649 | 23985454.05
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77409954 | 59TH ST - EL PASO 138KV CKT 1 | 2015-06-01 | 2017-06-01 |  |  | 618675 | 5693300 | 1913873.754
| 59TH ST - GILL ENERGY CENTER SOUTH 138KV CKT 1 | 2015-06-01 | 2017-06-01 |  |  | 548030 | 5043200 | 1695333.132
| GRAND ISLAND - SWEETWATER 345KV CKT 2 | 2013-12-01 | 2019-06-01 |  |  | 5460151 | 96288750 | 14395590.93
| HOLT - NELIGH 345KV CKT 1 | 2013-12-01 | 2019-06-01 |  |  | 1920584 | 30656000 | 4766436.606
| OKLAUNION 345KV SVC | 2014-10-01 | 2019-06-01 |  |  | 165556 | 18500000 | 527314.488
| SMAN_W_3 115.00 - SOUTH MANHATTAN 115KV CKT 1 | 2015-06-01 | 2016-06-01 |  |  | 223653 | 790000 | 686905.14
[5 empty] | Total | 8936649 | 156971250 | 23985454.05
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77409954 | 5 TRIBES - PECAN CREEK 161KV CKT 1 | 2014-06-01 | 2014-06-01
| IATAN - NASHUA 345KV CKT 1 | 2013-12-01 | 2015-06-01
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77409954 | Cherry Co - Gentleman 345 kV Ckt1 | 2013-12-01 | 2018-01-01
| Cherry Co - Holt Co 345 kV Ckt1 | 2013-12-01 | 2018-01-01
| Cherry Co 345 kV Terminal Upgrades | 2013-12-01 | 2018-01-01
| Multi - Centerton - Osage Creek 345 kV | 2014-06-01 | 2016-06-01
| Multi - Flint Creek – Centerton 345 kV and Centerton- East Centerton 161 kV | 2014-06-01 | 2014-06-01
| Neligh - Hoskins 345 kV Ckt1 | 2013-12-01 | 2019-03-01
| Neligh 345/115 kV Transformer | 2013-12-01 | 2019-03-01
| Viola - Clearwater 138kV Ckt1 | 2014-10-01 | 2018-06-01
| Viola - Gill 138kV Ckt1 | 2014-10-01 | 2018-06-01
| Viola 345/138kV Transformer Ckt 1 | 2014-10-01 | 2018-06-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77409954 | ADABELL - VBI 161KV CKT 1 | 2014-06-01 | 2016-06-01
| BEAVER - EUREKA SPRINGS 161KV CKT 1 AEPW | 2014-06-01 | 2015-06-01
| BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #1 Accelerate | 2014-06-01 | 2015-06-01
| BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #2 Accelerate | 2014-06-01 | 2017-06-01
| BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #1 Accelerate | 2014-06-01 | 2015-06-01
| BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #2 Accelerate | 2014-06-01 | 2016-06-01
| CHISHOLM - MAIZE 138KV CKT 1 #1 | 2015-06-01 | 2016-06-01
| CHISHOLM - MAIZE 138KV CKT 1 #2 | 2015-06-01 | 2017-06-01
| CIMARRON - DRAPER LAKE 345KV CKT 1 | 2019-10-01 | 2019-10-01
| EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 #1 | 2015-06-01 | 2016-06-01
| EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 #2 | 2015-06-01 | 2017-06-01
| FLINT CREEK - SILOAM SPRINGS TAP 345KV CKT 1 AEPW | 2019-06-01 | 2019-06-01
| FT SMITH - MUSKOGEE 345KV CKT 1 | 2014-06-01 | 2016-06-01
| FT SMITH (FTSMITH1) 500/345/13.8KV TRANSFORMER CKT 1 | 2014-06-01 | 2018-06-01
| GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #1 | 2015-06-01 | 2016-06-01
| GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #2 | 2015-06-01 | 2016-06-01
| HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 2013-12-01 | 2017-06-01
| Iatan - Jeffrey Energy Center 345 kV KACP | 2013-12-01 | 2019-06-01
| Iatan - Jeffrey Energy Center 345 kV WERE | 2013-12-01 | 2019-06-01
| Lacygne - Mariosa 345KV KACP | 2013-12-01 | 2019-06-01
| Muskogee - VBI 345 kV with 345/161 kV bus tie near VBI | 2014-06-01 | 2019-06-01
| VBI - Arkansas Nuclear One 345kV OKGE | 2014-06-01 | 2019-06-01
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77409954 | CIMARRON - DRAPER LAKE 345KV CKT 1 | 2014-10-01 | 2016-06-01
| HUGO POWER PLANT - VALLIANT 345 KV AEPW | 2012-07-01 | 2012-07-01
| HUGO POWER PLANT - VALLIANT 345KV CKT 1 WFEC | 2012-07-01 | 2012-07-01
Third Party Limitations.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | *Allocated E & C Cost | *Total E & C Cost
77409954 | 7JASPER 345.00 - BLACKBERRY 345KV CKT 1 #1 | 2015-06-01 | 2015-06-01 |  |  | 12225 | 100000
| 7OVERTON 345.00 () 345/161/13.8KV TRANSFORMER CKT 1 | 2014-01-01 | 2014-06-01 |  |  | 11.47% | 100%
| ARKANSAS NUCLEAR ONE - PLEASANT HILL 500KV CKT 1 | 2014-10-01 | 2014-10-01 |  |  | 11.68% | 100%
| Arkansas Nuclear One 500/345 Transformer | 2014-06-01 | 2019-06-01 |  |  | 1395827 | 12000000
| BEAVER - EUREKA SPRINGS 161KV CKT 1 SWPA | 2014-06-01 | 2015-06-01 |  |  | 0 | 0
| BUFORD 5 161.00 - BULL SHOALS 161KV CKT 1 | 2014-06-01 | 2017-06-01 |  |  | 0 | 0
| BUFORD 5 161.00 - NORFORK 161KV CKT 1 | 2014-06-01 | 2017-06-01 |  |  | 0 | 0
| CLINTON - MONTROSE 161KV CKT 1 AECI | 2015-06-01 | 2016-06-01 |  |  | 24133 | 180000
| Lacygne - Mariosa 345KV AMRN | 2013-12-01 | 2019-06-01 |  |  | 7.402% | 100%
| NORTH SLIDELL - SLIDELL 230KV CKT 1 CELE | 2015-10-01 | 2015-10-01 |  |  | 19.61% | 100%
| NORTH SLIDELL - SLIDELL 230KV CKT 1 EES | 2015-10-01 | 2015-10-01 |  |  | 19.61% | 100%
| VBI - Arkansas Nuclear One 345kV EES | 2014-06-01 | 2019-06-01 |  |  | 11.63% | 100%
[5 empty] | Total | 1432185 | 12280000
*Estimated cost allocation as a percentage of total cost is shown for third-party limitations when costs have not yet been established by the third-party.
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
INF | 2012-AG3-031
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
INF | 77409979 | SECI | EES | 200 | 2015-01-01 | 2020-01-01 | 2019-06-01 | 2024-06-01 | 0 | 15360000 | 8995376 | 24136383.024
[9 empty] | 0 | 15360000 | 8995376 | 24136383.024
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77409979 | 59TH ST - EL PASO 138KV CKT 1 | 2015-06-01 | 2017-06-01 |  |  | 619426 | 5693300 | 1916196.96
| 59TH ST - GILL ENERGY CENTER SOUTH 138KV CKT 1 | 2015-06-01 | 2017-06-01 |  |  | 548695 | 5043200 | 1697390.316
| GRAND ISLAND - SWEETWATER 345KV CKT 2 | 2013-12-01 | 2019-06-01 |  |  | 5508209 | 96288750 | 14522295
| HOLT - NELIGH 345KV CKT 1 | 2013-12-01 | 2019-06-01 |  |  | 1933778 | 30656000 | 4799181
| OKLAUNION 345KV SVC | 2014-10-01 | 2019-06-01 |  |  | 158563 | 18500000 | 505040.994
| SMAN_W_3 115.00 - SOUTH MANHATTAN 115KV CKT 1 | 2015-06-01 | 2016-06-01 |  |  | 226705 | 790000 | 696278.754
[5 empty] | Total | 8995376 | 156971250 | 24136383.02
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77409979 | 5 TRIBES - PECAN CREEK 161KV CKT 1 | 2014-06-01 | 2014-06-01
| IATAN - NASHUA 345KV CKT 1 | 2013-12-01 | 2015-06-01
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77409979 | Cherry Co - Gentleman 345 kV Ckt1 | 2013-12-01 | 2018-01-01
| Cherry Co - Holt Co 345 kV Ckt1 | 2013-12-01 | 2018-01-01
| Cherry Co 345 kV Terminal Upgrades | 2013-12-01 | 2018-01-01
| Multi - Centerton - Osage Creek 345 kV | 2014-06-01 | 2016-06-01
| Multi - Flint Creek – Centerton 345 kV and Centerton- East Centerton 161 kV | 2014-06-01 | 2014-06-01
| Neligh - Hoskins 345 kV Ckt1 | 2013-12-01 | 2019-03-01
| Neligh 345/115 kV Transformer | 2013-12-01 | 2019-03-01
| Viola - Clearwater 138kV Ckt1 | 2014-10-01 | 2018-06-01
| Viola - Gill 138kV Ckt1 | 2014-10-01 | 2018-06-01
| Viola 345/138kV Transformer Ckt 1 | 2014-10-01 | 2018-06-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77409979 | ADABELL - VBI 161KV CKT 1 | 2014-06-01 | 2016-06-01
| BEAVER - EUREKA SPRINGS 161KV CKT 1 AEPW | 2014-06-01 | 2015-06-01
| BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #1 Accelerate | 2014-06-01 | 2015-06-01
| BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #2 Accelerate | 2014-06-01 | 2017-06-01
| BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #1 Accelerate | 2014-06-01 | 2015-06-01
| BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #2 Accelerate | 2014-06-01 | 2016-06-01
| CHISHOLM - MAIZE 138KV CKT 1 #1 | 2015-06-01 | 2016-06-01
| CHISHOLM - MAIZE 138KV CKT 1 #2 | 2015-06-01 | 2017-06-01
| CIMARRON - DRAPER LAKE 345KV CKT 1 | 2019-10-01 | 2019-10-01
| EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 #1 | 2015-06-01 | 2016-06-01
| EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 #2 | 2015-06-01 | 2017-06-01
| FLINT CREEK - SILOAM SPRINGS TAP 345KV CKT 1 AEPW | 2019-06-01 | 2019-06-01
| FT SMITH - MUSKOGEE 345KV CKT 1 | 2014-06-01 | 2016-06-01
| FT SMITH (FTSMITH1) 500/345/13.8KV TRANSFORMER CKT 1 | 2014-06-01 | 2018-06-01
| GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #1 | 2015-06-01 | 2016-06-01
| GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #2 | 2015-06-01 | 2016-06-01
| HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 2013-12-01 | 2017-06-01
| Iatan - Jeffrey Energy Center 345 kV KACP | 2013-12-01 | 2019-06-01
| Iatan - Jeffrey Energy Center 345 kV WERE | 2013-12-01 | 2019-06-01
| Lacygne - Mariosa 345KV KACP | 2013-12-01 | 2019-06-01
| Muskogee - VBI 345 kV with 345/161 kV bus tie near VBI | 2014-06-01 | 2019-06-01
| VBI - Arkansas Nuclear One 345kV OKGE | 2014-06-01 | 2019-06-01
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77409979 | CIMARRON - DRAPER LAKE 345KV CKT 1 | 2014-10-01 | 2016-06-01
| HUGO POWER PLANT - VALLIANT 345 KV AEPW | 2012-07-01 | 2012-07-01
| HUGO POWER PLANT - VALLIANT 345KV CKT 1 WFEC | 2012-07-01 | 2012-07-01
Third Party Limitations.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | *Allocated E & C Cost | *Total E & C Cost
77409979 | 7JASPER 345.00 - BLACKBERRY 345KV CKT 1 #1 | 2015-06-01 | 2015-06-01 |  |  | 12727 | 100000
| 7OVERTON 345.00 () 345/161/13.8KV TRANSFORMER CKT 1 | 2014-01-01 | 2014-06-01 |  |  | 11.86% | 100%
| ARKANSAS NUCLEAR ONE - PLEASANT HILL 500KV CKT 1 | 2014-10-01 | 2014-10-01 |  |  | 11.68% | 100%
| Arkansas Nuclear One 500/345 Transformer | 2014-06-01 | 2019-06-01 |  |  | 1390370 | 12000000
| BEAVER - EUREKA SPRINGS 161KV CKT 1 SWPA | 2014-06-01 | 2015-06-01 |  |  | 0 | 0
| BUFORD 5 161.00 - BULL SHOALS 161KV CKT 1 | 2014-06-01 | 2017-06-01 |  |  | 0 | 0
| BUFORD 5 161.00 - NORFORK 161KV CKT 1 | 2014-06-01 | 2017-06-01 |  |  | 0 | 0
| CLINTON - MONTROSE 161KV CKT 1 AECI | 2015-06-01 | 2016-06-01 |  |  | 24846 | 180000
| Lacygne - Mariosa 345KV AMRN | 2013-12-01 | 2019-06-01 |  |  | 7.504% | 100%
| VBI - Arkansas Nuclear One 345kV EES | 2014-06-01 | 2019-06-01 |  |  | 11.59% | 100%
[5 empty] | Total | 1427943 | 12280000
*Estimated cost allocation as a percentage of total cost is shown for third-party limitations when costs have not yet been established by the third-party.
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
KBPU | 2012-AG3-029
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
KBPU | 77155691 | WR | KACY | 2 | 2013-04-01 | 2030-08-01 | 2019-06-01 | 2036-10-01 | 0 | 364832 | 49477 | 197128.0688
[9 empty] | 0 | 364832 | 49477 | 197128.0688
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77155691 | 59TH ST - EL PASO 138KV CKT 1 | 2015-06-01 | 2017-06-01 |  | No | 5288 | 5693300 | 24222.5568
| 59TH ST - GILL ENERGY CENTER SOUTH 138KV CKT 1 | 2015-06-01 | 2017-06-01 |  | No | 4684 | 5043200 | 21455.8448
| GRAND ISLAND - SWEETWATER 345KV CKT 2 | 2013-12-01 | 2019-06-01 |  | No | 25841 | 96288750 | 96661.7184
| HOLT - NELIGH 345KV CKT 1 | 2013-12-01 | 2019-06-01 |  | No | 7162 | 30656000 | 25218.2528
| KAW WEST 5 161/69KV TRANSFORMER CKT 1 | 2014-06-01 | 2014-06-01 |  |  | 0 | 0 | 0
| SMAN_W_3 115.00 - SOUTH MANHATTAN 115KV CKT 1 | 2015-06-01 | 2016-06-01 |  | No | 6502 | 790000 | 29569.696
[5 empty] | Total | 49477 | 138471250 | 197128.07
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77155691 | Auburn Road 230/115/13.8 kV Ckt 1 Auto Upgrade | 2013-12-01 | 2014-06-01 |  | No
| IATAN - NASHUA 345KV CKT 1 | 2013-12-01 | 2015-06-01 |  | No
| Line - Clark County - Thistle 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2014-07-01 |  | No
| Line - Hitchland - Woodward 345 kV dbl Ckt SPS | 2013-12-01 | 2014-07-01 |  | No
| Line - Spearville - Clark County 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt WERE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Tuco - Woodward 345 kV line OKGE | 2013-12-01 | 2014-06-01 |  | No
| Line - Tuco - Woodward 345 kV line SPS | 2013-12-01 | 2014-06-01 |  | No
| MOUNDRIDGE 138/115KV TRANSFORMER CKT 2 | 2013-12-01 | 2014-12-01 |  | No
| XFR - Thistle 345/138 kV | 2013-12-01 | 2015-01-01 |  | No
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77155691 | Cherry Co - Gentleman 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co - Holt Co 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co 345 kV Terminal Upgrades | 2013-12-01 | 2018-01-01 |  | No
| Cowskin - Westlink 69 kV Ckt 1 | 2013-12-01 | 2015-12-01 |  | No
| Hoover South - Tyler 69 kV Ckt 1 | 2013-12-01 | 2014-06-01 |  | No
| Neligh - Hoskins 345 kV Ckt1 | 2013-12-01 | 2019-03-01 |  | No
| Neligh 345/115 kV Transformer | 2013-12-01 | 2019-03-01 |  | No
| Tyler - Westlink 69 kV Ckt 1 | 2013-12-01 | 2015-06-01 |  | No
| Viola - Clearwater 138kV Ckt1 | 2014-10-01 | 2018-06-01 |  | No
| Viola - Gill 138kV Ckt1 | 2014-10-01 | 2018-06-01 |  | No
| Viola 345/138kV Transformer Ckt 1 | 2014-10-01 | 2018-06-01 |  | No
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77155691 | BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #1 Accelerate | 2014-06-01 | 2015-06-01 |  | No
| BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #2 Accelerate | 2014-06-01 | 2017-06-01 |  | No
| BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #1 Accelerate | 2014-06-01 | 2015-06-01 |  | No
| BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #2 Accelerate | 2014-06-01 | 2016-06-01 |  | No
| CHISHOLM - MAIZE 138KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| CHISHOLM - MAIZE 138KV CKT 1 #2 | 2015-06-01 | 2017-06-01 |  | No
| EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 #2 | 2015-06-01 | 2017-06-01 |  | No
| FT SMITH - MUSKOGEE 345KV CKT 1 | 2014-06-01 | 2016-06-01 |  | No
| GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #2 | 2015-06-01 | 2016-06-01 |  | No
| HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 2013-12-01 | 2017-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV KACP | 2013-12-01 | 2019-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV WERE | 2013-12-01 | 2019-06-01 |  | No
| Lacygne - Mariosa 345KV KACP | 2013-12-01 | 2019-06-01 |  | No
| Muskogee - VBI 345 kV with 345/161 kV bus tie near VBI | 2014-06-01 | 2019-06-01 |  | No
| VBI - Arkansas Nuclear One 345kV OKGE | 2014-06-01 | 2019-06-01 |  | No
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77155691 | CIRCLE - RICE_CO 230KV CKT 1 | 2012-10-01 | 2012-11-15
| LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01
| LYONS - RICE_CO 115KV CKT 1 | 2012-10-01 | 2013-04-01
| LYONS - WHEATLAND 115KV CKT 1 #1 | 2012-10-01 | 2013-07-15
| LYONS - WHEATLAND 115KV CKT 1 #2 | 2012-10-01 | 2013-07-15
| RICE_CO 230/115KV TRANSFORMER CKT 1 | 2012-10-01 | 2012-11-15
| TATONGA - WOODWARD 345KV CKT 1 | 2010-01-01 | 2010-01-01
Third Party Limitations.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | *Allocated E & C Cost | *Total E & C Cost
77155691 | 7JASPER 345.00 - BLACKBERRY 345KV CKT 1 #1 | 2015-06-01 | 2015-06-01 |  |  | 39 | 100000
| ARKANSAS NUCLEAR ONE - PLEASANT HILL 500KV CKT 1 | 2014-10-01 | 2014-10-01 |  |  | 0.01262% | 100%
| Arkansas Nuclear One 500/345 Transformer | 2014-06-01 | 2019-06-01 |  | No | 1213 | 12000000
| Lacygne - Mariosa 345KV AMRN | 2013-12-01 | 2019-06-01 |  | No | 0.09597% | 100%
| VBI - Arkansas Nuclear One 345kV EES | 2014-06-01 | 2019-06-01 |  | No | 0.01011% | 100%
[5 empty] | Total | 1252 | 12100000
*Estimated cost allocation as a percentage of total cost is shown for third-party limitations when costs have not yet been established by the third-party.
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
KPP | 2012-AG3-024
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
KPP | 77398979 | WR | WR | 15 | 2013-06-01 | 2023-06-01 | 2019-06-01 | 2029-06-01 | 2466000 | 0 | 3173666 | 9483093.108
[9 empty] | 2466000 | 0 | 3173666 | 9483093.108
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77398979 | GRAND ISLAND - SWEETWATER 345KV CKT 2 | 2013-12-01 | 2019-06-01 |  | No | 207454 | 96288750 | 634268.772
| HYDRALIC JCT NORTH - MACARTHUR 69KV CKT 1 | 2018-06-01 | 2018-06-01 |  |  | 1745900 | 1745900 | 5150282.52
| HYDRALIC JCT NORTH - OAKLAWN 69KV CKT 1 | 2018-06-01 | 2018-06-01 |  |  | 1098100 | 1098100 | 3239317.956
| SMAN_W_3 115.00 - SOUTH MANHATTAN 115KV CKT 1 | 2015-06-01 | 2016-06-01 |  |  | 78476 | 790000 | 285836.592
| ST JOHN - ST_JOHN 115KV CKT 1 MIDW | 2013-12-01 | 2016-06-01 |  | No | 19438 | 450000 | 55669.668
| ST JOHN - ST_JOHN 115KV CKT 1 MKEC | 2013-12-01 | 2016-06-01 |  | No | 24298 | 562500 | 117717.6
[5 empty] | Total | 3173666 | 100935250 | 9483093.11
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77398979 | Gill 138/69 kV Transformer Ckt 3 | 2015-06-01 | 2015-12-01
| HARPER - MILAN TAP 138KV CKT 1 #1 | 2013-12-01 | 2014-12-01 |  | No
| IATAN - NASHUA 345KV CKT 1 | 2013-12-01 | 2015-06-01 |  | No
| Line - Clark County - Thistle 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2014-07-01 |  | No
| Line - Hitchland - Woodward 345 kV dbl Ckt SPS | 2013-12-01 | 2014-07-01 |  | No
| Line - Spearville - Clark County 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt WERE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Tuco - Woodward 345 kV line OKGE | 2013-12-01 | 2014-06-01 |  | No
| Line - Tuco - Woodward 345 kV line SPS | 2013-12-01 | 2014-06-01 |  | No
| PRATT - ST JOHN 115KV CKT 1 | 2015-06-01 | 2015-06-01
| XFR - Thistle 345/138 kV | 2013-12-01 | 2015-01-01 |  | No
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77398979 | Cherry Co - Gentleman 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co - Holt Co 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co 345 kV Terminal Upgrades | 2013-12-01 | 2018-01-01 |  | No
| Neligh - Hoskins 345 kV Ckt1 | 2013-12-01 | 2019-03-01 |  | No
| Neligh 345/115 kV Transformer | 2013-12-01 | 2019-03-01 |  | No
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77398979 | CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | 2013-12-01 | 2017-06-01 |  | No
| CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | 2013-12-01 | 2017-06-01 |  | No
| FLATRDG3 138.00 - HARPER 138KV CKT 1 | 2013-12-01 | 2013-12-01 | 2013-06-15
| HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | 2013-12-01 | 2017-06-01 |  | No
| HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 2013-12-01 | 2017-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV KACP | 2013-12-01 | 2019-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV WERE | 2013-12-01 | 2019-06-01 |  | No
| Lacygne - Mariosa 345KV KACP | 2013-12-01 | 2019-06-01 |  | No
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77398979 | ALEXANDER - PRATT 115KV CKT 1 | 2009-12-01 | 2013-06-01
| ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 2009-12-01 | 2013-06-01
| BARBER - MEDICINE LODGE 115KV CKT 1 | 2009-12-01 | 2013-06-01
| BARBER - SAWYER 115KV CKT 1 | 2009-12-01 | 2013-06-01
| BARBER (BARBER 4) 138/115/2.72KV TRANSFORMER CKT 1 | 2009-12-01 | 2013-06-01
| CLIFTON - GREENLEAF 115KV CKT 1 | 2011-06-01 | 2013-06-01
| FLATRDG3 138.00 - MEDICINE LODGE 138KV CKT 1 | 2009-12-01 | 2013-06-01
| FLATRDG3 138.00 - HARPER 138KV CKT 1 | 2009-12-01 | 2013-06-01
| GREENLEAF - KNOB HILL 115KV CKT 1 MKEC | 2013-06-01 | 2013-06-01
| NORTHWEST - TATONGA 345KV CKT 1 | 2010-01-01 | 2010-01-01
| Spearville 345/115/13.8kV Transformer CKT 3 | 2013-10-01 | 2015-06-01
| TATONGA - WOODWARD 345KV CKT 1 | 2010-01-01 | 2010-01-01
Potential reservation deferral and redispatch requirement on the following upgrades due to positive MW Impact on limitations that require upgrade. No cost assignment due to negative MW impact on defined upgrade.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77398979 | HOLT - NELIGH 345KV CKT 1 | 2013-12-01 | 2019-06-01 |  | No
Third Party Limitations.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | *Allocated E & C Cost | *Total E & C Cost
77398979 | Lacygne - Mariosa 345KV AMRN | 2013-12-01 | 2019-06-01 |  | No | 2.757% | 100%
[5 empty] | Total | 0 | 0
*Estimated cost allocation as a percentage of total cost is shown for third-party limitations when costs have not yet been established by the third-party.
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
KPP | 2012-AG3-025
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
KPP | 77405406 | SPA | WR | 1 | 2013-06-01 | 2023-06-01 | 2013-12-01 | 2023-12-01 | 0 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0 | 0
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77405406 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
KPP | 2012-AG3-026
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
KPP | 77405413 | KACY | WR | 3 | 2013-06-01 | 2023-06-01 | 2013-12-01 | 2023-12-01 | 540000 | 0 | 1178583 | 2401955.196
[9 empty] | 540000 | 0 | 1178583 | 2401955.196
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77405413 | WOLF CREEK 345/69KV TRANSFORMER CKT 1 | 2014-10-01 | 2017-06-01 |  |  | 1178583 | 4400000 | 2401955.196
[5 empty] | Total | 1178583 | 4400000 | 2401955.2
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77405413 | GEARY 7 345.00 (GEARY1X) 345/115/13.8KV TRANSFORMER CKT 1 | 2019-06-01 | 2019-06-01
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77405413 | BUTLER - WEAVER 138KV CKT 1 | 2013-12-01 | 2017-06-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77405413 | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 2013-12-01 | 2017-06-01
| Iatan - Jeffrey Energy Center 345 kV KACP | 2013-12-01 | 2019-06-01
| Iatan - Jeffrey Energy Center 345 kV WERE | 2013-12-01 | 2019-06-01
| Lacygne - Mariosa 345KV KACP | 2013-12-01 | 2019-06-01
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77405413 | ALEXANDER - PRATT 115KV CKT 1 | 2009-12-01 | 2013-06-01
| ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 2009-12-01 | 2013-06-01
| BARBER - SAWYER 115KV CKT 1 | 2009-12-01 | 2013-06-01
| BARBER (BARBER 4) 138/115/2.72KV TRANSFORMER CKT 1 | 2009-12-01 | 2013-06-01
| FLATRDG3 138.00 - MEDICINE LODGE 138KV CKT 1 | 2009-12-01 | 2013-06-01
| FLATRDG3 138.00 - HARPER 138KV CKT 1 | 2009-12-01 | 2013-06-01
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
KPP | 2012-AG3-027
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
KPP | 77405416 | WR | WR | 9 | 2013-06-01 | 2023-06-01 | 2019-06-01 | 2029-06-01 | 1476000 | 0 | 3337224 | 10162713.456
[9 empty] | 1476000 | 0 | 3337224 | 10162713.456
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77405416 | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 MIDW | 2013-12-01 | 2018-06-01 |  | No | 33502 | 13864500 | 92828.424
| SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 WERE | 2013-12-01 | 2018-06-01 |  | No | 82305 | 34061343.75 | 284208.648
| WOLF CREEK 345/69KV TRANSFORMER CKT 1 | 2014-10-01 | 2017-06-01 |  | No | 3221417 | 4400000 | 9785676.384
[5 empty] | Total | 3337224 | 52325843.75 | 10162713.46
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77405416 | GEARY 7 345.00 (GEARY1X) 345/115/13.8KV TRANSFORMER CKT 1 | 2019-06-01 | 2019-06-01
| Line - Clark County - Thistle 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2014-07-01 |  | No
| Line - Hitchland - Woodward 345 kV dbl Ckt SPS | 2013-12-01 | 2014-07-01 |  | No
| Line - Spearville - Clark County 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt WERE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Tuco - Woodward 345 kV line OKGE | 2013-12-01 | 2014-06-01
| Line - Tuco - Woodward 345 kV line SPS | 2013-12-01 | 2014-06-01
| XFR - Thistle 345/138 kV | 2013-12-01 | 2015-01-01 |  | No
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77405416 | BUTLER - WEAVER 138KV CKT 1 | 2013-12-01 | 2017-06-01 |  | No
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77405416 | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 2013-12-01 | 2017-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV KACP | 2013-12-01 | 2019-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV WERE | 2013-12-01 | 2019-06-01 |  | No
| Lacygne - Mariosa 345KV KACP | 2013-12-01 | 2019-06-01 |  | No
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77405416 | ALEXANDER - PRATT 115KV CKT 1 | 2009-12-01 | 2013-06-01
| ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 2009-12-01 | 2013-06-01
| BARBER - SAWYER 115KV CKT 1 | 2009-12-01 | 2013-06-01
| BARBER (BARBER 4) 138/115/2.72KV TRANSFORMER CKT 1 | 2009-12-01 | 2013-06-01
| FLATRDG3 138.00 - MEDICINE LODGE 138KV CKT 1 | 2009-12-01 | 2013-06-01
| FLATRDG3 138.00 - HARPER 138KV CKT 1 | 2009-12-01 | 2013-06-01
| LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01
Potential reservation deferral and redispatch requirement on the following upgrades due to positive MW Impact on limitations that require upgrade. No cost assignment due to negative MW impact on defined upgrade.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77405416 | Lacygne - Mariosa 345KV AMRN | 2013-12-01 | 2019-06-01 |  | No
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
KPP | 2012-AG3-028
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
KPP | 77405426 | WR | WR | 4 | 2013-06-01 | 2015-01-01 | 2019-06-01 | 2021-01-01 | 0 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0 | 0
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77405426 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77405426 | GEARY 7 345.00 (GEARY1X) 345/115/13.8KV TRANSFORMER CKT 1 | 2019-06-01 | 2019-06-01
| Gill 138/69 kV Transformer Ckt 3 | 2015-06-01 | 2015-12-01 |  | No
| HARPER - MILAN TAP 138KV CKT 1 #1 | 2013-12-01 | 2014-12-01
| IATAN - NASHUA 345KV CKT 1 | 2013-12-01 | 2015-06-01 |  | No
| Line - Clark County - Thistle 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2014-07-01 |  | No
| Line - Hitchland - Woodward 345 kV dbl Ckt SPS | 2013-12-01 | 2014-07-01 |  | No
| Line - Spearville - Clark County 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt WERE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Tuco - Woodward 345 kV line OKGE | 2013-12-01 | 2014-06-01
| Line - Tuco - Woodward 345 kV line SPS | 2013-12-01 | 2014-06-01
| XFR - Thistle 345/138 kV | 2013-12-01 | 2015-01-01 |  | No
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77405426 | BUTLER - WEAVER 138KV CKT 1 | 2013-12-01 | 2017-06-01 |  | No
| Cowskin - Westlink 69 kV Ckt 1 | 2013-12-01 | 2015-12-01 |  | No
| Hoover South - Tyler 69 kV Ckt 1 | 2013-12-01 | 2014-06-01
| Tyler - Westlink 69 kV Ckt 1 | 2013-12-01 | 2015-06-01
| Viola - Clearwater 138kV Ckt1 | 2014-10-01 | 2018-06-01 |  | No
| Viola - Gill 138kV Ckt1 | 2014-10-01 | 2018-06-01 |  | No
| Viola 345/138kV Transformer Ckt 1 | 2014-10-01 | 2018-06-01 |  | No
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77405426 | CHISHOLM - MAIZE 138KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| CHISHOLM - MAIZE 138KV CKT 1 #2 | 2015-06-01 | 2017-06-01 |  | No
| CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | 2013-12-01 | 2017-06-01
| CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | 2013-12-01 | 2017-06-01
| EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 #2 | 2015-06-01 | 2017-06-01 |  | No
| HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | 2013-12-01 | 2017-06-01
| HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 2013-12-01 | 2017-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV KACP | 2013-12-01 | 2019-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV WERE | 2013-12-01 | 2019-06-01 |  | No
| Lacygne - Mariosa 345KV KACP | 2013-12-01 | 2019-06-01 |  | No
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77405426 | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | 2009-12-01 | 2013-06-01
| LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01
Potential reservation deferral and redispatch requirement on the following upgrades due to positive MW Impact on limitations that require upgrade. No cost assignment due to negative MW impact on defined upgrade.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77405426 | 59TH ST - EL PASO 138KV CKT 1 | 2015-06-01 | 2017-06-01 |  | No
| 59TH ST - GILL ENERGY CENTER SOUTH 138KV CKT 1 | 2015-06-01 | 2017-06-01 |  | No
| CLINTON - MONTROSE 161KV CKT 1 AECI | 2015-06-01 | 2016-06-01 |  | No
| Lacygne - Mariosa 345KV AMRN | 2013-12-01 | 2019-06-01 |  | No
| SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 MIDW | 2013-12-01 | 2018-06-01 |  | No
| SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 WERE | 2013-12-01 | 2018-06-01 |  | No
| WOLF CREEK 345/69KV TRANSFORMER CKT 1 | 2014-10-01 | 2017-06-01 |  | No
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
MIDW | 2012-AG3-013
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
MIDW | 77410531 | WR | WR | 28 | 2015-06-01 | 2038-06-01 | 2019-06-01 | 2042-06-01 | 5040000 | 0 | 6946657 | 32402705.0904
[9 empty] | 5040000 | 0 | 6946657 | 32402705.0904
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77410531 | Cimarron - Mathewson 345 kV Ckt 1 Accelerate | 2013-12-01 | 2015-06-01 |  |  | 18396 | 10704894 | 126129.6264
| GRAND ISLAND - SWEETWATER 345KV CKT 2 | 2013-12-01 | 2019-06-01 |  | No | 1784771 | 96288750 | 7709811.4344
| HOLT - NELIGH 345KV CKT 1 | 2013-12-01 | 2019-06-01 |  | No | 431820 | 30656000 | 1755899.6076
| Mathewson - Tatonga 345 kV Ckt 2 Accelerate | 2013-12-01 | 2015-06-01 |  |  | 99681 | 26823745 | 683449.0572
| Mathewson 345 kV Accelerate | 2013-12-01 | 2015-06-01 |  |  | 11319 | 6586619 | 77607.1428
| SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 MIDW | 2013-12-01 | 2018-06-01 |  | No | 1302553 | 13864500 | 5301516.2196
| SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 WERE | 2013-12-01 | 2018-06-01 |  | No | 3200022 | 34061343.75 | 16153667.6112
| ST JOHN - ST_JOHN 115KV CKT 1 MIDW | 2013-12-01 | 2016-06-01 |  | No | 43598 | 450000 | 183412.1016
| ST JOHN - ST_JOHN 115KV CKT 1 MKEC | 2013-12-01 | 2016-06-01 |  | No | 54497 | 562500 | 411212.2896
[5 empty] | Total | 6946657 | 219998351.75 | 32402705.0904
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77410531 | GEARY 7 345.00 (GEARY1X) 345/115/13.8KV TRANSFORMER CKT 1 | 2019-06-01 | 2019-06-01
| HARPER - MILAN TAP 138KV CKT 1 #1 | 2013-12-01 | 2014-12-01
| HAYS PLANT - SOUTH HAYS 115KV CKT 1 #2 | 2014-01-01 | 2015-06-01
| Line - Clark County - Thistle 345 kV dbl Ckt | 2013-12-01 | 2015-01-01
| Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2014-07-01
| Line - Hitchland - Woodward 345 kV dbl Ckt SPS | 2013-12-01 | 2014-07-01
| Line - Spearville - Clark County 345 kV dbl Ckt | 2013-12-01 | 2015-01-01
| Line - Thistle - Wichita 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01
| Line - Thistle - Wichita 345 kV dbl Ckt WERE | 2013-12-01 | 2015-01-01
| Line - Thistle - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2015-01-01
| Line - Thistle - Woodward 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01
| Line - Tuco - Woodward 345 kV line OKGE | 2013-12-01 | 2014-06-01
| Line - Tuco - Woodward 345 kV line SPS | 2013-12-01 | 2014-06-01
| XFR - Thistle 345/138 kV | 2013-12-01 | 2015-01-01
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77410531 | Cherry Co - Gentleman 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co - Holt Co 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co 345 kV Terminal Upgrades | 2013-12-01 | 2018-01-01 |  | No
| Neligh - Hoskins 345 kV Ckt1 | 2013-12-01 | 2019-03-01 |  | No
| Neligh 345/115 kV Transformer | 2013-12-01 | 2019-03-01 |  | No
| Viola - Clearwater 138kV Ckt1 | 2014-10-01 | 2018-06-01 |  | No
| Viola - Gill 138kV Ckt1 | 2014-10-01 | 2018-06-01 |  | No
| Viola 345/138kV Transformer Ckt 1 | 2014-10-01 | 2018-06-01 |  | No
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77410531 | CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | 2013-12-01 | 2017-06-01 |  | No
| CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | 2013-12-01 | 2017-06-01 |  | No
| HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | 2013-12-01 | 2017-06-01 |  | No
| HAYS PLANT - VINE STREET 115KV CKT 1 | 2014-01-01 | 2017-06-01 |  | No
| HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 2013-12-01 | 2017-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV KACP | 2013-12-01 | 2019-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV WERE | 2013-12-01 | 2019-06-01 |  | No
| Lacygne - Mariosa 345KV KACP | 2013-12-01 | 2019-06-01 |  | No
| Mullergren - Reno 345kV Dbl CKT MKEC | 2014-01-01 | 2019-06-01 |  | No
| Mullergren - Reno 345kV Dbl CKT WERE | 2014-01-01 | 2019-06-01 |  | No
| Spearville - Mullergren 345kV Dbl CKT | 2014-01-01 | 2019-06-01 |  | No
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77410531 | ALEXANDER - PRATT 115KV CKT 1 | 2009-12-01 | 2013-06-01
| BARBER - SAWYER 115KV CKT 1 | 2009-12-01 | 2013-06-01
| BARBER (BARBER 4) 138/115/2.72KV TRANSFORMER CKT 1 | 2009-12-01 | 2013-06-01
| CIRCLE - RICE_CO 230KV CKT 1 | 2012-10-01 | 2012-11-15
| FLATRDG3 138.00 - MEDICINE LODGE 138KV CKT 1 | 2009-12-01 | 2013-06-01
| LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01
| LYONS - RICE_CO 115KV CKT 1 | 2012-10-01 | 2013-04-01
| LYONS - WHEATLAND 115KV CKT 1 #1 | 2012-10-01 | 2013-07-15
| LYONS - WHEATLAND 115KV CKT 1 #2 | 2012-10-01 | 2013-07-15
| Mullergren - Reno 345kV Dbl CKT MKEC | 2013-10-01 | 2019-06-01
| Mullergren - Reno 345kV Dbl CKT WERE | 2013-10-01 | 2019-06-01
| RICE_CO 230/115KV TRANSFORMER CKT 1 | 2012-10-01 | 2012-11-15
| Spearville - Mullergren 345kV Dbl CKT | 2013-10-01 | 2019-06-01
| TATONGA - WOODWARD 345KV CKT 1 | 2010-01-01 | 2010-01-01
Third Party Limitations.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | *Allocated E & C Cost | *Total E & C Cost
77410531 | Lacygne - Mariosa 345KV AMRN | 2013-12-01 | 2019-06-01 |  | No | 1.427% | 100%
[5 empty] | Total | 0 | 0
*Estimated cost allocation as a percentage of total cost is shown for third-party limitations when costs have not yet been established by the third-party.
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
NPPM | 2012-AG3-012
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
NPPM | 77407262 | NPPD | NPPD | 115 | 2018-09-01 | 2028-09-01 |  |  | 1420998 | 0 | 1420998 | 4131126.192
[9 empty] | 1420998 | 0 | 1420998 | 4131126.192
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77407262 | GRAND ISLAND - SWEETWATER 345KV CKT 2 | 2013-12-01 | 2019-06-01 |  |  | 1420998 | 96288750 | 4131126.192
[5 empty] | Total | 1420998 | 96288750 | 4131126.19
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77407262 | Cherry Co - Gentleman 345 kV Ckt1 | 2013-12-01 | 2018-01-01
| Cherry Co - Holt Co 345 kV Ckt1 | 2013-12-01 | 2018-01-01
| Cherry Co 345 kV Terminal Upgrades | 2013-12-01 | 2018-01-01
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77407262 | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 2013-12-01 | 2017-06-01
| Iatan - Jeffrey Energy Center 345 kV KACP | 2013-12-01 | 2019-06-01
| Iatan - Jeffrey Energy Center 345 kV WERE | 2013-12-01 | 2019-06-01
| Lacygne - Mariosa 345KV KACP | 2013-12-01 | 2019-06-01
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77407262 | CLIFTON - GREENLEAF 115KV CKT 1 | 2011-06-01 | 2013-06-01
| GREENLEAF - KNOB HILL 115KV CKT 1 MKEC | 2013-06-01 | 2013-06-01
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
SPSM | 2012-AG3-009
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
SPSM | 77341873 | WFEC | SPS | 36 | 2017-06-01 | 2047-06-01 | 2020-01-01 | 2050-01-01 | 146243 | 0 | 146243 | 905317.668
[9 empty] | 146243 | 0 | 146243 | 905317.668
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77341873 | AMOCO SWITCHING STATION - SUNDOWN INTERCHANGE 230KV CKT 1 | 2015-10-01 | 2016-06-01 |  |  | 54421 | 480000 | 358472.988
| CARLISLE INTERCHANGE - TUCO INTERCHANGE 230KV CKT 1 | 2015-10-01 | 2016-06-01 |  |  | 17236 | 240000 | 113534.136
| CHAVES COUNTY INTERCHANGE - SAN JUAN MESA TAP 230KV CKT 1 | 2015-10-01 | 2016-06-01 |  |  | 37294 | 240000 | 245656.872
| FLETCHER - MARLOW JCT 69KV CKT 1 | 2019-06-01 | 2019-06-01 |  |  | 16307 | 225000 | 64551.6
| JONES STATION - TUCO INTERCHANGE 230KV CKT 1 | 2015-01-01 | 2016-06-01 |  |  | 17619 | 236250 | 109060.38
| LAKE CREEK - LONEWOLF 69KV CKT 1 | 2014-01-01 | 2016-06-01 |  |  | 3366 | 225000 | 14041.692
[5 empty] | Total | 146243 | 1646250 | 905317.67
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77341873 | Deaf Smith County Interchange 230/115 kV Transformer Ckt 1 #2 | 2013-12-01 | 2015-03-01
| Deaf Smith County Interchange 230/115 kV Transformer Ckt 2 | 2013-12-01 | 2015-03-01
| Line - Clark County - Thistle 345 kV dbl Ckt | 2013-12-01 | 2015-01-01
| Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2014-07-01
| Line - Hitchland - Woodward 345 kV dbl Ckt SPS | 2013-12-01 | 2014-07-01
| Line - Spearville - Clark County 345 kV dbl Ckt | 2013-12-01 | 2015-01-01
| Line - Thistle - Wichita 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01
| Line - Thistle - Wichita 345 kV dbl Ckt WERE | 2013-12-01 | 2015-01-01
| Line - Thistle - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2015-01-01
| Line - Thistle - Woodward 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01
| Line - Tuco - Woodward 345 kV line OKGE | 2013-12-01 | 2014-06-01
| Line - Tuco - Woodward 345 kV line SPS | 2013-12-01 | 2014-06-01
| XFR - Thistle 345/138 kV | 2013-12-01 | 2015-01-01
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77341873 | Amoco - Tuco 345 kV Ckt 1 | 2014-10-01 | 2020-01-01 |  | No
| Amoco 345/230 kV Transformer Ckt 1 | 2014-10-01 | 2020-01-01 |  | No
| Carlisle Interchange - Wolfforth Interchange 230 kV Ckt 1 | 2019-06-01 | 2019-06-01
| Cherry Co - Gentleman 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co - Holt Co 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co 345 kV Terminal Upgrades | 2013-12-01 | 2018-01-01 |  | No
| Elk City 345/230 kV | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV AEPW | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV OKGE | 2013-12-01 | 2018-03-01 |  | No
| HITCHLAND INTERCHANGE () 230/115/13.2KV TRANSFORMER CKT 2 | 2015-06-01 | 2017-06-01
| MULTI - Tuco-New Deal 345 kV | 2014-10-01 | 2018-06-01 |  | No
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77341873 | DENVER CITY INTERCHANGE N. - MUSTANG STATION N. 115KV CKT 1 | 2019-06-01 | 2019-06-01
| DENVER CITY INTERCHANGE S. - MUSTANG STATION N. 115KV CKT 2 | 2019-06-01 | 2019-06-01
| Potter to Tolk 345 kV | 2013-12-01 | 2019-06-01 |  | No
| SOUTHWESTERN STATION - WASHITA 138KV CKT 2 | 2013-12-01 | 2017-06-01
| YOAKUM COUNTY INTERCHANGE () 230/115/13.2KV TRANSFORMER CKT 1 | 2019-06-01 | 2019-06-01
| YOAKUM COUNTY INTERCHANGE () 230/115/13.2KV TRANSFORMER CKT 2 | 2019-06-01 | 2019-06-01
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77341873 | CHERRY6 230.00 - Harrington Station East Bus 230KV CKT 1 | 2015-06-01 | 2015-06-01
| CIMARRON - DRAPER LAKE 345KV CKT 1 | 2014-10-01 | 2016-06-01
| APACHE CO 138.00 - PARADISE 138KV CKT 1 | 2010-06-01 | 2013-06-01
| NORTHWEST - TATONGA 345KV CKT 1 | 2010-01-01 | 2010-01-01
| TATONGA - WOODWARD 345KV CKT 1 | 2010-01-01 | 2010-01-01
| WOODWARD - IODINE 138KV CKT 1 | 2010-01-01 | 2010-01-01
| WOODWARD - WOODWARD EHV 138KV CKT 1 | 2010-01-01 | 2010-01-01
| WOODWARD - WOODWARD EHV 138KV CKT 2 | 2010-01-01 | 2010-01-01
| WOODWARD 345/138KV TRANSFORMER CKT 1 | 2010-01-01 | 2010-01-01
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
SPSM | 2012-AG3-010
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
SPSM | 77341881 | WFEC | SPS | 44 | 2017-06-01 | 2047-06-01 | 2020-01-01 | 2050-01-01 | 96906 | 0 | 96906 | 568881.468
[9 empty] | 96906 | 0 | 96906 | 568881.468
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77341881 | AMOCO SWITCHING STATION - SUNDOWN INTERCHANGE 230KV CKT 1 | 2015-10-01 | 2016-06-01 |  |  | 20134 | 480000 | 132623.388
| CARLISLE INTERCHANGE - TUCO INTERCHANGE 230KV CKT 1 | 2015-10-01 | 2016-06-01 |  |  | 15725 | 240000 | 103581.108
| CHAVES COUNTY INTERCHANGE - SAN JUAN MESA TAP 230KV CKT 1 | 2015-10-01 | 2016-06-01 |  |  | 19043 | 240000 | 125436.888
| FLETCHER - MARLOW JCT 69KV CKT 1 | 2019-06-01 | 2019-06-01 |  |  | 19923 | 225000 | 78865.56
| JONES STATION - TUCO INTERCHANGE 230KV CKT 1 | 2015-01-01 | 2016-06-01 |  |  | 17966 | 236250 | 111208.284
| LAKE CREEK - LONEWOLF 69KV CKT 1 | 2014-01-01 | 2016-06-01 |  |  | 4115 | 225000 | 17166.24
[5 empty] | Total | 96906 | 1646250 | 568881.47
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77341881 | Deaf Smith County Interchange 230/115 kV Transformer Ckt 1 #2 | 2013-12-01 | 2015-03-01
| Deaf Smith County Interchange 230/115 kV Transformer Ckt 2 | 2013-12-01 | 2015-03-01
| Line - Clark County - Thistle 345 kV dbl Ckt | 2013-12-01 | 2015-01-01
| Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2014-07-01
| Line - Hitchland - Woodward 345 kV dbl Ckt SPS | 2013-12-01 | 2014-07-01
| Line - Spearville - Clark County 345 kV dbl Ckt | 2013-12-01 | 2015-01-01
| Line - Thistle - Wichita 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01
| Line - Thistle - Wichita 345 kV dbl Ckt WERE | 2013-12-01 | 2015-01-01
| Line - Thistle - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2015-01-01
| Line - Thistle - Woodward 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01
| Line - Tuco - Woodward 345 kV line OKGE | 2013-12-01 | 2014-06-01
| Line - Tuco - Woodward 345 kV line SPS | 2013-12-01 | 2014-06-01
| XFR - Thistle 345/138 kV | 2013-12-01 | 2015-01-01
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77341881 | Amoco - Tuco 345 kV Ckt 1 | 2014-10-01 | 2020-01-01 |  | No
| Amoco 345/230 kV Transformer Ckt 1 | 2014-10-01 | 2020-01-01 |  | No
| Carlisle Interchange - Wolfforth Interchange 230 kV Ckt 1 | 2019-06-01 | 2019-06-01
| Cherry Co - Gentleman 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co - Holt Co 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co 345 kV Terminal Upgrades | 2013-12-01 | 2018-01-01 |  | No
| Elk City 345/230 kV | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV AEPW | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV OKGE | 2013-12-01 | 2018-03-01 |  | No
| HITCHLAND INTERCHANGE () 230/115/13.2KV TRANSFORMER CKT 2 | 2015-06-01 | 2017-06-01
| MULTI - Tuco-New Deal 345 kV | 2014-10-01 | 2018-06-01 |  | No
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77341881 | DENVER CITY INTERCHANGE N. - MUSTANG STATION N. 115KV CKT 1 | 2019-06-01 | 2019-06-01
| DENVER CITY INTERCHANGE S. - MUSTANG STATION N. 115KV CKT 2 | 2019-06-01 | 2019-06-01
| Potter to Tolk 345 kV | 2013-12-01 | 2019-06-01 |  | No
| SOUTHWESTERN STATION - WASHITA 138KV CKT 2 | 2013-12-01 | 2017-06-01
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77341881 | CHERRY6 230.00 - Harrington Station East Bus 230KV CKT 1 | 2015-06-01 | 2015-06-01
| CIMARRON - DRAPER LAKE 345KV CKT 1 | 2014-10-01 | 2016-06-01
| APACHE CO 138.00 - PARADISE 138KV CKT 1 | 2010-06-01 | 2013-06-01
| NORTHWEST - TATONGA 345KV CKT 1 | 2010-01-01 | 2010-01-01
| TATONGA - WOODWARD 345KV CKT 1 | 2010-01-01 | 2010-01-01
| WOODWARD - IODINE 138KV CKT 1 | 2010-01-01 | 2010-01-01
| WOODWARD - WOODWARD EHV 138KV CKT 1 | 2010-01-01 | 2010-01-01
| WOODWARD - WOODWARD EHV 138KV CKT 2 | 2010-01-01 | 2010-01-01
| WOODWARD 345/138KV TRANSFORMER CKT 1 | 2010-01-01 | 2010-01-01
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
WFEC | 2012-AG3-008
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
WFEC | 77193289 | WFEC | WFEC | 320 | 2017-03-01 | 2042-03-01 | 2019-06-01 | 2044-06-01 | 22059704 | 0 | 22059704 | 140372169.72
[9 empty] | 22059704 | 0 | 22059704 | 140372169.72
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77193289 | 59TH ST - EL PASO 138KV CKT 1 | 2015-06-01 | 2017-06-01 |  | No | 943043 | 5693300 | 5277541.23
| 59TH ST - GILL ENERGY CENTER SOUTH 138KV CKT 1 | 2015-06-01 | 2017-06-01 |  | No | 835360 | 5043200 | 4674916.08
| Cimarron - Mathewson 345 kV Ckt 1 Accelerate | 2013-12-01 | 2015-06-01 |  |  | 3698646 | 10704894 | 26930745.48
| CORN TAP - PAOLI 138KV CKT 1 | 2019-06-01 | 2019-06-01 |  |  | 189172 | 225000 | 639249.84
| FLETCHER - MARLOW JCT 69KV CKT 1 | 2019-06-01 | 2019-06-01 |  |  | 96468 | 225000 | 338604.78
| GRAND ISLAND - SWEETWATER 345KV CKT 2 | 2013-12-01 | 2019-06-01 |  | No | 3915635 | 96288750 | 17752756.5
| HOLT - NELIGH 345KV CKT 1 | 2013-12-01 | 2019-06-01 |  | No | 1249982 | 30656000 | 5334614.28
| Mathewson - Tatonga 345 kV Ckt 2 Accelerate | 2013-12-01 | 2015-06-01 |  |  | 7451347 | 26823745 | 54255078.66
| Mathewson 345 kV Accelerate | 2013-12-01 | 2015-06-01 |  |  | 2275742 | 6586619 | 16570233.72
| OKLAUNION 345KV SVC | 2014-10-01 | 2019-06-01 |  | No | 1404309 | 18500000 | 8598429.15
[5 empty] | Total | 22059704 | 200746508 | 140372169.72
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77193289 | Line - Clark County - Thistle 345 kV dbl Ckt | 2013-12-01 | 2015-01-01
| Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2014-07-01
| Line - Hitchland - Woodward 345 kV dbl Ckt SPS | 2013-12-01 | 2014-07-01
| Line - Spearville - Clark County 345 kV dbl Ckt | 2013-12-01 | 2015-01-01
| Line - Thistle - Wichita 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01
| Line - Thistle - Wichita 345 kV dbl Ckt WERE | 2013-12-01 | 2015-01-01
| Line - Thistle - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2015-01-01
| Line - Thistle - Woodward 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01
| Line - Tuco - Woodward 345 kV line OKGE | 2013-12-01 | 2014-06-01
| Line - Tuco - Woodward 345 kV line SPS | 2013-12-01 | 2014-06-01
| XFR - Thistle 345/138 kV | 2013-12-01 | 2015-01-01
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77193289 | Cherry Co - Gentleman 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co - Holt Co 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co 345 kV Terminal Upgrades | 2013-12-01 | 2018-01-01 |  | No
| Elk City 345/230 kV | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV AEPW | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV OKGE | 2013-12-01 | 2018-03-01 |  | No
| ENOS 138KV | 2019-06-01 | 2019-06-01
| HITCHLAND INTERCHANGE () 230/115/13.2KV TRANSFORMER CKT 2 | 2015-06-01 | 2017-06-01 |  | No
| Neligh - Hoskins 345 kV Ckt1 | 2013-12-01 | 2019-03-01 |  | No
| Neligh 345/115 kV Transformer | 2013-12-01 | 2019-03-01 |  | No
| Viola - Clearwater 138kV Ckt1 | 2014-10-01 | 2018-06-01 |  | No
| Viola - Gill 138kV Ckt1 | 2014-10-01 | 2018-06-01 |  | No
| Viola 345/138kV Transformer Ckt 1 | 2014-10-01 | 2018-06-01 |  | No
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77193289 | CHISHOLM - MAIZE 138KV CKT 1 #1 | 2015-06-01 | 2016-06-01
| CHISHOLM - MAIZE 138KV CKT 1 #2 | 2015-06-01 | 2017-06-01 |  | No
| CIMARRON - DRAPER LAKE 345KV CKT 1 | 2019-10-01 | 2019-10-01
| EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 #1 | 2015-06-01 | 2016-06-01
| EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 #2 | 2015-06-01 | 2017-06-01 |  | No
| GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | 2014-01-01 | 2016-06-01
| HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 2013-12-01 | 2017-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV KACP | 2013-12-01 | 2019-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV WERE | 2013-12-01 | 2019-06-01 |  | No
| Lacygne - Mariosa 345KV KACP | 2013-12-01 | 2019-06-01 |  | No
| Potter to Tolk 345 kV | 2013-12-01 | 2019-06-01 |  | No
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77193289 | CIMARRON - DRAPER LAKE 345KV CKT 1 | 2014-10-01 | 2016-06-01
| APACHE CO 138.00 - PARADISE 138KV CKT 1 | 2010-06-01 | 2013-06-01
| HUGO POWER PLANT - VALLIANT 345 KV AEPW | 2012-07-01 | 2012-07-01
| HUGO POWER PLANT - VALLIANT 345KV CKT 1 WFEC | 2012-07-01 | 2012-07-01
| HUGO POWER PLANT 345/138KV TRANSFORMER CKT 1 | 2012-07-01 | 2012-07-01
| NORTHWEST - TATONGA 345KV CKT 1 | 2010-01-01 | 2010-01-01
| TATONGA - WOODWARD 345KV CKT 1 | 2010-01-01 | 2010-01-01
| WOODWARD - IODINE 138KV CKT 1 | 2010-01-01 | 2010-01-01
| WOODWARD - WOODWARD EHV 138KV CKT 1 | 2010-01-01 | 2010-01-01
| WOODWARD - WOODWARD EHV 138KV CKT 2 | 2010-01-01 | 2010-01-01
| WOODWARD 345/138KV TRANSFORMER CKT 1 | 2010-01-01 | 2010-01-01
Third Party Limitations.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | *Allocated E & C Cost | *Total E & C Cost
77193289 | Lacygne - Mariosa 345KV AMRN | 2013-12-01 | 2019-06-01 |  | No | 4.623% | 100%
[5 empty] | Total | 0 | 0
*Estimated cost allocation as a percentage of total cost is shown for third-party limitations when costs have not yet been established by the third-party.
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
WRGS | 2012-AG3-002
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
WRGS | 77379445 | WR | EES | 50 | 2014-01-01 | 2019-01-01 | 2019-06-01 | 2024-06-01 | 0 | 3840000 | 6440976 | 17694850.398
[9 empty] | 0 | 3840000 | 6440976 | 17694850.398
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77379445 | 59TH ST - EL PASO 138KV CKT 1 | 2015-06-01 | 2017-06-01 |  | No | 44097 | 5693300 | 136414.26
| 59TH ST - GILL ENERGY CENTER SOUTH 138KV CKT 1 | 2015-06-01 | 2017-06-01 |  | No | 39062 | 5043200 | 120838.458
| Cimarron - Mathewson 345 kV Ckt 1 Accelerate | 2013-12-01 | 2015-06-01 |  | No | 31497 | 10704894 | 112240.386
| GRAND ISLAND - SWEETWATER 345KV CKT 2 | 2013-12-01 | 2019-06-01 |  | No | 2193580 | 96288750 | 5783334.63
| HOLT - NELIGH 345KV CKT 1 | 2013-12-01 | 2019-06-01 |  | No | 636818 | 30656000 | 1580432.112
| Mathewson - Tatonga 345 kV Ckt 2 Accelerate | 2013-12-01 | 2015-06-01 |  | No | 196636 | 26823745 | 700717.632
| Mathewson 345 kV Accelerate | 2013-12-01 | 2015-06-01 |  | No | 19380 | 6586619 | 69061.134
| OKLAUNION 345KV SVC | 2014-10-01 | 2019-06-01 |  | No | 37731 | 18500000 | 120177.48
| SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 MIDW | 2013-12-01 | 2018-06-01 |  | No | 846994 | 13864500 | 1982027.43
| SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 WERE | 2013-12-01 | 2018-06-01 |  | No | 2080836 | 34061343.75 | 6058847.364
| ST JOHN - ST_JOHN 115KV CKT 1 MIDW | 2013-12-01 | 2016-06-01 |  | No | 139709 | 450000 | 337917.3
| ST JOHN - ST_JOHN 115KV CKT 1 MKEC | 2013-12-01 | 2016-06-01 |  | No | 174636 | 562500 | 692842.212
[5 empty] | Total | 6440976 | 249234851.75 | 17694850.398
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77379445 | HARPER - MILAN TAP 138KV CKT 1 #1 | 2013-12-01 | 2014-12-01 |  | No
| HAYS PLANT - SOUTH HAYS 115KV CKT 1 #2 | 2014-01-01 | 2015-06-01 |  | No
| Line - Clark County - Thistle 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2014-07-01 |  | No
| Line - Hitchland - Woodward 345 kV dbl Ckt SPS | 2013-12-01 | 2014-07-01 |  | No
| Line - Spearville - Clark County 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt WERE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Tuco - Woodward 345 kV line OKGE | 2013-12-01 | 2014-06-01 |  | No
| Line - Tuco - Woodward 345 kV line SPS | 2013-12-01 | 2014-06-01 |  | No
| MOUNDRIDGE 138/115KV TRANSFORMER CKT 2 | 2013-12-01 | 2014-12-01 |  | No
| XFR - Thistle 345/138 kV | 2013-12-01 | 2015-01-01 |  | No
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77379445 | Cherry Co - Gentleman 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co - Holt Co 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co 345 kV Terminal Upgrades | 2013-12-01 | 2018-01-01 |  | No
| Elk City 345/230 kV | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV AEPW | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV OKGE | 2013-12-01 | 2018-03-01 |  | No
| Neligh - Hoskins 345 kV Ckt1 | 2013-12-01 | 2019-03-01 |  | No
| Neligh 345/115 kV Transformer | 2013-12-01 | 2019-03-01 |  | No
| Viola - Clearwater 138kV Ckt1 | 2014-10-01 | 2018-06-01 |  | No
| Viola - Gill 138kV Ckt1 | 2014-10-01 | 2018-06-01 |  | No
| Viola 345/138kV Transformer Ckt 1 | 2014-10-01 | 2018-06-01 |  | No
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77379445 | ADABELL - VBI 161KV CKT 1 | 2014-06-01 | 2016-06-01
| BEAVER - EUREKA SPRINGS 161KV CKT 1 AEPW | 2014-06-01 | 2015-06-01 |  | No
| CHISHOLM - MAIZE 138KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| CHISHOLM - MAIZE 138KV CKT 1 #2 | 2015-06-01 | 2017-06-01 |  | No
| CIMARRON - DRAPER LAKE 345KV CKT 1 | 2019-10-01 | 2019-10-01
| CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | 2013-12-01 | 2017-06-01 |  | No
| CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | 2013-12-01 | 2017-06-01 |  | No
| EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 #2 | 2015-06-01 | 2017-06-01 |  | No
| FLINT CREEK - SILOAM SPRINGS TAP 345KV CKT 1 AEPW | 2019-06-01 | 2019-06-01
| FT SMITH - MUSKOGEE 345KV CKT 1 | 2014-06-01 | 2016-06-01 |  | No
| FT SMITH (FTSMITH1) 500/345/13.8KV TRANSFORMER CKT 1 | 2014-06-01 | 2018-06-01 |  | No
| GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #2 | 2015-06-01 | 2016-06-01 |  | No
| HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | 2013-12-01 | 2017-06-01 |  | No
| HAYS PLANT - VINE STREET 115KV CKT 1 | 2014-01-01 | 2017-06-01 |  | No
| HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 2013-12-01 | 2017-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV KACP | 2013-12-01 | 2019-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV WERE | 2013-12-01 | 2019-06-01 |  | No
| Lacygne - Mariosa 345KV KACP | 2013-12-01 | 2019-06-01 |  | No
| MEDICINE LODGE - PRATT 115KV CKT 1 | 2014-01-01 | 2014-06-15 |  | No
| Mullergren - Reno 345kV Dbl CKT MKEC | 2014-01-01 | 2019-06-01 |  | No
| Mullergren - Reno 345kV Dbl CKT WERE | 2014-01-01 | 2019-06-01 |  | No
| Muskogee - VBI 345 kV with 345/161 kV bus tie near VBI | 2014-06-01 | 2019-06-01 |  | No
| Potter to Tolk 345 kV | 2013-12-01 | 2019-06-01 |  | No
| Spearville - Mullergren 345kV Dbl CKT | 2014-01-01 | 2019-06-01 |  | No
| VBI - Arkansas Nuclear One 345kV OKGE | 2014-06-01 | 2019-06-01 |  | No
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77379445 | ALBION - PETERSBURG 115KV CKT 1 | 2013-01-01 | 2013-01-01
| ALEXANDER - PRATT 115KV CKT 1 | 2009-12-01 | 2013-06-01
| BARBER - SAWYER 115KV CKT 1 | 2009-12-01 | 2013-06-01
| BARBER (BARBER 4) 138/115/2.72KV TRANSFORMER CKT 1 | 2009-12-01 | 2013-06-01
| CANTON - TALOGA 69KV CKT 1 | 2011-06-01 | 2013-06-01
| CHERRY6 230.00 - Harrington Station East Bus 230KV CKT 1 | 2015-06-01 | 2015-06-01
| CIMARRON - DRAPER LAKE 345KV CKT 1 | 2014-10-01 | 2016-06-01
| CIRCLE - RICE_CO 230KV CKT 1 | 2012-10-01 | 2012-11-15
| CLIFTON - GREENLEAF 115KV CKT 1 | 2011-06-01 | 2013-06-01
| FLATRDG3 138.00 - MEDICINE LODGE 138KV CKT 1 | 2009-12-01 | 2013-06-01
| FLATRDG3 138.00 - HARPER 138KV CKT 1 | 2009-12-01 | 2013-06-01
| APACHE CO 138.00 - PARADISE 138KV CKT 1 | 2010-06-01 | 2013-06-01
| GREENLEAF - KNOB HILL 115KV CKT 1 MKEC | 2013-06-01 | 2013-06-01
| HUGO POWER PLANT - VALLIANT 345 KV AEPW | 2012-07-01 | 2012-07-01
| HUGO POWER PLANT - VALLIANT 345KV CKT 1 WFEC | 2012-07-01 | 2012-07-01
| KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1 | 2006-06-01 | 2008-06-01
| LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01
| LYONS - RICE_CO 115KV CKT 1 | 2012-10-01 | 2013-04-01
| LYONS - WHEATLAND 115KV CKT 1 #1 | 2012-10-01 | 2013-07-15
| LYONS - WHEATLAND 115KV CKT 1 #2 | 2012-10-01 | 2013-07-15
| Mullergren - Reno 345kV Dbl CKT MKEC | 2013-10-01 | 2019-06-01
| Mullergren - Reno 345kV Dbl CKT WERE | 2013-10-01 | 2019-06-01
| NELIGH - PETERSBURG 115KV CKT 1 | 2013-01-01 | 2013-01-01
| NORTHWEST - TATONGA 345KV CKT 1 | 2010-01-01 | 2010-01-01
| RICE_CO 230/115KV TRANSFORMER CKT 1 | 2012-10-01 | 2012-11-15
| Spearville - Mullergren 345kV Dbl CKT | 2013-10-01 | 2019-06-01
| Spearville 345/115/13.8kV Transformer CKT 3 | 2013-10-01 | 2015-06-01
| TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | 2010-10-01 | 2013-06-01
| TATONGA - WOODWARD 345KV CKT 1 | 2010-01-01 | 2010-01-01
| WOODWARD - IODINE 138KV CKT 1 | 2010-01-01 | 2010-01-01
| WOODWARD - WOODWARD EHV 138KV CKT 1 | 2010-01-01 | 2010-01-01
| WOODWARD - WOODWARD EHV 138KV CKT 2 | 2010-01-01 | 2010-01-01
| WOODWARD 345/138KV TRANSFORMER CKT 1 | 2010-01-01 | 2010-01-01
Potential reservation deferral and redispatch requirement on the following upgrades due to positive MW Impact on limitations that require upgrade. No cost assignment due to negative MW impact on defined upgrade.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77379445 | Arkansas Nuclear One 500/345 Transformer | 2014-06-01 | 2019-06-01 |  | No
| VBI - Arkansas Nuclear One 345kV EES | 2014-06-01 | 2019-06-01 |  | No
Third Party Limitations.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | *Allocated E & C Cost | *Total E & C Cost
77379445 | ARKANSAS NUCLEAR ONE - PLEASANT HILL 500KV CKT 1 | 2014-10-01 | 2014-10-01 |  |  | 0.07468% | 100%
| BEAVER - EUREKA SPRINGS 161KV CKT 1 SWPA | 2014-06-01 | 2015-06-01 |  | No | 0 | 0
| Lacygne - Mariosa 345KV AMRN | 2013-12-01 | 2019-06-01 |  | No | 4.783% | 100%
[5 empty] | Total | 0 | 0
*Estimated cost allocation as a percentage of total cost is shown for third-party limitations when costs have not yet been established by the third-party.
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
WRGS | 2012-AG3-005
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
WRGS | 77409901 | WR | EES | 106 | 2014-01-01 | 2019-01-01 | 2019-06-01 | 2024-06-01 | 0 | 8140800 | 7457000 | 21124735.314
[9 empty] | 0 | 8140800 | 7457000 | 21124735.314
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77409901 | 59TH ST - EL PASO 138KV CKT 1 | 2015-06-01 | 2017-06-01 |  | No | 172751 | 5693300 | 534405.954
| 59TH ST - GILL ENERGY CENTER SOUTH 138KV CKT 1 | 2015-06-01 | 2017-06-01 |  | No | 153025 | 5043200 | 473383.494
| Cimarron - Mathewson 345 kV Ckt 1 Accelerate | 2013-12-01 | 2015-06-01 |  |  | 171514 | 10704894 | 611194.698
| GRAND ISLAND - SWEETWATER 345KV CKT 2 | 2013-12-01 | 2019-06-01 |  | No | 1991624 | 96288750 | 5250881.226
| HOLT - NELIGH 345KV CKT 1 | 2013-12-01 | 2019-06-01 |  | No | 530432 | 30656000 | 1316407.14
| Mathewson - Tatonga 345 kV Ckt 2 Accelerate | 2013-12-01 | 2015-06-01 |  |  | 763714 | 26823745 | 2721515.22
| Mathewson 345 kV Accelerate | 2013-12-01 | 2015-06-01 |  |  | 105531 | 6586619 | 376062.534
| OKLAUNION 345KV SVC | 2014-10-01 | 2019-06-01 |  | No | 92876 | 18500000 | 295820.502
| SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 MIDW | 2013-12-01 | 2018-06-01 |  | No | 1005439 | 13864500 | 2352800.22
| SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 WERE | 2013-12-01 | 2018-06-01 |  | No | 2470094 | 34061343.75 | 7192264.326
[5 empty] | Total | 7457000 | 248222351.75 | 21124735.314
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77409901 | 5 TRIBES - PECAN CREEK 161KV CKT 1 | 2014-06-01 | 2014-06-01
| HARPER - MILAN TAP 138KV CKT 1 #1 | 2013-12-01 | 2014-12-01 |  | No
| IATAN - NASHUA 345KV CKT 1 | 2013-12-01 | 2015-06-01 |  | No
| Line - Clark County - Thistle 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2014-07-01 |  | No
| Line - Hitchland - Woodward 345 kV dbl Ckt SPS | 2013-12-01 | 2014-07-01 |  | No
| Line - Spearville - Clark County 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt WERE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Tuco - Woodward 345 kV line OKGE | 2013-12-01 | 2014-06-01 |  | No
| Line - Tuco - Woodward 345 kV line SPS | 2013-12-01 | 2014-06-01 |  | No
| NORTHWEST TEXARKANA - VALLIANT 345KV CKT 1 | 2014-06-01 | 2015-05-01 |  | No
| XFR - Thistle 345/138 kV | 2013-12-01 | 2015-01-01 |  | No
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77409901 | Cherry Co - Gentleman 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co - Holt Co 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co 345 kV Terminal Upgrades | 2013-12-01 | 2018-01-01 |  | No
| Elk City 345/230 kV | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV AEPW | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV OKGE | 2013-12-01 | 2018-03-01 |  | No
| Multi - Centerton - Osage Creek 345 kV | 2014-06-01 | 2016-06-01 |  | No
| Multi - Flint Creek – Centerton 345 kV and Centerton- East Centerton 161 kV | 2014-06-01 | 2014-06-01
| Neligh - Hoskins 345 kV Ckt1 | 2013-12-01 | 2019-03-01 |  | No
| Neligh 345/115 kV Transformer | 2013-12-01 | 2019-03-01 |  | No
| Viola - Clearwater 138kV Ckt1 | 2014-10-01 | 2018-06-01 |  | No
| Viola - Gill 138kV Ckt1 | 2014-10-01 | 2018-06-01 |  | No
| Viola 345/138kV Transformer Ckt 1 | 2014-10-01 | 2018-06-01 |  | No
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77409901 | ADABELL - VBI 161KV CKT 1 | 2014-06-01 | 2016-06-01 |  | No
| BEAVER - EUREKA SPRINGS 161KV CKT 1 AEPW | 2014-06-01 | 2015-06-01 |  | No
| BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #1 Accelerate | 2014-06-01 | 2015-06-01 |  | No
| BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #2 Accelerate | 2014-06-01 | 2017-06-01 |  | No
| BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #1 Accelerate | 2014-06-01 | 2015-06-01 |  | No
| BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #2 Accelerate | 2014-06-01 | 2016-06-01 |  | No
| CHISHOLM - MAIZE 138KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| CHISHOLM - MAIZE 138KV CKT 1 #2 | 2015-06-01 | 2017-06-01 |  | No
| CIMARRON - DRAPER LAKE 345KV CKT 1 | 2019-10-01 | 2019-10-01
| CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | 2013-12-01 | 2017-06-01 |  | No
| CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | 2013-12-01 | 2017-06-01 |  | No
| EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 #2 | 2015-06-01 | 2017-06-01 |  | No
| FLINT CREEK - SILOAM SPRINGS TAP 345KV CKT 1 AEPW | 2019-06-01 | 2019-06-01
| FT SMITH - MUSKOGEE 345KV CKT 1 | 2014-06-01 | 2016-06-01 |  | No
| FT SMITH (FTSMITH1) 500/345/13.8KV TRANSFORMER CKT 1 | 2014-06-01 | 2018-06-01 |  | No
| GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #2 | 2015-06-01 | 2016-06-01 |  | No
| HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | 2013-12-01 | 2017-06-01 |  | No
| HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 2013-12-01 | 2017-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV KACP | 2013-12-01 | 2019-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV WERE | 2013-12-01 | 2019-06-01 |  | No
| Lacygne - Mariosa 345KV KACP | 2013-12-01 | 2019-06-01 |  | No
| Muskogee - VBI 345 kV with 345/161 kV bus tie near VBI | 2014-06-01 | 2019-06-01 |  | No
| Potter to Tolk 345 kV | 2013-12-01 | 2019-06-01 |  | No
| VBI - Arkansas Nuclear One 345kV OKGE | 2014-06-01 | 2019-06-01 |  | No
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77409901 | ALEXANDER - PRATT 115KV CKT 1 | 2009-12-01 | 2013-06-01
| BANN - RED SPRINGS REC 138KV CKT 1 | 2012-07-01 | 2012-07-01
| BARBER - MEDICINE LODGE 115KV CKT 1 | 2009-12-01 | 2013-06-01
| BARBER - SAWYER 115KV CKT 1 | 2009-12-01 | 2013-06-01
| BARBER (BARBER 4) 138/115/2.72KV TRANSFORMER CKT 1 | 2009-12-01 | 2013-06-01
| BEELINE - EXPLORER GLENPOOL TAP 138KV CKT 1 | 2009-06-01 | 2009-06-01
| CANTON - TALOGA 69KV CKT 1 | 2011-06-01 | 2013-06-01
| CHERRY6 230.00 - Harrington Station East Bus 230KV CKT 1 | 2015-06-01 | 2015-06-01
| CIMARRON - DRAPER LAKE 345KV CKT 1 | 2014-10-01 | 2016-06-01
| CIRCLE - RICE_CO 230KV CKT 1 | 2012-10-01 | 2012-11-15
| CLIFTON - GREENLEAF 115KV CKT 1 | 2011-06-01 | 2013-06-01
| EXPLORER GLENPOOL TAP - RIVERSIDE STATION 138KV CKT 1 AEPW | 2009-06-01 | 2009-06-01
| EXPLORER GLENPOOL TAP - RIVERSIDE STATION 138KV CKT 1 OKGE | 2009-06-01 | 2009-06-01
| FLATRDG3 138.00 - MEDICINE LODGE 138KV CKT 1 | 2009-12-01 | 2013-06-01
| FLATRDG3 138.00 - HARPER 138KV CKT 1 | 2009-12-01 | 2013-06-01
| APACHE CO 138.00 - PARADISE 138KV CKT 1 | 2010-06-01 | 2013-06-01
| GREENLEAF - KNOB HILL 115KV CKT 1 MKEC | 2013-06-01 | 2013-06-01
| HUGO POWER PLANT - VALLIANT 345 KV AEPW | 2012-07-01 | 2012-07-01
| HUGO POWER PLANT - VALLIANT 345KV CKT 1 WFEC | 2012-07-01 | 2012-07-01
| KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1 | 2006-06-01 | 2008-06-01
| LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01
| LYONS - RICE_CO 115KV CKT 1 | 2012-10-01 | 2013-04-01
| LYONS - WHEATLAND 115KV CKT 1 #1 | 2012-10-01 | 2013-07-15
| LYONS - WHEATLAND 115KV CKT 1 #2 | 2012-10-01 | 2013-07-15
| MCNAB REC - TURK 115KV CKT 1 | 2012-07-01 | 2012-07-01
| Mullergren - Reno 345kV Dbl CKT MKEC | 2013-10-01 | 2019-06-01
| Mullergren - Reno 345kV Dbl CKT WERE | 2013-10-01 | 2019-06-01
| NORTHWEST - TATONGA 345KV CKT 1 | 2010-01-01 | 2010-01-01
| RICE_CO 230/115KV TRANSFORMER CKT 1 | 2012-10-01 | 2012-11-15
| Spearville - Mullergren 345kV Dbl CKT | 2013-10-01 | 2019-06-01
| Spearville 345/115/13.8kV Transformer CKT 3 | 2013-10-01 | 2015-06-01
| SUB 110 - ORONOGO JCT. - SUB 167 - RIVERTON 161KV CKT 1 | 2011-06-01 | 2011-06-01
| TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | 2010-10-01 | 2013-06-01
| TATONGA - WOODWARD 345KV CKT 1 | 2010-01-01 | 2010-01-01
| WOODWARD - IODINE 138KV CKT 1 | 2010-01-01 | 2010-01-01
| WOODWARD - WOODWARD EHV 138KV CKT 1 | 2010-01-01 | 2010-01-01
| WOODWARD - WOODWARD EHV 138KV CKT 2 | 2010-01-01 | 2010-01-01
| WOODWARD 345/138KV TRANSFORMER CKT 1 | 2010-01-01 | 2010-01-01
Third Party Limitations.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | *Allocated E & C Cost | *Total E & C Cost
77409901 | 7JASPER 345.00 - BLACKBERRY 345KV CKT 1 #1 | 2015-06-01 | 2015-06-01 |  |  | 856 | 100000
| ARKANSAS NUCLEAR ONE - PLEASANT HILL 500KV CKT 1 | 2014-10-01 | 2014-10-01 |  |  | 0.6018% | 100%
| Arkansas Nuclear One 500/345 Transformer | 2014-06-01 | 2019-06-01 |  | No | 83195 | 12000000
| BEAVER - EUREKA SPRINGS 161KV CKT 1 SWPA | 2014-06-01 | 2015-06-01 |  | No | 0 | 0
| BUFORD 5 161.00 - BULL SHOALS 161KV CKT 1 | 2014-06-01 | 2017-06-01 |  | No | 0 | 0
| BUFORD 5 161.00 - NORFORK 161KV CKT 1 | 2014-06-01 | 2017-06-01 |  | No | 0 | 0
| Lacygne - Mariosa 345KV AMRN | 2013-12-01 | 2019-06-01 |  | No | 7.235% | 100%
| VBI - Arkansas Nuclear One 345kV EES | 2014-06-01 | 2019-06-01 |  | No | 0.6933% | 100%
[5 empty] | Total | 84051 | 12100000
*Estimated cost allocation as a percentage of total cost is shown for third-party limitations when costs have not yet been established by the third-party.
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
WRGS | 2012-AG3-006
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
WRGS | 77409994 | SPS | EES | 106 | 2014-01-01 | 2019-01-01 | 2019-06-01 | 2024-06-01 | 0 | 8140800 | 13495436 | 37028265.642
[9 empty] | 0 | 8140800 | 13495436 | 37028265.642
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
77409994 | Cimarron - Mathewson 345 kV Ckt 1 Accelerate | 2013-12-01 | 2015-06-01 |  | No | 102423 | 10704894 | 364987.092
| GRAND ISLAND - SWEETWATER 345KV CKT 2 | 2013-12-01 | 2019-06-01 |  | No | 5094170 | 96288750 | 13430688.552
| HOLT - NELIGH 345KV CKT 1 | 2013-12-01 | 2019-06-01 |  | No | 1634749 | 30656000 | 4057061.532
| Mathewson - Tatonga 345 kV Ckt 2 Accelerate | 2013-12-01 | 2015-06-01 |  | No | 734381 | 26823745 | 2616986.292
| Mathewson 345 kV Accelerate | 2013-12-01 | 2015-06-01 |  | No | 63020 | 6586619 | 224573.442
| OKLAUNION 345KV SVC | 2014-10-01 | 2019-06-01 |  | No | 177257 | 18500000 | 564583.488
| SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 MIDW | 2013-12-01 | 2018-06-01 |  | No | 1567622 | 13864500 | 3668349.234
| SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 WERE | 2013-12-01 | 2018-06-01 |  | No | 3851224 | 34061343.75 | 11213751.768
| ST JOHN - ST_JOHN 115KV CKT 1 MIDW | 2013-12-01 | 2016-06-01 |  | No | 120262 | 450000 | 290880.402
| ST JOHN - ST_JOHN 115KV CKT 1 MKEC | 2013-12-01 | 2016-06-01 |  | No | 150328 | 562500 | 596403.84
[5 empty] | Total | 13495436 | 238498351.75 | 37028265.642
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77409994 | 5 TRIBES - PECAN CREEK 161KV CKT 1 | 2014-06-01 | 2014-06-01
| HARPER - MILAN TAP 138KV CKT 1 #1 | 2013-12-01 | 2014-12-01 |  | No
| HAYS PLANT - SOUTH HAYS 115KV CKT 1 #2 | 2014-01-01 | 2015-06-01 |  | No
| Line - Clark County - Thistle 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2014-07-01 |  | No
| Line - Hitchland - Woodward 345 kV dbl Ckt SPS | 2013-12-01 | 2014-07-01 |  | No
| Line - Spearville - Clark County 345 kV dbl Ckt | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Wichita 345 kV dbl Ckt WERE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt OKGE | 2013-12-01 | 2015-01-01 |  | No
| Line - Thistle - Woodward 345 kV dbl Ckt PW | 2013-12-01 | 2015-01-01 |  | No
| Line - Tuco - Woodward 345 kV line OKGE | 2013-12-01 | 2014-06-01 |  | No
| Line - Tuco - Woodward 345 kV line SPS | 2013-12-01 | 2014-06-01 |  | No
| MOUNDRIDGE 138/115KV TRANSFORMER CKT 2 | 2013-12-01 | 2014-12-01 |  | No
| NORTHWEST TEXARKANA - VALLIANT 345KV CKT 1 | 2014-06-01 | 2015-05-01 |  | No
| XFR - Thistle 345/138 kV | 2013-12-01 | 2015-01-01 |  | No
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77409994 | Cherry Co - Gentleman 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co - Holt Co 345 kV Ckt1 | 2013-12-01 | 2018-01-01 |  | No
| Cherry Co 345 kV Terminal Upgrades | 2013-12-01 | 2018-01-01 |  | No
| Elk City 345/230 kV | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV AEPW | 2013-12-01 | 2018-03-01 |  | No
| Elk City to Gracemont 345kV OKGE | 2013-12-01 | 2018-03-01 |  | No
| HITCHLAND INTERCHANGE () 230/115/13.2KV TRANSFORMER CKT 2 | 2015-06-01 | 2017-06-01 |  | No
| Multi - Centerton - Osage Creek 345 kV | 2014-06-01 | 2016-06-01 |  | No
| Multi - Flint Creek – Centerton 345 kV and Centerton- East Centerton 161 kV | 2014-06-01 | 2014-06-01
| Neligh - Hoskins 345 kV Ckt1 | 2013-12-01 | 2019-03-01 |  | No
| Neligh 345/115 kV Transformer | 2013-12-01 | 2019-03-01 |  | No
| Viola - Clearwater 138kV Ckt1 | 2014-10-01 | 2018-06-01 |  | No
| Viola - Gill 138kV Ckt1 | 2014-10-01 | 2018-06-01 |  | No
| Viola 345/138kV Transformer Ckt 1 | 2014-10-01 | 2018-06-01 |  | No
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77409994 | ADABELL - VBI 161KV CKT 1 | 2014-06-01 | 2016-06-01 |  | No
| BEAVER - EUREKA SPRINGS 161KV CKT 1 AEPW | 2014-06-01 | 2015-06-01 |  | No
| CIMARRON - DRAPER LAKE 345KV CKT 1 | 2019-10-01 | 2019-10-01
| CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | 2013-12-01 | 2017-06-01 |  | No
| CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | 2013-12-01 | 2017-06-01 |  | No
| FLINT CREEK - SILOAM SPRINGS TAP 345KV CKT 1 AEPW | 2019-06-01 | 2019-06-01
| FT SMITH - MUSKOGEE 345KV CKT 1 | 2014-06-01 | 2016-06-01 |  | No
| FT SMITH (FTSMITH1) 500/345/13.8KV TRANSFORMER CKT 1 | 2014-06-01 | 2018-06-01 |  | No
| GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #1 | 2015-06-01 | 2016-06-01 |  | No
| GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #2 | 2015-06-01 | 2016-06-01 |  | No
| HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | 2013-12-01 | 2017-06-01 |  | No
| HAYS PLANT - VINE STREET 115KV CKT 1 | 2014-01-01 | 2017-06-01 |  | No
| HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 2013-12-01 | 2017-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV KACP | 2013-12-01 | 2019-06-01 |  | No
| Iatan - Jeffrey Energy Center 345 kV WERE | 2013-12-01 | 2019-06-01 |  | No
| Lacygne - Mariosa 345KV KACP | 2013-12-01 | 2019-06-01 |  | No
| MEDICINE LODGE - PRATT 115KV CKT 1 | 2014-01-01 | 2014-06-15 |  | No
| Mullergren - Reno 345kV Dbl CKT MKEC | 2014-01-01 | 2019-06-01 |  | No
| Mullergren - Reno 345kV Dbl CKT WERE | 2014-01-01 | 2019-06-01 |  | No
| Muskogee - VBI 345 kV with 345/161 kV bus tie near VBI | 2014-06-01 | 2019-06-01 |  | No
| Potter to Tolk 345 kV | 2013-12-01 | 2019-06-01 |  | No
| Spearville - Mullergren 345kV Dbl CKT | 2014-01-01 | 2019-06-01 |  | No
| VBI - Arkansas Nuclear One 345kV OKGE | 2014-06-01 | 2019-06-01 |  | No
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
77409994 | ALBION - PETERSBURG 115KV CKT 1 | 2013-01-01 | 2013-01-01
| ALTUS SW - NAVAJO 69KV CKT 1 | 2013-06-01 | 2013-06-01
| BARBER - MEDICINE LODGE 115KV CKT 1 | 2009-12-01 | 2013-06-01
| BARBER (BARBER 4) 138/115/2.72KV TRANSFORMER CKT 1 | 2009-12-01 | 2013-06-01
| BEELINE - EXPLORER GLENPOOL TAP 138KV CKT 1 | 2009-06-01 | 2009-06-01
| CANTON - TALOGA 69KV CKT 1 | 2011-06-01 | 2013-06-01
| CHERRY6 230.00 - Harrington Station East Bus 230KV CKT 1 | 2015-06-01 | 2015-06-01
| CIMARRON - DRAPER LAKE 345KV CKT 1 | 2014-10-01 | 2016-06-01
| CIRCLE - RICE_CO 230KV CKT 1 | 2012-10-01 | 2012-11-15
| CLIFTON - GREENLEAF 115KV CKT 1 | 2011-06-01 | 2013-06-01
| EXPLORER GLENPOOL TAP - RIVERSIDE STATION 138KV CKT 1 AEPW | 2009-06-01 | 2009-06-01
| EXPLORER GLENPOOL TAP - RIVERSIDE STATION 138KV CKT 1 OKGE | 2009-06-01 | 2009-06-01
| FLATRDG3 138.00 - MEDICINE LODGE 138KV CKT 1 | 2009-12-01 | 2013-06-01
| FLATRDG3 138.00 - HARPER 138KV CKT 1 | 2009-12-01 | 2013-06-01
| APACHE CO 138.00 - PARADISE 138KV CKT 1 | 2010-06-01 | 2013-06-01
| GRACMNT4 138.00 - WASHITA 138KV CKT 2 OKGE | 2012-01-01 | 2012-01-01
| GRACMNT4 138.00 - WASHITA 138KV CKT 2 WFEC | 2012-01-01 | 2012-01-01
| GREENLEAF - KNOB HILL 115KV CKT 1 MKEC | 2013-06-01 | 2013-06-01
| HUGO POWER PLANT - VALLIANT 345 KV AEPW | 2012-07-01 | 2012-07-01
| HUGO POWER PLANT - VALLIANT 345KV CKT 1 WFEC | 2012-07-01 | 2012-07-01
| Judson Large - North Judson Large 115KV CKT 2 | 2013-10-01 | 2015-06-01
| KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1 | 2006-06-01 | 2008-06-01
| LACYGNE - WEST GARDNER 345KV CKT 1 | 2006-06-01 | 2006-06-01
| LYONS - RICE_CO 115KV CKT 1 | 2012-10-01 | 2013-04-01
| LYONS - WHEATLAND 115KV CKT 1 #1 | 2012-10-01 | 2013-07-15
| LYONS - WHEATLAND 115KV CKT 1 #2 | 2012-10-01 | 2013-07-15
| MCNAB REC - TURK 115KV CKT 1 | 2012-07-01 | 2012-07-01
| Mullergren - Reno 345kV Dbl CKT MKEC | 2013-10-01 | 2019-06-01
| Mullergren - Reno 345kV Dbl CKT WERE | 2013-10-01 | 2019-06-01
| NELIGH - PETERSBURG 115KV CKT 1 | 2013-01-01 | 2013-01-01
| North Judson Large - Spearville 115KV CKT 2 | 2013-10-01 | 2015-06-01
| NORTHWEST - TATONGA 345KV CKT 1 | 2010-01-01 | 2010-01-01
| RICE_CO 230/115KV TRANSFORMER CKT 1 | 2012-10-01 | 2012-11-15
| Spearville - Mullergren 345kV Dbl CKT | 2013-10-01 | 2019-06-01
| Spearville 345/115/13.8kV Transformer CKT 3 | 2013-10-01 | 2015-06-01
| SUB 110 - ORONOGO JCT. - SUB 167 - RIVERTON 161KV CKT 1 | 2011-06-01 | 2011-06-01
| TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | 2010-10-01 | 2013-06-01
| TATONGA - WOODWARD 345KV CKT 1 | 2010-01-01 | 2010-01-01
| WOODWARD - IODINE 138KV CKT 1 | 2010-01-01 | 2010-01-01
| WOODWARD - WOODWARD EHV 138KV CKT 1 | 2010-01-01 | 2010-01-01
| WOODWARD - WOODWARD EHV 138KV CKT 2 | 2010-01-01 | 2010-01-01
| WOODWARD 345/138KV TRANSFORMER CKT 1 | 2010-01-01 | 2010-01-01
Third Party Limitations.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | *Allocated E & C Cost | *Total E & C Cost
77409994 | ARKANSAS NUCLEAR ONE - PLEASANT HILL 500KV CKT 1 | 2014-10-01 | 2014-10-01 |  |  | 0.25% | 100%
| Arkansas Nuclear One 500/345 Transformer | 2014-06-01 | 2019-06-01 |  | No | 39814 | 12000000
| BEAVER - EUREKA SPRINGS 161KV CKT 1 SWPA | 2014-06-01 | 2015-06-01 |  | No | 0 | 0
| Lacygne - Mariosa 345KV AMRN | 2013-12-01 | 2019-06-01 |  | No | 7.516% | 100%
| VBI - Arkansas Nuclear One 345kV EES | 2014-06-01 | 2019-06-01 |  | No | 0.3318% | 100%
[5 empty] | Total | 39814 | 12000000
*Estimated cost allocation as a percentage of total cost is shown for third-party limitations when costs have not yet been established by the third-party.

## Table4
Transmission Owner | Upgrade | Solution | Earliest Date Upgrade Required (DUN) | Estimated Date of Upgrade Completion (EOC) | Estimated Engineering & Construction Cost
AEPW | AVOCA - EAST ROGERS 161KV CKT 1 Accelerate | Rebuild 5.81 miles with 1533.3 ACSR/TW + Substation Conductor | 2014-06-01 | 2017-06-01 | 822521
AEPW | BARTLESVILLE COMANCHE - MOUND ROAD 138KV CKT 1 | Rebuild 3.8 miles with 1533.3 ACSR/TW | 2014-01-01 | 2017-06-01 | 4750000
AEPW | ERCOT North HVDC Tie Expansion | Add 200 MW HVDC Tie | 2014-01-01 | 2019-06-01 | 65000000
AEPW | OKLAUNION 345KV SVC | Add +100/-50 SVC on 345 kV bus at Oklaunion. | 2014-10-01 | 2019-06-01 | 18500000
KACY | KAW WEST 5 161/69KV TRANSFORMER CKT 1 | Indeterminate | 2014-06-01 | 2014-06-01 | 0
MIDW | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 MIDW | Rebuild ownership of 39.5 mile circuit | 2013-12-01 | 2018-06-01 | 13864500
MIDW | ST JOHN - ST_JOHN 115KV CKT 1 MIDW | Replace terminal equipment | 2013-12-01 | 2016-06-01 | 450000
MKEC | ST JOHN - ST_JOHN 115KV CKT 1 MKEC | Rebuild 0.1 miles and replace terminal equipment | 2013-12-01 | 2016-06-01 | 562500
NPPD | GRAND ISLAND - SWEETWATER 345KV CKT 2 | Build 63.4 mile second circuit | 2013-12-01 | 2019-06-01 | 96288750
NPPD | HOLT - NELIGH 345KV CKT 1 | Build new 16 miles 345 kV Holt - Neligh and associated terminal equipment | 2013-12-01 | 2019-06-01 | 30656000
OKGE | Cimarron - Mathewson 345 kV Ckt 1 Accelerate | Build new 16 mile 345 kV line from Mathweson to Cimarron. | 2013-12-01 | 2015-06-01 | 10704894
OKGE | Mathewson - Tatonga 345 kV Ckt 2 Accelerate | Build new 61 mile Tatonga - Mathewson 345 kV line. | 2013-12-01 | 2015-06-01 | 26823745
OKGE | Mathewson 345 kV Accelerate | Build new Mathewson 345 kV substation at the intersection of the Woodring-Cimarron and the existing Northwest - Tatonga 345 kV lines. | 2013-12-01 | 2015-06-01 | 6586619
SPS | AMOCO SWITCHING STATION - SUNDOWN INTERCHANGE 230KV CKT 1 | Replace Terminal Equipment | 2015-10-01 | 2016-06-01 | 480000
SPS | CARLISLE INTERCHANGE - TUCO INTERCHANGE 230KV CKT 1 | Replace Terminal Equipment | 2015-10-01 | 2016-06-01 | 240000
SPS | CHAVES COUNTY INTERCHANGE - SAN JUAN MESA TAP 230KV CKT 1 | Replace Terminal Equipment | 2015-10-01 | 2016-06-01 | 240000
SPS | JONES STATION - TUCO INTERCHANGE 230KV CKT 1 | Replace Terminal Equipment | 2015-01-01 | 2016-06-01 | 236250
WERE | 59TH ST - EL PASO 138KV CKT 1 | Rebuild 5.78 miles | 2015-06-01 | 2017-06-01 | 5693300
WERE | 59TH ST - GILL ENERGY CENTER SOUTH 138KV CKT 1 | Rebuild 5.12 miles | 2015-06-01 | 2017-06-01 | 5043200
WERE | HYDRALIC JCT NORTH - MACARTHUR 69KV CKT 1 | Rebuild 2.21 miles | 2018-06-01 | 2018-06-01 | 1745900
WERE | HYDRALIC JCT NORTH - OAKLAWN 69KV CKT 1 | Rebuild 1.39 miles | 2018-06-01 | 2018-06-01 | 1098100
WERE | SMAN_W_3 115.00 - SOUTH MANHATTAN 115KV CKT 1 | Replace Terminal Equipment | 2015-06-01 | 2016-06-01 | 790000
WERE | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 WERE | Rebuild ownership of 39.5 mile circuit | 2013-12-01 | 2018-06-01 | 34061343.75
WERE | WOLF CREEK 345/69KV TRANSFORMER CKT 1 | Install New (2nd) 345/69 kV XFR at Wolfcreek | 2014-10-01 | 2017-06-01 | 4400000
WFEC | CORN TAP - PAOLI 138KV CKT 1 | Reset CT | 2019-06-01 | 2019-06-01 | 225000
WFEC | FLETCHER - MARLOW JCT 69KV CKT 1 | Replace Terminal Equipment | 2019-06-01 | 2019-06-01 | 225000
WFEC | LAKE CREEK - LONEWOLF 69KV CKT 1 | Replace Terminal Equipment | 2014-01-01 | 2016-06-01 | 225000
Construction Pending Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Transmission Owner | Upgrade | Solution | Earliest Date Upgrade Required (DUN) | Estimated Date of Upgrade Completion (EOC)
AEPW | BEAVER - EUREKA SPRINGS 161KV CKT 1 AEPW | Rebuild 1.25 miles of 795 ACSR with 1590 ACSR. Replace wavetrap & jumpers @ Eureka Springs | 2014-06-01 | 2015-06-01
AEPW | FLINT CREEK - SILOAM SPRINGS TAP 345KV CKT 1 AEPW | Replace Terminal Equipment | 2019-06-01 | 2019-06-01
AEPW | NORTH NEW BOSTON - NW TEXARKANA-BANN T 138KV CKT 1 | Rebuild 14.19 miles to 1533.6 ACSR/TW 54/19 | 2015-06-01 | 2017-06-01
GRDA | GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #1 | Add new pole to increase line clearance | 2015-06-01 | 2016-06-01
GRDA | GRDA1 - SILOAM SPRINGS TAP 345KV CKT 1 #2 | Replace Terminal Equipment | 2015-06-01 | 2016-06-01
KACP | Iatan - Jeffrey Energy Center 345 kV KACP | Build 14.2 miles of new 345 kV | 2013-12-01 | 2019-06-01
KACP | Lacygne - Mariosa 345KV KACP | Build approximately 181 miles of 345kV from KCPL Lacygne - AMRN Mariosa | 2013-12-01 | 2019-06-01
MIDW | HAYS PLANT - VINE STREET 115KV CKT 1 | Rebuild 0.23 miles | 2014-01-01 | 2017-06-01
MIPU | BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #1 Accelerate | Upgrade wave trap. | 2014-06-01 | 2015-06-01
MIPU | BLUE SPRING SOUTH - BLUE SPRINGS EAST 161KV CKT 1 #2 Accelerate | Reconductor 2.5 mile from Blue Springs South - Blue Springs East 161 kV to 795 ACSS. Upgrade substation equipment to 2000 Amps. | 2014-06-01 | 2017-06-01
MIPU | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #1 Accelerate | Upgrade Prairie Lee wavetrap to at least 1200 A. | 2014-06-01 | 2015-06-01
MIPU | BLUE SPRING SOUTH - PRAIRIE LEE 161KV CKT 1 #2 Accelerate | Reconductor 3.21 miles from Blue Springs South to Prairie Lee 161 kV to 954 ACSS. Upgrade substation equipment to 2000 Amps. | 2014-06-01 | 2016-06-01
MKEC | CLEARWATER - MILAN TAP 138KV CKT 1 MKEC Accelerate | Rebuild MKEC portion of the 5.6 mile Clearwater-Milan Tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 2013-12-01 | 2017-06-01
MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 2013-12-01 | 2013-12-01
MKEC | HARPER - MILAN TAP 138KV CKT 1 #2 Accelerate | Reconductor 22.1 mile Harper to Milan Tap 138 kV line. | 2013-12-01 | 2017-06-01
MKEC | MEDICINE LODGE - PRATT 115KV CKT 1 | Rebuild 26 mile line | 2014-01-01 | 2014-06-15
MKEC | Mullergren - Reno 345kV Dbl CKT MKEC | Build ownership of approximately 79 miles of double 345kV Mullergren - Reno | 2014-01-01 | 2019-06-01
MKEC | Spearville - Mullergren 345kV Dbl CKT | Build approximately 74 miles of double 345kV Spearville - Mullergren | 2014-01-01 | 2019-06-01
OKGE | ADABELL - VBI 161KV CKT 1 | Replace existing 800 amp wave trap with 1200 amp in VBI sub | 2014-06-01 | 2016-06-01
OKGE | CIMARRON - DRAPER LAKE 345KV CKT 1 | Increase capacity of Draper Lake CT and Cimarron wave trap | 2019-10-01 | 2019-10-01
OKGE | FT SMITH - MUSKOGEE 345KV CKT 1 | Upgrade Ft. Smith 345 kV breakers and switches to 2000 amps | 2014-06-01 | 2016-06-01
OKGE | FT SMITH (FTSMITH1) 500/345/13.8KV TRANSFORMER CKT 1 | Install 2nd 500/345 kV bus tie in Ft. Smith Sub | 2014-06-01 | 2018-06-01
OKGE | Muskogee - VBI 345 kV with 345/161 kV bus tie near VBI | Build 70.95 mile 345 kV line plus two new 345/161 kV bus ties near VBI sub and 10 miles of 161 kV line | 2014-06-01 | 2019-06-01
OKGE | VBI - Arkansas Nuclear One 345kV OKGE | Build 73 miles of 345kV line | 2014-06-01 | 2019-06-01
SPS | DENVER CITY INTERCHANGE N. - MUSTANG STATION N. 115KV CKT 1 | Rebuild 2.82 miles of 954 ACSR with 795 ACSS. | 2019-06-01 | 2019-06-01
SPS | DENVER CITY INTERCHANGE S. - MUSTANG STATION N. 115KV CKT 2 | Rebuild 2.96 miles of 954 ACSR with 795 ACSS. | 2019-06-01 | 2019-06-01
SPS | Potter to Tolk 345 kV | Build 111 mile 345 kV line from Potter to Tolk. Further study analysis will be performed with regard to the SPS North-South Stability Limit to determine whether its rating may be increased based on approved SPP Expansion Plan Network Upgrades scheduled t | 2013-12-01 | 2019-06-01
SPS | YOAKUM COUNTY INTERCHANGE () 230/115/13.2KV TRANSFORMER CKT 1 | Upgrade transformer to 250 MVA. | 2019-06-01 | 2019-06-01
SPS | YOAKUM COUNTY INTERCHANGE () 230/115/13.2KV TRANSFORMER CKT 2 | Upgrade transformer to 250 MVA. | 2019-06-01 | 2019-06-01
WERE | CHISHOLM - MAIZE 138KV CKT 1 #1 | Upgrade disconnect switches, wavetrap, breaker, jumpers | 2015-06-01 | 2016-06-01
WERE | CHISHOLM - MAIZE 138KV CKT 1 #2 | Rebuild 7.25 miles | 2015-06-01 | 2017-06-01
WERE | CLEARWATER - MILAN TAP 138KV CKT 1 WERE Accelerate | Rebuild Westar portion of the Clearwater-Milan tap 115 kV with bundled 1192.5 kcmil ACSR conductor (Bunting) | 2013-12-01 | 2017-06-01
WERE | EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 #1 | Upgrade disconnect switches, wavetrap, breaker, jumpers | 2015-06-01 | 2016-06-01
WERE | EVANS ENERGY CENTER NORTH - MAIZE 138KV CKT 1 #2 | Rebuild 4.8 miles | 2015-06-01 | 2017-06-01
WERE | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | Rebuild the JEC - Hoyt 345kV line as a single circuit with new conductor, poles, and shield wire. Substation work at JEC (Station 1) substation will include removal of 345kV carrier equipment and installation of new fiber optic relay panels. Substation | 2013-12-01 | 2017-06-01
WERE | Iatan - Jeffrey Energy Center 345 kV WERE | Build 56.8 miles of new 345 kV | 2013-12-01 | 2019-06-01
WERE | Mullergren - Reno 345kV Dbl CKT WERE | Build ownership of approximately 79 miles of double 345kV Mullergren - Reno | 2014-01-01 | 2019-06-01
WFEC | GLASS MOUNTAIN - MOORELAND 138KV CKT 1 | Reset CT | 2014-01-01 | 2016-06-01
WFEC | SOUTHWESTERN STATION - WASHITA 138KV CKT 2 | Add Second 138 kV line | 2013-12-01 | 2017-06-01
Expansion Plan Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Transmission Owner | Upgrade | Solution | Earliest Date Upgrade Required (DUN) | Estimated Date of Upgrade Completion (EOC)
AEPW | NORTHWEST TEXARKANA - VALLIANT 345KV CKT 1 | Build a new 76 mile 345 kV line from Valliant to NW Texarkana with at least 3000 A capacity. Upgrade the Valliant and NW Texarkana substations with the necessary breakers and terminal equipment. | 2014-06-01 | 2015-05-01
ITCGP | Line - Clark County - Thistle 345 kV dbl Ckt | Build a new 86 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle 345 kV substation to the new Clark County substation. Build a new 345 kV substation at Thistle with a ring bus and necessary terminal equipment. | 2013-12-01 | 2015-01-01
ITCGP | Line - Spearville - Clark County 345 kV dbl Ckt | Build a new 36 mile double circuit 345 kV line with at least 3000 A capacity from the Spearville substation to the new Clark County substation. Build the Clark County 345 kV substation with a ring bus and necessary terminal equipment. | 2013-12-01 | 2015-01-01
ITCGP | XFR - Thistle 345/138 kV | Install a 400 MVA 345/138 kV transformer at the new 345 kV Thistle substation. | 2013-12-01 | 2015-01-01
KACP | IATAN - NASHUA 345KV CKT 1 | Tap Nashua 345kV bus in Hawthorn - St. Joseph 345 kV line. Build new 345 kV line from Iatan to Nashua,Add Nashua 345/161 kV | 2013-12-01 | 2015-06-01
MIDW | HAYS PLANT - SOUTH HAYS 115KV CKT 1 #2 | Tear down and rebuild of exisiting South Hays - Hays Plant 115 kV line. Tentative plans include rebuilding on existing right-of-way with the possibility of re-routing a portion of the line to new right-of-way as necessary. | 2014-01-01 | 2015-06-01
MKEC | HARPER - MILAN TAP 138KV CKT 1 #1 | Replace Wave Trap at Harper Substation | 2013-12-01 | 2014-12-01
MKEC | PRATT - ST JOHN 115KV CKT 1 | Rebuild 21.9 mile St. John - Pratt 115 kV line with 795 ACSR conductor. | 2015-06-01 | 2015-06-01
OKGE | 5 TRIBES - PECAN CREEK 161KV CKT 1 | Reconductor 4.07 miles of 161 kV. Increase CT ratios at Pecan Creek to 2000A. Replace 2 wave traps, 1-161kV breaker, 3 switches at Five Tribes plus increase CTR. | 2014-06-01 | 2014-06-01
OKGE | Arcadia 345 kV Terminal Upgrades | Upgrade 345 kV 2000 amp breakers and associated switches to 3000 amp at Arcadia Sub. | 2013-12-01 | 2013-12-01
OKGE | Line - Hitchland - Woodward 345 kV dbl Ckt OKGE | Build a new 92 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the SPS interception from the Hitchland substation. Upgrade the Woodward District EHV substation with the necessary breakers and term | 2013-12-01 | 2014-07-01
OKGE | Line - Thistle - Woodward 345 kV dbl Ckt OKGE | Build a new 79 mile double circuit 345 kV line with at least 3000 A capacity from the Woodward District EHV substation to the Kansas/Oklahoma state border towards the Thistle substation. Upgrade the Woodward Distric EHV substation with the necessary brea | 2013-12-01 | 2015-01-01
OKGE | Line - Tuco - Woodward 345 kV line OKGE | Build new 345 kV line from Woodward EHV to Border - Project costs now include Border reactor substation | 2013-12-01 | 2014-06-01
PW | Line - Thistle - Wichita 345 kV dbl Ckt PW | Build a new 78 mile double circuit 345 kV line with at least 3000 A capacity from the Wichita substation to the new Thistle 345 kV substation. | 2013-12-01 | 2015-01-01
PW | Line - Thistle - Woodward 345 kV dbl Ckt PW | Build a new 30 mile double circuit 345 kV line with at least 3000 A capacity from the Thistle substation to the Kansas/Oklahoma state border towards the Woodward District EHV substation. | 2013-12-01 | 2015-01-01
SPS | BAILEY COUNTY INTERCHANGE - CURRY COUNTY INTERCHANGE 115KV CKT 1 | 40 miles 115 kV between Bailey and Curry. | 2014-06-01 | 2015-06-01
SPS | Deaf Smith County Interchange 230/115 kV Transformer Ckt 1 #2 | Upgrade Deaf Smith County Interchange 230/115 kV Ckt 1 transformer to 250 MVA. | 2013-12-01 | 2015-03-01
SPS | Deaf Smith County Interchange 230/115 kV Transformer Ckt 2 | Upgrade Deaf Smith Interchange 230/115 kV transformer Ckt 2 to 250 MVA. | 2013-12-01 | 2015-03-01
SPS | Line - Hitchland - Woodward 345 kV dbl Ckt SPS | Build 30 mile double circuit 345 kV line with at least 3000 A capacity from the Hitchland substation to the OGE interception point from the Woodward District EHV substation. Upgrade the Hitchland substation with the necessary breakers and terminal equipme | 2013-12-01 | 2014-07-01
SPS | Line - Tuco - Woodward 345 kV line SPS | Build new 345 kV line from Tuco to OGE Border station near TX/OK Stateline. Install line reactor outside Border station and line reactors at Tuco. | 2013-12-01 | 2014-06-01
SPS | LUBBOCK SOUTH INTERCHANGE 230/115/13.2KV TRANSFORMER CKT 2 | Install a second 230/115/13.2 kV transformer at Lubbock South. | 2013-12-01 | 2014-12-31
SPS | NEWHART INTERCHANGE PROJECT | Tap the Potter Interchange - Plant X Station 230 kV line for new Newhart Substation and install 230/115 kV, 150/173 MVA transformer. New 15 mile Lampton Interchange - Hart Industrial Substation 115 kV line. New 19 mile Swisher County Interchange - Newhart | 2014-06-01 | 2015-04-30
WERE | Auburn Road 230/115/13.8 kV Ckt 1 Auto Upgrade | Upgrade Auburn Road 230/115 kV transformer to 440 MVA. | 2013-12-01 | 2014-06-01
WERE | GEARY 7 345.00 (GEARY1X) 345/115/13.8KV TRANSFORMER CKT 1 | Tap JEC - Summit 345kV, Ft Jct - McDowell 115kV lines, add 345/115/13.8kV transformer at new Geary substation. | 2019-06-01 | 2019-06-01
WERE | Gill 138/69 kV Transformer Ckt 3 | Install a third 138/69 kV transformer at Gill Energy Center. | 2015-06-01 | 2015-12-01
WERE | Line - Thistle - Wichita 345 kV dbl Ckt WERE | Upgrade the Wichita substation with the necessary breakers and terminal equipment to accommodate two new 345 kV circuits from the new Thistle 345 kV substation | 2013-12-01 | 2015-01-01
WERE | MOUNDRIDGE 138/115KV TRANSFORMER CKT 2 | Install second 138/115 kV transformer at Moundridge. Operate both 138/115 kV transformers normally closed. | 2013-12-01 | 2014-12-01
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Transmission Owner | Upgrade | Solution | Earliest Date Upgrade Required (DUN) | Estimated Date of Upgrade Completion (EOC)
AEPW | BLUEBELL - PRATTVILLE 138KV CKT 1 | Rebuild 9.0 mile Prattville-Bluebell 138 kV line from 795 ACSR to 1926.9 ACSR/TW. Replace line switch near Prattville. New summer ratings 287/287 limited by breaker, switches, CTs, wave trap. | 2013-12-01 | 2015-06-01
AEPW | Elk City 345/230 kV | Expand Elk City substation (or build new station). Install a 345/230 kV 675 MVA transformer at Elk City. | 2013-12-01 | 2018-03-01
AEPW | Elk City to Gracemont 345kV AEPW | Build new 46.5 mile 345 kV line from Elk City to Gracemont (AEP portion). | 2013-12-01 | 2018-03-01
AEPW | Multi - Centerton - Osage Creek 345 kV | Install new 345/161 kV transformer at Kings River (Previous name Osage Creek); Install 9 miles of 345 kV line from Shipe Road to East Rogers; Install 32 miles of 345 kV line from East Rogers to Kings River (previous Osage Creek). | 2014-06-01 | 2016-06-01
AEPW | Multi - Flint Creek – Centerton 345 kV and Centerton- East Centerton 161 kV | Install 9 miles of 161 kV from new Shipe Road Substation to East Centerton Substation; Install 345/161 kV transformer at Shipe Road; Install 18 miles of new 345 kV, 2-954 ACSR line. | 2014-06-01 | 2014-06-01
AEPW | TERRA NITROGEN TAP - VERDIGRIS 138KV CKT 1 | Rebuild 4.31 miles with 1533.3 ACSR/TW | 2014-06-01 | 2017-06-01
NPPD | Cherry Co - Gentleman 345 kV Ckt1 | Build new 345 kV Transmission Line from GGS 345 kV Substation to a new Cherry County 345 kV Substation (76 miles). | 2013-12-01 | 2018-01-01
NPPD | Cherry Co - Holt Co 345 kV Ckt1 | Build new 345 kV Transmission Line from new Cherry County 345 kV Substation to new 345 kV Holt County Substation. (Estimated 146 miles). | 2013-12-01 | 2018-01-01
NPPD | Cherry Co 345 kV Terminal Upgrades | Build new Cherry County 345 kV Substation. | 2013-12-01 | 2018-01-01
NPPD | Neligh - Hoskins 345 kV Ckt1 | Build a new 50 mile 345 kV line from Hoskins to Neligh | 2013-12-01 | 2019-03-01
NPPD | Neligh 345/115 kV Transformer | Construct new substation at Neligh. Install a new 345/115 kV transformer at Neligh. | 2013-12-01 | 2019-03-01
OKGE | Elk City to Gracemont 345kV OKGE | Build new 46.5 mile 345 kV line from Elk City to Gracemont (OGE portion). | 2013-12-01 | 2018-03-01
SPS | Amoco - Tuco 345 kV Ckt 1 | Build new 67-mile 345 kV line from Tuco to Amoco. | 2014-10-01 | 2020-01-01
SPS | Amoco 345/230 kV Transformer Ckt 1 | Install new 345/230 kV transformer at Amoco. | 2014-10-01 | 2020-01-01
SPS | Carlisle Interchange - Wolfforth Interchange 230 kV Ckt 1 | Build 15 miles of new 230 kV line from Carlisle to Wolfforth South and install necessary terminal equipment. | 2019-06-01 | 2019-06-01
SPS | HITCHLAND INTERCHANGE () 230/115/13.2KV TRANSFORMER CKT 2 | Build a second 230/115/13.2 kV transformer at Hitchland. | 2015-06-01 | 2017-06-01
SPS | MULTI - Tuco-New Deal 345 kV | New 345/155kV transformer between Tuco and Stanton, Build new 345kV line between Tuco and high side of new transformer between Tuco and Stanton, Build new 115kV line between Stanton and low side of new transformer between Tuco and Stanton | 2014-10-01 | 2018-06-01
SPS | OXY PERMIAN SUB - SANGER SWITCHING STATION 115KV CKT 1 | Rebuild 0.5-mile Oxy Permian Substation - Sanger Switching Station 115 kV Ckt 1. | 2015-06-01 | 2015-06-01
WERE | BUTLER - WEAVER 138KV CKT 1 | Rebuild 16.31 miles | 2013-12-01 | 2017-06-01
WERE | Cowskin - Westlink 69 kV Ckt 1 | Rebuild 2.1-mile 69 kV line from Cowskin to Westlink. | 2013-12-01 | 2015-12-01
WERE | Hoover South - Tyler 69 kV Ckt 1 | Rebuild 1.96-mile 69 kV line from Tyler to Hoover. | 2013-12-01 | 2014-06-01
WERE | Tyler - Westlink 69 kV Ckt 1 | Rebuild 2.65-mile 69 kV line from Westlink to Tyler. Install terminal equipment at Tyler. | 2013-12-01 | 2015-06-01
WERE | Viola - Clearwater 138kV Ckt1 | Build new 138kV line between new Viola substation 345/138 kV transformer and existing Clearwater 138 kV substation. | 2014-10-01 | 2018-06-01
WERE | Viola - Gill 138kV Ckt1 | Build new 138kV line between new Viola substation 345/138 kV transformer and existing Gill 138 kV substation. | 2014-10-01 | 2018-06-01
WERE | Viola 345/138kV Transformer Ckt 1 | Install new 345/138 kV transformer at Viola substation | 2014-10-01 | 2018-06-01
WFEC | ENOS 138KV | Install 24 Mvar capacitor at ENOS 138KV | 2019-06-01 | 2019-06-01
Network Upgrades requiring credits per Attachment Z2 of the SPP OATT.
Transmission Owner | Upgrade | Solution | Earliest Date Upgrade Required (DUN) | Estimated Date of Upgrade Completion (EOC)
AEPW | ALUMAX TAP - BANN 138KV CKT 1 | Replace six (6) 138 kV switches, five at Bann & one at Alumax Tap. Rebuild 0.67 miles of 1024 ACAR with 2156 ACSR. Replace wavetrap & jumpers @ Bann. Replace breaker 3300 @ Bann. | 2008-06-01 | 2008-06-01
AEPW | ASHDOWN REC (MILLWOOD) - OKAY 138KV CKT 1 | Recunductor and convert line to 138 kV and replace switches at Ashdown REC | 2012-07-01 | 2012-07-01
AEPW | ASHDOWN REC (MILLWOOD) - PATTERSON 138KV CKT 1 | Reconductor Line & Convert Line to 138 kV and convert Patterson station to breaker-and-a half cofiguration | 2012-07-01 | 2012-07-01
AEPW | BANN - RED SPRINGS REC 138KV CKT 1 | Replace 138 kV breakers 3300 & 3310 | 2012-07-01 | 2012-07-01
AEPW | EXPLORER GLENPOOL TAP - RIVERSIDE STATION 138KV CKT 1 AEPW | Reconductor 1.82 miles with ACCC. Replace wave trap jumpers at Riverside. | 2009-06-01 | 2009-06-01
AEPW | HUGO POWER PLANT - VALLIANT 345 KV AEPW | Vallient 345 KV line terminal | 2012-07-01 | 2012-07-01
AEPW | MANDEVILTP4 - SE TEXARKANA 138KV CKT 1 | Build new Turk-SE Texarkana 138 kV line and add SE Texarkana 138 kV terminal. | 2012-07-01 | 2012-07-01
AEPW | MANDEVILTP4 - TURK 138KV CKT 1 | Build new Turk-SE Texarkana 138 kV line and add SE Texarkana 138 kV terminal. | 2012-07-01 | 2012-07-01
AEPW | MCNAB REC - TURK 115KV CKT 1 | Build a new two mile, 138 kV, 1590 ACSR line section (operated at 115 kV) from Turk Substation to the existing Okay- Hope 115 kV line to form a Turk - Hope 115 kV line. | 2012-07-01 | 2012-07-01
AEPW | SUGAR HILL - TURK 138KV CKT 1 | Build new Turk-Sugar Hill 138 kV line and add Sugar Hill 138 kV terminal. | 2012-07-01 | 2012-07-01
EMDE | SUB 110 - ORONOGO JCT. - SUB 167 - RIVERTON 161KV CKT 1 | Reconductor Oronogo 59467 to Riverton 59469 with Bundled 556 ACSR | 2011-06-01 | 2011-06-01
KACP | LACYGNE - WEST GARDNER 345KV CKT 1 | KCPL Sponsored Project to Reconductor Line to be In-Service by 6/1/2006 | 2006-06-01 | 2006-06-01
MIDW | CIRCLE - RICE_CO 230KV CKT 1 | Convert from 115kV to 230kV operation | 2012-10-01 | 2012-11-15
MIDW | LYONS - RICE_CO 115KV CKT 1 | Rebuild 11.7 mile line | 2012-10-01 | 2013-04-01
MIDW | RICE_CO 230/115KV TRANSFORMER CKT 1 | Add 230/115kV Transformer | 2012-10-01 | 2012-11-15
MKEC | ALEXANDER - PRATT 115KV CKT 1 | Rebuild line | 2009-12-01 | 2013-06-01
MKEC | ALEXANDER - SAWYER 3 115.00 115KV CKT 1 | Rebuild line | 2009-12-01 | 2013-06-01
MKEC | BARBER - MEDICINE LODGE 115KV CKT 1 | Rebuild line | 2009-12-01 | 2013-06-01
MKEC | BARBER - SAWYER 115KV CKT 1 | Rebuild line | 2009-12-01 | 2013-06-01
MKEC | BARBER (BARBER 4) 138/115/2.72KV TRANSFORMER CKT 1 | Upgrade transformer | 2009-12-01 | 2013-06-01
MKEC | CLIFTON - GREENLEAF 115KV CKT 1 | Rebuild 14.4 miles | 2011-06-01 | 2013-06-01
MKEC | FLATRDG3 138.00 - MEDICINE LODGE 138KV CKT 1 | Rebuild 8.05 mile line | 2009-12-01 | 2013-06-01
MKEC | FLATRDG3 138.00 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 2009-12-01 | 2013-06-01
MKEC | GREENLEAF - KNOB HILL 115KV CKT 1 MKEC | Rebuild 43.5% Ownership of 20.9 miles | 2013-06-01 | 2013-06-01
MKEC | Judson Large - North Judson Large 115KV CKT 2 | Construct approximately 1 mile of new 115kV for 2nd circuit | 2013-10-01 | 2015-06-01
MKEC | Mullergren - Reno 345kV Dbl CKT MKEC | Build ownership of approximately 79 miles of double 345kV Mullergren - Reno | 2013-10-01 | 2019-06-01
MKEC | North Judson Large - Spearville 115KV CKT 2 | Construct approximately 15 miles of new 115kV for 2nd circuit | 2013-10-01 | 2015-06-01
MKEC | Spearville - Mullergren 345kV Dbl CKT | Build approximately 74 miles of double 345kV Spearville - Mullergren | 2013-10-01 | 2019-06-01
MKEC | Spearville 345/115/13.8kV Transformer CKT 3 | Install 345/115/13.8kV Transformer CKT 3 at Spearville | 2013-10-01 | 2015-06-01
NPPD | ALBION - PETERSBURG 115KV CKT 1 | Replace Breaker Switch 1106-D and jumpers at Albion. Replace main bus at Petersburg. Upgrade and replace transmission structures on 115 kV lineto facilitate 100 degrees Centigrade line operation. | 2013-01-01 | 2013-01-01
NPPD | NELIGH - PETERSBURG 115KV CKT 1 | Replace Breaker 1106, jumpers, and 115 kV Switch 1106-D2 at Neligh. Replace main bus at Petersburg. Upgrade and replace transmission structures on 115 kV lineto facilitate 100 degrees Centigrade line operation. | 2013-01-01 | 2013-01-01
OKGE | BEELINE - EXPLORER GLENPOOL TAP 138KV CKT 1 | Reconductor .92miles of line with Drake ACCC/TW. | 2009-06-01 | 2009-06-01
OKGE | CIMARRON - DRAPER LAKE 345KV CKT 1 | Increase capacity of Draper Lake CT and Cimarron wave trap | 2014-10-01 | 2016-06-01
OKGE | EXPLORER GLENPOOL TAP - RIVERSIDE STATION 138KV CKT 1 OKGE | Reconductor 1.82 miles line with Drake ACCC/TW. | 2009-06-01 | 2009-06-01
OKGE | GRACMNT4 138.00 - WASHITA 138KV CKT 2 OKGE | Build 138kV Terminal. | 2012-01-01 | 2012-01-01
OKGE | KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1 | Replace bus tie with 100MVA transformer | 2006-06-01 | 2008-06-01
OKGE | NORTHWEST - TATONGA 345KV CKT 1 | Build 345 kV line | 2010-01-01 | 2010-01-01
OKGE | TATONGA - WOODWARD 345KV CKT 1 | Build 345 kV line | 2010-01-01 | 2010-01-01
OKGE | WOODWARD - IODINE 138KV CKT 1 | Tap Iodine to Woodward 138 kV line | 2010-01-01 | 2010-01-01
OKGE | WOODWARD - WOODWARD EHV 138KV CKT 1 | Build .5 miles of 138 kV and install terminal equipment | 2010-01-01 | 2010-01-01
OKGE | WOODWARD - WOODWARD EHV 138KV CKT 2 | Build .5 miles of 138 kV and install terminal equipment | 2010-01-01 | 2010-01-01
OKGE | WOODWARD 345/138KV TRANSFORMER CKT 1 | Install 345/138 kV XF | 2010-01-01 | 2010-01-01
SPS | CHERRY6 230.00 - Harrington Station East Bus 230KV CKT 1 | Replace wavetrap at Harrington East | 2015-06-01 | 2015-06-01
WERE | LYONS - WHEATLAND 115KV CKT 1 #1 | Replace CTs | 2012-10-01 | 2013-07-15
WERE | LYONS - WHEATLAND 115KV CKT 1 #2 | Rerate circuit to 1000 amps | 2012-10-01 | 2013-07-15
WERE | Mullergren - Reno 345kV Dbl CKT WERE | Build ownership of approximately 79 miles of double 345kV Mullergren - Reno | 2013-10-01 | 2019-06-01
WFEC | ALTUS SW - NAVAJO 69KV CKT 1 | Upgrade Terminal Equipment at Altus SW, 300-600A, new rating conductor 53/65MVA | 2013-06-01 | 2013-06-01
WFEC | CANTON - TALOGA 69KV CKT 1 | UPGRADE CANTON TO TALOGA TO 336.4 | 2011-06-01 | 2013-06-01
WFEC | APACHE CO 138.00 - PARADISE 138KV CKT 1 | Upgrade Paradise to Apache Co to 1113 | 2010-06-01 | 2013-06-01
WFEC | GRACMNT4 138.00 - WASHITA 138KV CKT 2 WFEC | Build approximately 6 miles of 138kV. | 2012-01-01 | 2012-01-01
WFEC | HUGO POWER PLANT - VALLIANT 345KV CKT 1 WFEC | New 19 miles 345 KV | 2012-07-01 | 2012-07-01
WFEC | HUGO POWER PLANT 345/138KV TRANSFORMER CKT 1 | New 345/138 kv Auto | 2012-07-01 | 2012-07-01
WFEC | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | Auto XFMR 56 to 112MVA | 2010-10-01 | 2013-06-01

## Table5
Transmission Owner | UpgradeName | Solution | Earliest Date Upgrade Required (DUN) | Estimated Date of Upgrade Completion (EOC) | Estimated Engineering & Construction Cost
AECI | 7JASPER 345.00 - BLACKBERRY 345KV CKT 1 #1 | Replace structures to rerate to 100C | 2015-06-01 | 2015-06-01 | 100000
AECI | CLINTON - MONTROSE 161KV CKT 1 AECI | Upgrade limiting terminal equipment at Clinton | 2015-06-01 | 2016-06-01 | 180000
AECI | FAIRFAX 138/69KV TRANSFORMER CKT 1 | Replace with 84 MVA unit | 2015-06-01 | 2017-06-01 | 2000000
AMMO | 7OVERTON 345.00 () 345/161/13.8KV TRANSFORMER CKT 1 | Replace existing 345-161kV transformer with 560MVA unit, install 345kV high side breaker, 138kV XFMR low side breaker and bus to obtain 2000A min | 2014-01-01 | 2014-06-01 | Note 1
AMRN | Lacygne - Mariosa 345KV AMRN | Indeterminate | 2013-12-01 | 2019-06-01 | Indeterminate
CELE | NORTH SLIDELL - SLIDELL 230KV CKT 1 CELE | Indeterminate | 2015-10-01 | 2015-10-01 | Indeterminate
EES | ARKANSAS NUCLEAR ONE - PLEASANT HILL 500KV CKT 1 | Indeterminate | 2014-10-01 | 2014-10-01 | Indeterminate
EES | Arkansas Nuclear One 500/345 Transformer | Build 500/345 kV Transformer at ANO | 2014-06-01 | 2019-06-01 | 12000000
EES | NORTH SLIDELL - SLIDELL 230KV CKT 1 EES | Indeterminate | 2015-10-01 | 2015-10-01 | Indeterminate
EES | VBI - Arkansas Nuclear One 345kV EES | Indeterminate | 2014-06-01 | 2019-06-01 | Indeterminate
SWPA | BEAVER - EUREKA SPRINGS 161KV CKT 1 SWPA | Rebuild line using 1590MCM ACSR conductor on tubular steel H-frame structures. Replace breakers and switches at Beaver. Remove wave traps. | 2014-06-01 | 2015-06-01 | Note 2
SWPA | BUFORD 5 161.00 - BULL SHOALS 161KV CKT 1 | Rebuild line with 1192 ACSR, Grackle | 2014-06-01 | 2017-06-01 | Note 2
SWPA | BUFORD 5 161.00 - NORFORK 161KV CKT 1 | Rebuild line with 1192 ACSR, Grackle | 2014-06-01 | 2017-06-01 | Note 2
Note 1: Overton 345/161/13.8 kV Transformer is included in the Ameren Expansion plan with an in-service date of 6/1/2014. Cost will not be allocated to the transmission customer.
Note 2: SWPA Network Upgrades - Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.

## Table6
Upgrade: | NORTH NEW BOSTON - NW TEXARKANA-BANN T 138KV CKT 1
Limiting Facility: | NORTH NEW BOSTON - NW TEXARKANA-BANN T 138KV CKT 1
Direction: | TO->FROM
Line Outage: | PATTERSON - SOUTH FOREMAN REC 138KV CKT 1
Flowgate: | 2012AG3AFS41T1255518SP
Date Redispatch Needed: | 6/1/18 - 10/1/18
Season Flowgate Identified: | 2018 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
77410350 | 1.8 | 1.8
Source Control Area | Source | Maximum Increment (MW) | GSF | Sink Control Area | Sink | Maximum Decrement (MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
AEPW | WILKES 138KV | 487.1183 | -0.06747 | AEPW | TURK 138KV | 618 | 0.03593 | -0.1034 | 18
AEPW | WILKES 138KV | 487.1183 | -0.06747 | AEPW | FULTON 115KV | 152.87 | 0.02795 | -0.09542 | 19
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | AEPW | TURK 138KV | 618 | 0.03593 | -0.08625 | 21
AEPW | WILKES 138KV | 487.1183 | -0.06747 | WFEC | HUGO 138KV | 440 | 0.01888 | -0.08635 | 21
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | AEPW | FULTON 115KV | 152.87 | 0.02795 | -0.07827 | 23
AEPW | WILKES 138KV | 487.1183 | -0.06747 | WFEC | ANADARKO 138KV | 410.7952 | 0.0105 | -0.07797 | 23
AEPW | WILKES 138KV | 487.1183 | -0.06747 | WFEC | BLUCAN2 0.6900 34KV | 227 | 0.01045 | -0.07792 | 23
AEPW | WILKES 138KV | 487.1183 | -0.06747 | AEPW | COMANCHE 138KV | 195 | 0.01089 | -0.07836 | 23
AEPW | WILKES 138KV | 487.1183 | -0.06747 | AEPW | COMANCHE 69KV | 78 | 0.01085 | -0.07832 | 23
AEPW | WILKES 138KV | 487.1183 | -0.06747 | WFEC | COMMANCHE CO SUB 34KV | 100 | 0.01045 | -0.07792 | 23
AEPW | WILKES 138KV | 487.1183 | -0.06747 | OKGE | SEMINOLE 138KV | 250.8129 | 0.01067 | -0.07814 | 23
AEPW | WILKES 138KV | 487.1183 | -0.06747 | OKGE | SEMINOLE 345KV | 668.6758 | 0.01049 | -0.07796 | 23
AEPW | WILKES 138KV | 487.1183 | -0.06747 | AEPW | SOUTHWESTERN STATION 138KV | 243.936 | 0.01049 | -0.07796 | 23
AEPW | WILKES 138KV | 487.1183 | -0.06747 | SPS | ANTELOPE 230KV | 78.9921 | 0.00924 | -0.07671 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | WERE | BARBER CO SUB 34KV | 200 | 0.00771 | -0.07518 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | SPS | BLACKHAWK 115KV | 224 | 0.00879 | -0.07626 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | GRDA | BOOMER 69KV | 24 | 0.00854 | -0.07601 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | AEPW | BUFFCK1 34.500 230KV | 99 | 0.00964 | -0.07711 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | OKGE | CANADN12 34.500 345KV | 298.2 | 0.00965 | -0.07712 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | SPS | CAPROCK 0KV | 80 | 0.00909 | -0.07656 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | OKGE | CENT 21 34.500 138KV | 120 | 0.00847 | -0.07594 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | OKGE | CHSHMVW1 34.500 345KV | 202 | 0.00841 | -0.07588 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | WERE | CITY OF AUGUSTA 69KV | 20 | 0.00729 | -0.07476 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | WERE | CITY OF MULVANE 69KV | 10.2 | 0.00731 | -0.07478 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | WERE | CLR_3 0.6900 34KV | 75 | 0.00712 | -0.07459 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | SPS | CLR_3 0.6900 34KV | 160 | 0.00887 | -0.07634 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | WERE | CLR_4 0.6900 34KV | 75 | 0.00712 | -0.07459 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | AEPW | COGENTRIX 345KV | 1038 | 0.00812 | -0.07559 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | OKGE | CRSRDW21 34.500 345KV | 177 | 0.00877 | -0.07624 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | SPS | CUNNINGHAM 230KV | 187 | 0.00913 | -0.0766 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | OKGE | DEWEY CO SUB 4 138KV | 130 | 0.00881 | -0.07628 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | WERE | EVANS ENERGY CENTER 138KV | 671 | 0.00727 | -0.07474 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | OKGE | FPLWND11 34.500 138KV | 102 | 0.00868 | -0.07615 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | WERE | GILL ENERGY CENTER 138KV | 194 | 0.00731 | -0.07478 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | OKGE | GRADY CO SUB 345KV | 99 | 0.01001 | -0.07748 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | GRDA | GRDA1 161KV | 480 | 0.0071 | -0.07457 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | SPS | GS-PHWDRNCH134.500 230KV | 79 | 0.00887 | -0.07634 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | WERE | HARPER CO SUB 34KV | 714 | 0.00771 | -0.07518 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | SPS | HARRINGTON 230KV | 1031 | 0.00886 | -0.07633 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | SPS | HOBBS PLANT #2 (CT) 115KV | 289 | 0.00913 | -0.0766 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | SPS | HOBBS PLANT #3 (ST) 230KV | 213 | 0.00913 | -0.0766 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | SPS | HOPI_SUB 112.470 115KV | 10 | 0.00912 | -0.07659 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | OKGE | HORSESHOE LAKE 138KV | 608 | 0.00972 | -0.07719 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | OKGE | HORSESHOE LAKE 69KV | 16 | 0.00977 | -0.07724 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | SPS | HUBRCO2 69KV | 8 | 0.0088 | -0.07627 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | SPS | JONES_4 116.500 230KV | 472 | 0.0092 | -0.07667 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | SPS | LEA_ROAD 112.470 115KV | 10 | 0.00913 | -0.0766 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | SPS | LP-BRND2 69KV | 21 | 0.00921 | -0.07668 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | SPS | LP-HOLL2 69KV | 132 | 0.0092 | -0.07667 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | SPS | LP-MACK2 69KV | 80 | 0.00921 | -0.07668 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | SPS | MADOX 115KV | 119 | 0.00913 | -0.0766 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | SPS | MAJESTIC WIND 115KV | 160 | 0.00884 | -0.07631 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | OKGE | MCCLAIN 138KV | 465.6 | 0.00987 | -0.07734 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | SPS | MONUMENT 112.470 115KV | 10 | 0.00913 | -0.0766 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | WFEC | MORLND 138KV | 272 | 0.00869 | -0.07616 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | OKGE | MUSKOGEE 345KV | 1542.5 | 0.00822 | -0.07569 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | SPS | MUSTANG 115KV | 350 | 0.00914 | -0.07661 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | OKGE | MUSTANG 138KV | 236 | 0.0097 | -0.07717 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | SPS | MUSTANG_6 18.000 230KV | 394 | 0.00914 | -0.07661 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | SPS | NICHOLS 115KV | 82 | 0.00888 | -0.07635 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | AEPW | NORTHEASTERN STATION 138KV | 854 | 0.00755 | -0.07502 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | AEPW | NORTHEASTERN STATION 345KV | 460 | 0.00762 | -0.07509 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | SPS | OCOTILLO 112.470 115KV | 10 | 0.00912 | -0.07659 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | AEPW | OEC 345KV | 1460 | 0.00794 | -0.07541 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | OMPA | OMPA-KAW 69KV | 28.8 | 0.00824 | -0.07571 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | OMPA | OMPA-PONCA CITY 69KV | 75.8066 | 0.00824 | -0.07571 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | OKGE | OU SPIRIT 138KV | 120 | 0.00844 | -0.07591 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | SPS | PLANTX 115KV | 67.8511 | 0.00909 | -0.07656 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | SPS | PLANTX 230KV | 183 | 0.00909 | -0.07656 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | WERE | PRATT 3KV | 8.8 | 0.00721 | -0.07468 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | SPS | QUAY_CNTY 113.800 115KV | 23 | 0.00909 | -0.07656 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | OKGE | REDBUD 345KV | 1203.5 | 0.00943 | -0.0769 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | WFEC | RHWIND1WG11 0.6900 34KV | 123 | 0.00976 | -0.07723 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | AEPW | RIVERSIDE STATION 138KV | 917 | 0.00814 | -0.07561 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | SPS | S_JAL 112.470 115KV | 10 | 0.00913 | -0.0766 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | SPS | SAN JUAN 230KV | 120 | 0.00911 | -0.07658 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | WFEC | SLEEPING BEAR 138KV | 80 | 0.00866 | -0.07613 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | OKGE | SMITH COGEN 138KV | 107 | 0.00973 | -0.0772 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | OKGE | SOONER 138KV | 535 | 0.00837 | -0.07584 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | OKGE | SOONER 345KV | 537 | 0.00837 | -0.07584 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | SPS | SPNSPUR_WND134.500 345KV | 161 | 0.00865 | -0.07612 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | OKGE | SPRING CREEK UNIT 3 AND 4 345KV | 300 | 0.00928 | -0.07675 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | SPS | STEER WATER 115KV | 80 | 0.00896 | -0.07643 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | SPS | TOLK 230KV | 1014.523 | 0.0091 | -0.07657 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | OKGE | WOODWARD CO SUB 2 138KV | 152 | 0.00844 | -0.07591 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | AEPW | WTH WIND 34.500 34KV | 148 | 0.00992 | -0.07739 | 24
AEPW | WILKES 138KV | 487.1183 | -0.06747 | WERE | 6TH STREET 115KV | 9.7 | 0.00593 | -0.0734 | 25
AEPW | WILKES 138KV | 487.1183 | -0.06747 | OKGE | AES 161KV | 320 | 0.00451 | -0.07198 | 25
AEPW | WILKES 138KV | 487.1183 | -0.06747 | WERE | ANDERSONCO 345.00 345KV | 85 | 0.00659 | -0.07406 | 25
AEPW | WILKES 138KV | 487.1183 | -0.06747 | EMDE | ASBURY 161KV | 192 | 0.00636 | -0.07383 | 25
AEPW | WILKES 138KV | 487.1183 | -0.06747 | SWPA | CARTHAGE 69KV | 32 | 0.00612 | -0.07359 | 25
AEPW | WILKES 138KV | 487.1183 | -0.06747 | WERE | CLAYCSS3 115.00 115KV | 22.3 | 0.00642 | -0.07389 | 25
AEPW | WILKES 138KV | 487.1183 | -0.06747 | WERE | ELK CO SUB 34KV | 401 | 0.00708 | -0.07455 | 25
AEPW | WILKES 138KV | 487.1183 | -0.06747 | AEPW | ELLIS 69KV | 17 | 0.00475 | -0.07222 | 25
AEPW | WILKES 138KV | 487.1183 | -0.06747 | WERE | EMPORIA ENERGY CENTER 345KV | 413.6875 | 0.00638 | -0.07385 | 25
AEPW | WILKES 138KV | 487.1183 | -0.06747 | AEPW | FLINT CREEK 161KV | 528 | 0.00673 | -0.0742 | 25
AEPW | WILKES 138KV | 487.1183 | -0.06747 | GRDA | GRDA1 345KV | 494 | 0.00705 | -0.07452 | 25
AEPW | WILKES 138KV | 487.1183 | -0.06747 | WERE | HUTCHINSON ENERGY CENTER 115KV | 166 | 0.00691 | -0.07438 | 25
AEPW | WILKES 138KV | 487.1183 | -0.06747 | WERE | JEFFREY ENERGY CENTER 230KV | 730 | 0.00618 | -0.07365 | 25
AEPW | WILKES 138KV | 487.1183 | -0.06747 | WERE | JEFFREY ENERGY CENTER 345KV | 1460 | 0.00617 | -0.07364 | 25
AEPW | WILKES 138KV | 487.1183 | -0.06747 | GRDA | KERR 115KV | 22.25 | 0.00708 | -0.07455 | 25
AEPW | WILKES 138KV | 487.1183 | -0.06747 | GRDA | KERR 161KV | 21.9191 | 0.00707 | -0.07454 | 25
AEPW | WILKES 138KV | 487.1183 | -0.06747 | EMDE | LARUSSEL 161KV | 100 | 0.00596 | -0.07343 | 25
AEPW | WILKES 138KV | 487.1183 | -0.06747 | WERE | LAWRENCE ENERGY CENTER 115KV | 159 | 0.00593 | -0.0734 | 25
AEPW | WILKES 138KV | 487.1183 | -0.06747 | WERE | LAWRENCE ENERGY CENTER 230KV | 350.7009 | 0.00598 | -0.07345 | 25
AEPW | WILKES 138KV | 487.1183 | -0.06747 | EMDE | OZARK BEACH 161KV | 18 | 0.00505 | -0.07252 | 25
AEPW | WILKES 138KV | 487.1183 | -0.06747 | GRDA | PENSACOLA 161KV | 17 | 0.00696 | -0.07443 | 25
AEPW | WILKES 138KV | 487.1183 | -0.06747 | GRDA | PENSACOLA 69KV | 17 | 0.00693 | -0.0744 | 25
AEPW | WILKES 138KV | 487.1183 | -0.06747 | EMDE | RIVERTON 161KV | 72 | 0.00642 | -0.07389 | 25
AEPW | WILKES 138KV | 487.1183 | -0.06747 | EMDE | RIVERTON 69KV | 40.9406 | 0.00639 | -0.07386 | 25
AEPW | WILKES 138KV | 487.1183 | -0.06747 | GRDA | SALINA 161KV | 199.9855 | 0.00707 | -0.07454 | 25
AEPW | WILKES 138KV | 487.1183 | -0.06747 | EMDE | STATE LINE 161KV | 523.4572 | 0.00636 | -0.07383 | 25
AEPW | WILKES 138KV | 487.1183 | -0.06747 | WERE | TECUMSEH ENERGY CENTER 115KV | 204 | 0.00602 | -0.07349 | 25
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | WFEC | HUGO 138KV | 440 | 0.01888 | -0.0692 | 26
AEPW | WILKES 138KV | 487.1183 | -0.06747 | AEPW | FITZHUGH 161KV | 171 | 0.0039 | -0.07137 | 26
AEPW | WILKES 138KV | 487.1183 | -0.06747 | SWPA | JONESBORO 161KV | 97.7328 | 0.00103 | -0.0685 | 27
AEPW | WILKES 138KV | 487.1183 | -0.06747 | SWPA | PARAGOULD 69KV | 10 | 0.00111 | -0.06858 | 27
AEPW | WILKES 138KV | 487.1183 | -0.06747 | SWPA | SIKESTON 161KV | 235 | 0.00142 | -0.06889 | 27
AEPW | WILKES 345KV | 354 | -0.02869 | AEPW | TURK 138KV | 618 | 0.03593 | -0.06462 | 28
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | OKGE | G12_004_2 0.6900 34KV | 40 | 0.01249 | -0.06281 | 29
AEPW | WILKES 138KV | 487.1183 | -0.06747 | LEPA | BAYOU RAMOS 138KV | 30.1531 | -0.00507 | -0.0624 | 29
AEPW | WILKES 138KV | 487.1183 | -0.06747 | LEPA | CITY OF HOUMA SUB 115KV | 70 | -0.00429 | -0.06318 | 29
AEPW | WILKES 138KV | 487.1183 | -0.06747 | LEPA | IRION SUB 69KV | 25 | -0.00455 | -0.06292 | 29
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | AEPW | TURK 138KV | 618 | 0.03593 | -0.06022 | 30
AEPW | KNOXLEE 138KV | 474 | -0.02403 | AEPW | TURK 138KV | 618 | 0.03593 | -0.05996 | 30
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | AEPW | TURK 138KV | 618 | 0.03593 | -0.0606 | 30
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | WFEC | ANADARKO 138KV | 410.7952 | 0.0105 | -0.06082 | 30
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | WFEC | BLUCAN2 0.6900 34KV | 227 | 0.01045 | -0.06077 | 30
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | AEPW | BUFFCK1 34.500 230KV | 99 | 0.00964 | -0.05996 | 30
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | OKGE | CANADN12 34.500 345KV | 298.2 | 0.00965 | -0.05997 | 30
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | AEPW | COMANCHE 138KV | 195 | 0.01089 | -0.06121 | 30
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | AEPW | COMANCHE 69KV | 78 | 0.01085 | -0.06117 | 30
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | WFEC | COMMANCHE CO SUB 34KV | 100 | 0.01045 | -0.06077 | 30
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | AEPW | G09-16 0.6900 34KV | 100 | 0.00986 | -0.06018 | 30
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | WFEC | G12-028 0.6900 34KV | 323.62 | 0.00995 | -0.06027 | 30
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | OKGE | GRADY CO SUB 345KV | 99 | 0.01001 | -0.06033 | 30
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | OKGE | HORSESHOE LAKE 138KV | 608 | 0.00972 | -0.06004 | 30
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | OKGE | HORSESHOE LAKE 69KV | 16 | 0.00977 | -0.06009 | 30
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | OKGE | MCCLAIN 138KV | 465.6 | 0.00987 | -0.06019 | 30
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | OKGE | MUSTANG 138KV | 236 | 0.0097 | -0.06002 | 30
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | WFEC | RHWIND1WG11 0.6900 34KV | 123 | 0.00976 | -0.06008 | 30
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | OKGE | SEMINOLE 138KV | 250.8129 | 0.01067 | -0.06099 | 30
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | OKGE | SEMINOLE 345KV | 668.6758 | 0.01049 | -0.06081 | 30
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | OKGE | SMITH COGEN 138KV | 107 | 0.00973 | -0.06005 | 30
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | AEPW | SOUTHWESTERN STATION 138KV | 243.936 | 0.01049 | -0.06081 | 30
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | AEPW | WTH WIND 34.500 34KV | 148 | 0.00992 | -0.06024 | 30
AEPW | WILKES 138KV | 487.1183 | -0.06747 | AEPW | WELSH 345KV | 1056 | -0.00713 | -0.06034 | 30
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | SPS | ANTELOPE 230KV | 78.9921 | 0.00924 | -0.05956 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | SPS | ASGI-10-10 13.800 115KV | 42 | 0.00913 | -0.05945 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | SPS | ASGI2011-0010.6900 34KV | 28.8 | 0.00913 | -0.05945 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | WERE | BARBER CO SUB 34KV | 200 | 0.00771 | -0.05803 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | SPS | BLACKHAWK 115KV | 224 | 0.00879 | -0.05911 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | GRDA | BOOMER 69KV | 24 | 0.00854 | -0.05886 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | SPS | CAPROCK 0KV | 80 | 0.00909 | -0.05941 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | OKGE | CENT 21 34.500 138KV | 120 | 0.00847 | -0.05879 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | OKGE | CHSHMVW1 34.500 345KV | 202 | 0.00841 | -0.05873 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | SPS | CLR_3 0.6900 34KV | 160 | 0.00887 | -0.05919 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | AEPW | COGENTRIX 345KV | 1038 | 0.00812 | -0.05844 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | OKGE | CRSRDW21 34.500 345KV | 177 | 0.00877 | -0.05909 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | SPS | CUNNINGHAM 230KV | 187 | 0.00913 | -0.05945 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | OKGE | DEWEY CO SUB 4 138KV | 130 | 0.00881 | -0.05913 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | OKGE | FPLWND11 34.500 138KV | 102 | 0.00868 | -0.059 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | SPS | G08-47 0.5750 34KV | 200 | 0.00829 | -0.05861 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | SPS | G12-038 18.000 345KV | 712 | 0.00917 | -0.05949 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | SPS | GS-PHWDRNCH134.500 230KV | 79 | 0.00887 | -0.05919 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | WERE | HARPER CO SUB 34KV | 714 | 0.00771 | -0.05803 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | SPS | HARRINGTON 230KV | 1031 | 0.00886 | -0.05918 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | SPS | HOBBS PLANT #2 (CT) 115KV | 289 | 0.00913 | -0.05945 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | SPS | HOBBS PLANT #3 (ST) 230KV | 213 | 0.00913 | -0.05945 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | SPS | JONES_4 116.500 230KV | 472 | 0.0092 | -0.05952 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | SPS | LP-BRND2 69KV | 21 | 0.00921 | -0.05953 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | SPS | LP-HOLL2 69KV | 132 | 0.0092 | -0.05952 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | SPS | LP-MACK2 69KV | 80 | 0.00921 | -0.05953 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | SPS | MADOX 115KV | 119 | 0.00913 | -0.05945 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | SPS | MAJESTIC WIND 115KV | 160 | 0.00884 | -0.05916 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | WFEC | MORLND 138KV | 272 | 0.00869 | -0.05901 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | OKGE | MUSKOGEE 345KV | 1542.5 | 0.00822 | -0.05854 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | SPS | MUSTANG 115KV | 350 | 0.00914 | -0.05946 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | SPS | MUSTANG_6 18.000 230KV | 394 | 0.00914 | -0.05946 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | SPS | NICHOLS 115KV | 82 | 0.00888 | -0.0592 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | AEPW | OEC 345KV | 1460 | 0.00794 | -0.05826 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | OMPA | OMPA-KAW 69KV | 28.8 | 0.00824 | -0.05856 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | OMPA | OMPA-PONCA CITY 69KV | 75.8066 | 0.00824 | -0.05856 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | OKGE | OU SPIRIT 138KV | 120 | 0.00844 | -0.05876 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | SPS | PLANTX 115KV | 67.8511 | 0.00909 | -0.05941 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | SPS | PLANTX 230KV | 183 | 0.00909 | -0.05941 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | SPS | QUAY_CNTY 113.800 115KV | 23 | 0.00909 | -0.05941 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | OKGE | REDBUD 345KV | 1203.5 | 0.00943 | -0.05975 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | AEPW | RIVERSIDE STATION 138KV | 917 | 0.00814 | -0.05846 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | SPS | SAN JUAN 230KV | 120 | 0.00911 | -0.05943 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | WFEC | SLEEPING BEAR 138KV | 80 | 0.00866 | -0.05898 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | OKGE | SOONER 138KV | 535 | 0.00837 | -0.05869 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | OKGE | SOONER 345KV | 537 | 0.00837 | -0.05869 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | SPS | SPNSPUR_WND134.500 345KV | 161 | 0.00865 | -0.05897 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | OKGE | SPRING CREEK UNIT 3 AND 4 345KV | 300 | 0.00928 | -0.0596 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | SPS | STEER WATER 115KV | 80 | 0.00896 | -0.05928 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | SPS | TOLK 230KV | 1014.523 | 0.0091 | -0.05942 | 31
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | OKGE | WOODWARD CO SUB 2 138KV | 152 | 0.00844 | -0.05876 | 31
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | AEPW | TURK 138KV | 618 | 0.03593 | -0.05759 | 32
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | WERE | ANDERSONCO 345.00 345KV | 85 | 0.00659 | -0.05691 | 32
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | EMDE | ASBURY 161KV | 192 | 0.00636 | -0.05668 | 32
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | SWPA | CARTHAGE 69KV | 32 | 0.00612 | -0.05644 | 32
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | WERE | CITY OF AUGUSTA 69KV | 20 | 0.00729 | -0.05761 | 32
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | WERE | CLAYCSS3 115.00 115KV | 22.3 | 0.00642 | -0.05674 | 32
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | WERE | CLR_3 0.6900 34KV | 75 | 0.00712 | -0.05744 | 32
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | WERE | CLR_4 0.6900 34KV | 75 | 0.00712 | -0.05744 | 32
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | WERE | ELK CO SUB 34KV | 401 | 0.00708 | -0.0574 | 32
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | WERE | EMPORIA ENERGY CENTER 345KV | 413.6875 | 0.00638 | -0.0567 | 32
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | WERE | EVANS ENERGY CENTER 138KV | 671 | 0.00727 | -0.05759 | 32
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | AEPW | FLINT CREEK 161KV | 528 | 0.00673 | -0.05705 | 32
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | WERE | GILL ENERGY CENTER 138KV | 194 | 0.00731 | -0.05763 | 32
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | GRDA | GRDA1 161KV | 480 | 0.0071 | -0.05742 | 32
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | GRDA | GRDA1 345KV | 494 | 0.00705 | -0.05737 | 32
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | WERE | HUTCHINSON ENERGY CENTER 115KV | 166 | 0.00691 | -0.05723 | 32
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | WERE | JEFFREY ENERGY CENTER 230KV | 730 | 0.00618 | -0.0565 | 32
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | WERE | JEFFREY ENERGY CENTER 345KV | 1460 | 0.00617 | -0.05649 | 32
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | GRDA | KERR 115KV | 22.25 | 0.00708 | -0.0574 | 32
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | GRDA | KERR 161KV | 21.9191 | 0.00707 | -0.05739 | 32
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | EMDE | LARUSSEL 161KV | 100 | 0.00596 | -0.05628 | 32
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | WERE | LAWRENCE ENERGY CENTER 115KV | 159 | 0.00593 | -0.05625 | 32
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | WERE | LAWRENCE ENERGY CENTER 230KV | 350.7009 | 0.00598 | -0.0563 | 32
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | AEPW | NORTHEASTERN STATION 138KV | 854 | 0.00755 | -0.05787 | 32
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | AEPW | NORTHEASTERN STATION 345KV | 460 | 0.00762 | -0.05794 | 32
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | GRDA | PENSACOLA 161KV | 17 | 0.00696 | -0.05728 | 32
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | GRDA | PENSACOLA 69KV | 17 | 0.00693 | -0.05725 | 32
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | EMDE | RIVERTON 161KV | 72 | 0.00642 | -0.05674 | 32
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | EMDE | RIVERTON 69KV | 40.9406 | 0.00639 | -0.05671 | 32
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | GRDA | SALINA 161KV | 199.9855 | 0.00707 | -0.05739 | 32
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | EMDE | STATE LINE 161KV | 523.4572 | 0.00636 | -0.05668 | 32
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | WERE | TECUMSEH ENERGY CENTER 115KV | 204 | 0.00602 | -0.05634 | 32
AEPW | WILKES 345KV | 354 | -0.02869 | AEPW | FULTON 115KV | 152.87 | 0.02795 | -0.05664 | 32
AEPW | LEBROCK 345KV | 146.9838 | -0.01947 | AEPW | TURK 138KV | 618 | 0.03593 | -0.0554 | 33
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | OKGE | AES 161KV | 320 | 0.00451 | -0.05483 | 33
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | AEPW | ELLIS 69KV | 17 | 0.00475 | -0.05507 | 33
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | EMDE | OZARK BEACH 161KV | 18 | 0.00505 | -0.05537 | 33
AEPW | TENASKA GATEWAY 345KV | 937.03 | -0.01869 | AEPW | TURK 138KV | 618 | 0.03593 | -0.05462 | 33
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | AEPW | FITZHUGH 161KV | 171 | 0.0039 | -0.05422 | 34
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | AEPW | FULTON 115KV | 152.87 | 0.02795 | -0.05224 | 35
AEPW | KNOXLEE 138KV | 474 | -0.02403 | AEPW | FULTON 115KV | 152.87 | 0.02795 | -0.05198 | 35
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | AEPW | FULTON 115KV | 152.87 | 0.02795 | -0.05262 | 35
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | SWPA | SIKESTON 161KV | 235 | 0.00142 | -0.05174 | 35
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | SWPA | JONESBORO 161KV | 97.7328 | 0.00103 | -0.05135 | 36
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | AEPW | FULTON 115KV | 152.87 | 0.02795 | -0.04961 | 37
AEPW | WILKES 138KV | 487.1183 | -0.06747 | AEPW | LEBROCK 345KV | 550.0162 | -0.01947 | -0.048 | 38
AEPW | WILKES 345KV | 354 | -0.02869 | WFEC | HUGO 138KV | 440 | 0.01888 | -0.04757 | 38
AEPW | LEBROCK 345KV | 146.9838 | -0.01947 | AEPW | FULTON 115KV | 152.87 | 0.02795 | -0.04742 | 39
AEPW | TENASKA GATEWAY 345KV | 937.03 | -0.01869 | AEPW | FULTON 115KV | 152.87 | 0.02795 | -0.04664 | 39
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | LEPA | BAYOU RAMOS 138KV | 30.1531 | -0.00507 | -0.04525 | 40
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | LEPA | CITY OF HOUMA SUB 115KV | 70 | -0.00429 | -0.04603 | 40
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | LEPA | IRION SUB 69KV | 25 | -0.00455 | -0.04577 | 40
AEPW | WILKES 138KV | 487.1183 | -0.06747 | AEPW | ARSENAL HILL 138KV | 540 | -0.02174 | -0.04573 | 40
AEPW | WILKES 138KV | 487.1183 | -0.06747 | AEPW | PIRKEY GENERATION 138KV | 675 | -0.02224 | -0.04523 | 40
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | WFEC | HUGO 138KV | 440 | 0.01888 | -0.04317 | 42
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | WFEC | HUGO 138KV | 440 | 0.01888 | -0.04355 | 42
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | AEPW | WELSH 345KV | 1056 | -0.00713 | -0.04319 | 42
AEPW | WELSH 345KV | 528 | -0.00713 | AEPW | TURK 138KV | 618 | 0.03593 | -0.04306 | 42
AEPW | WILKES 138KV | 487.1183 | -0.06747 | AEPW | EASTMAN 138KV | 325.0638 | -0.02429 | -0.04318 | 42
AEPW | KNOXLEE 138KV | 474 | -0.02403 | WFEC | HUGO 138KV | 440 | 0.01888 | -0.04291 | 43
AEPW | WILKES 345KV | 354 | -0.02869 | OKGE | G12_004_2 0.6900 34KV | 40 | 0.01249 | -0.04118 | 44
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | WFEC | HUGO 138KV | 440 | 0.01888 | -0.04054 | 45
LEPA | BAYOU RAMOS 138KV | 37.8469 | -0.00507 | AEPW | TURK 138KV | 618 | 0.03593 | -0.041 | 45
LEPA | IRION SUB 69KV | 19 | -0.00455 | AEPW | TURK 138KV | 618 | 0.03593 | -0.04048 | 45
AEPW | WILKES 345KV | 354 | -0.02869 | AEPW | COMANCHE 138KV | 195 | 0.01089 | -0.03958 | 46
AEPW | WILKES 345KV | 354 | -0.02869 | AEPW | COMANCHE 69KV | 78 | 0.01085 | -0.03954 | 46
AEPW | WILKES 345KV | 354 | -0.02869 | OKGE | SEMINOLE 138KV | 250.8129 | 0.01067 | -0.03936 | 46
AEPW | WILKES 345KV | 354 | -0.02869 | WFEC | ANADARKO 138KV | 410.7952 | 0.0105 | -0.03919 | 47
AEPW | WILKES 345KV | 354 | -0.02869 | WFEC | BLUCAN2 0.6900 34KV | 227 | 0.01045 | -0.03914 | 47
AEPW | WILKES 345KV | 354 | -0.02869 | WFEC | COMMANCHE CO SUB 34KV | 100 | 0.01045 | -0.03914 | 47
AEPW | WILKES 345KV | 354 | -0.02869 | AEPW | G09-16 0.6900 34KV | 100 | 0.00986 | -0.03855 | 47
AEPW | WILKES 345KV | 354 | -0.02869 | WFEC | G12-028 0.6900 34KV | 323.62 | 0.00995 | -0.03864 | 47
AEPW | WILKES 345KV | 354 | -0.02869 | OKGE | GRADY CO SUB 345KV | 99 | 0.01001 | -0.0387 | 47
AEPW | WILKES 345KV | 354 | -0.02869 | OKGE | MCCLAIN 138KV | 465.6 | 0.00987 | -0.03856 | 47
AEPW | WILKES 345KV | 354 | -0.02869 | OKGE | SEMINOLE 345KV | 668.6758 | 0.01049 | -0.03918 | 47
AEPW | WILKES 345KV | 354 | -0.02869 | AEPW | SOUTHWESTERN STATION 138KV | 243.936 | 0.01049 | -0.03918 | 47
AEPW | WILKES 345KV | 354 | -0.02869 | AEPW | WTH WIND 34.500 34KV | 148 | 0.00992 | -0.03861 | 47
AEPW | LEBROCK 345KV | 146.9838 | -0.01947 | WFEC | HUGO 138KV | 440 | 0.01888 | -0.03835 | 48
AEPW | WILKES 345KV | 354 | -0.02869 | SPS | ANTELOPE 230KV | 78.9921 | 0.00924 | -0.03793 | 48
AEPW | WILKES 345KV | 354 | -0.02869 | SPS | ASGI-10-10 13.800 115KV | 42 | 0.00913 | -0.03782 | 48
AEPW | WILKES 345KV | 354 | -0.02869 | SPS | ASGI2011-0010.6900 34KV | 28.8 | 0.00913 | -0.03782 | 48
AEPW | WILKES 345KV | 354 | -0.02869 | AEPW | BUFFCK1 34.500 230KV | 99 | 0.00964 | -0.03833 | 48
AEPW | WILKES 345KV | 354 | -0.02869 | OKGE | CANADN12 34.500 345KV | 298.2 | 0.00965 | -0.03834 | 48
AEPW | WILKES 345KV | 354 | -0.02869 | SPS | CAPROCK 0KV | 80 | 0.00909 | -0.03778 | 48
AEPW | WILKES 345KV | 354 | -0.02869 | SPS | CUNNINGHAM 230KV | 187 | 0.00913 | -0.03782 | 48
AEPW | WILKES 345KV | 354 | -0.02869 | SPS | G12-038 18.000 345KV | 712 | 0.00917 | -0.03786 | 48
AEPW | WILKES 345KV | 354 | -0.02869 | SPS | HOBBS PLANT #2 (CT) 115KV | 289 | 0.00913 | -0.03782 | 48
AEPW | WILKES 345KV | 354 | -0.02869 | SPS | HOBBS PLANT #3 (ST) 230KV | 213 | 0.00913 | -0.03782 | 48
AEPW | WILKES 345KV | 354 | -0.02869 | OKGE | HORSESHOE LAKE 138KV | 608 | 0.00972 | -0.03841 | 48
AEPW | WILKES 345KV | 354 | -0.02869 | OKGE | HORSESHOE LAKE 69KV | 16 | 0.00977 | -0.03846 | 48
AEPW | WILKES 345KV | 354 | -0.02869 | SPS | JONES_4 116.500 230KV | 472 | 0.0092 | -0.03789 | 48
AEPW | WILKES 345KV | 354 | -0.02869 | SPS | LP-BRND2 69KV | 21 | 0.00921 | -0.0379 | 48
AEPW | WILKES 345KV | 354 | -0.02869 | SPS | LP-HOLL2 69KV | 132 | 0.0092 | -0.03789 | 48
AEPW | WILKES 345KV | 354 | -0.02869 | SPS | LP-MACK2 69KV | 80 | 0.00921 | -0.0379 | 48
AEPW | WILKES 345KV | 354 | -0.02869 | SPS | MADOX 115KV | 119 | 0.00913 | -0.03782 | 48
AEPW | WILKES 345KV | 354 | -0.02869 | SPS | MUSTANG 115KV | 350 | 0.00914 | -0.03783 | 48
AEPW | WILKES 345KV | 354 | -0.02869 | OKGE | MUSTANG 138KV | 236 | 0.0097 | -0.03839 | 48
AEPW | WILKES 345KV | 354 | -0.02869 | SPS | MUSTANG_6 18.000 230KV | 394 | 0.00914 | -0.03783 | 48
AEPW | WILKES 345KV | 354 | -0.02869 | SPS | PLANTX 115KV | 67.8511 | 0.00909 | -0.03778 | 48
AEPW | WILKES 345KV | 354 | -0.02869 | SPS | PLANTX 230KV | 183 | 0.00909 | -0.03778 | 48
AEPW | WILKES 345KV | 354 | -0.02869 | SPS | QUAY_CNTY 113.800 115KV | 23 | 0.00909 | -0.03778 | 48
AEPW | WILKES 345KV | 354 | -0.02869 | OKGE | REDBUD 345KV | 1203.5 | 0.00943 | -0.03812 | 48
AEPW | WILKES 345KV | 354 | -0.02869 | WFEC | RHWIND1WG11 0.6900 34KV | 123 | 0.00976 | -0.03845 | 48
AEPW | WILKES 345KV | 354 | -0.02869 | SPS | SAN JUAN 230KV | 120 | 0.00911 | -0.0378 | 48
AEPW | WILKES 345KV | 354 | -0.02869 | OKGE | SMITH COGEN 138KV | 107 | 0.00973 | -0.03842 | 48
AEPW | WILKES 345KV | 354 | -0.02869 | OKGE | SPRING CREEK UNIT 3 AND 4 345KV | 300 | 0.00928 | -0.03797 | 48
AEPW | WILKES 345KV | 354 | -0.02869 | SPS | TOLK 230KV | 1014.523 | 0.0091 | -0.03779 | 48
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | OKGE | G12_004_2 0.6900 34KV | 40 | 0.01249 | -0.03716 | 49
AEPW | TENASKA GATEWAY 345KV | 937.03 | -0.01869 | WFEC | HUGO 138KV | 440 | 0.01888 | -0.03757 | 49
AEPW | WILKES 345KV | 354 | -0.02869 | SPS | BLACKHAWK 115KV | 224 | 0.00879 | -0.03748 | 49
AEPW | WILKES 345KV | 354 | -0.02869 | GRDA | BOOMER 69KV | 24 | 0.00854 | -0.03723 | 49
AEPW | WILKES 345KV | 354 | -0.02869 | OKGE | CENT 21 34.500 138KV | 120 | 0.00847 | -0.03716 | 49
AEPW | WILKES 345KV | 354 | -0.02869 | OKGE | CHSHMVW1 34.500 345KV | 202 | 0.00841 | -0.0371 | 49
AEPW | WILKES 345KV | 354 | -0.02869 | SPS | CLR_3 0.6900 34KV | 160 | 0.00887 | -0.03756 | 49
AEPW | WILKES 345KV | 354 | -0.02869 | OKGE | CRSRDW21 34.500 345KV | 177 | 0.00877 | -0.03746 | 49
AEPW | WILKES 345KV | 354 | -0.02869 | OKGE | DEWEY CO SUB 4 138KV | 130 | 0.00881 | -0.0375 | 49
AEPW | WILKES 345KV | 354 | -0.02869 | OKGE | FPLWND11 34.500 138KV | 102 | 0.00868 | -0.03737 | 49
AEPW | WILKES 345KV | 354 | -0.02869 | SPS | G08-47 0.5750 34KV | 200 | 0.00829 | -0.03698 | 49
AEPW | WILKES 345KV | 354 | -0.02869 | SPS | GS-PHWDRNCH134.500 230KV | 79 | 0.00887 | -0.03756 | 49
AEPW | WILKES 345KV | 354 | -0.02869 | SPS | HARRINGTON 230KV | 1031 | 0.00886 | -0.03755 | 49
AEPW | WILKES 345KV | 354 | -0.02869 | SPS | MAJESTIC WIND 115KV | 160 | 0.00884 | -0.03753 | 49
AEPW | WILKES 345KV | 354 | -0.02869 | WFEC | MORLND 138KV | 272 | 0.00869 | -0.03738 | 49
AEPW | WILKES 345KV | 354 | -0.02869 | OKGE | MUSKOGEE 345KV | 1542.5 | 0.00822 | -0.03691 | 49
AEPW | WILKES 345KV | 354 | -0.02869 | SPS | NICHOLS 115KV | 82 | 0.00888 | -0.03757 | 49
AEPW | WILKES 345KV | 354 | -0.02869 | OMPA | OMPA-KAW 69KV | 28.8 | 0.00824 | -0.03693 | 49
AEPW | WILKES 345KV | 354 | -0.02869 | OMPA | OMPA-PONCA CITY 69KV | 75.8066 | 0.00824 | -0.03693 | 49
AEPW | WILKES 345KV | 354 | -0.02869 | OKGE | OU SPIRIT 138KV | 120 | 0.00844 | -0.03713 | 49
AEPW | WILKES 345KV | 354 | -0.02869 | WFEC | SLEEPING BEAR 138KV | 80 | 0.00866 | -0.03735 | 49
AEPW | WILKES 345KV | 354 | -0.02869 | OKGE | SOONER 138KV | 535 | 0.00837 | -0.03706 | 49
AEPW | WILKES 345KV | 354 | -0.02869 | OKGE | SOONER 345KV | 537 | 0.00837 | -0.03706 | 49
AEPW | WILKES 345KV | 354 | -0.02869 | SPS | SPNSPUR_WND134.500 345KV | 161 | 0.00865 | -0.03734 | 49
AEPW | WILKES 345KV | 354 | -0.02869 | SPS | STEER WATER 115KV | 80 | 0.00896 | -0.03765 | 49
AEPW | WILKES 345KV | 354 | -0.02869 | OKGE | WOODWARD CO SUB 2 138KV | 152 | 0.00844 | -0.03713 | 49
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | OKGE | G12_004_2 0.6900 34KV | 40 | 0.01249 | -0.03678 | 50
AEPW | KNOXLEE 138KV | 474 | -0.02403 | OKGE | G12_004_2 0.6900 34KV | 40 | 0.01249 | -0.03652 | 50
AEPW | WILKES 345KV | 354 | -0.02869 | WERE | BARBER CO SUB 34KV | 200 | 0.00771 | -0.0364 | 50
AEPW | WILKES 345KV | 354 | -0.02869 | AEPW | COGENTRIX 345KV | 1038 | 0.00812 | -0.03681 | 50
AEPW | WILKES 345KV | 354 | -0.02869 | WERE | HARPER CO SUB 34KV | 714 | 0.00771 | -0.0364 | 50
AEPW | WILKES 345KV | 354 | -0.02869 | AEPW | NORTHEASTERN STATION 138KV | 854 | 0.00755 | -0.03624 | 50
AEPW | WILKES 345KV | 354 | -0.02869 | AEPW | NORTHEASTERN STATION 345KV | 460 | 0.00762 | -0.03631 | 50
AEPW | WILKES 345KV | 354 | -0.02869 | AEPW | OEC 345KV | 1460 | 0.00794 | -0.03663 | 50
AEPW | WILKES 345KV | 354 | -0.02869 | AEPW | RIVERSIDE STATION 138KV | 917 | 0.00814 | -0.03683 | 50
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | AEPW | COMANCHE 138KV | 195 | 0.01089 | -0.03556 | 51
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | AEPW | COMANCHE 69KV | 78 | 0.01085 | -0.03552 | 51
AEPW | WILKES 345KV | 354 | -0.02869 | WERE | CITY OF AUGUSTA 69KV | 20 | 0.00729 | -0.03598 | 51
AEPW | WILKES 345KV | 354 | -0.02869 | WERE | CLR_3 0.6900 34KV | 75 | 0.00712 | -0.03581 | 51
AEPW | WILKES 345KV | 354 | -0.02869 | WERE | CLR_4 0.6900 34KV | 75 | 0.00712 | -0.03581 | 51
AEPW | WILKES 345KV | 354 | -0.02869 | WERE | ELK CO SUB 34KV | 401 | 0.00708 | -0.03577 | 51
AEPW | WILKES 345KV | 354 | -0.02869 | WERE | EVANS ENERGY CENTER 138KV | 671 | 0.00727 | -0.03596 | 51
AEPW | WILKES 345KV | 354 | -0.02869 | WERE | GILL ENERGY CENTER 138KV | 194 | 0.00731 | -0.036 | 51
AEPW | WILKES 345KV | 354 | -0.02869 | GRDA | GRDA1 161KV | 480 | 0.0071 | -0.03579 | 51
AEPW | WILKES 345KV | 354 | -0.02869 | GRDA | GRDA1 345KV | 494 | 0.00705 | -0.03574 | 51
AEPW | WILKES 345KV | 354 | -0.02869 | WERE | HUTCHINSON ENERGY CENTER 115KV | 166 | 0.00691 | -0.0356 | 51
AEPW | WILKES 345KV | 354 | -0.02869 | GRDA | KERR 115KV | 22.25 | 0.00708 | -0.03577 | 51
AEPW | WILKES 345KV | 354 | -0.02869 | GRDA | KERR 161KV | 21.9191 | 0.00707 | -0.03576 | 51
AEPW | WILKES 345KV | 354 | -0.02869 | GRDA | PENSACOLA 161KV | 17 | 0.00696 | -0.03565 | 51
AEPW | WILKES 345KV | 354 | -0.02869 | GRDA | PENSACOLA 69KV | 17 | 0.00693 | -0.03562 | 51
AEPW | WILKES 345KV | 354 | -0.02869 | GRDA | SALINA 161KV | 199.9855 | 0.00707 | -0.03576 | 51
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | AEPW | COMANCHE 138KV | 195 | 0.01089 | -0.03518 | 52
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | AEPW | COMANCHE 69KV | 78 | 0.01085 | -0.03514 | 52
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | OKGE | SEMINOLE 138KV | 250.8129 | 0.01067 | -0.03496 | 52
SWPA | JBOGENE1 13.800 69KV | 138.68 | 0.00101 | AEPW | TURK 138KV | 618 | 0.03593 | -0.03492 | 52
SWPA | JONESBORO 161KV | 149.3872 | 0.00103 | AEPW | TURK 138KV | 618 | 0.03593 | -0.0349 | 52
AEPW | KNOXLEE 138KV | 474 | -0.02403 | AEPW | COMANCHE 138KV | 195 | 0.01089 | -0.03492 | 52
AEPW | KNOXLEE 138KV | 474 | -0.02403 | AEPW | COMANCHE 69KV | 78 | 0.01085 | -0.03488 | 52
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | WFEC | ANADARKO 138KV | 410.7952 | 0.0105 | -0.03517 | 52
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | WFEC | BLUCAN2 0.6900 34KV | 227 | 0.01045 | -0.03512 | 52
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | WFEC | COMMANCHE CO SUB 34KV | 100 | 0.01045 | -0.03512 | 52
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | OKGE | SEMINOLE 138KV | 250.8129 | 0.01067 | -0.03534 | 52
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | OKGE | SEMINOLE 345KV | 668.6758 | 0.01049 | -0.03516 | 52
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | AEPW | SOUTHWESTERN STATION 138KV | 243.936 | 0.01049 | -0.03516 | 52
AEPW | WELSH 345KV | 528 | -0.00713 | AEPW | FULTON 115KV | 152.87 | 0.02795 | -0.03508 | 52
AEPW | WILKES 345KV | 354 | -0.02869 | WERE | ANDERSONCO 345.00 345KV | 85 | 0.00659 | -0.03528 | 52
AEPW | WILKES 345KV | 354 | -0.02869 | EMDE | ASBURY 161KV | 192 | 0.00636 | -0.03505 | 52
AEPW | WILKES 345KV | 354 | -0.02869 | SWPA | CARTHAGE 69KV | 32 | 0.00612 | -0.03481 | 52
AEPW | WILKES 345KV | 354 | -0.02869 | WERE | CLAYCSS3 115.00 115KV | 22.3 | 0.00642 | -0.03511 | 52
AEPW | WILKES 345KV | 354 | -0.02869 | WERE | EMPORIA ENERGY CENTER 345KV | 413.6875 | 0.00638 | -0.03507 | 52
AEPW | WILKES 345KV | 354 | -0.02869 | AEPW | FLINT CREEK 161KV | 528 | 0.00673 | -0.03542 | 52
AEPW | WILKES 345KV | 354 | -0.02869 | WERE | JEFFREY ENERGY CENTER 230KV | 730 | 0.00618 | -0.03487 | 52
AEPW | WILKES 345KV | 354 | -0.02869 | WERE | JEFFREY ENERGY CENTER 345KV | 1460 | 0.00617 | -0.03486 | 52
AEPW | WILKES 345KV | 354 | -0.02869 | EMDE | RIVERTON 161KV | 72 | 0.00642 | -0.03511 | 52
AEPW | WILKES 345KV | 354 | -0.02869 | EMDE | RIVERTON 69KV | 40.9406 | 0.00639 | -0.03508 | 52
AEPW | WILKES 345KV | 354 | -0.02869 | EMDE | STATE LINE 161KV | 523.4572 | 0.00636 | -0.03505 | 52
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | OKGE | G12_004_2 0.6900 34KV | 40 | 0.01249 | -0.03415 | 53
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | WFEC | ANADARKO 138KV | 410.7952 | 0.0105 | -0.03479 | 53
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | WFEC | BLUCAN2 0.6900 34KV | 227 | 0.01045 | -0.03474 | 53
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | WFEC | COMMANCHE CO SUB 34KV | 100 | 0.01045 | -0.03474 | 53
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | AEPW | G09-16 0.6900 34KV | 100 | 0.00986 | -0.03415 | 53
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | WFEC | G12-028 0.6900 34KV | 323.62 | 0.00995 | -0.03424 | 53
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | OKGE | GRADY CO SUB 345KV | 99 | 0.01001 | -0.0343 | 53
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | OKGE | MCCLAIN 138KV | 465.6 | 0.00987 | -0.03416 | 53
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | OKGE | SEMINOLE 345KV | 668.6758 | 0.01049 | -0.03478 | 53
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | AEPW | SOUTHWESTERN STATION 138KV | 243.936 | 0.01049 | -0.03478 | 53
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | AEPW | WTH WIND 34.500 34KV | 148 | 0.00992 | -0.03421 | 53
SWPA | KENNETT 69KV | 29 | 0.0012 | AEPW | TURK 138KV | 618 | 0.03593 | -0.03473 | 53
AEPW | KNOXLEE 138KV | 474 | -0.02403 | WFEC | ANADARKO 138KV | 410.7952 | 0.0105 | -0.03453 | 53
AEPW | KNOXLEE 138KV | 474 | -0.02403 | WFEC | BLUCAN2 0.6900 34KV | 227 | 0.01045 | -0.03448 | 53
AEPW | KNOXLEE 138KV | 474 | -0.02403 | WFEC | COMMANCHE CO SUB 34KV | 100 | 0.01045 | -0.03448 | 53
AEPW | KNOXLEE 138KV | 474 | -0.02403 | OKGE | SEMINOLE 138KV | 250.8129 | 0.01067 | -0.0347 | 53
AEPW | KNOXLEE 138KV | 474 | -0.02403 | OKGE | SEMINOLE 345KV | 668.6758 | 0.01049 | -0.03452 | 53
AEPW | KNOXLEE 138KV | 474 | -0.02403 | AEPW | SOUTHWESTERN STATION 138KV | 243.936 | 0.01049 | -0.03452 | 53
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | AEPW | BUFFCK1 34.500 230KV | 99 | 0.00964 | -0.03431 | 53
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | OKGE | CANADN12 34.500 345KV | 298.2 | 0.00965 | -0.03432 | 53
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | AEPW | G09-16 0.6900 34KV | 100 | 0.00986 | -0.03453 | 53
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | WFEC | G12-028 0.6900 34KV | 323.62 | 0.00995 | -0.03462 | 53
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | OKGE | GRADY CO SUB 345KV | 99 | 0.01001 | -0.03468 | 53
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | OKGE | HORSESHOE LAKE 138KV | 608 | 0.00972 | -0.03439 | 53
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | OKGE | MCCLAIN 138KV | 465.6 | 0.00987 | -0.03454 | 53
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | OKGE | MUSTANG 138KV | 236 | 0.0097 | -0.03437 | 53
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | WFEC | RHWIND1WG11 0.6900 34KV | 123 | 0.00976 | -0.03443 | 53
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | OKGE | SMITH COGEN 138KV | 107 | 0.00973 | -0.0344 | 53
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | AEPW | WTH WIND 34.500 34KV | 148 | 0.00992 | -0.03459 | 53
SWPA | POPLAR BLUFF 69KV | 32 | 0.00168 | AEPW | TURK 138KV | 618 | 0.03593 | -0.03425 | 53
AEPW | WILKES 345KV | 354 | -0.02869 | EMDE | LARUSSEL 161KV | 100 | 0.00596 | -0.03465 | 53
AEPW | WILKES 345KV | 354 | -0.02869 | WERE | LAWRENCE ENERGY CENTER 115KV | 159 | 0.00593 | -0.03462 | 53
AEPW | WILKES 345KV | 354 | -0.02869 | WERE | LAWRENCE ENERGY CENTER 230KV | 350.7009 | 0.00598 | -0.03467 | 53
AEPW | WILKES 345KV | 354 | -0.02869 | WERE | TECUMSEH ENERGY CENTER 115KV | 204 | 0.00602 | -0.03471 | 53
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | SPS | ANTELOPE 230KV | 78.9921 | 0.00924 | -0.03353 | 54
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | AEPW | BUFFCK1 34.500 230KV | 99 | 0.00964 | -0.03393 | 54
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | OKGE | CANADN12 34.500 345KV | 298.2 | 0.00965 | -0.03394 | 54
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | OKGE | HORSESHOE LAKE 138KV | 608 | 0.00972 | -0.03401 | 54
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | OKGE | MUSTANG 138KV | 236 | 0.0097 | -0.03399 | 54
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | OKGE | REDBUD 345KV | 1203.5 | 0.00943 | -0.03372 | 54
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | WFEC | RHWIND1WG11 0.6900 34KV | 123 | 0.00976 | -0.03405 | 54
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | OKGE | SMITH COGEN 138KV | 107 | 0.00973 | -0.03402 | 54
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | OKGE | SPRING CREEK UNIT 3 AND 4 345KV | 300 | 0.00928 | -0.03357 | 54
AEPW | KNOXLEE 138KV | 474 | -0.02403 | AEPW | BUFFCK1 34.500 230KV | 99 | 0.00964 | -0.03367 | 54
AEPW | KNOXLEE 138KV | 474 | -0.02403 | OKGE | CANADN12 34.500 345KV | 298.2 | 0.00965 | -0.03368 | 54
AEPW | KNOXLEE 138KV | 474 | -0.02403 | AEPW | G09-16 0.6900 34KV | 100 | 0.00986 | -0.03389 | 54
AEPW | KNOXLEE 138KV | 474 | -0.02403 | WFEC | G12-028 0.6900 34KV | 323.62 | 0.00995 | -0.03398 | 54
AEPW | KNOXLEE 138KV | 474 | -0.02403 | OKGE | GRADY CO SUB 345KV | 99 | 0.01001 | -0.03404 | 54
AEPW | KNOXLEE 138KV | 474 | -0.02403 | OKGE | HORSESHOE LAKE 138KV | 608 | 0.00972 | -0.03375 | 54
AEPW | KNOXLEE 138KV | 474 | -0.02403 | OKGE | MCCLAIN 138KV | 465.6 | 0.00987 | -0.0339 | 54
AEPW | KNOXLEE 138KV | 474 | -0.02403 | OKGE | MUSTANG 138KV | 236 | 0.0097 | -0.03373 | 54
AEPW | KNOXLEE 138KV | 474 | -0.02403 | WFEC | RHWIND1WG11 0.6900 34KV | 123 | 0.00976 | -0.03379 | 54
AEPW | KNOXLEE 138KV | 474 | -0.02403 | OKGE | SMITH COGEN 138KV | 107 | 0.00973 | -0.03376 | 54
AEPW | KNOXLEE 138KV | 474 | -0.02403 | AEPW | WTH WIND 34.500 34KV | 148 | 0.00992 | -0.03395 | 54
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | SPS | ANTELOPE 230KV | 78.9921 | 0.00924 | -0.03391 | 54
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | SPS | ASGI-10-10 13.800 115KV | 42 | 0.00913 | -0.0338 | 54
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | SPS | ASGI2011-0010.6900 34KV | 28.8 | 0.00913 | -0.0338 | 54
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | SPS | CAPROCK 0KV | 80 | 0.00909 | -0.03376 | 54
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | SPS | CLR_3 0.6900 34KV | 160 | 0.00887 | -0.03354 | 54
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | SPS | CUNNINGHAM 230KV | 187 | 0.00913 | -0.0338 | 54
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | SPS | G12-038 18.000 345KV | 712 | 0.00917 | -0.03384 | 54
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | SPS | GS-PHWDRNCH134.500 230KV | 79 | 0.00887 | -0.03354 | 54
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | SPS | HARRINGTON 230KV | 1031 | 0.00886 | -0.03353 | 54
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | SPS | HOBBS PLANT #2 (CT) 115KV | 289 | 0.00913 | -0.0338 | 54
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | SPS | HOBBS PLANT #3 (ST) 230KV | 213 | 0.00913 | -0.0338 | 54
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | SPS | JONES_4 116.500 230KV | 472 | 0.0092 | -0.03387 | 54
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | SPS | LP-BRND2 69KV | 21 | 0.00921 | -0.03388 | 54
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | SPS | LP-HOLL2 69KV | 132 | 0.0092 | -0.03387 | 54
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | SPS | LP-MACK2 69KV | 80 | 0.00921 | -0.03388 | 54
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | SPS | MADOX 115KV | 119 | 0.00913 | -0.0338 | 54
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | SPS | MUSTANG 115KV | 350 | 0.00914 | -0.03381 | 54
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | SPS | MUSTANG_6 18.000 230KV | 394 | 0.00914 | -0.03381 | 54
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | SPS | NICHOLS 115KV | 82 | 0.00888 | -0.03355 | 54
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | SPS | PLANTX 115KV | 67.8511 | 0.00909 | -0.03376 | 54
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | SPS | PLANTX 230KV | 183 | 0.00909 | -0.03376 | 54
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | SPS | QUAY_CNTY 113.800 115KV | 23 | 0.00909 | -0.03376 | 54
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | OKGE | REDBUD 345KV | 1203.5 | 0.00943 | -0.0341 | 54
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | SPS | SAN JUAN 230KV | 120 | 0.00911 | -0.03378 | 54
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | OKGE | SPRING CREEK UNIT 3 AND 4 345KV | 300 | 0.00928 | -0.03395 | 54
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | SPS | STEER WATER 115KV | 80 | 0.00896 | -0.03363 | 54
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | SPS | TOLK 230KV | 1014.523 | 0.0091 | -0.03377 | 54
AEPW | WILKES 345KV | 354 | -0.02869 | EMDE | OZARK BEACH 161KV | 18 | 0.00505 | -0.03374 | 54
LEPA | BAYOU RAMOS 138KV | 37.8469 | -0.00507 | AEPW | FULTON 115KV | 152.87 | 0.02795 | -0.03302 | 55
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | SPS | ASGI-10-10 13.800 115KV | 42 | 0.00913 | -0.03342 | 55
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | SPS | ASGI2011-0010.6900 34KV | 28.8 | 0.00913 | -0.03342 | 55
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | SPS | BLACKHAWK 115KV | 224 | 0.00879 | -0.03308 | 55
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | SPS | CAPROCK 0KV | 80 | 0.00909 | -0.03338 | 55
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | SPS | CLR_3 0.6900 34KV | 160 | 0.00887 | -0.03316 | 55
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | OKGE | CRSRDW21 34.500 345KV | 177 | 0.00877 | -0.03306 | 55
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | SPS | CUNNINGHAM 230KV | 187 | 0.00913 | -0.03342 | 55
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | OKGE | DEWEY CO SUB 4 138KV | 130 | 0.00881 | -0.0331 | 55
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | OKGE | FPLWND11 34.500 138KV | 102 | 0.00868 | -0.03297 | 55
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | SPS | G12-038 18.000 345KV | 712 | 0.00917 | -0.03346 | 55
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | SPS | GS-PHWDRNCH134.500 230KV | 79 | 0.00887 | -0.03316 | 55
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | SPS | HARRINGTON 230KV | 1031 | 0.00886 | -0.03315 | 55
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | SPS | HOBBS PLANT #2 (CT) 115KV | 289 | 0.00913 | -0.03342 | 55
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | SPS | HOBBS PLANT #3 (ST) 230KV | 213 | 0.00913 | -0.03342 | 55
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | SPS | JONES_4 116.500 230KV | 472 | 0.0092 | -0.03349 | 55
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | SPS | LP-BRND2 69KV | 21 | 0.00921 | -0.0335 | 55
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | SPS | LP-HOLL2 69KV | 132 | 0.0092 | -0.03349 | 55
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | SPS | LP-MACK2 69KV | 80 | 0.00921 | -0.0335 | 55
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | SPS | MADOX 115KV | 119 | 0.00913 | -0.03342 | 55
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | SPS | MAJESTIC WIND 115KV | 160 | 0.00884 | -0.03313 | 55
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | WFEC | MORLND 138KV | 272 | 0.00869 | -0.03298 | 55
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | SPS | MUSTANG 115KV | 350 | 0.00914 | -0.03343 | 55
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | SPS | MUSTANG_6 18.000 230KV | 394 | 0.00914 | -0.03343 | 55
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | SPS | NICHOLS 115KV | 82 | 0.00888 | -0.03317 | 55
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | SPS | PLANTX 115KV | 67.8511 | 0.00909 | -0.03338 | 55
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | SPS | PLANTX 230KV | 183 | 0.00909 | -0.03338 | 55
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | SPS | QUAY_CNTY 113.800 115KV | 23 | 0.00909 | -0.03338 | 55
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | SPS | SAN JUAN 230KV | 120 | 0.00911 | -0.0334 | 55
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | WFEC | SLEEPING BEAR 138KV | 80 | 0.00866 | -0.03295 | 55
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | SPS | SPNSPUR_WND134.500 345KV | 161 | 0.00865 | -0.03294 | 55
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | SPS | STEER WATER 115KV | 80 | 0.00896 | -0.03325 | 55
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | SPS | TOLK 230KV | 1014.523 | 0.0091 | -0.03339 | 55
AEPW | KNOXLEE 138KV | 474 | -0.02403 | SPS | ANTELOPE 230KV | 78.9921 | 0.00924 | -0.03327 | 55
AEPW | KNOXLEE 138KV | 474 | -0.02403 | SPS | ASGI-10-10 13.800 115KV | 42 | 0.00913 | -0.03316 | 55
AEPW | KNOXLEE 138KV | 474 | -0.02403 | SPS | ASGI2011-0010.6900 34KV | 28.8 | 0.00913 | -0.03316 | 55
AEPW | KNOXLEE 138KV | 474 | -0.02403 | SPS | CAPROCK 0KV | 80 | 0.00909 | -0.03312 | 55
AEPW | KNOXLEE 138KV | 474 | -0.02403 | SPS | CUNNINGHAM 230KV | 187 | 0.00913 | -0.03316 | 55
AEPW | KNOXLEE 138KV | 474 | -0.02403 | SPS | G12-038 18.000 345KV | 712 | 0.00917 | -0.0332 | 55
AEPW | KNOXLEE 138KV | 474 | -0.02403 | SPS | HOBBS PLANT #2 (CT) 115KV | 289 | 0.00913 | -0.03316 | 55
AEPW | KNOXLEE 138KV | 474 | -0.02403 | SPS | HOBBS PLANT #3 (ST) 230KV | 213 | 0.00913 | -0.03316 | 55
AEPW | KNOXLEE 138KV | 474 | -0.02403 | SPS | JONES_4 116.500 230KV | 472 | 0.0092 | -0.03323 | 55
AEPW | KNOXLEE 138KV | 474 | -0.02403 | SPS | LP-BRND2 69KV | 21 | 0.00921 | -0.03324 | 55
AEPW | KNOXLEE 138KV | 474 | -0.02403 | SPS | LP-HOLL2 69KV | 132 | 0.0092 | -0.03323 | 55
AEPW | KNOXLEE 138KV | 474 | -0.02403 | SPS | LP-MACK2 69KV | 80 | 0.00921 | -0.03324 | 55
AEPW | KNOXLEE 138KV | 474 | -0.02403 | SPS | MADOX 115KV | 119 | 0.00913 | -0.03316 | 55
AEPW | KNOXLEE 138KV | 474 | -0.02403 | SPS | MUSTANG 115KV | 350 | 0.00914 | -0.03317 | 55
AEPW | KNOXLEE 138KV | 474 | -0.02403 | SPS | MUSTANG_6 18.000 230KV | 394 | 0.00914 | -0.03317 | 55
AEPW | KNOXLEE 138KV | 474 | -0.02403 | SPS | PLANTX 115KV | 67.8511 | 0.00909 | -0.03312 | 55
AEPW | KNOXLEE 138KV | 474 | -0.02403 | SPS | PLANTX 230KV | 183 | 0.00909 | -0.03312 | 55
AEPW | KNOXLEE 138KV | 474 | -0.02403 | SPS | QUAY_CNTY 113.800 115KV | 23 | 0.00909 | -0.03312 | 55
AEPW | KNOXLEE 138KV | 474 | -0.02403 | OKGE | REDBUD 345KV | 1203.5 | 0.00943 | -0.03346 | 55
AEPW | KNOXLEE 138KV | 474 | -0.02403 | SPS | SAN JUAN 230KV | 120 | 0.00911 | -0.03314 | 55
AEPW | KNOXLEE 138KV | 474 | -0.02403 | OKGE | SPRING CREEK UNIT 3 AND 4 345KV | 300 | 0.00928 | -0.03331 | 55
AEPW | KNOXLEE 138KV | 474 | -0.02403 | SPS | STEER WATER 115KV | 80 | 0.00896 | -0.03299 | 55
AEPW | KNOXLEE 138KV | 474 | -0.02403 | SPS | TOLK 230KV | 1014.523 | 0.0091 | -0.03313 | 55
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | SPS | BLACKHAWK 115KV | 224 | 0.00879 | -0.03346 | 55
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | GRDA | BOOMER 69KV | 24 | 0.00854 | -0.03321 | 55
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | OKGE | CENT 21 34.500 138KV | 120 | 0.00847 | -0.03314 | 55
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | OKGE | CHSHMVW1 34.500 345KV | 202 | 0.00841 | -0.03308 | 55
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | OKGE | CRSRDW21 34.500 345KV | 177 | 0.00877 | -0.03344 | 55
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | OKGE | DEWEY CO SUB 4 138KV | 130 | 0.00881 | -0.03348 | 55
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | OKGE | FPLWND11 34.500 138KV | 102 | 0.00868 | -0.03335 | 55
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | SPS | G08-47 0.5750 34KV | 200 | 0.00829 | -0.03296 | 55
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | SPS | MAJESTIC WIND 115KV | 160 | 0.00884 | -0.03351 | 55
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | WFEC | MORLND 138KV | 272 | 0.00869 | -0.03336 | 55
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | OKGE | OU SPIRIT 138KV | 120 | 0.00844 | -0.03311 | 55
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | WFEC | SLEEPING BEAR 138KV | 80 | 0.00866 | -0.03333 | 55
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | OKGE | SOONER 138KV | 535 | 0.00837 | -0.03304 | 55
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | OKGE | SOONER 345KV | 537 | 0.00837 | -0.03304 | 55
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | SPS | SPNSPUR_WND134.500 345KV | 161 | 0.00865 | -0.03332 | 55
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | OKGE | WOODWARD CO SUB 2 138KV | 152 | 0.00844 | -0.03311 | 55
AEPW | WILKES 345KV | 354 | -0.02869 | OKGE | AES 161KV | 320 | 0.00451 | -0.0332 | 55
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | AEPW | COMANCHE 138KV | 195 | 0.01089 | -0.03255 | 56
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | AEPW | COMANCHE 69KV | 78 | 0.01085 | -0.03251 | 56
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | GRDA | BOOMER 69KV | 24 | 0.00854 | -0.03283 | 56
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | OKGE | CENT 21 34.500 138KV | 120 | 0.00847 | -0.03276 | 56
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | OKGE | CHSHMVW1 34.500 345KV | 202 | 0.00841 | -0.0327 | 56
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | AEPW | COGENTRIX 345KV | 1038 | 0.00812 | -0.03241 | 56
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | SPS | G08-47 0.5750 34KV | 200 | 0.00829 | -0.03258 | 56
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | OKGE | MUSKOGEE 345KV | 1542.5 | 0.00822 | -0.03251 | 56
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | OMPA | OMPA-KAW 69KV | 28.8 | 0.00824 | -0.03253 | 56
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | OMPA | OMPA-PONCA CITY 69KV | 75.8066 | 0.00824 | -0.03253 | 56
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | OKGE | OU SPIRIT 138KV | 120 | 0.00844 | -0.03273 | 56
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | AEPW | RIVERSIDE STATION 138KV | 917 | 0.00814 | -0.03243 | 56
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | OKGE | SOONER 138KV | 535 | 0.00837 | -0.03266 | 56
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | OKGE | SOONER 345KV | 537 | 0.00837 | -0.03266 | 56
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | OKGE | WOODWARD CO SUB 2 138KV | 152 | 0.00844 | -0.03273 | 56
LEPA | IRION SUB 69KV | 19 | -0.00455 | AEPW | FULTON 115KV | 152.87 | 0.02795 | -0.0325 | 56
AEPW | KNOXLEE 138KV | 474 | -0.02403 | SPS | BLACKHAWK 115KV | 224 | 0.00879 | -0.03282 | 56
AEPW | KNOXLEE 138KV | 474 | -0.02403 | GRDA | BOOMER 69KV | 24 | 0.00854 | -0.03257 | 56
AEPW | KNOXLEE 138KV | 474 | -0.02403 | OKGE | CENT 21 34.500 138KV | 120 | 0.00847 | -0.0325 | 56
AEPW | KNOXLEE 138KV | 474 | -0.02403 | OKGE | CHSHMVW1 34.500 345KV | 202 | 0.00841 | -0.03244 | 56
AEPW | KNOXLEE 138KV | 474 | -0.02403 | SPS | CLR_3 0.6900 34KV | 160 | 0.00887 | -0.0329 | 56
AEPW | KNOXLEE 138KV | 474 | -0.02403 | OKGE | CRSRDW21 34.500 345KV | 177 | 0.00877 | -0.0328 | 56
AEPW | KNOXLEE 138KV | 474 | -0.02403 | OKGE | DEWEY CO SUB 4 138KV | 130 | 0.00881 | -0.03284 | 56
AEPW | KNOXLEE 138KV | 474 | -0.02403 | OKGE | FPLWND11 34.500 138KV | 102 | 0.00868 | -0.03271 | 56
AEPW | KNOXLEE 138KV | 474 | -0.02403 | SPS | GS-PHWDRNCH134.500 230KV | 79 | 0.00887 | -0.0329 | 56
AEPW | KNOXLEE 138KV | 474 | -0.02403 | SPS | HARRINGTON 230KV | 1031 | 0.00886 | -0.03289 | 56
AEPW | KNOXLEE 138KV | 474 | -0.02403 | SPS | MAJESTIC WIND 115KV | 160 | 0.00884 | -0.03287 | 56
AEPW | KNOXLEE 138KV | 474 | -0.02403 | WFEC | MORLND 138KV | 272 | 0.00869 | -0.03272 | 56
AEPW | KNOXLEE 138KV | 474 | -0.02403 | SPS | NICHOLS 115KV | 82 | 0.00888 | -0.03291 | 56
AEPW | KNOXLEE 138KV | 474 | -0.02403 | OKGE | OU SPIRIT 138KV | 120 | 0.00844 | -0.03247 | 56
AEPW | KNOXLEE 138KV | 474 | -0.02403 | WFEC | SLEEPING BEAR 138KV | 80 | 0.00866 | -0.03269 | 56
AEPW | KNOXLEE 138KV | 474 | -0.02403 | OKGE | SOONER 138KV | 535 | 0.00837 | -0.0324 | 56
AEPW | KNOXLEE 138KV | 474 | -0.02403 | OKGE | SOONER 345KV | 537 | 0.00837 | -0.0324 | 56
AEPW | KNOXLEE 138KV | 474 | -0.02403 | SPS | SPNSPUR_WND134.500 345KV | 161 | 0.00865 | -0.03268 | 56
AEPW | KNOXLEE 138KV | 474 | -0.02403 | OKGE | WOODWARD CO SUB 2 138KV | 152 | 0.00844 | -0.03247 | 56
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | WERE | BARBER CO SUB 34KV | 200 | 0.00771 | -0.03238 | 56
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | AEPW | COGENTRIX 345KV | 1038 | 0.00812 | -0.03279 | 56
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | WERE | HARPER CO SUB 34KV | 714 | 0.00771 | -0.03238 | 56
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | OKGE | MUSKOGEE 345KV | 1542.5 | 0.00822 | -0.03289 | 56
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | AEPW | OEC 345KV | 1460 | 0.00794 | -0.03261 | 56
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | OMPA | OMPA-KAW 69KV | 28.8 | 0.00824 | -0.03291 | 56
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | OMPA | OMPA-PONCA CITY 69KV | 75.8066 | 0.00824 | -0.03291 | 56
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | AEPW | RIVERSIDE STATION 138KV | 917 | 0.00814 | -0.03281 | 56
AEPW | WILKES 345KV | 354 | -0.02869 | AEPW | FITZHUGH 161KV | 171 | 0.0039 | -0.03259 | 56
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | WFEC | ANADARKO 138KV | 410.7952 | 0.0105 | -0.03216 | 57
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | WFEC | BLUCAN2 0.6900 34KV | 227 | 0.01045 | -0.03211 | 57
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | WFEC | COMMANCHE CO SUB 34KV | 100 | 0.01045 | -0.03211 | 57
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | OKGE | SEMINOLE 138KV | 250.8129 | 0.01067 | -0.03233 | 57
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | OKGE | SEMINOLE 345KV | 668.6758 | 0.01049 | -0.03215 | 57
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | AEPW | SOUTHWESTERN STATION 138KV | 243.936 | 0.01049 | -0.03215 | 57
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | WERE | BARBER CO SUB 34KV | 200 | 0.00771 | -0.032 | 57
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | WERE | HARPER CO SUB 34KV | 714 | 0.00771 | -0.032 | 57
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | AEPW | NORTHEASTERN STATION 138KV | 854 | 0.00755 | -0.03184 | 57
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | AEPW | NORTHEASTERN STATION 345KV | 460 | 0.00762 | -0.03191 | 57
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | AEPW | OEC 345KV | 1460 | 0.00794 | -0.03223 | 57
AEPW | KNOXLEE 138KV | 474 | -0.02403 | AEPW | COGENTRIX 345KV | 1038 | 0.00812 | -0.03215 | 57
AEPW | KNOXLEE 138KV | 474 | -0.02403 | SPS | G08-47 0.5750 34KV | 200 | 0.00829 | -0.03232 | 57
AEPW | KNOXLEE 138KV | 474 | -0.02403 | OKGE | MUSKOGEE 345KV | 1542.5 | 0.00822 | -0.03225 | 57
AEPW | KNOXLEE 138KV | 474 | -0.02403 | AEPW | OEC 345KV | 1460 | 0.00794 | -0.03197 | 57
AEPW | KNOXLEE 138KV | 474 | -0.02403 | OMPA | OMPA-KAW 69KV | 28.8 | 0.00824 | -0.03227 | 57
AEPW | KNOXLEE 138KV | 474 | -0.02403 | OMPA | OMPA-PONCA CITY 69KV | 75.8066 | 0.00824 | -0.03227 | 57
AEPW | KNOXLEE 138KV | 474 | -0.02403 | AEPW | RIVERSIDE STATION 138KV | 917 | 0.00814 | -0.03217 | 57
AEPW | LEBROCK 345KV | 146.9838 | -0.01947 | OKGE | G12_004_2 0.6900 34KV | 40 | 0.01249 | -0.03196 | 57
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | WERE | CITY OF AUGUSTA 69KV | 20 | 0.00729 | -0.03196 | 57
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | WERE | CLR_3 0.6900 34KV | 75 | 0.00712 | -0.03179 | 57
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | WERE | CLR_4 0.6900 34KV | 75 | 0.00712 | -0.03179 | 57
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | WERE | EVANS ENERGY CENTER 138KV | 671 | 0.00727 | -0.03194 | 57
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | WERE | GILL ENERGY CENTER 138KV | 194 | 0.00731 | -0.03198 | 57
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | AEPW | NORTHEASTERN STATION 138KV | 854 | 0.00755 | -0.03222 | 57
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | AEPW | NORTHEASTERN STATION 345KV | 460 | 0.00762 | -0.03229 | 57
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | AEPW | BUFFCK1 34.500 230KV | 99 | 0.00964 | -0.0313 | 58
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | OKGE | CANADN12 34.500 345KV | 298.2 | 0.00965 | -0.03131 | 58
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | AEPW | G09-16 0.6900 34KV | 100 | 0.00986 | -0.03152 | 58
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | WFEC | G12-028 0.6900 34KV | 323.62 | 0.00995 | -0.03161 | 58
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | OKGE | GRADY CO SUB 345KV | 99 | 0.01001 | -0.03167 | 58
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | OKGE | HORSESHOE LAKE 138KV | 608 | 0.00972 | -0.03138 | 58
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | OKGE | MCCLAIN 138KV | 465.6 | 0.00987 | -0.03153 | 58
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | OKGE | MUSTANG 138KV | 236 | 0.0097 | -0.03136 | 58
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | WFEC | RHWIND1WG11 0.6900 34KV | 123 | 0.00976 | -0.03142 | 58
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | OKGE | SMITH COGEN 138KV | 107 | 0.00973 | -0.03139 | 58
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | AEPW | WTH WIND 34.500 34KV | 148 | 0.00992 | -0.03158 | 58
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | WERE | CITY OF AUGUSTA 69KV | 20 | 0.00729 | -0.03158 | 58
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | WERE | CLR_3 0.6900 34KV | 75 | 0.00712 | -0.03141 | 58
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | WERE | CLR_4 0.6900 34KV | 75 | 0.00712 | -0.03141 | 58
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | WERE | ELK CO SUB 34KV | 401 | 0.00708 | -0.03137 | 58
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | WERE | EVANS ENERGY CENTER 138KV | 671 | 0.00727 | -0.03156 | 58
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | WERE | GILL ENERGY CENTER 138KV | 194 | 0.00731 | -0.0316 | 58
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | GRDA | GRDA1 161KV | 480 | 0.0071 | -0.03139 | 58
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | GRDA | GRDA1 345KV | 494 | 0.00705 | -0.03134 | 58
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | GRDA | KERR 115KV | 22.25 | 0.00708 | -0.03137 | 58
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | GRDA | KERR 161KV | 21.9191 | 0.00707 | -0.03136 | 58
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | GRDA | SALINA 161KV | 199.9855 | 0.00707 | -0.03136 | 58
AEPW | KNOXLEE 138KV | 474 | -0.02403 | WERE | BARBER CO SUB 34KV | 200 | 0.00771 | -0.03174 | 58
AEPW | KNOXLEE 138KV | 474 | -0.02403 | WERE | CITY OF AUGUSTA 69KV | 20 | 0.00729 | -0.03132 | 58
AEPW | KNOXLEE 138KV | 474 | -0.02403 | WERE | EVANS ENERGY CENTER 138KV | 671 | 0.00727 | -0.0313 | 58
AEPW | KNOXLEE 138KV | 474 | -0.02403 | WERE | GILL ENERGY CENTER 138KV | 194 | 0.00731 | -0.03134 | 58
AEPW | KNOXLEE 138KV | 474 | -0.02403 | WERE | HARPER CO SUB 34KV | 714 | 0.00771 | -0.03174 | 58
AEPW | KNOXLEE 138KV | 474 | -0.02403 | AEPW | NORTHEASTERN STATION 138KV | 854 | 0.00755 | -0.03158 | 58
AEPW | KNOXLEE 138KV | 474 | -0.02403 | AEPW | NORTHEASTERN STATION 345KV | 460 | 0.00762 | -0.03165 | 58
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | WERE | ANDERSONCO 345.00 345KV | 85 | 0.00659 | -0.03126 | 58
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | WERE | ELK CO SUB 34KV | 401 | 0.00708 | -0.03175 | 58
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | AEPW | FLINT CREEK 161KV | 528 | 0.00673 | -0.0314 | 58
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | GRDA | GRDA1 161KV | 480 | 0.0071 | -0.03177 | 58
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | GRDA | GRDA1 345KV | 494 | 0.00705 | -0.03172 | 58
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | WERE | HUTCHINSON ENERGY CENTER 115KV | 166 | 0.00691 | -0.03158 | 58
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | GRDA | KERR 115KV | 22.25 | 0.00708 | -0.03175 | 58
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | GRDA | KERR 161KV | 21.9191 | 0.00707 | -0.03174 | 58
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | GRDA | SALINA 161KV | 199.9855 | 0.00707 | -0.03174 | 58
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | SPS | ANTELOPE 230KV | 78.9921 | 0.00924 | -0.0309 | 59
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | SPS | ASGI-10-10 13.800 115KV | 42 | 0.00913 | -0.03079 | 59
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | SPS | ASGI2011-0010.6900 34KV | 28.8 | 0.00913 | -0.03079 | 59
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | SPS | CAPROCK 0KV | 80 | 0.00909 | -0.03075 | 59
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | SPS | CUNNINGHAM 230KV | 187 | 0.00913 | -0.03079 | 59
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | SPS | G12-038 18.000 345KV | 712 | 0.00917 | -0.03083 | 59
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | SPS | HOBBS PLANT #2 (CT) 115KV | 289 | 0.00913 | -0.03079 | 59
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | SPS | HOBBS PLANT #3 (ST) 230KV | 213 | 0.00913 | -0.03079 | 59
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | SPS | JONES_4 116.500 230KV | 472 | 0.0092 | -0.03086 | 59
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | SPS | LP-BRND2 69KV | 21 | 0.00921 | -0.03087 | 59
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | SPS | LP-HOLL2 69KV | 132 | 0.0092 | -0.03086 | 59
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | SPS | LP-MACK2 69KV | 80 | 0.00921 | -0.03087 | 59
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | SPS | MADOX 115KV | 119 | 0.00913 | -0.03079 | 59
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | SPS | MUSTANG 115KV | 350 | 0.00914 | -0.0308 | 59
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | SPS | MUSTANG_6 18.000 230KV | 394 | 0.00914 | -0.0308 | 59
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | SPS | PLANTX 115KV | 67.8511 | 0.00909 | -0.03075 | 59
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | SPS | PLANTX 230KV | 183 | 0.00909 | -0.03075 | 59
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | SPS | QUAY_CNTY 113.800 115KV | 23 | 0.00909 | -0.03075 | 59
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | OKGE | REDBUD 345KV | 1203.5 | 0.00943 | -0.03109 | 59
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | SPS | SAN JUAN 230KV | 120 | 0.00911 | -0.03077 | 59
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | OKGE | SPRING CREEK UNIT 3 AND 4 345KV | 300 | 0.00928 | -0.03094 | 59
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | SPS | TOLK 230KV | 1014.523 | 0.0091 | -0.03076 | 59
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | WERE | ANDERSONCO 345.00 345KV | 85 | 0.00659 | -0.03088 | 59
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | WERE | CLAYCSS3 115.00 115KV | 22.3 | 0.00642 | -0.03071 | 59
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | AEPW | FLINT CREEK 161KV | 528 | 0.00673 | -0.03102 | 59
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | WERE | HUTCHINSON ENERGY CENTER 115KV | 166 | 0.00691 | -0.0312 | 59
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | EMDE | RIVERTON 161KV | 72 | 0.00642 | -0.03071 | 59
AEPW | KNOXLEE 138KV | 474 | -0.02403 | WERE | CLR_3 0.6900 34KV | 75 | 0.00712 | -0.03115 | 59
AEPW | KNOXLEE 138KV | 474 | -0.02403 | WERE | CLR_4 0.6900 34KV | 75 | 0.00712 | -0.03115 | 59
AEPW | KNOXLEE 138KV | 474 | -0.02403 | WERE | ELK CO SUB 34KV | 401 | 0.00708 | -0.03111 | 59
AEPW | KNOXLEE 138KV | 474 | -0.02403 | AEPW | FLINT CREEK 161KV | 528 | 0.00673 | -0.03076 | 59
AEPW | KNOXLEE 138KV | 474 | -0.02403 | GRDA | GRDA1 161KV | 480 | 0.0071 | -0.03113 | 59
AEPW | KNOXLEE 138KV | 474 | -0.02403 | GRDA | GRDA1 345KV | 494 | 0.00705 | -0.03108 | 59
AEPW | KNOXLEE 138KV | 474 | -0.02403 | WERE | HUTCHINSON ENERGY CENTER 115KV | 166 | 0.00691 | -0.03094 | 59
AEPW | KNOXLEE 138KV | 474 | -0.02403 | GRDA | KERR 115KV | 22.25 | 0.00708 | -0.03111 | 59
AEPW | KNOXLEE 138KV | 474 | -0.02403 | GRDA | KERR 161KV | 21.9191 | 0.00707 | -0.0311 | 59
AEPW | KNOXLEE 138KV | 474 | -0.02403 | GRDA | SALINA 161KV | 199.9855 | 0.00707 | -0.0311 | 59
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | EMDE | ASBURY 161KV | 192 | 0.00636 | -0.03103 | 59
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | SWPA | CARTHAGE 69KV | 32 | 0.00612 | -0.03079 | 59
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | WERE | CLAYCSS3 115.00 115KV | 22.3 | 0.00642 | -0.03109 | 59
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | WERE | EMPORIA ENERGY CENTER 345KV | 413.6875 | 0.00638 | -0.03105 | 59
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | WERE | JEFFREY ENERGY CENTER 230KV | 730 | 0.00618 | -0.03085 | 59
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | WERE | JEFFREY ENERGY CENTER 345KV | 1460 | 0.00617 | -0.03084 | 59
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | EMDE | RIVERTON 161KV | 72 | 0.00642 | -0.03109 | 59
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | EMDE | RIVERTON 69KV | 40.9406 | 0.00639 | -0.03106 | 59
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | EMDE | STATE LINE 161KV | 523.4572 | 0.00636 | -0.03103 | 59
AEPW | LONESTAR POWER PLANT 69KV | 50 | -0.05032 | AEPW | LEBROCK 345KV | 550.0162 | -0.01947 | -0.03085 | 59
AEPW | TENASKA GATEWAY 345KV | 937.03 | -0.01869 | OKGE | G12_004_2 0.6900 34KV | 40 | 0.01249 | -0.03118 | 59
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | SPS | BLACKHAWK 115KV | 224 | 0.00879 | -0.03045 | 60
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | GRDA | BOOMER 69KV | 24 | 0.00854 | -0.0302 | 60
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | SPS | CLR_3 0.6900 34KV | 160 | 0.00887 | -0.03053 | 60
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | OKGE | CRSRDW21 34.500 345KV | 177 | 0.00877 | -0.03043 | 60
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | OKGE | DEWEY CO SUB 4 138KV | 130 | 0.00881 | -0.03047 | 60
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | OKGE | FPLWND11 34.500 138KV | 102 | 0.00868 | -0.03034 | 60
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | SPS | GS-PHWDRNCH134.500 230KV | 79 | 0.00887 | -0.03053 | 60
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | SPS | HARRINGTON 230KV | 1031 | 0.00886 | -0.03052 | 60
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | SPS | MAJESTIC WIND 115KV | 160 | 0.00884 | -0.0305 | 60
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | WFEC | MORLND 138KV | 272 | 0.00869 | -0.03035 | 60
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | SPS | NICHOLS 115KV | 82 | 0.00888 | -0.03054 | 60
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | WFEC | SLEEPING BEAR 138KV | 80 | 0.00866 | -0.03032 | 60
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | SPS | SPNSPUR_WND134.500 345KV | 161 | 0.00865 | -0.03031 | 60
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | SPS | STEER WATER 115KV | 80 | 0.00896 | -0.03062 | 60
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | EMDE | ASBURY 161KV | 192 | 0.00636 | -0.03065 | 60
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | SWPA | CARTHAGE 69KV | 32 | 0.00612 | -0.03041 | 60
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | WERE | EMPORIA ENERGY CENTER 345KV | 413.6875 | 0.00638 | -0.03067 | 60
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | WERE | JEFFREY ENERGY CENTER 230KV | 730 | 0.00618 | -0.03047 | 60
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | WERE | JEFFREY ENERGY CENTER 345KV | 1460 | 0.00617 | -0.03046 | 60
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | EMDE | LARUSSEL 161KV | 100 | 0.00596 | -0.03025 | 60
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | WERE | LAWRENCE ENERGY CENTER 115KV | 159 | 0.00593 | -0.03022 | 60
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | WERE | LAWRENCE ENERGY CENTER 230KV | 350.7009 | 0.00598 | -0.03027 | 60
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | EMDE | RIVERTON 69KV | 40.9406 | 0.00639 | -0.03068 | 60
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | EMDE | STATE LINE 161KV | 523.4572 | 0.00636 | -0.03065 | 60
AEPW | EASTMAN 138KV | 159.9462 | -0.02429 | WERE | TECUMSEH ENERGY CENTER 115KV | 204 | 0.00602 | -0.03031 | 60
WERE | G07-15 0.5750 34KV | 135 | 0.00548 | AEPW | TURK 138KV | 618 | 0.03593 | -0.03045 | 60
AEPW | KNOXLEE 138KV | 474 | -0.02403 | WERE | ANDERSONCO 345.00 345KV | 85 | 0.00659 | -0.03062 | 60
AEPW | KNOXLEE 138KV | 474 | -0.02403 | EMDE | ASBURY 161KV | 192 | 0.00636 | -0.03039 | 60
AEPW | KNOXLEE 138KV | 474 | -0.02403 | WERE | CLAYCSS3 115.00 115KV | 22.3 | 0.00642 | -0.03045 | 60
AEPW | KNOXLEE 138KV | 474 | -0.02403 | WERE | EMPORIA ENERGY CENTER 345KV | 413.6875 | 0.00638 | -0.03041 | 60
AEPW | KNOXLEE 138KV | 474 | -0.02403 | WERE | JEFFREY ENERGY CENTER 230KV | 730 | 0.00618 | -0.03021 | 60
AEPW | KNOXLEE 138KV | 474 | -0.02403 | WERE | JEFFREY ENERGY CENTER 345KV | 1460 | 0.00617 | -0.0302 | 60
AEPW | KNOXLEE 138KV | 474 | -0.02403 | EMDE | RIVERTON 161KV | 72 | 0.00642 | -0.03045 | 60
AEPW | KNOXLEE 138KV | 474 | -0.02403 | EMDE | RIVERTON 69KV | 40.9406 | 0.00639 | -0.03042 | 60
AEPW | KNOXLEE 138KV | 474 | -0.02403 | EMDE | STATE LINE 161KV | 523.4572 | 0.00636 | -0.03039 | 60
AEPW | LEBROCK 345KV | 146.9838 | -0.01947 | AEPW | COMANCHE 138KV | 195 | 0.01089 | -0.03036 | 60
AEPW | LEBROCK 345KV | 146.9838 | -0.01947 | AEPW | COMANCHE 69KV | 78 | 0.01085 | -0.03032 | 60
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | EMDE | LARUSSEL 161KV | 100 | 0.00596 | -0.03063 | 60
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | WERE | LAWRENCE ENERGY CENTER 115KV | 159 | 0.00593 | -0.0306 | 60
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | WERE | LAWRENCE ENERGY CENTER 230KV | 350.7009 | 0.00598 | -0.03065 | 60
AEPW | LIEBERMAN 138KV | 271 | -0.02467 | WERE | TECUMSEH ENERGY CENTER 115KV | 204 | 0.00602 | -0.03069 | 60
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | OKGE | CENT 21 34.500 138KV | 120 | 0.00847 | -0.03013 | 61
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | OKGE | CHSHMVW1 34.500 345KV | 202 | 0.00841 | -0.03007 | 61
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | OKGE | OU SPIRIT 138KV | 120 | 0.00844 | -0.0301 | 61
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | OKGE | SOONER 138KV | 535 | 0.00837 | -0.03003 | 61
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | OKGE | SOONER 345KV | 537 | 0.00837 | -0.03003 | 61
AEPW | ARSENAL HILL 69KV | 110 | -0.02166 | OKGE | WOODWARD CO SUB 2 138KV | 152 | 0.00844 | -0.0301 | 61
AEPW | KNOXLEE 138KV | 474 | -0.02403 | SWPA | CARTHAGE 69KV | 32 | 0.00612 | -0.03015 | 61
AEPW | KNOXLEE 138KV | 474 | -0.02403 | WERE | LAWRENCE ENERGY CENTER 230KV | 350.7009 | 0.00598 | -0.03001 | 61
AEPW | KNOXLEE 138KV | 474 | -0.02403 | WERE | TECUMSEH ENERGY CENTER 115KV | 204 | 0.00602 | -0.03005 | 61
AEPW | LEBROCK 345KV | 146.9838 | -0.01947 | OKGE | SEMINOLE 138KV | 250.8129 | 0.01067 | -0.03014 | 61
AEPW | WILKES 345KV | 354 | -0.02869 | SWPA | SIKESTON 161KV | 235 | 0.00142 | -0.03011 | 61
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor