## tblAllFacilityLog
STUDYDES | STUDYDES2 | EVENTTYPE | AssessmentSOLUTIONTYPE | AssessmenFDNS-TERMINATION | SOLUTIONTYPE | FDNS-TERMINATION | GROUP | SCENARIO | FGName | DIRECTION | FacilityName | FacilityUpgradeCode | ModelArea1 | ModelArea2 | FZONENAME | TZONENAME | MONTFLAG | MONTFB | MONTFNAME | MONTTB1 | MONTTNAME1 | MONTTB2 | MONTTNAME2 | MONTCKT | Case | RATEA | RATEB | RATEC | Assessment Loading | BaseCaseLoading | TransferCaseLoading | NameOfBusWithMonitoredVoltage | Assessment Voltage | BaseCaseVoltage | TransferCaseVoltage | VINIT | VMIN | VMAX | CATEGORY | CONTTYPE | CONTNAME | CONTXFMRFLAG | CONTFB | CONTFNAME | CONTTB1 | CONTTNAME1 | CONTTB2 | CONTTNAME2 | CONTCKT | TransmissionProviderCommentsNotes | RequiredRateB | TransmissionOwnerComments | OwnerDesignation | UpgradeName | UpgradeComponentWithinFacility | NewSummerA | NewSummerB | NewOtherA | NewOtherB | DistToConstruct | TotalLead | ConstructionLeadOnly | NewOrConstructWhileEnergized | NewR | NewX | NewB | CommentsRegardingUpgradeRequirements | NewCost | EffDate | NetPlantDate | ReusableEx_GrossValue | ReusableEx_NetValue | Reusable_EndofDepr | SalvageValue | NewCostWhileExpediting | EffDateExpedited | StartDeprExpedited | EndDeprExpedited | NetPlantDateExpedited | ReusableEx_GrossExpedited | ReusableEx_NetExpedited | Reusable_EndofDeprExpedited | SalvageValueExpedited | Generation 1 Owner & Unit (Name) | Generation 1 Redispatch Cost ($) | Generation 1 Redispatch Date (M/D/Y) | Generation 2 Owner & Unit (Name) | Generation 2 Redispatch Cost ($) | Generation 2 Redispatch Date (M/D/Y) | Generation 3 Owner & Unit (Name) | Generation 3 Redispatch Cost ($) | Generation 3 Redispatch Date (M/D/Y) | ActualCompletion | ActualNewCost | ActualNetPlantDate | ActualReusableEx_GrossValue | ActualReusableEx_NetValue | ActualReusable_EndofDepr | ActualSalvageValue | Actual_NewCostWhileExpediting | Actual_StartDeprExp | Actual_EndDeprExp | Actual_NetPlantDateExpedited | ActualReusableEx_GrossExpedited | ActualReusableEx_NetExpedited | ActualReusable_EndofDeprExpedited | Actual_SalvageValueExpedited | SPPReliabilityDate | DUN | EOC | EarliestDate
GI | GEN-2006-044N | [9 empty] | ALBION - PETERSBURG 115KV CKT 1 | U | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640318 | PETRSBG7 115.00 | 640054 | ALBION 7 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | NPPD | Albion - Petersburg 115kV Ckt 1 GEN-2006-044N Upgrade | Replace Breaker Switch 1106-D & jumpers; Replace Petersburg 115kV Substation main bus; Upgrade and replace transmission structures on 115kV lines TL1168 A & B to facilitate 100 degrees Centigrade line operation | [13 empty] | 2011-01-01 | [39 empty] | 2012-12-31 | 2012-12-31
2009-AGP1 | AFS-5 | [9 empty] | ALTUS SW - NAVAJO 69KV CKT 1 | U | WFEC | WFEC | AEP-KP | AEP-KP | 0 | 521009 | NAVAJO 2 69.000 | 520805 | ALTUSSW2 69.000 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WFEC | ALTUS SW - NAVAJO 69KV CKT 1 | Upgrade Terminal Equipment at Altus SW, 300-600A, new rating conductor 53/65MVA | [53 empty] | 2013-06-01 | 2013-06-01
2006-AG1 | AFS-4 | [9 empty] | ALUMAX TAP - BANN 138KV CKT 1 | U | AEPW | AEPW |  |  | 0 | 508049 | ALUMXT 4 138 | 508054 | BANN 4 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | ALUMAX TAP - BANN 138KV CKT 1 | Replace six (6) 138 kV switches, five at Bann & one at Alumax Tap. Rebuild 0.67 miles of 1024 ACAR with 2156 ACSR. Replace wavetrap & jumpers @ Bann. Replace breaker 3300 @ Bann. | [53 empty] | 2008-06-01 | 2008-06-01
GI-DP | GEN-2006-010 | [9 empty] | Ashdown REC (AECC delivery point) | U | AEPW | AEPW | SARK | SARKAECC | 0 | 507428 | OKAY 4 138.00 | 507402 | ASHDWNR4 138.00 | 507431 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | Ashdown REC (AECC delivery point) | Replace switches 6276 and 6277 with 3000 A, 138 kV switches and replace the conductor between them with 1590 ACSR. | [13 empty] | 2007-10-01 | [39 empty] | 2011-12-01 | 2011-12-01
GI | GEN-2006-010 | [9 empty] | ASHDOWN REC (MILLWOOD) - OKAY 138KV CKT 1 | U | AEPW | AEPW | SARK | SARKAECC | 0 | 507428 | OKAY 4 138.00 | 507402 | ASHDWNR4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | ASHDOWN REC (MILLWOOD) - OKAY 138KV CKT 1 | Rebuild fourteen (14.3) miles of 115 kV line to 138 kV and reconductor with 1590 ACSR. | [13 empty] | 2007-10-01 | [39 empty] | 2011-12-01 | 2011-12-01
GI | GEN-2006-010 | [9 empty] | ASHDOWN REC (MILLWOOD) - PATTERSON 138KV CKT 1 | U | AEPW | AEPW | SARKAECC | SARK | 0 | 507402 | ASHDWNR4 138.00 | 507431 | PATTERS4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | ASHDOWN REC (MILLWOOD) - PATTERSON 138KV CKT 1 | Reconductor line and convert line to 138 kV. Convert Patterson station to breaker-and-a half configuration. | [13 empty] | 2007-10-01 | [39 empty] | 2011-12-01 | 2011-12-01
2007-AG3 | AFS-9 | [9 empty] | BARBER - MEDICINE LODGE 115KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539673 | MED-LDG3 115.00 | 539760 | BARBER 3 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | BARBER - MEDICINE LODGE 115KV CKT 1 | Rebuild line | [53 empty] | 2009-12-01 | 2013-06-01
2007-AG3 | AFS-9 | [9 empty] | BARBER - SAWYER 115KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539760 | BARBER 3 | 539649 | SAWYER 3 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | BARBER - SAWYER 115KV CKT 1 | Rebuild line | [53 empty] | 2009-12-01 | 2013-06-01
2007-AG3 | AFS-9 | [9 empty] | BARBER (BARBER 4) 138/115/2.72KV TRANSFORMER CKT 1 | U | MKEC |  |  |  | 2 | 539674 | BARBER 4 | 539760 | BARBER 3 | 539917 | BARBER-T | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | BARBER (BARBER 4) 138/115/2.72KV TRANSFORMER CKT 1 | Upgrade transformer | [53 empty] | 2009-12-01 | 2013-06-01
2005-AG2 | AFS-3 | [9 empty] | BEELINE - EXPLORER GLENPOOL 138KV CKT 1 | U | OKGE | OKGE |  |  | 0 | 515473 | EXPLGLN4 138 | 515247 | BEELINE4 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OKGE | BEELINE - EXPLORER GLENPOOL 138KV CKT 1 | Reconductor .92miles of line with Drake ACCC/TW. | [53 empty] | 2009-06-01 | 2009-06-01
2005-AG2 | AFS-3 | [9 empty] | BROWN - EXPLORER TAP 138KV CKT 1 | U | OKGE | OKGE |  |  | 0 | 515157 | BROWN 4 138 | 515153 | COLEMNT4 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OKGE | BROWN - EXPLORER TAP 138KV CKT 1 | Upgrade CT at Brown. | [53 empty] | 2006-06-01 | 2006-06-01
2005-AG2 | AFS-3 | [9 empty] | CACHE - SNYDER 138KV CKT 1 | U | AEPW | AEPW |  |  | 0 | 511500 | CACHE4 138 | 511435 | SNYDER-4 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | CACHE - SNYDER 138KV CKT 1 | Replace Snyder wavetrap | [53 empty] | 2008-05-21 | 2008-05-21
2009-AGP2 | AFS-6 | [9 empty] | CANTON - TALOGA 69KV CKT 1 | U | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521064 | TALOGA 2 69.000 | 520843 | CANTON-2 69.000 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WFEC | CANTON - TALOGA 69KV CKT 1 | UPGRADE CANTON TO TALOGA TO 336.4 | 106 | 132 |  |  | 9.7 | 24 | 24 |  | 0.04013 | 0.16101 | 0.00252 | [42 empty] | 2011-06-01 | 2013-06-01
2013-AG2 | AFS8 |  | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T12065025SP | FROM->TO | CARLISLE INTERCHANGE (WH XHS70711) 230/115/13.2KV TRANSFORMER CKT 1 | REL | SPS | SPS | SPS-CNPL | SPS-CNPL | 1 | 526161 | CARLISLE 6230.00 | 526160 | CARLISLE 3115.00 | 526157 | CRLSLE_TR1 113.200 | 1 | 25SP | 168 | 168 | 0 | 105 | 104.9966 | 105.823 | [7 empty] | CATEGORYB | SINGLE | WOLFFORTH INTERCHANGE (WH 7001668) 230/115/13.2KV TRANSFORMER CKT 1 | 1 | 526524 | WOLFFORTH 3115.00 | 526525 | WOLFFORTH 6230.00 | 526522 | WOLFRTH_TR1113.200 | 1 |  |  |  | SPS | CARLISLE INTERCHANGE (WH XHS70711) 230/115/13.2KV TRANSFORMER CKT 1 | Upgrade transformer to 250 MVA. | 250 | 250 |  |  |  | 24 | 24 | [46 empty] | 2024-06-01 | 2024-06-01
2013-AG2 | AFS8 |  | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T2545025SP | FROM->TO | CARLISLE INTERCHANGE (WH XHS70711) 230/115/13.2KV TRANSFORMER CKT 1 | REL | SPS | SPS | SPS-CNPL | SPS-CNPL | 1 | 526161 | CARLISLE 6230.00 | 526160 | CARLISLE 3115.00 | 526157 | CRLSLE_TR1 113.200 | 1 | 25SP | 168 | 168 | 0 | 106.4 | 106.4046 | 105.2663 | [7 empty] | CATEGORYB | SINGLE | ALLEN SUB - LUBBOCK SOUTH INTERCHANGE 115KV CKT 1 | 0 | 526213 | ALLEN 3115.00 | 526268 | LUBBCK_STH 3115.00 | 0 |  | 1 |  |  |  | SPS | CARLISLE INTERCHANGE (WH XHS70711) 230/115/13.2KV TRANSFORMER CKT 1 | Upgrade transformer to 250 MVA. | 250 | 250 |  |  |  | 24 | 24 | [46 empty] | 2024-06-01 | 2024-06-01
2009-AGP1 | AFS-5 | [9 empty] | CHERRY6 230.00 - Harrington Station East Bus 230KV CKT 1 | U | SPS | SPS | SPS-AMA |  | 0 | 523977 |  | 524010 |  | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | SPS | CHERRY6 230.00 - Harrington Station East Bus 230KV CKT 1 | Replace wavetrap at Harrington East | [53 empty] | 2015-06-01 | 2015-06-01
2007-AG3 | AFS-9 | [9 empty] | CLIFTON - GREENLEAF 115KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539656 | CLIFTON3 115.00 | 539665 | GRNLEAF3 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | CLIFTON - GREENLEAF 115KV CKT 1 | Rebuild 14.4 miles | [53 empty] | 2011-06-01 | 2013-06-01
2007-AG3 | AFS-9 | [9 empty] | DEARING 138KV | U | WERE |  | SEAST |  |  | 533002 | DEARING4 138.00 | [20 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WERE | DEARING 138KV | Dearing 138 kV 20 MVAR Capacitor Addition | [53 empty] | 2012-06-01 | 2012-06-01
NA | SPONSORED | [9 empty] | EASTOWN7 345.00 (EASTOWN 345) 345/161/13.8KV TRANSFORMER CKT 1 | U | GMO | GMO |  |  | 1 | 541400 | EASTOWN7 345.00 | 541401 | EASTOWN5 161.00 | 541402 | EASTOWN1 13.800 | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | KACP | EASTOWN7 345.00 (EASTOWN 345) 345/161/13.8KV TRANSFORMER CKT 1 | Replace 715 MVA transformer. | [53 empty] | 2014-05-01 | 2014-05-01
2005-AG2 | AFS-3 | [9 empty] | EXPLORER GLENPOOL - RIVERSIDE STATION 138KV CKT 1 | U | AEPW | OKGE |  |  | 0 | 509783 | R.S.S.-4 138 | 515473 | EXPLGLN4 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | EXPLORER GLENPOOL - RIVERSIDE STATION 138KV CKT 1 (AEP) | Reconductor 1.9 miles with ACCC. Replace wave trap jumpers at Riverside. | [53 empty] | 2009-06-01 | 2009-06-01
2005-AG2 | AFS-3 | [9 empty] | EXPLORER GLENPOOL - RIVERSIDE STATION 138KV CKT 1 OKGE | U | AEPW | OKGE |  |  | 0 | 509783 | R.S.S.-4 138 | 515473 | EXPLGLN4 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OKGE | EXPLORER GLENPOOL - RIVERSIDE STATION 138KV CKT 1 (OGE) | Reconductor 1.82 miles line with Drake ACCC/TW. | [53 empty] | 2009-06-01 | 2009-06-01
GI | ASGI-2010-006 | [9 empty] | Fairfax - Pawnee 138kV Ckt 1 | U |  |  |  |  | 0 | 300139 |  | 512749 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | GRDA | Fairfax - Pawnee 138kV Ckt 1 | Construct Approx. 15 miles of 138kV transmission line from Fairfax to a new substation on the Cleveland-Stillwater 138kV line near Pawnee. & Fairfax Substation: Install 138kV line terminal and any additional modifications that are necessary to connect to | [13 empty] | 2011-06-15 | [39 empty] | 2014-06-30 | 2014-06-01
2007-AG3 | AFS-9 | [9 empty] | FLATRDG3 138.00 - MEDICINE LODGE 138KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539674 | MED-LDG4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | FLATRDG3 - MEDICINE LODGE 138KV CKT 1 | Rebuild 8.05 mile line | [53 empty] | 2009-12-01 | 2013-06-01
2007-AG3 | AFS-9 | [9 empty] | FLATRDG3 138.00 - HARPER 138KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | FLATRDG3 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 |  |  | 24.15 | 24 | 24 | [46 empty] | 2009-12-01 | 2013-06-01
GI | GEN-2008-086N02 | [9 empty] | Fort Randall - Madison County 230kV Ckt 1 | U |  |  |  |  | 0 | 640540 |  | 652509 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | NPPD | Fort Randall - Madison County 230kV Ckt 1 | Raise structures and line clearances as necessary to re-rate the transmission line to 320 MVA | [53 empty] | 2014-10-01 | 2014-10-01
2006-AG1 | AFS-4 | [9 empty] | FT SUPPLY 138/69KV TRANSFORMER CKT 1 | U | WFEC | WFEC |  |  | 1 | 520920 | FTSUPLY4 138 | 520919 | FTSUPLY269.0 | 521182 |  | 2 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WFEC | FT SUPPLY 138/69KV TRANSFORMER CKT 2 | Install 2nd 70 MVA auto at Ft Supply | [53 empty] | 2006-12-01 | 2008-06-01
2009-AGP1 | AFS-5 | [9 empty] | G03-05T 138.00 - PARADISE 138KV CKT 1 | U | WFEC | WFEC | AEP-OP-I | AEP-KP | 0 | 521129 | G03-05T 138.00 | 521024 | PARADSE4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WFEC | BLUCAN5 4 138.00 - PARADISE 138KV CKT 1 | Upgrade Paradise to G03-05T to 1113 | [53 empty] | 2010-06-01 | 2013-06-01
GI | GEN-2008-037 | [9 empty] | GRACMNT4 138.00 - WASHITA 138KV CKT 2 OKGE | U | WFEC | OKGE | AEP-CS | ARDMORE | 0 | 521089 | WASHITA4 138.00 | 515802 | GRACMNT4 138.00 | 0 |  | 2 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OKGE | Gracemont 138kV line terminal addition | 138kV line terminal at Gracemont substation, including breaker, line relaying, disconnect switches and associated equipment, dead end structures, revenue metering with CT's and PT's. | [13 empty] | 2010-11-20 | [39 empty] | 2011-10-15 | 2011-10-15
GI | GEN-2008-037 | [9 empty] | GRACMNT4 138.00 - WASHITA 138KV CKT 2 WFEC | U | WFEC | OKGE | AEP-CS | ARDMORE | 0 | 521089 | WASHITA4 138.00 | 515802 | GRACMNT4 138.00 | 0 |  | 2 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WFEC | WASHITA - GRACEMONT 138 KV CKT 2 | BUILD WASHITA - GRACEMONT 138KV CKT 2 (APPROXIMATELY 7 MILES). ADD LINE TERMINAL AT WASHITA AND PROCURE RIGHT OF WAY. REQUIRED AS SHARED NETWORK UPGRADE FOR INTERCONNECTION OF GEN-2008-037. | [13 empty] | 2010-11-20 | [39 empty] | 2012-10-12 | 2012-10-12
2008-AGP1 | AFS-9 | [9 empty] | GREENLEAF - KNOB HILL 115KV CKT 1 | U | SUNC | WERE |  | NCENTRAL | 0 | 539665 | GRNLEAF3 115.00 | 533332 | KNOB HL3 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | GREENLEAF - KNOB HILL 115KV CKT 1 (MKEC) | Rebuild 43.5% Ownership of 20.9 miles | [53 empty] | 2013-06-01 | 2013-06-01
GI | GEN-2008-051 | [9 empty] | Harrington Mid - Nichols 230 kV Ckt 2 | U | SPS | SPS |  |  | 0 | 523978 |  | 524044 |  |  |  | 2 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | SPS | Harrington Mid - Nichols 230 kV Ckt 2 | Reconductor Harrington Mid - Nichols 230kV. Replace switches and breakers to get circuit to 727/727 MVA rating. New limit should be bus rating. | [13 empty] | 2011-10-01 | [39 empty] | 2012-12-01 | 2012-12-01
GI | GEN-2008-051 | [9 empty] | Harrington West - Nichols 230kV Ckt 1 | U | SPS | SPS |  |  | 0 | 523977 |  | 524044 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | SPS | Harrington West - Nichols 230kV Ckt 1 | Reconductor Harrington West - Nichols 230kV. Replace switches and breakers to get circuit to 727/727 MVA rating. New limit should be bus rating. | [13 empty] | 2011-10-01 | [39 empty] | 2012-12-01 | 2012-12-01
2013-AG2 | AFS8 | NCONV |  |  | FDNSLock-Blown up | FDNS-Blown up | 5 | 0 | 2013AG2AFS84L95025SP |  | HOBBS - KIOWA 7345.00 345KV CKT 1 | REL | SPS | SPS | SPS-HOBB | SPS-PECO | 0 | 527896 | HOBBS_INT 7345.00 | 527965 | KIOWA 7345.00 | 0 |  | 1 | 25SP | 2302 | 2532 | 0 |  | 30.0594 | 30.1192 | [8 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | China Draw_Road Runner_SVC | New 200 Mvar SVC at China Draw 115kV; new 200 Mvar SVC at Road Runner 115kV | [53 empty] | 2017-06-01 | 2017-08-01
2013-AG2 | AFS8 | NCONV |  |  | FDNSLock-Blown up | FDNS-Blown up | 5 | 0 | 2013AG2AFS84L95025SP |  | HOBBS - KIOWA 7345.00 345KV CKT 1 | REL | SPS | SPS | SPS-HOBB | SPS-PECO | 0 | 527896 | HOBBS_INT 7345.00 | 527965 | KIOWA 7345.00 | 0 |  | 1 | 25SP | 2302 | 2532 | 0 |  | 30.0594 | 30.1192 | [8 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | IMC Area Rebuild and Capacitors Additions | Reconductoring IMC #1 Tap-Intrepid West, IMC #1-Livingston Ridge, Intrepid West-Potash Junction, Byrd-Monument, Ponderosa Tap-Whitten, National Enrichment Plant-Targa 115 kV lines, Upgrading terminal equipment at Byrd 115 kV substation. A wave trap will | [53 empty] | 2017-06-01 | 2017-06-01
2013-AG2 | AFS8 | NCONV |  |  | FDNSLock-Blown up | FDNS-Blown up | 5 | 0 | 2013AG2AFS84L95025SP |  | HOBBS - KIOWA 7345.00 345KV CKT 1 | REL | SPS | SPS | SPS-HOBB | SPS-PECO | 0 | 527896 | HOBBS_INT 7345.00 | 527965 | KIOWA 7345.00 | 0 |  | 1 | 25SP | 2302 | 2532 | 0 |  | 30.0594 | 30.1192 | [8 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | North Loving 115 kV Cap Banks | Install two (2) stages of 14.4 MVAR capacitor banks at North Loving 115 kV. | [53 empty] | 2022-06-01 | 2022-06-01
2013-AG2 | AFS8 | NCONV |  |  | FDNSLock-Blown up | FDNS-Blown up | 5 | 0 | 2013AG2AFS84L95025SP |  | HOBBS - KIOWA 7345.00 345KV CKT 1 | REL | SPS | SPS | SPS-HOBB | SPS-PECO | 0 | 527896 | HOBBS_INT 7345.00 | 527965 | KIOWA 7345.00 | 0 |  | 1 | 25SP | 2302 | 2532 | 0 |  | 30.0594 | 30.1192 | [8 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Andrews - Hobbs 345 kV Ckt 1 Voltage Conversion | Convert existing 30.5-mile 230 kV line from Andrews to Hobbs to 345 kV. Re-terminate line on 345 kV bus at Hobbs. Ratings will be based on current conductors - bundled 795 ACSR. | [53 empty] | 2022-06-01 | 2022-06-01
2013-AG2 | AFS8 | NCONV |  |  | FDNSLock-Blown up | FDNS-Blown up | 5 | 5 | 2013AG2AFS84L45525SP |  | HOBBS - KIOWA 7345.00 345KV CKT 1 | REL | SPS | SPS | SPS-HOBB | SPS-PECO | 0 | 527896 | HOBBS_INT 7345.00 | 527965 | KIOWA 7345.00 | 0 |  | 1 | 25SP | 2302 | 2532 | 0 |  | 29.05 | 29.1306 | [8 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | China Draw_Road Runner_SVC | New 200 Mvar SVC at China Draw 115kV; new 200 Mvar SVC at Road Runner 115kV | [53 empty] | 2017-06-01 | 2017-08-01
2013-AG2 | AFS8 | NCONV |  |  | FDNSLock-Blown up | FDNS-Blown up | 5 | 5 | 2013AG2AFS84L45525SP |  | HOBBS - KIOWA 7345.00 345KV CKT 1 | REL | SPS | SPS | SPS-HOBB | SPS-PECO | 0 | 527896 | HOBBS_INT 7345.00 | 527965 | KIOWA 7345.00 | 0 |  | 1 | 25SP | 2302 | 2532 | 0 |  | 29.05 | 29.1306 | [8 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | IMC Area Rebuild and Capacitors Additions | Reconductoring IMC #1 Tap-Intrepid West, IMC #1-Livingston Ridge, Intrepid West-Potash Junction, Byrd-Monument, Ponderosa Tap-Whitten, National Enrichment Plant-Targa 115 kV lines, Upgrading terminal equipment at Byrd 115 kV substation. A wave trap will | [53 empty] | 2017-06-01 | 2017-06-01
2013-AG2 | AFS8 | NCONV |  |  | FDNSLock-Blown up | FDNS-Blown up | 5 | 5 | 2013AG2AFS84L45525SP |  | HOBBS - KIOWA 7345.00 345KV CKT 1 | REL | SPS | SPS | SPS-HOBB | SPS-PECO | 0 | 527896 | HOBBS_INT 7345.00 | 527965 | KIOWA 7345.00 | 0 |  | 1 | 25SP | 2302 | 2532 | 0 |  | 29.05 | 29.1306 | [8 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | North Loving 115 kV Cap Banks | Install two (2) stages of 14.4 MVAR capacitor banks at North Loving 115 kV. | [53 empty] | 2022-06-01 | 2022-06-01
2013-AG2 | AFS8 | NCONV |  |  | FDNSLock-Blown up | FDNS-Blown up | 5 | 5 | 2013AG2AFS84L45525SP |  | HOBBS - KIOWA 7345.00 345KV CKT 1 | REL | SPS | SPS | SPS-HOBB | SPS-PECO | 0 | 527896 | HOBBS_INT 7345.00 | 527965 | KIOWA 7345.00 | 0 |  | 1 | 25SP | 2302 | 2532 | 0 |  | 29.05 | 29.1306 | [8 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | Andrews - Hobbs 345 kV Ckt 1 Voltage Conversion | Convert existing 30.5-mile 230 kV line from Andrews to Hobbs to 345 kV. Re-terminate line on 345 kV bus at Hobbs. Ratings will be based on current conductors - bundled 795 ACSR. | [53 empty] | 2022-06-01 | 2022-06-01
2013-AG2 | AFS8 | NCONV |  |  | FDNSLock-Blown up | FDNS-Blown up | 5 | 5 | 2013AG2AFS84L25520SP |  | HOBBS - KIOWA 7345.00 345KV CKT 1 | REL | SPS | SPS | SPS-HOBB | SPS-PECO | 0 | 527896 | HOBBS_INT 7345.00 | 527965 | KIOWA 7345.00 | 0 |  | 1 | 20SP | 2302 | 2532 | 0 |  | 24.4844 | 24.819 | [8 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | IMC Area Rebuild and Capacitors Additions | Reconductoring IMC #1 Tap-Intrepid West, IMC #1-Livingston Ridge, Intrepid West-Potash Junction, Byrd-Monument, Ponderosa Tap-Whitten, National Enrichment Plant-Targa 115 kV lines, Upgrading terminal equipment at Byrd 115 kV substation. A wave trap will | [53 empty] | 2017-06-01 | 2017-06-01
2013-AG2 | AFS8 | NCONV |  |  | FDNSLock-Blown up | FDNS-Blown up | 5 | 5 | 2013AG2AFS84L25520SP |  | HOBBS - KIOWA 7345.00 345KV CKT 1 | REL | SPS | SPS | SPS-HOBB | SPS-PECO | 0 | 527896 | HOBBS_INT 7345.00 | 527965 | KIOWA 7345.00 | 0 |  | 1 | 20SP | 2302 | 2532 | 0 |  | 24.4844 | 24.819 | [8 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | China Draw_Road Runner_SVC | New 200 Mvar SVC at China Draw 115kV; new 200 Mvar SVC at Road Runner 115kV | [53 empty] | 2017-06-01 | 2017-08-01
2013-AG2 | AFS8 | NCONV |  |  | FDNSLock-Blown up | FDNS-Blown up | 5 | 0 | 2013AG2AFS84L15020SP |  | HOBBS - KIOWA 7345.00 345KV CKT 1 | REL | SPS | SPS | SPS-HOBB | SPS-PECO | 0 | 527896 | HOBBS_INT 7345.00 | 527965 | KIOWA 7345.00 | 0 |  | 1 | 20SP | 2302 | 2532 | 0 |  | 24.6878 | 24.7755 | [8 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | IMC Area Rebuild and Capacitors Additions | Reconductoring IMC #1 Tap-Intrepid West, IMC #1-Livingston Ridge, Intrepid West-Potash Junction, Byrd-Monument, Ponderosa Tap-Whitten, National Enrichment Plant-Targa 115 kV lines, Upgrading terminal equipment at Byrd 115 kV substation. A wave trap will | [53 empty] | 2017-06-01 | 2017-06-01
2013-AG2 | AFS8 | NCONV |  |  | FDNSLock-Blown up | FDNS-Blown up | 5 | 0 | 2013AG2AFS84L15020SP |  | HOBBS - KIOWA 7345.00 345KV CKT 1 | REL | SPS | SPS | SPS-HOBB | SPS-PECO | 0 | 527896 | HOBBS_INT 7345.00 | 527965 | KIOWA 7345.00 | 0 |  | 1 | 20SP | 2302 | 2532 | 0 |  | 24.6878 | 24.7755 | [8 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | China Draw_Road Runner_SVC | New 200 Mvar SVC at China Draw 115kV; new 200 Mvar SVC at Road Runner 115kV | [53 empty] | 2017-06-01 | 2017-08-01
2013-AG2 | AFS8 | NCONV |  |  | FDNSLock-Blown up | FDNS-Blown up | 5 | 5 | 2013AG2AFS84L125525WP |  | HOBBS - YOAKUM_345 345.00 345KV CKT 1 | REL | SPS | SPS | SPS-YOGS | SPS-HOBB | 0 | 526936 | YOAKUM_345 345.00 | 527896 | HOBBS_INT 7345.00 | 0 |  | 1 | 25WP | 2388 | 2626 | 0 |  | 21.3849 | 21.4829 | [8 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | IMC Area Rebuild and Capacitors Additions | Reconductoring IMC #1 Tap-Intrepid West, IMC #1-Livingston Ridge, Intrepid West-Potash Junction, Byrd-Monument, Ponderosa Tap-Whitten, National Enrichment Plant-Targa 115 kV lines, Upgrading terminal equipment at Byrd 115 kV substation. A wave trap will | [53 empty] | 2017-06-01 | 2017-06-01
2013-AG2 | AFS8 | NCONV |  |  | FDNSLock-Blown up | FDNS-Blown up | 5 | 5 | 2013AG2AFS84L125525WP |  | HOBBS - YOAKUM_345 345.00 345KV CKT 1 | REL | SPS | SPS | SPS-YOGS | SPS-HOBB | 0 | 526936 | YOAKUM_345 345.00 | 527896 | HOBBS_INT 7345.00 | 0 |  | 1 | 25WP | 2388 | 2626 | 0 |  | 21.3849 | 21.4829 | [8 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | China Draw_Road Runner_SVC | New 200 Mvar SVC at China Draw 115kV; new 200 Mvar SVC at Road Runner 115kV | [53 empty] | 2017-06-01 | 2017-08-01
2013-AG2 | AFS8 | NCONV |  |  | FDNSLock-Blown up | FDNS-Blown up | 5 | 0 | 2013AG2AFS84L85025WP |  | HOBBS - YOAKUM_345 345.00 345KV CKT 1 | REL | SPS | SPS | SPS-YOGS | SPS-HOBB | 0 | 526936 | YOAKUM_345 345.00 | 527896 | HOBBS_INT 7345.00 | 0 |  | 1 | 25WP | 2388 | 2626 | 0 |  | 21.1643 | 21.1743 | [8 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | China Draw_Road Runner_SVC | New 200 Mvar SVC at China Draw 115kV; new 200 Mvar SVC at Road Runner 115kV | [53 empty] | 2017-06-01 | 2017-08-01
2013-AG2 | AFS8 | NCONV |  |  | FDNSLock-Blown up | FDNS-Blown up | 5 | 0 | 2013AG2AFS84L85025WP |  | HOBBS - YOAKUM_345 345.00 345KV CKT 1 | REL | SPS | SPS | SPS-YOGS | SPS-HOBB | 0 | 526936 | YOAKUM_345 345.00 | 527896 | HOBBS_INT 7345.00 | 0 |  | 1 | 25WP | 2388 | 2626 | 0 |  | 21.1643 | 21.1743 | [8 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | IMC Area Rebuild and Capacitors Additions | Reconductoring IMC #1 Tap-Intrepid West, IMC #1-Livingston Ridge, Intrepid West-Potash Junction, Byrd-Monument, Ponderosa Tap-Whitten, National Enrichment Plant-Targa 115 kV lines, Upgrading terminal equipment at Byrd 115 kV substation. A wave trap will | [53 empty] | 2017-06-01 | 2017-06-01
2013-AG2 | AFS8 | NCONV |  |  | FDNSLock-Blown up | FDNS-Blown up | 5 | 0 | 2013AG2AFS84L65025SP |  | HOBBS - YOAKUM_345 345.00 345KV CKT 1 | REL | SPS | SPS | SPS-YOGS | SPS-HOBB | 0 | 526936 | YOAKUM_345 345.00 | 527896 | HOBBS_INT 7345.00 | 0 |  | 1 | 25SP | 2302 | 2532 | 0 |  | 23.4063 | 23.6197 | [8 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | IMC Area Rebuild and Capacitors Additions | Reconductoring IMC #1 Tap-Intrepid West, IMC #1-Livingston Ridge, Intrepid West-Potash Junction, Byrd-Monument, Ponderosa Tap-Whitten, National Enrichment Plant-Targa 115 kV lines, Upgrading terminal equipment at Byrd 115 kV substation. A wave trap will | [53 empty] | 2017-06-01 | 2017-06-01
2013-AG2 | AFS8 | NCONV |  |  | FDNSLock-Blown up | FDNS-Blown up | 5 | 0 | 2013AG2AFS84L65025SP |  | HOBBS - YOAKUM_345 345.00 345KV CKT 1 | REL | SPS | SPS | SPS-YOGS | SPS-HOBB | 0 | 526936 | YOAKUM_345 345.00 | 527896 | HOBBS_INT 7345.00 | 0 |  | 1 | 25SP | 2302 | 2532 | 0 |  | 23.4063 | 23.6197 | [8 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | China Draw_Road Runner_SVC | New 200 Mvar SVC at China Draw 115kV; new 200 Mvar SVC at Road Runner 115kV | [53 empty] | 2017-06-01 | 2017-08-01
2013-AG2 | AFS8 | NCONV |  |  | FDNSLock-Blown up | FDNS-Blown up | 5 | 5 | 2013AG2AFS84L25525SP |  | HOBBS - YOAKUM_345 345.00 345KV CKT 1 | REL | SPS | SPS | SPS-YOGS | SPS-HOBB | 0 | 526936 | YOAKUM_345 345.00 | 527896 | HOBBS_INT 7345.00 | 0 |  | 1 | 25SP | 2302 | 2532 | 0 |  | 20.9992 | 21.219 | [8 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | China Draw_Road Runner_SVC | New 200 Mvar SVC at China Draw 115kV; new 200 Mvar SVC at Road Runner 115kV | [53 empty] | 2017-06-01 | 2017-08-01
2013-AG2 | AFS8 | NCONV |  |  | FDNSLock-Blown up | FDNS-Blown up | 5 | 5 | 2013AG2AFS84L25525SP |  | HOBBS - YOAKUM_345 345.00 345KV CKT 1 | REL | SPS | SPS | SPS-YOGS | SPS-HOBB | 0 | 526936 | YOAKUM_345 345.00 | 527896 | HOBBS_INT 7345.00 | 0 |  | 1 | 25SP | 2302 | 2532 | 0 |  | 20.9992 | 21.219 | [8 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | IMC Area Rebuild and Capacitors Additions | Reconductoring IMC #1 Tap-Intrepid West, IMC #1-Livingston Ridge, Intrepid West-Potash Junction, Byrd-Monument, Ponderosa Tap-Whitten, National Enrichment Plant-Targa 115 kV lines, Upgrading terminal equipment at Byrd 115 kV substation. A wave trap will | [53 empty] | 2017-06-01 | 2017-06-01
2013-AG2 | AFS8 | NCONV |  |  | FDNSLock-Blown up | FDNS-Blown up | 5 | 5 | 2013AG2AFS84L35520WP |  | HOBBS - YOAKUM_345 345.00 345KV CKT 1 | REL | SPS | SPS | SPS-YOGS | SPS-HOBB | 0 | 526936 | YOAKUM_345 345.00 | 527896 | HOBBS_INT 7345.00 | 0 |  | 1 | 20WP | 2388 | 2626 | 0 |  | 18.3083 | 18.6045 | [8 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | IMC Area Rebuild and Capacitors Additions | Reconductoring IMC #1 Tap-Intrepid West, IMC #1-Livingston Ridge, Intrepid West-Potash Junction, Byrd-Monument, Ponderosa Tap-Whitten, National Enrichment Plant-Targa 115 kV lines, Upgrading terminal equipment at Byrd 115 kV substation. A wave trap will | [53 empty] | 2017-06-01 | 2017-06-01
2013-AG2 | AFS8 | NCONV |  |  | FDNSLock-Blown up | FDNS-Blown up | 5 | 5 | 2013AG2AFS84L35520WP |  | HOBBS - YOAKUM_345 345.00 345KV CKT 1 | REL | SPS | SPS | SPS-YOGS | SPS-HOBB | 0 | 526936 | YOAKUM_345 345.00 | 527896 | HOBBS_INT 7345.00 | 0 |  | 1 | 20WP | 2388 | 2626 | 0 |  | 18.3083 | 18.6045 | [8 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | China Draw_Road Runner_SVC | New 200 Mvar SVC at China Draw 115kV; new 200 Mvar SVC at Road Runner 115kV | [53 empty] | 2017-06-01 | 2017-08-01
2013-AG2 | AFS8 | NCONV |  |  | FDNSLock-Blown up | FDNS-Blown up | 5 | 5 | 2013AG2AFS84L15520SP |  | HOBBS - YOAKUM_345 345.00 345KV CKT 1 | REL | SPS | SPS | SPS-YOGS | SPS-HOBB | 0 | 526936 | YOAKUM_345 345.00 | 527896 | HOBBS_INT 7345.00 | 0 |  | 1 | 20SP | 2302 | 2532 | 0 |  | 17.8496 | 19.1779 | [8 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | IMC Area Rebuild and Capacitors Additions | Reconductoring IMC #1 Tap-Intrepid West, IMC #1-Livingston Ridge, Intrepid West-Potash Junction, Byrd-Monument, Ponderosa Tap-Whitten, National Enrichment Plant-Targa 115 kV lines, Upgrading terminal equipment at Byrd 115 kV substation. A wave trap will | [53 empty] | 2017-06-01 | 2017-06-01
2013-AG2 | AFS8 | NCONV |  |  | FDNSLock-Blown up | FDNS-Blown up | 5 | 5 | 2013AG2AFS84L15520SP |  | HOBBS - YOAKUM_345 345.00 345KV CKT 1 | REL | SPS | SPS | SPS-YOGS | SPS-HOBB | 0 | 526936 | YOAKUM_345 345.00 | 527896 | HOBBS_INT 7345.00 | 0 |  | 1 | 20SP | 2302 | 2532 | 0 |  | 17.8496 | 19.1779 | [8 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | China Draw_Road Runner_SVC | New 200 Mvar SVC at China Draw 115kV; new 200 Mvar SVC at Road Runner 115kV | [53 empty] | 2017-06-01 | 2017-08-01
GI | GEN-2011-027 | [9 empty] | Hoskins - Dixon County 230kV Line Upgrade | U |  |  |  |  | 0 | 560347 |  | 640227 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | NPPD | Hoskins - Dixon County 230kV Line Upgrade | Increase clearances to accommodate 320MVA facility rating to address loading issues | [53 empty] | 2015-10-24 | 2015-10-24
2005-AG2 | AFS-3 | [9 empty] | HUGO POWER PLANT - VALLIANT 138KV CKT 1 | U | WFEC | AEPW |  |  | 0 | 521157 | HUGO PP4 138 | 510911 | VALIANT4 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WFEC | HUGO - VALLIANT 345KV CKT 1 | New 19 miles 345 KV | [53 empty] | 2012-07-01 | 2012-07-01
2005-AG2 | AFS-3 | [9 empty] | HUGO POWER PLANT - VALLIANT 138KV CKT 1 | U | WFEC | AEPW |  |  | 0 | 521157 | HUGO PP4 138 | 510911 | VALIANT4 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | Valliant 345 kV (AEP) | Vallient 345 KV line terminal | [53 empty] | 2012-07-01 | 2012-07-01
2005-AG2 | AFS-3 | [9 empty] | HUGO POWER PLANT 345/138KV TRANSFORMER CKT 1 | U | WFEC | AEPW |  |  | 1 | 521157 | HUGO PP4 138 | 520948 | HUGO PP4 138.00 | 521189 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WFEC | HUGO 345/138KV TRANSFORMER CKT 1 | New 345/138 kv Auto | [53 empty] | 2012-07-01 | 2012-07-01
GI | GEN-2004-008 | [9 empty] | Iatan - Platte City 161kV | U | KACP | KACP |  |  | 0 | 541350 |  | 541221 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | KACP | IATAN - PLATTE CITY 161KV CKT 1 | Platte City to Stranger Creek 161kV Ckt 1 Tap and addition of 4 miles 161kV transmission line to create Iatan - Platte City 161kV Ckt 1. | [13 empty] | 2006-05-01 | [39 empty] | 2010-03-18 | 2010-03-18
GI | GEN-2004-008 | [9 empty] | Iatan - Platte City 161kV | U | KACP | KACP |  |  | 0 | 541350 |  | 541221 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | KACP | IATAN - PLATTE CITY 161KV CKT 1 #2 | Terminal equipment planned to be upgraded to allow for 2000 Amps at Platte City | [13 empty] | 2006-05-01 | [39 empty] | 2009-12-15 | 2009-12-15
GI | GEN-2004-008 | [9 empty] | Iatan - Platte City 161kV | U | KACP | KACP |  |  | 0 | 541350 |  | 541221 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | KACP | PLATTE CITY 161KV | Install a 6 ohm reactor at Platte City substation on the Platte City-Iatan 161 kV line. | [13 empty] | 2006-05-01 | [39 empty] | 2010-12-12 | 2010-12-12
GI | GEN-2004-008 | [9 empty] | Iatan - Stranger Creek 161kV | U | KACP | KACP |  |  | 0 | 541350 |  | 541231 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | KACP | IATAN - STRANGER 161KV CKT 1 | Platte City to Stranger Creek 161kV Ckt 1 Tap and addition of 4 miles 161kV transmission line to create Iatan - Stranger Creek 161kV Ckt 1. | [13 empty] | 2006-05-01 | [39 empty] | 2010-03-18 | 2010-03-18
GI | GEN-2004-008 | [9 empty] | Iatan 345/161kV XFMR | U | KACP | KACP |  |  | 1 | 542982 |  | 541350 |  | 541150 |  | 11 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | KACP | IATAN - ST JOE 345KV CKT 1 | Relocate Iatan St. Joseph 345kV line | [13 empty] | 2006-05-01 | [39 empty] | 2009-12-15 | 2009-12-15
GI | GEN-2004-008 | [9 empty] | Iatan 345/161kV XFMR | U | KACP | KACP |  |  | 1 | 542982 |  | 541350 |  | 541150 |  | 11 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | KACP | Iatan 161 kV | Iatan 161kV substation work including the installation of a ring bus, three (3) 161kV circuit breakers, and associated equipment | [13 empty] | 2006-05-01 | [39 empty] | 2009-12-15 | 2009-12-15
GI | GEN-2004-008 | [9 empty] | Iatan 345/161kV XFMR | U | KACP | KACP |  |  | 1 | 542982 |  | 541350 |  | 541150 |  | 11 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | KACP | Iatan 345/161 kV transformer | Iatan 345/161 kV XFMR and Iatan 161 kV substation work | [13 empty] | 2006-05-01 | [39 empty] | 2009-12-15 | 2009-12-15
GI | GEN-2008-129 | [9 empty] | KC SOUTH - LONGVIEW 161 KV CKT 1 | U | MIPU | MIPU |  |  | 0 | 541245 |  | 541224 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MIPU | Longview - KC South 161kV Ckt 1 | Install new 161kV wavetrap in place of existing wavetrap | [13 empty] | 2011-01-05 | [39 empty] | 2011-01-31 | 2011-01-31
GI | GEN-2008-086N02 | [9 empty] | Kelly - Madison County 230kV Ckt 1 | U |  |  |  |  | 0 | 640540 |  | 640133 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | NPPD | Kelly - Madison County 230kV Ckt 1 | Raise structures and line clearances as necessary to re-rate the transmission line to 320 MVA | [53 empty] | 2014-10-01 | 2014-10-01
2006-AG1 | AFS-4 | [9 empty] | KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1 | U | OKGE |  |  |  | 1 | 514795 | KNOBHIL4 138 | 514794 | KNOBHIL269.0 | 515732 | KNOBHIL113.2 | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OKGE | KNOBHILL 138/69KV TRANSFORMER CKT 1 | Replace bus tie with 100MVA transformer | [53 empty] | 2006-06-01 | 2008-06-01
NA | SPONSORED | [9 empty] | LACYGNE - WEST GARDNER 345KV CKT 1 | U | KACP | KACP |  |  | 0 | 542981 | LACYGNE7 | 542965 | W.GRDNR7 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | KACP | LACYGNE - WEST GARDNER 345KV CKT 1 | KCPL Sponsored Project to Reconductor Line to be In-Service by 6/1/2006 | [53 empty] | 2006-06-01 | 2006-06-01
GI | GEN-2008-079 | [9 empty] | Lancer - North Judson Large 115KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539759 |  | 539771 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | Lancer - North Judson Large 115KV CKT 1 | Build appoximately 20 mile 115 kV line | [53 empty] | 2013-10-01 | 2016-06-01
GI | GEN-2008-079 | [9 empty] | Lancer - Spearville 345KV CKT 1 | U | MKEC | MKEC |  |  | 1 | 531469 |  | 539759 |  | 539960 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | Lancer - Spearville 345KV CKT 1 | Build appoximately 0.5 mile 345 kV line | [53 empty] | 2013-10-01 | 2016-06-01
GI | GEN-2008-079 | [9 empty] | Lancer 345/115/13.8kV Transformer CKT 1 | U | MKEC | MKEC |  |  | 1 | 531469 |  | 539759 |  | 539960 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | Lancer 345/115/13.8kV Transformer CKT 1 | Build new Lancer Substation with 345/115 kV transformer | [53 empty] | 2013-10-01 | 2016-06-01
GI | GEN-2010-057 | [9 empty] | LYONS - WHEATLAND 115KV CKT 1 #2 | U | WERE | WERE |  |  | 0 | 530620 | LYONS 3 115.00 | 533439 | WHEATLD3 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WERE | Wheatland 115 kV #2 | Install metering equipment at the Wheatland 115 kV substation for GEN-2010-057. | [13 empty] | 2011-12-27 | [39 empty] | 2012-12-31 | 2012-12-31
GI | GEN-2006-010 | [9 empty] | MANDEVILTP4 - SE TEXARKANA 138KV CKT 1 | U | AEPW | AEPW | SARK | TEXARK | 0 | 508105 | MANDEVILTP4 | 508078 | SETEXAR4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | MANDEVILTP4 - SE TEXARKANA 138KV CKT 1 | Build new Turk-SE Texarkana 138 kV line and add SE Texarkana 138 kV terminal. | [53 empty] | 2012-07-01 | 2012-07-01
GI | GEN-2006-010 | [9 empty] | MANDEVILTP4 - TURK 138KV CKT 1 | U | AEPW | AEPW | SARK | TEXARK | 0 | 507454 | TURK 4 138.00 | 508105 | MANDEVILTP4 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | SE TEXARKANA - TURK 138KV CKT 1 | Build new Turk-SE Texarkana 138 kV line and add SE Texarkana 138 kV terminal. | [53 empty] | 2012-07-01 | 2012-07-01
NA | SPONSORED | [9 empty] | MATHEWSON - TATONGA 345KV CKT 1 | U | OKGE | OKGE | ENID | ENID | 0 | 515497 |  | 515407 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OKGE | MATHEWSON - TATONGA 345KV CKT 1 | Build 345 kV line | [53 empty] | 2010-01-01 | 2010-01-01
GI | GEN-2006-010 | [9 empty] | MCNAB REC - TURK 115KV CKT 1 | U | AEPW | AEPW | SARK | SARKAECC | 0 | 507456 | HEMPSTD3 115.00 | 504122 | MCNAB 3 115.00 |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | MCNAB REC - Turk 115KV CKT 1 #2 (AEP) | Build a new two mile, 138kV, 1590 ACSR line section (operated at 115kV) from Turk Substation to the existing Okay-Hope 115kV line to form a Turk - Hope 115kV line. | [13 empty] | 2007-10-01 | [39 empty] | 2011-12-01 | 2011-12-01
GI | GEN-2006-044N | [9 empty] | NELIGH - PETERSBURG 115KV CKT 1 | U | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640444 |  | 640293 | NELIGH 7 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | NPPD | Neligh - Petersburg North 115kV Ckt 1 | Replace Breaker 1106, jumpers, & 115kV Switch 1106-D2; Replace Petersburg 115kV Substation main bus; Upgrade and replace transmission structures on 115kV lines TL1168 A & B to facilitate 100 degrees Centigrade line operation | [13 empty] | 2011-01-01 | [39 empty] | 2012-12-31 | 2012-12-31
NA | SPONSORED | [9 empty] | NORTHWEST - MATHEWSON 345KV CKT 1 | U | OKGE | OKGE | ENID | ENID | 0 | 514880 |  | 515497 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OKGE | MATHEWSON - NORTHWEST 345KV CKT 1 | Build 345 kV line | [53 empty] | 2010-01-01 | 2010-01-01
GI | GEN-2006-010 | [9 empty] | OKAY - TURK 138KV CKT 1 | U | AEPW | AEPW | SARK | SARK | 0 | 507454 | TURK 4 138.00 | 507428 | OKAY 4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | OKAY - TURK 138KV CKT 1 | Build a new two mile, 138kV, 1590 ACSR line section from Turk Substation to the existing Okay-Hope 115kV line and rebuild twelve miles of 115kV line to Okay Substation to 138kV, 1590 ACSR, to form a Turk - Okay 138kV line. | [13 empty] | 2007-10-01 | [39 empty] | 2011-12-01 | 2011-12-01
GI | GEN-2006-010 | [9 empty] | OKAY 138/69KV TRANSFORMER CKT 1 | U | AEPW | AEPW | SARK | SARK | 1 | 507428 | OKAY 4 138.00 | 507427 | OKAY 2 69.000 | 507442 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | OKAY 138/69KV TRANSFORMER CKT 1 | Replace three single-phase 115-69kV autotransformers with one 90 MVA, three-phase 138-69kV autotransformer and convert high side of station to 138kV. | [13 empty] | 2007-10-01 | [39 empty] | 2011-12-01 | 2011-12-01
2013-AG2 | AFS8 |  | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T1735525SP | TO->FROM | OMPA-MARLOW - RUSH SPRINGS TAP 138KV CKT 1 | REL | AEPW | OMPA | PSO_WESTERN | DOE | 0 | 511491 | RUSHSPT4 138.00 | 529307 | OMMARLO4 138.00 | 0 |  | 1 | 25SP | 106 | 106 | 0 | 101.8 | 101.7797 | 101.6992 | [7 empty] | CATEGORYB | SINGLE | COMANCHE TAP - OMPA-DUNCAN 840 138KV CKT 1 | 0 | 511494 | COMMTAP4 138.00 | 529304 | OMDUNCN4 138.00 | 0 |  | 1 |  |  |  | AEPW | OMPA-MARLOW - RUSH SPRINGS TAP 138KV CKT 1 | Rebuild 8.59 miles with 1533.3 ACSR/TW | 272 | 376 | 361 | 430 | 8.59 | 36 | 24 |  | 0.00317 | 0.03122 | 0.01007 | New limit will be a line switch | 8600000 | 2013-07-02 | [39 empty] | 2021-06-01 | 2021-06-01
GI | ASGI-2010-006 | [9 empty] | Osage - Shidler 138kV | U |  |  |  |  | 0 | 301369 |  | 510403 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | Osage - Shidler 138kV | Osage Substation:Replace Shidler 138kV line terminal primary and redundant relaying with SEL uProcessor based relays, install 3-138kV PTs, Install 1-138kV CB, Install metering, Install 2000A line Trap | [13 empty] | 2012-01-15 | [39 empty] | 2014-01-15 | 2014-01-15
2013-AG2 | AFS8 |  | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T915515SP | TO->FROM | PARK LANE - SEMINOLE 138KV CKT 1 | S | OKGE | OKGE | SHAWNEE | ARDMORE | 0 | 515044 | SEMINOL4 138.00 | 515178 | PARKLN 4 138.00 | 0 |  | 1 | 15SP | 287 | 287 | 0 | 97.6 | 97.5739 | 100.8296 | [7 empty] | CATEGORYB | SINGLE | SEMINOLE - VANOSTP4 138.00 138KV CKT 1 | 0 | 515044 | SEMINOL4 138.00 | 515531 | VANOSTP4 138.00 | 0 |  | 1 |  |  |  | OKGE | Park Lane - Seminole 138 kV Ckt Terminal Upgrades | Upgrade Park Lane 138 kV CTs and wave trap from 1200 amp to minimum 1600 amp. | 382.4 | 382.4 | [10 empty] | 143812 | 2015-01-01 | [39 empty] | 2015-06-01 | 2016-06-01
GI | ASGI-2010-006 | [9 empty] | Pawnee 138 kV | U |  |  |  |  | 0 | 300139 |  | 512749 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | GRDA | Pawnee 138 kV | New three breaker ring bus on the Cleveland-Stillwater 138kV line near Pawnee. Station will have terminals to Cleveland, Stillwater, and Fairfax. | [13 empty] | 2011-06-15 | [39 empty] | 2014-06-30 | 2014-06-01
GI | GEN-2010-057 | [9 empty] | Rice - Circle 230 kV Ckt 1 (MIDW portion) | U | WERE | MIDW |  |  | 0 | 530686 | RICECO 230.00 | 532871 | CIRCLE 6 230.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MIDW | Rice - Circle 230 kV Ckt 1 (MIDW portion) | ALL WORK REQUIRED TO CONVERT RICE - CIRCLE 115KV TO 230KV OPERATION. INCLUDES NEW 230KV 3 BREAKER RING BUS, AN EXTENSION OF THE 230KV FROM CURRENT RICE STATION TO NEW RICE SUBSTATION, AND ANY ADDITIONAL WORK REQUIRED FOR THE CONVERSION. | [13 empty] | 2011-12-27 | [39 empty] | 2012-11-07 | 2012-11-07
GI | GEN-2010-057 | [9 empty] | Rice - Circle 230 kV Ckt 1 (WR portion) | U | WERE | MIDW |  |  | 0 | 530686 | RICECO 230.00 | 532871 | CIRCLE 6 230.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MIDW | Rice - Circle 230 kV Ckt 1 (WR portion) | Install necessary equipment and perform line work at Circle substation to accommodate new bus position. | [13 empty] | 2012-01-15 | [39 empty] | 2012-11-29 | 2012-11-29
GI | GEN-2010-057 | [9 empty] | Rice - Lyons 115 kV Ckt 1 | U | MIDW | WERE |  |  | 0 | 530623 | RICE 3 115.00 | 530620 | LYONS 3 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MIDW | Rice - Lyons 115 kV Ckt 1 | Rebuild and extend 115 kV transmission line from existing Rice Co. substation to new Rice Co. substation, including engineering, surveying, and modification of existing easements as required. | [13 empty] | 2011-12-27 | [39 empty] | 2013-04-01 | 2013-04-01
GI | GEN-2010-057 | [9 empty] | Rice County 230/115 kV transformer Ckt 1 | U | MIDW | MIDW |  |  | 1 | 530686 | RICECO 230.00 | 530623 | RICE 3 115.00 | 530687 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MIDW | Rice County 230/115 kV transformer Ckt 1 | Install 230/115 kV transformer at Rice County. | [13 empty] | 2011-12-27 | [39 empty] | 2012-10-01 | 2012-10-01
2007-AG3 | AFS-9 | [9 empty] | RIVER ROAD - SAWYER 115KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | RIVER ROAD - SAWYER 115KV CKT 1 | Rebuild line | [53 empty] | 2009-12-01 | 2013-06-01
GI | ASGI-2010-006 | [9 empty] | Shidler 138 kV | U |  |  |  |  | 0 | 510403 |  | 301369 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | Shidler 138 kV | At Shidler 138kV: Replace existing 138kV CB at Shidler substation with 4 breaker ring. Provide Terminal for KAMO's 138kV line from Remington Station. Replace ground switch and circuit switcher, Move terminal for OG&E Osage 138kV line. Replace relay panels for OGE Osage and AEP Mound Road line terminals. Install 138kV meter transformers and meter at Shidler station. Install relay panel, line trap and RTU at Mound Road station for line to Shidler station.Required in mitigation of SPP Affected Facilities from new AECI GI project located near Burbank, OK. SPP STUDY ID - ASGI-2010-006 | [13 empty] | 2011-07-28 | [39 empty] | 2014-02-08 | 2014-02-08
GI | GEN-2003-004 | [9 empty] | Southwestern Station - Washita 138kV Ckt 1 | U |  |  |  |  | 0 | 521089 |  | 511477 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WFEC | Southwestern Station - Washita 138kV Ckt 1 | Expand Washita Switch Station from a 4-breaker to a 5-breaker 138kV ring bus & Construct 2.75 mile 138kV Transmission Line to the AEP/PSO Southwestern Station | [53 empty] | 2005-10-01 | 2005-10-01
GI | GEN-2003-004 | [9 empty] | Southwestern Station - Washita 138kV Ckt 1 (AEP) | U |  |  |  |  | 0 | 521089 |  | 511477 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | Southwestern Station - Washita 138kV Ckt 1 (AEP) | Expand Southwestern Station for termination of WFEC 2.75 mile 138kV Transmission Line from Washita Switch Station | [53 empty] | 2005-10-01 | 2005-10-01
2005-AG2 | AFS-3 | [9 empty] | SUB 110 - ORONOGO JCT. - SUB 167 - RIVERTON 161KV CKT 1 | U | EMDE | EMDE |  |  | 0 | 547469 | RIV167 5 161 | 547467 | ORO110 5 161 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | EMDE | SUB 110 - ORONOGO JCT. - SUB 452 - RIVERTON 161KV CKT 1 | Reconductor Oronogo 59467 to Riverton 59469 with Bundled 556 ACSR | [53 empty] | 2011-06-01 | 2011-06-01
GI | GEN-2006-010 | [9 empty] | SUGAR HILL - TURK 138KV CKT 1 | U | AEPW | AEPW | SARK | TEXARK | 0 | 507454 | TURK 4 138.00 | 508080 | SUGARHL4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | SUGAR HILL - TURK 138KV CKT 1 | Build new 24 mile Turk - Sugar Hill 138 kV line and add Sugar Hill 138 kV terminal. | [13 empty] | 2007-10-01 | [39 empty] | 2010-12-16 | 2010-12-16
2013-AG2 | AFS8 |  | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T2695025SP | FROM->TO | SUNDOWN INTERCHANGE (WH XDS70381) 230/115/13.8KV TRANSFORMER CKT 1 | REL | SPS | SPS | SPS-CNPL | SPS-CNPL | 1 | 526435 | SUNDOWN 6230.00 | 526434 | SUNDOWN 3115.00 | 526432 | SUNDOWN_TR1113.800 | 1 | 25SP | 187 | 187 | 0 | 106.1 | 106.0567 | 106.213 | [7 empty] | CATEGORYB | SINGLE | LEA COUNTY REC-PLAINS INTERCHANGE - YOAKUM COUNTY INTERCHANGE 115KV CKT 1 | 0 | 526928 | LE-PLNSINT 3115.00 | 526934 | YOAKUM 3115.00 | 0 |  | 1 |  |  |  | SPS | SUNDOWN INTERCHANGE (WH XDS70381) 230/115/13.8KV TRANSFORMER CKT 1 | Upgrade transformer to 250 MVA. | [53 empty] | 2023-06-01 | 2023-06-01
GI | GEN-2011-040 | [9 empty] | Sunnyside to tap on Pooleville - Ratliff 138kV Ckt 1 | U |  |  |  |  | 0 | 515561 |  | 515135 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OKGE | Sunnyside to tap on Pooleville - Ratliff 138kV Ckt 1 | Rebuild 0.75 mi of 138kV Transmission Line DBL CKT | [53 empty] | 2014-06-30 | 2014-06-01
2009-AGP2 | AFS-6 | [9 empty] | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | U | WFEC | WFEC | AEP-OP | AEP-OP | 2 | 521065 | TALOGA 4 138.00 | 521064 | TALOGA 2 69.000 | 521178 | TLGTERT 13.800 | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WFEC | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | Auto XFMR 56 to 112MVA | 112 | 112 | 112 | 112 |  | 24 | 24 | [46 empty] | 2010-10-01 | 2013-06-01
NA | SPONSORED | [9 empty] | TATONGA - WOODWARD 345KV CKT 1 | U | OKGE | OKGE | ENID | ENID | 0 | 515407 |  | 515375 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OKGE | TATONGA - WOODWARD 345KV CKT 1 | Build 345 kV line | [53 empty] | 2010-01-01 | 2010-01-01
2013-AG2 | AFS8 | NCONV |  |  | FDNSLock-Blown up | FDNS-Blown up | 5 | 0 | 2013AG2AFS84L65025WP |  | TUCO INTERCHANGE - YOAKUM_345 345.00 345KV CKT 1 | REL | SPS | SPS | SPS-CNPL | SPS-YOGS | 0 | 525832 | TUCO_INT 7345.00 | 526936 | YOAKUM_345 345.00 | 0 |  | 1 | 25WP | 2388 | 2626 | 0 |  | 19.3082 | 19.3321 | [8 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | China Draw_Road Runner_SVC | New 200 Mvar SVC at China Draw 115kV; new 200 Mvar SVC at Road Runner 115kV | [53 empty] | 2017-06-01 | 2017-08-01
2013-AG2 | AFS8 | NCONV |  |  | FDNSLock-Blown up | FDNS-Blown up | 5 | 0 | 2013AG2AFS84L65025WP |  | TUCO INTERCHANGE - YOAKUM_345 345.00 345KV CKT 1 | REL | SPS | SPS | SPS-CNPL | SPS-YOGS | 0 | 525832 | TUCO_INT 7345.00 | 526936 | YOAKUM_345 345.00 | 0 |  | 1 | 25WP | 2388 | 2626 | 0 |  | 19.3082 | 19.3321 | [8 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | IMC Area Rebuild and Capacitors Additions | Reconductoring IMC #1 Tap-Intrepid West, IMC #1-Livingston Ridge, Intrepid West-Potash Junction, Byrd-Monument, Ponderosa Tap-Whitten, National Enrichment Plant-Targa 115 kV lines, Upgrading terminal equipment at Byrd 115 kV substation. A wave trap will | [53 empty] | 2017-06-01 | 2017-06-01
2013-AG2 | AFS8 | NCONV |  |  | FDNSLock-Blown up | FDNS-Blown up | 5 | 5 | 2013AG2AFS84L85525WP |  | TUCO INTERCHANGE - YOAKUM_345 345.00 345KV CKT 1 | REL | SPS | SPS | SPS-CNPL | SPS-YOGS | 0 | 525832 | TUCO_INT 7345.00 | 526936 | YOAKUM_345 345.00 | 0 |  | 1 | 25WP | 2388 | 2626 | 0 |  | 18.7787 | 19.166 | [8 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | China Draw_Road Runner_SVC | New 200 Mvar SVC at China Draw 115kV; new 200 Mvar SVC at Road Runner 115kV | [53 empty] | 2017-06-01 | 2017-08-01
2013-AG2 | AFS8 | NCONV |  |  | FDNSLock-Blown up | FDNS-Blown up | 5 | 5 | 2013AG2AFS84L85525WP |  | TUCO INTERCHANGE - YOAKUM_345 345.00 345KV CKT 1 | REL | SPS | SPS | SPS-CNPL | SPS-YOGS | 0 | 525832 | TUCO_INT 7345.00 | 526936 | YOAKUM_345 345.00 | 0 |  | 1 | 25WP | 2388 | 2626 | 0 |  | 18.7787 | 19.166 | [8 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | IMC Area Rebuild and Capacitors Additions | Reconductoring IMC #1 Tap-Intrepid West, IMC #1-Livingston Ridge, Intrepid West-Potash Junction, Byrd-Monument, Ponderosa Tap-Whitten, National Enrichment Plant-Targa 115 kV lines, Upgrading terminal equipment at Byrd 115 kV substation. A wave trap will | [53 empty] | 2017-06-01 | 2017-06-01
2013-AG2 | AFS8 | NCONV |  |  | FDNSLock-Blown up | FDNS-Blown up | 5 | 0 | 2013AG2AFS84L55025SP |  | TUCO INTERCHANGE - YOAKUM_345 345.00 345KV CKT 1 | REL | SPS | SPS | SPS-CNPL | SPS-YOGS | 0 | 525832 | TUCO_INT 7345.00 | 526936 | YOAKUM_345 345.00 | 0 |  | 1 | 25SP | 2302 | 2532 | 0 |  | 20.0671 | 20.5661 | [8 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | China Draw_Road Runner_SVC | New 200 Mvar SVC at China Draw 115kV; new 200 Mvar SVC at Road Runner 115kV | [53 empty] | 2017-06-01 | 2017-08-01
2013-AG2 | AFS8 | NCONV |  |  | FDNSLock-Blown up | FDNS-Blown up | 5 | 0 | 2013AG2AFS84L55025SP |  | TUCO INTERCHANGE - YOAKUM_345 345.00 345KV CKT 1 | REL | SPS | SPS | SPS-CNPL | SPS-YOGS | 0 | 525832 | TUCO_INT 7345.00 | 526936 | YOAKUM_345 345.00 | 0 |  | 1 | 25SP | 2302 | 2532 | 0 |  | 20.0671 | 20.5661 | [8 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | IMC Area Rebuild and Capacitors Additions | Reconductoring IMC #1 Tap-Intrepid West, IMC #1-Livingston Ridge, Intrepid West-Potash Junction, Byrd-Monument, Ponderosa Tap-Whitten, National Enrichment Plant-Targa 115 kV lines, Upgrading terminal equipment at Byrd 115 kV substation. A wave trap will | [53 empty] | 2017-06-01 | 2017-06-01
2013-AG2 | AFS8 | NCONV |  |  | FDNSLock-Blown up | FDNS-Blown up | 5 | 5 | 2013AG2AFS84L25520WP |  | TUCO INTERCHANGE - YOAKUM_345 345.00 345KV CKT 1 | REL | SPS | SPS | SPS-CNPL | SPS-YOGS | 0 | 525832 | TUCO_INT 7345.00 | 526936 | YOAKUM_345 345.00 | 0 |  | 1 | 20WP | 2388 | 2626 | 0 |  | 16.1948 | 17.8992 | [8 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | China Draw_Road Runner_SVC | New 200 Mvar SVC at China Draw 115kV; new 200 Mvar SVC at Road Runner 115kV | [53 empty] | 2017-06-01 | 2017-08-01
2013-AG2 | AFS8 | NCONV |  |  | FDNSLock-Blown up | FDNS-Blown up | 5 | 5 | 2013AG2AFS84L25520WP |  | TUCO INTERCHANGE - YOAKUM_345 345.00 345KV CKT 1 | REL | SPS | SPS | SPS-CNPL | SPS-YOGS | 0 | 525832 | TUCO_INT 7345.00 | 526936 | YOAKUM_345 345.00 | 0 |  | 1 | 20WP | 2388 | 2626 | 0 |  | 16.1948 | 17.8992 | [8 empty] | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | IMC Area Rebuild and Capacitors Additions | Reconductoring IMC #1 Tap-Intrepid West, IMC #1-Livingston Ridge, Intrepid West-Potash Junction, Byrd-Monument, Ponderosa Tap-Whitten, National Enrichment Plant-Targa 115 kV lines, Upgrading terminal equipment at Byrd 115 kV substation. A wave trap will | [53 empty] | 2017-06-01 | 2017-06-01
2013-AG2 | AFS8 |  | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T11875025SP | FROM->TO | TUCO INTERCHANGE (GE M102345) 230/115/13.2KV TRANSFORMER CKT 1 | CP | SPS | SPS | SPS-CNPL | SPS-CNPL | 1 | 525830 | TUCO_INT 6230.00 | 525828 | TUCO_INT 3115.00 | 525821 | TUCO_TR4 113.200 | 1 | 25SP | 242 | 252 | 0 | 112.7 | 112.6653 | 114.5313 | [7 empty] | CATEGORYB | SINGLE | TUCO INTERCHANGE (ENRCO 136401) 230/115/13.2KV TRANSFORMER CKT 2 | 1 | 525828 | TUCO_INT 3115.00 | 525830 | TUCO_INT 6230.00 | 525819 | TUCO_TR3 113.200 | 2 |  |  |  | SPS | TUCO INTERCHANGE (GE M102345) 230/115/13.2KV TRANSFORMER CKT 1 | Replace 1st 230/115 kV transformer at Tuco with 230/115 kV 288 MVA transformer. | [53 empty] | 2021-06-01 | 2021-06-01
GI | GEN-2006-010 | [9 empty] | TURK 138/115KV TRANSFORMER CKT 1 | U | AEPW |  | SARK |  | 1 | 507454 | TURK 4 138.00 | 507456 | HEMPSTD3 115.00 | 507458 | HEMP1 1 13.800 | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | TURK 138/115KV TRANSFORMER CKT 1 | Build Turk 138-115 kV station and relocate autotransformer (and spare) from Patterson to this new Turk station | [13 empty] | 2007-10-01 | [39 empty] | 2011-12-01 | 2011-12-01
GI | GEN-2010-051 | [9 empty] | Twin Church - Dixon County 230kV Line Upgrade | U |  |  |  |  | 0 | 560347 |  | 640386 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | NPPD | Twin Church - Dixon County 230kV Line Upgrade | Increase clearances to accommodate 320MVA facility rating | [53 empty] | 2015-10-24 | 2015-10-24
2013-AG2 | AFS8 |  | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T2485025SP | FROM->TO | WOLFFORTH INTERCHANGE (WH 7001668) 230/115/13.2KV TRANSFORMER CKT 1 | REL | SPS | SPS | SPS-CNPL | SPS-CNPL | 1 | 526525 | WOLFFORTH 6230.00 | 526524 | WOLFFORTH 3115.00 | 526522 | WOLFRTH_TR1113.200 | 1 | 25SP | 120 | 154 | 0 | 119.6 | 119.5963 | 120.1406 | [7 empty] | CATEGORYB | SINGLE | CARLISLE INTERCHANGE - LP-DOUD_TP 3115.00 115KV CKT 1 | 0 | 526160 | CARLISLE 3115.00 | 526162 | LP-DOUD_TP 3115.00 | 0 |  | 1 |  |  |  | SPS | WOLFFORTH INTERCHANGE (WH 7001668) 230/115/13.2KV TRANSFORMER CKT 1 | Upgrade transformer to 250 MVA. | [53 empty] | 2024-06-01 | 2024-06-01
2013-AG2 | AFS8 |  | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T11945025SP | FROM->TO | WOLFFORTH INTERCHANGE (WH 7001668) 230/115/13.2KV TRANSFORMER CKT 1 | REL | SPS | SPS | SPS-CNPL | SPS-CNPL | 1 | 526525 | WOLFFORTH 6230.00 | 526524 | WOLFFORTH 3115.00 | 526522 | WOLFRTH_TR1113.200 | 1 | 25SP | 120 | 154 | 0 | 112.3 | 112.2997 | 112.3793 | [7 empty] | CATEGORYB | SINGLE | CARLISLE INTERCHANGE (WH XHS70711) 230/115/13.2KV TRANSFORMER CKT 1 | 1 | 526160 | CARLISLE 3115.00 | 526161 | CARLISLE 6230.00 | 526157 | CRLSLE_TR1 113.200 | 1 |  |  |  | SPS | WOLFFORTH INTERCHANGE (WH 7001668) 230/115/13.2KV TRANSFORMER CKT 1 | Upgrade transformer to 250 MVA. | [53 empty] | 2024-06-01 | 2024-06-01
2013-AG2 | AFS8 |  | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T2565025SP | FROM->TO | WOLFFORTH INTERCHANGE (WH 7001668) 230/115/13.2KV TRANSFORMER CKT 1 | REL | SPS | SPS | SPS-CNPL | SPS-CNPL | 1 | 526525 | WOLFFORTH 6230.00 | 526524 | WOLFFORTH 3115.00 | 526522 | WOLFRTH_TR1113.200 | 1 | 25SP | 120 | 154 | 0 | 105.1 | 105.1382 | 105.5071 | [7 empty] | CATEGORYB | SINGLE | ALLEN SUB - LUBBOCK SOUTH INTERCHANGE 115KV CKT 1 | 0 | 526213 | ALLEN 3115.00 | 526268 | LUBBCK_STH 3115.00 | 0 |  | 1 |  |  |  | SPS | WOLFFORTH INTERCHANGE (WH 7001668) 230/115/13.2KV TRANSFORMER CKT 1 | Upgrade transformer to 250 MVA. | [53 empty] | 2024-06-01 | 2024-06-01
NA | SPONSORED | [9 empty] | WOODWARD - IODINE 138KV CKT 1 | U | OKGE | OKGE | ENID | ENID | 0 | 515376 |  | 514796 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OKGE | WOODWARD - IODINE 138KV CKT 1 | Tap Iodine to Woodward 138 kV line | [53 empty] | 2010-01-01 | 2010-01-01
NA | SPONSORED | [9 empty] | WOODWARD - WOODWARD EHV 138KV CKT 1 | U | OKGE | OKGE | ENID | ENID | 0 | 515376 |  | 514785 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OKGE | WOODWARD - WOODWARD EHV 138KV CKT 1 | Build .5 miles of 138 kV and install terminal equipment | [53 empty] | 2010-01-01 | 2010-01-01
NA | SPONSORED | [9 empty] | WOODWARD - WOODWARD EHV 138KV CKT 2 | U | OKGE | OKGE | ENID | ENID | 0 | 515376 |  | 514785 |  |  |  | 2 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OKGE | WOODWARD - WOODWARD EHV 138KV CKT 2 | Build .5 miles of 138 kV and install terminal equipment | [53 empty] | 2010-01-01 | 2010-01-01
NA | SPONSORED | [9 empty] | WOODWARD 345/138KV TRANSFORMER CKT 1 | U | OKGE | OKGE | ENID | ENID | 1 | 515375 |  | 515376 |  | 515795 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OKGE | WOODWARD 345/138KV TRANSFORMER CKT 1 | Install 345/138 kV XF | [53 empty] | 2010-01-01 | 2010-01-01

## tblAllFacilityLog<100%
STUDYDES | STUDYDES2 | EVENTTYPE | AssessmentSOLUTIONTYPE | AssessmenFDNS-TERMINATION | SOLUTIONTYPE | FDNS-TERMINATION | GROUP | SCENARIO | FGName | DIRECTION | FacilityName | FacilityUpgradeCode | ModelArea1 | ModelArea2 | FZONENAME | TZONENAME | MONTFLAG | MONTFB | MONTFNAME | MONTTB1 | MONTTNAME1 | MONTTB2 | MONTTNAME2 | MONTCKT | Case | RATEA | RATEB | RATEC | Assessment Loading | BaseCaseLoading | TransferCaseLoading | NameOfBusWithMonitoredVoltage | Assessment Voltage | BaseCaseVoltage | TransferCaseVoltage | VINIT | VMIN | VMAX | CATEGORY | CONTTYPE | CONTNAME | CONTXFMRFLAG | CONTFB | CONTFNAME | CONTTB1 | CONTTNAME1 | CONTTB2 | CONTTNAME2 | CONTCKT | TransmissionProviderCommentsNotes | RequiredRateB | TransmissionOwnerComments | OwnerDesignation | UpgradeName | UpgradeComponentWithinFacility | NewSummerA | NewSummerB | NewOtherA | NewOtherB | DistToConstruct | TotalLead | ConstructionLeadOnly | NewOrConstructWhileEnergized | NewR | NewX | NewB | CommentsRegardingUpgradeRequirements | NewCost | EffDate | NetPlantDate | ReusableEx_GrossValue | ReusableEx_NetValue | Reusable_EndofDepr | SalvageValue | NewCostWhileExpediting | EffDateExpedited | StartDeprExpedited | EndDeprExpedited | NetPlantDateExpedited | ReusableEx_GrossExpedited | ReusableEx_NetExpedited | Reusable_EndofDeprExpedited | SalvageValueExpedited | Generation 1 Owner & Unit (Name) | Generation 1 Redispatch Cost ($) | Generation 1 Redispatch Date (M/D/Y) | Generation 2 Owner & Unit (Name) | Generation 2 Redispatch Cost ($) | Generation 2 Redispatch Date (M/D/Y) | Generation 3 Owner & Unit (Name) | Generation 3 Redispatch Cost ($) | Generation 3 Redispatch Date (M/D/Y) | ActualCompletion | ActualNewCost | ActualNetPlantDate | ActualReusableEx_GrossValue | ActualReusableEx_NetValue | ActualReusable_EndofDepr | ActualSalvageValue | Actual_NewCostWhileExpediting | Actual_StartDeprExp | Actual_EndDeprExp | Actual_NetPlantDateExpedited | ActualReusableEx_GrossExpedited | ActualReusableEx_NetExpedited | ActualReusable_EndofDeprExpedited | Actual_SalvageValueExpedited | SPPReliabilityDate | DUN | EOC | EarliestDate
2013-AG2 | AFS8 | INVALID | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T1305025SP | TO->FROM | CARNEGIE - SOUTHWESTERN STATION 138KV CKT 1 | E | AEPW | AEPW | PSO_WESTERN | PSO_WESTERN | 0 | 511477 | S.W.S.-4 138.00 | 511445 | CARNEG-4 138.00 | 0 |  | 1 | 25SP | 136 | 136 | 0 | 99.8 | 99.8082 | 97.6939 | [7 empty] | CATEGORYB | SINGLE | LAWTON 112TH & WEST GORE - LAWTON AIRGAS TAP 138KV CKT 1 | 0 | 511488 | 112GORE4 138.00 | 511510 | LAIRGST4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 |  | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T745516SP | FROM->TO | DUNCAN - DUNCHERTP4 138.00 138KV CKT 1 | E | AEPW | AEPW | PSO_WESTERN | PSO_WESTERN | 0 | 511453 | DUNCAN-4 138.00 | 511552 | DUNCHERTP4 138.00 | 0 |  | 1 | 16SP | 96 | 99 | 0 | 97.6 | 97.5977 | 97.6 | [7 empty] | CATEGORYB | SINGLE | CORNVILLE - RUSH SPRINGS NATURAL GAS TAP 138KV CKT 1 | 0 | 511449 | CORNVIL4 138.00 | 511492 | RUSHNGT4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 |  | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T255525SP | FROM->TO | ELK CITY (ELKCTY-4) 138/69/13.8KV TRANSFORMER CKT 1 | E | AEPW | AEPW | PSO_WESTERN | PSO_WESTERN | 1 | 511458 | ELKCTY-4 138.00 | 511459 | ELKCTY-2 69.000 | 511493 | ELKC4-1 13.800 | 1 | 25SP | 68 | 89 | 0 | 97.5 | 97.4634 | 98 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T10475015WP | FROM->TO | FITZHUGH 161/13.8KV TRANSFORMER CKT 1 | E | AEPW | AEPW | GREENWD AECC | GREENWD AECC | 0 | 503901 | FITZ_ST1 1 13.800 | 503902 | FITZHUGH 5 161.00 | 0 |  | 1 | 15WP | 65 | 65 | 0 |  | 99.1736 | 99.1635 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 44 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T11015016WP | FROM->TO | FITZHUGH 161/13.8KV TRANSFORMER CKT 1 | E | AEPW | AEPW | GREENWD AECC | GREENWD AECC | 0 | 503901 | FITZ_ST1 1 13.800 | 503902 | FITZHUGH 5 161.00 | 0 |  | 1 | 16WP | 65 | 65 | 0 |  | 98.89 | 98.9351 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 44 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T11825020WP | FROM->TO | FITZHUGH 161/13.8KV TRANSFORMER CKT 1 | E | AEPW | AEPW | GREENWD AECC | GREENWD AECC | 0 | 503901 | FITZ_ST1 1 13.800 | 503902 | FITZHUGH 5 161.00 | 0 |  | 1 | 20WP | 65 | 65 | 0 |  | 97.0491 | 97.1059 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 47 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T17575025WP | FROM->TO | FITZHUGH 161/13.8KV TRANSFORMER CKT 1 | E | AEPW | AEPW | GREENWD AECC | GREENWD AECC | 0 | 503901 | FITZ_ST1 1 13.800 | 503902 | FITZHUGH 5 161.00 | 0 |  | 1 | 25WP | 65 | 65 | 0 |  | 95.6216 | 95.7584 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 48 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 |  | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T1155025SP | FROM->TO | NORTHEAST STATION - WATOVA 138KV CKT 1 | E | AEPW | AEPW | PSO_NORTHERN | TS-KAMO | 0 | 510396 | N.E.S.-4 138.00 | 510384 | WATOVA 4 138.00 | 0 |  | 1 | 25SP | 191 | 199 | 0 | 96 | 95.9749 | 96.8 | [7 empty] | CATEGORYB | SINGLE | NORTHEAST STATION - RICE CREEK 138KV CKT 1 | 0 | 510385 | RICE CK4 138.00 | 510396 | N.E.S.-4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 |  | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T1105025SP | TO->FROM | PRATTVILLE - SAND SPRINGS 138KV CKT 1 | E | AEPW | AEPW | PSO_TULSA | PSO_TULSA | 0 | 509815 | S.S.---4 138.00 | 509758 | PRATTV-4 138.00 | 0 |  | 1 | 25SP | 265 | 286 | 0 | 99.5 | 99.4856 | 98.9 | [7 empty] | CATEGORYB | SINGLE | EXPGLNT4 138.00 - RIVERSIDE STATION 138KV CKT 1 | 0 | 509783 | R.S.S.-4 138.00 | 515473 | EXPGLNT4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 |  | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T1715025SP | TO->FROM | PRATTVILLE - SAND SPRINGS 138KV CKT 1 | E | AEPW | AEPW | PSO_TULSA | PSO_TULSA | 0 | 509815 | S.S.---4 138.00 | 509758 | PRATTV-4 138.00 | 0 |  | 1 | 25SP | 265 | 286 | 0 | 97.5 | 97.4706 | 96.8 | [7 empty] | CATEGORYB | SINGLE | BEELINE - EXPGLNT4 138.00 138KV CKT 1 | 0 | 515247 | BEELINE4 138.00 | 515473 | EXPGLNT4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 |  | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T1025520SP | TO->FROM | OMPA-MARLOW - RUSH SPRINGS TAP 138KV CKT 1 | E | AEPW | OMPA | PSO_WESTERN | DOE | 0 | 511491 | RUSHSPT4 138.00 | 529307 | OMMARLO4 138.00 | 0 |  | 1 | 20SP | 106 | 106 | 0 | 95.2 | 95.2343 | 95.3 | [7 empty] | CATEGORYB | SINGLE | COMANCHE TAP - OMPA-DUNCAN 840 138KV CKT 1 | 0 | 511494 | COMMTAP4 138.00 | 529304 | OMDUNCN4 138.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2021-06-01
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T11305015SP | FROM->TO | 4MER 1&4 138.00 138/16.5KV TRANSFORMER CKT 1 | E | AMMO | AMMO | AMRNMO | AMRNMO | 0 | 345132 | 1MER 1 16.500 | 345123 | 4MER 1&4 138.00 | 0 |  | 1 | 15SP | 150 | 150 | 150 |  | 98.788 | 98.788 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 25 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T11915515SP | FROM->TO | 4MER 1&4 138.00 138/16.5KV TRANSFORMER CKT 1 | E | AMMO | AMMO | AMRNMO | AMRNMO | 0 | 345132 | 1MER 1 16.500 | 345123 | 4MER 1&4 138.00 | 0 |  | 1 | 15SP | 150 | 150 | 150 |  | 98.7877 | 98.7877 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 25 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T18425516SP | FROM->TO | 4MER 1&4 138.00 138/16.5KV TRANSFORMER CKT 1 | E | AMMO | AMMO | AMRNMO | AMRNMO | 0 | 345132 | 1MER 1 16.500 | 345123 | 4MER 1&4 138.00 | 0 |  | 1 | 16SP | 150 | 150 | 150 |  | 98.7971 | 98.7971 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 25 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T17485016SP | FROM->TO | 4MER 1&4 138.00 138/16.5KV TRANSFORMER CKT 1 | E | AMMO | AMMO | AMRNMO | AMRNMO | 0 | 345132 | 1MER 1 16.500 | 345123 | 4MER 1&4 138.00 | 0 |  | 1 | 16SP | 150 | 150 | 150 |  | 98.788 | 98.788 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 26 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T18385020SP | FROM->TO | 4MER 1&4 138.00 138/16.5KV TRANSFORMER CKT 1 | E | AMMO | AMMO | AMRNMO | AMRNMO | 0 | 345132 | 1MER 1 16.500 | 345123 | 4MER 1&4 138.00 | 0 |  | 1 | 20SP | 150 | 150 | 150 |  | 98.788 | 98.788 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 27 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T19165520SP | FROM->TO | 4MER 1&4 138.00 138/16.5KV TRANSFORMER CKT 1 | E | AMMO | AMMO | AMRNMO | AMRNMO | 0 | 345132 | 1MER 1 16.500 | 345123 | 4MER 1&4 138.00 | 0 |  | 1 | 20SP | 150 | 150 | 150 |  | 98.788 | 98.788 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 27 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T26365025SP | FROM->TO | 4MER 1&4 138.00 138/16.5KV TRANSFORMER CKT 1 | E | AMMO | AMMO | AMRNMO | AMRNMO | 0 | 345132 | 1MER 1 16.500 | 345123 | 4MER 1&4 138.00 | 0 |  | 1 | 25SP | 150 | 150 | 150 |  | 98.788 | 98.788 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 44 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T26345025SP | FROM->TO | 4MER 1&4 138.00 138/16.5KV TRANSFORMER CKT 1 | E | AMMO | AMMO | AMRNMO | AMRNMO | 0 | 345132 | 1MER 1 16.500 | 345123 | 4MER 1&4 138.00 | 0 |  | 1 | 25SP | 150 | 150 | 150 |  | 98.788 | 98.788 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 30 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T26355025SP | FROM->TO | 4MER 1&4 138.00 138/16.5KV TRANSFORMER CKT 1 | E | AMMO | AMMO | AMRNMO | AMRNMO | 0 | 345132 | 1MER 1 16.500 | 345123 | 4MER 1&4 138.00 | 0 |  | 1 | 25SP | 150 | 150 | 150 |  | 98.788 | 98.788 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 43 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T26335025SP | FROM->TO | 4MER 1&4 138.00 138/16.5KV TRANSFORMER CKT 1 | E | AMMO | AMMO | AMRNMO | AMRNMO | 0 | 345132 | 1MER 1 16.500 | 345123 | 4MER 1&4 138.00 | 0 |  | 1 | 25SP | 150 | 150 | 150 |  | 98.788 | 98.7879 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 29 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T9065025SP | FROM->TO | RODEMACHER 230/22.0KV TRANSFORMER CKT 1 | E | CLEC | CLEC | CLE_CENTRAL | CLE_CENTRAL | 0 | 501811 | G1NESBIT 22.000 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | 25SP | 476 | 476 | 0 | 98.4 | 98.3716 | 98.4 | [7 empty] | CATEGORYB | SINGLE | COLFAX - RODEMACHER 230KV CKT 1 | 0 | 500200 | COLFAX 6 230.00 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T11685525SP | FROM->TO | RODEMACHER 230/22.0KV TRANSFORMER CKT 1 | E | CLEC | CLEC | CLE_CENTRAL | CLE_CENTRAL | 0 | 501811 | G1NESBIT 22.000 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | 25SP | 476 | 476 | 0 | 98.3 | 98.2856 | 98.2 | [7 empty] | CATEGORYB | SINGLE | COLFAX - RODEMACHER 230KV CKT 1 | 0 | 500200 | COLFAX 6 230.00 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T7995025SP | FROM->TO | RODEMACHER 230/22.0KV TRANSFORMER CKT 1 | E | CLEC | CLEC | CLE_CENTRAL | CLE_CENTRAL | 0 | 501811 | G1NESBIT 22.000 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | 25SP | 476 | 476 | 0 | 97.2 | 97.232 | 97.2 | [7 empty] | CATEGORYB | SINGLE | COLFAX - MONTGOMERY 230KV CKT 1 | 0 | 337304 | 6MONTGY 230.00 | 500200 | COLFAX 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T10545525SP | FROM->TO | RODEMACHER 230/22.0KV TRANSFORMER CKT 1 | E | CLEC | CLEC | CLE_CENTRAL | CLE_CENTRAL | 0 | 501811 | G1NESBIT 22.000 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | 25SP | 476 | 476 | 0 | 97.2 | 97.1549 | 97.1 | [7 empty] | CATEGORYB | SINGLE | COLFAX - MONTGOMERY 230KV CKT 1 | 0 | 337304 | 6MONTGY 230.00 | 500200 | COLFAX 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T11665525SP | FROM->TO | RODEMACHER 230/22.0KV TRANSFORMER CKT 1 | E | CLEC | CLEC | CLE_CENTRAL | CLE_CENTRAL | 0 | 501811 | G1NESBIT 22.000 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | 25SP | 476 | 476 | 0 | 96.3 | 96.3002 | 96.3 | [7 empty] | CATEGORYB | SINGLE | COCODRIE - VILLE PLATTE 230KV CKT 1 | 0 | 500190 | COCODR 6 230.00 | 500880 | VILPLT 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T9045025SP | FROM->TO | RODEMACHER 230/22.0KV TRANSFORMER CKT 1 | E | CLEC | CLEC | CLE_CENTRAL | CLE_CENTRAL | 0 | 501811 | G1NESBIT 22.000 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | 25SP | 476 | 476 | 0 | 96.2 | 96.2386 | 96.2 | [7 empty] | CATEGORYB | SINGLE | COCODRIE - VILLE PLATTE 230KV CKT 1 | 0 | 500190 | COCODR 6 230.00 | 500880 | VILPLT 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T11745525SP | FROM->TO | RODEMACHER 230/22.0KV TRANSFORMER CKT 1 | E | CLEC | CLEC | CLE_CENTRAL | CLE_CENTRAL | 0 | 501811 | G1NESBIT 22.000 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | 25SP | 476 | 476 | 0 | 95.7 | 95.6739 | 95.7 | [7 empty] | CATEGORYB | SINGLE | EAST LEESVILLE - RODEMACHER 230KV CKT 1 | 0 | 500280 | ELEESV 6 230.00 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T9115025SP | FROM->TO | RODEMACHER 230/22.0KV TRANSFORMER CKT 1 | E | CLEC | CLEC | CLE_CENTRAL | CLE_CENTRAL | 0 | 501811 | G1NESBIT 22.000 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | 25SP | 476 | 476 | 0 | 95.6 | 95.5975 | 95.6 | [7 empty] | CATEGORYB | SINGLE | EAST LEESVILLE - RODEMACHER 230KV CKT 1 | 0 | 500280 | ELEESV 6 230.00 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T11825525SP | FROM->TO | RODEMACHER 230/22.0KV TRANSFORMER CKT 1 | E | CLEC | CLEC | CLE_CENTRAL | CLE_CENTRAL | 0 | 501811 | G1NESBIT 22.000 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | 25SP | 476 | 476 | 0 | 95.6 | 95.6305 | 95.6 | [7 empty] | CATEGORYB | SINGLE | VILLE PLATTE - WESTFORK 230KV CKT 1 | 0 | 500880 | VILPLT 6 230.00 | 500920 | WSTFORK6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T9185025SP | FROM->TO | RODEMACHER 230/22.0KV TRANSFORMER CKT 1 | E | CLEC | CLEC | CLE_CENTRAL | CLE_CENTRAL | 0 | 501811 | G1NESBIT 22.000 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | 25SP | 476 | 476 | 0 | 95.5 | 95.4671 | 95.5 | [7 empty] | CATEGORYB | SINGLE | VILLE PLATTE - WESTFORK 230KV CKT 1 | 0 | 500880 | VILPLT 6 230.00 | 500920 | WSTFORK6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T11855525SP | FROM->TO | RODEMACHER 230/22.0KV TRANSFORMER CKT 1 | E | CLEC | CLEC | CLE_CENTRAL | CLE_CENTRAL | 0 | 501811 | G1NESBIT 22.000 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | 25SP | 476 | 476 | 0 | 95.4 | 95.3543 | 95.4 | [7 empty] | CATEGORYB | SINGLE | WELLS - WESTFORK 230KV CKT 1 | 0 | 500920 | WSTFORK6 230.00 | 500940 | WELLS 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T28605525SP | FROM->TO | RODEMACHER 230/22.0KV TRANSFORMER CKT 1 | E | CLEC | CLEC | CLE_CENTRAL | CLE_CENTRAL | 0 | 501811 | G1NESBIT 22.000 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | 25SP | 476 | 476 | 0 | 95.3 | 95.2637 | 95.3 | [7 empty] | CATEGORYB | GENOUT | GEN501812 1-RODEMACHER UNIT 2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T9215025SP | FROM->TO | RODEMACHER 230/22.0KV TRANSFORMER CKT 1 | E | CLEC | CLEC | CLE_CENTRAL | CLE_CENTRAL | 0 | 501811 | G1NESBIT 22.000 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | 25SP | 476 | 476 | 0 | 95.2 | 95.1921 | 95.2 | [7 empty] | CATEGORYB | SINGLE | WELLS - WESTFORK 230KV CKT 1 | 0 | 500920 | WSTFORK6 230.00 | 500940 | WELLS 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T6025514WP | FROM->TO | 4URLAND! 138.00 138/13.8KV TRANSFORMER CKT 1 | E | EES | EES | EES_TEXAS | EES_TEXAS | 0 | 334313 | 1WOODVILLE 13.800 | 334314 | 4URLAND! 138.00 | 0 |  | 1 | 14WP | 55 | 55 | 0 |  | 98.3411 | 98.3389 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 11 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T6545014WP | FROM->TO | 4URLAND! 138.00 138/13.8KV TRANSFORMER CKT 1 | E | EES | EES | EES_TEXAS | EES_TEXAS | 0 | 334313 | 1WOODVILLE 13.800 | 334314 | 4URLAND! 138.00 | 0 |  | 1 | 14WP | 55 | 55 | 0 |  | 97.4464 | 97.4855 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 11 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T11905515SP | FROM->TO | DUKE MCADAMS 500/18.0KV TRANSFORMER CKT 1 | E | EES | EES | EES_MISS | EES_MISS | 0 | 337007 | 1ATTALA G2 18.000 | 337005 | 8ATTALA 500.00 | 0 |  | 1 | 15SP | 193 | 193 | 0 |  | 95.073 | 95.0723 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 17 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T11895515SP | FROM->TO | DUKE MCADAMS 500/18.0KV TRANSFORMER CKT 1 | E | EES | EES | EES_MISS | EES_MISS | 0 | 337006 | 1ATTALA G1 18.000 | 337005 | 8ATTALA 500.00 | 0 |  | 1 | 15SP | 193 | 193 | 0 |  | 95.073 | 95.0723 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 17 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T2635515SP | FROM->TO | GRAND GULF 500/22.0KV TRANSFORMER CKT 1 | E | EES | EES | EES_MISS | EES_MISS | 0 | 336821 | 1GGULF U1 22.000 | 336820 | 8G.GULF 500.00 | 0 |  | 1 | 15SP | 1650 | 1650 | 0 | 95.7 | 95.7154 | 95.7 | [7 empty] | CATEGORYB | SINGLE | CYPRESS - HARTBURG 500KV CKT 1 | 0 | 334320 | 8CYPRESS 500.00 | 334325 | 8HARTBRG 500.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2016-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T2965515SP | FROM->TO | GRAND GULF 500/22.0KV TRANSFORMER CKT 1 | E | EES | EES | EES_MISS | EES_MISS | 0 | 336821 | 1GGULF U1 22.000 | 336820 | 8G.GULF 500.00 | 0 |  | 1 | 15SP | 1650 | 1650 | 0 | 95.2 | 95.2036 | 95.2 | [7 empty] | CATEGORYB | SINGLE | FRANKLIN - GRAND GULF 500KV CKT 1 | 0 | 336562 | 8FRKLIN 500.00 | 336820 | 8G.GULF 500.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2016-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T10215515SP | FROM->TO | GRAND GULF 500/22.0KV TRANSFORMER CKT 1 | E | EES | EES | EES_MISS | EES_MISS | 0 | 336821 | 1GGULF U1 22.000 | 336820 | 8G.GULF 500.00 | 0 |  | 1 | 15SP | 1650 | 1650 | 0 | 95.2 | 95.1919 | 95.2 | [7 empty] | CATEGORYB | NONSINGLE | CATALYST-CHO | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2016-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T10315515SP | FROM->TO | GRAND GULF 500/22.0KV TRANSFORMER CKT 1 | E | EES | EES | EES_MISS | EES_MISS | 0 | 336821 | 1GGULF U1 22.000 | 336820 | 8G.GULF 500.00 | 0 |  | 1 | 15SP | 1650 | 1650 | 0 | 95.2 | 95.1919 | 95.2 | [7 empty] | CATEGORYB | NONSINGLE | C015 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2016-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T3155515SP | FROM->TO | GRAND GULF 500/22.0KV TRANSFORMER CKT 1 | E | EES | EES | EES_MISS | EES_MISS | 0 | 336821 | 1GGULF U1 22.000 | 336820 | 8G.GULF 500.00 | 0 |  | 1 | 15SP | 1650 | 1650 | 0 | 95.1 | 95.127 | 95.1 | [7 empty] | CATEGORYB | SINGLE | BAXTER WILSON SES - RAY BRASWELL SES 500KV CKT 1 | 0 | 336830 | 8B.WLSN 500.00 | 336839 | 8R.BRAS 500.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2016-06-01
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T6555014WP | FROM->TO | PERRYVILLE 500/18.0KV TRANSFORMER CKT 1 | E | EES | EES | EES_ELL-N | EES_ELL-N | 0 | 337428 | 1C1PERYV 18.000 | 337427 | 8PERYVIL 500.00 | 0 |  | 1 | 14WP | 215 | 215 | 0 |  | 96.7786 | 96.7912 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 19 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T6565014WP | FROM->TO | PERRYVILLE 500/18.0KV TRANSFORMER CKT 1 | E | EES | EES | EES_ELL-N | EES_ELL-N | 0 | 337430 | 1C3PERYV 18.000 | 337427 | 8PERYVIL 500.00 | 0 |  | 1 | 14WP | 215 | 215 | 0 |  | 96.7786 | 96.7912 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 19 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T11005016WP | FROM->TO | PERYVILLE UNIT #6 500/18.0KV TRANSFORMER CKT 1 | E | EES | EES | EES_ELL-N | EES_ELL-N | 0 | 337430 | 1C3PERYV 18.000 | 337433 | 8PERRYV2 500.00 | 0 |  | 1 | 16WP | 215 | 215 | 0 |  | 96.895 | 96.8698 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 18 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T10995016WP | FROM->TO | PERYVILLE UNIT #6 500/18.0KV TRANSFORMER CKT 1 | E | EES | EES | EES_ELL-N | EES_ELL-N | 0 | 337428 | 1C1PERYV 18.000 | 337433 | 8PERRYV2 500.00 | 0 |  | 1 | 16WP | 215 | 215 | 0 |  | 96.6111 | 96.586 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 18 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T9845516WP | FROM->TO | PERYVILLE UNIT #6 500/18.0KV TRANSFORMER CKT 1 | E | EES | EES | EES_ELL-N | EES_ELL-N | 0 | 337430 | 1C3PERYV 18.000 | 337433 | 8PERRYV2 500.00 | 0 |  | 1 | 16WP | 215 | 215 | 0 |  | 95.0452 | 95.0048 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 18 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T17545025WP | FROM->TO | PERYVILLE UNIT #6 500/18.0KV TRANSFORMER CKT 1 | E | EES | EES | EES_ELL-N | EES_ELL-N | 0 | 337430 | 1C3PERYV 18.000 | 337433 | 8PERRYV2 500.00 | 0 |  | 1 | 25WP | 215 | 215 | 0 |  | 97.8142 | 97.7819 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 19 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T17535025WP | FROM->TO | PERYVILLE UNIT #6 500/18.0KV TRANSFORMER CKT 1 | E | EES | EES | EES_ELL-N | EES_ELL-N | 0 | 337428 | 1C1PERYV 18.000 | 337433 | 8PERRYV2 500.00 | 0 |  | 1 | 25WP | 215 | 215 | 0 |  | 97.526 | 97.4938 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 19 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 |  |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T11805020WP | FROM->TO | 8OSWALD# 500.00 (KNWRIVL1) 500/13.8/13.8KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI |  | EES_ARK | 2 | 338507 | 1C1KNWRI 13.800 | 338520 | 8OSWALD# 500.00 | 338508 | 1C3KNWRI 13.800 | 1 | 20WP | 235 | 235 | 0 |  | 97.0985 | 96.9 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 9 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 |  |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T11815020WP | FROM->TO | 8OSWALD# 500.00 (KNWRIVL2) 500/13.8/13.8KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI |  | EES_ARK | 2 | 338509 | 1C5KNWRI 13.800 | 338520 | 8OSWALD# 500.00 | 338510 | 1S1KNWRI 13.800 | 1 | 20WP | 235 | 235 | 0 |  | 97.0985 | 96.9 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 9 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T1475014WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 14WP | 910 | 910 | 0 | 96.2 | 96.196 | 96.2 | [7 empty] | CATEGORYB | SINGLE | DELL 500 - INDEPENDENCE 500KV CKT 1 | 0 | 338145 | 8ISES 500.00 | 338187 | 8DELL 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T2385014WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 14WP | 910 | 910 | 0 | 96.3 | 96.2737 | 96.2 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T1605514WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 14WP | 910 | 910 | 0 | 96.2 | 96.1757 | 96.2 | [7 empty] | CATEGORYB | SINGLE | DELL 500 - INDEPENDENCE 500KV CKT 1 | 0 | 338145 | 8ISES 500.00 | 338187 | 8DELL 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T4535014WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 14WP | 910 | 910 | 0 | 95.9 | 95.9376 | 95.9 | [7 empty] | CATEGORYB | SINGLE | 8SHELBY TN 500.00 - PLUM POINT 500KV CKT 1 | 0 | 338188 | 8SANSOUC 500.00 | 360021 | 8SHELBY TN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T4685514WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 14WP | 910 | 910 | 0 | 95.8 | 95.8348 | 95.8 | [7 empty] | CATEGORYB | SINGLE | 8SHELBY TN 500.00 - PLUM POINT 500KV CKT 1 | 0 | 338188 | 8SANSOUC 500.00 | 360021 | 8SHELBY TN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T5195014WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 14WP | 910 | 910 | 0 | 95.7 | 95.7105 | 95.7 | [7 empty] | CATEGORYB | NONSINGLE | A129 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T6275014WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 14WP | 910 | 910 | 0 | 95.6 | 95.6038 | 95.6 | [7 empty] | CATEGORYB | GENOUT | GEN337652 1-WHITE BLUFF UNIT #1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T5865514WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 14WP | 910 | 910 | 0 | 95.6 | 95.5607 | 95.6 | [7 empty] | CATEGORYB | GENOUT | GEN337652 1-WHITE BLUFF UNIT #1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T1485014WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 14WP | 910 | 910 | 0 | 95.5 | 95.457 | 95.4 | [7 empty] | CATEGORYB | SINGLE | NEWPORT - NEWPORT INDUSTRIAL 161KV CKT 1 | 0 | 338151 | 5NEWPO 161.00 | 338173 | 5NEW-IN 161.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T1525014WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 14WP | 910 | 910 | 0 | 95.4 | 95.4054 | 95.4 | [7 empty] | CATEGORYB | SINGLE | NEWPORT AB - NEWPORT INDUSTRIAL 161KV CKT 1 | 0 | 338172 | 5NEW-AB 161.00 | 338173 | 5NEW-IN 161.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T1255014WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 14WP | 910 | 910 | 0 | 95.4 | 95.3548 | 95.3 | [7 empty] | CATEGORYB | SINGLE | ELDORADO EHV 500/115KV TRANSFORMER CKT 1 | 0 | 337539 | 3ELDEHV 115.00 | 337561 | 8ELDEHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T1515014WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 14WP | 910 | 910 | 0 | 95.3 | 95.271 | 95.3 | [7 empty] | CATEGORYB | SINGLE | CASH - NEWPORT AB 161KV CKT 1 | 0 | 338171 | 5CASH 161.00 | 338172 | 5NEW-AB 161.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T1505014WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 14WP | 910 | 910 | 0 | 95.2 | 95.2398 | 95.2 | [7 empty] | CATEGORYB | SINGLE | CASH - JONESBORO 161KV CKT 1 | 0 | 338170 | 5JONES 161.00 | 338171 | 5CASH 161.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T6335014WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 14WP | 910 | 910 | 0 | 95.2 | 95.2362 | 95.2 | [7 empty] | CATEGORYB | GENOUT | GEN337911 1-ARKANSAS NUCLEAR ONE UNIT #2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T5245514WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 14WP | 910 | 910 | 0 | 95.2 | 95.2155 | 95.2 | [7 empty] | CATEGORYB | NONSINGLE | A129 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T5065014WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 14WP | 910 | 910 | 0 | 95.1 | 95.0601 | 95.1 | [7 empty] | CATEGORYB | NONSINGLE | AMRN_OUTS5 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T1295014WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 14WP | 910 | 910 | 0 | 95.1 | 95.1094 | 95.1 | [7 empty] | CATEGORYB | SINGLE | MAGNET COVE - SHERIDAN EHV 500KV CKT 1 | 0 | 337643 | 8SHERID 500.00 | 337763 | 8MAGCOVE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T1495014WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 14WP | 910 | 910 | 0 | 95.1 | 95.0813 | 95.1 | [7 empty] | CATEGORYB | SINGLE | WEST MEMPHIS 500 500/161KV TRANSFORMER CKT 1 | 0 | 338161 | 5WM-EHV 161.00 | 338162 | 8WM-EHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T6375014WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 14WP | 910 | 910 | 0 | 95.2 | 95.1645 | 95.1 | [7 empty] | CATEGORYB | GENOUT | GEN338146 1-INDEPENDENCE UNIT #2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T1245014WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 14WP | 910 | 910 | 0 | 95 | 95.0233 | 95 | [7 empty] | CATEGORYB | SINGLE | ETTA (DUKE HOTSPRINGS) - MC NIEL 500KV CKT 1 | 0 | 337515 | 8MCNEIL 500.00 | 337754 | 8ETTA 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T6305014WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 14WP | 910 | 910 | 0 | 95 | 95.0374 | 95 | [7 empty] | CATEGORYB | GENOUT | GEN337910 1-ARKANSAS NUCLEAR ONE UNIT #1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T1235014WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 14WP | 910 | 910 | 0 | 95 | 95.0265 | 95 | [7 empty] | CATEGORYB | SINGLE | MC NIEL 500/115KV TRANSFORMER CKT 1 | 0 | 337515 | 8MCNEIL 500.00 | 337516 | 3MCNEIL 115.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T9075515SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 15SP | 910 | 910 | 0 | 96 | 96.0467 | 96.1 | [7 empty] | CATEGORYB | SINGLE | 8SHELBY TN 500.00 - PLUM POINT 500KV CKT 1 | 0 | 338188 | 8SANSOUC 500.00 | 360021 | 8SHELBY TN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T8265015SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 15SP | 910 | 910 | 0 | 96 | 95.9576 | 96 | [7 empty] | CATEGORYB | SINGLE | 8SHELBY TN 500.00 - PLUM POINT 500KV CKT 1 | 0 | 338188 | 8SANSOUC 500.00 | 360021 | 8SHELBY TN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T3805515SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 15SP | 910 | 910 | 0 | 96 | 96.0012 | 96 | [7 empty] | CATEGORYB | SINGLE | DELL 500 - INDEPENDENCE 500KV CKT 1 | 0 | 338145 | 8ISES 500.00 | 338187 | 8DELL 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T4755015SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 15SP | 910 | 910 | 0 | 95.6 | 95.5701 | 95.6 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T3215015SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 15SP | 910 | 910 | 0 | 95.4 | 95.418 | 95.5 | [7 empty] | CATEGORYB | SINGLE | DELL 500 - INDEPENDENCE 500KV CKT 1 | 0 | 338145 | 8ISES 500.00 | 338187 | 8DELL 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T3675515SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 15SP | 910 | 910 | 0 | 95.2 | 95.2376 | 95.2 | [7 empty] | CATEGORYB | SINGLE | KEO EHV - WEST MEMPHIS 500 500KV CKT 1 | 0 | 337957 | 8KEO 500.00 | 338162 | 8WM-EHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T6295015WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 15WP | 910 | 910 | 0 | 96 | 96.0059 | 96 | [7 empty] | CATEGORYB | SINGLE | 8SHELBY TN 500.00 - PLUM POINT 500KV CKT 1 | 0 | 338188 | 8SANSOUC 500.00 | 360021 | 8SHELBY TN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T2305015WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 15WP | 910 | 910 | 0 | 95.8 | 95.7937 | 95.7 | [7 empty] | CATEGORYB | SINGLE | DELL 500 - INDEPENDENCE 500KV CKT 1 | 0 | 338145 | 8ISES 500.00 | 338187 | 8DELL 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T2455515WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 15WP | 910 | 910 | 0 | 95.6 | 95.6373 | 95.7 | [7 empty] | CATEGORYB | SINGLE | DELL 500 - INDEPENDENCE 500KV CKT 1 | 0 | 338145 | 8ISES 500.00 | 338187 | 8DELL 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T10255015WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 15WP | 910 | 910 | 0 |  | -999 | 95.6 | [7 empty] | CATEGORYB | GENOUT | GEN337652 1-WHITE BLUFF UNIT #1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T6705515WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 15WP | 910 | 910 | 0 | 95.1 | 95.1268 | 95.4 | [7 empty] | CATEGORYB | SINGLE | 8SHELBY TN 500.00 - PLUM POINT 500KV CKT 1 | 0 | 338188 | 8SANSOUC 500.00 | 360021 | 8SHELBY TN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T10095515WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 15WP | 910 | 910 | 0 | 95.3 | 95.3072 | 95.3 | [7 empty] | CATEGORYB | GENOUT | GEN337652 1-WHITE BLUFF UNIT #1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T3245015WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 15WP | 910 | 910 | 0 | 95.1 | 95.1438 | 95 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T8375015WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 15WP | 910 | 910 | 0 | 95.1 | 95.0615 | 95 | [7 empty] | CATEGORYB | NONSINGLE | A129 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T5165516SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16SP | 910 | 910 | 0 | 96.6 | 96.5906 | 96.8 | [7 empty] | CATEGORYB | SINGLE | DELL 500 - INDEPENDENCE 500KV CKT 1 | 0 | 338145 | 8ISES 500.00 | 338187 | 8DELL 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T10815016SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16SP | 910 | 910 | 0 | 96.5 | 96.5378 | 96.5 | [7 empty] | CATEGORYB | SINGLE | 5ISES 2 161/26.0KV TRANSFORMER CKT 2 | 0 | 338152 | 5ISES-2 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 2 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T5215516SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16SP | 910 | 910 | 0 | 96.4 | 96.4123 | 96.5 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - PLUM POINT 500KV CKT 1 | 0 | 338188 | 8SANSOUC 500.00 | 338198 | 8DRIVER% 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T11915516SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16SP | 910 | 910 | 0 | 96.4 | 96.383 | 96.5 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - 8SHELBY TN 500.00 500KV CKT 1 | 0 | 338198 | 8DRIVER% 500.00 | 360021 | 8SHELBY TN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T11835516SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16SP | 910 | 910 | 0 | 96.4 | 96.3724 | 96.4 | [7 empty] | CATEGORYB | SINGLE | INDEPENDENCE 161/26.0KV TRANSFORMER CKT 1 | 0 | 338142 | 5ISES-1 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T10775016SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16SP | 910 | 910 | 0 | 96.3 | 96.3471 | 96.3 | [7 empty] | CATEGORYB | SINGLE | INDEPENDENCE 161/26.0KV TRANSFORMER CKT 1 | 0 | 338142 | 5ISES-1 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T10855016SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16SP | 910 | 910 | 0 | 96 | 96.0208 | 96.3 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - 8SHELBY TN 500.00 500KV CKT 1 | 0 | 338198 | 8DRIVER% 500.00 | 360021 | 8SHELBY TN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T6245016SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16SP | 910 | 910 | 0 | 96.3 | 96.2892 | 96.2 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T4475016SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16SP | 910 | 910 | 0 | 96.2 | 96.1826 | 96.2 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - PLUM POINT 500KV CKT 1 | 0 | 338188 | 8SANSOUC 500.00 | 338198 | 8DRIVER% 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T5085516SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16SP | 910 | 910 | 0 | 96 | 96.0252 | 96.1 | [7 empty] | CATEGORYB | SINGLE | KEO EHV - WEST MEMPHIS 500 500KV CKT 1 | 0 | 337957 | 8KEO 500.00 | 338162 | 8WM-EHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T11875516SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16SP | 910 | 910 | 0 | 95.8 | 95.7806 | 95.8 | [7 empty] | CATEGORYB | SINGLE | 5ISES 2 161/26.0KV TRANSFORMER CKT 2 | 0 | 338152 | 5ISES-2 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 2 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T4245016SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16SP | 910 | 910 | 0 | 95.6 | 95.6293 | 95.6 | [7 empty] | CATEGORYB | SINGLE | MAGNET COVE - SHERIDAN EHV 500KV CKT 1 | 0 | 337643 | 8SHERID 500.00 | 337763 | 8MAGCOVE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T4425016SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16SP | 910 | 910 | 0 | 95.6 | 95.6276 | 95.6 | [7 empty] | CATEGORYB | SINGLE | DELL 500 - INDEPENDENCE 500KV CKT 1 | 0 | 338145 | 8ISES 500.00 | 338187 | 8DELL 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T4315016SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16SP | 910 | 910 | 0 | 95.3 | 95.3244 | 95.3 | [7 empty] | CATEGORYB | SINGLE | KEO EHV - WEST MEMPHIS 500 500KV CKT 1 | 0 | 337957 | 8KEO 500.00 | 338162 | 8WM-EHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T5025516SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16SP | 910 | 910 | 0 | 95.3 | 95.29 | 95.3 | [7 empty] | CATEGORYB | SINGLE | MAGNET COVE - SHERIDAN EHV 500KV CKT 1 | 0 | 337643 | 8SHERID 500.00 | 337763 | 8MAGCOVE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T10795016WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 | 97.5 | 97.4702 | 97.4 | [7 empty] | CATEGORYB | GENOUT | GEN337652 1-WHITE BLUFF UNIT #1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T6775016WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 | 97.2 | 97.1591 | 97.1 | [7 empty] | CATEGORYB | SINGLE | 5ISES 2 161/26.0KV TRANSFORMER CKT 2 | 0 | 338152 | 5ISES-2 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 2 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T6745016WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 | 97.1 | 97.0636 | 97 | [7 empty] | CATEGORYB | SINGLE | INDEPENDENCE 161/26.0KV TRANSFORMER CKT 1 | 0 | 338142 | 5ISES-1 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T6525516WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 | 96.3 | 96.3194 | 96.3 | [7 empty] | CATEGORYB | SINGLE | 5ISES 2 161/26.0KV TRANSFORMER CKT 2 | 0 | 338152 | 5ISES-2 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 2 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T6495516WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 | 96.2 | 96.2219 | 96.2 | [7 empty] | CATEGORYB | SINGLE | INDEPENDENCE 161/26.0KV TRANSFORMER CKT 1 | 0 | 338142 | 5ISES-1 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T9725516WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 | 96.2 | 96.1617 | 96.1 | [7 empty] | CATEGORYB | GENOUT | GEN337652 1-WHITE BLUFF UNIT #1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T6795016WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 | 96 | 96.0088 | 96 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - 8SHELBY TN 500.00 500KV CKT 1 | 0 | 338198 | 8DRIVER% 500.00 | 360021 | 8SHELBY TN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T3805016WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 | 96 | 96.0419 | 95.9 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T2425016WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 | 95.8 | 95.8107 | 95.8 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - PLUM POINT 500KV CKT 1 | 0 | 338188 | 8SANSOUC 500.00 | 338198 | 8DRIVER% 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T8875016WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 | 95.5 | 95.4676 | 95.4 | [7 empty] | CATEGORYB | NONSINGLE | A129 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T10985016WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 |  | 95.288 | 95.2 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 6 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T2415016WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 | 95.1 | 95.1372 | 95.1 | [7 empty] | CATEGORYB | SINGLE | NEWPORT AB - NEWPORT INDUSTRIAL 161KV CKT 1 | 0 | 338172 | 5NEW-AB 161.00 | 338173 | 5NEW-IN 161.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T2405016WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 | 95.2 | 95.1794 | 95.1 | [7 empty] | CATEGORYB | SINGLE | NEWPORT - NEWPORT INDUSTRIAL 161KV CKT 1 | 0 | 338151 | 5NEWPO 161.00 | 338173 | 5NEW-IN 161.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T2385016WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 | 95.1 | 95.1465 | 95.1 | [7 empty] | CATEGORYB | SINGLE | DELL 500 - INDEPENDENCE 500KV CKT 1 | 0 | 338145 | 8ISES 500.00 | 338187 | 8DELL 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T6545516WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 | 95.1 | 95.0839 | 95.1 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - 8SHELBY TN 500.00 500KV CKT 1 | 0 | 338198 | 8DRIVER% 500.00 | 360021 | 8SHELBY TN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T2185016WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 | 95.1 | 95.0721 | 95 | [7 empty] | CATEGORYB | SINGLE | ELDORADO EHV 500/115KV TRANSFORMER CKT 1 | 0 | 337539 | 3ELDEHV 115.00 | 337561 | 8ELDEHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T10805016WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 | 95 | 95.0401 | 95 | [7 empty] | CATEGORYB | GENOUT | GEN337911 1-ARKANSAS NUCLEAR ONE UNIT #2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T7125020SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20SP | 910 | 910 | 0 | 97.6 | 97.5894 | 97.4 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T6365520SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20SP | 910 | 910 | 0 | 97.3 | 97.3296 | 97.4 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - PLUM POINT 500KV CKT 1 | 0 | 338188 | 8SANSOUC 500.00 | 338198 | 8DRIVER% 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T13285520SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20SP | 910 | 910 | 0 | 97.3 | 97.3164 | 97.4 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - 8SHELBY TN 500.00 500KV CKT 1 | 0 | 338198 | 8DRIVER% 500.00 | 360021 | 8SHELBY TN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T6315520SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20SP | 910 | 910 | 0 | 97.1 | 97.1326 | 97.3 | [7 empty] | CATEGORYB | SINGLE | DELL 500 - INDEPENDENCE 500KV CKT 1 | 0 | 338145 | 8ISES 500.00 | 338187 | 8DELL 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T12345020SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20SP | 910 | 910 | 0 | 96.9 | 96.9074 | 97 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - 8SHELBY TN 500.00 500KV CKT 1 | 0 | 338198 | 8DRIVER% 500.00 | 360021 | 8SHELBY TN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T5245020SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20SP | 910 | 910 | 0 | 96.9 | 96.9417 | 97 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - PLUM POINT 500KV CKT 1 | 0 | 338188 | 8SANSOUC 500.00 | 338198 | 8DRIVER% 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T6185520SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20SP | 910 | 910 | 0 | 96.6 | 96.5799 | 96.7 | [7 empty] | CATEGORYB | SINGLE | KEO EHV - WEST MEMPHIS 500 500KV CKT 1 | 0 | 337957 | 8KEO 500.00 | 338162 | 8WM-EHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T5195020SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20SP | 910 | 910 | 0 | 96.2 | 96.239 | 96.4 | [7 empty] | CATEGORYB | SINGLE | DELL 500 - INDEPENDENCE 500KV CKT 1 | 0 | 338145 | 8ISES 500.00 | 338187 | 8DELL 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T13265520SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20SP | 910 | 910 | 0 | 96.1 | 96.1273 | 96.2 | [7 empty] | CATEGORYB | SINGLE | 5ISES 2 161/26.0KV TRANSFORMER CKT 2 | 0 | 338152 | 5ISES-2 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 2 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T12325020SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20SP | 910 | 910 | 0 | 96.1 | 96.0832 | 96.1 | [7 empty] | CATEGORYB | SINGLE | 5ISES 2 161/26.0KV TRANSFORMER CKT 2 | 0 | 338152 | 5ISES-2 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 2 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T12285020SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20SP | 910 | 910 | 0 | 95.9 | 95.9389 | 96 | [7 empty] | CATEGORYB | SINGLE | INDEPENDENCE 161/26.0KV TRANSFORMER CKT 1 | 0 | 338142 | 5ISES-1 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T4985020SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20SP | 910 | 910 | 0 | 96 | 95.9716 | 96 | [7 empty] | CATEGORYB | SINGLE | MAGNET COVE - SHERIDAN EHV 500KV CKT 1 | 0 | 337643 | 8SHERID 500.00 | 337763 | 8MAGCOVE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T13225520SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20SP | 910 | 910 | 0 | 96 | 95.9784 | 96 | [7 empty] | CATEGORYB | SINGLE | INDEPENDENCE 161/26.0KV TRANSFORMER CKT 1 | 0 | 338142 | 5ISES-1 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T5095020SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20SP | 910 | 910 | 0 | 95.8 | 95.8439 | 95.9 | [7 empty] | CATEGORYB | SINGLE | KEO EHV - WEST MEMPHIS 500 500KV CKT 1 | 0 | 337957 | 8KEO 500.00 | 338162 | 8WM-EHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T6095520SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20SP | 910 | 910 | 0 | 95.5 | 95.4785 | 95.5 | [7 empty] | CATEGORYB | SINGLE | MAGNET COVE - SHERIDAN EHV 500KV CKT 1 | 0 | 337643 | 8SHERID 500.00 | 337763 | 8MAGCOVE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T6165520SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20SP | 910 | 910 | 0 | 95.1 | 95.0736 | 95.2 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - PLEASANT HILL 500KV CKT 1 | 0 | 337909 | 8ANO 500.00 | 337922 | 8P HILL 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T4995020SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20SP | 910 | 910 | 0 |  | 94.9916 | 95 | [7 empty] | CATEGORYB | SINGLE | KEO EHV - WHITE BLUFF 500KV CKT 1 | 0 | 337651 | 8WH BLF 500.00 | 337957 | 8KEO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T6105520SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20SP | 910 | 910 | 0 |  | 93.9699 | 95 | [7 empty] | CATEGORYB | SINGLE | KEO EHV - WHITE BLUFF 500KV CKT 1 | 0 | 337651 | 8WH BLF 500.00 | 337957 | 8KEO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T7565020WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20WP | 910 | 910 | 0 | 96.2 | 96.1778 | 96.2 | [7 empty] | CATEGORYB | SINGLE | 5ISES 2 161/26.0KV TRANSFORMER CKT 2 | 0 | 338152 | 5ISES-2 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 2 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T7525020WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20WP | 910 | 910 | 0 | 96.1 | 96.0829 | 96.1 | [7 empty] | CATEGORYB | SINGLE | INDEPENDENCE 161/26.0KV TRANSFORMER CKT 1 | 0 | 338142 | 5ISES-1 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T7675520WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20WP | 910 | 910 | 0 | 95.6 | 95.5868 | 95.7 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - 8SHELBY TN 500.00 500KV CKT 1 | 0 | 338198 | 8DRIVER% 500.00 | 360021 | 8SHELBY TN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T7655520WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20WP | 910 | 910 | 0 | 95.7 | 95.7039 | 95.7 | [7 empty] | CATEGORYB | SINGLE | 5ISES 2 161/26.0KV TRANSFORMER CKT 2 | 0 | 338152 | 5ISES-2 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 2 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T7585020WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20WP | 910 | 910 | 0 | 95.7 | 95.6874 | 95.6 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - 8SHELBY TN 500.00 500KV CKT 1 | 0 | 338198 | 8DRIVER% 500.00 | 360021 | 8SHELBY TN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T4345020WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20WP | 910 | 910 | 0 | 95.7 | 95.7022 | 95.6 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T7615520WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20WP | 910 | 910 | 0 | 95.6 | 95.6091 | 95.6 | [7 empty] | CATEGORYB | SINGLE | INDEPENDENCE 161/26.0KV TRANSFORMER CKT 1 | 0 | 338142 | 5ISES-1 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T3055020WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20WP | 910 | 910 | 0 | 95.5 | 95.5488 | 95.5 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - PLUM POINT 500KV CKT 1 | 0 | 338188 | 8SANSOUC 500.00 | 338198 | 8DRIVER% 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T3445520WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20WP | 910 | 910 | 0 | 95.6 | 95.5881 | 95.5 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - PLUM POINT 500KV CKT 1 | 0 | 338188 | 8SANSOUC 500.00 | 338198 | 8DRIVER% 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T11775020WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20WP | 910 | 910 | 0 |  | 95.3062 | 95.3 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 6 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T3395520WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20WP | 910 | 910 | 0 | 95 | 95.0138 | 95.1 | [7 empty] | CATEGORYB | SINGLE | DELL 500 - INDEPENDENCE 500KV CKT 1 | 0 | 338145 | 8ISES 500.00 | 338187 | 8DELL 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T11285025SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25SP | 910 | 910 | 0 | 97.7 | 97.7477 | 97.7 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T20785525SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25SP | 910 | 910 | 0 | 96.9 | 96.9193 | 97 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - 8SHELBY TN 500.00 500KV CKT 1 | 0 | 338198 | 8DRIVER% 500.00 | 360021 | 8SHELBY TN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T11065525SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25SP | 910 | 910 | 0 | 96.5 | 96.4609 | 96.6 | [7 empty] | CATEGORYB | SINGLE | DELL 500 - INDEPENDENCE 500KV CKT 1 | 0 | 338145 | 8ISES 500.00 | 338187 | 8DELL 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T8575025SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25SP | 910 | 910 | 0 | 96.3 | 96.3296 | 96.4 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - PLUM POINT 500KV CKT 1 | 0 | 338188 | 8SANSOUC 500.00 | 338198 | 8DRIVER% 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T17695025SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25SP | 910 | 910 | 0 | 96.3 | 96.3024 | 96.3 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - 8SHELBY TN 500.00 500KV CKT 1 | 0 | 338198 | 8DRIVER% 500.00 | 360021 | 8SHELBY TN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T20765525SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25SP | 910 | 910 | 0 | 96.1 | 96.0889 | 96.2 | [7 empty] | CATEGORYB | SINGLE | 5ISES 2 161/26.0KV TRANSFORMER CKT 2 | 0 | 338152 | 5ISES-2 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 2 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T17675025SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25SP | 910 | 910 | 0 | 96.1 | 96.1251 | 96.1 | [7 empty] | CATEGORYB | SINGLE | 5ISES 2 161/26.0KV TRANSFORMER CKT 2 | 0 | 338152 | 5ISES-2 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 2 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T10885525SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25SP | 910 | 910 | 0 | 96 | 96.0045 | 96.1 | [7 empty] | CATEGORYB | SINGLE | KEO EHV - WEST MEMPHIS 500 500KV CKT 1 | 0 | 337957 | 8KEO 500.00 | 338162 | 8WM-EHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T8225025SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25SP | 910 | 910 | 0 | 96 | 96.0471 | 96 | [7 empty] | CATEGORYB | SINGLE | MAGNET COVE - SHERIDAN EHV 500KV CKT 1 | 0 | 337643 | 8SHERID 500.00 | 337763 | 8MAGCOVE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T17635025SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25SP | 910 | 910 | 0 | 96 | 95.9756 | 96 | [7 empty] | CATEGORYB | SINGLE | INDEPENDENCE 161/26.0KV TRANSFORMER CKT 1 | 0 | 338142 | 5ISES-1 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T20725525SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25SP | 910 | 910 | 0 | 95.9 | 95.9376 | 96 | [7 empty] | CATEGORYB | SINGLE | INDEPENDENCE 161/26.0KV TRANSFORMER CKT 1 | 0 | 338142 | 5ISES-1 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T8505025SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25SP | 910 | 910 | 0 | 95.9 | 95.8857 | 95.9 | [7 empty] | CATEGORYB | SINGLE | DELL 500 - INDEPENDENCE 500KV CKT 1 | 0 | 338145 | 8ISES 500.00 | 338187 | 8DELL 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T8355025SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25SP | 910 | 910 | 0 | 95.4 | 95.4307 | 95.5 | [7 empty] | CATEGORYB | SINGLE | KEO EHV - WEST MEMPHIS 500 500KV CKT 1 | 0 | 337957 | 8KEO 500.00 | 338162 | 8WM-EHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T10795525SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25SP | 910 | 910 | 0 | 95.5 | 95.5367 | 95.5 | [7 empty] | CATEGORYB | SINGLE | MAGNET COVE - SHERIDAN EHV 500KV CKT 1 | 0 | 337643 | 8SHERID 500.00 | 337763 | 8MAGCOVE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T8235025SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25SP | 910 | 910 | 0 | 95 | 95.0363 | 95 | [7 empty] | CATEGORYB | SINGLE | KEO EHV - WHITE BLUFF 500KV CKT 1 | 0 | 337651 | 8WH BLF 500.00 | 337957 | 8KEO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T11025025WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25WP | 910 | 910 | 0 | 96.2 | 96.1957 | 96.1 | [7 empty] | CATEGORYB | SINGLE | 5ISES 2 161/26.0KV TRANSFORMER CKT 2 | 0 | 338152 | 5ISES-2 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 2 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T11005025WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25WP | 910 | 910 | 0 | 96.1 | 96.1008 | 96 | [7 empty] | CATEGORYB | SINGLE | INDEPENDENCE 161/26.0KV TRANSFORMER CKT 1 | 0 | 338142 | 5ISES-1 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T7285025WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25WP | 910 | 910 | 0 | 96.1 | 96.0558 | 95.9 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T5175525WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25WP | 910 | 910 | 0 | 95.8 | 95.8185 | 95.9 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - PLUM POINT 500KV CKT 1 | 0 | 338188 | 8SANSOUC 500.00 | 338198 | 8DRIVER% 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T10025525WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25WP | 910 | 910 | 0 | 95.7 | 95.7078 | 95.7 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - 8SHELBY TN 500.00 500KV CKT 1 | 0 | 338198 | 8DRIVER% 500.00 | 360021 | 8SHELBY TN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T9985525WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25WP | 910 | 910 | 0 | 95.7 | 95.7281 | 95.7 | [7 empty] | CATEGORYB | SINGLE | 5ISES 2 161/26.0KV TRANSFORMER CKT 2 | 0 | 338152 | 5ISES-2 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 2 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T11065025WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25WP | 910 | 910 | 0 | 95.6 | 95.6461 | 95.6 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - 8SHELBY TN 500.00 500KV CKT 1 | 0 | 338198 | 8DRIVER% 500.00 | 360021 | 8SHELBY TN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T9935525WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25WP | 910 | 910 | 0 | 95.6 | 95.6332 | 95.6 | [7 empty] | CATEGORYB | SINGLE | INDEPENDENCE 161/26.0KV TRANSFORMER CKT 1 | 0 | 338142 | 5ISES-1 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T5455025WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25WP | 910 | 910 | 0 | 95.5 | 95.5302 | 95.4 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - PLUM POINT 500KV CKT 1 | 0 | 338188 | 8SANSOUC 500.00 | 338198 | 8DRIVER% 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T17465025WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25WP | 910 | 910 | 0 |  | 95.2361 | 95.2 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 6 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T18315020SP | FROM->TO | DUKE LAKEOVER 230/18.0KV TRANSFORMER CKT 1 | E | EES-EMI | EES-EMI | EES_MISS | EES_MISS | 0 | 336851 | 1IG1DUKEH 18.000 | 336850 | 6DUKELO1 230.00 | 0 |  | 1 | 20SP | 193 | 193 | 0 |  | 97.5071 | 97.507 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T19055520SP | FROM->TO | DUKE LAKEOVER 230/18.0KV TRANSFORMER CKT 1 | E | EES-EMI | EES-EMI | EES_MISS | EES_MISS | 0 | 336851 | 1IG1DUKEH 18.000 | 336850 | 6DUKELO1 230.00 | 0 |  | 1 | 20SP | 193 | 193 | 0 |  | 97.5035 | 97.5035 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T26255025SP | FROM->TO | DUKE LAKEOVER 230/18.0KV TRANSFORMER CKT 1 | E | EES-EMI | EES-EMI | EES_MISS | EES_MISS | 0 | 336851 | 1IG1DUKEH 18.000 | 336850 | 6DUKELO1 230.00 | 0 |  | 1 | 25SP | 193 | 193 | 0 |  | 97.5035 | 97.5035 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T28875525SP | FROM->TO | DUKE LAKEOVER 230/18.0KV TRANSFORMER CKT 1 | E | EES-EMI | EES-EMI | EES_MISS | EES_MISS | 0 | 336851 | 1IG1DUKEH 18.000 | 336850 | 6DUKELO1 230.00 | 0 |  | 1 | 25SP | 193 | 193 | 0 |  | 97.5034 | 97.5034 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T15625525WP | FROM->TO | DUKE MCADAMS 500/18.0KV TRANSFORMER CKT 1 | E | EES-EMI | EES-EMI | EES_MISS | EES_MISS | 0 | 337006 | 1ATTALA G1 18.000 | 337005 | 8ATTALA 500.00 | 0 |  | 1 | 25WP | 193 | 193 | 0 |  | 96.6372 | 96.5953 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 19 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T15635525WP | FROM->TO | DUKE MCADAMS 500/18.0KV TRANSFORMER CKT 1 | E | EES-EMI | EES-EMI | EES_MISS | EES_MISS | 0 | 337007 | 1ATTALA G2 18.000 | 337005 | 8ATTALA 500.00 | 0 |  | 1 | 25WP | 193 | 193 | 0 |  | 96.6372 | 96.5953 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 19 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T55014WP | FROM->TO | SUB 167 - RIVERTON 69/13.2KV TRANSFORMER CKT 1 | E | EMDE | EMDE | BAXTER | BAXTER | 0 | 547645 | R8G167 1 13.200 | 547541 | RIV167 2 69.000 | 0 |  | 1 | 14WP | 52 | 52 | 0 | 96.2 | 96.1538 | 97.2 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2014-10-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T165514WP | FROM->TO | SUB 167 - RIVERTON 69/13.2KV TRANSFORMER CKT 1 | E | EMDE | EMDE | BAXTER | BAXTER | 0 | 547645 | R8G167 1 13.200 | 547541 | RIV167 2 69.000 | 0 |  | 1 | 14WP | 52 | 52 | 0 | 96.2 | 96.1538 | 96.2 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2014-10-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T27975525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 97.7 | 97.7258 | 97.7 | [7 empty] | CATEGORYB | GENOUT | GEN303008 1-1BC2 U3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T27955525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 97.5 | 97.5392 | 97.5 | [7 empty] | CATEGORYB | GENOUT | GEN303006 1-1BC2 U1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T28245525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 97.1 | 97.0782 | 97.1 | [7 empty] | CATEGORYB | GENOUT | GEN336153 1-WATERFORD UNIT#3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T28165525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 96.7 | 96.737 | 96.7 | [7 empty] | CATEGORYB | GENOUT | GEN335831 1-RIVERBEND UNIT#1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T9815525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 96.5 | 96.5203 | 96.5 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T9665525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 96.2 | 96.2319 | 96.2 | [7 empty] | CATEGORYB | SINGLE | WATERFORD - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WGLEN 500.00 | 336150 | 8WATERFO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T24745525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 96.2 | 96.2318 | 96.2 | [7 empty] | CATEGORYB | NONSINGLE | L015 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T9445525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 96.1 | 96.1157 | 96.1 | [7 empty] | CATEGORYB | SINGLE | WEBRE - WELLS 500KV CKT 1 | 0 | 335368 | 8WELLS 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T11605525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 96.1 | 96.0744 | 96.1 | [7 empty] | CATEGORYB | SINGLE | BAYOU SALE - WAXLAKE 138KV CKT 1 | 0 | 500050 | BSALES 4 138.00 | 500890 | WAXLAKE4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T10135525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 96.1 | 96.0734 | 96.1 | [7 empty] | CATEGORYB | SINGLE | BAXTER WILSON SES - GRAND GULF 500KV CKT 1 | 0 | 336820 | 8G.GULF 500.00 | 336830 | 8B.WLSN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T10095525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 96.1 | 96.0656 | 96.1 | [7 empty] | CATEGORYB | SINGLE | FRANKLIN - GRAND GULF 500KV CKT 1 | 0 | 336562 | 8FRKLIN 500.00 | 336820 | 8G.GULF 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T28325525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 96.1 | 96.118 | 96.1 | [7 empty] | CATEGORYB | GENOUT | GEN336251 1-NINEMILE POINT UNIT#4 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T28345525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 96.1 | 96.138 | 96.1 | [7 empty] | CATEGORYB | GENOUT | GEN336252 1-NINEMILE POINT UNIT#5 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T11585525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 96 | 95.9748 | 96 | [7 empty] | CATEGORYB | SINGLE | BAYOU SALE - TECHE 138KV CKT 1 | 0 | 500050 | BSALES 4 138.00 | 500820 | TECHE 4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T10165525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 95.9 | 95.9057 | 95.9 | [7 empty] | CATEGORYB | SINGLE | BAXTER WILSON SES - RAY BRASWELL SES 500KV CKT 1 | 0 | 336830 | 8B.WLSN 500.00 | 336839 | 8R.BRAS 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T9545525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 95.9 | 95.9156 | 95.9 | [7 empty] | CATEGORYB | SINGLE | 6MEAUX - SELLRD 230KV CKT 1 | 0 | 335381 | 6MEAUX 230.00 | 500776 | SELLRD6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T22805525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 95.9 | 95.9006 | 95.9 | [7 empty] | CATEGORYB | NONSINGLE | ADAMS CREEK- | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T9495525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 95.9 | 95.9151 | 95.9 | [7 empty] | CATEGORYB | SINGLE | 6MEAUX 230/138KV TRANSFORMER CKT 1 | 0 | 335380 | 4MEAUX 138.00 | 335381 | 6MEAUX 230.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T10025525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 95.9 | 95.8735 | 95.9 | [7 empty] | CATEGORYB | SINGLE | WATERFORD 500/230KV TRANSFORMER CKT 1 | 0 | 336150 | 8WATERFO 500.00 | 336154 | 6WATFRD 230.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T28285525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 96 | 95.9502 | 95.9 | [7 empty] | CATEGORYB | GENOUT | GEN336191 1-LITTLE GYPSY UNIT#3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T11755525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 95.9 | 95.9273 | 95.9 | [7 empty] | CATEGORYB | SINGLE | EL PASO TAP - WAXLAKE 138KV CKT 1 | 0 | 500290 | ELPTAP 4 138.00 | 500890 | WAXLAKE4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T28365525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 95.9 | 95.8762 | 95.9 | [7 empty] | CATEGORYB | GENOUT | GEN336464 1-MICHOUD UNIT #3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T28155525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 95.9 | 95.8815 | 95.9 | [7 empty] | CATEGORYB | GENOUT | GEN335614 1-WILLOW GLENN UNIT#4 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T9985525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 95.9 | 95.9016 | 95.9 | [7 empty] | CATEGORYB | SINGLE | BOGALUSA - FRANKLIN 500KV CKT 1 | 0 | 336130 | 8BOGALUS 500.00 | 336562 | 8FRKLIN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T25395025SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 95.6 | 95.5732 | 95.5 | [7 empty] | CATEGORYB | GENOUT | GEN303008 1-1BC2 U3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T25375025SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 95.4 | 95.4153 | 95.4 | [7 empty] | CATEGORYB | GENOUT | GEN303006 1-1BC2 U1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T675525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 95.4 | 95.381 | 95.4 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T25585025SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 95.1 | 95.1361 | 95.1 | [7 empty] | CATEGORYB | GENOUT | GEN336153 1-WATERFORD UNIT#3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T18415516SP | FROM->TO | 8XMFRINT3 500.00 500/13.8KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303025 | 1S3INTHB 13.800 | 303022 | 8XMFRINT3 500.00 | 0 |  | 1 | 16SP | 130 | 130 | 0 |  | 95.3257 | 95.343 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 18 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T19115520SP | FROM->TO | 8XMFRINT3 500.00 500/13.8KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303025 | 1S3INTHB 13.800 | 303022 | 8XMFRINT3 500.00 | 0 |  | 1 | 20SP | 130 | 130 | 0 |  | 95.3163 | 95.3163 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 14 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T11455520WP | FROM->TO | 8XMFRINT3 500.00 500/13.8KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303025 | 1S3INTHB 13.800 | 303022 | 8XMFRINT3 500.00 | 0 |  | 1 | 20WP | 130 | 130 | 0 |  | 95.421 | 95.421 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 13 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T26295025SP | FROM->TO | 8XMFRINT3 500.00 500/13.8KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303025 | 1S3INTHB 13.800 | 303022 | 8XMFRINT3 500.00 | 0 |  | 1 | 25SP | 130 | 130 | 0 |  | 99.5174 | 99.497 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 19 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T15595525WP | FROM->TO | 8XMFRINT3 500.00 500/13.8KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303025 | 1S3INTHB 13.800 | 303022 | 8XMFRINT3 500.00 | 0 |  | 1 | 25WP | 130 | 130 | 0 |  | 95.4063 | 95.4063 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 12 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T18395516SP | FROM->TO | 8XMFRINT4 500.00 500/13.8KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303027 | 1S4INTHB 13.800 | 303023 | 8XMFRINT4 500.00 | 0 |  | 1 | 16SP | 130 | 130 | 0 |  | 95.2334 | 95.2334 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 11 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T19105520SP | FROM->TO | 8XMFRINT4 500.00 500/13.8KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303027 | 1S4INTHB 13.800 | 303023 | 8XMFRINT4 500.00 | 0 |  | 1 | 20SP | 130 | 130 | 0 |  | 95.3163 | 95.3163 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 13 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T11445520WP | FROM->TO | 8XMFRINT4 500.00 500/13.8KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303027 | 1S4INTHB 13.800 | 303023 | 8XMFRINT4 500.00 | 0 |  | 1 | 20WP | 130 | 130 | 0 |  | 95.421 | 95.421 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 12 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T28945525SP | FROM->TO | 8XMFRINT4 500.00 500/13.8KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303027 | 1S4INTHB 13.800 | 303023 | 8XMFRINT4 500.00 | 0 |  | 1 | 25SP | 130 | 130 | 0 |  | 95.2836 | 95.2871 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 20 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T28905525SP | FROM->TO | 8XMFRINT4 500.00 500/13.8KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303027 | 1S4INTHB 13.800 | 303023 | 8XMFRINT4 500.00 | 0 |  | 1 | 25SP | 130 | 130 | 0 |  | 95.2836 | 95.2831 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 13 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T15585525WP | FROM->TO | 8XMFRINT4 500.00 500/13.8KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303027 | 1S4INTHB 13.800 | 303023 | 8XMFRINT4 500.00 | 0 |  | 1 | 25WP | 130 | 130 | 0 |  | 95.4063 | 95.4063 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 11 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T2335516SP | FROM->TO | SHELDON 115/13.8KV TRANSFORMER CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640020 | SHELDN2G 13.800 | 640278 | SHELDON7 115.00 | 0 |  | 1 | 16SP | 140 | 140 | 140 | 95.3 | 95.2863 | 95.3 | [7 empty] | CATEGORYB | SINGLE | GRAND ISLAND - SWEETWATER 345KV CKT 1 | 0 | 640374 | SWEET W3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T2785020SP | FROM->TO | SHELDON 115/13.8KV TRANSFORMER CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640020 | SHELDN2G 13.800 | 640278 | SHELDON7 115.00 | 0 |  | 1 | 20SP | 140 | 140 | 140 | 99.2 | 99.1971 | 97.8 | [7 empty] | CATEGORYB | SINGLE | GERALD GENTLEMAN STATION - RED WILLOW 345KV CKT 1 | 0 | 640183 | GENTLMN3 345.00 | 640325 | REDWILO3 345.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T4845025SP | FROM->TO | SHELDON 115/13.8KV TRANSFORMER CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640020 | SHELDN2G 13.800 | 640278 | SHELDON7 115.00 | 0 |  | 1 | 25SP | 140 | 140 | 140 | 101 | 100.9937 | 99.2 | [7 empty] | CATEGORYB | SINGLE | GERALD GENTLEMAN STATION - RED WILLOW 345KV CKT 1 | 0 | 640183 | GENTLMN3 345.00 | 640325 | REDWILO3 345.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T6915525SP | FROM->TO | SHELDON 115/13.8KV TRANSFORMER CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640020 | SHELDN2G 13.800 | 640278 | SHELDON7 115.00 | 0 |  | 1 | 25SP | 140 | 140 | 140 | 96.3 | 96.3399 | 96.2 | [7 empty] | CATEGORYB | SINGLE | AINSWORTH - AINSWORTH 115KV CKT 1 | 0 | 640050 | AINSWND7 115.00 | 640051 | AINSWRT7 115.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 |  | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T3455515WP | FROM->TO | NORTHWEST (NORTWST2) 345/138/13.8KV TRANSFORMER CKT 1 | E | OKGE | OKGE |  |  | 2 | 514880 | NORTWST7 345.00 | 514879 | NORTWST4 138.00 | 515742 | NORTWS21 13.800 | 1 | 15WP | 493 | 493 | 0 | 97.2 | 97.2388 | 97.7 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST (NORTWST3) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514879 | NORTWST4 138.00 | 514880 | NORTWST7 345.00 | 515743 | NORTWS31 13.800 | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 |  |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T5025515SP | FROM->TO | NORTHWEST (NORTWST3) 345/138/13.8KV TRANSFORMER CKT 1 | E | OKGE | OKGE |  |  | 2 | 514880 | NORTWST7 345.00 | 514879 | NORTWST4 138.00 | 515743 | NORTWS31 13.800 | 1 | 15SP | 493 | 493 | 0 |  | 93.8705 | 96.1 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST (NORTWST2) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514879 | NORTWST4 138.00 | 514880 | NORTWST7 345.00 | 515742 | NORTWS21 13.800 | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 |  |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T6935516SP | FROM->TO | NORTHWEST (NORTWST3) 345/138/13.8KV TRANSFORMER CKT 1 | E | OKGE | OKGE |  |  | 2 | 514880 | NORTWST7 345.00 | 514879 | NORTWST4 138.00 | 515743 | NORTWS31 13.800 | 1 | 16SP | 493 | 493 | 0 |  | 94.5826 | 96.8 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST (NORTWST2) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 514879 | NORTWST4 138.00 | 514880 | NORTWST7 345.00 | 515742 | NORTWS21 13.800 | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 |  | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T1025516SP | TO->FROM | PARK LANE - SEMINOLE 138KV CKT 1 | E | OKGE | OKGE | SHAWNEE | ARDMORE | 0 | 515044 | SEMINOL4 138.00 | 515178 | PARKLN 4 138.00 | 0 |  | 1 | 16SP | 287 | 287 | 0 | 96.3 | 96.3425 | 99.8 | [7 empty] | CATEGORYB | SINGLE | SEMINOLE - VANOSTP4 138.00 138KV CKT 1 | 0 | 515044 | SEMINOL4 138.00 | 515531 | VANOSTP4 138.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 |  | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T1315520SP | TO->FROM | PARK LANE - SEMINOLE 138KV CKT 1 | E | OKGE | OKGE | SHAWNEE | ARDMORE | 0 | 515044 | SEMINOL4 138.00 | 515178 | PARKLN 4 138.00 | 0 |  | 1 | 20SP | 287 | 287 | 0 | 99.6 | 99.6262 | 99.6 | [7 empty] | CATEGORYB | SINGLE | SEMINOLE - VANOSTP4 138.00 138KV CKT 1 | 0 | 515044 | SEMINOL4 138.00 | 515531 | VANOSTP4 138.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 |  | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T2515520SP | TO->FROM | OMMORANT - OSAGE 69KV CKT 1 | E | OKGE | OMPA | ENID | DOE | 0 | 514742 | OSGE 2 69.000 | 529241 | OMMORANT 69.000 | 0 |  | 1 | 20SP | 95 | 95 | 0 | 97.9 | 97.9 | 98 | [7 empty] | CATEGORYB | SINGLE | OMGONTER 69.000 - OMKAWS 69KV CKT 1 | 0 | 529245 | OMGONTER 69.000 | 529246 | OMKAWS 69.000 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T11705016SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 16SP | 250 | 250 | 250 | 99.6 | 71.4274 | 99.6 | [7 empty] | CATEGORYB | GENOUT | NO3_GEN-NORTH OMAHA 3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2014-10-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T12725516SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 16SP | 250 | 250 | 250 | 95.1 | 73.0152 | 95.2 | [7 empty] | CATEGORYB | GENOUT | SARPY3_GEN-SARPY COUNTY 3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2014-10-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T22095525SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 25SP | 250 | 250 | 250 | 103.9 | 73.1316 | 99.5 | [7 empty] | CATEGORYB | GENOUT | NO3_GEN-NORTH OMAHA 3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2014-10-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T11775025WP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 25WP | 250 | 250 | 250 | 98.4 | 67.4772 | 98.4 | [7 empty] | CATEGORYB | GENOUT | FRE8_GEN-FREMONT 8 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2014-10-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T65014WP | FROM->TO | SOUTHWEST 161/20.0KV TRANSFORMER CKT 1 | E | SPRM | SPRM | SPRM | SPRM | 0 | 549893 | JTEC GEN#2 120.000 | 549954 | JTEC 5161.00 | 0 |  | 1 | 14WP | 334 | 400 | 0 | 97 | 96.9898 | 97 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T175514WP | FROM->TO | SOUTHWEST 161/20.0KV TRANSFORMER CKT 1 | E | SPRM | SPRM | SPRM | SPRM | 0 | 549893 | JTEC GEN#2 120.000 | 549954 | JTEC 5161.00 | 0 |  | 1 | 14WP | 334 | 400 | 0 | 97 | 96.9898 | 97 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T265515SP | FROM->TO | SOUTHWEST 161/20.0KV TRANSFORMER CKT 1 | E | SPRM | SPRM | SPRM | SPRM | 0 | 549893 | JTEC GEN#2 120.000 | 549954 | JTEC 5161.00 | 0 |  | 1 | 15SP | 334 | 400 | 0 | 97 | 96.9898 | 97 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T75015WP | FROM->TO | SOUTHWEST 161/20.0KV TRANSFORMER CKT 1 | E | SPRM | SPRM | SPRM | SPRM | 0 | 549893 | JTEC GEN#2 120.000 | 549954 | JTEC 5161.00 | 0 |  | 1 | 15WP | 334 | 400 | 0 | 97 | 96.9898 | 97 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T165515WP | FROM->TO | SOUTHWEST 161/20.0KV TRANSFORMER CKT 1 | E | SPRM | SPRM | SPRM | SPRM | 0 | 549893 | JTEC GEN#2 120.000 | 549954 | JTEC 5161.00 | 0 |  | 1 | 15WP | 334 | 400 | 0 | 97 | 96.9898 | 97 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T255516SP | FROM->TO | SOUTHWEST 161/20.0KV TRANSFORMER CKT 1 | E | SPRM | SPRM | SPRM | SPRM | 0 | 549893 | JTEC GEN#2 120.000 | 549954 | JTEC 5161.00 | 0 |  | 1 | 16SP | 334 | 400 | 0 | 97 | 96.9898 | 97 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T55016WP | FROM->TO | SOUTHWEST 161/20.0KV TRANSFORMER CKT 1 | E | SPRM | SPRM | SPRM | SPRM | 0 | 549893 | JTEC GEN#2 120.000 | 549954 | JTEC 5161.00 | 0 |  | 1 | 16WP | 334 | 400 | 0 | 97 | 96.9898 | 97 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T145516WP | FROM->TO | SOUTHWEST 161/20.0KV TRANSFORMER CKT 1 | E | SPRM | SPRM | SPRM | SPRM | 0 | 549893 | JTEC GEN#2 120.000 | 549954 | JTEC 5161.00 | 0 |  | 1 | 16WP | 334 | 400 | 0 | 97 | 96.9898 | 97 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T325520SP | FROM->TO | SOUTHWEST 161/20.0KV TRANSFORMER CKT 1 | E | SPRM | SPRM | SPRM | SPRM | 0 | 549893 | JTEC GEN#2 120.000 | 549954 | JTEC 5161.00 | 0 |  | 1 | 20SP | 334 | 400 | 0 | 97 | 96.9898 | 97 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T115020WP | FROM->TO | SOUTHWEST 161/20.0KV TRANSFORMER CKT 1 | E | SPRM | SPRM | SPRM | SPRM | 0 | 549893 | JTEC GEN#2 120.000 | 549954 | JTEC 5161.00 | 0 |  | 1 | 20WP | 334 | 400 | 0 | 97 | 96.9898 | 97 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T145520WP | FROM->TO | SOUTHWEST 161/20.0KV TRANSFORMER CKT 1 | E | SPRM | SPRM | SPRM | SPRM | 0 | 549893 | JTEC GEN#2 120.000 | 549954 | JTEC 5161.00 | 0 |  | 1 | 20WP | 334 | 400 | 0 | 97 | 96.9898 | 97 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T515525SP | FROM->TO | SOUTHWEST 161/20.0KV TRANSFORMER CKT 1 | E | SPRM | SPRM | SPRM | SPRM | 0 | 549893 | JTEC GEN#2 120.000 | 549954 | JTEC 5161.00 | 0 |  | 1 | 25SP | 334 | 400 | 0 | 97 | 96.9898 | 97 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T155025WP | FROM->TO | SOUTHWEST 161/20.0KV TRANSFORMER CKT 1 | E | SPRM | SPRM | SPRM | SPRM | 0 | 549893 | JTEC GEN#2 120.000 | 549954 | JTEC 5161.00 | 0 |  | 1 | 25WP | 334 | 400 | 0 | 97 | 96.9898 | 97 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T205525WP | FROM->TO | SOUTHWEST 161/20.0KV TRANSFORMER CKT 1 | E | SPRM | SPRM | SPRM | SPRM | 0 | 549893 | JTEC GEN#2 120.000 | 549954 | JTEC 5161.00 | 0 |  | 1 | 25WP | 334 | 400 | 0 | 97 | 96.9898 | 97 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 |  | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T12035025SP | FROM->TO | CARLISLE INTERCHANGE - LP-DOUD_TP 3115.00 115KV CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 0 | 526160 | CARLISLE 3115.00 | 526162 | LP-DOUD_TP 3115.00 | 0 |  | 1 | 25SP | 159 | 160 | 0 | 98.1 | 98.1208 | 98.8 | [7 empty] | CATEGORYB | SINGLE | WOLFFORTH INTERCHANGE (WH 7001668) 230/115/13.2KV TRANSFORMER CKT 1 | 1 | 526524 | WOLFFORTH 3115.00 | 526525 | WOLFFORTH 6230.00 | 526522 | WOLFRTH_TR1113.200 | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 |  | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T8305520SP | FROM->TO | CASTRO COUNTY INTERCHANGE (ABB MLL92041) 115/69/13.2KV TRANSFORMER CKT 2 | E | SPS | SPS | SPS-CLHF | SPS-CLHF | 1 | 524746 | CASTRO_CNTY3115.00 | 524745 | CASTRO_CNTY269.000 | 524743 | CASTRO_TR2 113.200 | 2 | 20SP | 84 | 84 | 0 | 96.5 | 96.5492 | 96.6 | [7 empty] | CATEGORYB | SINGLE | CASTRO COUNTY INTERCHANGE (ABB MLL92042) 115/69/13.2KV TRANSFORMER CKT 1 | 1 | 524745 | CASTRO_CNTY269.000 | 524746 | CASTRO_CNTY3115.00 | 524744 | CASTRO_TR1 113.200 | 1 | Transfer Loading < 100% | [58 empty] | 2021-06-01
2013-AG2 | AFS8 |  | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T8285520SP | FROM->TO | CASTRO COUNTY INTERCHANGE (ABB MLL92042) 115/69/13.2KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CLHF | SPS-CLHF | 1 | 524746 | CASTRO_CNTY3115.00 | 524745 | CASTRO_CNTY269.000 | 524744 | CASTRO_TR1 113.200 | 1 | 20SP | 84 | 84 | 0 | 96.6 | 96.5557 | 96.6 | [7 empty] | CATEGORYB | SINGLE | CASTRO COUNTY INTERCHANGE (ABB MLL92041) 115/69/13.2KV TRANSFORMER CKT 2 | 1 | 524745 | CASTRO_CNTY269.000 | 524746 | CASTRO_CNTY3115.00 | 524743 | CASTRO_TR2 113.200 | 2 | Transfer Loading < 100% | [58 empty] | 2021-06-01
2013-AG2 | AFS8 |  |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T1635520SP | FROM->TO | CUNNINGHAM STATION - MADDOX STATION 115KV CKT 1 | E | SPS | SPS | SPS-PECO | SPS-HOBB | 0 | 527864 | CUNNINHAM 3115.00 | 528355 | MADDOX 3115.00 | 0 |  | 1 | 20SP | 160 | 160 | 0 |  | 75.8439 | 96.4 | [7 empty] | CATEGORYB | SINGLE | HOBBS INTERCHANGE - MADDOX STATION 115KV CKT 1 | 0 | 527891 | HOBBS_INT 3115.00 | 528355 | MADDOX 3115.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 |  | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T14305525SP | FROM->TO | DEAF SMITH COUNTY INTERCHANGE (LIKE POTTER) 230/115/13.2KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CLHF | SPS-CLHF | 1 | 524623 | DEAFSMITH 6230.00 | 524622 | DEAFSMITH 3115.00 | 524620 | DEFSMTH_TR1113.200 | 1 | 25SP | 250 | 250 | 0 | 95.7 | 95.7279 | 95.3 | [7 empty] | CATEGORYB | SINGLE | DEAF SMITH COUNTY INTERCHANGE (LIKE POTTER) 230/115/13.8KV TRANSFORMER CKT 2 | 1 | 524622 | DEAFSMITH 3115.00 | 524623 | DEAFSMITH 6230.00 | 524621 | DEFSMTH_TR2113.800 | 2 | Transfer Loading < 100%
2013-AG2 | AFS8 |  | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T2585025SP | FROM->TO | JONES STATION - LUBBOCK SOUTH INTERCHANGE 230KV CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 0 | 526337 | JONES 6230.00 | 526269 | LUBBCK_STH 6230.00 | 0 |  | 1 | 25SP | 502 | 502 | 0 | 97 | 97.0291 | 97.7 | [7 empty] | CATEGORYB | SINGLE | JONES STATION - LUBBOCK SOUTH INTERCHANGE 230KV CKT 2 | 0 | 526269 | LUBBCK_STH 6230.00 | 526337 | JONES 6230.00 | 0 |  | 2 | Transfer Loading < 100%
2013-AG2 | AFS8 |  | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T2575025SP | FROM->TO | JONES STATION - LUBBOCK SOUTH INTERCHANGE 230KV CKT 2 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 0 | 526337 | JONES 6230.00 | 526269 | LUBBCK_STH 6230.00 | 0 |  | 2 | 25SP | 502 | 502 | 0 | 97 | 97.0291 | 97.7 | [7 empty] | CATEGORYB | SINGLE | JONES STATION - LUBBOCK SOUTH INTERCHANGE 230KV CKT 1 | 0 | 526269 | LUBBCK_STH 6230.00 | 526337 | JONES 6230.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 |  | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T205520SP | FROM->TO | KRESS INTERCHANGE (ENRCO 136155) 115/69/13.2KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 1 | 525192 | KRESS_INT 3115.00 | 525191 | KRESS_INT 269.000 | 525190 | KRESS_TR1 113.200 | 1 | 20SP | 84 | 97 | 0 | 98.2 | 98.2293 | 98.2 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2021-06-01
2013-AG2 | AFS8 |  |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T29025525SP | TO->FROM | NORTHWEST INTERCHANGE - ROLLHILLS 3115.00 115KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524007 | ROLLHILLS 3115.00 | 524106 | NORTHWEST 3115.00 | 0 |  | 1 | 25SP | 120 | 154 | 0 |  | 101.6031 | 99.4 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 105 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 |  |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T28995525SP | TO->FROM | NORTHWEST INTERCHANGE - ROLLHILLS 3115.00 115KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524007 | ROLLHILLS 3115.00 | 524106 | NORTHWEST 3115.00 | 0 |  | 1 | 25SP | 120 | 154 | 0 |  | 100.4226 | 98.6 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 99 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T19215520SP | FROM->TO | PLANT X STATION 230/20.0KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 0 | 525494 | PLANT_X4 120.000 | 525481 | PLANT_X 6230.00 | 0 |  | 1 | 20SP | 215 | 215 | 0 |  | 90.2959 | 96.1421 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 92 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T29005525SP | FROM->TO | PLANT X STATION 230/20.0KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 0 | 525494 | PLANT_X4 120.000 | 525481 | PLANT_X 6230.00 | 0 |  | 1 | 25SP | 215 | 215 | 0 |  | 100.7277 | 98.5519 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 99 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T17665025WP | FROM->TO | PLANT X STATION 230/20.0KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 0 | 525494 | PLANT_X4 120.000 | 525481 | PLANT_X 6230.00 | 0 |  | 1 | 25WP | 215 | 215 | 0 |  | 95.7184 | 95.6177 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 68 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T22215525SP | FROM->TO | TOLK STATION EAST 230/24.0KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 0 | 525561 | TOLK_1 124.000 | 525524 | TOLK_EAST 6230.00 | 0 |  | 1 | 25SP | 728 | 728 | 0 | 95.7 | 95.684 | 95.8 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-04 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 |  | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T11885025SP | FROM->TO | TUCO INTERCHANGE (ENRCO 136401) 230/115/13.2KV TRANSFORMER CKT 2 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 1 | 525830 | TUCO_INT 6230.00 | 525828 | TUCO_INT 3115.00 | 525819 | TUCO_TR3 113.200 | 2 | 25SP | 250 | 288 | 0 | 97.4 | 97.432 | 99.1 | [7 empty] | CATEGORYB | SINGLE | TUCO INTERCHANGE (GE M102345) 230/115/13.2KV TRANSFORMER CKT 1 | 1 | 525828 | TUCO_INT 3115.00 | 525830 | TUCO_INT 6230.00 | 525821 | TUCO_TR4 113.200 | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 |  |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T1515520SP | FROM->TO | WOLFFORTH INTERCHANGE (WH 7001668) 230/115/13.2KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 1 | 526525 | WOLFFORTH 6230.00 | 526524 | WOLFFORTH 3115.00 | 526522 | WOLFRTH_TR1113.200 | 1 | 20SP | 120 | 154 | 0 |  | 94.9358 | 97.9 | [7 empty] | CATEGORYB | SINGLE | CARLISLE INTERCHANGE - LP-DOUD_TP 3115.00 115KV CKT 1 | 0 | 526160 | CARLISLE 3115.00 | 526162 | LP-DOUD_TP 3115.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2021-06-01
2013-AG2 | AFS8 |  | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T2425025SP | FROM->TO | WOLFFORTH INTERCHANGE (WH 7001668) 230/115/13.2KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 1 | 526525 | WOLFFORTH 6230.00 | 526524 | WOLFFORTH 3115.00 | 526522 | WOLFRTH_TR1113.200 | 1 | 25SP | 120 | 154 | 0 | 95.8 | 95.8034 | 95.9 | [7 empty] | CATEGORYB | SINGLE | STANTON SUB - TUCO INTERCHANGE 115KV CKT 1 | 0 | 525828 | TUCO_INT 3115.00 | 526076 | STANTON_W 3115.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2021-06-01
2013-AG2 | AFS8 |  | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T2625025SP | FROM->TO | WOLFFORTH INTERCHANGE (WH 7001668) 230/115/13.2KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 1 | 526525 | WOLFFORTH 6230.00 | 526524 | WOLFFORTH 3115.00 | 526522 | WOLFRTH_TR1113.200 | 1 | 25SP | 120 | 154 | 0 | 95.8 | 95.828 | 95.7 | [7 empty] | CATEGORYB | SINGLE | AMOCO TAP - SUNDOWN INTERCHANGE 115KV CKT 1 | 0 | 526434 | SUNDOWN 3115.00 | 526445 | AMOCO_TP 3115.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2021-06-01
2013-AG2 | AFS8 |  | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T19405025SP | FROM->TO | WOLFFORTH INTERCHANGE (WH 7001668) 230/115/13.2KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 1 | 526525 | WOLFFORTH 6230.00 | 526524 | WOLFFORTH 3115.00 | 526522 | WOLFRTH_TR1113.200 | 1 | 25SP | 120 | 154 | 0 | 95 | 95.022 | 95.6 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-T71 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2021-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T5075514WP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 14WP | 159.3 | 159.3 | 0 | 97.1 | 97.0837 | 97.2 | [7 empty] | CATEGORYB | NONSINGLE | SPSCONT-06 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T5445515SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 15SP | 159.3 | 159.3 | 0 | 98.4 | 98.3728 | 98.4 | [7 empty] | CATEGORYB | SINGLE | MINGO (MINGO) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 531429 | MINGO 3 115.00 | 531451 | MINGO 7 345.00 | 531452 | MINGTER1 13.800 | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T5475515SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 15SP | 159.3 | 159.3 | 0 | 98.3 | 98.3042 | 98.3 | [7 empty] | CATEGORYB | SINGLE | HOLCOMB (HOLCOMB) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 531448 | HOLCOMB3 115.00 | 531449 | HOLCOMB7 345.00 | 531450 | HOLCTER1 13.800 | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T1405515SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 15SP | 159.3 | 159.3 | 0 | 95.6 | 95.5736 | 95.6 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T9915515SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 15SP | 159.3 | 159.3 | 0 | 95.4 | 95.418 | 95.4 | [7 empty] | CATEGORYB | NONSINGLE | SPP-MKEC-01 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T9935515SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 15SP | 159.3 | 159.3 | 0 | 95.4 | 95.3548 | 95.4 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T1955515SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 15SP | 159.3 | 159.3 | 0 | 95.3 | 95.3322 | 95.3 | [7 empty] | CATEGORYB | SINGLE | GREENSBURG - SSTARTP3 115.00 115KV CKT 1 | 0 | 539664 | GRNBURG3 115.00 | 539763 | SSTARTP3 115.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNSLock |  | FDNSLock |  | 5 | 5 | 2013AG2AFS82T45515SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 15SP | 159.3 | 159.3 | 0 | 95.1 | 95.0755 | 95.1 | [7 empty] | CATEGORYB | SINGLE | CTU SUBLETTE - HASKELL 115KV CKT 1 | 0 | 531374 | HASKELL3 115.00 | 531442 | SAT-TAP3 115.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T7345516SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 16SP | 159.3 | 159.3 | 0 | 99.4 | 99.4367 | 99.4 | [7 empty] | CATEGORYB | SINGLE | HOLCOMB (HOLCOMB) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 531448 | HOLCOMB3 115.00 | 531449 | HOLCOMB7 345.00 | 531450 | HOLCTER1 13.800 | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T7305516SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 16SP | 159.3 | 159.3 | 0 | 99.2 | 99.2499 | 99.2 | [7 empty] | CATEGORYB | SINGLE | MINGO (MINGO) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 531429 | MINGO 3 115.00 | 531451 | MINGO 7 345.00 | 531452 | MINGTER1 13.800 | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T12825516SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 16SP | 159.3 | 159.3 | 0 | 96.4 | 96.3821 | 96.4 | [7 empty] | CATEGORYB | NONSINGLE | SPP-MKEC-01 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T12845516SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 16SP | 159.3 | 159.3 | 0 | 95.9 | 95.9321 | 95.9 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T1345516SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 16SP | 159.3 | 159.3 | 0 | 95.8 | 95.8098 | 95.8 | [7 empty] | CATEGORYB | SINGLE | CTU SUBLETTE - HASKELL 115KV CKT 1 | 0 | 531374 | HASKELL3 115.00 | 531442 | SAT-TAP3 115.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T2005516SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 16SP | 159.3 | 159.3 | 0 | 95.7 | 95.6673 | 95.7 | [7 empty] | CATEGORYB | SINGLE | GREENSBURG - SSTARTP3 115.00 115KV CKT 1 | 0 | 539664 | GRNBURG3 115.00 | 539763 | SSTARTP3 115.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T1315516SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 16SP | 159.3 | 159.3 | 0 | 95.9 | 95.8572 | 95.5 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T6655016SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 16SP | 159.3 | 159.3 | 0 | 95.5 | 95.5027 | 95.4 | [7 empty] | CATEGORYB | SINGLE | HOLCOMB (HOLCOMB) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 531448 | HOLCOMB3 115.00 | 531449 | HOLCOMB7 345.00 | 531450 | HOLCTER1 13.800 | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T1375516SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 16SP | 159.3 | 159.3 | 0 | 95.2 | 95.2125 | 95.2 | [7 empty] | CATEGORYB | SINGLE | HASKELL - SEWARD-3 115KV CKT 1 | 0 | 531374 | HASKELL3 115.00 | 531467 | SEWARD-3 115.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T8095020SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 20SP | 159.3 | 159.3 | 0 | 96.9 | 96.9204 | 97 | [7 empty] | CATEGORYB | SINGLE | HOLCOMB (HOLCOMB) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 531448 | HOLCOMB3 115.00 | 531449 | HOLCOMB7 345.00 | 531450 | HOLCTER1 13.800 | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T3205520SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 20SP | 159.3 | 159.3 | 0 | 96.6 | 96.6201 | 96.7 | [7 empty] | CATEGORYB | SINGLE | GREENSBURG - SSTARTP3 115.00 115KV CKT 1 | 0 | 539664 | GRNBURG3 115.00 | 539763 | SSTARTP3 115.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T14265520SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 20SP | 159.3 | 159.3 | 0 | 96.1 | 96.0899 | 96.2 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T2545520SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 20SP | 159.3 | 159.3 | 0 | 96.1 | 96.0679 | 96.1 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T2555520SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 20SP | 159.3 | 159.3 | 0 | 95.8 | 95.8447 | 95.9 | [7 empty] | CATEGORYB | SINGLE | CTU SUBLETTE - HASKELL 115KV CKT 1 | 0 | 531374 | HASKELL3 115.00 | 531442 | SAT-TAP3 115.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T5595525SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 25SP | 159.3 | 159.3 | 0 | 99.7 | 99.673 | 99.7 | [7 empty] | CATEGORYB | SINGLE | CTU SUBLETTE - HASKELL 115KV CKT 1 | 0 | 531374 | HASKELL3 115.00 | 531442 | SAT-TAP3 115.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T6455525SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 25SP | 159.3 | 159.3 | 0 | 98.3 | 98.3343 | 98.3 | [7 empty] | CATEGORYB | SINGLE | GREENSBURG - SSTARTP3 115.00 115KV CKT 1 | 0 | 539664 | GRNBURG3 115.00 | 539763 | SSTARTP3 115.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T5605525SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 25SP | 159.3 | 159.3 | 0 | 97.8 | 97.7994 | 97.8 | [7 empty] | CATEGORYB | SINGLE | HASKELL - SEWARD-3 115KV CKT 1 | 0 | 531374 | HASKELL3 115.00 | 531467 | SEWARD-3 115.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T22225525SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 25SP | 159.3 | 159.3 | 0 | 98.1 | 98.0814 | 97.5 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T12715025SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 25SP | 159.3 | 159.3 | 0 | 97.7 | 97.748 | 97 | [7 empty] | CATEGORYB | SINGLE | HOLCOMB (HOLCOMB) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 531448 | HOLCOMB3 115.00 | 531449 | HOLCOMB7 345.00 | 531450 | HOLCTER1 13.800 | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T5565525SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 25SP | 159.3 | 159.3 | 0 | 96.3 | 96.2782 | 96.8 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T5675525SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 25SP | 159.3 | 159.3 | 0 |  | 92.131 | 95.9 | [7 empty] | CATEGORYB | SINGLE | N-CIMRN3 115.00 - SEWARD-3 115KV CKT 1 | 0 | 531467 | SEWARD-3 115.00 | 539749 | N-CIMRN3 115.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T6445525SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 25SP | 159.3 | 159.3 | 0 |  | 92.1245 | 95.8 | [7 empty] | CATEGORYB | SINGLE | CIMARRON RIVER PLANT - N-CIMRN3 115.00 115KV CKT 1 | 0 | 539654 | CIM-PLT3 115.00 | 539749 | N-CIMRN3 115.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T12665025SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 25SP | 159.3 | 159.3 | 0 | 96 | 96.0404 | 95.5 | [7 empty] | CATEGORYB | SINGLE | MINGO (MINGO) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 531429 | MINGO 3 115.00 | 531451 | MINGO 7 345.00 | 531452 | MINGTER1 13.800 | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T5665525SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 25SP | 159.3 | 159.3 | 0 |  | 94.7708 | 95.4 | [7 empty] | CATEGORYB | SINGLE | MINGO - SETAB 345KV CKT 1 | 0 | 531451 | MINGO 7 345.00 | 531465 | SETAB 7 345.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T5575525SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 25SP | 159.3 | 159.3 | 0 | 95.3 | 95.3213 | 95.2 | [7 empty] | CATEGORYB | SINGLE | 5 HICKOCK - RUBART 3 115.00 115KV CKT 1 | 0 | 531200 | RUBART 3 115.00 | 531378 | HICKOCK3 115.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNSLock |  | FDNSLock |  | 5 | 5 | 2013AG2AFS82T15525WP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 25WP | 159.3 | 159.3 | 0 | 95.7 | 95.7215 | 95.7 | [7 empty] | CATEGORYB | SINGLE | CRKCK 3 115.00 - CUDAHY 115KV CKT 1 | 0 | 539659 | CUDAHY 3 115.00 | 539783 | CRKCK 3 115.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 |  |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T29055525SP | FROM->TO | PRATT (PRATT 3) 115/34.5/3.6KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 2 | 539687 | PRATT 3 115.00 | 539726 | PRATT 1 34.500 | 539929 | PRATT-T 3.6000 | 1 | 25SP | 28 | 28 | 28 |  | 97.0853 | 97.9 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 120 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 |  |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T26395025SP | FROM->TO | PRATT (PRATT 3) 115/34.5/3.6KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 2 | 539687 | PRATT 3 115.00 | 539726 | PRATT 1 34.500 | 539929 | PRATT-T 3.6000 | 1 | 25SP | 28 | 28 | 28 |  | 97.1998 | 97.1 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 118 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 |  |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T26405025SP | FROM->TO | PRATT (PRATT 3) 115/34.5/3.6KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 2 | 539687 | PRATT 3 115.00 | 539726 | PRATT 1 34.500 | 539929 | PRATT-T 3.6000 | 1 | 25SP | 28 | 28 | 28 |  | 97.2939 | 97 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 125 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 |  |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T7185515WP | TO->FROM | CLAY - SPRINGFIELD 161KV CKT 1 | E | SWPA | SPRM | EMINTH | SPRM | 0 | 505492 | SPRGFLD5 161.00 | 549970 | CLAY 5161.00 | 0 |  | 1 | 15WP | 189 | 189 | 0 |  | 94.8738 | 95.8 | [7 empty] | CATEGORYB | NONSINGLE | AI03 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2015-10-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T5105014WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 14WP | 68 | 68 | 0 | 98.6 | 98.577 | 98.8 | [7 empty] | CATEGORYB | NONSINGLE | EUREKA SPRIN | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T1345014WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 14WP | 68 | 68 | 0 | 98.6 | 98.5701 | 98.8 | [7 empty] | CATEGORYB | SINGLE | BERRYVILLE - GREEN FOREST 161KV CKT 1 | 0 | 338100 | 5BERRYV 161.00 | 338101 | 5GR FOR 161.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T1375014WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 14WP | 68 | 68 | 0 | 98.4 | 98.3744 | 98.5 | [7 empty] | CATEGORYB | SINGLE | BERRYVILLE - OSAGE CREEK (AECC) 161KV CKT 1 | 0 | 338100 | 5BERRYV 161.00 | 338682 | 5OSAGE# 161.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T5305014WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 14WP | 68 | 68 | 0 | 98.6 | 98.5704 | 98.5 | [7 empty] | CATEGORYB | GENOUT | GEN505484 2-BEAVER | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T5315514WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 14WP | 68 | 68 | 0 | 98 | 97.9998 | 97.8 | [7 empty] | CATEGORYB | GENOUT | GEN505484 2-BEAVER | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T1495514WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 14WP | 68 | 68 | 0 | 98 | 97.9995 | 97.8 | [7 empty] | CATEGORYB | SINGLE | BERRYVILLE - GREEN FOREST 161KV CKT 1 | 0 | 338100 | 5BERRYV 161.00 | 338101 | 5GR FOR 161.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T5165514WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 14WP | 68 | 68 | 0 | 98 | 98.0073 | 97.8 | [7 empty] | CATEGORYB | NONSINGLE | EUREKA SPRIN | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T1515514WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 14WP | 68 | 68 | 0 | 97.7 | 97.6528 | 97.5 | [7 empty] | CATEGORYB | SINGLE | BERRYVILLE - OSAGE CREEK (AECC) 161KV CKT 1 | 0 | 338100 | 5BERRYV 161.00 | 338682 | 5OSAGE# 161.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T6415014WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 14WP | 68 | 68 | 0 | 97.3 | 97.2949 | 97.4 | [7 empty] | CATEGORYB | SWSHUNT | GREEN FOREST 161KV SWITCHED SHUNT | 0 | 338101 | 5GR FOR 161.00 | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T1425014WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 14WP | 68 | 68 | 0 | 97.1 | 97.0636 | 97 | [7 empty] | CATEGORYB | SINGLE | HARRISON SOUTH AECC - HARRISON-EAST 161KV CKT 1 | 0 | 338104 | 5HARR-E 161.00 | 338681 | 5HARR-S# 161.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T1325014WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 14WP | 68 | 68 | 0 | 97 | 96.9883 | 96.8 | [7 empty] | CATEGORYB | SINGLE | BEE BRANCH (AECC) - QUITMAN 161KV CKT 1 | 0 | 337926 | 5QUITMN 161.00 | 338831 | 5BEE BR# 161.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T1535514WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 14WP | 68 | 68 | 0 | 96.8 | 96.7597 | 96.6 | [7 empty] | CATEGORYB | SINGLE | HARRISON SOUTH AECC - HARRISON-EAST 161KV CKT 1 | 0 | 338104 | 5HARR-E 161.00 | 338681 | 5HARR-S# 161.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T5935514WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 14WP | 68 | 68 | 0 | 96.8 | 96.7965 | 96.6 | [7 empty] | CATEGORYB | SWSHUNT | GREEN FOREST 161KV SWITCHED SHUNT | 0 | 338101 | 5GR FOR 161.00 | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T5225514WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 14WP | 68 | 68 | 0 | 96.3 | 96.3211 | 96.2 | [7 empty] | CATEGORYB | NONSINGLE | A059 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T1615514WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 14WP | 68 | 68 | 0 | 96 | 95.968 | 95.9 | [7 empty] | CATEGORYB | SINGLE | NEWPORT - NEWPORT INDUSTRIAL 161KV CKT 1 | 0 | 338151 | 5NEWPO 161.00 | 338173 | 5NEW-IN 161.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T1625514WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 14WP | 68 | 68 | 0 |  | 95.7931 | 95.7 | [7 empty] | CATEGORYB | SINGLE | NEWPORT AB - NEWPORT INDUSTRIAL 161KV CKT 1 | 0 | 338172 | 5NEW-AB 161.00 | 338173 | 5NEW-IN 161.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T75015SP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 15SP | 68 | 68 | 0 | 98.5 | 98.4642 | 98.3 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T95515SP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 15SP | 68 | 68 | 0 | 98.3 | 98.3491 | 98.1 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T2165015WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 15WP | 68 | 68 | 0 | 98.7 | 98.6638 | 98.4 | [7 empty] | CATEGORYB | SINGLE | BERRYVILLE - GREEN FOREST 161KV CKT 1 | 0 | 338100 | 5BERRYV 161.00 | 338101 | 5GR FOR 161.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T2195015WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 15WP | 68 | 68 | 0 | 98.7 | 98.6643 | 98.4 | [7 empty] | CATEGORYB | SINGLE | BERRYVILLE - OSAGE CREEK (AECC) 161KV CKT 1 | 0 | 338100 | 5BERRYV 161.00 | 338682 | 5OSAGE# 161.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T8215015WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 15WP | 68 | 68 | 0 | 98.7 | 98.6655 | 98.4 | [7 empty] | CATEGORYB | NONSINGLE | EUREKA SPRIN | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T9315015WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 15WP | 68 | 68 | 0 | 98.7 | 98.6636 | 98.4 | [7 empty] | CATEGORYB | GENOUT | GEN505484 2-BEAVER | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T10355015WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 15WP | 68 | 68 | 0 | 98.2 | 98.1924 | 98.1 | [7 empty] | CATEGORYB | SWSHUNT | GREEN FOREST 161KV SWITCHED SHUNT | 0 | 338101 | 5GR FOR 161.00 | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T2145015WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 15WP | 68 | 68 | 0 | 98.2 | 98.2282 | 98 | [7 empty] | CATEGORYB | SINGLE | BEE BRANCH (AECC) - QUITMAN 161KV CKT 1 | 0 | 337926 | 5QUITMN 161.00 | 338831 | 5BEE BR# 161.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T2245015WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 15WP | 68 | 68 | 0 | 98 | 97.9521 | 97.9 | [7 empty] | CATEGORYB | SINGLE | HARRISON SOUTH AECC - HARRISON-EAST 161KV CKT 1 | 0 | 338104 | 5HARR-E 161.00 | 338681 | 5HARR-S# 161.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T9555515WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 15WP | 68 | 68 | 0 | 97.5 | 97.4798 | 97.5 | [7 empty] | CATEGORYB | GENOUT | GEN505484 2-BEAVER | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T10145515WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 15WP | 68 | 68 | 0 | 97.4 | 97.3773 | 97.5 | [7 empty] | CATEGORYB | SWSHUNT | GREEN FOREST 161KV SWITCHED SHUNT | 0 | 338101 | 5GR FOR 161.00 | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T2335515WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 15WP | 68 | 68 | 0 | 97.5 | 97.48 | 97.5 | [7 empty] | CATEGORYB | SINGLE | BERRYVILLE - GREEN FOREST 161KV CKT 1 | 0 | 338100 | 5BERRYV 161.00 | 338101 | 5GR FOR 161.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T8495515WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 15WP | 68 | 68 | 0 | 97.5 | 97.4865 | 97.5 | [7 empty] | CATEGORYB | NONSINGLE | EUREKA SPRIN | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T2355515WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 15WP | 68 | 68 | 0 | 97.5 | 97.48 | 97.5 | [7 empty] | CATEGORYB | SINGLE | BERRYVILLE - OSAGE CREEK (AECC) 161KV CKT 1 | 0 | 338100 | 5BERRYV 161.00 | 338682 | 5OSAGE# 161.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T8355015WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 15WP | 68 | 68 | 0 | 97.4 | 97.3935 | 97.3 | [7 empty] | CATEGORYB | NONSINGLE | A059 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T2375515WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 15WP | 68 | 68 | 0 | 97.1 | 97.0878 | 97.3 | [7 empty] | CATEGORYB | SINGLE | HARRISON SOUTH AECC - HARRISON-EAST 161KV CKT 1 | 0 | 338104 | 5HARR-E 161.00 | 338681 | 5HARR-S# 161.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T235015WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 15WP | 68 | 68 | 0 | 97.3 | 97.3182 | 97.1 | [7 empty] | CATEGORYB | SINGLE | BEAVER - EUREKA SPRINGS 161KV CKT 1 | 0 | 505480 | BEAVER 5 161.00 | 506932 | EUREKA 5 161.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T8615515WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 15WP | 68 | 68 | 0 | 97 | 96.9755 | 97.1 | [7 empty] | CATEGORYB | NONSINGLE | A059 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T205015WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 15WP | 68 | 68 | 0 |  | 96.9218 | 97 | [7 empty] | CATEGORYB | SINGLE | AVOCA - EAST ROGERS 161KV CKT 1 | 0 | 504000 | AVOCA 5 161.00 | 506931 | EROGERS5 161.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T2315015WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 15WP | 68 | 68 | 0 |  | 96.996 | 96.9 | [7 empty] | CATEGORYB | SINGLE | NEWPORT - NEWPORT INDUSTRIAL 161KV CKT 1 | 0 | 338151 | 5NEWPO 161.00 | 338173 | 5NEW-IN 161.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T2465515WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 15WP | 68 | 68 | 0 |  | 95.9504 | 96.3 | [7 empty] | CATEGORYB | SINGLE | NEWPORT - NEWPORT INDUSTRIAL 161KV CKT 1 | 0 | 338151 | 5NEWPO 161.00 | 338173 | 5NEW-IN 161.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T65016SP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 16SP | 68 | 68 | 0 | 98.5 | 98.4619 | 98.1 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T75516SP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 16SP | 68 | 68 | 0 | 98.2 | 98.1777 | 98.1 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T2435016WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 16WP | 68 | 68 | 0 | 100.1 | 100.0551 | 99.8 | [7 empty] | CATEGORYB | SINGLE | BEE BRANCH (AECC) - CLINTON 161KV CKT 1 | 0 | 338831 | 5BEE BR# 161.00 | 338833 | 5CLIN-IN# 161.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T2445016WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 16WP | 68 | 68 | 0 | 99.4 | 99.444 | 99.1 | [7 empty] | CATEGORYB | SINGLE | CLINTON - CLINTON WEST (AECC) 161KV CKT 1 | 0 | 338832 | 5CLIN-W# 161.00 | 338833 | 5CLIN-IN# 161.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T8735016WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 16WP | 68 | 68 | 0 | 98.9 | 98.858 | 98.6 | [7 empty] | CATEGORYB | NONSINGLE | EUREKA SPRIN | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T10865016WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 16WP | 68 | 68 | 0 | 98.6 | 98.6403 | 98.4 | [7 empty] | CATEGORYB | SWSHUNT | GREEN FOREST 161KV SWITCHED SHUNT | 0 | 338101 | 5GR FOR 161.00 | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T2305016WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 16WP | 68 | 68 | 0 | 98.3 | 98.2523 | 98.4 | [7 empty] | CATEGORYB | SINGLE | HARRISON SOUTH AECC - HARRISON-EAST 161KV CKT 1 | 0 | 338104 | 5HARR-E 161.00 | 338681 | 5HARR-S# 161.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T2255016WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 16WP | 68 | 68 | 0 | 98.6 | 98.6344 | 98.4 | [7 empty] | CATEGORYB | SINGLE | BERRYVILLE - GREEN FOREST 161KV CKT 1 | 0 | 338100 | 5BERRYV 161.00 | 338101 | 5GR FOR 161.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T3175016WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 16WP | 68 | 68 | 0 | 98.6 | 98.6344 | 98.4 | [7 empty] | CATEGORYB | SINGLE | BERRYVILLE - KINGRIV5 161.00 161KV CKT 1 | 0 | 506988 | KINGRIV5 161.00 | 338100 | 5BERRYV 161.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T9785016WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 16WP | 68 | 68 | 0 | 98.6 | 98.635 | 98.4 | [7 empty] | CATEGORYB | GENOUT | GEN505484 2-BEAVER | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T2695016WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 16WP | 68 | 68 | 0 | 98.4 | 98.4109 | 98.2 | [7 empty] | CATEGORYB | SINGLE | JONESBORO - JONESBORO 161KV CKT 1 | 0 | 505418 | JONESBO5 161.00 | 338170 | 5JONES 161.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T235016WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 16WP | 68 | 68 | 0 | 98.3 | 98.27 | 98 | [7 empty] | CATEGORYB | SINGLE | BEAVER - EUREKA SPRINGS 161KV CKT 1 | 0 | 505480 | BEAVER 5 161.00 | 506932 | EUREKA 5 161.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T2395016WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 16WP | 68 | 68 | 0 | 98 | 98.0412 | 97.9 | [7 empty] | CATEGORYB | SINGLE | NEWPORT - NEWPORT INDUSTRIAL 161KV CKT 1 | 0 | 338151 | 5NEWPO 161.00 | 338173 | 5NEW-IN 161.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T2525516WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 16WP | 68 | 68 | 0 | 97.4 | 97.3702 | 97.6 | [7 empty] | CATEGORYB | SINGLE | NEWPORT AB - NEWPORT INDUSTRIAL 161KV CKT 1 | 0 | 338172 | 5NEW-AB 161.00 | 338173 | 5NEW-IN 161.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T355516WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 16WP | 68 | 68 | 0 |  | 96.9772 | 97.4 | [7 empty] | CATEGORYB | SINGLE | AVOCA - EAST ROGERS 161KV CKT 1 | 0 | 504000 | AVOCA 5 161.00 | 506931 | EROGERS5 161.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T2725516WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 16WP | 68 | 68 | 0 | 97.2 | 97.212 | 97.4 | [7 empty] | CATEGORYB | SINGLE | JONESBORO - JONESBORO 161KV CKT 1 | 0 | 505418 | JONESBO5 161.00 | 338170 | 5JONES 161.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T125520SP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 20SP | 68 | 68 | 0 | 98.6 | 98.5746 | 98.4 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T105020SP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 20SP | 68 | 68 | 0 | 98.8 | 98.8439 | 98.3 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T35520WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 20WP | 68 | 68 | 0 | 97.5 | 97.5143 | 97.8 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T65020WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 20WP | 68 | 68 | 0 | 96 | 96.0206 | 95.6 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T205525SP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 25SP | 68 | 68 | 0 | 98 | 97.9835 | 97.9 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T205025SP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 25SP | 68 | 68 | 0 | 97.8 | 97.7753 | 97.2 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T65525WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 25WP | 68 | 68 | 0 | 96.8 | 96.7608 | 96.7 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T85025WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 25WP | 68 | 68 | 0 | 97.1 | 97.101 | 96.4 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100% | [58 empty] | 2015-06-01
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T11335015SP | FROM->TO | DARDANELLE 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505510 | DAR1&2 1 13.800 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 15SP | 76 | 76 | 0 |  | 98.6518 | 98.6498 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 55 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T11325015SP | FROM->TO | DARDANELLE 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505512 | DAR3&4 1 13.800 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 15SP | 76 | 76 | 0 |  | 97.9783 | 97.9832 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 54 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T11945515SP | FROM->TO | DARDANELLE 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505510 | DAR1&2 1 13.800 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 15SP | 76 | 76 | 0 |  | 97.23 | 97.2434 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 52 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T11935515SP | FROM->TO | DARDANELLE 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505512 | DAR3&4 1 13.800 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 15SP | 76 | 76 | 0 |  | 96.5756 | 96.5891 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 51 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T17515016SP | FROM->TO | DARDANELLE 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505510 | DAR1&2 1 13.800 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 16SP | 76 | 76 | 0 |  | 98.6524 | 98.6572 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 56 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T17505016SP | FROM->TO | DARDANELLE 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505512 | DAR3&4 1 13.800 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 16SP | 76 | 76 | 0 |  | 97.9855 | 97.9902 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 55 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T18455516SP | FROM->TO | DARDANELLE 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505510 | DAR1&2 1 13.800 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 16SP | 76 | 76 | 0 |  | 95.87 | 95.9034 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 52 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T18445516SP | FROM->TO | DARDANELLE 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505512 | DAR3&4 1 13.800 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 16SP | 76 | 76 | 0 |  | 95.2044 | 95.238 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 51 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T19185520SP | FROM->TO | DARDANELLE 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505510 | DAR1&2 1 13.800 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 20SP | 76 | 76 | 0 |  | 98.6553 | 98.6594 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 56 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T18405020SP | FROM->TO | DARDANELLE 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505510 | DAR1&2 1 13.800 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 20SP | 76 | 76 | 0 |  | 98.6453 | 98.65 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 61 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T19175520SP | FROM->TO | DARDANELLE 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505512 | DAR3&4 1 13.800 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 20SP | 76 | 76 | 0 |  | 97.9884 | 97.9924 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 55 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T18395020SP | FROM->TO | DARDANELLE 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505512 | DAR3&4 1 13.800 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 20SP | 76 | 76 | 0 |  | 97.9784 | 97.983 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 60 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T28985525SP | FROM->TO | DARDANELLE 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505510 | DAR1&2 1 13.800 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 25SP | 76 | 76 | 0 |  | 98.6483 | 98.6594 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 67 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T26385025SP | FROM->TO | DARDANELLE 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505510 | DAR1&2 1 13.800 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 25SP | 76 | 76 | 0 |  | 98.6453 | 98.6499 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 66 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T28975525SP | FROM->TO | DARDANELLE 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505512 | DAR3&4 1 13.800 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 25SP | 76 | 76 | 0 |  | 97.9815 | 97.9924 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 66 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T26375025SP | FROM->TO | DARDANELLE 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505512 | DAR3&4 1 13.800 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 25SP | 76 | 76 | 0 |  | 97.9784 | 97.9829 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 65 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T6035514WP | FROM->TO | TABLE ROCK 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505476 | TBR1&2 1 13.800 | 505472 | TABLE R5 161.00 | 0 |  | 1 | 14WP | 121 | 121 | 0 |  | 96.4594 | 96.4673 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 37 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T10245515WP | FROM->TO | TABLE ROCK 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505476 | TBR1&2 1 13.800 | 505472 | TABLE R5 161.00 | 0 |  | 1 | 15WP | 121 | 121 | 0 |  | 97.1303 | 97.2918 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 40 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T10235515WP | FROM->TO | TABLE ROCK 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505478 | TBR3&4 1 13.800 | 505472 | TABLE R5 161.00 | 0 |  | 1 | 15WP | 121 | 121 | 0 |  | 96.4969 | 96.6585 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 39 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T9865516WP | FROM->TO | TABLE ROCK 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505476 | TBR1&2 1 13.800 | 505472 | TABLE R5 161.00 | 0 |  | 1 | 16WP | 121 | 121 | 0 |  | 98.4678 | 98.6737 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 40 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T9855516WP | FROM->TO | TABLE ROCK 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505478 | TBR3&4 1 13.800 | 505472 | TABLE R5 161.00 | 0 |  | 1 | 16WP | 121 | 121 | 0 |  | 97.4342 | 97.6756 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 39 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T11475520WP | FROM->TO | TABLE ROCK 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505476 | TBR1&2 1 13.800 | 505472 | TABLE R5 161.00 | 0 |  | 1 | 20WP | 121 | 121 | 0 |  | 98.6697 | 98.6742 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 42 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T11465520WP | FROM->TO | TABLE ROCK 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505478 | TBR3&4 1 13.800 | 505472 | TABLE R5 161.00 | 0 |  | 1 | 20WP | 121 | 121 | 0 |  | 98.0985 | 98.103 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 41 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T15685525WP | FROM->TO | TABLE ROCK 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505476 | TBR1&2 1 13.800 | 505472 | TABLE R5 161.00 | 0 |  | 1 | 25WP | 121 | 121 | 0 |  | 98.6685 | 98.6727 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 41 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T15675525WP | FROM->TO | TABLE ROCK 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505478 | TBR3&4 1 13.800 | 505472 | TABLE R5 161.00 | 0 |  | 1 | 25WP | 121 | 121 | 0 |  | 98.0974 | 98.1016 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 40 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 |  |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T26425025SP | TO->FROM | MONT 7 115.00 - WILLISTON27 115.00 115KV CKT 1 | E | WAPA | WAPA | WAPA_1602 | BEPC_1628 | 0 | 652391 | WILLISTON27 115.00 | 659360 | MONT 7 115.00 | 0 |  | 1 | 25SP | 120 | 120 | 0 |  | 98.0761 | 98.1 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 190 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 |  |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T29075525SP | TO->FROM | MONT 7 115.00 - WILLISTON27 115.00 115KV CKT 1 | E | WAPA | WAPA | WAPA_1602 | BEPC_1628 | 0 | 652391 | WILLISTON27 115.00 | 659360 | MONT 7 115.00 | 0 |  | 1 | 25SP | 120 | 120 | 0 |  | 98.0946 | 98.1 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 192 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T1945015SP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 15SP | 103 | 129 | 0 | 98.1 | 98.0568 | 98 | [7 empty] | CATEGORYB | SINGLE | ANTELOPE VALLEY - CHARLIE CREEK 345KV CKT 1 | 0 | 659101 | ANTELOP3 345.00 | 659183 | CHAR.CK3 345.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2014-10-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T2285515SP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 15SP | 103 | 129 | 0 | 98.1 | 98.086 | 98 | [7 empty] | CATEGORYB | SINGLE | ANTELOPE VALLEY - CHARLIE CREEK 345KV CKT 1 | 0 | 659101 | ANTELOP3 345.00 | 659183 | CHAR.CK3 345.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2014-10-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T1865016SP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 16SP | 103 | 129 | 0 | 98.1 | 98.0649 | 98 | [7 empty] | CATEGORYB | SINGLE | ANTELOPE VALLEY - CHARLIE CREEK 345KV CKT 1 | 0 | 659101 | ANTELOP3 345.00 | 659183 | CHAR.CK3 345.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2014-10-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T2435516SP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 16SP | 103 | 129 | 0 | 98 | 98.046 | 98 | [7 empty] | CATEGORYB | SINGLE | ANTELOPE VALLEY - CHARLIE CREEK 345KV CKT 1 | 0 | 659101 | ANTELOP3 345.00 | 659183 | CHAR.CK3 345.00 | 0 |  | 1 | Transfer Loading < 100% | [58 empty] | 2014-10-01
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T1465515SP | FROM->TO | LAWRENCE ENERGY CENTER UNIT 5 230/24.0KV TRANSFORMER CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532663 | LEC U5 24.000 | 532854 | LEC U5 6 230.00 | 0 |  | 1 | 15SP | 448 | 448 | 0 | 95.6 | 95.6145 | 95.6 | [7 empty] | CATEGORYB | SINGLE | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T1475516SP | FROM->TO | LAWRENCE ENERGY CENTER UNIT 5 230/24.0KV TRANSFORMER CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532663 | LEC U5 24.000 | 532854 | LEC U5 6 230.00 | 0 |  | 1 | 16SP | 448 | 448 | 0 | 95.5 | 95.5164 | 95.5 | [7 empty] | CATEGORYB | SINGLE | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T5735525SP | FROM->TO | LAWRENCE ENERGY CENTER UNIT 5 230/24.0KV TRANSFORMER CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532663 | LEC U5 24.000 | 532854 | LEC U5 6 230.00 | 0 |  | 1 | 25SP | 448 | 448 | 0 | 95 | 95.0345 | 95.1 | [7 empty] | CATEGORYB | SINGLE | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | INVALID | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T1315025SP | FROM->TO | ANADARKO - BLUCAN5 4 138.00 138KV CKT 1 | E | WFEC | WFEC | WFEC-RED RIV | WFEC-RED RIV | 0 | 520814 | ANADARK4 138.00 | 521129 | BLUCAN5 4 138.00 | 0 |  | 1 | 25SP | 132 | 143 | 143 | 99.9 | 99.8818 | 98.4135 | [7 empty] | CATEGORYB | SINGLE | LAWTON 112TH & WEST GORE - LAWTON AIRGAS TAP 138KV CKT 1 | 0 | 511488 | 112GORE4 138.00 | 511510 | LAIRGST4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 |  | FDNS |  | FDNS |  | 5 | 0 | 2013AG2AFS81T1235025SP | FROM->TO | ANADARKO - BLUCAN5 4 138.00 138KV CKT 1 | E | WFEC | WFEC | WFEC-RED RIV | WFEC-RED RIV | 0 | 520814 | ANADARK4 138.00 | 521129 | BLUCAN5 4 138.00 | 0 |  | 1 | 25SP | 132 | 143 | 143 | 96.7 | 96.6681 | 95.1 | [7 empty] | CATEGORYB | SINGLE | CACHE - SNYDER 138KV CKT 1 | 0 | 511435 | SNYDER-4 138.00 | 511500 | CACHE4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T18385516SP | FROM->TO | DUKE MCADAMS 500/18.0KV TRANSFORMER CKT 1 | E |  |  | EES_MISS | EES_MISS | 0 | 337007 | 1ATTALA G2 18.000 | 337005 | 8ATTALA 500.00 | 0 |  | 1 | 16SP | 193 | 193 | 0 |  | 99.6138 | 99.6757 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 5 | 2013AG2AFS81T18375516SP | FROM->TO | DUKE MCADAMS 500/18.0KV TRANSFORMER CKT 1 | E |  |  | EES_MISS | EES_MISS | 0 | 337006 | 1ATTALA G1 18.000 | 337005 | 8ATTALA 500.00 | 0 |  | 1 | 16SP | 193 | 193 | 0 |  | 99.6138 | 99.6756 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T17465016SP | FROM->TO | DUKE MCADAMS 500/18.0KV TRANSFORMER CKT 1 | E |  |  | EES_MISS | EES_MISS | 0 | 337007 | 1ATTALA G2 18.000 | 337005 | 8ATTALA 500.00 | 0 |  | 1 | 16SP | 193 | 193 | 0 |  | 98.4288 | 98.4764 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 | GSU |  |  | FDNS |  | 5 | 0 | 2013AG2AFS81T17455016SP | FROM->TO | DUKE MCADAMS 500/18.0KV TRANSFORMER CKT 1 | E |  |  | EES_MISS | EES_MISS | 0 | 337006 | 1ATTALA G1 18.000 | 337005 | 8ATTALA 500.00 | 0 |  | 1 | 16SP | 193 | 193 | 0 |  | 98.4287 | 98.4763 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2013-AG2 | AFS8 |  | FDNS |  | FDNS |  | 5 | 5 | 2013AG2AFS81T425525WP | FROM->TO | SPSNORTH_STX | E |  |  |  |  | SPSNORTH_STX | 0 |  | 0 |  | 0 |  |  | 25WP | 980 | 980 | 980 | 96.6 | 96.6849 | 97.1 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%