## Table1
Customer | Study Number | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date without interim redispatch (ACA Parameter 3) | Deferred Stop Date without interim redispatch | Start Date with interim redispatch | Stop Date with interim redispatch | Minimum Allocated ATC (MW) within reservation period | Season of Minimum Allocated ATC within reservation period
AEPM | 2013-AG3-003 | 78775996 | OKGE | CSWS | 200 | 2016-01-01 | 2036-01-01 | 2016-01-01 | 2036-01-01 | 2016-01-01 | 2036-01-01 | 0 | 16SP
AEPM | 2013-AG3-004 | 78776033 | SPS | CSWS | 200 | 2016-01-01 | 2036-01-01 | 2016-01-01 | 2036-01-01 | 2016-01-01 | 2036-01-01 | 0 | 16SP
AEPM | 2013-AG3-005 | 78776041 | OKGE | CSWS | 199 | 2016-01-01 | 2036-01-01 | 2016-01-01 | 2036-01-01 | 2016-01-01 | 2036-01-01 | 0 | 16SP
ETEC | 2013-AG3-006 | 78774012 | CSWS | CSWS | 31 | 2015-01-01 | 2024-01-01 | 2015-06-01 | 2024-06-01 | 2015-06-01 | 2024-06-01 | 0 | 15SP
OMPA | 2013-AG3-025 | 78697838 | OKGE | OKGE | 4 | 2014-10-01 | 2040-12-01 | 2015-06-01 | 2041-08-01 | 2015-06-01 | 2041-08-01 | 0 | 15SP
SPSM | 2013-AG3-027 | 78751808 | SPS | SPS | 250 | 2015-12-01 | 2035-12-01 | 2018-12-15 | 2035-12-01 | 2015-12-01 | 2035-12-01 | 0 | 16SP
TEXL | 2013-AG3-028 | 78773933 | CSWS | CSWS | 50 | 2015-01-01 | 2025-01-01 | 2015-06-01 | 2025-06-01 | 2015-06-01 | 2025-06-01 | 0 | 15SP
TEXL | 2013-AG3-029 | 78773967 | CSWS | CSWS | 27 | 2015-01-01 | 2030-01-01 | 2015-06-01 | 2030-06-01 | 2015-06-01 | 2030-06-01 | 0 | 15SP
961
Note 1: Start and Stop Dates with interim redispatch are determined based on customers choosing option to pursue redispatch to start service at Requested Start and Stop Dates or earliest date possible.
Note 2: Start dates with and without redispatch are based on the assumed completion dates of previous Aggregate Transmission Service Studies currently being conducted. Actual start dates may differ from the potential start dates upon completion of the previous studies.
Note 3: Request is unable to be deferred due to fixed stop dates.
Note 4: Transmission customer did not select “remain in the study using interim redispatch” option.

## Table2
Customer | Study Number | Reservation | Engineering and Construction Cost of Upgrades Allocated to Customer for Revenue Requirements | 1Letter of Credit Amount Required (ACA Parameter 5) | 2Potential Base Plan Engineering and Construction Funding Allowable | Notes | 4Additional Engineering and Construction Cost for 3rd Party Upgrades (ACA Parameter 2) | 3 5Total Revenue Requirements for Assigned Upgrades Over Term of Reservation WITH Potential Base Plan Funding Allocation | Point-to-Point Base Rate Over Reservation Period | 4Total Cost of Reservation Assignable to Customer Contingent Upon Base Plan Funding | Directly Assigned Upgrade Cost (DAUC) (ACA Parameter 1)
AEPM | 2013-AG3-003 | 78775996 | 0 | 0 | 0 |  | 0 | 0 | 0 | Schedule 9 & 11 Charges | 0
AEPM | 2013-AG3-004 | 78776033 | 0 | 0 | 0 |  | 0 | 0 | 0 | Schedule 9 & 11 Charges | 0
AEPM | 2013-AG3-005 | 78776041 | 0 | 0 | 0 |  | 0 | 0 | 0 | Schedule 9 & 11 Charges | 0
ETEC | 2013-AG3-006 | 78774012 | 0 | 0 | 0 |  | 0 | 0 | 0 | Schedule 9 & 11 Charges | 0
OMPA | 2013-AG3-025 | 78697838 | 0 | 0 | 0 |  | 0 | 0 | 0 | Schedule 9 & 11 Charges | 0
SPSM | 2013-AG3-027 | 78751808 | 9485379 | 0 | 9485379 |  | 0 | 0 | 0 | Schedule 9 & 11 Charges | 0
TEXL | 2013-AG3-028 | 78773933 | 0 | 0 | 0 |  | 0 | 0 | 0 | Schedule 9 & 11 Charges | 0
TEXL | 2013-AG3-029 | 78773967 | 0 | 0 | 0 |  | 0 | 0 | 0 | Schedule 9 & 11 Charges | 0
Grand Total |  |  | 9485379 |  | 9485379 |  |  | 0 |  |  | 0
Note 1: Letter of Credit required for financial security for transmission owner for network upgrades is determined by allocated engineering and construction costs less engineering and construction costs for upgrades when network customer is the transmission owner less the E & C allocation of expedited projects. Letter of Credit is required for upgrades assigned to PTP requests. The amount of the letter of credit will be adjusted down on an annual basis to reflect cost recovery based on revenue allocation. This letter of credit is not required for those facilities that are fully base plan funded. The Letter Of Credit Amount listed is based on meeting OATT Attachment J requirements for base plan funding.
Note 2: If potential base plan funding is applicable, this value is the lesser of the Engineering and Construction costs of assignable upgrades or the value of base plan funding calculated pursuant to Attachment J, Section III B criteria. Allocation of base plan funding is contingent upon verification of customer agreements meeting Attachment J, Section II B criteria. Not applicable if Point-to-Point base rate exceeds revenue requirements.
Note 3: Revenue Requirements (RR) are based upon deferred end dates if applicable. Deferred dates are based upon customer's choice to pursue redispatch. Achievable Base Plan Avoided RR in the case of a Base Plan upgrade being displaced or deferred by an earlier in service date for a Requested Upgrade shall be determined per Attachment J, Section VII.C methodology. Assumption of a 40 year service life is utilized for Base Plan funded projects. A present worth analysis of RR on a common year basis between the Base Plan and Requested Upgrades was performed to determine avoided Base Plan RR due to the displacement or deferral of the Base Plan upgrade by the Requested Upgrade. The incremental increase in present worth of a Requested Upgrade on a common year basis as a Base Plan upgrade is assigned to the transmission requests impacting the upgrade based on the displacement or deferral. If the displacement analysis results in lower RR due to the shorter amortization period of the requested upgrade when compared to a base plan amortization period, then no direct assignment of the upgrade cost is made due to the displacement to an earlier start date.
Note 4: For Point-to-Point requests, total cost is based on the higher of the base rate or assigned upgrade revenue requirements. For Network requests, the total cost is based on the assigned upgrade revenue requirement. Allocation of base plan funding will be determined after verification of designated resource meeting Attachment J, Section II B Criteria. Additionally E & C of 3rd Party upgrades is assignable to Customer. This includes prepayments required for any SWPA upgrades. Revenue requirements for 3rd Party facilities are not calculated. Total cost to customer is based on assumption of Revenue Requirements with confirmation of base plan funding. Customer is responsible for negotiating redispatch costs if applicable. Customer is also responsible to pay credits for previously assigned upgrades that are impacted by their request. Credits can be paid from base plan funding if applicable.
Note 5: RR with base plan funding may increase or decrease even if no base plan funding is applicable to a particular request if another request that shares the upgrade is now full base plan funded resulting in a different amortization period for the upgrade and thus different RR.

## Table3
Customer | Study Number
AEPM | 2013-AG3-003
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AEPM | 78775996 | OKGE | CSWS | 200 | 2016-01-01 | 2036-01-01 | 2016-01-01 | 2036-01-01 | 0 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0 | 0
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Base Plan Funding for Wind | Directly Assigned for Wind | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
78775996 | None |  |  |  |  | 0 | 0 | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0 | 0 | 0
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
78775996 | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 AECC | 2021-06-01 | 2021-06-01
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
78775996 | Gracemont 138kV line terminal addition | 2011-10-15 | 2011-10-15
| Harrington Mid - Nichols 230 kV Ckt 2 | 2012-12-01 | 2012-12-01
| Harrington West - Nichols 230kV Ckt 1 | 2012-12-01 | 2012-12-01
| HUGO - VALLIANT 345KV CKT 1 | 2012-07-01 | 2012-07-01
| MATHEWSON - NORTHWEST 345KV CKT 1 | 2010-01-01 | 2010-01-01
| MATHEWSON - TATONGA 345KV CKT 1 | 2010-01-01 | 2010-01-01
| Southwestern Station - Washita 138kV Ckt 1 | 2005-10-01 | 2005-10-01
| Southwestern Station - Washita 138kV Ckt 1 (AEP) | 2005-10-01 | 2005-10-01
| TATONGA - WOODWARD 345KV CKT 1 | 2010-01-01 | 2010-01-01
| Valliant 345 kV (AEP) | 2012-07-01 | 2012-07-01
| WASHITA - GRACEMONT 138 KV CKT 2 | 2012-10-12 | 2012-10-12
| WOODWARD - IODINE 138KV CKT 1 | 2010-01-01 | 2010-01-01
| WOODWARD - WOODWARD EHV 138KV CKT 1 | 2010-01-01 | 2010-01-01
| WOODWARD 345/138KV TRANSFORMER CKT 1 | 2010-01-01 | 2010-01-01
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
AEPM | 2013-AG3-004
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AEPM | 78776033 | SPS | CSWS | 200 | 2016-01-01 | 2036-01-01 | 2016-01-01 | 2036-01-01 | 0 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0 | 0
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Base Plan Funding for Wind | Directly Assigned for Wind | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
78776033 | None |  |  |  |  | 0 | 0 | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0 | 0 | 0
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
78776033 | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 AECC | 2021-06-01 | 2021-06-01
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
78776033 | Gracemont 138kV line terminal addition | 2011-10-15 | 2011-10-15
| Harrington Mid - Nichols 230 kV Ckt 2 | 2012-12-01 | 2012-12-01
| Harrington West - Nichols 230kV Ckt 1 | 2012-12-01 | 2012-12-01
| HUGO - VALLIANT 345KV CKT 1 | 2012-07-01 | 2012-07-01
| MATHEWSON - NORTHWEST 345KV CKT 1 | 2010-01-01 | 2010-01-01
| MATHEWSON - TATONGA 345KV CKT 1 | 2010-01-01 | 2010-01-01
| Southwestern Station - Washita 138kV Ckt 1 | 2005-10-01 | 2005-10-01
| Southwestern Station - Washita 138kV Ckt 1 (AEP) | 2005-10-01 | 2005-10-01
| TATONGA - WOODWARD 345KV CKT 1 | 2010-01-01 | 2010-01-01
| Valliant 345 kV (AEP) | 2012-07-01 | 2012-07-01
| WASHITA - GRACEMONT 138 KV CKT 2 | 2012-10-12 | 2012-10-12
| WOODWARD - WOODWARD EHV 138KV CKT 1 | 2010-01-01 | 2010-01-01
| WOODWARD 345/138KV TRANSFORMER CKT 1 | 2010-01-01 | 2010-01-01
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
AEPM | 2013-AG3-005
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
AEPM | 78776041 | OKGE | CSWS | 199 | 2016-01-01 | 2036-01-01 | 2016-01-01 | 2036-01-01 | 0 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0 | 0
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Base Plan Funding for Wind | Directly Assigned for Wind | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
78776041 | None |  |  |  |  | 0 | 0 | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0 | 0 | 0
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
78776041 | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 AECC | 2021-06-01 | 2021-06-01
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
78776041 | Gracemont 138kV line terminal addition | 2011-10-15 | 2011-10-15
| HUGO - VALLIANT 345KV CKT 1 | 2012-07-01 | 2012-07-01
| MATHEWSON - NORTHWEST 345KV CKT 1 | 2010-01-01 | 2010-01-01
| MATHEWSON - TATONGA 345KV CKT 1 | 2010-01-01 | 2010-01-01
| Southwestern Station - Washita 138kV Ckt 1 | 2005-10-01 | 2005-10-01
| Southwestern Station - Washita 138kV Ckt 1 (AEP) | 2005-10-01 | 2005-10-01
| TATONGA - WOODWARD 345KV CKT 1 | 2010-01-01 | 2010-01-01
| Valliant 345 kV (AEP) | 2012-07-01 | 2012-07-01
| WASHITA - GRACEMONT 138 KV CKT 2 | 2012-10-12 | 2012-10-12
| WOODWARD - WOODWARD EHV 138KV CKT 1 | 2010-01-01 | 2010-01-01
| WOODWARD 345/138KV TRANSFORMER CKT 1 | 2010-01-01 | 2010-01-01
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
ETEC | 2013-AG3-006
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
ETEC | 78774012 | CSWS | CSWS | 31 | 2015-01-01 | 2024-01-01 | 2015-06-01 | 2024-06-01 | 0 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0 | 0
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
78774012 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
78774012 | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 AECC | 2021-06-01 | 2021-06-01
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
78774012 | Gracemont 138kV line terminal addition | 2011-10-15 | 2011-10-15
| HUGO - VALLIANT 345KV CKT 1 | 2012-07-01 | 2012-07-01
| Southwestern Station - Washita 138kV Ckt 1 | 2005-10-01 | 2005-10-01
| Southwestern Station - Washita 138kV Ckt 1 (AEP) | 2005-10-01 | 2005-10-01
| Valliant 345 kV (AEP) | 2012-07-01 | 2012-07-01
| WASHITA - GRACEMONT 138 KV CKT 2 | 2012-10-12 | 2012-10-12
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
OMPA | 2013-AG3-025
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
OMPA | 78697838 | OKGE | OKGE | 4 | 2014-10-01 | 2040-12-01 | 2015-06-01 | 2041-08-01 | 0 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0 | 0
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
78697838 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
78697838 | OMPA-MARLOW - RUSH SPRINGS TAP 138KV CKT 1 | 2021-06-01 | 2021-06-01
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
78697838 | CACHE - SNYDER 138KV CKT 1 | 2008-05-21 | 2008-05-21
| Fairfax - Pawnee 138kV Ckt 1 | 2014-06-30 | 2014-06-01
| MATHEWSON - NORTHWEST 345KV CKT 1 | 2010-01-01 | 2010-01-01
| MATHEWSON - TATONGA 345KV CKT 1 | 2010-01-01 | 2010-01-01
| Osage - Shidler 138kV | 2014-01-15 | 2014-01-15
| Pawnee 138 kV | 2014-06-30 | 2014-06-01
| Shidler 138 kV | 2014-02-08 | 2014-02-08
| TATONGA - WOODWARD 345KV CKT 1 | 2010-01-01 | 2010-01-01
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
SPSM | 2013-AG3-027
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
SPSM | 78751808 | SPS | SPS | 250 | 2015-12-01 | 2035-12-01 | 2018-12-15 | 2035-12-01 | 9485379 | 0 | 9485379 | 24172663.584
[9 empty] | 9485379 | 0 | 9485379 | 24172663.584
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Base Plan Funding for Wind | Directly Assigned for Wind | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
78751808 | EDDY CO 230kV Bus Tie | 2017-10-01 | 2018-12-15 |  | Yes | 9485379 | 0 | 9485379 | 9485379 | 24172663.584
[5 empty] | Total | 9485379 | 0 | 9485379 | 9485379 | 24172663.58
Expansion Plan - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
78751808 | Mustang to Shell CO2 115 kV | 2016-06-01 | 2017-06-01 |  | Yes
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
78751808 | AMOCO SWITCHING STATION - SUNDOWN INTERCHANGE 230KV CKT 1 | 2017-10-01 | 2017-10-01
| CARLSBAD INTERCHANGE - PECOS INTERCHANGE 115KV CKT 1 | 2021-10-01 | 2021-10-01
| IMC Area Rebuild and Capacitors Additions | 2021-06-01 | 2021-06-01
| LIVSTNRIDGE3115.00 - WIPP SUB 115KV CKT 1 | 2021-06-01 | 2021-06-01
| North Loving 115 kV Cap Banks | 2022-06-01 | 2022-06-01
| SAND DUNES SUB - WIPP SUB 115KV CKT 1 | 2021-06-01 | 2021-06-01
| SUNDOWN INTERCHANGE (WH XDS70381) 230/115/13.8KV TRANSFORMER CKT 1 | 2021-06-01 | 2021-06-01
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
TEXL | 2013-AG3-028
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
TEXL | 78773933 | CSWS | CSWS | 50 | 2015-01-01 | 2025-01-01 | 2015-06-01 | 2025-06-01 | 0 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0 | 0
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
78773933 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
78773933 | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 AECC | 2021-06-01 | 2021-06-01
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
78773933 | Gracemont 138kV line terminal addition | 2011-10-15 | 2011-10-15
| HUGO - VALLIANT 345KV CKT 1 | 2012-07-01 | 2012-07-01
| Southwestern Station - Washita 138kV Ckt 1 | 2005-10-01 | 2005-10-01
| Southwestern Station - Washita 138kV Ckt 1 (AEP) | 2005-10-01 | 2005-10-01
| Valliant 345 kV (AEP) | 2012-07-01 | 2012-07-01
| WASHITA - GRACEMONT 138 KV CKT 2 | 2012-10-12 | 2012-10-12
*Credits may be required for applicable generation interconnection network upgrades.
Customer | Study Number
TEXL | 2013-AG3-029
Customer | Reservation | POR | POD | Requested Amount | Requested Start Date | Requested Stop Date | Deferred Start Date Without Redispatch | Deferred Stop Date Without Redispatch | Potential Base Plan Funding Allowable | Point-to-Point Base Rate | Allocated E & C Cost | Total Revenue Requirements
TEXL | 78773967 | CSWS | CSWS | 27 | 2015-01-01 | 2030-01-01 | 2015-06-01 | 2030-06-01 | 0 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0 | 0
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available | Allocated E & C Cost | Total E & C Cost | Total Revenue Requirements
78773967 | None |  |  |  |  | 0 | 0 | 0
[5 empty] | Total | 0 | 0 | 0
Construction Pending - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
78773967 | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 AECC | 2021-06-01 | 2021-06-01
Credits may be required for the following Network Upgrades in accordance with Attachment Z2 of the SPP OATT.
Reservation | Upgrade Name | DUN | EOC | Earliest Start Date | Redispatch Available
78773967 | Gracemont 138kV line terminal addition | 2011-10-15 | 2011-10-15
| HUGO - VALLIANT 345KV CKT 1 | 2012-07-01 | 2012-07-01
| Southwestern Station - Washita 138kV Ckt 1 | 2005-10-01 | 2005-10-01
| Southwestern Station - Washita 138kV Ckt 1 (AEP) | 2005-10-01 | 2005-10-01
| Valliant 345 kV (AEP) | 2012-07-01 | 2012-07-01
| WASHITA - GRACEMONT 138 KV CKT 2 | 2012-10-12 | 2012-10-12
*Credits may be required for applicable generation interconnection network upgrades.

## Table4
Transmission Owner | Upgrade | Solution | Earliest Date Upgrade Required (DUN) | Estimated Date of Upgrade Completion (EOC) | Estimated Engineering & Construction Cost
SPS | EDDY CO 230kV Bus Tie | Build the 230kV main and transfer bus to a double breaker double bus. | 2017-10-01 | 2018-12-15 | 9485379
Construction Pending Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Transmission Owner | Upgrade | Solution | Earliest Date Upgrade Required (DUN) | Estimated Date of Upgrade Completion (EOC)
AECC | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 AECC | Upgrade 1272 AAC bus at Farmington REC. Replace bus at Farmington REC and rebuild 400 feet of the 161 kV line going to Chamber Springs. | 2021-06-01 | 2021-06-01
Expansion Plan Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Transmission Owner | Upgrade | Solution | Earliest Date Upgrade Required (DUN) | Estimated Date of Upgrade Completion (EOC)
SPS | Mustang to Shell CO2 115 kV | Build 6.3 mile 115 kV line from Mustang to Shell CO2 Build a new 6.9 mile 115kV line between the Mustang and Shell CO2 substations. | 2016-06-01 | 2017-06-01
Reliability Projects - The requested service is contingent upon completion of the following upgrades. Cost is not assignable to the transmission customer.
Transmission Owner | Upgrade | Solution | Earliest Date Upgrade Required (DUN) | Estimated Date of Upgrade Completion (EOC)
AEPW | OMPA-MARLOW - RUSH SPRINGS TAP 138KV CKT 1 | Rebuild 8.59 miles with 1533.3 ACSR/TW | 2021-06-01 | 2021-06-01
SPS | AMOCO SWITCHING STATION - SUNDOWN INTERCHANGE 230KV CKT 1 | Replace wave trap at Amoco and Sundown 230 kV | 2017-10-01 | 2017-10-01
SPS | CARLSBAD INTERCHANGE - PECOS INTERCHANGE 115KV CKT 1 | Replace Terminal Equipment | 2021-10-01 | 2021-10-01
SPS | IMC Area Rebuild and Capacitors Additions | Reconductoring IMC #1 Tap-Intrepid West, IMC #1-Livingston Ridge, Intrepid West-Potash Junction, Byrd-Monument, Ponderosa Tap-Whitten, National Enrichment Plant-Targa 115 kV lines, Upgrading terminal equipment at Byrd 115 kV substation. A wave trap will | 2021-06-01 | 2021-06-01
SPS | LIVSTNRIDGE3115.00 - WIPP SUB 115KV CKT 1 | Rebuild 2.75 miles of transmission line. | 2021-06-01 | 2021-06-01
SPS | North Loving 115 kV Cap Banks | Install two (2) stages of 14.4 MVAR capacitor banks at North Loving 115 kV. | 2022-06-01 | 2022-06-01
SPS | SAND DUNES SUB - WIPP SUB 115KV CKT 1 | Rebuild 5.63 miles of line | 2021-06-01 | 2021-06-01
SPS | SUNDOWN INTERCHANGE (WH XDS70381) 230/115/13.8KV TRANSFORMER CKT 1 | Upgrade Transformer to 250 MVA | 2021-06-01 | 2021-06-01
Network Upgrades requiring credits per Attachment Z2 of the SPP OATT.
Transmission Owner | Upgrade | Solution | Earliest Date Upgrade Required (DUN) | Estimated Date of Upgrade Completion (EOC)
AEPW | CACHE - SNYDER 138KV CKT 1 | Replace Snyder wavetrap | 2008-05-21 | 2008-05-21
AEPW | Osage - Shidler 138kV | Osage Substation:Replace Shidler 138kV line terminal primary and redundant relaying with SEL uProcessor based relays, install 3-138kV PTs, Install 1-138kV CB, Install metering, Install 2000A line Trap | 2014-01-15 | 2014-01-15
AEPW | Shidler 138 kV | 138kV four (4) Breaker ring-bus including 138kV transmission line terminal to KAMO's Remington 138kV Substation, replace grounding switch with circuit switcher , move OGE's Osage 138kV line terminal, replace relay panels on OGE's Osage and Mound Road 138kV line terminals, metering, and associated equipment. | 2014-02-08 | 2014-02-08
AEPW | Southwestern Station - Washita 138kV Ckt 1 (AEP) | Expand Southwestern Station for termination of WFEC 2.75 mile 138kV Transmission Line from Washita Switch Station | 2005-10-01 | 2005-10-01
AEPW | Valliant 345 kV (AEP) | Valliant 345 KV line terminal | 2012-07-01 | 2012-07-01
GRDA | Fairfax - Pawnee 138kV Ckt 1 | Construct Approx. 15 miles of 138kV transmission line from Fairfax to a new substation on the Cleveland-Stillwater 138kV line near Pawnee. & Fairfax Substation: Install 138kV line terminal and any additional modifications that are necessary to connect to | 2014-06-30 | 2014-06-01
GRDA | Pawnee 138 kV | New three breaker ring bus on the Cleveland-Stillwater 138kV line near Pawnee. Station will have terminals to Cleveland, Stillwater, and Fairfax. | 2014-06-30 | 2014-06-01
OKGE | Gracemont 138kV line terminal addition | 138kV line terminal at Gracemont substation, including breaker, line relaying, disconnect switches and associated equipment, dead end structures, revenue metering with CT's and PT's. | 2011-10-15 | 2011-10-15
OKGE | MATHEWSON - NORTHWEST 345KV CKT 1 | Build 345 kV line | 2010-01-01 | 2010-01-01
OKGE | MATHEWSON - TATONGA 345KV CKT 1 | Build 345 kV line | 2010-01-01 | 2010-01-01
OKGE | TATONGA - WOODWARD 345KV CKT 1 | Build 345 kV line | 2010-01-01 | 2010-01-01
OKGE | WOODWARD - IODINE 138KV CKT 1 | Tap Iodine to Woodward 138 kV line | 2010-01-01 | 2010-01-01
OKGE | WOODWARD - WOODWARD EHV 138KV CKT 1 | Build .5 miles of 138 kV and install terminal equipment | 2010-01-01 | 2010-01-01
OKGE | WOODWARD 345/138KV TRANSFORMER CKT 1 | Install 345/138 kV XF | 2010-01-01 | 2010-01-01
SPS | Harrington Mid - Nichols 230 kV Ckt 2 | Reconductor Harrington Mid - Nichols 230kV. Replace switches and breakers to get circuit to 727/727 MVA rating. New limit should be bus rating. | 2012-12-01 | 2012-12-01
SPS | Harrington West - Nichols 230kV Ckt 1 | Reconductor Harrington West - Nichols 230kV. Replace switches and breakers to get circuit to 727/727 MVA rating. New limit should be bus rating. | 2012-12-01 | 2012-12-01
WFEC | HUGO - VALLIANT 345KV CKT 1 | New 19 miles 345 KV | 2012-07-01 | 2012-07-01
WFEC | Southwestern Station - Washita 138kV Ckt 1 | Expand Washita Switch Station from a 4-breaker to a 5-breaker 138kV ring bus & Construct 2.75 mile 138kV Transmission Line to the AEP/PSO Southwestern Station | 2005-10-01 | 2005-10-01
WFEC | WASHITA - GRACEMONT 138 KV CKT 2 | BUILD WASHITA - GRACEMONT 138KV CKT 2 (APPROXIMATELY 7 MILES). ADD LINE TERMINAL AT WASHITA AND PROCURE RIGHT OF WAY. REQUIRED AS SHARED NETWORK UPGRADE FOR INTERCONNECTION OF GEN-2008-037. | 2012-10-12 | 2012-10-12

## Table5
Transmission Owner | UpgradeName | Solution | Earliest Date Upgrade Required (DUN) | Estimated Date of Upgrade Completion (EOC) | Estimated Engineering & Construction Cost
None

## Table6
Upgrade: | EDDY CO 230kV Bus Tie
Limiting Facility: | EDDY_NORTH 6230.00 (WAUK WT01134) 230/115/13.2KV TRANSFORMER CKT 2
Direction: | FROM->TO
Line Outage: | EDDY COUNTY INTERCHANGE - EDDY_NORTH 6230.00 230KV CKT @1
Flowgate: | 2013AG3AFS61T3675520WP
Date Redispatch Needed: | Starting 2020 12/1 - 4/1 Until EOC of Upgrade
Season Flowgate Identified: | 2020 Winter Peak
Reservation | Relief Amount | Aggregate Relief Amount
78751808 | 44.6 | 44.6
Source Control Area | Source | Maximum Increment (MW) | GSF | Sink Control Area | Sink | Maximum Decrement (MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
SPS | CUNNINGHAM 230KV | 201 | -0.1464 | SPS | ROOSEVELT_3 0.6900 34KV | 348.4 | 0.13236 | -0.27876 | 160
SPS | CUNNINGHAM 230KV | 201 | -0.1464 | SPS | SN_JUAN_TAP6230.00 230KV | 120 | 0.1237 | -0.2701 | 165
SPS | CUNNINGHAM 115KV | 169 | -0.13312 | SPS | ROOSEVELT_3 0.6900 34KV | 348.4 | 0.13236 | -0.26548 | 168
SPS | MADOX 115KV | 150 | -0.13154 | SPS | ROOSEVELT_3 0.6900 34KV | 348.4 | 0.13236 | -0.2639 | 169
SPS | CUNNINGHAM 115KV | 169 | -0.13312 | SPS | SN_JUAN_TAP6230.00 230KV | 120 | 0.1237 | -0.25682 | 174
SPS | MADOX 115KV | 150 | -0.13154 | SPS | SN_JUAN_TAP6230.00 230KV | 120 | 0.1237 | -0.25524 | 175
SPS | CUNNINGHAM 230KV | 201 | -0.1464 | SPS | CAPROCK 0KV | 80 | 0.06305 | -0.20945 | 213
SPS | MUSTANG_6 118.000 230KV | 531 | -0.0725 | SPS | ROOSEVELT_3 0.6900 34KV | 348.4 | 0.13236 | -0.20486 | 218
SPS | CUNNINGHAM 115KV | 169 | -0.13312 | SPS | CAPROCK 0KV | 80 | 0.06305 | -0.19617 | 227
SPS | MUSTANG_6 118.000 230KV | 531 | -0.0725 | SPS | SN_JUAN_TAP6230.00 230KV | 120 | 0.1237 | -0.1962 | 227
SPS | MADOX 115KV | 150 | -0.13154 | SPS | CAPROCK 0KV | 80 | 0.06305 | -0.19459 | 229
SPS | CUNNINGHAM 230KV | 201 | -0.1464 | SPS | TOLK 230KV | 1018 | 0.04726 | -0.19366 | 230
SPS | CUNNINGHAM 115KV | 169 | -0.13312 | SPS | TOLK 230KV | 1018 | 0.04726 | -0.18038 | 247
SPS | MADOX 115KV | 150 | -0.13154 | SPS | TOLK 230KV | 1018 | 0.04726 | -0.1788 | 249
SPS | CUNNINGHAM 230KV | 201 | -0.1464 | SPS | WILWIND 34KV | 160 | 0.01681 | -0.16321 | 273
SPS | CUNNINGHAM 230KV | 201 | -0.1464 | SPS | HARRINGTON 230KV | 1017 | 0.01188 | -0.15828 | 282
SPS | CUNNINGHAM 230KV | 201 | -0.1464 | SPS | MAJSTC-WTG210.6900 34KV | 159 | 0.01125 | -0.15765 | 283
SPS | CUNNINGHAM 230KV | 201 | -0.1464 | SPS | BLACKHAWK 115KV | 190 | 0.0106 | -0.157 | 284
SPS | CUNNINGHAM 230KV | 201 | -0.1464 | SPS | SPNSPUR_WND134.500 345KV | 160 | 0.01018 | -0.15658 | 285
SPS | CUNNINGHAM 230KV | 201 | -0.1464 | SPS | GOODWELL_2 10.6900 34KV | 200 | 0.00639 | -0.15279 | 292
SPS | CUNNINGHAM 115KV | 169 | -0.13312 | SPS | WILWIND 34KV | 160 | 0.01681 | -0.14993 | 297
SPS | ELK_1 118.000 345KV | 202 | -0.01747 | SPS | ROOSEVELT_3 0.6900 34KV | 348.4 | 0.13236 | -0.14983 | 297
SPS | HALE_2 18.000 345KV | 203 | -0.01747 | SPS | ROOSEVELT_3 0.6900 34KV | 348.4 | 0.13236 | -0.14983 | 297
SPS | CUNNINGHAM 230KV | 201 | -0.1464 | SPS | BUFF_DUNES2134.500 34KV | 202 | 0.00222 | -0.14862 | 300
SPS | CUNNINGHAM 230KV | 201 | -0.1464 | SUNC | HOLCOMB 115KV | 360 | 0.00212 | -0.14852 | 300
SPS | MADOX 115KV | 150 | -0.13154 | SPS | WILWIND 34KV | 160 | 0.01681 | -0.14835 | 300
SPS | CUNNINGHAM 230KV | 201 | -0.1464 | SUNC | CIMRRN 1 34.500 345KV | 297 | 0.00173 | -0.14813 | 301
SPS | CUNNINGHAM 230KV | 201 | -0.1464 | SUNC | EDWARDS 0.7000 34KV | 123.3832 | 0.00121 | -0.14761 | 302
SPS | CUNNINGHAM 230KV | 201 | -0.1464 | SUNC | GPW_G1 0.7000 34KV | 127.6168 | 0.00121 | -0.14761 | 302
SPS | CUNNINGHAM 230KV | 201 | -0.1464 | SUNC | GRAY COUNTY WIND FARM 115KV | 110 | 0.00125 | -0.14765 | 302
SPS | CUNNINGHAM 230KV | 201 | -0.1464 | SUNC | IRONWOOD 1 34.500 345KV | 167.9 | 0.00123 | -0.14763 | 302
SPS | CUNNINGHAM 230KV | 201 | -0.1464 | SUNC | SSWIND 1 34.500 115KV | 104 | 0.00106 | -0.14746 | 302
SPS | CUNNINGHAM 230KV | 201 | -0.1464 | SUNC | MRWYP16 230KV | 196 | 0.00048 | -0.14688 | 303
SPS | CUNNINGHAM 230KV | 201 | -0.1464 | AEPW | RKYRDGW1-1 34.500 138KV | 150 | 0.00019 | -0.14659 | 304
SPS | CUNNINGHAM 230KV | 201 | -0.1464 | AEPW | WTH WIND 34.500 34KV | 147 | 0.00028 | -0.14668 | 304
SPS | CUNNINGHAM 230KV | 201 | -0.1464 | AEPW | ARSENAL HILL 138KV | 509 | -0.00035 | -0.14605 | 305
SPS | CUNNINGHAM 230KV | 201 | -0.1464 | AEPW | COGENTRIX 345KV | 512.9847 | -0.0002 | -0.1462 | 305
SPS | CUNNINGHAM 230KV | 201 | -0.1464 | AEPW | EASTMAN 138KV | 289.1187 | -0.00038 | -0.14602 | 305
SPS | CUNNINGHAM 230KV | 201 | -0.1464 | AEPW | FLINT CREEK 161KV | 528 | -9e-05 | -0.14631 | 305
SPS | CUNNINGHAM 230KV | 201 | -0.1464 | AEPW | LEBROCK 345KV | 379.3791 | -0.00038 | -0.14602 | 305
SPS | CUNNINGHAM 230KV | 201 | -0.1464 | AEPW | NORTHEASTERN STATION 138KV | 785 | -0.00011 | -0.14629 | 305
SPS | CUNNINGHAM 230KV | 201 | -0.1464 | AEPW | NORTHEASTERN STATION 345KV | 460 | -0.00018 | -0.14622 | 305
SPS | CUNNINGHAM 230KV | 201 | -0.1464 | AEPW | OEC 345KV | 1180 | -0.00018 | -0.14622 | 305
SPS | CUNNINGHAM 230KV | 201 | -0.1464 | AEPW | PIRKEY GENERATION 138KV | 675 | -0.00038 | -0.14602 | 305
SPS | CUNNINGHAM 230KV | 201 | -0.1464 | AEPW | RIVERSIDE STATION 138KV | 220.9209 | -0.00019 | -0.14621 | 305
SPS | CUNNINGHAM 230KV | 201 | -0.1464 | AEPW | TURK 138KV | 650 | -0.00047 | -0.14593 | 305
SPS | CUNNINGHAM 230KV | 201 | -0.1464 | AEPW | WELSH 345KV | 1056 | -0.00043 | -0.14597 | 305
SPS | CUNNINGHAM 115KV | 169 | -0.13312 | SPS | HARRINGTON 230KV | 1017 | 0.01188 | -0.145 | 307
SPS | LUBBOCK CO SUB 230KV | 375 | -0.01264 | SPS | ROOSEVELT_3 0.6900 34KV | 348.4 | 0.13236 | -0.145 | 307
SPS | CUNNINGHAM 230KV | 201 | -0.1464 | AEPW | COMANCHE 138KV | 170 | -0.00177 | -0.14463 | 308
SPS | CUNNINGHAM 115KV | 169 | -0.13312 | SPS | MAJSTC-WTG210.6900 34KV | 159 | 0.01125 | -0.14437 | 309
SPS | CUNNINGHAM 115KV | 169 | -0.13312 | SPS | BLACKHAWK 115KV | 190 | 0.0106 | -0.14372 | 310
SPS | CUNNINGHAM 115KV | 169 | -0.13312 | SPS | SPNSPUR_WND134.500 345KV | 160 | 0.01018 | -0.1433 | 311
SPS | MADOX 115KV | 150 | -0.13154 | SPS | HARRINGTON 230KV | 1017 | 0.01188 | -0.14342 | 311
SPS | MADOX 115KV | 150 | -0.13154 | SPS | MAJSTC-WTG210.6900 34KV | 159 | 0.01125 | -0.14279 | 312
SPS | MADOX 115KV | 150 | -0.13154 | SPS | BLACKHAWK 115KV | 190 | 0.0106 | -0.14214 | 314
SPS | MADOX 115KV | 150 | -0.13154 | SPS | SPNSPUR_WND134.500 345KV | 160 | 0.01018 | -0.14172 | 314
SPS | ELK_1 118.000 345KV | 202 | -0.01747 | SPS | SN_JUAN_TAP6230.00 230KV | 120 | 0.1237 | -0.14117 | 316
SPS | HALE_2 18.000 345KV | 203 | -0.01747 | SPS | SN_JUAN_TAP6230.00 230KV | 120 | 0.1237 | -0.14117 | 316
SPS | CUNNINGHAM 115KV | 169 | -0.13312 | SPS | GOODWELL_2 10.6900 34KV | 200 | 0.00639 | -0.13951 | 319
SPS | MADOX 115KV | 150 | -0.13154 | SPS | GOODWELL_2 10.6900 34KV | 200 | 0.00639 | -0.13793 | 323
SPS | CUNNINGHAM 230KV | 201 | -0.1464 | SPS | ANTELOPE 230KV | 126.4657 | -0.00923 | -0.13717 | 325
SPS | LUBBOCK CO SUB 230KV | 375 | -0.01264 | SPS | SN_JUAN_TAP6230.00 230KV | 120 | 0.1237 | -0.13634 | 327
SPS | CUNNINGHAM 115KV | 169 | -0.13312 | SPS | BUFF_DUNES2134.500 34KV | 202 | 0.00222 | -0.13534 | 329
SPS | CUNNINGHAM 115KV | 169 | -0.13312 | SUNC | HOLCOMB 115KV | 360 | 0.00212 | -0.13524 | 330
SPS | CUNNINGHAM 115KV | 169 | -0.13312 | SUNC | CIMRRN 1 34.500 345KV | 297 | 0.00173 | -0.13485 | 331
SPS | CUNNINGHAM 115KV | 169 | -0.13312 | SUNC | EDWARDS 0.7000 34KV | 123.3832 | 0.00121 | -0.13433 | 332
SPS | CUNNINGHAM 115KV | 169 | -0.13312 | SUNC | GPW_G1 0.7000 34KV | 127.6168 | 0.00121 | -0.13433 | 332
SPS | CUNNINGHAM 115KV | 169 | -0.13312 | SUNC | IRONWOOD 1 34.500 345KV | 167.9 | 0.00123 | -0.13435 | 332
SPS | CUNNINGHAM 230KV | 201 | -0.1464 | SPS | LUBBOCK CO SUB 230KV | 294 | -0.01264 | -0.13376 | 333
SPS | MADOX 115KV | 150 | -0.13154 | SPS | BUFF_DUNES2134.500 34KV | 202 | 0.00222 | -0.13376 | 333
SPS | MADOX 115KV | 150 | -0.13154 | SUNC | HOLCOMB 115KV | 360 | 0.00212 | -0.13366 | 333
SPS | CUNNINGHAM 115KV | 169 | -0.13312 | SUNC | MRWYP16 230KV | 196 | 0.00048 | -0.1336 | 334
SPS | CUNNINGHAM 115KV | 169 | -0.13312 | AEPW | RKYRDGW1-1 34.500 138KV | 150 | 0.00019 | -0.13331 | 334
SPS | CUNNINGHAM 115KV | 169 | -0.13312 | AEPW | WTH WIND 34.500 34KV | 147 | 0.00028 | -0.1334 | 334
SPS | MADOX 115KV | 150 | -0.13154 | SUNC | CIMRRN 1 34.500 345KV | 297 | 0.00173 | -0.13327 | 334
SPS | CUNNINGHAM 115KV | 169 | -0.13312 | AEPW | COGENTRIX 345KV | 512.9847 | -0.0002 | -0.13292 | 335
SPS | CUNNINGHAM 115KV | 169 | -0.13312 | AEPW | FLINT CREEK 161KV | 528 | -9e-05 | -0.13303 | 335
SPS | CUNNINGHAM 115KV | 169 | -0.13312 | AEPW | NORTHEASTERN STATION 138KV | 785 | -0.00011 | -0.13301 | 335
SPS | CUNNINGHAM 115KV | 169 | -0.13312 | AEPW | NORTHEASTERN STATION 345KV | 460 | -0.00018 | -0.13294 | 335
SPS | CUNNINGHAM 115KV | 169 | -0.13312 | AEPW | OEC 345KV | 1180 | -0.00018 | -0.13294 | 335
SPS | CUNNINGHAM 115KV | 169 | -0.13312 | AEPW | RIVERSIDE STATION 138KV | 220.9209 | -0.00019 | -0.13293 | 335
AEPW | SOUTHWESTERN STATION 138KV | 636 | -0.00086 | SPS | ROOSEVELT_3 0.6900 34KV | 348.4 | 0.13236 | -0.13322 | 335
AEPW | COGENTRIX 345KV | 381.0153 | -0.0002 | SPS | ROOSEVELT_3 0.6900 34KV | 348.4 | 0.13236 | -0.13256 | 336
SPS | CUNNINGHAM 115KV | 169 | -0.13312 | AEPW | ARSENAL HILL 138KV | 509 | -0.00035 | -0.13277 | 336
SPS | CUNNINGHAM 115KV | 169 | -0.13312 | AEPW | EASTMAN 138KV | 289.1187 | -0.00038 | -0.13274 | 336
SPS | CUNNINGHAM 115KV | 169 | -0.13312 | AEPW | LEBROCK 345KV | 379.3791 | -0.00038 | -0.13274 | 336
SPS | CUNNINGHAM 115KV | 169 | -0.13312 | AEPW | PIRKEY GENERATION 138KV | 675 | -0.00038 | -0.13274 | 336
SPS | CUNNINGHAM 115KV | 169 | -0.13312 | AEPW | TURK 138KV | 650 | -0.00047 | -0.13265 | 336
SPS | CUNNINGHAM 115KV | 169 | -0.13312 | AEPW | WELSH 345KV | 1056 | -0.00043 | -0.13269 | 336
AEPW | EASTMAN 138KV | 195.8913 | -0.00038 | SPS | ROOSEVELT_3 0.6900 34KV | 348.4 | 0.13236 | -0.13274 | 336
AEPW | FITZHUGH 161KV | 165 | -0.00016 | SPS | ROOSEVELT_3 0.6900 34KV | 348.4 | 0.13236 | -0.13252 | 336
AEPW | FULTON 115KV | 153 | -0.00041 | SPS | ROOSEVELT_3 0.6900 34KV | 348.4 | 0.13236 | -0.13277 | 336
AEPW | KNOXLEE 138KV | 475 | -0.00038 | SPS | ROOSEVELT_3 0.6900 34KV | 348.4 | 0.13236 | -0.13274 | 336
AEPW | LEBROCK 345KV | 156.6209 | -0.00038 | SPS | ROOSEVELT_3 0.6900 34KV | 348.4 | 0.13236 | -0.13274 | 336
AEPW | LIEBERMAN 138KV | 242 | -0.00035 | SPS | ROOSEVELT_3 0.6900 34KV | 348.4 | 0.13236 | -0.13271 | 336
SPS | MADOX 115KV | 150 | -0.13154 | SUNC | EDWARDS 0.7000 34KV | 123.3832 | 0.00121 | -0.13275 | 336
SPS | MADOX 115KV | 150 | -0.13154 | SUNC | GPW_G1 0.7000 34KV | 127.6168 | 0.00121 | -0.13275 | 336
SPS | MADOX 115KV | 150 | -0.13154 | SUNC | IRONWOOD 1 34.500 345KV | 167.9 | 0.00123 | -0.13277 | 336
AEPW | NORTHEASTERN STATION 138KV | 133 | -0.00011 | SPS | ROOSEVELT_3 0.6900 34KV | 348.4 | 0.13236 | -0.13247 | 336
AEPW | NORTHEASTERN STATION 345KV | 481 | -0.00018 | SPS | ROOSEVELT_3 0.6900 34KV | 348.4 | 0.13236 | -0.13254 | 336
AEPW | RIVERSIDE STATION 138KV | 838.0792 | -0.00019 | SPS | ROOSEVELT_3 0.6900 34KV | 348.4 | 0.13236 | -0.13255 | 336
AEPW | TONTITOWN 161KV | 313 | -0.00011 | SPS | ROOSEVELT_3 0.6900 34KV | 348.4 | 0.13236 | -0.13247 | 336
AEPW | TULSA POWER STATION 138KV | 307 | -0.00018 | SPS | ROOSEVELT_3 0.6900 34KV | 348.4 | 0.13236 | -0.13254 | 336
AEPW | WELEETKA 138KV | 198 | -0.00034 | SPS | ROOSEVELT_3 0.6900 34KV | 348.4 | 0.13236 | -0.1327 | 336
AEPW | WELSH 345KV | 528 | -0.00043 | SPS | ROOSEVELT_3 0.6900 34KV | 348.4 | 0.13236 | -0.13279 | 336
AEPW | WILKES 138KV | 408 | -0.0004 | SPS | ROOSEVELT_3 0.6900 34KV | 348.4 | 0.13236 | -0.13276 | 336
AEPW | WILKES 345KV | 360 | -0.00039 | SPS | ROOSEVELT_3 0.6900 34KV | 348.4 | 0.13236 | -0.13275 | 336
SPS | MADOX 115KV | 150 | -0.13154 | SUNC | MRWYP16 230KV | 196 | 0.00048 | -0.13202 | 338
SPS | MADOX 115KV | 150 | -0.13154 | AEPW | RKYRDGW1-1 34.500 138KV | 150 | 0.00019 | -0.13173 | 338
SPS | MADOX 115KV | 150 | -0.13154 | AEPW | WTH WIND 34.500 34KV | 147 | 0.00028 | -0.13182 | 338
SPS | CUNNINGHAM 115KV | 169 | -0.13312 | AEPW | COMANCHE 138KV | 170 | -0.00177 | -0.13135 | 339
SPS | MADOX 115KV | 150 | -0.13154 | AEPW | COGENTRIX 345KV | 512.9847 | -0.0002 | -0.13134 | 339
SPS | MADOX 115KV | 150 | -0.13154 | AEPW | FLINT CREEK 161KV | 528 | -9e-05 | -0.13145 | 339
SPS | MADOX 115KV | 150 | -0.13154 | AEPW | NORTHEASTERN STATION 138KV | 785 | -0.00011 | -0.13143 | 339
SPS | MADOX 115KV | 150 | -0.13154 | AEPW | NORTHEASTERN STATION 345KV | 460 | -0.00018 | -0.13136 | 339
SPS | MADOX 115KV | 150 | -0.13154 | AEPW | OEC 345KV | 1180 | -0.00018 | -0.13136 | 339
SPS | MADOX 115KV | 150 | -0.13154 | AEPW | RIVERSIDE STATION 138KV | 220.9209 | -0.00019 | -0.13135 | 339
SPS | MADOX 115KV | 150 | -0.13154 | AEPW | ARSENAL HILL 138KV | 509 | -0.00035 | -0.13119 | 340
SPS | MADOX 115KV | 150 | -0.13154 | AEPW | EASTMAN 138KV | 289.1187 | -0.00038 | -0.13116 | 340
SPS | MADOX 115KV | 150 | -0.13154 | AEPW | LEBROCK 345KV | 379.3791 | -0.00038 | -0.13116 | 340
SPS | MADOX 115KV | 150 | -0.13154 | AEPW | PIRKEY GENERATION 138KV | 675 | -0.00038 | -0.13116 | 340
SPS | MADOX 115KV | 150 | -0.13154 | AEPW | TURK 138KV | 650 | -0.00047 | -0.13107 | 340
SPS | MADOX 115KV | 150 | -0.13154 | AEPW | WELSH 345KV | 1056 | -0.00043 | -0.13111 | 340
SUNC | PIONWF-7 34.500 345KV | 200 | 0.00124 | SPS | ROOSEVELT_3 0.6900 34KV | 348.4 | 0.13236 | -0.13112 | 340
SUNC | GARDEN CITY 115KV | 209 | 0.00209 | SPS | ROOSEVELT_3 0.6900 34KV | 348.4 | 0.13236 | -0.13027 | 342
SPS | MADOX 115KV | 150 | -0.13154 | AEPW | COMANCHE 138KV | 170 | -0.00177 | -0.12977 | 343
AEPW | SOUTHWESTERN STATION 138KV | 636 | -0.00086 | SPS | SN_JUAN_TAP6230.00 230KV | 120 | 0.1237 | -0.12456 | 358
AEPW | EASTMAN 138KV | 195.8913 | -0.00038 | SPS | SN_JUAN_TAP6230.00 230KV | 120 | 0.1237 | -0.12408 | 359
AEPW | FULTON 115KV | 153 | -0.00041 | SPS | SN_JUAN_TAP6230.00 230KV | 120 | 0.1237 | -0.12411 | 359
AEPW | KNOXLEE 138KV | 475 | -0.00038 | SPS | SN_JUAN_TAP6230.00 230KV | 120 | 0.1237 | -0.12408 | 359
AEPW | LEBROCK 345KV | 156.6209 | -0.00038 | SPS | SN_JUAN_TAP6230.00 230KV | 120 | 0.1237 | -0.12408 | 359
AEPW | LIEBERMAN 138KV | 242 | -0.00035 | SPS | SN_JUAN_TAP6230.00 230KV | 120 | 0.1237 | -0.12405 | 359
AEPW | WELEETKA 138KV | 198 | -0.00034 | SPS | SN_JUAN_TAP6230.00 230KV | 120 | 0.1237 | -0.12404 | 359
AEPW | WELSH 345KV | 528 | -0.00043 | SPS | SN_JUAN_TAP6230.00 230KV | 120 | 0.1237 | -0.12413 | 359
AEPW | WILKES 138KV | 408 | -0.0004 | SPS | SN_JUAN_TAP6230.00 230KV | 120 | 0.1237 | -0.1241 | 359
AEPW | WILKES 345KV | 360 | -0.00039 | SPS | SN_JUAN_TAP6230.00 230KV | 120 | 0.1237 | -0.12409 | 359
AEPW | COGENTRIX 345KV | 381.0153 | -0.0002 | SPS | SN_JUAN_TAP6230.00 230KV | 120 | 0.1237 | -0.1239 | 360
SPS | CUNNINGHAM 115KV | 169 | -0.13312 | SPS | ANTELOPE 230KV | 126.4657 | -0.00923 | -0.12389 | 360
AEPW | FITZHUGH 161KV | 165 | -0.00016 | SPS | SN_JUAN_TAP6230.00 230KV | 120 | 0.1237 | -0.12386 | 360
AEPW | NORTHEASTERN STATION 138KV | 133 | -0.00011 | SPS | SN_JUAN_TAP6230.00 230KV | 120 | 0.1237 | -0.12381 | 360
AEPW | NORTHEASTERN STATION 345KV | 481 | -0.00018 | SPS | SN_JUAN_TAP6230.00 230KV | 120 | 0.1237 | -0.12388 | 360
AEPW | RIVERSIDE STATION 138KV | 838.0792 | -0.00019 | SPS | SN_JUAN_TAP6230.00 230KV | 120 | 0.1237 | -0.12389 | 360
AEPW | TONTITOWN 161KV | 313 | -0.00011 | SPS | SN_JUAN_TAP6230.00 230KV | 120 | 0.1237 | -0.12381 | 360
AEPW | TULSA POWER STATION 138KV | 307 | -0.00018 | SPS | SN_JUAN_TAP6230.00 230KV | 120 | 0.1237 | -0.12388 | 360
SPS | MADOX 115KV | 150 | -0.13154 | SPS | ANTELOPE 230KV | 126.4657 | -0.00923 | -0.12231 | 364
SPS | NICHOLS 115KV | 213 | 0.01168 | SPS | ROOSEVELT_3 0.6900 34KV | 348.4 | 0.13236 | -0.12068 | 369
SPS | CUNNINGHAM 115KV | 169 | -0.13312 | SPS | LUBBOCK CO SUB 230KV | 294 | -0.01264 | -0.12048 | 370
SPS | NICHOLS 230KV | 244 | 0.01182 | SPS | ROOSEVELT_3 0.6900 34KV | 348.4 | 0.13236 | -0.12054 | 370
SPS | MUSTANG_6 118.000 230KV | 531 | -0.0725 | SPS | TOLK 230KV | 1018 | 0.04726 | -0.11976 | 372
SPS | MADOX 115KV | 150 | -0.13154 | SPS | LUBBOCK CO SUB 230KV | 294 | -0.01264 | -0.1189 | 375
SPS | PLANTX 115KV | 222 | 0.02896 | SPS | ROOSEVELT_3 0.6900 34KV | 348.4 | 0.13236 | -0.1034 | 431
SPS | PLANTX 230KV | 189 | 0.03689 | SPS | ROOSEVELT_3 0.6900 34KV | 348.4 | 0.13236 | -0.09547 | 467
SPS | MUSTANG_6 118.000 230KV | 531 | -0.0725 | SPS | HARRINGTON 230KV | 1017 | 0.01188 | -0.08438 | 528
SPS | MUSTANG_6 118.000 230KV | 531 | -0.0725 | SPS | BLACKHAWK 115KV | 190 | 0.0106 | -0.0831 | 536
SPS | MUSTANG_6 118.000 230KV | 531 | -0.0725 | SPS | GOODWELL_2 10.6900 34KV | 200 | 0.00639 | -0.07889 | 565
SPS | MUSTANG_6 118.000 230KV | 531 | -0.0725 | SPS | BUFF_DUNES2134.500 34KV | 202 | 0.00222 | -0.07472 | 597
SPS | MUSTANG_6 118.000 230KV | 531 | -0.0725 | SUNC | HOLCOMB 115KV | 360 | 0.00212 | -0.07462 | 597
SPS | MUSTANG_6 118.000 230KV | 531 | -0.0725 | SUNC | CIMRRN 1 34.500 345KV | 297 | 0.00173 | -0.07423 | 600
SPS | MUSTANG_6 118.000 230KV | 531 | -0.0725 | AEPW | COGENTRIX 345KV | 512.9847 | -0.0002 | -0.0723 | 616
SPS | MUSTANG_6 118.000 230KV | 531 | -0.0725 | AEPW | FLINT CREEK 161KV | 528 | -9e-05 | -0.07241 | 616
SPS | MUSTANG_6 118.000 230KV | 531 | -0.0725 | AEPW | NORTHEASTERN STATION 138KV | 785 | -0.00011 | -0.07239 | 616
SPS | MUSTANG_6 118.000 230KV | 531 | -0.0725 | AEPW | NORTHEASTERN STATION 345KV | 460 | -0.00018 | -0.07232 | 616
SPS | MUSTANG_6 118.000 230KV | 531 | -0.0725 | AEPW | OEC 345KV | 1180 | -0.00018 | -0.07232 | 616
SPS | MUSTANG_6 118.000 230KV | 531 | -0.0725 | AEPW | RIVERSIDE STATION 138KV | 220.9209 | -0.00019 | -0.07231 | 616
SPS | MUSTANG_6 118.000 230KV | 531 | -0.0725 | AEPW | ARSENAL HILL 138KV | 509 | -0.00035 | -0.07215 | 618
SPS | MUSTANG_6 118.000 230KV | 531 | -0.0725 | AEPW | EASTMAN 138KV | 289.1187 | -0.00038 | -0.07212 | 618
SPS | MUSTANG_6 118.000 230KV | 531 | -0.0725 | AEPW | LEBROCK 345KV | 379.3791 | -0.00038 | -0.07212 | 618
SPS | MUSTANG_6 118.000 230KV | 531 | -0.0725 | AEPW | PIRKEY GENERATION 138KV | 675 | -0.00038 | -0.07212 | 618
SPS | MUSTANG_6 118.000 230KV | 531 | -0.0725 | AEPW | WELSH 345KV | 1056 | -0.00043 | -0.07207 | 618
SPS | MUSTANG_6 118.000 230KV | 531 | -0.0725 | AEPW | TURK 138KV | 650 | -0.00047 | -0.07203 | 619
SPS | LUBBOCK CO SUB 230KV | 375 | -0.01264 | SPS | TOLK 230KV | 1018 | 0.04726 | -0.0599 | 744
SPS | MUSTANG_6 118.000 230KV | 531 | -0.0725 | SPS | LUBBOCK CO SUB 230KV | 294 | -0.01264 | -0.05986 | 745
AEPW | SOUTHWESTERN STATION 138KV | 636 | -0.00086 | SPS | TOLK 230KV | 1018 | 0.04726 | -0.04812 | 926
AEPW | WELSH 345KV | 528 | -0.00043 | SPS | TOLK 230KV | 1018 | 0.04726 | -0.04769 | 935
AEPW | WILKES 138KV | 408 | -0.0004 | SPS | TOLK 230KV | 1018 | 0.04726 | -0.04766 | 935
AEPW | WILKES 345KV | 360 | -0.00039 | SPS | TOLK 230KV | 1018 | 0.04726 | -0.04765 | 935
AEPW | KNOXLEE 138KV | 475 | -0.00038 | SPS | TOLK 230KV | 1018 | 0.04726 | -0.04764 | 936
AEPW | COGENTRIX 345KV | 381.0153 | -0.0002 | SPS | TOLK 230KV | 1018 | 0.04726 | -0.04746 | 939
AEPW | RIVERSIDE STATION 138KV | 838.0792 | -0.00019 | SPS | TOLK 230KV | 1018 | 0.04726 | -0.04745 | 939
AEPW | NORTHEASTERN STATION 345KV | 481 | -0.00018 | SPS | TOLK 230KV | 1018 | 0.04726 | -0.04744 | 940
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | Mustang to Shell CO2 115 kV
Limiting Facility: | DENVER CITY INTERCHANGE N. - MUSTANG STATION N. 115KV CKT 1
Direction: | TO->FROM
Line Outage: | DENVER CITY INTERCHANGE S. - MUSTANG STATION N. 115KV CKT 2
Flowgate: | 2013AG3AFS61T1025016SP
Date Redispatch Needed: | Starting 2016 6/1 - 10/1 Until EOC of Upgrade
Season Flowgate Identified: | 2016 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
78751808 | 7.6 | 7.6
Source Control Area | Source | Maximum Increment (MW) | GSF | Sink Control Area | Sink | Maximum Decrement (MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.58383 | 13
SPS | HOBBS PLANT #2 (CT) 115KV | 9 | -0.09994 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.58668 | 13
SPS | MADOX 115KV | 148 | -0.09984 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.58658 | 13
SPS | CARLSBAD 69KV | 10 | -0.05892 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.54566 | 14
SPS | CUNNINGHAM 230KV | 35 | -0.06402 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.55076 | 14
SPS | HOBBS PLANT #3 (ST) 230KV | 13 | -0.06308 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.54982 | 14
SPS | ROOSEVELT_3 0.6900 34KV | 200 | -0.01238 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.49912 | 15
SPS | QUAY_CNTY 113.800 115KV | 23 | -0.00621 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.49295 | 15
SPS | SN_JUAN_TAP6230.00 230KV | 106.7 | -0.01995 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.50669 | 15
SPS | ANTELOPE 230KV | 8.933 | 0.0001 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.48664 | 16
SUNC | CIMARRON RIVER 115KV | 33 | -1e-05 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.48675 | 16
SUNC | CIM-PLT 13.800 13KV | 14 | -1e-05 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.48675 | 16
SUNC | CITY OF GOODLAND 115KV | 13.9 | -1e-05 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.48675 | 16
SUNC | CITY OF HILL CITY 115KV | 6.1 | -1e-05 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.48675 | 16
SUNC | CITY OF HUGOTON 69KV | 15.17 | -1e-05 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.48675 | 16
AEPW | COGENTRIX 345KV | 381.9511 | 0 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.48674 | 16
SUNC | COMMANCHE COUNTY 115KV | 110 | -1e-05 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.48675 | 16
SUNC | DONLEY CO SUB 69KV | 21.25 | -1e-05 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.48675 | 16
AEPW | EASTMAN 138KV | 207.8902 | 0 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.48674 | 16
SUNC | GARDEN CITY 115KV | 8 | -1e-05 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.48675 | 16
SUNC | GARDEN CITY 69KV | 10 | -1e-05 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.48675 | 16
SUNC | HOLCOMB 115KV | 24 | -1e-05 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.48675 | 16
SPS | HUBRCO2 69KV | 11 | -6e-05 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.4868 | 16
SUNC | JUDSON LARGE 115KV | 10.7 | -1e-05 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.48675 | 16
AEPW | KNOXLEE 138KV | 127 | 0 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.48674 | 16
AEPW | LEBROCK 345KV | 322.8378 | 0 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.48674 | 16
AEPW | LIEBERMAN 138KV | 25 | 0 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.48674 | 16
AEPW | LONESTAR POWER PLANT 69KV | 50 | 0 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.48674 | 16
SPS | LP-HOLL2 69KV | 62.67 | 0.00149 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.48525 | 16
SPS | LUBBOCK CO SUB 230KV | 71.2754 | 0.00166 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.48508 | 16
SUNC | MRWYP16 230KV | 189 | 0 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.48674 | 16
SPS | NICHOLS 115KV | 28 | -7e-05 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.48681 | 16
SPS | NICHOLS 230KV | 90 | -7e-05 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.48681 | 16
SUNC | NORTH WEST GREAT BEND 115KV | 10.21 | -1e-05 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.48675 | 16
AEPW | NORTHEASTERN STATION 345KV | 481 | 0 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.48674 | 16
AEPW | OEC 345KV | 100 | 0 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.48674 | 16
SUNC | PIONWF-7 34.500 345KV | 200 | -1e-05 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.48675 | 16
SPS | PLANTX 115KV | 142 | -0.00011 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.48685 | 16
SPS | PLANTX 230KV | 12 | 0.00028 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.48646 | 16
AEPW | RIVERSIDE STATION 138KV | 139 | 0 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.48674 | 16
SUNC | RUSSELL 115KV | 8.17 | -1e-05 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.48675 | 16
SPS | SIDRCH 69KV | 15 | -6e-05 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.4868 | 16
AEPW | SOUTHWESTERN STATION 138KV | 282.8135 | 0 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.48674 | 16
SPS | TOLK 230KV | 47 | -0.0007 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.48744 | 16
AEPW | TONTITOWN 161KV | 301 | 0 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.48674 | 16
AEPW | TURK 138KV | 34 | 0 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.48674 | 16
AEPW | WELEETKA 138KV | 158 | 0 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.48674 | 16
AEPW | WELSH 345KV | 528 | 0 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.48674 | 16
AEPW | WILKES 138KV | 10 | 0 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.48674 | 16
SPS | MUSTANG_6 118.000 230KV | 51 | 0.0973 | SPS | MUSTANG 115KV | 310 | 0.48674 | -0.38944 | 20
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0973 | -0.19439 | 39
SPS | MADOX 115KV | 148 | -0.09984 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0973 | -0.19714 | 39
SPS | CUNNINGHAM 230KV | 35 | -0.06402 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0973 | -0.16132 | 47
SPS | SN_JUAN_TAP6230.00 230KV | 106.7 | -0.01995 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0973 | -0.11725 | 65
SPS | ROOSEVELT_3 0.6900 34KV | 200 | -0.01238 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0973 | -0.10968 | 70
SPS | MADOX 115KV | 148 | -0.09984 | SPS | LUBBOCK CO SUB 230KV | 585.7245 | 0.00166 | -0.1015 | 75
SPS | MADOX 115KV | 148 | -0.09984 | SUNC | A. M. MULLERGREN GENERATOR 115KV | 93 | -1e-05 | -0.09983 | 76
SPS | MADOX 115KV | 148 | -0.09984 | SPS | ANTELOPE 230KV | 151.861 | 0.0001 | -0.09994 | 76
SPS | MADOX 115KV | 148 | -0.09984 | AEPW | ARSENAL HILL 138KV | 509 | 0 | -0.09984 | 76
SPS | MADOX 115KV | 148 | -0.09984 | AEPW | ARSENAL HILL 69KV | 110 | 0 | -0.09984 | 76
SPS | MADOX 115KV | 148 | -0.09984 | SPS | BLACKHAWK 115KV | 220 | -6e-05 | -0.09978 | 76
SPS | MADOX 115KV | 148 | -0.09984 | SUNC | CLIFTON 115KV | 68.3522 | 0 | -0.09984 | 76
SPS | MADOX 115KV | 148 | -0.09984 | AEPW | COGENTRIX 345KV | 512.0489 | 0 | -0.09984 | 76
SPS | MADOX 115KV | 148 | -0.09984 | AEPW | COMANCHE 138KV | 170 | 1e-05 | -0.09985 | 76
SPS | MADOX 115KV | 148 | -0.09984 | AEPW | COMANCHE 69KV | 71 | 1e-05 | -0.09985 | 76
SPS | MADOX 115KV | 148 | -0.09984 | AEPW | EASTMAN 138KV | 277.1198 | 0 | -0.09984 | 76
SPS | MADOX 115KV | 148 | -0.09984 | SPS | ELK_1 118.000 345KV | 196 | 9e-05 | -0.09993 | 76
SPS | MADOX 115KV | 148 | -0.09984 | AEPW | ELKINS GENERATOR 69KV | 60 | 0 | -0.09984 | 76
SPS | MADOX 115KV | 148 | -0.09984 | AEPW | FITZHUGH 161KV | 165 | 0 | -0.09984 | 76
SPS | MADOX 115KV | 148 | -0.09984 | AEPW | FLINT CREEK 161KV | 528 | 0 | -0.09984 | 76
SPS | MADOX 115KV | 148 | -0.09984 | AEPW | FULTON 115KV | 153 | 0 | -0.09984 | 76
SPS | MADOX 115KV | 148 | -0.09984 | SUNC | GARDEN CITY 115KV | 201 | -1e-05 | -0.09983 | 76
SPS | MADOX 115KV | 148 | -0.09984 | SPS | GOODWELL_2 10.6900 34KV | 200 | -4e-05 | -0.0998 | 76
SPS | MADOX 115KV | 148 | -0.09984 | SUNC | GRAY COUNTY WIND FARM 115KV | 36 | -1e-05 | -0.09983 | 76
SPS | MADOX 115KV | 148 | -0.09984 | SPS | HARRINGTON 230KV | 1017 | -7e-05 | -0.09977 | 76
SPS | MADOX 115KV | 148 | -0.09984 | SUNC | HOLCOMB 115KV | 360 | -1e-05 | -0.09983 | 76
SPS | MADOX 115KV | 148 | -0.09984 | SUNC | JAM_EC2 13.800 34KV | 26.6 | -1e-05 | -0.09983 | 76
SPS | MADOX 115KV | 148 | -0.09984 | SUNC | JUDSON LARGE 115KV | 132.3 | -1e-05 | -0.09983 | 76
SPS | MADOX 115KV | 148 | -0.09984 | AEPW | KNOXLEE 138KV | 342 | 0 | -0.09984 | 76
SPS | MADOX 115KV | 148 | -0.09984 | AEPW | LEBROCK 345KV | 187.1622 | 0 | -0.09984 | 76
SPS | MADOX 115KV | 148 | -0.09984 | AEPW | LIEBERMAN 138KV | 217 | 0 | -0.09984 | 76
SPS | MADOX 115KV | 148 | -0.09984 | SUNC | MRWYP16 230KV | 31 | 0 | -0.09984 | 76
SPS | MADOX 115KV | 148 | -0.09984 | SPS | NICHOLS 115KV | 180 | -7e-05 | -0.09977 | 76
SPS | MADOX 115KV | 148 | -0.09984 | SPS | NICHOLS 230KV | 150 | -7e-05 | -0.09977 | 76
SPS | MADOX 115KV | 148 | -0.09984 | AEPW | NORTHEASTERN STATION 138KV | 851 | 0 | -0.09984 | 76
SPS | MADOX 115KV | 148 | -0.09984 | AEPW | NORTHEASTERN STATION 345KV | 460 | 0 | -0.09984 | 76
SPS | MADOX 115KV | 148 | -0.09984 | AEPW | OEC 345KV | 1110 | 0 | -0.09984 | 76
SPS | MADOX 115KV | 148 | -0.09984 | AEPW | PIRKEY GENERATION 138KV | 675 | 0 | -0.09984 | 76
SPS | MADOX 115KV | 148 | -0.09984 | SPS | PLANTX 230KV | 175 | 0.00028 | -0.10012 | 76
SPS | MADOX 115KV | 148 | -0.09984 | SUNC | PRATT 115KV | 26.37 | 0 | -0.09984 | 76
SPS | MADOX 115KV | 148 | -0.09984 | AEPW | RIVERSIDE STATION 138KV | 908.0001 | 0 | -0.09984 | 76
SPS | MADOX 115KV | 148 | -0.09984 | SUNC | RUBART 2 13.800 115KV | 108 | -1e-05 | -0.09983 | 76
SPS | MADOX 115KV | 148 | -0.09984 | AEPW | SOUTHWESTERN STATION 138KV | 325.1865 | 0 | -0.09984 | 76
SPS | MADOX 115KV | 148 | -0.09984 | AEPW | TULSA POWER STATION 138KV | 306 | 0 | -0.09984 | 76
SPS | MADOX 115KV | 148 | -0.09984 | AEPW | TURK 138KV | 650 | 0 | -0.09984 | 76
SPS | MADOX 115KV | 148 | -0.09984 | AEPW | WELSH 345KV | 1056 | 0 | -0.09984 | 76
SPS | MADOX 115KV | 148 | -0.09984 | AEPW | WILKES 138KV | 468 | 0 | -0.09984 | 76
SPS | MADOX 115KV | 148 | -0.09984 | AEPW | WILKES 345KV | 348 | 0 | -0.09984 | 76
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | SPS | LUBBOCK CO SUB 230KV | 585.7245 | 0.00166 | -0.09875 | 77
SPS | MADOX 115KV | 148 | -0.09984 | SPS | PLANTX 115KV | 80 | -0.00011 | -0.09973 | 77
SPS | MADOX 115KV | 148 | -0.09984 | SPS | TOLK 230KV | 1018 | -0.0007 | -0.09914 | 77
SPS | MADOX 115KV | 148 | -0.09984 | SPS | WILWIND 34KV | 31.878 | -0.00013 | -0.09971 | 77
SUNC | CIMARRON RIVER 115KV | 33 | -1e-05 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0973 | -0.09731 | 78
AEPW | COGENTRIX 345KV | 381.9511 | 0 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0973 | -0.0973 | 78
SUNC | COMMANCHE COUNTY 115KV | 110 | -1e-05 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0973 | -0.09731 | 78
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | SPS | PLANTX 230KV | 175 | 0.00028 | -0.09737 | 78
AEPW | EASTMAN 138KV | 207.8902 | 0 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0973 | -0.0973 | 78
AEPW | KNOXLEE 138KV | 127 | 0 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0973 | -0.0973 | 78
AEPW | LEBROCK 345KV | 322.8378 | 0 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0973 | -0.0973 | 78
AEPW | LONESTAR POWER PLANT 69KV | 50 | 0 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0973 | -0.0973 | 78
SUNC | MRWYP16 230KV | 189 | 0 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0973 | -0.0973 | 78
SPS | NICHOLS 115KV | 28 | -7e-05 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0973 | -0.09737 | 78
SPS | NICHOLS 230KV | 90 | -7e-05 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0973 | -0.09737 | 78
AEPW | NORTHEASTERN STATION 345KV | 481 | 0 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0973 | -0.0973 | 78
AEPW | OEC 345KV | 100 | 0 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0973 | -0.0973 | 78
SUNC | PIONWF-7 34.500 345KV | 200 | -1e-05 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0973 | -0.09731 | 78
SPS | PLANTX 115KV | 142 | -0.00011 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0973 | -0.09741 | 78
AEPW | RIVERSIDE STATION 138KV | 139 | 0 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0973 | -0.0973 | 78
AEPW | SOUTHWESTERN STATION 138KV | 282.8135 | 0 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0973 | -0.0973 | 78
SPS | TOLK 230KV | 47 | -0.0007 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0973 | -0.098 | 78
AEPW | TONTITOWN 161KV | 301 | 0 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0973 | -0.0973 | 78
AEPW | TURK 138KV | 34 | 0 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0973 | -0.0973 | 78
AEPW | WELEETKA 138KV | 158 | 0 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0973 | -0.0973 | 78
AEPW | WELSH 345KV | 528 | 0 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0973 | -0.0973 | 78
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | SUNC | A. M. MULLERGREN GENERATOR 115KV | 93 | -1e-05 | -0.09708 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | SPS | ANTELOPE 230KV | 151.861 | 0.0001 | -0.09719 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | AEPW | ARSENAL HILL 138KV | 509 | 0 | -0.09709 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | AEPW | ARSENAL HILL 69KV | 110 | 0 | -0.09709 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | SPS | BLACKHAWK 115KV | 220 | -6e-05 | -0.09703 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | SUNC | CLIFTON 115KV | 68.3522 | 0 | -0.09709 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | AEPW | COGENTRIX 345KV | 512.0489 | 0 | -0.09709 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | AEPW | COMANCHE 138KV | 170 | 1e-05 | -0.0971 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | AEPW | COMANCHE 69KV | 71 | 1e-05 | -0.0971 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | AEPW | EASTMAN 138KV | 277.1198 | 0 | -0.09709 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | SPS | ELK_1 118.000 345KV | 196 | 9e-05 | -0.09718 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | AEPW | ELKINS GENERATOR 69KV | 60 | 0 | -0.09709 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | AEPW | FITZHUGH 161KV | 165 | 0 | -0.09709 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | AEPW | FLINT CREEK 161KV | 528 | 0 | -0.09709 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | AEPW | FULTON 115KV | 153 | 0 | -0.09709 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | SUNC | GARDEN CITY 115KV | 201 | -1e-05 | -0.09708 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | SPS | GOODWELL_2 10.6900 34KV | 200 | -4e-05 | -0.09705 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | SUNC | GRAY COUNTY WIND FARM 115KV | 36 | -1e-05 | -0.09708 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | SPS | HARRINGTON 230KV | 1017 | -7e-05 | -0.09702 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | SUNC | HOLCOMB 115KV | 360 | -1e-05 | -0.09708 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | SUNC | JAM_EC2 13.800 34KV | 26.6 | -1e-05 | -0.09708 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | SUNC | JUDSON LARGE 115KV | 132.3 | -1e-05 | -0.09708 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | AEPW | KNOXLEE 138KV | 342 | 0 | -0.09709 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | AEPW | LEBROCK 345KV | 187.1622 | 0 | -0.09709 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | AEPW | LIEBERMAN 138KV | 217 | 0 | -0.09709 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | SUNC | MRWYP16 230KV | 31 | 0 | -0.09709 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | SPS | NICHOLS 115KV | 180 | -7e-05 | -0.09702 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | SPS | NICHOLS 230KV | 150 | -7e-05 | -0.09702 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | AEPW | NORTHEASTERN STATION 138KV | 851 | 0 | -0.09709 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | AEPW | NORTHEASTERN STATION 345KV | 460 | 0 | -0.09709 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | AEPW | OEC 345KV | 1110 | 0 | -0.09709 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | AEPW | PIRKEY GENERATION 138KV | 675 | 0 | -0.09709 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | SPS | PLANTX 115KV | 80 | -0.00011 | -0.09698 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | SUNC | PRATT 115KV | 26.37 | 0 | -0.09709 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | AEPW | RIVERSIDE STATION 138KV | 908.0001 | 0 | -0.09709 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | SUNC | RUBART 2 13.800 115KV | 108 | -1e-05 | -0.09708 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | AEPW | SOUTHWESTERN STATION 138KV | 325.1865 | 0 | -0.09709 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | SPS | TOLK 230KV | 1018 | -0.0007 | -0.09639 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | AEPW | TULSA POWER STATION 138KV | 306 | 0 | -0.09709 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | AEPW | TURK 138KV | 650 | 0 | -0.09709 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | AEPW | WELSH 345KV | 1056 | 0 | -0.09709 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | AEPW | WILKES 138KV | 468 | 0 | -0.09709 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | AEPW | WILKES 345KV | 348 | 0 | -0.09709 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | SPS | WILWIND 34KV | 31.878 | -0.00013 | -0.09696 | 79
SPS | LP-HOLL2 69KV | 62.67 | 0.00149 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0973 | -0.09581 | 80
SPS | LUBBOCK CO SUB 230KV | 71.2754 | 0.00166 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0973 | -0.09564 | 80
SPS | MADOX 115KV | 148 | -0.09984 | SPS | ROOSEVELT_3 0.6900 34KV | 248.4 | -0.01238 | -0.08746 | 87
SPS | CUNNINGHAM 115KV | 56 | -0.09709 | SPS | ROOSEVELT_3 0.6900 34KV | 248.4 | -0.01238 | -0.08471 | 90
SPS | MADOX 115KV | 148 | -0.09984 | SPS | HOBBS PLANT #3 (ST) 230KV | 200 | -0.06308 | -0.03676 | 208
SPS | MADOX 115KV | 148 | -0.09984 | SPS | CUNNINGHAM 230KV | 254 | -0.06402 | -0.03582 | 213
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor
Upgrade: | Mustang to Shell CO2 115 kV
Limiting Facility: | DENVER CITY INTERCHANGE S. - MUSTANG STATION N. 115KV CKT 2
Direction: | TO->FROM
Line Outage: | DENVER CITY INTERCHANGE N. - MUSTANG STATION N. 115KV CKT 1
Flowgate: | 2013AG3AFS61T1015016SP
Date Redispatch Needed: | Starting 2016 6/1 - 10/1 Until EOC of Upgrade
Season Flowgate Identified: | 2016 Summer Peak
Reservation | Relief Amount | Aggregate Relief Amount
78751808 | 7.6 | 7.6
Source Control Area | Source | Maximum Increment (MW) | GSF | Sink Control Area | Sink | Maximum Decrement (MW) | GSF | Factor | Aggregate Redispatch Amount (MW)
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.57882 | 13
SPS | HOBBS PLANT #2 (CT) 115KV | 9 | -0.09915 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.58164 | 13
SPS | MADOX 115KV | 148 | -0.09905 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.58154 | 13
SPS | CARLSBAD 69KV | 10 | -0.05847 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.54096 | 14
SPS | CUNNINGHAM 230KV | 35 | -0.06353 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.54602 | 14
SPS | HOBBS PLANT #3 (ST) 230KV | 13 | -0.0626 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.54509 | 14
SPS | ROOSEVELT_3 0.6900 34KV | 200 | -0.0123 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.49479 | 15
SPS | QUAY_CNTY 113.800 115KV | 23 | -0.00617 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.48866 | 15
SPS | SN_JUAN_TAP6230.00 230KV | 106.7 | -0.0198 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.50229 | 15
SPS | ANTELOPE 230KV | 8.933 | 0.0001 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.48239 | 16
SUNC | CIMARRON RIVER 115KV | 33 | -1e-05 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.4825 | 16
SUNC | CIM-PLT 13.800 13KV | 14 | -1e-05 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.4825 | 16
SUNC | CITY OF GOODLAND 115KV | 13.9 | -1e-05 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.4825 | 16
SUNC | CITY OF HILL CITY 115KV | 6.1 | -1e-05 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.4825 | 16
SUNC | CITY OF HUGOTON 69KV | 15.17 | -1e-05 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.4825 | 16
AEPW | COGENTRIX 345KV | 381.9511 | 0 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.48249 | 16
SUNC | COMMANCHE COUNTY 115KV | 110 | -1e-05 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.4825 | 16
SUNC | DONLEY CO SUB 69KV | 21.25 | -1e-05 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.4825 | 16
AEPW | EASTMAN 138KV | 207.8902 | 0 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.48249 | 16
SUNC | GARDEN CITY 115KV | 8 | -1e-05 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.4825 | 16
SUNC | GARDEN CITY 69KV | 10 | -1e-05 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.4825 | 16
SUNC | HOLCOMB 115KV | 24 | -1e-05 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.4825 | 16
SPS | HUBRCO2 69KV | 11 | -6e-05 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.48255 | 16
SUNC | JUDSON LARGE 115KV | 10.7 | -1e-05 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.4825 | 16
AEPW | KNOXLEE 138KV | 127 | 0 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.48249 | 16
AEPW | LEBROCK 345KV | 322.8378 | 0 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.48249 | 16
AEPW | LIEBERMAN 138KV | 25 | 0 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.48249 | 16
AEPW | LONESTAR POWER PLANT 69KV | 50 | 0 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.48249 | 16
SPS | LP-HOLL2 69KV | 62.67 | 0.00149 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.481 | 16
SPS | LUBBOCK CO SUB 230KV | 71.2754 | 0.00165 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.48084 | 16
SUNC | MRWYP16 230KV | 189 | 0 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.48249 | 16
SPS | NICHOLS 115KV | 28 | -7e-05 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.48256 | 16
SPS | NICHOLS 230KV | 90 | -7e-05 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.48256 | 16
SUNC | NORTH WEST GREAT BEND 115KV | 10.21 | -1e-05 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.4825 | 16
AEPW | NORTHEASTERN STATION 345KV | 481 | 0 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.48249 | 16
AEPW | OEC 345KV | 100 | 0 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.48249 | 16
SUNC | PIONWF-7 34.500 345KV | 200 | -1e-05 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.4825 | 16
SPS | PLANTX 115KV | 142 | -0.00011 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.4826 | 16
SPS | PLANTX 230KV | 12 | 0.00027 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.48222 | 16
AEPW | RIVERSIDE STATION 138KV | 139 | 0 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.48249 | 16
SUNC | RUSSELL 115KV | 8.17 | -1e-05 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.4825 | 16
SPS | SIDRCH 69KV | 15 | -6e-05 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.48255 | 16
AEPW | SOUTHWESTERN STATION 138KV | 282.8135 | 0 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.48249 | 16
SPS | TOLK 230KV | 47 | -0.0007 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.48319 | 16
AEPW | TONTITOWN 161KV | 301 | 0 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.48249 | 16
AEPW | TURK 138KV | 34 | 0 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.48249 | 16
AEPW | WELEETKA 138KV | 158 | 0 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.48249 | 16
AEPW | WELSH 345KV | 528 | 0 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.48249 | 16
AEPW | WILKES 138KV | 10 | 0 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.48249 | 16
SPS | MUSTANG_6 118.000 230KV | 51 | 0.0964 | SPS | MUSTANG 115KV | 310 | 0.48249 | -0.38609 | 20
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0964 | -0.19273 | 39
SPS | MADOX 115KV | 148 | -0.09905 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0964 | -0.19545 | 39
SPS | CUNNINGHAM 230KV | 35 | -0.06353 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0964 | -0.15993 | 47
SPS | SN_JUAN_TAP6230.00 230KV | 106.7 | -0.0198 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0964 | -0.1162 | 65
SPS | ROOSEVELT_3 0.6900 34KV | 200 | -0.0123 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0964 | -0.1087 | 70
SPS | MADOX 115KV | 148 | -0.09905 | SPS | LUBBOCK CO SUB 230KV | 585.7245 | 0.00165 | -0.1007 | 75
SPS | MADOX 115KV | 148 | -0.09905 | SUNC | A. M. MULLERGREN GENERATOR 115KV | 93 | -1e-05 | -0.09904 | 76
SPS | MADOX 115KV | 148 | -0.09905 | SPS | ANTELOPE 230KV | 151.861 | 0.0001 | -0.09915 | 76
SPS | MADOX 115KV | 148 | -0.09905 | AEPW | ARSENAL HILL 138KV | 509 | 0 | -0.09905 | 76
SPS | MADOX 115KV | 148 | -0.09905 | AEPW | ARSENAL HILL 69KV | 110 | 0 | -0.09905 | 76
SPS | MADOX 115KV | 148 | -0.09905 | SPS | BLACKHAWK 115KV | 220 | -6e-05 | -0.09899 | 76
SPS | MADOX 115KV | 148 | -0.09905 | SUNC | CLIFTON 115KV | 68.3522 | 0 | -0.09905 | 76
SPS | MADOX 115KV | 148 | -0.09905 | AEPW | COGENTRIX 345KV | 512.0489 | 0 | -0.09905 | 76
SPS | MADOX 115KV | 148 | -0.09905 | AEPW | COMANCHE 138KV | 170 | 1e-05 | -0.09906 | 76
SPS | MADOX 115KV | 148 | -0.09905 | AEPW | COMANCHE 69KV | 71 | 1e-05 | -0.09906 | 76
SPS | MADOX 115KV | 148 | -0.09905 | AEPW | EASTMAN 138KV | 277.1198 | 0 | -0.09905 | 76
SPS | MADOX 115KV | 148 | -0.09905 | SPS | ELK_1 118.000 345KV | 196 | 9e-05 | -0.09914 | 76
SPS | MADOX 115KV | 148 | -0.09905 | AEPW | ELKINS GENERATOR 69KV | 60 | 0 | -0.09905 | 76
SPS | MADOX 115KV | 148 | -0.09905 | AEPW | FITZHUGH 161KV | 165 | 0 | -0.09905 | 76
SPS | MADOX 115KV | 148 | -0.09905 | AEPW | FLINT CREEK 161KV | 528 | 0 | -0.09905 | 76
SPS | MADOX 115KV | 148 | -0.09905 | AEPW | FULTON 115KV | 153 | 0 | -0.09905 | 76
SPS | MADOX 115KV | 148 | -0.09905 | SUNC | GARDEN CITY 115KV | 201 | -1e-05 | -0.09904 | 76
SPS | MADOX 115KV | 148 | -0.09905 | SPS | GOODWELL_2 10.6900 34KV | 200 | -4e-05 | -0.09901 | 76
SPS | MADOX 115KV | 148 | -0.09905 | SUNC | GRAY COUNTY WIND FARM 115KV | 36 | -1e-05 | -0.09904 | 76
SPS | MADOX 115KV | 148 | -0.09905 | SPS | HARRINGTON 230KV | 1017 | -7e-05 | -0.09898 | 76
SPS | MADOX 115KV | 148 | -0.09905 | SUNC | HOLCOMB 115KV | 360 | -1e-05 | -0.09904 | 76
SPS | MADOX 115KV | 148 | -0.09905 | SUNC | JAM_EC2 13.800 34KV | 26.6 | -1e-05 | -0.09904 | 76
SPS | MADOX 115KV | 148 | -0.09905 | SUNC | JUDSON LARGE 115KV | 132.3 | -1e-05 | -0.09904 | 76
SPS | MADOX 115KV | 148 | -0.09905 | AEPW | KNOXLEE 138KV | 342 | 0 | -0.09905 | 76
SPS | MADOX 115KV | 148 | -0.09905 | AEPW | LEBROCK 345KV | 187.1622 | 0 | -0.09905 | 76
SPS | MADOX 115KV | 148 | -0.09905 | AEPW | LIEBERMAN 138KV | 217 | 0 | -0.09905 | 76
SPS | MADOX 115KV | 148 | -0.09905 | SUNC | MRWYP16 230KV | 31 | 0 | -0.09905 | 76
SPS | MADOX 115KV | 148 | -0.09905 | SPS | NICHOLS 115KV | 180 | -7e-05 | -0.09898 | 76
SPS | MADOX 115KV | 148 | -0.09905 | SPS | NICHOLS 230KV | 150 | -7e-05 | -0.09898 | 76
SPS | MADOX 115KV | 148 | -0.09905 | AEPW | NORTHEASTERN STATION 138KV | 851 | 0 | -0.09905 | 76
SPS | MADOX 115KV | 148 | -0.09905 | AEPW | NORTHEASTERN STATION 345KV | 460 | 0 | -0.09905 | 76
SPS | MADOX 115KV | 148 | -0.09905 | AEPW | OEC 345KV | 1110 | 0 | -0.09905 | 76
SPS | MADOX 115KV | 148 | -0.09905 | AEPW | PIRKEY GENERATION 138KV | 675 | 0 | -0.09905 | 76
SPS | MADOX 115KV | 148 | -0.09905 | SPS | PLANTX 115KV | 80 | -0.00011 | -0.09894 | 76
SPS | MADOX 115KV | 148 | -0.09905 | SPS | PLANTX 230KV | 175 | 0.00027 | -0.09932 | 76
SPS | MADOX 115KV | 148 | -0.09905 | SUNC | PRATT 115KV | 26.37 | 0 | -0.09905 | 76
SPS | MADOX 115KV | 148 | -0.09905 | AEPW | RIVERSIDE STATION 138KV | 908.0001 | 0 | -0.09905 | 76
SPS | MADOX 115KV | 148 | -0.09905 | SUNC | RUBART 2 13.800 115KV | 108 | -1e-05 | -0.09904 | 76
SPS | MADOX 115KV | 148 | -0.09905 | AEPW | SOUTHWESTERN STATION 138KV | 325.1865 | 0 | -0.09905 | 76
SPS | MADOX 115KV | 148 | -0.09905 | AEPW | TULSA POWER STATION 138KV | 306 | 0 | -0.09905 | 76
SPS | MADOX 115KV | 148 | -0.09905 | AEPW | TURK 138KV | 650 | 0 | -0.09905 | 76
SPS | MADOX 115KV | 148 | -0.09905 | AEPW | WELSH 345KV | 1056 | 0 | -0.09905 | 76
SPS | MADOX 115KV | 148 | -0.09905 | AEPW | WILKES 138KV | 468 | 0 | -0.09905 | 76
SPS | MADOX 115KV | 148 | -0.09905 | AEPW | WILKES 345KV | 348 | 0 | -0.09905 | 76
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | SPS | LUBBOCK CO SUB 230KV | 585.7245 | 0.00165 | -0.09798 | 77
SPS | MADOX 115KV | 148 | -0.09905 | SPS | TOLK 230KV | 1018 | -0.0007 | -0.09835 | 77
SPS | MADOX 115KV | 148 | -0.09905 | SPS | WILWIND 34KV | 31.878 | -0.00014 | -0.09891 | 77
SUNC | CIMARRON RIVER 115KV | 33 | -1e-05 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0964 | -0.09641 | 78
SUNC | COMMANCHE COUNTY 115KV | 110 | -1e-05 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0964 | -0.09641 | 78
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | SPS | ANTELOPE 230KV | 151.861 | 0.0001 | -0.09643 | 78
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | SPS | ELK_1 118.000 345KV | 196 | 9e-05 | -0.09642 | 78
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | SPS | PLANTX 230KV | 175 | 0.00027 | -0.0966 | 78
SPS | NICHOLS 115KV | 28 | -7e-05 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0964 | -0.09647 | 78
SPS | NICHOLS 230KV | 90 | -7e-05 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0964 | -0.09647 | 78
SUNC | PIONWF-7 34.500 345KV | 200 | -1e-05 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0964 | -0.09641 | 78
SPS | PLANTX 115KV | 142 | -0.00011 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0964 | -0.09651 | 78
SPS | TOLK 230KV | 47 | -0.0007 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0964 | -0.0971 | 78
AEPW | COGENTRIX 345KV | 381.9511 | 0 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0964 | -0.0964 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | SUNC | A. M. MULLERGREN GENERATOR 115KV | 93 | -1e-05 | -0.09632 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | AEPW | ARSENAL HILL 138KV | 509 | 0 | -0.09633 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | AEPW | ARSENAL HILL 69KV | 110 | 0 | -0.09633 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | SPS | BLACKHAWK 115KV | 220 | -6e-05 | -0.09627 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | SUNC | CLIFTON 115KV | 68.3522 | 0 | -0.09633 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | AEPW | COGENTRIX 345KV | 512.0489 | 0 | -0.09633 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | AEPW | COMANCHE 138KV | 170 | 1e-05 | -0.09634 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | AEPW | COMANCHE 69KV | 71 | 1e-05 | -0.09634 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | AEPW | EASTMAN 138KV | 277.1198 | 0 | -0.09633 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | AEPW | ELKINS GENERATOR 69KV | 60 | 0 | -0.09633 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | AEPW | FITZHUGH 161KV | 165 | 0 | -0.09633 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | AEPW | FLINT CREEK 161KV | 528 | 0 | -0.09633 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | AEPW | FULTON 115KV | 153 | 0 | -0.09633 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | SUNC | GARDEN CITY 115KV | 201 | -1e-05 | -0.09632 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | SPS | GOODWELL_2 10.6900 34KV | 200 | -4e-05 | -0.09629 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | SUNC | GRAY COUNTY WIND FARM 115KV | 36 | -1e-05 | -0.09632 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | SPS | HARRINGTON 230KV | 1017 | -7e-05 | -0.09626 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | SUNC | HOLCOMB 115KV | 360 | -1e-05 | -0.09632 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | SUNC | JAM_EC2 13.800 34KV | 26.6 | -1e-05 | -0.09632 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | SUNC | JUDSON LARGE 115KV | 132.3 | -1e-05 | -0.09632 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | AEPW | KNOXLEE 138KV | 342 | 0 | -0.09633 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | AEPW | LEBROCK 345KV | 187.1622 | 0 | -0.09633 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | AEPW | LIEBERMAN 138KV | 217 | 0 | -0.09633 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | SUNC | MRWYP16 230KV | 31 | 0 | -0.09633 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | SPS | NICHOLS 115KV | 180 | -7e-05 | -0.09626 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | SPS | NICHOLS 230KV | 150 | -7e-05 | -0.09626 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | AEPW | NORTHEASTERN STATION 138KV | 851 | 0 | -0.09633 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | AEPW | NORTHEASTERN STATION 345KV | 460 | 0 | -0.09633 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | AEPW | OEC 345KV | 1110 | 0 | -0.09633 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | AEPW | PIRKEY GENERATION 138KV | 675 | 0 | -0.09633 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | SPS | PLANTX 115KV | 80 | -0.00011 | -0.09622 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | SUNC | PRATT 115KV | 26.37 | 0 | -0.09633 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | AEPW | RIVERSIDE STATION 138KV | 908.0001 | 0 | -0.09633 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | SUNC | RUBART 2 13.800 115KV | 108 | -1e-05 | -0.09632 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | AEPW | SOUTHWESTERN STATION 138KV | 325.1865 | 0 | -0.09633 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | SPS | TOLK 230KV | 1018 | -0.0007 | -0.09563 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | AEPW | TULSA POWER STATION 138KV | 306 | 0 | -0.09633 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | AEPW | TURK 138KV | 650 | 0 | -0.09633 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | AEPW | WELSH 345KV | 1056 | 0 | -0.09633 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | AEPW | WILKES 138KV | 468 | 0 | -0.09633 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | AEPW | WILKES 345KV | 348 | 0 | -0.09633 | 79
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | SPS | WILWIND 34KV | 31.878 | -0.00014 | -0.09619 | 79
AEPW | EASTMAN 138KV | 207.8902 | 0 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0964 | -0.0964 | 79
AEPW | KNOXLEE 138KV | 127 | 0 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0964 | -0.0964 | 79
AEPW | LEBROCK 345KV | 322.8378 | 0 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0964 | -0.0964 | 79
AEPW | LONESTAR POWER PLANT 69KV | 50 | 0 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0964 | -0.0964 | 79
SUNC | MRWYP16 230KV | 189 | 0 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0964 | -0.0964 | 79
AEPW | NORTHEASTERN STATION 345KV | 481 | 0 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0964 | -0.0964 | 79
AEPW | OEC 345KV | 100 | 0 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0964 | -0.0964 | 79
AEPW | RIVERSIDE STATION 138KV | 139 | 0 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0964 | -0.0964 | 79
AEPW | SOUTHWESTERN STATION 138KV | 282.8135 | 0 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0964 | -0.0964 | 79
AEPW | TONTITOWN 161KV | 301 | 0 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0964 | -0.0964 | 79
AEPW | TURK 138KV | 34 | 0 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0964 | -0.0964 | 79
AEPW | WELEETKA 138KV | 158 | 0 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0964 | -0.0964 | 79
AEPW | WELSH 345KV | 528 | 0 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0964 | -0.0964 | 79
SPS | LP-HOLL2 69KV | 62.67 | 0.00149 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0964 | -0.09491 | 80
SPS | LUBBOCK CO SUB 230KV | 71.2754 | 0.00165 | SPS | MUSTANG_6 118.000 230KV | 622 | 0.0964 | -0.09475 | 80
SPS | MADOX 115KV | 148 | -0.09905 | SPS | ROOSEVELT_3 0.6900 34KV | 248.4 | -0.0123 | -0.08675 | 87
SPS | CUNNINGHAM 115KV | 56 | -0.09633 | SPS | ROOSEVELT_3 0.6900 34KV | 248.4 | -0.0123 | -0.08403 | 90
SPS | MADOX 115KV | 148 | -0.09905 | SPS | HOBBS PLANT #3 (ST) 230KV | 200 | -0.0626 | -0.03645 | 208
SPS | MADOX 115KV | 148 | -0.09905 | SPS | CUNNINGHAM 230KV | 254 | -0.06353 | -0.03552 | 213
Maximum Decrement and Maximum Increment were determine from the Souce and Sink Operating Points in the study models where limiting facility was identified.
Factor = Source GSF - Sink GSF
Redispatch Amount = Relief Amount / Factor

## Table7
Upgrade Name | Customer | Study Number | Reservation | Allocation Percentage | Allocated E & C Cost
EDDY CO 230kV Bus Tie | SPSM | 2013-AG3-027 | 78751808 | 100% | 9485379
|  |  |  | Total: | 9485379