## tblAllFacilityLog
STUDYDES | STUDYDES2 | EVENTTYPE | AssessmentSOLUTIONTYPE | AssessmenFDNS-TERMINATION | SOLUTIONTYPE | FDNS-TERMINATION | GROUP | SCENARIO | FGName | DIRECTION | FacilityName | FacilityUpgradeCode | ModelArea1 | ModelArea2 | FZONENAME | TZONENAME | MONTFLAG | MONTFB | MONTFNAME | MONTTB1 | MONTTNAME1 | MONTTB2 | MONTTNAME2 | MONTCKT | Case | RATEA | RATEB | RATEC | Assessment Loading | BaseCaseLoading | TransferCaseLoading | NameOfBusWithMonitoredVoltage | Assessment Voltage | BaseCaseVoltage | TransferCaseVoltage | VINIT | VMIN | VMAX | CATEGORY | CONTTYPE | CONTNAME | CONTXFMRFLAG | CONTFB | CONTFNAME | CONTTB1 | CONTTNAME1 | CONTTB2 | CONTTNAME2 | CONTCKT | TransmissionProviderCommentsNotes | RequiredRateB | TransmissionOwnerComments | OwnerDesignation | UpgradeName | UpgradeComponentWithinFacility | NewSummerA | NewSummerB | NewOtherA | NewOtherB | DistToConstruct | TotalLead | ConstructionLeadOnly | NewOrConstructWhileEnergized | NewR | NewX | NewB | CommentsRegardingUpgradeRequirements | NewCost | EffDate | NetPlantDate | ReusableEx_GrossValue | ReusableEx_NetValue | Reusable_EndofDepr | SalvageValue | NewCostWhileExpediting | EffDateExpedited | StartDeprExpedited | EndDeprExpedited | NetPlantDateExpedited | ReusableEx_GrossExpedited | ReusableEx_NetExpedited | Reusable_EndofDeprExpedited | SalvageValueExpedited | Generation 1 Owner & Unit (Name) | Generation 1 Redispatch Cost ($) | Generation 1 Redispatch Date (M/D/Y) | Generation 2 Owner & Unit (Name) | Generation 2 Redispatch Cost ($) | Generation 2 Redispatch Date (M/D/Y) | Generation 3 Owner & Unit (Name) | Generation 3 Redispatch Cost ($) | Generation 3 Redispatch Date (M/D/Y) | ActualCompletion | ActualNewCost | ActualNetPlantDate | ActualReusableEx_GrossValue | ActualReusableEx_NetValue | ActualReusable_EndofDepr | ActualSalvageValue | Actual_NewCostWhileExpediting | Actual_StartDeprExp | Actual_EndDeprExp | Actual_NetPlantDateExpedited | ActualReusableEx_GrossExpedited | ActualReusableEx_NetExpedited | ActualReusable_EndofDeprExpedited | Actual_SalvageValueExpedited | SPPReliabilityDate | DUN | EOC | EarliestDate
2015-AG1 | AFS2 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2405516SP | FROM->TO | 45TH ST4 138.00 - COWSKIN 138KV CKT 1 | EXP | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533074 | 45TH ST4 138.00 | 533038 | COWSKIN4 138.00 | 0 |  | 1 | 16SP | 382 | 382 | 0 | 100.8 | 100.8033 | 108.3691 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | WERE | Multi - Viola 345/138kV Transformer and 138 kV Lines to Clearwater and Gill | Install 345/138 kV transformer at future Viola 345 kV substation. Build 138kV line from Viola to Clearwater substation. Build 138 kV line from Viola to Gill substation | [53 empty] | 2016-06-01 | 2019-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T14225516SP | FROM->TO | 45TH ST4 138.00 - COWSKIN 138KV CKT 1 | EXP | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533074 | 45TH ST4 138.00 | 533038 | COWSKIN4 138.00 | 0 |  | 1 | 16SP | 382 | 382 | 0 | 97.3 | 97.3316 | 104.5405 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WR-416 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | Multi - Viola 345/138kV Transformer and 138 kV Lines to Clearwater and Gill | Install 345/138 kV transformer at future Viola 345 kV substation. Build 138kV line from Viola to Clearwater substation. Build 138 kV line from Viola to Gill substation | [53 empty] | 2016-06-01 | 2019-06-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T14335516SP | FROM->TO | 45TH ST4 138.00 - COWSKIN 138KV CKT 1 | EXP | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533074 | 45TH ST4 138.00 | 533038 | COWSKIN4 138.00 | 0 |  | 1 | 16SP | 382 | 382 | 0 |  | 94.5148 | 101.7756 | [7 empty] | CATEGORYB | NONSINGLE | WR-B3-14 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | Multi - Viola 345/138kV Transformer and 138 kV Lines to Clearwater and Gill | Install 345/138 kV transformer at future Viola 345 kV substation. Build 138kV line from Viola to Clearwater substation. Build 138 kV line from Viola to Gill substation | [53 empty] | 2016-06-01 | 2019-06-01
2015-AG1 | AFS2 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2415516SP | TO->FROM | 45TH ST4 138.00 - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | EXP | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533041 | EVANS S4 138.00 | 533074 | 45TH ST4 138.00 | 0 |  | 1 | 16SP | 382 | 382 | 0 | 102.1 | 102.1156 | 109.6762 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 |  |  |  | WERE | Multi - Viola 345/138kV Transformer and 138 kV Lines to Clearwater and Gill | Install 345/138 kV transformer at future Viola 345 kV substation. Build 138kV line from Viola to Clearwater substation. Build 138 kV line from Viola to Gill substation | [53 empty] | 2016-06-01 | 2019-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T14235516SP | TO->FROM | 45TH ST4 138.00 - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | EXP | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533041 | EVANS S4 138.00 | 533074 | 45TH ST4 138.00 | 0 |  | 1 | 16SP | 382 | 382 | 0 | 98.6 | 98.6433 | 105.8487 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WR-416 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | Multi - Viola 345/138kV Transformer and 138 kV Lines to Clearwater and Gill | Install 345/138 kV transformer at future Viola 345 kV substation. Build 138kV line from Viola to Clearwater substation. Build 138 kV line from Viola to Gill substation | [53 empty] | 2016-06-01 | 2019-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T14345516SP | TO->FROM | 45TH ST4 138.00 - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | EXP | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533041 | EVANS S4 138.00 | 533074 | 45TH ST4 138.00 | 0 |  | 1 | 16SP | 382 | 382 | 0 | 95.8 | 95.8262 | 103.0831 | [7 empty] | CATEGORYB | NONSINGLE | WR-B3-14 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | Multi - Viola 345/138kV Transformer and 138 kV Lines to Clearwater and Gill | Install 345/138 kV transformer at future Viola 345 kV substation. Build 138kV line from Viola to Clearwater substation. Build 138 kV line from Viola to Gill substation | [53 empty] | 2016-06-01 | 2019-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T695520SP | FROM->TO | 5WASHBRN 161.00 161/69KV TRANSFORMER CKT 1 | S | AECI | AECI | KAMO-MO | KAMO-MO | 0 | 300129 | 5WASHBRN 161.00 | 300763 | 2WASHBRN 69.000 | 0 |  | 1 | 20SP | 56 | 56 | 0 | 110 | 110.0248 | 109.3833 | [7 empty] | CATEGORYB | SINGLE | BEAVER - EUREKA SPRINGS 161KV CKT 1 | 0 | 505480 | BEAVER 5 161.00 | 506932 | EUREKA 5 161.00 | 0 |  | 1 |  |  |  | AECI | 5WASHBRN 161.00 161/69KV TRANSFORMER CKT 1 | Replace existing transformer | [11 empty] | SPP Estimate | 1978085 | 2015-06-03 | [39 empty] | 2017-06-01 | 2017-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T5645520SP | TO->FROM | AINSWORTH - AINSWORTH 115KV CKT 1 | EXP | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640050 | AINSWND7 115.00 | 640051 | AINSWRT7 115.00 | 0 |  | 1 | 20SP | 120 | 120 | 132 | 106.6 | 106.5608 | 110.239 | [7 empty] | CATEGORYB | SINGLE | FT RANDAL - SPENCER 115KV CKT 1 | 0 | 640349 | SPENCER7 115.00 | 652510 | FTRANDL7 115.00 | 0 |  | 1 |  |  |  | NPPD | Ainsworth - Ainsworth Wind 115 kV Ckt 1 | Rebuild 7.1-mile 115 kV line from Ainsworth to Ainsworth Wind to achieve a new emergency rating of 140 MVA. | [53 empty] | 2017-06-01 | 2020-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T5625520SP | TO->FROM | AINSWORTH - AINSWORTH 115KV CKT 1 | EXP | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640050 | AINSWND7 115.00 | 640051 | AINSWRT7 115.00 | 0 |  | 1 | 20SP | 120 | 120 | 132 | 105.4 | 105.3537 | 109.6244 | [7 empty] | CATEGORYB | SINGLE | ONEILL - SPENCER 115KV CKT 1 | 0 | 640305 | ONEILL 7 115.00 | 640349 | SPENCER7 115.00 | 0 |  | 1 |  |  |  | NPPD | Ainsworth - Ainsworth Wind 115 kV Ckt 1 | Rebuild 7.1-mile 115 kV line from Ainsworth to Ainsworth Wind to achieve a new emergency rating of 140 MVA. | [53 empty] | 2017-06-01 | 2020-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T17465520SP | TO->FROM | AINSWORTH - AINSWORTH 115KV CKT 1 | EXP | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640050 | AINSWND7 115.00 | 640051 | AINSWRT7 115.00 | 0 |  | 1 | 20SP | 120 | 120 | 132 | 105.3 | 105.2893 | 109.5585 | [7 empty] | CATEGORYB | NONSINGLE | LN-WAPA6 | 0 | 0 |  | 0 |  | 0 | [5 empty] | NPPD | Ainsworth - Ainsworth Wind 115 kV Ckt 1 | Rebuild 7.1-mile 115 kV line from Ainsworth to Ainsworth Wind to achieve a new emergency rating of 140 MVA. | [53 empty] | 2017-06-01 | 2020-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T17475520SP | TO->FROM | AINSWORTH - AINSWORTH 115KV CKT 1 | EXP | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640050 | AINSWND7 115.00 | 640051 | AINSWRT7 115.00 | 0 |  | 1 | 20SP | 120 | 120 | 132 | 97.8 | 97.7768 | 101.7583 | [7 empty] | CATEGORYB | NONSINGLE | WAPA-OG-2 | 0 | 0 |  | 0 |  | 0 | [5 empty] | NPPD | Ainsworth - Ainsworth Wind 115 kV Ckt 1 | Rebuild 7.1-mile 115 kV line from Ainsworth to Ainsworth Wind to achieve a new emergency rating of 140 MVA. | [53 empty] | 2017-06-01 | 2020-06-01
GI | GEN-2006-044N | [9 empty] | ALBION - PETERSBURG 115KV CKT 1 | U | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640318 | PETRSBG7 115.00 | 640054 | ALBION 7 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | NPPD | Albion - Petersburg 115kV Ckt 1 GEN-2006-044N Upgrade | Replace Breaker Switch 1106-D & jumpers; Replace Petersburg 115kV Substation main bus; Upgrade and replace transmission structures on 115kV lines TL1168 A & B to facilitate 100 degrees Centigrade line operation | [13 empty] | 2011-01-01 | [39 empty] | 2012-12-31 | 2012-12-31 | 2012-12-01
2009-AGP1 | AFS-5 | [9 empty] | ALTUS SW - NAVAJO 69KV CKT 1 | U | WFEC | WFEC | AEP-KP | AEP-KP | 0 | 521009 | NAVAJO 2 69.000 | 520805 | ALTUSSW2 69.000 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WFEC | ALTUS SW - NAVAJO 69KV CKT 1 | Upgrade Terminal Equipment at Altus SW, 300-600A, new rating conductor 53/65MVA | [53 empty] | 2013-06-01 | 2013-06-01
2006-AG1 | AFS-4 | [9 empty] | ALUMAX TAP - BANN 138KV CKT 1 | U | AEPW | AEPW |  |  | 0 | 508049 | ALUMXT 4 138 | 508054 | BANN 4 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | ALUMAX TAP - BANN 138KV CKT 1 | Replace six (6) 138 kV switches, five at Bann & one at Alumax Tap. Rebuild 0.67 miles of 1024 ACAR with 2156 ACSR. Replace wavetrap & jumpers @ Bann. Replace breaker 3300 @ Bann. | [53 empty] | 2008-06-01 | 2008-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T945025WP | TO->FROM | AMOCO SWITCHING STATION - SUNDOWN INTERCHANGE 230KV CKT 1 | EXP | SPS | SPS | SPS-CNPL | SPS-CNPL | 0 | 526435 | SUNDOWN 6230.00 | 526460 | AMOCO_SS 6230.00 | 0 |  | 1 | 25WP | 329 | 361 | 0 | 120.8 | 120.7992 | 114.3918 | [7 empty] | CATEGORYB | SINGLE | TUCO INTERCHANGE - YOAKUM_345 345.00 345KV CKT 1 | 0 | 525832 | TUCO_INT 7345.00 | 526936 | YOAKUM_345 345.00 | 0 |  | 1 |  |  |  | SPS | Amoco - Sundown 230 kV Terminal Upgrades | Upgrade wave traps at Sundown and Amoco to 1200 A to achieve a new emergency rating of 437 MVA on the 230 kV line from Amoco to Sundown. | [53 empty] | 2021-10-01 | 2021-10-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T7095525WP | FROM->TO | ANDREWS 6230.00 (FROM BORDEN) 230/115/13.2KV TRANSFORMER CKT 2 | CP | SPS | SPS | SPS-HOBB | SPS-HOBB | 1 | 528604 | ANDREWS 6230.00 | 528602 | ANDREWS 3115.00 | 528600 | ANDREWS_TR2113.200 | 2 | 25WP | 168 | 168 | 0 | 110.1 | 110.1199 | 110.3329 | [7 empty] | CATEGORYB | SINGLE | ANDREWS 6230.00 (FROM MIDLAND) 230/115/13.2KV TRANSFORMER CKT 1 | 1 | 528602 | ANDREWS 3115.00 | 528604 | ANDREWS 6230.00 | 528601 | ANDREWS_TR1113.200 | 1 |  |  |  | SPS | Andrews - Hobbs 345 kV Ckt 1 Voltage Conversion | Convert existing 30.5-mile 230 kV line from Andrews to Hobbs to 345 kV. Re-terminate line on 345 kV bus at Hobbs. Ratings will be based on current conductors - bundled 795 ACSR. | [12 empty] | 15000000 | 2014-04-22 | [39 empty] | 2022-06-01 | 2022-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T7075525WP | FROM->TO | ANDREWS 6230.00 (FROM MIDLAND) 230/115/13.2KV TRANSFORMER CKT 1 | CP | SPS | SPS | SPS-HOBB | SPS-HOBB | 1 | 528604 | ANDREWS 6230.00 | 528602 | ANDREWS 3115.00 | 528601 | ANDREWS_TR1113.200 | 1 | 25WP | 168 | 168 | 0 | 110 | 109.9584 | 110.171 | [7 empty] | CATEGORYB | SINGLE | ANDREWS 6230.00 (FROM BORDEN) 230/115/13.2KV TRANSFORMER CKT 2 | 1 | 528602 | ANDREWS 3115.00 | 528604 | ANDREWS 6230.00 | 528600 | ANDREWS_TR2113.200 | 2 |  |  |  | SPS | Andrews - Hobbs 345 kV Ckt 1 Voltage Conversion | Convert existing 30.5-mile 230 kV line from Andrews to Hobbs to 345 kV. Re-terminate line on 345 kV bus at Hobbs. Ratings will be based on current conductors - bundled 795 ACSR. | [12 empty] | 15000000 | 2014-04-22 | [39 empty] | 2022-06-01 | 2022-06-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T4555520SP | TO->FROM | ARKANSAS CITY - PARIS 69KV CKT 1 | S | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533548 | PARIS 2 69.000 | 533542 | ARKCITY2 69.000 | 0 |  | 1 | 20SP | 72 | 72 | 0 |  | 68.5087 | 100.9908 | [7 empty] | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 |  |  |  | WERE | ARKANSAS CITY - PARIS 69KV CKT 1 | Terminal Equipment | [12 empty] | 145773 | 2015-04-13 | [39 empty] | 2017-06-01 | 2017-06-01
GI-DP | GEN-2006-010 | [9 empty] | Ashdown REC (AECC delivery point) | U | AEPW | AEPW | SARK | SARKAECC | 0 | 507428 | OKAY 4 138.00 | 507402 | ASHDWNR4 138.00 | 507431 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | Ashdown REC (AECC delivery point) | Replace switches 6276 and 6277 with 3000 A, 138 kV switches and replace the conductor between them with 1590 ACSR. | [13 empty] | 2007-10-01 | [39 empty] | 2011-12-01 | 2011-12-01
GI | GEN-2006-010 | [9 empty] | ASHDOWN REC (MILLWOOD) - OKAY 138KV CKT 1 | U | AEPW | AEPW | SARK | SARKAECC | 0 | 507428 | OKAY 4 138.00 | 507402 | ASHDWNR4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | ASHDOWN REC (MILLWOOD) - OKAY 138KV CKT 1 | Rebuild fourteen (14.3) miles of 115 kV line to 138 kV and reconductor with 1590 ACSR. | [13 empty] | 2007-10-01 | [39 empty] | 2011-12-01 | 2011-12-01
GI | GEN-2006-010 | [9 empty] | ASHDOWN REC (MILLWOOD) - PATTERSON 138KV CKT 1 | U | AEPW | AEPW | SARKAECC | SARK | 0 | 507402 | ASHDWNR4 138.00 | 507431 | PATTERS4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | ASHDOWN REC (MILLWOOD) - PATTERSON 138KV CKT 1 | Reconductor line and convert line to 138 kV. Convert Patterson station to breaker-and-a half configuration. | [13 empty] | 2007-10-01 | [39 empty] | 2011-12-01 | 2011-12-01
2007-AG3 | AFS-9 | [9 empty] | BARBER - MEDICINE LODGE 115KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539673 | MED-LDG3 115.00 | 539760 | BARBER 3 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | BARBER - MEDICINE LODGE 115KV CKT 1 | Rebuild line | [53 empty] | 2009-12-01 | 2013-06-01
2007-AG3 | AFS-9 | [9 empty] | BARBER - SAWYER 115KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539760 | BARBER 3 | 539649 | SAWYER 3 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | BARBER - SAWYER 115KV CKT 1 | Rebuild line | [53 empty] | 2009-12-01 | 2013-06-01
2007-AG3 | AFS-9 | [9 empty] | BARBER (BARBER 4) 138/115/2.72KV TRANSFORMER CKT 1 | U | MKEC |  |  |  | 2 | 539674 | BARBER 4 | 539760 | BARBER 3 | 539917 | BARBER-T | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | BARBER (BARBER 4) 138/115/2.72KV TRANSFORMER CKT 1 | Upgrade transformer | [53 empty] | 2009-12-01 | 2013-06-01
2005-AG2 | AFS-3 | [9 empty] | BEELINE - EXPLORER GLENPOOL 138KV CKT 1 | U | OKGE | OKGE |  |  | 0 | 515473 | EXPLGLN4 138 | 515247 | BEELINE4 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OKGE | BEELINE - EXPLORER GLENPOOL 138KV CKT 1 | Reconductor .92miles of line with Drake ACCC/TW. | [53 empty] | 2009-06-01 | 2009-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T8575516SP | FROM->TO | BENTON (BENT TX-1) 345/138/13.8KV TRANSFORMER CKT 1 | EXP | WERE | WERE | SCENTRAL | SCENTRAL | 1 | 532791 | BENTON 7 345.00 | 532986 | BENTON 4 138.00 | 532821 | BENTN1 1 13.800 | 1 | 16SP | 382 | 382 | 500 | 105.9 | 105.8603 | 113.7039 | [7 empty] | CATEGORYB | SINGLE | BENTON (BENT TX-2) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532791 | BENTON 7 345.00 | 532986 | BENTON 4 138.00 | 532822 | BENTN2 1 13.800 | 1 |  |  |  | WERE | BENTON 138kV Terminal Equipment | Replace Terminal Equipment | [53 empty] | 2016-06-01 | 2016-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T11685520SP | FROM->TO | BENTON (BENT TX-1) 345/138/13.8KV TRANSFORMER CKT 1 | EXP | WERE | WERE | SCENTRAL | SCENTRAL | 1 | 532791 | BENTON 7 345.00 | 532986 | BENTON 4 138.00 | 532821 | BENTN1 1 13.800 | 1 | 20SP | 382 | 382 | 500 | 101 | 101.0175 | 103.8871 | [7 empty] | CATEGORYB | SINGLE | BENTON (BENT TX-2) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532791 | BENTON 7 345.00 | 532986 | BENTON 4 138.00 | 532822 | BENTN2 1 13.800 | 1 |  |  |  | WERE | BENTON 138kV Terminal Equipment | Replace Terminal Equipment | [53 empty] | 2016-06-01 | 2016-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T8555516SP | FROM->TO | BENTON (BENT TX-2) 345/138/13.8KV TRANSFORMER CKT 1 | EXP | WERE | WERE | SCENTRAL | SCENTRAL | 1 | 532791 | BENTON 7 345.00 | 532986 | BENTON 4 138.00 | 532822 | BENTN2 1 13.800 | 1 | 16SP | 382 | 382 | 500 | 103.4 | 103.3594 | 111.0189 | [7 empty] | CATEGORYB | SINGLE | BENTON (BENT TX-1) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532791 | BENTON 7 345.00 | 532986 | BENTON 4 138.00 | 532821 | BENTN1 1 13.800 | 1 |  |  |  | WERE | BENTON 138kV Terminal Equipment | Replace Terminal Equipment | [53 empty] | 2016-06-01 | 2016-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T11675520SP | FROM->TO | BENTON (BENT TX-2) 345/138/13.8KV TRANSFORMER CKT 1 | EXP | WERE | WERE | SCENTRAL | SCENTRAL | 1 | 532791 | BENTON 7 345.00 | 532986 | BENTON 4 138.00 | 532822 | BENTN2 1 13.800 | 1 | 20SP | 382 | 382 | 500 | 98.6 | 98.6041 | 101.4069 | [7 empty] | CATEGORYB | SINGLE | BENTON (BENT TX-1) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532791 | BENTON 7 345.00 | 532986 | BENTON 4 138.00 | 532821 | BENTN1 1 13.800 | 1 |  |  |  | WERE | BENTON 138kV Terminal Equipment | Replace Terminal Equipment | [53 empty] | 2016-06-01 | 2016-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T14375525SP | TO->FROM | BPU - CITY OF MCPHERSON PLANT - WEST MCPHERSON 115KV CKT 1 | REL | WERE | WERE | WEST | WEST | 0 | 533438 | WMCPHER3 115.00 | 533428 | MCPHER 3 115.00 | 0 |  | 1 | 25SP | 159 | 159 | 0 | 111.5 | 111.5137 | 112.3565 | [7 empty] | CATEGORYB | SINGLE | EAST MCPHERSON (EMCP TX-1) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532872 | EMCPHER6 230.00 | 533417 | EMCPHER3 115.00 | 532894 | EMCPHER1 13.800 | 1 |  |  |  | WERE | BPU - CITY OF MCPHERSON PLANT - WEST MCPHERSON 115KV CKT 1 | Replace Terminal Equipment | [53 empty] | 2021-06-01 | 2021-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T4755525SP | TO->FROM | BPU - CITY OF MCPHERSON PLANT - WEST MCPHERSON 115KV CKT 1 | REL | WERE | WERE | WEST | WEST | 0 | 533438 | WMCPHER3 115.00 | 533428 | MCPHER 3 115.00 | 0 |  | 1 | 25SP | 159 | 159 | 0 | 110.8 | 110.7879 | 111.6284 | [7 empty] | CATEGORYB | SINGLE | EAST MCPHERSON SWITCHING STATION - REFINRY3 115.00 115KV CKT 1 | 0 | 533417 | EMCPHER3 115.00 | 533427 | REFINRY3 115.00 | 0 |  | 1 |  |  |  | WERE | BPU - CITY OF MCPHERSON PLANT - WEST MCPHERSON 115KV CKT 1 | Replace Terminal Equipment | [53 empty] | 2021-06-01 | 2021-06-01
2005-AG2 | AFS-3 | [9 empty] | BROWN - EXPLORER TAP 138KV CKT 1 | U | OKGE | OKGE |  |  | 0 | 515157 | BROWN 4 138 | 515153 | COLEMNT4 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OKGE | BROWN - EXPLORER TAP 138KV CKT 1 | Upgrade CT at Brown. | [53 empty] | 2006-06-01 | 2006-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T1395516SP | FROM->TO | BUCKNER7 345.00 - SPEARVILLE 345KV CKT 1 | EXP | SUNC | SUNC | SEPC | SEPC | 0 | 531501 | BUCKNER7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 | 16SP | 611.9 | 611.9 | 0 | 103.3 | 103.3191 | 102.3546 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 |  |  |  | SUNC | BUCKNER - SPEARVILLE 345 KV CKT 1 Terminal Upgrades | Replace breaker, switches, CTs, and relays at the Buckner and Spearville 345 kV substations to increase the rating of the 345 kV line from Buckner to Spearville. | [53 empty] | 2016-06-01 | 2016-12-31
2005-AG2 | AFS-3 | [9 empty] | CACHE - SNYDER 138KV CKT 1 | U | AEPW | AEPW |  |  | 0 | 511500 | CACHE4 138 | 511435 | SNYDER-4 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | CACHE - SNYDER 138KV CKT 1 | Replace Snyder wavetrap | [53 empty] | 2008-05-21 | 2008-05-21
2009-AGP2 | AFS-6 | [9 empty] | CANTON - TALOGA 69KV CKT 1 | U | WFEC | WFEC | AEP-OP | AEP-OP | 0 | 521064 | TALOGA 2 69.000 | 520843 | CANTON-2 69.000 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WFEC | CANTON - TALOGA 69KV CKT 1 | UPGRADE CANTON TO TALOGA TO 336.4 | 106 | 132 |  |  | 9.7 | 24 | 24 |  | 0.04013 | 0.16101 | 0.00252 | [42 empty] | 2011-06-01 | 2013-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2425520SP | FROM->TO | CANYON WEST SUB - DAWN SUB 115KV CKT 1 | EXP | SPS | SPS | SPS-CLHF | SPS-CLHF | 0 | 524516 | CANYON_WEST3115.00 | 524590 | DAWN 3115.00 | 0 |  | 1 | 20SP | 96 | 96 | 0 | 95.6 | 95.5889 | 105.9806 | [7 empty] | CATEGORYB | SINGLE | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 |  |  |  | SPS | Canyon West - Dawn 115 kV Ckt 1 | Rebuild 13.7-mile 115 kV line from Canyon West to Dawn to achieve a new emergency rating of 273 MVA. | [53 empty] | 2017-06-01 | 2018-04-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T1185520WP | FROM->TO | CANYON WEST SUB - DAWN SUB 115KV CKT 1 | EXP | SPS | SPS | SPS-CLHF | SPS-CLHF | 0 | 524516 | CANYON_WEST3115.00 | 524590 | DAWN 3115.00 | 0 |  | 1 | 20WP | 106 | 106 | 0 |  | 89.0301 | 105.2691 | [7 empty] | CATEGORYB | SINGLE | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 |  |  |  | SPS | Canyon West - Dawn 115 kV Ckt 1 | Rebuild 13.7-mile 115 kV line from Canyon West to Dawn to achieve a new emergency rating of 273 MVA. | [53 empty] | 2017-06-01 | 2018-04-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2645525SP | FROM->TO | CANYON WEST SUB - DAWN SUB 115KV CKT 1 | EXP | SPS | SPS | SPS-CLHF | SPS-CLHF | 0 | 524516 | CANYON_WEST3115.00 | 524590 | DAWN 3115.00 | 0 |  | 1 | 25SP | 96 | 96 | 0 |  | 89.7229 | 103.6449 | [7 empty] | CATEGORYB | SINGLE | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 |  |  |  | SPS | Canyon West - Dawn 115 kV Ckt 1 | Rebuild 13.7-mile 115 kV line from Canyon West to Dawn to achieve a new emergency rating of 273 MVA. | [53 empty] | 2017-06-01 | 2018-04-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3315520SP | TO->FROM | CARLSBAD INTERCHANGE - PECOS INTERCHANGE 115KV CKT 1 | S | SPS | SPS | SPS-PECO | SPS-PECO | 0 | 528178 | PECOS 3115.00 | 528160 | CARLSBAD 3115.00 | 0 |  | 1 | 20SP | 141 | 141 | 0 | 96.7 | 96.7343 | 105.5416 | [7 empty] | CATEGORYB | SINGLE | HOBBS - KIOWA 7345.00 345KV CKT 1 | 0 | 527896 | HOBBS_INT 7345.00 | 527965 | KIOWA 7345.00 | 0 |  | 1 |  |  |  | SPS | CARLSBAD INTERCHANGE - PECOS INTERCHANGE 115KV CKT 1 Accelerate | Replace Terminal Equipment | [12 empty] | 324585 | 2015-04-16 | [39 empty] | 2017-06-01 | 2017-06-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3175525SP | TO->FROM | CARLSBAD INTERCHANGE - PECOS INTERCHANGE 115KV CKT 1 | S | SPS | SPS | SPS-PECO | SPS-PECO | 0 | 528178 | PECOS 3115.00 | 528160 | CARLSBAD 3115.00 | 0 |  | 1 | 25SP | 141 | 141 | 0 |  | -999 | 132.8086 | [7 empty] | CATEGORYB | SINGLE | HOBBS - KIOWA 7345.00 345KV CKT 1 | 0 | 527896 | HOBBS_INT 7345.00 | 527965 | KIOWA 7345.00 | 0 |  | 1 |  |  |  | SPS | CARLSBAD INTERCHANGE - PECOS INTERCHANGE 115KV CKT 1 Accelerate | Replace Terminal Equipment | [12 empty] | 324585 | 2015-04-16 | [39 empty] | 2017-06-01 | 2017-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2035525WP | TO->FROM | CARLSBAD INTERCHANGE - PECOS INTERCHANGE 115KV CKT 1 | S | SPS | SPS | SPS-PECO | SPS-PECO | 0 | 528178 | PECOS 3115.00 | 528160 | CARLSBAD 3115.00 | 0 |  | 1 | 25WP | 156 | 156 | 0 | 116.7 | 116.7434 | 122.1856 | [7 empty] | CATEGORYB | SINGLE | HOBBS - KIOWA 7345.00 345KV CKT 1 | 0 | 527896 | HOBBS_INT 7345.00 | 527965 | KIOWA 7345.00 | 0 |  | 1 |  |  |  | SPS | CARLSBAD INTERCHANGE - PECOS INTERCHANGE 115KV CKT 1 Accelerate | Replace Terminal Equipment | [12 empty] | 324585 | 2015-04-16 | [39 empty] | 2017-06-01 | 2017-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3605520SP | TO->FROM | CIMARRON RIVER TAP - KISMET 3 115.00 115KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539646 | KISMET 3 115.00 | 539652 | CMRIVTP3 115.00 | 0 |  | 1 | 20SP | 133.9 | 133.9 | 0 | 101.9 | 101.9369 | 104.1337 | [7 empty] | CATEGORYB | SINGLE | CTU SUBLETTE - HASKELL 115KV CKT 1 | 0 | 531374 | HASKELL3 115.00 | 531442 | SAT-TAP3 115.00 | 0 |  | 1 |  |  |  | SUNC | Walkemeyer - Walkemeyer Tap 115 kV Ckt 1 (SEPC) | Construct new 115kV line from Walkemeyer to the new Walkemekyer Tap substation. The total estimated length of the Walkemeyer to Walkemeyer Tap line is 1 mile. | [53 empty] | 2017-06-01 | 2018-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3635520SP | TO->FROM | CIMARRON RIVER TAP - KISMET 3 115.00 115KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539646 | KISMET 3 115.00 | 539652 | CMRIVTP3 115.00 | 0 |  | 1 | 20SP | 133.9 | 133.9 | 0 | 99 | 99.047 | 100.9812 | [7 empty] | CATEGORYB | SINGLE | HASKELL - SEWARD-3 115KV CKT 1 | 0 | 531374 | HASKELL3 115.00 | 531467 | SEWARD-3 115.00 | 0 |  | 1 |  |  |  | SUNC | Walkemeyer - Walkemeyer Tap 115 kV Ckt 1 (SEPC) | Construct new 115kV line from Walkemeyer to the new Walkemekyer Tap substation. The total estimated length of the Walkemeyer to Walkemeyer Tap line is 1 mile. | [53 empty] | 2017-06-01 | 2018-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3895525SP | TO->FROM | CIMARRON RIVER TAP - KISMET 3 115.00 115KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539646 | KISMET 3 115.00 | 539652 | CMRIVTP3 115.00 | 0 |  | 1 | 25SP | 133.9 | 133.9 | 0 | 109.7 | 109.6678 | 112.2509 | [7 empty] | CATEGORYB | SINGLE | CTU SUBLETTE - HASKELL 115KV CKT 1 | 0 | 531374 | HASKELL3 115.00 | 531442 | SAT-TAP3 115.00 | 0 |  | 1 |  |  |  | SUNC | Walkemeyer - Walkemeyer Tap 115 kV Ckt 1 (SEPC) | Construct new 115kV line from Walkemeyer to the new Walkemekyer Tap substation. The total estimated length of the Walkemeyer to Walkemeyer Tap line is 1 mile. | [53 empty] | 2017-06-01 | 2018-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3935525SP | TO->FROM | CIMARRON RIVER TAP - KISMET 3 115.00 115KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539646 | KISMET 3 115.00 | 539652 | CMRIVTP3 115.00 | 0 |  | 1 | 25SP | 133.9 | 133.9 | 0 | 106.2 | 106.243 | 108.1901 | [7 empty] | CATEGORYB | SINGLE | HASKELL - SEWARD-3 115KV CKT 1 | 0 | 531374 | HASKELL3 115.00 | 531467 | SEWARD-3 115.00 | 0 |  | 1 |  |  |  | SUNC | Walkemeyer - Walkemeyer Tap 115 kV Ckt 1 (SEPC) | Construct new 115kV line from Walkemeyer to the new Walkemekyer Tap substation. The total estimated length of the Walkemeyer to Walkemeyer Tap line is 1 mile. | [53 empty] | 2017-06-01 | 2018-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T21185525SP | TO->FROM | CIMARRON RIVER TAP - KISMET 3 115.00 115KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539646 | KISMET 3 115.00 | 539652 | CMRIVTP3 115.00 | 0 |  | 1 | 25SP | 133.9 | 133.9 | 0 | 104.1 | 104.0643 | 106.1427 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SEPC-07 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SUNC | Walkemeyer - Walkemeyer Tap 115 kV Ckt 1 (SEPC) | Construct new 115kV line from Walkemeyer to the new Walkemekyer Tap substation. The total estimated length of the Walkemeyer to Walkemeyer Tap line is 1 mile. | [53 empty] | 2017-06-01 | 2018-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T12805525SP | FROM->TO | CLAREMORE (CLRAUTO1) 161/69/13.8KV TRANSFORMER CKT 1 | REL | GRDA | GRDA | GRDA | GRDA-MUN | 2 | 512651 | CLARMR 5 161.00 | 512679 | CLARMR 2 69.000 | 512814 | CLARMR1 13.800 | 1 | 25SP | 140 | 168 | 0 | 101.7 | 101.6503 | 101.9171 | [7 empty] | CATEGORYB | SINGLE | CLAREMORE (CLRAUTO2) 161/69/13.8KV TRANSFORMER CKT 2 | 1 | 512651 | CLARMR 5 161.00 | 512679 | CLARMR 2 69.000 | 512815 | CLARMR2 13.800 | 2 |  |  |  | GRDA | CLAREMORE (CLRAUTO1) 161/69/13.8KV TRANSFORMER CKT 1 | Upgrade the 161/69/13.8KV TRANSFORMER. | [53 empty] | 2021-06-01 | 2021-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T12785525SP | FROM->TO | CLAREMORE (CLRAUTO2) 161/69/13.8KV TRANSFORMER CKT 2 | REL | GRDA | GRDA | GRDA | GRDA-MUN | 2 | 512651 | CLARMR 5 161.00 | 512679 | CLARMR 2 69.000 | 512815 | CLARMR2 13.800 | 2 | 25SP | 140 | 168 | 0 | 101.7 | 101.6503 | 101.9171 | [7 empty] | CATEGORYB | SINGLE | CLAREMORE (CLRAUTO1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 512651 | CLARMR 5 161.00 | 512679 | CLARMR 2 69.000 | 512814 | CLARMR1 13.800 | 1 |  |  |  | GRDA | CLAREMORE (CLRAUTO1) 161/69/13.8KV TRANSFORMER CKT 2 | Upgrade the 161/69/13.8KV TRANSFORMER. | [53 empty] | 2021-06-01 | 2021-06-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T4465520SP | FROM->TO | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | EXP | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533036 | CLEARWT4 138.00 | 533045 | GILL W 4 138.00 | 0 |  | 1 | 20SP | 143 | 143 | 0 |  | 84.4042 | 120.7948 | [7 empty] | CATEGORYB | SINGLE | GILL ENERGY CENTER SOUTH - VIOLA 4 138.00 138KV CKT 1 | 0 | 533046 | GILL S 4 138.00 | 533075 | VIOLA 4 138.00 | 0 |  | 1 |  |  |  | WERE | Multi - Viola 345/138kV Transformer and 138 kV Lines to Clearwater and Gill | Install 345/138 kV transformer at future Viola 345 kV substation. Build 138kV line from Viola to Clearwater substation. Build 138 kV line from Viola to Gill substation | [53 empty] | 2016-06-01 | 2019-06-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T4455520SP | FROM->TO | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | EXP | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533036 | CLEARWT4 138.00 | 533045 | GILL W 4 138.00 | 0 |  | 1 | 20SP | 143 | 143 | 0 |  | 74.4404 | 101.1166 | [7 empty] | CATEGORYB | SINGLE | 45TH ST4 138.00 - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533074 | 45TH ST4 138.00 | 0 |  | 1 |  |  |  | WERE | Multi - Viola 345/138kV Transformer and 138 kV Lines to Clearwater and Gill | Install 345/138 kV transformer at future Viola 345 kV substation. Build 138kV line from Viola to Clearwater substation. Build 138 kV line from Viola to Gill substation | [53 empty] | 2016-06-01 | 2019-06-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T4435520SP | FROM->TO | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | EXP | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533036 | CLEARWT4 138.00 | 533045 | GILL W 4 138.00 | 0 |  | 1 | 20SP | 143 | 143 | 0 |  | 73.9364 | 100.6056 | [7 empty] | CATEGORYB | SINGLE | 45TH ST4 138.00 - COWSKIN 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533074 | 45TH ST4 138.00 | 0 |  | 1 |  |  |  | WERE | Multi - Viola 345/138kV Transformer and 138 kV Lines to Clearwater and Gill | Install 345/138 kV transformer at future Viola 345 kV substation. Build 138kV line from Viola to Clearwater substation. Build 138 kV line from Viola to Gill substation | [53 empty] | 2016-06-01 | 2019-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T1635520WP | FROM->TO | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | EXP | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533036 | CLEARWT4 138.00 | 533045 | GILL W 4 138.00 | 0 |  | 1 | 20WP | 143 | 143 | 0 | 105.7 | 105.7194 | 121.2492 | [7 empty] | CATEGORYB | SINGLE | GILL ENERGY CENTER SOUTH - VIOLA 4 138.00 138KV CKT 1 | 0 | 533046 | GILL S 4 138.00 | 533075 | VIOLA 4 138.00 | 0 |  | 1 |  |  |  | WERE | Multi - Viola 345/138kV Transformer and 138 kV Lines to Clearwater and Gill | Install 345/138 kV transformer at future Viola 345 kV substation. Build 138kV line from Viola to Clearwater substation. Build 138 kV line from Viola to Gill substation | [53 empty] | 2016-06-01 | 2019-06-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T4675525SP | FROM->TO | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | EXP | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533036 | CLEARWT4 138.00 | 533045 | GILL W 4 138.00 | 0 |  | 1 | 25SP | 143 | 143 | 0 |  | 86.1775 | 104.3729 | [7 empty] | CATEGORYB | SINGLE | GILL ENERGY CENTER SOUTH - VIOLA 4 138.00 138KV CKT 1 | 0 | 533046 | GILL S 4 138.00 | 533075 | VIOLA 4 138.00 | 0 |  | 1 |  |  |  | WERE | Multi - Viola 345/138kV Transformer and 138 kV Lines to Clearwater and Gill | Install 345/138 kV transformer at future Viola 345 kV substation. Build 138kV line from Viola to Clearwater substation. Build 138 kV line from Viola to Gill substation | [53 empty] | 2016-06-01 | 2019-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2385525WP | FROM->TO | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | EXP | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533036 | CLEARWT4 138.00 | 533045 | GILL W 4 138.00 | 0 |  | 1 | 25WP | 143 | 143 | 0 | 112.2 | 112.1936 | 127.985 | [7 empty] | CATEGORYB | SINGLE | GILL ENERGY CENTER SOUTH - VIOLA 4 138.00 138KV CKT 1 | 0 | 533046 | GILL S 4 138.00 | 533075 | VIOLA 4 138.00 | 0 |  | 1 |  |  |  | WERE | Multi - Viola 345/138kV Transformer and 138 kV Lines to Clearwater and Gill | Install 345/138 kV transformer at future Viola 345 kV substation. Build 138kV line from Viola to Clearwater substation. Build 138 kV line from Viola to Gill substation | [53 empty] | 2016-06-01 | 2019-06-01
2007-AG3 | AFS-9 | [9 empty] | CLIFTON - GREENLEAF 115KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539656 | CLIFTON3 115.00 | 539665 | GRNLEAF3 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | CLIFTON - GREENLEAF 115KV CKT 1 | Rebuild 14.4 miles | [53 empty] | 2011-06-01 | 2013-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T885516SP | FROM->TO | CPP TRANSF #2 - WILGRO 69KV CKT 1 | REL | GRDA | GRDA | GR-SIN | GR-LIN | 0 | 512661 | CPPXF#22 69.000 | 512699 | PRYORCHEM2 69.000 | 0 |  | 1 | 16SP | 72 | 72 | 0 | 117.1 | 117.0647 | 117.0535 | [7 empty] | CATEGORYB | SINGLE | HUNT - MAIDTP2 69.000 69KV CKT 1 | 0 | 512625 | MAIDTP2 69.000 | 512671 | HUNT 2 69.000 | 0 |  | 1 |  |  |  | GRDA | CPP TRANSF #2 - WILGRO 69KV CKT 1 | Upgrade break and relay at CPPX 69 kV station. | [53 empty] | 2016-06-01 | 2016-07-25
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T895516SP | FROM->TO | CPP TRANSF #2 - WILGRO 69KV CKT 1 | REL | GRDA | GRDA | GR-SIN | GR-LIN | 0 | 512661 | CPPXF#22 69.000 | 512699 | PRYORCHEM2 69.000 | 0 |  | 1 | 16SP | 72 | 72 | 0 | 117.1 | 117.0541 | 117.043 | [7 empty] | CATEGORYB | SINGLE | GRDA1 - MAIDTP2 69.000 69KV CKT 1 | 0 | 512625 | MAIDTP2 69.000 | 512727 | GRDA1 2 69.000 | 0 |  | 1 |  |  |  | GRDA | CPP TRANSF #2 - WILGRO 69KV CKT 1 | Upgrade break and relay at CPPX 69 kV station. | [53 empty] | 2016-06-01 | 2016-07-25
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T7705516SP | FROM->TO | CPP TRANSF #2 - WILGRO 69KV CKT 1 | REL | GRDA | GRDA | GR-SIN | GR-LIN | 0 | 512661 | CPPXF#22 69.000 | 512699 | PRYORCHEM2 69.000 | 0 |  | 1 | 16SP | 72 | 72 | 0 | 117.1 | 117.0501 | 117.0391 | [7 empty] | CATEGORYB | SINGLE | GRDA1 (GRDAUTO1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 512656 | GRDA1 5 161.00 | 512727 | GRDA1 2 69.000 | 512816 | GRDA 13.800 | 1 |  |  |  | GRDA | CPP TRANSF #2 - WILGRO 69KV CKT 1 | Upgrade break and relay at CPPX 69 kV station. | [53 empty] | 2016-06-01 | 2016-07-25
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T835020SP | FROM->TO | CPP TRANSF #2 - WILGRO 69KV CKT 1 | REL | GRDA | GRDA | GR-SIN | GR-LIN | 0 | 512661 | CPPXF#22 69.000 | 512699 | PRYORCHEM2 69.000 | 0 |  | 1 | 20SP | 72 | 72 | 0 | 122.8 | 122.7914 | 117.1796 | [7 empty] | CATEGORYB | SINGLE | HUNT - MAIDTP2 69.000 69KV CKT 1 | 0 | 512625 | MAIDTP2 69.000 | 512671 | HUNT 2 69.000 | 0 |  | 1 |  |  |  | GRDA | CPP TRANSF #2 - WILGRO 69KV CKT 1 | Upgrade break and relay at CPPX 69 kV station. | [53 empty] | 2016-06-01 | 2016-07-25
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T845020SP | FROM->TO | CPP TRANSF #2 - WILGRO 69KV CKT 1 | REL | GRDA | GRDA | GR-SIN | GR-LIN | 0 | 512661 | CPPXF#22 69.000 | 512699 | PRYORCHEM2 69.000 | 0 |  | 1 | 20SP | 72 | 72 | 0 | 122.8 | 122.7824 | 117.1688 | [7 empty] | CATEGORYB | SINGLE | GRDA1 - MAIDTP2 69.000 69KV CKT 1 | 0 | 512625 | MAIDTP2 69.000 | 512727 | GRDA1 2 69.000 | 0 |  | 1 |  |  |  | GRDA | CPP TRANSF #2 - WILGRO 69KV CKT 1 | Upgrade break and relay at CPPX 69 kV station. | [53 empty] | 2016-06-01 | 2016-07-25
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T6275020SP | FROM->TO | CPP TRANSF #2 - WILGRO 69KV CKT 1 | REL | GRDA | GRDA | GR-SIN | GR-LIN | 0 | 512661 | CPPXF#22 69.000 | 512699 | PRYORCHEM2 69.000 | 0 |  | 1 | 20SP | 72 | 72 | 0 | 122.8 | 122.7791 | 117.1647 | [7 empty] | CATEGORYB | SINGLE | GRDA1 (GRDAUTO1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 512656 | GRDA1 5 161.00 | 512727 | GRDA1 2 69.000 | 512816 | GRDA 13.800 | 1 |  |  |  | GRDA | CPP TRANSF #2 - WILGRO 69KV CKT 1 | Upgrade break and relay at CPPX 69 kV station. | [53 empty] | 2016-06-01 | 2016-07-25
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T1725525SP | FROM->TO | CPP TRANSF #2 - WILGRO 69KV CKT 1 | REL | GRDA | GRDA | GR-SIN | GR-LIN | 0 | 512661 | CPPXF#22 69.000 | 512699 | PRYORCHEM2 69.000 | 0 |  | 1 | 25SP | 72 | 72 | 0 | 110.2 | 110.186 | 110.8174 | [7 empty] | CATEGORYB | SINGLE | HUNT - MAIDTP2 69.000 69KV CKT 1 | 0 | 512625 | MAIDTP2 69.000 | 512671 | HUNT 2 69.000 | 0 |  | 1 |  |  |  | GRDA | CPP TRANSF #2 - WILGRO 69KV CKT 1 | Upgrade break and relay at CPPX 69 kV station. | [53 empty] | 2016-06-01 | 2016-07-25
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T1735525SP | FROM->TO | CPP TRANSF #2 - WILGRO 69KV CKT 1 | REL | GRDA | GRDA | GR-SIN | GR-LIN | 0 | 512661 | CPPXF#22 69.000 | 512699 | PRYORCHEM2 69.000 | 0 |  | 1 | 25SP | 72 | 72 | 0 | 110.2 | 110.1711 | 110.8021 | [7 empty] | CATEGORYB | SINGLE | GRDA1 - MAIDTP2 69.000 69KV CKT 1 | 0 | 512625 | MAIDTP2 69.000 | 512727 | GRDA1 2 69.000 | 0 |  | 1 |  |  |  | GRDA | CPP TRANSF #2 - WILGRO 69KV CKT 1 | Upgrade break and relay at CPPX 69 kV station. | [53 empty] | 2016-06-01 | 2016-07-25
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T12825525SP | FROM->TO | CPP TRANSF #2 - WILGRO 69KV CKT 1 | REL | GRDA | GRDA | GR-SIN | GR-LIN | 0 | 512661 | CPPXF#22 69.000 | 512699 | PRYORCHEM2 69.000 | 0 |  | 1 | 25SP | 72 | 72 | 0 | 110.2 | 110.1655 | 110.7963 | [7 empty] | CATEGORYB | SINGLE | GRDA1 (GRDAUTO1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 512656 | GRDA1 5 161.00 | 512727 | GRDA1 2 69.000 | 512816 | GRDA 13.800 | 1 |  |  |  | GRDA | CPP TRANSF #2 - WILGRO 69KV CKT 1 | Upgrade break and relay at CPPX 69 kV station. | [53 empty] | 2016-06-01 | 2016-07-25
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T21555525SP | TO->FROM | CRAWFORD - NEOSHO 69KV CKT 1 | S | WERE | WERE | SEAST | SEAST | 0 | 533768 | NEOSHO 2 69.000 | 533758 | CRAWFOR2 69.000 | 0 |  | 1 | 25SP | 41 | 48 | 0 | 97.1 | 97.1309 | 103.0781 | [7 empty] | CATEGORYB | NONSINGLE | WR-B3-24 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | CRAWFORD - NEOSHO 69KV CKT 1 | Rebuild 6.7 Miles of line | [12 empty] | 4916868 | 2015-04-14 | [39 empty] | 2021-06-01 | 2021-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3615520SP | FROM->TO | CUDAHY - KISMET 3 115.00 115KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539659 | CUDAHY 3 115.00 | 539646 | KISMET 3 115.00 | 0 |  | 1 | 20SP | 119.5 | 135.8 | 0 | 102.6 | 102.5579 | 104.7511 | [7 empty] | CATEGORYB | SINGLE | CTU SUBLETTE - HASKELL 115KV CKT 1 | 0 | 531374 | HASKELL3 115.00 | 531442 | SAT-TAP3 115.00 | 0 |  | 1 |  |  |  | SUNC | Walkemeyer - Walkemeyer Tap 115 kV Ckt 1 (SEPC) | Construct new 115kV line from Walkemeyer to the new Walkemekyer Tap substation. The total estimated length of the Walkemeyer to Walkemeyer Tap line is 1 mile. | [53 empty] | 2017-06-01 | 2018-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3645520SP | FROM->TO | CUDAHY - KISMET 3 115.00 115KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539659 | CUDAHY 3 115.00 | 539646 | KISMET 3 115.00 | 0 |  | 1 | 20SP | 119.5 | 135.8 | 0 | 99.7 | 99.6706 | 101.6066 | [7 empty] | CATEGORYB | SINGLE | HASKELL - SEWARD-3 115KV CKT 1 | 0 | 531374 | HASKELL3 115.00 | 531467 | SEWARD-3 115.00 | 0 |  | 1 |  |  |  | SUNC | Walkemeyer - Walkemeyer Tap 115 kV Ckt 1 (SEPC) | Construct new 115kV line from Walkemeyer to the new Walkemekyer Tap substation. The total estimated length of the Walkemeyer to Walkemeyer Tap line is 1 mile. | [53 empty] | 2017-06-01 | 2018-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3905525SP | FROM->TO | CUDAHY - KISMET 3 115.00 115KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539659 | CUDAHY 3 115.00 | 539646 | KISMET 3 115.00 | 0 |  | 1 | 25SP | 119.5 | 135.8 | 0 | 110.4 | 110.3897 | 112.997 | [7 empty] | CATEGORYB | SINGLE | CTU SUBLETTE - HASKELL 115KV CKT 1 | 0 | 531374 | HASKELL3 115.00 | 531442 | SAT-TAP3 115.00 | 0 |  | 1 |  |  |  | SUNC | Walkemeyer - Walkemeyer Tap 115 kV Ckt 1 (SEPC) | Construct new 115kV line from Walkemeyer to the new Walkemekyer Tap substation. The total estimated length of the Walkemeyer to Walkemeyer Tap line is 1 mile. | [53 empty] | 2017-06-01 | 2018-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3945525SP | FROM->TO | CUDAHY - KISMET 3 115.00 115KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539659 | CUDAHY 3 115.00 | 539646 | KISMET 3 115.00 | 0 |  | 1 | 25SP | 119.5 | 135.8 | 0 | 107 | 106.9745 | 108.9192 | [7 empty] | CATEGORYB | SINGLE | HASKELL - SEWARD-3 115KV CKT 1 | 0 | 531374 | HASKELL3 115.00 | 531467 | SEWARD-3 115.00 | 0 |  | 1 |  |  |  | SUNC | Walkemeyer - Walkemeyer Tap 115 kV Ckt 1 (SEPC) | Construct new 115kV line from Walkemeyer to the new Walkemekyer Tap substation. The total estimated length of the Walkemeyer to Walkemeyer Tap line is 1 mile. | [53 empty] | 2017-06-01 | 2018-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T21195525SP | FROM->TO | CUDAHY - KISMET 3 115.00 115KV CKT 1 | EXP | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539659 | CUDAHY 3 115.00 | 539646 | KISMET 3 115.00 | 0 |  | 1 | 25SP | 119.5 | 135.8 | 0 | 104.8 | 104.8319 | 106.9056 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SEPC-07 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SUNC | Walkemeyer - Walkemeyer Tap 115 kV Ckt 1 (SEPC) | Construct new 115kV line from Walkemeyer to the new Walkemekyer Tap substation. The total estimated length of the Walkemeyer to Walkemeyer Tap line is 1 mile. | [53 empty] | 2017-06-01 | 2018-06-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3305520SP | TO->FROM | CUNNINGHAM STATION - HOBBS INTERCHANGE 115KV CKT 1 | S | SPS | SPS | SPS-HOBB | SPS-PECO | 0 | 527891 | HOBBS_INT 3115.00 | 527864 | CUNNINHAM 3115.00 | 0 |  | 1 | 20SP | 160 | 160 | 0 |  | 83.7858 | 101.4973 | [7 empty] | CATEGORYB | SINGLE | HOBBS INTERCHANGE - MADDOX STATION 115KV CKT 1 | 0 | 527891 | HOBBS_INT 3115.00 | 528355 | MADDOX 3115.00 | 0 |  | 1 |  |  |  | SPS | CUNNINGHAM STATION - HOBBS INTERCHANGE 115KV CKT 1 | Terminal Equipment | [12 empty] | 324585 | 2015-04-13 | [39 empty] | 2017-06-01 | 2017-06-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3115525SP | FROM->TO | CUNNINGHAM STATION - MADDOX STATION 115KV CKT 1 | S | SPS | SPS | SPS-PECO | SPS-HOBB | 0 | 527864 | CUNNINHAM 3115.00 | 528355 | MADDOX 3115.00 | 0 |  | 1 | 25SP | 160 | 160 | 0 |  | 79.8952 | 104.4316 | [7 empty] | CATEGORYB | SINGLE | HOBBS INTERCHANGE - MADDOX STATION 115KV CKT 1 | 0 | 527891 | HOBBS_INT 3115.00 | 528355 | MADDOX 3115.00 | 0 |  | 1 |  |  |  | SPS | CUNNINGHAM STATION - MADDOX STATION 115KV CKT 1 | Rebuild 3.1-mile 115 kV line to at least 167 MVA Rate B | [12 empty] | 2117364.0667 | [40 empty] | 2021-06-01 | 2021-06-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3145525SP | FROM->TO | CUNNINGHAM STATION - POTASH JUNCTION INTERCHANGE 230KV CKT 1 | REL | SPS | SPS | SPS-PECO | SPS-PECO | 0 | 527865 | CUNNINHAM 6230.00 | 527963 | POTASH_JCT 6230.00 | 0 |  | 1 | 25SP | 319 | 351 | 0 |  | -999 | 113.3609 | [7 empty] | CATEGORYB | SINGLE | HOBBS - KIOWA 7345.00 345KV CKT 1 | 0 | 527896 | HOBBS_INT 7345.00 | 527965 | KIOWA 7345.00 | 0 |  | 1 |  |  |  | SPS | CUNNINGHAM STATION - POTASH JUNCTION INTERCHANGE 230KV CKT 1 | Replace WaveTrap at Chaves | 478 | 617 | [10 empty] | 63251 | [40 empty] | 2021-06-01 | 2021-06-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2435520SP | FROM->TO | DAWN SUB - Panda Energy Substation Hereford 115KV CKT 1 | EXP | SPS | SPS | SPS-CLHF | SPS-CLHF | 0 | 524590 | DAWN 3115.00 | 524597 | PANDAHFD 3115.00 | 0 |  | 1 | 20SP | 96 | 96 | 0 |  | 91.0248 | 101.3094 | [7 empty] | CATEGORYB | SINGLE | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 |  |  |  | SPS | Dawn - Panda 115 kV Ckt 1 | Rebuild 8.4-mile 115 kV line from Dawn to Panda achieve a new emergency rating of 273 MVA. | [53 empty] | 2017-06-01 | 2018-04-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T1195520WP | FROM->TO | DAWN SUB - Panda Energy Substation Hereford 115KV CKT 1 | EXP | SPS | SPS | SPS-CLHF | SPS-CLHF | 0 | 524590 | DAWN 3115.00 | 524597 | PANDAHFD 3115.00 | 0 |  | 1 | 20WP | 106 | 106 | 0 |  | 85.6846 | 101.8775 | [7 empty] | CATEGORYB | SINGLE | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 |  |  |  | SPS | Dawn - Panda 115 kV Ckt 1 | Rebuild 8.4-mile 115 kV line from Dawn to Panda achieve a new emergency rating of 273 MVA. | [53 empty] | 2017-06-01 | 2018-04-01
2007-AG3 | AFS-9 | [9 empty] | DEARING 138KV | U | WERE |  | SEAST |  |  | 533002 | DEARING4 138.00 | [20 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WERE | DEARING 138KV | Dearing 138 kV 20 MVAR Capacitor Addition | [53 empty] | 2012-06-01 | 2012-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T17745520SP | FROM->TO | EAST PLANT INTERCHANGE - MANHATTAN SUB 115KV CKT 1 | CP | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524162 | EAST_PLANT 3115.00 | 524224 | MANHATTAN 3115.00 | 0 |  | 1 | 20SP | 160 | 160 | 0 | 101.9 | 101.9263 | 103.3036 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-K19 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | EAST PLANT INTERCHANGE - MANHATTAN SUB 115KV CKT 1 | Rebuild 2.236 miles to at least 192 MVA Rate B | [12 empty] | 1118328 | 2014-12-11 | [39 empty] | 2017-06-01 | 2018-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T21355525SP | FROM->TO | EAST PLANT INTERCHANGE - MANHATTAN SUB 115KV CKT 1 | CP | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524162 | EAST_PLANT 3115.00 | 524224 | MANHATTAN 3115.00 | 0 |  | 1 | 25SP | 160 | 160 | 0 | 104.9 | 104.8772 | 112.714 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-K19 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | EAST PLANT INTERCHANGE - MANHATTAN SUB 115KV CKT 1 | Rebuild 2.236 miles to at least 192 MVA Rate B | [12 empty] | 1118328 | 2014-12-11 | [39 empty] | 2017-06-01 | 2018-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2465525SP | FROM->TO | EAST PLANT INTERCHANGE - MANHATTAN SUB 115KV CKT 1 | CP | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524162 | EAST_PLANT 3115.00 | 524224 | MANHATTAN 3115.00 | 0 |  | 1 | 25SP | 160 | 160 | 0 | 95.2 | 95.2253 | 103.2725 | [7 empty] | CATEGORYB | SINGLE | Harrington Station Mid Bus - RANDALL COUNTY INTERCHANGE 230KV CKT 1 | 0 | 523978 | HARRNG_MID 6230.00 | 524365 | RANDALL 6230.00 | 0 |  | 1 |  |  |  | SPS | EAST PLANT INTERCHANGE - MANHATTAN SUB 115KV CKT 1 | Rebuild 2.236 miles to at least 192 MVA Rate B | [12 empty] | 1118328 | 2014-12-11 | [39 empty] | 2017-06-01 | 2018-06-01
NA | SPONSORED | [9 empty] | EASTOWN7 345.00 (EASTOWN 345) 345/161/13.8KV TRANSFORMER CKT 1 | U | GMO | GMO |  |  | 1 | 541400 | EASTOWN7 345.00 | 541401 | EASTOWN5 161.00 | 541402 | EASTOWN1 13.800 | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | KACP | EASTOWN7 345.00 (EASTOWN 345) 345/161/13.8KV TRANSFORMER CKT 1 | Replace 715 MVA transformer. | [53 empty] | 2014-05-01 | 2014-05-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3015516WP | FROM->TO | EDDY_NORTH 6230.00 (WAUK WT01134) 230/115/13.2KV TRANSFORMER CKT 2 | CP | SPS | SPS | SPS-PECO | SPS-PECO | 2 | 527799 | EDDY_NORTH 6230.00 | 527793 | EDDY_STH 3115.00 | 527795 | EDDY_TR3 113.200 | 2 | 16WP | 250 | 250 | 0 | 108.8 | 108.8129 | 118.1795 | [7 empty] | CATEGORYB | SINGLE | EDDY COUNTY INTERCHANGE - EDDY_NORTH 6230.00 230KV CKT @1 | 0 | 527799 | EDDY_NORTH 6230.00 | 527800 | EDDY_SOUTH 6230.00 | 0 |  | @1 |  |  |  | SPS | EDCO 230 kV Double Bus Double Breaker | Build the 230kV main and transfer bus to a double breaker double bus. | [12 empty] | 9485379.1663 | 2015-04-16 | [39 empty] | 2016-10-01 | 2018-12-15
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T5925525WP | FROM->TO | EDDY_NORTH 6230.00 (WAUK WT01134) 230/115/13.2KV TRANSFORMER CKT 2 | CP | SPS | SPS | SPS-PECO | SPS-PECO | 1 | 527799 | EDDY_NORTH 6230.00 | 527793 | EDDY_STH 3115.00 | 527795 | EDDY_TR3 113.200 | 2 | 25WP | 250 | 250 | 0 | 121.7 | 121.7462 | 129.1461 | [7 empty] | CATEGORYB | SINGLE | EDDY COUNTY INTERCHANGE - EDDY_NORTH 6230.00 230KV CKT @1 | 0 | 527799 | EDDY_NORTH 6230.00 | 527800 | EDDY_SOUTH 6230.00 | 0 |  | @1 |  |  |  | SPS | EDCO 230 kV Double Bus Double Breaker | Build the 230kV main and transfer bus to a double breaker double bus. | [12 empty] | 9485379.1663 | 2015-04-16 | [39 empty] | 2016-10-01 | 2018-12-15
2005-AG2 | AFS-3 | [9 empty] | EXPLORER GLENPOOL - RIVERSIDE STATION 138KV CKT 1 | U | AEPW | OKGE |  |  | 0 | 509783 | R.S.S.-4 138 | 515473 | EXPLGLN4 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | EXPLORER GLENPOOL - RIVERSIDE STATION 138KV CKT 1 (AEP) | Reconductor 1.9 miles with ACCC. Replace wave trap jumpers at Riverside. | [53 empty] | 2009-06-01 | 2009-06-01
2005-AG2 | AFS-3 | [9 empty] | EXPLORER GLENPOOL - RIVERSIDE STATION 138KV CKT 1 OKGE | U | AEPW | OKGE |  |  | 0 | 509783 | R.S.S.-4 138 | 515473 | EXPLGLN4 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OKGE | EXPLORER GLENPOOL - RIVERSIDE STATION 138KV CKT 1 (OGE) | Reconductor 1.82 miles line with Drake ACCC/TW. | [53 empty] | 2009-06-01 | 2009-06-01
GI | ASGI-2010-006 | [9 empty] | Fairfax - Pawnee 138kV Ckt 1 | U |  |  |  |  | 0 | 300139 |  | 512749 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | GRDA | Fairfax - Pawnee 138kV Ckt 1 | Construct Approx. 15 miles of 138kV transmission line from Fairfax to a new substation on the Cleveland-Stillwater 138kV line near Pawnee. & Fairfax Substation: Install 138kV line terminal and any additional modifications that are necessary to connect to | [13 empty] | 2011-06-15 | [39 empty] | 2014-06-30 | 2014-06-01 | 2014-06-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T6205520SP | FROM->TO | FAIRFAX 138/69KV TRANSFORMER CKT 1 | CP | AECI | AECI | KAMO-OK | KAMO-OK | 0 | 300139 | 4FAIRFAX 138.00 | 300929 | 2FAIRFAX 69.000 | 0 |  | 1 | 20SP | 56 | 56 | 0 |  | 92.0685 | 101.8838 | [7 empty] | CATEGORYB | SINGLE | 4CLEVLNDXFMR138.00 - CLEAVELAND 138KV CKT Z1 | 0 | 300138 | 4CLEVLND 138.00 | 301429 | 4CLEVLNDXFMR138.00 | 0 |  | Z1 |  |  |  | AECI | FAIRFAX 138/69KV TRANSFORMER CKT 1 | Replace with 84 MVA unit | [5 empty] | 24 | 24 | [5 empty] | 1800000 | [40 empty] | 2017-06-01 | 2017-06-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T6465520SP | FROM->TO | FAIRFAX 138/69KV TRANSFORMER CKT 1 | CP | AECI | AECI | KAMO-OK | KAMO-OK | 0 | 300139 | 4FAIRFAX 138.00 | 300929 | 2FAIRFAX 69.000 | 0 |  | 1 | 20SP | 56 | 56 | 0 |  | 92.0655 | 101.8761 | [7 empty] | CATEGORYB | SINGLE | 2CLEVLNDXFMR69.000 - CLEAVELAND 69KV CKT Z1 | 0 | 300927 | 2CLEVLND 69.000 | 301430 | 2CLEVLNDXFMR69.000 | 0 |  | Z1 |  |  |  | AECI | FAIRFAX 138/69KV TRANSFORMER CKT 1 | Replace with 84 MVA unit | [5 empty] | 24 | 24 | [5 empty] | 1800000 | [40 empty] | 2017-06-01 | 2017-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T7295525SP | FROM->TO | FAIRFAX 138/69KV TRANSFORMER CKT 1 | CP | AECI | AECI | KAMO-OK | KAMO-OK | 0 | 300139 | 4FAIRFAX 138.00 | 300929 | 2FAIRFAX 69.000 | 0 |  | 1 | 25SP | 56 | 56 | 0 | 95.9 | 95.8567 | 106.0723 | [7 empty] | CATEGORYB | SINGLE | 4CLEVLNDXFMR138.00 - CLEAVELAND 138KV CKT Z1 | 0 | 300138 | 4CLEVLND 138.00 | 301429 | 4CLEVLNDXFMR138.00 | 0 |  | Z1 |  |  |  | AECI | FAIRFAX 138/69KV TRANSFORMER CKT 1 | Replace with 84 MVA unit | [5 empty] | 24 | 24 | [5 empty] | 1800000 | [40 empty] | 2017-06-01 | 2017-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T7675525SP | FROM->TO | FAIRFAX 138/69KV TRANSFORMER CKT 1 | CP | AECI | AECI | KAMO-OK | KAMO-OK | 0 | 300139 | 4FAIRFAX 138.00 | 300929 | 2FAIRFAX 69.000 | 0 |  | 1 | 25SP | 56 | 56 | 0 | 95.9 | 95.8648 | 106.0693 | [7 empty] | CATEGORYB | SINGLE | 2CLEVLNDXFMR69.000 - CLEAVELAND 69KV CKT Z1 | 0 | 300927 | 2CLEVLND 69.000 | 301430 | 2CLEVLNDXFMR69.000 | 0 |  | Z1 |  |  |  | AECI | FAIRFAX 138/69KV TRANSFORMER CKT 1 | Replace with 84 MVA unit | [5 empty] | 24 | 24 | [5 empty] | 1800000 | [40 empty] | 2017-06-01 | 2017-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T7695525SP | FROM->TO | FAIRFAX 138/69KV TRANSFORMER CKT 1 | CP | AECI | AECI | KAMO-OK | KAMO-OK | 0 | 300139 | 4FAIRFAX 138.00 | 300929 | 2FAIRFAX 69.000 | 0 |  | 1 | 25SP | 56 | 56 | 0 | 95.9 | 95.9238 | 101.9784 | [7 empty] | CATEGORYB | SINGLE | HALLETT TAP - PAWNEE 69KV CKT 1 | 0 | 300934 | 2HALETTP 69.000 | 300939 | 2PAWNEE 69.000 | 0 |  | 1 |  |  |  | AECI | FAIRFAX 138/69KV TRANSFORMER CKT 1 | Replace with 84 MVA unit | [5 empty] | 24 | 24 | [5 empty] | 1800000 | [40 empty] | 2017-06-01 | 2017-06-01
2007-AG3 | AFS-9 | [9 empty] | FLATRDG3 138.00 - MEDICINE LODGE 138KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539674 | MED-LDG4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | FLATRDG3 - MEDICINE LODGE 138KV CKT 1 | Rebuild 8.05 mile line | [53 empty] | 2009-12-01 | 2013-06-01
2007-AG3 | AFS-9 | [9 empty] | FLATRDG3 138.00 - HARPER 138KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | FLATRDG3 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 |  |  | 24.15 | 24 | 24 | [46 empty] | 2009-12-01 | 2013-06-01
GI | GEN-2008-086N02 | [9 empty] | Fort Randall - Madison County 230kV Ckt 1 | U |  |  |  |  | 0 | 640540 |  | 652509 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | NPPD | Fort Randall - Madison County 230kV Ckt 1 | Raise structures and line clearances as necessary to re-rate the transmission line to 320 MVA | [53 empty] | 2014-10-01 | 2014-10-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T615516WP | FROM->TO | FPL SWITCH - MOORELAND 138KV CKT 1 | EXP | OKGE | WFEC | ENID | WFEC-NORTHFO | 0 | 515785 | WINDFRM4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 16WP | 287 | 287 | 0 |  | 71.6439 | 103.3926 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Multi - Woodward District EHV - Tatonga - Matthewson - Cimarron 345 kV | Build new 126 mile Woodward - Tatonga 345 kV circuit 2 and Tatonga - Matthewson - Cimarron 345 kV line. | [53 empty] | 2015-10-01 | 2021-03-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T855520WP | FROM->TO | FPL SWITCH - MOORELAND 138KV CKT 1 | EXP | OKGE | WFEC | ENID | WFEC-NORTHFO | 0 | 515785 | WINDFRM4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 20WP | 287 | 287 | 0 |  | 65.3899 | 107.3863 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Multi - Woodward District EHV - Tatonga - Matthewson - Cimarron 345 kV | Build new 126 mile Woodward - Tatonga 345 kV circuit 2 and Tatonga - Matthewson - Cimarron 345 kV line. | [53 empty] | 2015-10-01 | 2021-03-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T515515WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 15WP | 171 | 185 | 0 |  | 90.6474 | 116.5847 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Multi - Woodward District EHV - Tatonga - Matthewson - Cimarron 345 kV | Build new 126 mile Woodward - Tatonga 345 kV circuit 2 and Tatonga - Matthewson - Cimarron 345 kV line. | [53 empty] | 2015-10-01 | 2021-03-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T7225515WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 15WP | 171 | 185 | 0 |  | 76.4062 | 102.6546 | [7 empty] | CATEGORYB | NONSINGLE | SPSCONT-05B | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Multi - Woodward District EHV - Tatonga - Matthewson - Cimarron 345 kV | Build new 126 mile Woodward - Tatonga 345 kV circuit 2 and Tatonga - Matthewson - Cimarron 345 kV line. | [53 empty] | 2015-10-01 | 2021-03-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T7215515WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 15WP | 171 | 185 | 0 |  | 75.9305 | 101.8069 | [7 empty] | CATEGORYB | NONSINGLE | SPSCONT-04 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Multi - Woodward District EHV - Tatonga - Matthewson - Cimarron 345 kV | Build new 126 mile Woodward - Tatonga 345 kV circuit 2 and Tatonga - Matthewson - Cimarron 345 kV line. | [53 empty] | 2015-10-01 | 2021-03-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T1145516SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 16SP | 133 | 153 | 0 |  | 94.8707 | 145.281 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Multi - Woodward District EHV - Tatonga - Matthewson - Cimarron 345 kV | Build new 126 mile Woodward - Tatonga 345 kV circuit 2 and Tatonga - Matthewson - Cimarron 345 kV line. | [53 empty] | 2015-10-01 | 2021-03-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T13875516SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 16SP | 133 | 153 | 0 |  | 76.9957 | 127.8065 | [7 empty] | CATEGORYB | NONSINGLE | SPSCONT-05B | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Multi - Woodward District EHV - Tatonga - Matthewson - Cimarron 345 kV | Build new 126 mile Woodward - Tatonga 345 kV circuit 2 and Tatonga - Matthewson - Cimarron 345 kV line. | [53 empty] | 2015-10-01 | 2021-03-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T13855516SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 16SP | 133 | 153 | 0 |  | 76.8528 | 126.9508 | [7 empty] | CATEGORYB | NONSINGLE | SPSCONT-04 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Multi - Woodward District EHV - Tatonga - Matthewson - Cimarron 345 kV | Build new 126 mile Woodward - Tatonga 345 kV circuit 2 and Tatonga - Matthewson - Cimarron 345 kV line. | [53 empty] | 2015-10-01 | 2021-03-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T25516SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 16SP | 133 | 153 | 0 |  | 54.2452 | 105.0515 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Multi - Woodward District EHV - Tatonga - Matthewson - Cimarron 345 kV | Build new 126 mile Woodward - Tatonga 345 kV circuit 2 and Tatonga - Matthewson - Cimarron 345 kV line. | [53 empty] | 2015-10-01 | 2021-03-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T605516WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 16WP | 171 | 185 | 0 |  | 91.0315 | 137.5084 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Multi - Woodward District EHV - Tatonga - Matthewson - Cimarron 345 kV | Build new 126 mile Woodward - Tatonga 345 kV circuit 2 and Tatonga - Matthewson - Cimarron 345 kV line. | [53 empty] | 2015-10-01 | 2021-03-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T7435516WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 16WP | 171 | 185 | 0 |  | 76.7645 | 123.5918 | [7 empty] | CATEGORYB | NONSINGLE | SPSCONT-05B | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Multi - Woodward District EHV - Tatonga - Matthewson - Cimarron 345 kV | Build new 126 mile Woodward - Tatonga 345 kV circuit 2 and Tatonga - Matthewson - Cimarron 345 kV line. | [53 empty] | 2015-10-01 | 2021-03-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T7425516WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 16WP | 171 | 185 | 0 |  | 76.2132 | 122.4761 | [7 empty] | CATEGORYB | NONSINGLE | SPSCONT-04 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Multi - Woodward District EHV - Tatonga - Matthewson - Cimarron 345 kV | Build new 126 mile Woodward - Tatonga 345 kV circuit 2 and Tatonga - Matthewson - Cimarron 345 kV line. | [53 empty] | 2015-10-01 | 2021-03-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T1695520SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 20SP | 133 | 153 | 0 |  | 81.9376 | 157.9591 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Multi - Woodward District EHV - Tatonga - Matthewson - Cimarron 345 kV | Build new 126 mile Woodward - Tatonga 345 kV circuit 2 and Tatonga - Matthewson - Cimarron 345 kV line. | [53 empty] | 2015-10-01 | 2021-03-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T17365520SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 20SP | 133 | 153 | 0 |  | 63.9796 | 139.8643 | [7 empty] | CATEGORYB | NONSINGLE | SPSCONT-05B | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Multi - Woodward District EHV - Tatonga - Matthewson - Cimarron 345 kV | Build new 126 mile Woodward - Tatonga 345 kV circuit 2 and Tatonga - Matthewson - Cimarron 345 kV line. | [53 empty] | 2015-10-01 | 2021-03-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T17335520SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 20SP | 133 | 153 | 0 |  | 64.2549 | 138.8827 | [7 empty] | CATEGORYB | NONSINGLE | SPSCONT-04 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Multi - Woodward District EHV - Tatonga - Matthewson - Cimarron 345 kV | Build new 126 mile Woodward - Tatonga 345 kV circuit 2 and Tatonga - Matthewson - Cimarron 345 kV line. | [53 empty] | 2015-10-01 | 2021-03-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T35520SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 20SP | 133 | 153 | 0 |  | 44.4661 | 113.2176 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Multi - Woodward District EHV - Tatonga - Matthewson - Cimarron 345 kV | Build new 126 mile Woodward - Tatonga 345 kV circuit 2 and Tatonga - Matthewson - Cimarron 345 kV line. | [53 empty] | 2015-10-01 | 2021-03-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T17315520SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 20SP | 133 | 153 | 0 |  | 41.3334 | 103.9679 | [7 empty] | CATEGORYB | NONSINGLE | SPSCONT-02 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Multi - Woodward District EHV - Tatonga - Matthewson - Cimarron 345 kV | Build new 126 mile Woodward - Tatonga 345 kV circuit 2 and Tatonga - Matthewson - Cimarron 345 kV line. | [53 empty] | 2015-10-01 | 2021-03-01
2015-AG1 | AFS2 | CONT-LaCygne Neosho 345kv |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T4225520SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 20SP | 133 | 153 | 0 |  | 40.8055 | 100.8473 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - NEOSHO 345KV CKT 1 | 0 | 532793 | NEOSHO 7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 |  |  |  | OKGE | Multi - Woodward District EHV - Tatonga - Matthewson - Cimarron 345 kV | Build new 126 mile Woodward - Tatonga 345 kV circuit 2 and Tatonga - Matthewson - Cimarron 345 kV line. | [53 empty] | 2015-10-01 | 2021-03-01
2015-AG1 | AFS2 | CONT-0400 - JEC - Hoyt 345kV |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3855520SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 20SP | 133 | 153 | 0 |  | 40.5712 | 100.7868 | [7 empty] | CATEGORYB | SINGLE | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 |  |  |  | OKGE | Multi - Woodward District EHV - Tatonga - Matthewson - Cimarron 345 kV | Build new 126 mile Woodward - Tatonga 345 kV circuit 2 and Tatonga - Matthewson - Cimarron 345 kV line. | [53 empty] | 2015-10-01 | 2021-03-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T845520WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 20WP | 171 | 185 | 0 |  | 81.8617 | 145.482 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 |  |  |  | OKGE | Multi - Woodward District EHV - Tatonga - Matthewson - Cimarron 345 kV | Build new 126 mile Woodward - Tatonga 345 kV circuit 2 and Tatonga - Matthewson - Cimarron 345 kV line. | [53 empty] | 2015-10-01 | 2021-03-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T9005520WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 20WP | 171 | 185 | 0 |  | 66.7476 | 130.6729 | [7 empty] | CATEGORYB | NONSINGLE | SPSCONT-05B | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Multi - Woodward District EHV - Tatonga - Matthewson - Cimarron 345 kV | Build new 126 mile Woodward - Tatonga 345 kV circuit 2 and Tatonga - Matthewson - Cimarron 345 kV line. | [53 empty] | 2015-10-01 | 2021-03-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T8985520WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 20WP | 171 | 185 | 0 |  | 66.735 | 129.5144 | [7 empty] | CATEGORYB | NONSINGLE | SPSCONT-04 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Multi - Woodward District EHV - Tatonga - Matthewson - Cimarron 345 kV | Build new 126 mile Woodward - Tatonga 345 kV circuit 2 and Tatonga - Matthewson - Cimarron 345 kV line. | [53 empty] | 2015-10-01 | 2021-03-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T15520WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | EXP | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 20WP | 171 | 185 | 0 |  | 45.832 | 101.0954 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Multi - Woodward District EHV - Tatonga - Matthewson - Cimarron 345 kV | Build new 126 mile Woodward - Tatonga 345 kV circuit 2 and Tatonga - Matthewson - Cimarron 345 kV line. | [53 empty] | 2015-10-01 | 2021-03-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T2075016SP | FROM->TO | FT RANDAL - SPENCER 115KV CKT 1 | EXP | WAPA | NPPD | WAPA_1604 | NPPD_686 | 0 | 652510 | FTRANDL7 115.00 | 640349 | SPENCER7 115.00 | 0 |  | 1 | 16SP | 120 | 120 | 124 | 102.4 | 102.3567 | 102.6597 | [7 empty] | CATEGORYB | SINGLE | HOSKINS - NELIGH.EAST3345.00 345KV CKT 1 | 0 | 640226 | HOSKINS3 345.00 | 640520 | NELIGH.EAST3345.00 | 0 |  | 1 |  |  |  | NPPD | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Build new 222 mile, 345 kV line from Gentleman - Cherry Co - Holt Co. Build new 345 kV substations at Cherry Co and Holt Co. Terminal upgrades at Gentleman. This project is contingent upon WAPA approval to tap the Grand Island - Fort Thompson 345 kV line. | [53 empty] | 2016-06-01 | 2018-01-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T8675016SP | FROM->TO | FT RANDAL - SPENCER 115KV CKT 1 | EXP | WAPA | NPPD | WAPA_1604 | NPPD_686 | 0 | 652510 | FTRANDL7 115.00 | 640349 | SPENCER7 115.00 | 0 |  | 1 | 16SP | 120 | 120 | 124 | 102.3 | 102.3002 | 102.6118 | [7 empty] | CATEGORYB | SINGLE | NELIGH.EAST3345.00 (NELIGH.E T1) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 640520 | NELIGH.EAST3345.00 | 640521 | NELIGH.EAST7115.00 | 640524 | NELIGH.EAST913.800 | 1 |  |  |  | NPPD | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Build new 222 mile, 345 kV line from Gentleman - Cherry Co - Holt Co. Build new 345 kV substations at Cherry Co and Holt Co. Terminal upgrades at Gentleman. This project is contingent upon WAPA approval to tap the Grand Island - Fort Thompson 345 kV line. | [53 empty] | 2016-06-01 | 2018-01-01
2006-AG1 | AFS-4 | [9 empty] | FT SUPPLY 138/69KV TRANSFORMER CKT 1 | U | WFEC | WFEC |  |  | 1 | 520920 | FTSUPLY4 138 | 520919 | FTSUPLY269.0 | 521182 |  | 2 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WFEC | FT SUPPLY 138/69KV TRANSFORMER CKT 2 | Install 2nd 70 MVA auto at Ft Supply | [53 empty] | 2006-12-01 | 2008-06-01
2009-AGP1 | AFS-5 | [9 empty] | G03-05T 138.00 - PARADISE 138KV CKT 1 | U | WFEC | WFEC | AEP-OP-I | AEP-KP | 0 | 521129 | G03-05T 138.00 | 521024 | PARADSE4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WFEC | BLUCAN5 4 138.00 - PARADISE 138KV CKT 1 | Upgrade Paradise to G03-05T to 1113 | [53 empty] | 2010-06-01 | 2013-06-01
GI | GEN-2008-037 | [9 empty] | GRACMNT4 138.00 - WASHITA 138KV CKT 2 OKGE | U | WFEC | OKGE | AEP-CS | ARDMORE | 0 | 521089 | WASHITA4 138.00 | 515802 | GRACMNT4 138.00 | 0 |  | 2 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OKGE | Gracemont 138kV line terminal addition | 138kV line terminal at Gracemont substation, including breaker, line relaying, disconnect switches and associated equipment, dead end structures, revenue metering with CT's and PT's. | [13 empty] | 2010-11-20 | [39 empty] | 2011-10-15 | 2011-10-15
GI | GEN-2008-037 | [9 empty] | GRACMNT4 138.00 - WASHITA 138KV CKT 2 WFEC | U | WFEC | OKGE | AEP-CS | ARDMORE | 0 | 521089 | WASHITA4 138.00 | 515802 | GRACMNT4 138.00 | 0 |  | 2 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WFEC | WASHITA - GRACEMONT 138 KV CKT 2 | BUILD WASHITA - GRACEMONT 138KV CKT 2 (APPROXIMATELY 7 MILES). ADD LINE TERMINAL AT WASHITA AND PROCURE RIGHT OF WAY. REQUIRED AS SHARED NETWORK UPGRADE FOR INTERCONNECTION OF GEN-2008-037. | [13 empty] | 2010-11-20 | [39 empty] | 2012-10-12 | 2012-10-12
2008-AGP1 | AFS-9 | [9 empty] | GREENLEAF - KNOB HILL 115KV CKT 1 | U | SUNC | WERE |  | NCENTRAL | 0 | 539665 | GRNLEAF3 115.00 | 533332 | KNOB HL3 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | GREENLEAF - KNOB HILL 115KV CKT 1 (MKEC) | Rebuild 43.5% Ownership of 20.9 miles | [53 empty] | 2013-06-01 | 2013-06-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T21275525SP | TO->FROM | GREENSBURG - SSTARTP3 115.00 115KV CKT 1 | S | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539763 | SSTARTP3 115.00 | 539664 | GRNBURG3 115.00 | 0 |  | 1 | 25SP | 115.1 | 115.1 | 0 |  | 91.0409 | 100.3846 | [7 empty] | CATEGORYB | NONSINGLE | SPP-MKEC-01 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SUNC | GREENSBURG - SSTARTP3 115.00 115KV CKT 1 | Rebuild 7.6 Miles of line | [12 empty] | 5577343 | 2015-04-15 | [39 empty] | 2021-06-01 | 2021-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2145525SP | FROM->TO | HANCOCK - MUSKOGEE 161KV CKT 1 | CP | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515250 | HANCOK-5 161.00 | 515222 | MUSKOGE5 161.00 | 0 |  | 1 | 25SP | 223 | 223 | 0 | 102.3 | 102.2877 | 101.3362 | [7 empty] | CATEGORYB | SINGLE | AGENCY - PECAN CREEK 161KV CKT 1 | 0 | 515230 | AGENCY 5 161.00 | 515234 | PECANCK5 161.00 | 0 |  | 1 |  |  |  | OKGE | HANCOCK - MUSKOGEE 161KV CKT 1 | Replace Muskogee Terminal Equipment | 273 | 312 | [10 empty] | 330000 | 2010-01-01 | [39 empty] | 2021-06-01 | 2021-06-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21V7365516SP |  | HARPER 138KV | EXP | SUNC |  | GREAT PL |  |  | 539668 | HARPER 4 138.00 | [5 empty] | 16SP | [8 empty] | 0.92321 | 0.89365 | 0.98029 | 0.9 | 1.05 | CATEGORYB | NONSINGLE | SPP-MKEC-08 | 0 | 0 |  | 0 |  | 0 | [5 empty] | MKEC | Anthony - Harper 138 kV Ckt 1 | Construct new 21-mile 138 kV line from Anthony to Harper. | [53 empty] | 2016-06-01 | 2018-02-18
GI | GEN-2008-051 | [9 empty] | Harrington Mid - Nichols 230 kV Ckt 2 | U | SPS | SPS |  |  | 0 | 523978 |  | 524044 |  |  |  | 2 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | SPS | Harrington Mid - Nichols 230 kV Ckt 2 | Reconductor Harrington Mid - Nichols 230kV. Replace switches and breakers to get circuit to 727/727 MVA rating. New limit should be bus rating. | [13 empty] | 2011-10-01 | [39 empty] | 2012-12-01 | 2012-12-01
GI | GEN-2008-051 | [9 empty] | Harrington West - Nichols 230kV Ckt 1 | U | SPS | SPS |  |  | 0 | 523977 |  | 524044 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | SPS | Harrington West - Nichols 230kV Ckt 1 | Reconductor Harrington West - Nichols 230kV. Replace switches and breakers to get circuit to 727/727 MVA rating. New limit should be bus rating. | [13 empty] | 2011-10-01 | [39 empty] | 2012-12-01 | 2012-12-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T1875016SP | TO->FROM | HARRIONSVILLE NORTH - RALPH GREEN 69KV CKT 1 | REL | KCPL | KCPL |  |  | 0 | 541279 | RGREEN 2 69.000 | 541297 | HSNVLN 2 69.000 | 0 |  | 1 | 16SP | 43 | 49 | 49 | 110.2 | 110.2424 | 110.4428 | [7 empty] | CATEGORYB | SINGLE | HARRISONVILLE - HARRISONVILLE SWITCHING 69KV CKT 1 | 0 | 541295 | HSNVL 2 69.000 | 541296 | HSNVLSW2 69.000 | 0 |  | 1 |  |  |  | MIPU | HARRIONSVILLE NORTH - RALPH GREEN 69KV CKT 1 | Rebuild of Harrisonville North and Ralph Green 69kV line. | [53 empty] | 2016-06-01 | 2017-01-21
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T1875016SP | TO->FROM | HARRIONSVILLE NORTH - RALPH GREEN 69KV CKT 1 | REL | KCPL | KCPL |  |  | 0 | 541279 | RGREEN 2 69.000 | 541297 | HSNVLN 2 69.000 | 0 |  | 1 | 16SP | 43 | 49 | 49 | 110.2 | 110.2424 | 110.4428 | [7 empty] | CATEGORYB | SINGLE | HARRISONVILLE - HARRISONVILLE SWITCHING 69KV CKT 1 | 0 | 541295 | HSNVL 2 69.000 | 541296 | HSNVLSW2 69.000 | 0 |  | 1 |  |  |  | MIPU | HARRIONSVILLE NORTH - RALPH GREEN 69KV CKT 1 | Rebuild of Harrisonville North and Ralph Green 69kV line. | [53 empty] | 2016-06-01 | 2017-01-21
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T5075520SP | TO->FROM | HARRIONSVILLE NORTH - RALPH GREEN 69KV CKT 1 | REL | KCPL | KCPL |  |  | 0 | 541279 | RGREEN 2 69.000 | 541297 | HSNVLN 2 69.000 | 0 |  | 1 | 20SP | 43 | 49 | 49 | 101.8 | 101.8421 | 101.7729 | [7 empty] | CATEGORYB | SINGLE | HARRISONVILLE - HARRISONVILLE SWITCHING 69KV CKT 1 | 0 | 541295 | HSNVL 2 69.000 | 541296 | HSNVLSW2 69.000 | 0 |  | 1 |  |  |  | MIPU | HARRIONSVILLE NORTH - RALPH GREEN 69KV CKT 1 | Rebuild of Harrisonville North and Ralph Green 69kV line. | [53 empty] | 2016-06-01 | 2017-01-21
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T5075520SP | TO->FROM | HARRIONSVILLE NORTH - RALPH GREEN 69KV CKT 1 | REL | KCPL | KCPL |  |  | 0 | 541279 | RGREEN 2 69.000 | 541297 | HSNVLN 2 69.000 | 0 |  | 1 | 20SP | 43 | 49 | 49 | 101.8 | 101.8421 | 101.7729 | [7 empty] | CATEGORYB | SINGLE | HARRISONVILLE - HARRISONVILLE SWITCHING 69KV CKT 1 | 0 | 541295 | HSNVL 2 69.000 | 541296 | HSNVLSW2 69.000 | 0 |  | 1 |  |  |  | MIPU | HARRIONSVILLE NORTH - RALPH GREEN 69KV CKT 1 | Rebuild of Harrisonville North and Ralph Green 69kV line. | [53 empty] | 2016-06-01 | 2017-01-21
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2435516SP | TO->FROM | HOOVER NORTH - LAKERIDGE 138KV CKT 1 | EXP | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533053 | LAKERDG4 138.00 | 533049 | HOOVERN4 138.00 | 0 |  | 1 | 16SP | 369 | 382 | 0 |  | 94.9696 | 101.443 | [7 empty] | CATEGORYB | SINGLE | 45TH ST4 138.00 - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533074 | 45TH ST4 138.00 | 0 |  | 1 |  |  |  | WERE | Multi - Viola 345/138kV Transformer and 138 kV Lines to Clearwater and Gill | Install 345/138 kV transformer at future Viola 345 kV substation. Build 138kV line from Viola to Clearwater substation. Build 138 kV line from Viola to Gill substation | [53 empty] | 2016-06-01 | 2019-06-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2395516SP | TO->FROM | HOOVER NORTH - LAKERIDGE 138KV CKT 1 | EXP | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533053 | LAKERDG4 138.00 | 533049 | HOOVERN4 138.00 | 0 |  | 1 | 16SP | 369 | 382 | 0 |  | 94.3971 | 100.8264 | [7 empty] | CATEGORYB | SINGLE | 45TH ST4 138.00 - COWSKIN 138KV CKT 1 | 0 | 533038 | COWSKIN4 138.00 | 533074 | 45TH ST4 138.00 | 0 |  | 1 |  |  |  | WERE | Multi - Viola 345/138kV Transformer and 138 kV Lines to Clearwater and Gill | Install 345/138 kV transformer at future Viola 345 kV substation. Build 138kV line from Viola to Clearwater substation. Build 138 kV line from Viola to Gill substation | [53 empty] | 2016-06-01 | 2019-06-01
GI | GEN-2011-027 | [9 empty] | Hoskins - Dixon County 230kV Line Upgrade | U |  |  |  |  | 0 | 560347 |  | 640227 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | NPPD | Hoskins - Dixon County 230kV Line Upgrade | Increase clearances to accommodate 320MVA facility rating to address loading issues | [53 empty] | 2015-10-24 | 2015-10-24
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T1935516SP | TO->FROM | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | EXP | WERE | WERE | NEAST | NEAST | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 | 16SP | 1076 | 1076 | 0 | 99.5 | 99.4506 | 100.6832 | [7 empty] | CATEGORYB | SINGLE | JEFFREY ENERGY CENTER - MORRIS COUNTY 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532770 | MORRIS 7 345.00 | 0 |  | 1 |  |  |  | WERE | East Manhattan - Jeffrey Energy Center 230 kV Ckt 1 Rebuild | Rebuild 27-mile 230 kV line from East Manhattan to Jeffrey Energy Center to 345 kV standards but operate as 230 kV using bundled 1590 ACSR conductor. Upgrade terminal equipment at East Manhattan and Jeffrey Energy Center to a minimum emergency rating of 2 | [12 empty] | 58317000 | 2014-08-28 | [39 empty] | 2016-06-01 | 2017-06-01
2005-AG2 | AFS-3 | [9 empty] | HUGO POWER PLANT - VALLIANT 138KV CKT 1 | U | WFEC | AEPW |  |  | 0 | 521157 | HUGO PP4 138 | 510911 | VALIANT4 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WFEC | HUGO - VALLIANT 345KV CKT 1 | New 19 miles 345 KV | [53 empty] | 2012-07-01 | 2012-07-01 | 2012-06-01
2005-AG2 | AFS-3 | [9 empty] | HUGO POWER PLANT - VALLIANT 138KV CKT 1 | U | WFEC | AEPW |  |  | 0 | 521157 | HUGO PP4 138 | 510911 | VALIANT4 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | Valliant 345 kV (AEP) | Vallient 345 KV line terminal | [53 empty] | 2012-07-01 | 2012-07-01 | 2012-06-01
2005-AG2 | AFS-3 | [9 empty] | HUGO POWER PLANT 345/138KV TRANSFORMER CKT 1 | U | WFEC | AEPW |  |  | 1 | 521157 | HUGO PP4 138 | 520948 | HUGO PP4 138.00 | 521189 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WFEC | HUGO 345/138KV TRANSFORMER CKT 1 | New 345/138 kv Auto | [53 empty] | 2012-07-01 | 2012-07-01 | 2012-06-01
GI | GEN-2004-008 | [9 empty] | Iatan - Platte City 161kV | U | KACP | KACP |  |  | 0 | 541350 |  | 541221 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | KACP | IATAN - PLATTE CITY 161KV CKT 1 | Platte City to Stranger Creek 161kV Ckt 1 Tap and addition of 4 miles 161kV transmission line to create Iatan - Platte City 161kV Ckt 1. | [13 empty] | 2006-05-01 | [39 empty] | 2010-03-18 | 2010-03-18
GI | GEN-2004-008 | [9 empty] | Iatan - Platte City 161kV | U | KACP | KACP |  |  | 0 | 541350 |  | 541221 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | KACP | IATAN - PLATTE CITY 161KV CKT 1 #2 | Terminal equipment planned to be upgraded to allow for 2000 Amps at Platte City | [13 empty] | 2006-05-01 | [39 empty] | 2009-12-15 | 2009-12-15 | 2009-12-01
GI | GEN-2004-008 | [9 empty] | Iatan - Platte City 161kV | U | KACP | KACP |  |  | 0 | 541350 |  | 541221 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | KACP | PLATTE CITY 161KV | Install a 6 ohm reactor at Platte City substation on the Platte City-Iatan 161 kV line. | [13 empty] | 2006-05-01 | [39 empty] | 2010-12-12 | 2010-12-12 | 2010-12-01
GI | GEN-2004-008 | [9 empty] | Iatan - Stranger Creek 161kV | U | KACP | KACP |  |  | 0 | 541350 |  | 541231 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | KACP | IATAN - STRANGER 161KV CKT 1 | Platte City to Stranger Creek 161kV Ckt 1 Tap and addition of 4 miles 161kV transmission line to create Iatan - Stranger Creek 161kV Ckt 1. | [13 empty] | 2006-05-01 | [39 empty] | 2010-03-18 | 2010-03-18
GI | GEN-2004-008 | [9 empty] | Iatan 345/161kV XFMR | U | KACP | KACP |  |  | 1 | 542982 |  | 541350 |  | 541150 |  | 11 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | KACP | IATAN - ST JOE 345KV CKT 1 | Relocate Iatan St. Joseph 345kV line | [13 empty] | 2006-05-01 | [39 empty] | 2009-12-15 | 2009-12-15 | 2009-12-01
GI | GEN-2004-008 | [9 empty] | Iatan 345/161kV XFMR | U | KACP | KACP |  |  | 1 | 542982 |  | 541350 |  | 541150 |  | 11 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | KACP | Iatan 161 kV | Iatan 161kV substation work including the installation of a ring bus, three (3) 161kV circuit breakers, and associated equipment | [13 empty] | 2006-05-01 | [39 empty] | 2009-12-15 | 2009-12-15 | 2009-12-01
GI | GEN-2004-008 | [9 empty] | Iatan 345/161kV XFMR | U | KACP | KACP |  |  | 1 | 542982 |  | 541350 |  | 541150 |  | 11 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | KACP | Iatan 345/161 kV transformer | Iatan 345/161 kV XFMR and Iatan 161 kV substation work | [13 empty] | 2006-05-01 | [39 empty] | 2009-12-15 | 2009-12-15 | 2009-12-01
GI | GEN-2008-129 | [9 empty] | KC SOUTH - LONGVIEW 161 KV CKT 1 | U | MIPU | MIPU |  |  | 0 | 541245 |  | 541224 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MIPU | Longview - KC South 161kV Ckt 1 | Install new 161kV wavetrap in place of existing wavetrap | [13 empty] | 2011-01-05 | [39 empty] | 2011-01-31 | 2011-01-31 | 2010-12-01
GI | GEN-2008-086N02 | [9 empty] | Kelly - Madison County 230kV Ckt 1 | U |  |  |  |  | 0 | 640540 |  | 640133 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | NPPD | Kelly - Madison County 230kV Ckt 1 | Raise structures and line clearances as necessary to re-rate the transmission line to 320 MVA | [53 empty] | 2014-10-01 | 2014-10-01
2006-AG1 | AFS-4 | [9 empty] | KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1 | U | OKGE |  |  |  | 1 | 514795 | KNOBHIL4 138 | 514794 | KNOBHIL269.0 | 515732 | KNOBHIL113.2 | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OKGE | KNOBHILL 138/69KV TRANSFORMER CKT 1 | Replace bus tie with 100MVA transformer | [53 empty] | 2006-06-01 | 2008-06-01
NA | SPONSORED | [9 empty] | LACYGNE - WEST GARDNER 345KV CKT 1 | U | KACP | KACP |  |  | 0 | 542981 | LACYGNE7 | 542965 | W.GRDNR7 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | KACP | LACYGNE - WEST GARDNER 345KV CKT 1 | KCPL Sponsored Project to Reconductor Line to be In-Service by 6/1/2006 | [53 empty] | 2006-06-01 | 2006-06-01
GI | GEN-2008-079 | [9 empty] | Lancer - North Judson Large 115KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539759 |  | 539771 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | Lancer - North Judson Large 115KV CKT 1 | Build appoximately 20 mile 115 kV line | [53 empty] | 2013-10-01 | 2016-06-01
GI | GEN-2008-079 | [9 empty] | Lancer - Spearville 345KV CKT 1 | U | MKEC | MKEC |  |  | 1 | 531469 |  | 539759 |  | 539960 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | Lancer - Spearville 345KV CKT 1 | Build appoximately 0.5 mile 345 kV line | [53 empty] | 2013-10-01 | 2016-06-01
GI | GEN-2008-079 | [9 empty] | Lancer 345/115/13.8kV Transformer CKT 1 | U | MKEC | MKEC |  |  | 1 | 531469 |  | 539759 |  | 539960 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | Lancer 345/115/13.8kV Transformer CKT 1 | Build new Lancer Substation with 345/115 kV transformer | [53 empty] | 2013-10-01 | 2016-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T2835025SP | FROM->TO | LIVSTNRIDGE3115.00 - WIPP SUB 115KV CKT 1 | REL | SPS | SPS | SPS-PECO | SPS-PECO | 0 | 527953 | LIVSTNRIDGE3115.00 | 528009 | WIPP 3115.00 | 0 |  | 1 | 25SP | 159 | 160 | 0 | 108.2 | 108.1614 | 108.0751 | [7 empty] | CATEGORYB | SINGLE | KIOWA 7345.00 - RDRUNNER 7345.00 345KV CKT 1 | 0 | 527965 | KIOWA 7345.00 | 528027 | RDRUNNER 7345.00 | 0 |  | 1 |  |  |  | SPS | LIVSTNRIDGE3115.00 - WIPP SUB 115KV CKT 1 | Rebuild 2.75 miles of transmission line. | [53 empty] | 2021-06-01 | 2021-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T12105025SP | FROM->TO | LIVSTNRIDGE3115.00 - WIPP SUB 115KV CKT 1 | REL | SPS | SPS | SPS-PECO | SPS-PECO | 0 | 527953 | LIVSTNRIDGE3115.00 | 528009 | WIPP 3115.00 | 0 |  | 1 | 25SP | 159 | 160 | 0 | 107.7 | 107.7026 | 107.639 | [7 empty] | CATEGORYB | SINGLE | RDRUNNER 7345.00 (UPDATE LATER) 345/115/13.2KV TRANSFORMER CKT 1 | 1 | 528025 | RDRUNNER 3115.00 | 528027 | RDRUNNER 7345.00 | 528023 | RDRNNER_TR1113.200 | 1 |  |  |  | SPS | LIVSTNRIDGE3115.00 - WIPP SUB 115KV CKT 1 | Rebuild 2.75 miles of transmission line. | [53 empty] | 2021-06-01 | 2021-06-01
GI | GEN-2010-057 | [9 empty] | LYONS - WHEATLAND 115KV CKT 1 #2 | U | WERE | WERE |  |  | 0 | 530620 | LYONS 3 115.00 | 533439 | WHEATLD3 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WERE | Wheatland 115 kV #2 | Install metering equipment at the Wheatland 115 kV substation for GEN-2010-057. | [13 empty] | 2011-12-27 | [39 empty] | 2012-12-31 | 2012-12-31 | 2012-12-01
GI | GEN-2006-010 | [9 empty] | MANDEVILTP4 - SE TEXARKANA 138KV CKT 1 | U | AEPW | AEPW | SARK | TEXARK | 0 | 508105 | MANDEVILTP4 | 508078 | SETEXAR4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | MANDEVILTP4 - SE TEXARKANA 138KV CKT 1 | Build new Turk-SE Texarkana 138 kV line and add SE Texarkana 138 kV terminal. | [53 empty] | 2012-07-01 | 2012-07-01
GI | GEN-2006-010 | [9 empty] | MANDEVILTP4 - TURK 138KV CKT 1 | U | AEPW | AEPW | SARK | TEXARK | 0 | 507454 | TURK 4 138.00 | 508105 | MANDEVILTP4 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | SE TEXARKANA - TURK 138KV CKT 1 | Build new Turk-SE Texarkana 138 kV line and add SE Texarkana 138 kV terminal. | [53 empty] | 2012-07-01 | 2012-07-01
NA | SPONSORED | [9 empty] | MATHEWSON - TATONGA 345KV CKT 1 | U | OKGE | OKGE | ENID | ENID | 0 | 515497 |  | 515407 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OKGE | MATHEWSON - TATONGA 345KV CKT 1 | Build 345 kV line | [53 empty] | 2010-01-01 | 2010-01-01 | 2009-12-01
GI | GEN-2006-010 | [9 empty] | MCNAB REC - TURK 115KV CKT 1 | U | AEPW | AEPW | SARK | SARKAECC | 0 | 507456 | HEMPSTD3 115.00 | 504122 | MCNAB 3 115.00 |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | MCNAB REC - Turk 115KV CKT 1 #2 (AEP) | Build a new two mile, 138kV, 1590 ACSR line section (operated at 115kV) from Turk Substation to the existing Okay-Hope 115kV line to form a Turk - Hope 115kV line. | [13 empty] | 2007-10-01 | [39 empty] | 2011-12-01 | 2011-12-01
2015-AG1 | AFS2 |  | FDNSLock |  | FDNSLock |  | 5 | 0 | 2015AG1AFS22T215016SP | FROM->TO | MISSION - ST FRANCIS 115KV CKT 1 | EXP | WAPA | NPPD | WAPA_1603 | NPPD_686 | 0 | 652482 | MISSION7 115.00 | 640351 | ST.FRANC 115.00 | 0 |  | 1 | 16SP | 80 | 80 | 88 | 113 | -999 | 112.1563 | [7 empty] | CATEGORYB | SINGLE | EMMETE.TAP 7115.00 - ONEILL 115KV CKT 1 | 0 | 640305 | ONEILL 7 115.00 | 640465 | EMMETE.TAP 7115.00 | 0 |  | 1 |  |  |  | NPPD | Thedford 345/115 kV Transformer | Install new 345/115 kV 400 MVA transformer at Thedford substation. Install any necessary 115 kV terminal equipment. | [53 empty] | 2016-06-01 | 2018-01-01
GI | GEN-2006-044N | [9 empty] | NELIGH - PETERSBURG 115KV CKT 1 | U | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640444 |  | 640293 | NELIGH 7 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | NPPD | Neligh - Petersburg North 115kV Ckt 1 | Replace Breaker 1106, jumpers, & 115kV Switch 1106-D2; Replace Petersburg 115kV Substation main bus; Upgrade and replace transmission structures on 115kV lines TL1168 A & B to facilitate 100 degrees Centigrade line operation | [13 empty] | 2011-01-01 | [39 empty] | 2012-12-31 | 2012-12-31 | 2012-12-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T3615025SP | TO->FROM | NORTH STREET - NORTHVIEW 115KV CKT 1 | S | WERE | WERE | WEST | WEST | 0 | 533371 | NORTHVW3 115.00 | 533370 | NORTHST3 115.00 | 0 |  | 1 | 25SP | 68 | 68 | 0 |  | 89.3623 | 100.363 | [7 empty] | CATEGORYB | SINGLE | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | 0 | 533368 | EXIDE J3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  |  | WERE | NORTH STREET - NORTHVIEW 115KV CKT 1 | Rebuild 3.2 Miles of line | [12 empty] | 2348355 | 2015-04-14 | [39 empty] | 2021-06-01 | 2021-06-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T3625025SP | TO->FROM | NORTH STREET - NORTHVIEW 115KV CKT 2 | S | WERE | WERE | WEST | WEST | 0 | 533371 | NORTHVW3 115.00 | 533370 | NORTHST3 115.00 | 0 |  | 2 | 25SP | 68 | 68 | 0 |  | 89.3623 | 100.363 | [7 empty] | CATEGORYB | SINGLE | EXIDE JUNCTION - SUMMIT 115KV CKT 1 | 0 | 533368 | EXIDE J3 115.00 | 533381 | SUMMIT 3 115.00 | 0 |  | 1 |  |  |  | WERE | NORTH STREET - NORTHVIEW 115KV CKT 2 | Rebuild 3.2 Miles of line | [12 empty] | 2348355 | 2015-04-14 | [39 empty] | 2021-06-01 | 2021-06-01
NA | SPONSORED | [9 empty] | NORTHWEST - MATHEWSON 345KV CKT 1 | U | OKGE | OKGE | ENID | ENID | 0 | 514880 |  | 515497 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OKGE | MATHEWSON - NORTHWEST 345KV CKT 1 | Build 345 kV line | [53 empty] | 2010-01-01 | 2010-01-01 | 2009-12-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T55520SP | TO->FROM | NORTHWEST INTERCHANGE - ROLLHILLS 3115.00 115KV CKT 1 | REL | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524007 | ROLLHILLS 3115.00 | 524106 | NORTHWEST 3115.00 | 0 |  | 1 | 20SP | 120 | 154 | 0 | 103.4 | 103.4197 | 102.8245 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | NORTHWEST INTERCHANGE - ROLLHILLS 3115.00 115KV CKT 1 | Rebuild 8.34 miles of line | [12 empty] | 6120400 | 2015-04-13 | [39 empty] | 2017-06-01 | 2018-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T55525SP | TO->FROM | NORTHWEST INTERCHANGE - ROLLHILLS 3115.00 115KV CKT 1 | REL | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524007 | ROLLHILLS 3115.00 | 524106 | NORTHWEST 3115.00 | 0 |  | 1 | 25SP | 120 | 154 | 0 | 119.5 | 119.4722 | 122.5358 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | NORTHWEST INTERCHANGE - ROLLHILLS 3115.00 115KV CKT 1 | Rebuild 8.34 miles of line | [12 empty] | 6120400 | 2015-04-13 | [39 empty] | 2017-06-01 | 2018-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2615525SP | TO->FROM | NORTHWEST INTERCHANGE - ROLLHILLS 3115.00 115KV CKT 1 | REL | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524007 | ROLLHILLS 3115.00 | 524106 | NORTHWEST 3115.00 | 0 |  | 1 | 25SP | 120 | 154 | 0 | 113.1 | 113.0963 | 113.8629 | [7 empty] | CATEGORYB | SINGLE | COULTER INTERCHANGE - PUCKETT SUB 115KV CKT 1 | 0 | 524256 | PUCKETT 3115.00 | 524306 | COULTER 3115.00 | 0 |  | 1 |  |  |  | SPS | NORTHWEST INTERCHANGE - ROLLHILLS 3115.00 115KV CKT 1 | Rebuild 8.34 miles of line | [12 empty] | 6120400 | 2015-04-13 | [39 empty] | 2017-06-01 | 2018-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2695525SP | TO->FROM | NORTHWEST INTERCHANGE - ROLLHILLS 3115.00 115KV CKT 1 | REL | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524007 | ROLLHILLS 3115.00 | 524106 | NORTHWEST 3115.00 | 0 |  | 1 | 25SP | 120 | 154 | 0 | 111 | 111.0223 | 112.7849 | [7 empty] | CATEGORYB | SINGLE | RANDALL COUNTY INTERCHANGE - SOUTH GEORGIA INTERCHANGE 115KV CKT 1 | 0 | 524322 | GEORGIA 3115.00 | 524364 | RANDALL 3115.00 | 0 |  | 1 |  |  |  | SPS | NORTHWEST INTERCHANGE - ROLLHILLS 3115.00 115KV CKT 1 | Rebuild 8.34 miles of line | [12 empty] | 6120400 | 2015-04-13 | [39 empty] | 2017-06-01 | 2018-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T1785025SP | TO->FROM | NORTHWEST INTERCHANGE - ROLLHILLS 3115.00 115KV CKT 1 | REL | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524007 | ROLLHILLS 3115.00 | 524106 | NORTHWEST 3115.00 | 0 |  | 1 | 25SP | 120 | 154 | 0 | 114.7 | 114.6587 | 110.501 | [7 empty] | CATEGORYB | SINGLE | BUSHLAND INTERCHANGE - POTTER COUNTY INTERCHANGE 230KV CKT 1 | 0 | 523959 | POTTER_CO 6230.00 | 524267 | BUSHLAND 6230.00 | 0 |  | 1 |  |  |  | SPS | NORTHWEST INTERCHANGE - ROLLHILLS 3115.00 115KV CKT 1 | Rebuild 8.34 miles of line | [12 empty] | 6120400 | 2015-04-13 | [39 empty] | 2017-06-01 | 2018-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T21345525SP | TO->FROM | NORTHWEST INTERCHANGE - ROLLHILLS 3115.00 115KV CKT 1 | REL | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524007 | ROLLHILLS 3115.00 | 524106 | NORTHWEST 3115.00 | 0 |  | 1 | 25SP | 120 | 154 | 0 | 106.8 | 106.7549 | 109.8874 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-K19 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | NORTHWEST INTERCHANGE - ROLLHILLS 3115.00 115KV CKT 1 | Rebuild 8.34 miles of line | [12 empty] | 6120400 | 2015-04-13 | [39 empty] | 2017-06-01 | 2018-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T21415525SP | TO->FROM | NORTHWEST INTERCHANGE - ROLLHILLS 3115.00 115KV CKT 1 | REL | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524007 | ROLLHILLS 3115.00 | 524106 | NORTHWEST 3115.00 | 0 |  | 1 | 25SP | 120 | 154 | 0 | 103.9 | 103.9085 | 106.5011 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-V43 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | NORTHWEST INTERCHANGE - ROLLHILLS 3115.00 115KV CKT 1 | Rebuild 8.34 miles of line | [12 empty] | 6120400 | 2015-04-13 | [39 empty] | 2017-06-01 | 2018-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T21405525SP | TO->FROM | NORTHWEST INTERCHANGE - ROLLHILLS 3115.00 115KV CKT 1 | REL | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524007 | ROLLHILLS 3115.00 | 524106 | NORTHWEST 3115.00 | 0 |  | 1 | 25SP | 120 | 154 | 0 | 99.7 | 99.689 | 102.3102 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-V03 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SPS | NORTHWEST INTERCHANGE - ROLLHILLS 3115.00 115KV CKT 1 | Rebuild 8.34 miles of line | [12 empty] | 6120400 | 2015-04-13 | [39 empty] | 2017-06-01 | 2018-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2865516SP | FROM->TO | ODESSA 161/69KV TRANSFORMER CKT 1 | EXP | KCPL | KCPL |  |  | 0 | 541229 | ODESSA 5 161.00 | 541267 | ODESSA 2 69.000 | 0 |  | 1 | 16SP | 33 | 36.3 | 36 | 102.7 | 102.6653 | 102.6616 | [7 empty] | CATEGORYB | SINGLE | LEXINGTON - LEXINGTON 69KV CKT 1 | 0 | 541264 | LEX69 2 69.000 | 541265 | LEXNTON2 69.000 | 0 |  | 1 |  |  |  | KCPL | South Waverly 161/69 kV Ckt 1 Transformer | Replace Existing 161/69 kV transformer at South Waverly to increase ratings from 22 MVA to 50 MVA. | [12 empty] | 2000000 | 2015-04-13 | [39 empty] | 2016-06-01 | 2016-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2855516SP | FROM->TO | ODESSA 161/69KV TRANSFORMER CKT 1 | EXP | KCPL | KCPL |  |  | 0 | 541229 | ODESSA 5 161.00 | 541267 | ODESSA 2 69.000 | 0 |  | 1 | 16SP | 33 | 36.3 | 36 | 102.7 | 102.6551 | 102.6513 | [7 empty] | CATEGORYB | SINGLE | LEXINGTON 161/69KV TRANSFORMER CKT 1 | 0 | 541232 | LEX161 5 161.00 | 541264 | LEX69 2 69.000 | 0 |  | 1 |  |  |  | KCPL | South Waverly 161/69 kV Ckt 1 Transformer | Replace Existing 161/69 kV transformer at South Waverly to increase ratings from 22 MVA to 50 MVA. | [12 empty] | 2000000 | 2015-04-13 | [39 empty] | 2016-06-01 | 2016-06-01
GI | GEN-2006-010 | [9 empty] | OKAY - TURK 138KV CKT 1 | U | AEPW | AEPW | SARK | SARK | 0 | 507454 | TURK 4 138.00 | 507428 | OKAY 4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | OKAY - TURK 138KV CKT 1 | Build a new two mile, 138kV, 1590 ACSR line section from Turk Substation to the existing Okay-Hope 115kV line and rebuild twelve miles of 115kV line to Okay Substation to 138kV, 1590 ACSR, to form a Turk - Okay 138kV line. | [13 empty] | 2007-10-01 | [39 empty] | 2011-12-01 | 2011-12-01
GI | GEN-2006-010 | [9 empty] | OKAY 138/69KV TRANSFORMER CKT 1 | U | AEPW | AEPW | SARK | SARK | 1 | 507428 | OKAY 4 138.00 | 507427 | OKAY 2 69.000 | 507442 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | OKAY 138/69KV TRANSFORMER CKT 1 | Replace three single-phase 115-69kV autotransformers with one 90 MVA, three-phase 138-69kV autotransformer and convert high side of station to 138kV. | [13 empty] | 2007-10-01 | [39 empty] | 2011-12-01 | 2011-12-01
GI | ASGI-2010-006 | [9 empty] | Osage - Shidler 138kV | U |  |  |  |  | 0 | 301369 |  | 510403 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | Osage - Shidler 138kV | Osage Substation:Replace Shidler 138kV line terminal primary and redundant relaying with SEL uProcessor based relays, install 3-138kV PTs, Install 1-138kV CB, Install metering, Install 2000A line Trap | [13 empty] | 2012-01-15 | [39 empty] | 2014-01-15 | 2014-01-15
GI | ASGI-2010-006 | [9 empty] | Pawnee 138 kV | U |  |  |  |  | 0 | 300139 |  | 512749 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | GRDA | Pawnee 138 kV | New three breaker ring bus on the Cleveland-Stillwater 138kV line near Pawnee. Station will have terminals to Cleveland, Stillwater, and Fairfax. | [13 empty] | 2011-06-15 | [39 empty] | 2014-06-30 | 2014-06-01 | 2014-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T1135020SP | TO->FROM | PCA INTERCHANGE - QUAHADA 3115.00 115KV CKT 1 | EXP | SPS | SPS | SPS-HOBB | SPS-PECO | 0 | 528394 | QUAHADA 3115.00 | 527930 | PCA 3115.00 | 0 |  | 1 | 20SP | 139 | 160 | 0 | 112.1 | 112.1168 | 105.6115 | [7 empty] | CATEGORYB | SINGLE | HOBBS - KIOWA 7345.00 345KV CKT 1 | 0 | 527896 | HOBBS_INT 7345.00 | 527965 | KIOWA 7345.00 | 0 |  | 1 |  |  |  | SPS | PCA Interchange - Quahada 115 kV Ckt 1 | Rebuild of the PCA Interchange and Quahada 115kV line. | [53 empty] | 2017-06-01 | 2017-06-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3165525SP | TO->FROM | PCA INTERCHANGE - QUAHADA 3115.00 115KV CKT 1 | EXP | SPS | SPS | SPS-HOBB | SPS-PECO | 0 | 528394 | QUAHADA 3115.00 | 527930 | PCA 3115.00 | 0 |  | 1 | 25SP | 139 | 160 | 0 |  | -999 | 122.186 | [7 empty] | CATEGORYB | SINGLE | HOBBS - KIOWA 7345.00 345KV CKT 1 | 0 | 527896 | HOBBS_INT 7345.00 | 527965 | KIOWA 7345.00 | 0 |  | 1 |  |  |  | SPS | PCA Interchange - Quahada 115 kV Ckt 1 | Rebuild of the PCA Interchange and Quahada 115kV line. | [53 empty] | 2017-06-01 | 2017-06-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3325525SP | FROM->TO | PECOS INTERCHANGE (WH BCS15041) 230/115/13.2KV TRANSFORMER CKT 1 | REL | SPS | SPS | SPS-PECO | SPS-PECO | 2 | 528179 | PECOS 6230.00 | 528178 | PECOS 3115.00 | 528176 | PECOS_TR1 113.200 | 1 | 25SP | 168 | 168 | 0 |  | -999 | 110.5979 | [7 empty] | CATEGORYB | SINGLE | HOBBS - KIOWA 7345.00 345KV CKT 1 | 0 | 527896 | HOBBS_INT 7345.00 | 527965 | KIOWA 7345.00 | 0 |  | 1 |  |  |  | SPS | PECOS INTERCHANGE (WH BCS15041) 230/115/13.2KV TRANSFORMER CKT 1 | Replace Transformer to at least 186 MVA | [12 empty] | 5778860 | 2015-04-13 | [39 empty] | 2021-06-01 | 2021-06-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3305525SP | FROM->TO | POTASH JUNCTION INTERCHANGE (UPDATE LATER) 230/115/13.2KV TRANSFORMER CKT 1 | REL | SPS | SPS | SPS-PECO | SPS-PECO | 1 | 527963 | POTASH_JCT 6230.00 | 527962 | POTASH_JCT 3115.00 | 527958 | POTASH_TR1 113.200 | 1 | 25SP | 250 | 288 | 0 |  | -999 | 113.4907 | [7 empty] | CATEGORYB | SINGLE | HOBBS - KIOWA 7345.00 345KV CKT 1 | 0 | 527896 | HOBBS_INT 7345.00 | 527965 | KIOWA 7345.00 | 0 |  | 1 |  |  |  | SPS | POTASH JUNCTION INTERCHANGE (UPDATE LATER) 230/115/13.2KV TRANSFORMER CKT 1 | Replace Transformer to at least 327 MVA | [12 empty] | 5778860 | 2015-04-13 | [39 empty] | 2021-06-01 | 2021-06-01
GI | GEN-2010-057 | [9 empty] | Rice - Circle 230 kV Ckt 1 (MIDW portion) | U | WERE | MIDW |  |  | 0 | 530686 | RICECO 230.00 | 532871 | CIRCLE 6 230.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MIDW | Rice - Circle 230 kV Ckt 1 (MIDW portion) | ALL WORK REQUIRED TO CONVERT RICE - CIRCLE 115KV TO 230KV OPERATION. INCLUDES NEW 230KV 3 BREAKER RING BUS, AN EXTENSION OF THE 230KV FROM CURRENT RICE STATION TO NEW RICE SUBSTATION, AND ANY ADDITIONAL WORK REQUIRED FOR THE CONVERSION. | [13 empty] | 2011-12-27 | [39 empty] | 2012-11-07 | 2012-11-07
GI | GEN-2010-057 | [9 empty] | Rice - Circle 230 kV Ckt 1 (WR portion) | U | WERE | MIDW |  |  | 0 | 530686 | RICECO 230.00 | 532871 | CIRCLE 6 230.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MIDW | Rice - Circle 230 kV Ckt 1 (WR portion) | Install necessary equipment and perform line work at Circle substation to accommodate new bus position. | [13 empty] | 2012-01-15 | [39 empty] | 2012-11-29 | 2012-11-29
GI | GEN-2010-057 | [9 empty] | Rice - Lyons 115 kV Ckt 1 | U | MIDW | WERE |  |  | 0 | 530623 | RICE 3 115.00 | 530620 | LYONS 3 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MIDW | Rice - Lyons 115 kV Ckt 1 | Rebuild and extend 115 kV transmission line from existing Rice Co. substation to new Rice Co. substation, including engineering, surveying, and modification of existing easements as required. | [13 empty] | 2011-12-27 | [39 empty] | 2013-04-01 | 2013-04-01
GI | GEN-2010-057 | [9 empty] | Rice County 230/115 kV transformer Ckt 1 | U | MIDW | MIDW |  |  | 1 | 530686 | RICECO 230.00 | 530623 | RICE 3 115.00 | 530687 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MIDW | Rice County 230/115 kV transformer Ckt 1 | Install 230/115 kV transformer at Rice County. | [13 empty] | 2011-12-27 | [39 empty] | 2012-10-01 | 2012-10-01
2007-AG3 | AFS-9 | [9 empty] | RIVER ROAD - SAWYER 115KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | RIVER ROAD - SAWYER 115KV CKT 1 | Rebuild line | [53 empty] | 2009-12-01 | 2013-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T2845025SP | TO->FROM | SAND DUNES SUB - WIPP SUB 115KV CKT 1 | REL | SPS | SPS | SPS-PECO | SPS-PECO | 0 | 528009 | WIPP 3115.00 | 528016 | SAND_DUNES 3115.00 | 0 |  | 1 | 25SP | 159 | 160 | 0 | 100.3 | 100.3455 | 100.3506 | [7 empty] | CATEGORYB | SINGLE | KIOWA 7345.00 - RDRUNNER 7345.00 345KV CKT 1 | 0 | 527965 | KIOWA 7345.00 | 528027 | RDRUNNER 7345.00 | 0 |  | 1 |  |  |  | SPS | SAND DUNES SUB - WIPP SUB 115KV CKT 1 | Rebuild 5.63 miles of line | [53 empty] | 2021-06-01 | 2021-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T6145525SP | FROM->TO | SHELDON - SW7&BENNET7 115.00 115KV CKT 1 | S | NPPD | LES | NPPD_686 | LES_696 | 0 | 640278 | SHELDON7 115.00 | 650244 | SW7&BENNET7 115.00 | 0 |  | 1 | 25SP | 240 | 240 | 348 | 96 | 96.0242 | 101.8145 | [7 empty] | CATEGORYB | SINGLE | SHELDON - SW7TH & PLEASANT HILL 115KV CKT 1 | 0 | 640278 | SHELDON7 115.00 | 650242 | FOLSM&PHIL7 115.00 | 0 |  | 1 |  |  |  | NPPD | SHELDON - SW7&BENNET7 115.00 115KV CKT 1 | Terminal Equipment | [12 empty] | 324585 | 2015-04-22 | [39 empty] | 2021-06-01 | 2021-06-01
GI | ASGI-2010-006 | [9 empty] | Shidler 138 kV | U |  |  |  |  | 0 | 510403 |  | 301369 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | Shidler 138 kV | 138kV four (4) Breaker ring-bus including 138kV transmission line terminal to KAMO's Remington 138kV Substation, replace grounding switch with circuit switcher , move OGE's Osage 138kV line terminal, replace relay panels on OGE's Osage and Mound Road 138kV line terminals, metering, and associated equipment. | [13 empty] | 2011-07-28 | [39 empty] | 2014-02-08 | 2014-02-08
GI | GEN-2003-004 | [9 empty] | Southwestern Station - Washita 138kV Ckt 1 | U |  |  |  |  | 0 | 521089 |  | 511477 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WFEC | Southwestern Station - Washita 138kV Ckt 1 | Expand Washita Switch Station from a 4-breaker to a 5-breaker 138kV ring bus & Construct 2.75 mile 138kV Transmission Line to the AEP/PSO Southwestern Station | [53 empty] | 2005-10-01 | 2005-10-01
GI | GEN-2003-004 | [9 empty] | Southwestern Station - Washita 138kV Ckt 1 (AEP) | U |  |  |  |  | 0 | 521089 |  | 511477 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | Southwestern Station - Washita 138kV Ckt 1 (AEP) | Expand Southwestern Station for termination of WFEC 2.75 mile 138kV Transmission Line from Washita Switch Station | [53 empty] | 2005-10-01 | 2005-10-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T155520SP | FROM->TO | STILLWATER KINZIE (KINAUTO1) 138/69/13.8KV TRANSFORMER CKT 1 | REL | GRDA | GRDA | GRDA-COW | GRDA-COW | 2 | 512710 | KINZEGR4 138.00 | 512713 | KINZEGR2 69.000 | 512811 | KINZIE 13.800 | 1 | 20SP | 56 | 70 | 0 | 104.2 | 104.228 | 104.2118 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | GRDA | STILLWATER KINZIE (KINAUTO1) 138/69/13.8KV TRANSFORMER CKT 1 | Replace Stillwater Kinzie Transformer with 112/140 unit | [53 empty] | 2017-06-01 | 2019-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T155520SP | FROM->TO | STILLWATER KINZIE (KINAUTO1) 138/69/13.8KV TRANSFORMER CKT 1 | REL | GRDA | GRDA | GRDA-COW | GRDA-COW | 2 | 512710 | KINZEGR4 138.00 | 512713 | KINZEGR2 69.000 | 512811 | KINZIE 13.800 | 1 | 20SP | 56 | 70 | 0 | 104.2 | 104.228 | 104.2118 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | GRDA | STILLWATER KINZIE (KINAUTO1) 138/69/13.8KV TRANSFORMER CKT 1 | Replace Stillwater Kinzie Transformer with 112/140 unit | [53 empty] | 2017-06-01 | 2019-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T255525SP | FROM->TO | STILLWATER KINZIE (KINAUTO1) 138/69/13.8KV TRANSFORMER CKT 1 | REL | GRDA | GRDA | GRDA-COW | GRDA-COW | 2 | 512710 | KINZEGR4 138.00 | 512713 | KINZEGR2 69.000 | 512811 | KINZIE 13.800 | 1 | 25SP | 56 | 70 | 0 | 128.3 | 128.3189 | 128.3137 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | GRDA | STILLWATER KINZIE (KINAUTO1) 138/69/13.8KV TRANSFORMER CKT 1 | Replace Stillwater Kinzie Transformer with 112/140 unit | [53 empty] | 2017-06-01 | 2019-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T255525SP | FROM->TO | STILLWATER KINZIE (KINAUTO1) 138/69/13.8KV TRANSFORMER CKT 1 | REL | GRDA | GRDA | GRDA-COW | GRDA-COW | 2 | 512710 | KINZEGR4 138.00 | 512713 | KINZEGR2 69.000 | 512811 | KINZIE 13.800 | 1 | 25SP | 56 | 70 | 0 | 128.3 | 128.3189 | 128.3137 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | GRDA | STILLWATER KINZIE (KINAUTO1) 138/69/13.8KV TRANSFORMER CKT 1 | Replace Stillwater Kinzie Transformer with 112/140 unit | [53 empty] | 2017-06-01 | 2019-06-01
2005-AG2 | AFS-3 | [9 empty] | SUB 110 - ORONOGO JCT. - SUB 167 - RIVERTON 161KV CKT 1 | U | EMDE | EMDE |  |  | 0 | 547469 | RIV167 5 161 | 547467 | ORO110 5 161 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | EMDE | SUB 110 - ORONOGO JCT. - SUB 452 - RIVERTON 161KV CKT 1 | Reconductor Oronogo 59467 to Riverton 59469 with Bundled 556 ACSR | [53 empty] | 2011-06-01 | 2011-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T16315525SP | TO->FROM | SUB 1221 - SUB 1255 161KV CKT 1 | EXP | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 646255 | S1255 5 161.00 | 646221 | S1221 5 161.00 | 0 |  | 1 | 25SP | 352 | 352 | 352 | 102.1 | 102.13 | 105.2823 | [7 empty] | CATEGORYB | SINGLE | SUB 3459 (S3459 T3) 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 645459 | S3459 3 345.00 | 646209 | S1209 5 161.00 | 648259 | S3459T39 13.800 | 1 |  |  |  | OPPD | S3459 345/161 kV Transformer | Install a new 345/161 kV transformer at S3459. Install any necessary 161 kV terminal equipment. | [53 empty] | 2021-06-01 | 2021-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T6315525SP | TO->FROM | SUB 1221 - SUB 1255 161KV CKT 1 | EXP | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 646255 | S1255 5 161.00 | 646221 | S1221 5 161.00 | 0 |  | 1 | 25SP | 352 | 352 | 352 | 103.1 | 103.1114 | 105.039 | [7 empty] | CATEGORYB | SINGLE | SUB 1233 - SUB 1255 161KV CKT 1 | 0 | 646233 | S1233 5 161.00 | 646255 | S1255 5 161.00 | 0 |  | 1 |  |  |  | OPPD | S3459 345/161 kV Transformer | Install a new 345/161 kV transformer at S3459. Install any necessary 161 kV terminal equipment. | [53 empty] | 2021-06-01 | 2021-06-01
GI | GEN-2006-010 | [9 empty] | SUGAR HILL - TURK 138KV CKT 1 | U | AEPW | AEPW | SARK | TEXARK | 0 | 507454 | TURK 4 138.00 | 508080 | SUGARHL4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | SUGAR HILL - TURK 138KV CKT 1 | Build new 24 mile Turk - Sugar Hill 138 kV line and add Sugar Hill 138 kV terminal. | [13 empty] | 2007-10-01 | [39 empty] | 2010-12-16 | 2010-12-16 | 2010-12-01
2015-AG1 | AFS2 | CONT-0613 - Summit 230-115kV XFMR | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T8785516SP | FROM->TO | SUMMIT (SUMM TX-2) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE | WERE | WEST | WEST | 2 | 532873 | SUMMIT 6 230.00 | 533381 | SUMMIT 3 115.00 | 532896 | SUMIT2 1 13.800 | 1 | 16SP | 239 | 239 | 0 | 103.9 | 103.9374 | 107.1342 | [7 empty] | CATEGORYB | SINGLE | SUMMIT (SUMM TX-3) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532873 | SUMMIT 6 230.00 | 533381 | SUMMIT 3 115.00 | 532897 | SUMIT3 1 13.800 | 1 |  |  |  | WERE | Multi - Geary County 345/115 kV and Geary - Chapman 115 kV | Build new Geary County 345/115 kV substation south of Junction City where JEC-Summit and McDowell Creek-Junction City #2 ckt separate. Construct new Geary County - Chapman 115 kV line. | [53 empty] | 2016-06-01 | 2018-06-01
2015-AG1 | AFS2 | CONT-0613 - Summit 230-115kV XFMR | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T14395525SP | FROM->TO | SUMMIT (SUMM TX-2) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE | WERE | WEST | WEST | 2 | 532873 | SUMMIT 6 230.00 | 533381 | SUMMIT 3 115.00 | 532896 | SUMIT2 1 13.800 | 1 | 25SP | 239 | 239 | 0 | 95.1 | 95.0501 | 101.5367 | [7 empty] | CATEGORYB | SINGLE | SUMMIT (SUMM TX-3) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532873 | SUMMIT 6 230.00 | 533381 | SUMMIT 3 115.00 | 532897 | SUMIT3 1 13.800 | 1 |  |  |  | WERE | Multi - Geary County 345/115 kV and Geary - Chapman 115 kV | Build new Geary County 345/115 kV substation south of Junction City where JEC-Summit and McDowell Creek-Junction City #2 ckt separate. Construct new Geary County - Chapman 115 kV line. | [53 empty] | 2016-06-01 | 2018-06-01
2015-AG1 | AFS2 | CONT-0613 - Summit 230-115kV XFMR | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T8775516SP | FROM->TO | SUMMIT (SUMM TX-3) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE | WERE | WEST | WEST | 2 | 532873 | SUMMIT 6 230.00 | 533381 | SUMMIT 3 115.00 | 532897 | SUMIT3 1 13.800 | 1 | 16SP | 239 | 239 | 0 | 104.2 | 104.1519 | 107.3518 | [7 empty] | CATEGORYB | SINGLE | SUMMIT (SUMM TX-2) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532873 | SUMMIT 6 230.00 | 533381 | SUMMIT 3 115.00 | 532896 | SUMIT2 1 13.800 | 1 |  |  |  | WERE | Multi - Geary County 345/115 kV and Geary - Chapman 115 kV | Build new Geary County 345/115 kV substation south of Junction City where JEC-Summit and McDowell Creek-Junction City #2 ckt separate. Construct new Geary County - Chapman 115 kV line. | [53 empty] | 2016-06-01 | 2018-06-01
2015-AG1 | AFS2 | CONT-0613 - Summit 230-115kV XFMR | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T14385525SP | FROM->TO | SUMMIT (SUMM TX-3) 230/115/13.8KV TRANSFORMER CKT 1 | EXP | WERE | WERE | WEST | WEST | 2 | 532873 | SUMMIT 6 230.00 | 533381 | SUMMIT 3 115.00 | 532897 | SUMIT3 1 13.800 | 1 | 25SP | 239 | 239 | 0 | 95.3 | 95.2529 | 101.756 | [7 empty] | CATEGORYB | SINGLE | SUMMIT (SUMM TX-2) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532873 | SUMMIT 6 230.00 | 533381 | SUMMIT 3 115.00 | 532896 | SUMIT2 1 13.800 | 1 |  |  |  | WERE | Multi - Geary County 345/115 kV and Geary - Chapman 115 kV | Build new Geary County 345/115 kV substation south of Junction City where JEC-Summit and McDowell Creek-Junction City #2 ckt separate. Construct new Geary County - Chapman 115 kV line. | [53 empty] | 2016-06-01 | 2018-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T2685025SP | FROM->TO | SUNDOWN INTERCHANGE (WH XDS70381) 230/115/13.8KV TRANSFORMER CKT 1 | REL | SPS | SPS | SPS-CNPL | SPS-CNPL | 1 | 526435 | SUNDOWN 6230.00 | 526434 | SUNDOWN 3115.00 | 526432 | SUNDOWN_TR1113.800 | 1 | 25SP | 187 | 187 | 0 | 106.3 | 106.3271 | 104.6096 | [7 empty] | CATEGORYB | SINGLE | LEA COUNTY REC-PLAINS INTERCHANGE - YOAKUM COUNTY INTERCHANGE 115KV CKT 1 | 0 | 526928 | LE-PLNSINT 3115.00 | 526934 | YOAKUM 3115.00 | 0 |  | 1 |  |  |  | SPS | SUNDOWN INTERCHANGE (WH XDS70381) 230/115/13.8KV TRANSFORMER CKT 1 | Increase Sundown 230/115 kV transformer to 250 MVA | [53 empty] | 2021-06-01 | 2021-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T2305025SP | FROM->TO | SUNDOWN INTERCHANGE (WH XDS70381) 230/115/13.8KV TRANSFORMER CKT 1 | REL | SPS | SPS | SPS-CNPL | SPS-CNPL | 1 | 526435 | SUNDOWN 6230.00 | 526434 | SUNDOWN 3115.00 | 526432 | SUNDOWN_TR1113.800 | 1 | 25SP | 187 | 187 | 0 | 103.6 | 103.6053 | 101.2092 | [7 empty] | CATEGORYB | SINGLE | HOCKLEY COUNTY INTERCHANGE - LAMB COUNTY INTERCHANGE 115KV CKT 1 | 0 | 525636 | LAMB_CNTY 3115.00 | 526020 | HOCKLEY 3115.00 | 0 |  | 1 |  |  |  | SPS | SUNDOWN INTERCHANGE (WH XDS70381) 230/115/13.8KV TRANSFORMER CKT 1 | Increase Sundown 230/115 kV transformer to 250 MVA | [53 empty] | 2021-06-01 | 2021-06-01
GI | GEN-2011-040 | [9 empty] | Sunnyside to tap on Pooleville - Ratliff 138kV Ckt 1 | U |  |  |  |  | 0 | 515561 |  | 515135 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OKGE | Sunnyside to tap on Pooleville - Ratliff 138kV Ckt 1 | Rebuild 0.75 mi of 138kV Transmission Line DBL CKT | [53 empty] | 2014-06-30 | 2014-06-01 | 2014-06-01
2009-AGP2 | AFS-6 | [9 empty] | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | U | WFEC | WFEC | AEP-OP | AEP-OP | 2 | 521065 | TALOGA 4 138.00 | 521064 | TALOGA 2 69.000 | 521178 | TLGTERT 13.800 | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WFEC | TALOGA (TALOGA) 138/69/13.8KV TRANSFORMER CKT 1 | Auto XFMR 56 to 112MVA | 112 | 112 | 112 | 112 |  | 24 | 24 | [46 empty] | 2010-10-01 | 2013-06-01
NA | SPONSORED | [9 empty] | TATONGA - WOODWARD 345KV CKT 1 | U | OKGE | OKGE | ENID | ENID | 0 | 515407 |  | 515375 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OKGE | TATONGA - WOODWARD 345KV CKT 1 | Build 345 kV line | [53 empty] | 2010-01-01 | 2010-01-01 | 2009-12-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T10985520SP | FROM->TO | TUCO INTERCHANGE (GE M102345) 230/115/13.2KV TRANSFORMER CKT 1 | CP | SPS | SPS | SPS-CNPL | SPS-CNPL | 1 | 525830 | TUCO_INT 6230.00 | 525828 | TUCO_INT 3115.00 | 525821 | TUCO_TR4 113.200 | 1 | 20SP | 242 | 252 | 0 | 102.6 | 102.6044 | 106.8802 | [7 empty] | CATEGORYB | SINGLE | TUCO INTERCHANGE (ENRCO 136401) 230/115/13.2KV TRANSFORMER CKT 2 | 1 | 525828 | TUCO_INT 3115.00 | 525830 | TUCO_INT 6230.00 | 525819 | TUCO_TR3 113.200 | 2 |  |  |  | SPS | TUCO INTERCHANGE (GE M102345) 230/115/13.2KV TRANSFORMER CKT 1 Accelerate | Replace 1st 230/115 kV transformer at Tuco with 230/115 kV 288 MVA transformer. | [53 empty] | 2017-06-01 | 2018-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T13405525SP | FROM->TO | TUCO INTERCHANGE (GE M102345) 230/115/13.2KV TRANSFORMER CKT 1 | CP | SPS | SPS | SPS-CNPL | SPS-CNPL | 1 | 525830 | TUCO_INT 6230.00 | 525828 | TUCO_INT 3115.00 | 525821 | TUCO_TR4 113.200 | 1 | 25SP | 242 | 252 | 0 | 106.1 | 106.0539 | 114.1393 | [7 empty] | CATEGORYB | SINGLE | TUCO INTERCHANGE (ENRCO 136401) 230/115/13.2KV TRANSFORMER CKT 2 | 1 | 525828 | TUCO_INT 3115.00 | 525830 | TUCO_INT 6230.00 | 525819 | TUCO_TR3 113.200 | 2 |  |  |  | SPS | TUCO INTERCHANGE (GE M102345) 230/115/13.2KV TRANSFORMER CKT 1 Accelerate | Replace 1st 230/115 kV transformer at Tuco with 230/115 kV 288 MVA transformer. | [53 empty] | 2017-06-01 | 2018-06-01
GI | GEN-2006-010 | [9 empty] | TURK 138/115KV TRANSFORMER CKT 1 | U | AEPW |  | SARK |  | 1 | 507454 | TURK 4 138.00 | 507456 | HEMPSTD3 115.00 | 507458 | HEMP1 1 13.800 | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | TURK 138/115KV TRANSFORMER CKT 1 | Build Turk 138-115 kV station and relocate autotransformer (and spare) from Patterson to this new Turk station | [13 empty] | 2007-10-01 | [39 empty] | 2011-12-01 | 2011-12-01
GI | GEN-2010-051 | [9 empty] | Twin Church - Dixon County 230kV Line Upgrade | U |  |  |  |  | 0 | 560347 |  | 640386 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | NPPD | Twin Church - Dixon County 230kV Line Upgrade | Increase clearances to accommodate 320MVA facility rating | [53 empty] | 2015-10-24 | 2015-10-24
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T8665516SP | FROM->TO | WICHITA (WICH TX-12) 345/138/13.8KV TRANSFORMER CKT 1 | EXP | WERE | WERE | SCENTRAL | SCENTRAL | 1 | 532796 | WICHITA7 345.00 | 533040 | EVANS N4 138.00 | 532830 | WICH12 1 13.800 | 1 | 16SP | 400 | 430 | 0 |  | 63.9559 | 101.604 | [7 empty] | CATEGORYB | SINGLE | WICHITA (WICH TX-11) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532796 | WICHITA7 345.00 | 533040 | EVANS N4 138.00 | 532829 | WICH11 1 13.800 | 1 |  |  |  | WERE | Multi - Viola 345/138kV Transformer and 138 kV Lines to Clearwater and Gill | Install 345/138 kV transformer at future Viola 345 kV substation. Build 138kV line from Viola to Clearwater substation. Build 138 kV line from Viola to Gill substation | [53 empty] | 2016-06-01 | 2019-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3975516WP | FROM->TO | WICHITA (WICH TX-12) 345/138/13.8KV TRANSFORMER CKT 1 | EXP | WERE | WERE | SCENTRAL | SCENTRAL | 1 | 532796 | WICHITA7 345.00 | 533040 | EVANS N4 138.00 | 532830 | WICH12 1 13.800 | 1 | 16WP | 400 | 430 | 0 | 101.7 | 101.6563 | 102.1051 | [7 empty] | CATEGORYB | SINGLE | WICHITA (WICH TX-11) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532796 | WICHITA7 345.00 | 533040 | EVANS N4 138.00 | 532829 | WICH11 1 13.800 | 1 |  |  |  | WERE | Multi - Viola 345/138kV Transformer and 138 kV Lines to Clearwater and Gill | Install 345/138 kV transformer at future Viola 345 kV substation. Build 138kV line from Viola to Clearwater substation. Build 138 kV line from Viola to Gill substation | [53 empty] | 2016-06-01 | 2019-06-01
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T2445025SP | FROM->TO | WOLFFORTH INTERCHANGE (WH 7001668) 230/115/13.2KV TRANSFORMER CKT 1 | REL | SPS | SPS | SPS-CNPL | SPS-CNPL | 1 | 526525 | WOLFFORTH 6230.00 | 526524 | WOLFFORTH 3115.00 | 526522 | WOLFRTH_TR1113.200 | 1 | 25SP | 120 | 154 | 0 | 119.7 | 119.731 | 114.345 | [7 empty] | CATEGORYB | SINGLE | CARLISLE INTERCHANGE - LP-DOUD_TP 3115.00 115KV CKT 1 | 0 | 526160 | CARLISLE 3115.00 | 526162 | LP-DOUD_TP 3115.00 | 0 |  | 1 |  |  |  | SPS | WOLFFORTH INTERCHANGE (WH 7001668) 230/115/13.2KV TRANSFORMER CKT 1 | Upgrade transformer to 250 MVA. | [53 empty] | 2021-06-01 | 2021-06-01
NA | SPONSORED | [9 empty] | WOODWARD - IODINE 138KV CKT 1 | U | OKGE | OKGE | ENID | ENID | 0 | 515376 |  | 514796 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OKGE | WOODWARD - IODINE 138KV CKT 1 | Tap Iodine to Woodward 138 kV line | [53 empty] | 2010-01-01 | 2010-01-01 | 2009-12-01
NA | SPONSORED | [9 empty] | WOODWARD - WOODWARD EHV 138KV CKT 1 | U | OKGE | OKGE | ENID | ENID | 0 | 515376 |  | 514785 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OKGE | WOODWARD - WOODWARD EHV 138KV CKT 1 | Build .5 miles of 138 kV and install terminal equipment | [53 empty] | 2010-01-01 | 2010-01-01 | 2009-12-01
NA | SPONSORED | [9 empty] | WOODWARD - WOODWARD EHV 138KV CKT 2 | U | OKGE | OKGE | ENID | ENID | 0 | 515376 |  | 514785 |  |  |  | 2 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OKGE | WOODWARD - WOODWARD EHV 138KV CKT 2 | Build .5 miles of 138 kV and install terminal equipment | [53 empty] | 2010-01-01 | 2010-01-01 | 2009-12-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T1855520SP | FROM->TO | WOODWARD (WOODWRD2) 138/69/13.2KV TRANSFORMER CKT 1 | EXP | OKGE | OKGE | ENID | ENID | 1 | 514785 | WOODWRD4 138.00 | 514782 | WODWRD 2 69.000 | 515771 | WOODWR21 13.200 | 1 | 20SP | 123 | 134 | 0 |  | 71.563 | 101.5306 | [7 empty] | CATEGORYB | SINGLE | FPL SWITCH - MOORELAND 138KV CKT 1 | 0 | 515785 | WINDFRM4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 |  |  |  | OKGE | Multi - Woodward District EHV - Tatonga - Matthewson - Cimarron 345 kV | Build new 126 mile Woodward - Tatonga 345 kV circuit 2 and Tatonga - Matthewson - Cimarron 345 kV line. | [53 empty] | 2015-10-01 | 2021-03-01
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T945520WP | FROM->TO | WOODWARD (WOODWRD2) 138/69/13.2KV TRANSFORMER CKT 1 | EXP | OKGE | OKGE | ENID | ENID | 1 | 514785 | WOODWRD4 138.00 | 514782 | WODWRD 2 69.000 | 515771 | WOODWR21 13.200 | 1 | 20WP | 123 | 134 | 0 |  | 69.4395 | 100.1722 | [7 empty] | CATEGORYB | SINGLE | FPL SWITCH - MOORELAND 138KV CKT 1 | 0 | 515785 | WINDFRM4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 |  |  |  | OKGE | Multi - Woodward District EHV - Tatonga - Matthewson - Cimarron 345 kV | Build new 126 mile Woodward - Tatonga 345 kV circuit 2 and Tatonga - Matthewson - Cimarron 345 kV line. | [53 empty] | 2015-10-01 | 2021-03-01
NA | SPONSORED | [9 empty] | WOODWARD 345/138KV TRANSFORMER CKT 1 | U | OKGE | OKGE | ENID | ENID | 1 | 515375 |  | 515376 |  | 515795 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OKGE | WOODWARD 345/138KV TRANSFORMER CKT 1 | Install 345/138 kV XF | [53 empty] | 2010-01-01 | 2010-01-01 | 2009-12-01

## tblAllFacilityLog<100%
STUDYDES | STUDYDES2 | EVENTTYPE | AssessmentSOLUTIONTYPE | AssessmenFDNS-TERMINATION | SOLUTIONTYPE | FDNS-TERMINATION | GROUP | SCENARIO | FGName | DIRECTION | FacilityName | FacilityUpgradeCode | ModelArea1 | ModelArea2 | FZONENAME | TZONENAME | MONTFLAG | MONTFB | MONTFNAME | MONTTB1 | MONTTNAME1 | MONTTB2 | MONTTNAME2 | MONTCKT | Case | RATEA | RATEB | RATEC | Assessment Loading | BaseCaseLoading | TransferCaseLoading | NameOfBusWithMonitoredVoltage | Assessment Voltage | BaseCaseVoltage | TransferCaseVoltage | VINIT | VMIN | VMAX | CATEGORY | CONTTYPE | CONTNAME | CONTXFMRFLAG | CONTFB | CONTFNAME | CONTTB1 | CONTTNAME1 | CONTTB2 | CONTTNAME2 | CONTCKT | TransmissionProviderCommentsNotes | RequiredRateB | TransmissionOwnerComments | OwnerDesignation | UpgradeName | UpgradeComponentWithinFacility | NewSummerA | NewSummerB | NewOtherA | NewOtherB | DistToConstruct | TotalLead | ConstructionLeadOnly | NewOrConstructWhileEnergized | NewR | NewX | NewB | CommentsRegardingUpgradeRequirements | NewCost | EffDate | NetPlantDate | ReusableEx_GrossValue | ReusableEx_NetValue | Reusable_EndofDepr | SalvageValue | NewCostWhileExpediting | EffDateExpedited | StartDeprExpedited | EndDeprExpedited | NetPlantDateExpedited | ReusableEx_GrossExpedited | ReusableEx_NetExpedited | Reusable_EndofDeprExpedited | SalvageValueExpedited | Generation 1 Owner & Unit (Name) | Generation 1 Redispatch Cost ($) | Generation 1 Redispatch Date (M/D/Y) | Generation 2 Owner & Unit (Name) | Generation 2 Redispatch Cost ($) | Generation 2 Redispatch Date (M/D/Y) | Generation 3 Owner & Unit (Name) | Generation 3 Redispatch Cost ($) | Generation 3 Redispatch Date (M/D/Y) | ActualCompletion | ActualNewCost | ActualNetPlantDate | ActualReusableEx_GrossValue | ActualReusableEx_NetValue | ActualReusable_EndofDepr | ActualSalvageValue | Actual_NewCostWhileExpediting | Actual_StartDeprExp | Actual_EndDeprExp | Actual_NetPlantDateExpedited | ActualReusableEx_GrossExpedited | ActualReusableEx_NetExpedited | ActualReusable_EndofDeprExpedited | Actual_SalvageValueExpedited | SPPReliabilityDate | DUN | EOC | EarliestDate
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T6575016SP | TO->FROM | 4FISHERTP - KEYSTONE DAM 138KV CKT 1 | E | SWPA | AECI | EMINTH | KAMO-OK | 0 | 505610 | KEYSTON4 138.00 | 300131 | 4FISHERTP 138.00 | 0 |  | 1 | 16SP | 174 | 174 | 0 | 98.7 | 98.7351 | 95.2 | [7 empty] | CATEGORYB | SINGLE | SILVCTYGR4 138.00 - SILVER CITY 138KV CKT 1 | 0 | 512726 | SILVCTYGR4 138.00 | 300140 | 4SILVCTY 138.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T10765025SP | TO->FROM | 4FISHERTP - KEYSTONE DAM 138KV CKT 1 | E | SWPA | AECI | EMINTH | KAMO-OK | 0 | 505610 | KEYSTON4 138.00 | 300131 | 4FISHERTP 138.00 | 0 |  | 1 | 25SP | 174 | 174 | 0 | 107.3 | 107.3376 | 99 | [7 empty] | CATEGORYB | SINGLE | SILVCTYGR4 138.00 - SILVER CITY 138KV CKT 1 | 0 | 512726 | SILVCTYGR4 138.00 | 300140 | 4SILVCTY 138.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T1025025SP | TO->FROM | 4FISHERTP - KEYSTONE DAM 138KV CKT 1 | E | SWPA | AECI | EMINTH | KAMO-OK | 0 | 505610 | KEYSTON4 138.00 | 300131 | 4FISHERTP 138.00 | 0 |  | 1 | 25SP | 174 | 174 | 0 | 107.3 | 107.3201 | 98.9 | [7 empty] | CATEGORYB | SINGLE | SILVCTYGR4 138.00 - WEKIWA 138KV CKT 1 | 0 | 509757 | WEKIWA-4 138.00 | 512726 | SILVCTYGR4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T1945525SP | FROM->TO | 4MEMORAL 138.00 - LUTHER 138KV CKT 1 | E | AECI | AECI | KAMO-OK | KAMO-OK | 0 | 300136 | 4MEMORAL 138.00 | 300135 | 4LUTHER 138.00 | 0 |  | 1 | 25SP | 137 | 137 | 0 | 104.7 | 104.742 | 98.8 | [7 empty] | CATEGORYB | SINGLE | KINZE - STILLWATER KINZIE 138KV CKT Z1 | 0 | 512710 | KINZEGR4 138.00 | 515008 | KINZE 4 138.00 | 0 |  | Z1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T20945525SP | FROM->TO | 4MEMORAL 138.00 - LUTHER 138KV CKT 1 | E | AECI | AECI | KAMO-OK | KAMO-OK | 0 | 300136 | 4MEMORAL 138.00 | 300135 | 4LUTHER 138.00 | 0 |  | 1 | 25SP | 137 | 137 | 0 | 104.8 | 104.7859 | 98.7 | [7 empty] | CATEGORYB | NONSINGLE | 3TERM47 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T18235016SP | FROM->TO | 4MER 1&4 138.00 138/16.5KV TRANSFORMER CKT 1 | E | AMMO | AMMO | AMRNMO | AMRNMO | 0 | 345132 | 1MER 1 16.500 | 345123 | 4MER 1&4 138.00 | 0 |  | 1 | 16SP | 150 | 150 | 150 |  | 98.788 | 98.788 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 26 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T19945516SP | FROM->TO | 4MER 1&4 138.00 138/16.5KV TRANSFORMER CKT 1 | E | AMMO | AMMO | AMRNMO | AMRNMO | 0 | 345132 | 1MER 1 16.500 | 345123 | 4MER 1&4 138.00 | 0 |  | 1 | 16SP | 150 | 150 | 150 |  | 98.788 | 98.7877 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 25 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T23975520SP | FROM->TO | 4MER 1&4 138.00 138/16.5KV TRANSFORMER CKT 1 | E | AMMO | AMMO | AMRNMO | AMRNMO | 0 | 345132 | 1MER 1 16.500 | 345123 | 4MER 1&4 138.00 | 0 |  | 1 | 20SP | 150 | 150 | 150 |  | 98.788 | 98.788 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 27 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T16565020SP | FROM->TO | 4MER 1&4 138.00 138/16.5KV TRANSFORMER CKT 1 | E | AMMO | AMMO | AMRNMO | AMRNMO | 0 | 345132 | 1MER 1 16.500 | 345123 | 4MER 1&4 138.00 | 0 |  | 1 | 20SP | 150 | 150 | 150 |  | 98.788 | 98.788 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 27 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T25215025SP | FROM->TO | 4MER 1&4 138.00 138/16.5KV TRANSFORMER CKT 1 | E | AMMO | AMMO | AMRNMO | AMRNMO | 0 | 345132 | 1MER 1 16.500 | 345123 | 4MER 1&4 138.00 | 0 |  | 1 | 25SP | 150 | 150 | 150 |  | 98.788 | 98.788 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 43 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T25225025SP | FROM->TO | 4MER 1&4 138.00 138/16.5KV TRANSFORMER CKT 1 | E | AMMO | AMMO | AMRNMO | AMRNMO | 0 | 345132 | 1MER 1 16.500 | 345123 | 4MER 1&4 138.00 | 0 |  | 1 | 25SP | 150 | 150 | 150 |  | 98.788 | 98.788 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 44 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T25205025SP | FROM->TO | 4MER 1&4 138.00 138/16.5KV TRANSFORMER CKT 1 | E | AMMO | AMMO | AMRNMO | AMRNMO | 0 | 345132 | 1MER 1 16.500 | 345123 | 4MER 1&4 138.00 | 0 |  | 1 | 25SP | 150 | 150 | 150 |  | 98.788 | 98.788 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 30 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T25195025SP | FROM->TO | 4MER 1&4 138.00 138/16.5KV TRANSFORMER CKT 1 | E | AMMO | AMMO | AMRNMO | AMRNMO | 0 | 345132 | 1MER 1 16.500 | 345123 | 4MER 1&4 138.00 | 0 |  | 1 | 25SP | 150 | 150 | 150 |  | 98.7879 | 98.788 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 29 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T26735525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 97.7 | 97.7136 | 97.7 | [7 empty] | CATEGORYB | GENOUT | GEN303008 1-1BC2 U3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T26715525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 97.5 | 97.5282 | 97.6 | [7 empty] | CATEGORYB | GENOUT | GEN303006 1-1BC2 U1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T27055525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 97.1 | 97.0581 | 97.1 | [7 empty] | CATEGORYB | GENOUT | GEN336153 1-WATERFORD UNIT#3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T26975525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 96.7 | 96.7308 | 96.8 | [7 empty] | CATEGORYB | GENOUT | GEN335831 1-RIVERBEND UNIT#1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T9125525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 96.5 | 96.5407 | 96.6 | [7 empty] | CATEGORYB | SINGLE | COLY - MCKNIGHT 500KV CKT 1 | 0 | 335836 | 8MCKNT 500.00 | 335837 | 8COLY 5 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T23665525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 96.2 | 96.234 | 96.3 | [7 empty] | CATEGORYB | NONSINGLE | L015 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T8965525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 96.2 | 96.2341 | 96.3 | [7 empty] | CATEGORYB | SINGLE | WATERFORD - WILLOW GLEN 500KV CKT 1 | 0 | 335618 | 8WGLEN 500.00 | 336150 | 8WATERFO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T27165525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 96.1 | 96.1364 | 96.2 | [7 empty] | CATEGORYB | GENOUT | GEN336252 1-NINEMILE POINT UNIT#5 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T9445525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 96.1 | 96.0818 | 96.1 | [7 empty] | CATEGORYB | SINGLE | BAXTER WILSON SES - GRAND GULF 500KV CKT 1 | 0 | 336820 | 8G.GULF 500.00 | 336830 | 8B.WLSN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T9405525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 96.1 | 96.0613 | 96.1 | [7 empty] | CATEGORYB | SINGLE | FRANKLIN - GRAND GULF 500KV CKT 1 | 0 | 336562 | 8FRKLIN 500.00 | 336820 | 8G.GULF 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T8745525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 96.1 | 96.085 | 96.1 | [7 empty] | CATEGORYB | SINGLE | WEBRE - WELLS 500KV CKT 1 | 0 | 335368 | 8WELLS 500.00 | 335500 | 8WEBRE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T27145525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 96.1 | 96.1165 | 96.1 | [7 empty] | CATEGORYB | GENOUT | GEN336251 1-NINEMILE POINT UNIT#4 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T10815525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 96.1 | 96.0753 | 96.1 | [7 empty] | CATEGORYB | SINGLE | BAYOU SALE - WAXLAKE 138KV CKT 1 | 0 | 500050 | BSALES 4 138.00 | 500890 | WAXLAKE4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T8845525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 95.9 | 95.9246 | 96 | [7 empty] | CATEGORYB | SINGLE | 6MEAUX - SELLRD 230KV CKT 1 | 0 | 335381 | 6MEAUX 230.00 | 500776 | SELLRD6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T27105525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 96 | 95.9509 | 96 | [7 empty] | CATEGORYB | GENOUT | GEN336191 1-LITTLE GYPSY UNIT#3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T8795525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 95.9 | 95.924 | 96 | [7 empty] | CATEGORYB | SINGLE | 6MEAUX 230/138KV TRANSFORMER CKT 1 | 0 | 335380 | 4MEAUX 138.00 | 335381 | 6MEAUX 230.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T10795525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 96 | 95.9771 | 96 | [7 empty] | CATEGORYB | SINGLE | BAYOU SALE - TECHE 138KV CKT 1 | 0 | 500050 | BSALES 4 138.00 | 500820 | TECHE 4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T10965525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 95.9 | 95.9296 | 96 | [7 empty] | CATEGORYB | SINGLE | EL PASO TAP - WAXLAKE 138KV CKT 1 | 0 | 500290 | ELPTAP 4 138.00 | 500890 | WAXLAKE4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T9335525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 95.9 | 95.877 | 95.9 | [7 empty] | CATEGORYB | SINGLE | WATERFORD 500/230KV TRANSFORMER CKT 1 | 0 | 336150 | 8WATERFO 500.00 | 336154 | 6WATFRD 230.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T9295525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 95.9 | 95.9065 | 95.9 | [7 empty] | CATEGORYB | SINGLE | BOGALUSA - FRANKLIN 500KV CKT 1 | 0 | 336130 | 8BOGALUS 500.00 | 336562 | 8FRKLIN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T9475525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 95.9 | 95.8989 | 95.9 | [7 empty] | CATEGORYB | SINGLE | BAXTER WILSON SES - RAY BRASWELL SES 500KV CKT 1 | 0 | 336830 | 8B.WLSN 500.00 | 336839 | 8R.BRAS 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T26955525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 95.9 | 95.8863 | 95.9 | [7 empty] | CATEGORYB | GENOUT | GEN335614 1-WILLOW GLENN UNIT#4 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T27205525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 95.9 | 95.877 | 95.9 | [7 empty] | CATEGORYB | GENOUT | GEN336464 1-MICHOUD UNIT #3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T21725525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 95.9 | 95.9056 | 95.9 | [7 empty] | CATEGORYB | NONSINGLE | ADAMS CREEK- | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T24045025SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 95.6 | 95.5707 | 95.6 | [7 empty] | CATEGORYB | GENOUT | GEN303008 1-1BC2 U3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T745525SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 95.4 | 95.3875 | 95.4 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T24025025SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 95.4 | 95.4129 | 95.4 | [7 empty] | CATEGORYB | GENOUT | GEN303006 1-1BC2 U1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T24265025SP | FROM->TO | 8CAJUN2 500/24.0KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303007 | 1BC2 U2 24.000 | 303005 | 8CAJUN2 500.00 | 0 |  | 1 | 25SP | 615 | 615 | 0 | 95.1 | 95.1356 | 95.2 | [7 empty] | CATEGORYB | GENOUT | GEN336153 1-WATERFORD UNIT#3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T11255020WP | FROM->TO | 8OSWALD# 500.00 (KNWRIVL1) 500/13.8/13.8KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI |  | EES_ARK | 2 | 338507 | 1C1KNWRI 13.800 | 338520 | 8OSWALD# 500.00 | 338508 | 1C3KNWRI 13.800 | 1 | 20WP | 235 | 235 | 0 |  | 96.9413 | 97.1 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 9 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T11265020WP | FROM->TO | 8OSWALD# 500.00 (KNWRIVL2) 500/13.8/13.8KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI |  | EES_ARK | 2 | 338509 | 1C5KNWRI 13.800 | 338520 | 8OSWALD# 500.00 | 338510 | 1S1KNWRI 13.800 | 1 | 20WP | 235 | 235 | 0 |  | 96.9413 | 97.1 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 9 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T19935516SP | FROM->TO | 8XMFRINT3 500.00 500/13.8KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303025 | 1S3INTHB 13.800 | 303022 | 8XMFRINT3 500.00 | 0 |  | 1 | 16SP | 130 | 130 | 0 |  | 95.7202 | 96.4101 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 18 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T23905520SP | FROM->TO | 8XMFRINT3 500.00 500/13.8KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303025 | 1S3INTHB 13.800 | 303022 | 8XMFRINT3 500.00 | 0 |  | 1 | 20SP | 130 | 130 | 0 |  | 95.3163 | 95.3164 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 14 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T12225520WP | FROM->TO | 8XMFRINT3 500.00 500/13.8KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303025 | 1S3INTHB 13.800 | 303022 | 8XMFRINT3 500.00 | 0 |  | 1 | 20WP | 130 | 130 | 0 |  | 95.421 | 95.421 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 13 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T15245525WP | FROM->TO | 8XMFRINT3 500.00 500/13.8KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303025 | 1S3INTHB 13.800 | 303022 | 8XMFRINT3 500.00 | 0 |  | 1 | 25WP | 130 | 130 | 0 |  | 95.4063 | 95.4063 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 12 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T19915516SP | FROM->TO | 8XMFRINT4 500.00 500/13.8KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303027 | 1S4INTHB 13.800 | 303023 | 8XMFRINT4 500.00 | 0 |  | 1 | 16SP | 130 | 130 | 0 |  | 95.2335 | 95.2336 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 11 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T23895520SP | FROM->TO | 8XMFRINT4 500.00 500/13.8KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303027 | 1S4INTHB 13.800 | 303023 | 8XMFRINT4 500.00 | 0 |  | 1 | 20SP | 130 | 130 | 0 |  | 95.3163 | 95.3164 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 13 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T12215520WP | FROM->TO | 8XMFRINT4 500.00 500/13.8KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303027 | 1S4INTHB 13.800 | 303023 | 8XMFRINT4 500.00 | 0 |  | 1 | 20WP | 130 | 130 | 0 |  | 95.421 | 95.421 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 12 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T27825525SP | FROM->TO | 8XMFRINT4 500.00 500/13.8KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303027 | 1S4INTHB 13.800 | 303023 | 8XMFRINT4 500.00 | 0 |  | 1 | 25SP | 130 | 130 | 0 |  | 95.2876 | 95.2872 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 20 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T27765525SP | FROM->TO | 8XMFRINT4 500.00 500/13.8KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303027 | 1S4INTHB 13.800 | 303023 | 8XMFRINT4 500.00 | 0 |  | 1 | 25SP | 130 | 130 | 0 |  | 95.2838 | 95.2839 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 13 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T15235525WP | FROM->TO | 8XMFRINT4 500.00 500/13.8KV TRANSFORMER CKT 1 | E | LAGN | LAGN | LAGN_NATIVE | LAGN_NATIVE | 0 | 303027 | 1S4INTHB 13.800 | 303023 | 8XMFRINT4 500.00 | 0 |  | 1 | 25WP | 130 | 130 | 0 |  | 95.4063 | 95.4063 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 11 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T1325525SP | TO->FROM | ADORA REC - ADORA T 69KV CKT 1 | E | AEPW | AEPW | MT. PLEASANT | MT PLES NTEC | 0 | 508285 | ADORA T2 69.000 | 508284 | ADORA 2 69.000 | 0 |  | 1 | 25SP | 76 | 76 | 0 |  | 94.7874 | 95.7 | [7 empty] | CATEGORYB | SINGLE | K37 - PITTSBURG 138KV CKT 1 | 0 | 508313 | PITTSB_4 138.00 | 508368 | SCROGNSSW4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2135525SP | TO->FROM | AGENCY - PECAN CREEK 161KV CKT 1 | E | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515234 | PECANCK5 161.00 | 515230 | AGENCY 5 161.00 | 0 |  | 1 | 25SP | 313 | 335 | 0 | 96.9 | 96.8674 | 96.2 | [7 empty] | CATEGORYB | SINGLE | 5 TRIBES - PECAN CREEK 161KV CKT 1 | 0 | 515228 | 5TRIBES5 161.00 | 515234 | PECANCK5 161.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T20515520SP | TO->FROM | AINSWORTH - AINSWORTH 115KV CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640050 | AINSWND7 115.00 | 640051 | AINSWRT7 115.00 | 0 |  | 1 | 20SP | 120 | 120 | 132 | 96.1 | 96.0753 | 99.9 | [7 empty] | CATEGORYB | NONSINGLE | DAK11WAPAB2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T24355520SP | TO->FROM | AINSWORTH - AINSWORTH 115KV CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640050 | AINSWND7 115.00 | 640051 | AINSWRT7 115.00 | 0 |  | 1 | 20SP | 120 | 120 | 132 |  | 96.1411 | 99.9 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 161 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T5865520SP | TO->FROM | AINSWORTH - AINSWORTH 115KV CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640050 | AINSWND7 115.00 | 640051 | AINSWRT7 115.00 | 0 |  | 1 | 20SP | 120 | 120 | 132 | 96.1 | 96.0535 | 99.8 | [7 empty] | CATEGORYB | SINGLE | MISSION - VETAL TAP 115KV CKT 1 | 0 | 652482 | MISSION7 115.00 | 659153 | VETALTP7 115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T95520SP | TO->FROM | AINSWORTH - AINSWORTH 115KV CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640050 | AINSWND7 115.00 | 640051 | AINSWRT7 115.00 | 0 |  | 1 | 20SP | 120 | 120 | 132 |  | 93.523 | 97.3 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T27995525SP | TO->FROM | AINSWORTH - AINSWORTH 115KV CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640050 | AINSWND7 115.00 | 640051 | AINSWRT7 115.00 | 0 |  | 1 | 25SP | 120 | 120 | 132 |  | 94.355 | 95.9 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 180 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2985525WP | TO->FROM | AINSWORTH - AINSWORTH 115KV CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640050 | AINSWND7 115.00 | 640051 | AINSWRT7 115.00 | 0 |  | 1 | 25WP | 120 | 120 | 132 |  | 91.0437 | 97 | [7 empty] | CATEGORYB | SINGLE | FT THOMPSON - YANKTON 345KV CKT 1 | 0 | 652506 | FTTHOMP3 345.00 | 652532 | GR PRAIRIE 3345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T1145520WP | FROM->TO | AMARILLO SOUTH INTERCHANGE - SWISHER COUNTY INTERCHANGE 230KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-CNPL | 0 | 524415 | AMA_SOUTH 6230.00 | 525213 | SWISHER 6230.00 | 0 |  | 1 | 20WP | 329 | 361 | 0 |  | 83.133 | 97 | [7 empty] | CATEGORYB | SINGLE | NEWHART 230 - POTTER COUNTY INTERCHANGE 230KV CKT 1 | 0 | 523959 | POTTER_CO 6230.00 | 525461 | NEWHART 6230.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T5195520WP | FROM->TO | ANDREWS 6230.00 (FROM BORDEN) 230/115/13.2KV TRANSFORMER CKT 2 | E | SPS | SPS | SPS-HOBB | SPS-HOBB | 1 | 528604 | ANDREWS 6230.00 | 528602 | ANDREWS 3115.00 | 528600 | ANDREWS_TR2113.200 | 2 | 20WP | 168 | 168 | 0 | 99.7 | 99.6629 | 99.1 | [7 empty] | CATEGORYB | SINGLE | ANDREWS 6230.00 (FROM MIDLAND) 230/115/13.2KV TRANSFORMER CKT 1 | 1 | 528602 | ANDREWS 3115.00 | 528604 | ANDREWS 6230.00 | 528601 | ANDREWS_TR1113.200 | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T5175520WP | FROM->TO | ANDREWS 6230.00 (FROM MIDLAND) 230/115/13.2KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-HOBB | SPS-HOBB | 1 | 528604 | ANDREWS 6230.00 | 528602 | ANDREWS 3115.00 | 528601 | ANDREWS_TR1113.200 | 1 | 20WP | 168 | 168 | 0 | 99.5 | 99.515 | 98.9 | [7 empty] | CATEGORYB | SINGLE | ANDREWS 6230.00 (FROM BORDEN) 230/115/13.2KV TRANSFORMER CKT 2 | 1 | 528602 | ANDREWS 3115.00 | 528604 | ANDREWS 6230.00 | 528600 | ANDREWS_TR2113.200 | 2 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2495516SP | TO->FROM | ARKANSAS CITY - PARIS 69KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533548 | PARIS 2 69.000 | 533542 | ARKCITY2 69.000 | 0 |  | 1 | 16SP | 72 | 72 | 0 |  | 79.2542 | 95.3 | [7 empty] | CATEGORYB | SINGLE | CRESWELL - OAK 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | 0400 - JEC - Hoyt 345kV |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3875520SP | TO->FROM | AUBURN ROAD - JEFFREY ENERGY CENTER 230KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532852 | JEC 6 230.00 | 532851 | AUBURN 6 230.00 | 0 |  | 1 | 20SP | 612 | 612 | 0 |  | 92.2121 | 96.6 | [7 empty] | CATEGORYB | SINGLE | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | 0400 - JEC - Hoyt 345kV |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T4145525SP | TO->FROM | AUBURN ROAD - JEFFREY ENERGY CENTER 230KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532852 | JEC 6 230.00 | 532851 | AUBURN 6 230.00 | 0 |  | 1 | 25SP | 612 | 612 | 0 |  | 93.2323 | 97.3 | [7 empty] | CATEGORYB | SINGLE | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2495515WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 15WP | 68 | 68 | 0 | 95.7 | 95.7264 | 98.6 | [7 empty] | CATEGORYB | SINGLE | BERRYVILLE - GREEN FOREST 161KV CKT 1 | 0 | 338100 | 5BERRYV 161.00 | 338101 | 5GR FOR 161.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2515515WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 15WP | 68 | 68 | 0 | 95.7 | 95.7264 | 98.6 | [7 empty] | CATEGORYB | SINGLE | BERRYVILLE - OSAGE CREEK (AECC) 161KV CKT 1 | 0 | 338100 | 5BERRYV 161.00 | 338682 | 5OSAGE# 161.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T8595515WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 15WP | 68 | 68 | 0 | 95.7 | 95.7331 | 98.6 | [7 empty] | CATEGORYB | NONSINGLE | EUREKA SPRIN | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T9625515WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 15WP | 68 | 68 | 0 | 95.7 | 95.726 | 98.6 | [7 empty] | CATEGORYB | GENOUT | GEN505484 2-BEAVER | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T8815015WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 15WP | 68 | 68 | 0 | 98.5 | 98.5153 | 98.5 | [7 empty] | CATEGORYB | GENOUT | GEN505484 2-BEAVER | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T7705015WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 15WP | 68 | 68 | 0 | 98.5 | 98.522 | 98.5 | [7 empty] | CATEGORYB | NONSINGLE | EUREKA SPRIN | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T2105015WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 15WP | 68 | 68 | 0 | 98.5 | 98.5161 | 98.5 | [7 empty] | CATEGORYB | SINGLE | BERRYVILLE - OSAGE CREEK (AECC) 161KV CKT 1 | 0 | 338100 | 5BERRYV 161.00 | 338682 | 5OSAGE# 161.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T2075015WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 15WP | 68 | 68 | 0 | 98.5 | 98.5164 | 98.5 | [7 empty] | CATEGORYB | SINGLE | BERRYVILLE - GREEN FOREST 161KV CKT 1 | 0 | 338100 | 5BERRYV 161.00 | 338101 | 5GR FOR 161.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T8715515WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 15WP | 68 | 68 | 0 | 95.4 | 95.4317 | 98.2 | [7 empty] | CATEGORYB | NONSINGLE | A059 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T9905515WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 15WP | 68 | 68 | 0 | 95.3 | 95.2841 | 97.9 | [7 empty] | CATEGORYB | SWSHUNT | GREEN FOREST 161KV SWITCHED SHUNT | 0 | 338101 | 5GR FOR 161.00 | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T2055015WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 15WP | 68 | 68 | 0 | 98.1 | 98.1124 | 97.7 | [7 empty] | CATEGORYB | SINGLE | BEE BRANCH (AECC) - QUITMAN 161KV CKT 1 | 0 | 337926 | 5QUITMN 161.00 | 338831 | 5BEE BR# 161.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2535515WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 15WP | 68 | 68 | 0 | 95 | 95.0356 | 97.6 | [7 empty] | CATEGORYB | SINGLE | HARRISON SOUTH AECC - HARRISON-EAST 161KV CKT 1 | 0 | 338104 | 5HARR-E 161.00 | 338681 | 5HARR-S# 161.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T9735015WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 15WP | 68 | 68 | 0 | 98 | 98.0357 | 97.6 | [7 empty] | CATEGORYB | SWSHUNT | GREEN FOREST 161KV SWITCHED SHUNT | 0 | 338101 | 5GR FOR 161.00 | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T2155015WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 15WP | 68 | 68 | 0 | 97.8 | 97.7991 | 97.3 | [7 empty] | CATEGORYB | SINGLE | HARRISON SOUTH AECC - HARRISON-EAST 161KV CKT 1 | 0 | 338104 | 5HARR-E 161.00 | 338681 | 5HARR-S# 161.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T7845015WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 15WP | 68 | 68 | 0 | 97.4 | 97.4237 | 97 | [7 empty] | CATEGORYB | NONSINGLE | A059 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T85516SP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 16SP | 68 | 68 | 0 | 98.3 | 98.2701 | 98.6 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T65016SP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 16SP | 68 | 68 | 0 | 98.6 | 98.5655 | 98.6 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T2525016WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 16WP | 68 | 68 | 0 | 99.9 | 99.9419 | 99.4 | [7 empty] | CATEGORYB | SINGLE | BEE BRANCH (AECC) - CLINTON 161KV CKT 1 | 0 | 338831 | 5BEE BR# 161.00 | 338833 | 5CLIN-IN# 161.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T2535016WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 16WP | 68 | 68 | 0 | 99.3 | 99.3339 | 98.8 | [7 empty] | CATEGORYB | SINGLE | CLINTON - CLINTON WEST (AECC) 161KV CKT 1 | 0 | 338832 | 5CLIN-W# 161.00 | 338833 | 5CLIN-IN# 161.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T8325016WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 16WP | 68 | 68 | 0 | 98.9 | 98.884 | 98.7 | [7 empty] | CATEGORYB | NONSINGLE | EUREKA SPRIN | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T2345016WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 16WP | 68 | 68 | 0 | 98.9 | 98.8647 | 98.4 | [7 empty] | CATEGORYB | SINGLE | HARRISON SOUTH AECC - HARRISON-EAST 161KV CKT 1 | 0 | 338104 | 5HARR-E 161.00 | 338681 | 5HARR-S# 161.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T3225016WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 16WP | 68 | 68 | 0 | 98.5 | 98.4725 | 98.3 | [7 empty] | CATEGORYB | SINGLE | BERRYVILLE - KINGRIV5 161.00 161KV CKT 1 | 0 | 506988 | KINGRIV5 161.00 | 338100 | 5BERRYV 161.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T9395016WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 16WP | 68 | 68 | 0 | 98.5 | 98.4731 | 98.3 | [7 empty] | CATEGORYB | GENOUT | GEN505484 2-BEAVER | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T2295016WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 16WP | 68 | 68 | 0 | 98.5 | 98.4725 | 98.3 | [7 empty] | CATEGORYB | SINGLE | BERRYVILLE - GREEN FOREST 161KV CKT 1 | 0 | 338100 | 5BERRYV 161.00 | 338101 | 5GR FOR 161.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T10395016WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 16WP | 68 | 68 | 0 | 98.5 | 98.4784 | 98.3 | [7 empty] | CATEGORYB | SWSHUNT | GREEN FOREST 161KV SWITCHED SHUNT | 0 | 338101 | 5GR FOR 161.00 | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2695516WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 16WP | 68 | 68 | 0 | 95.1 | 95.0846 | 98.1 | [7 empty] | CATEGORYB | SINGLE | BERRYVILLE - GREEN FOREST 161KV CKT 1 | 0 | 338100 | 5BERRYV 161.00 | 338101 | 5GR FOR 161.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2735516WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 16WP | 68 | 68 | 0 | 95.1 | 95.0846 | 98.1 | [7 empty] | CATEGORYB | SINGLE | HARRISON SOUTH AECC - HARRISON-EAST 161KV CKT 1 | 0 | 338104 | 5HARR-E 161.00 | 338681 | 5HARR-S# 161.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3545516WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 16WP | 68 | 68 | 0 | 95.1 | 95.0846 | 98.1 | [7 empty] | CATEGORYB | SINGLE | BERRYVILLE - KINGRIV5 161.00 161KV CKT 1 | 0 | 506988 | KINGRIV5 161.00 | 338100 | 5BERRYV 161.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T9745516WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 16WP | 68 | 68 | 0 | 95.1 | 95.0839 | 98.1 | [7 empty] | CATEGORYB | GENOUT | GEN505484 2-BEAVER | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T8795516WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 16WP | 68 | 68 | 0 | 95.1 | 95.0846 | 98.1 | [7 empty] | CATEGORYB | NONSINGLE | EUREKA SPRIN | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T10015516WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 16WP | 68 | 68 | 0 | 95.1 | 95.0888 | 98.1 | [7 empty] | CATEGORYB | SWSHUNT | GREEN FOREST 161KV SWITCHED SHUNT | 0 | 338101 | 5GR FOR 161.00 | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2845516WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 16WP | 68 | 68 | 0 | 95.2 | 95.1853 | 97.9 | [7 empty] | CATEGORYB | SINGLE | NEWPORT AB - NEWPORT INDUSTRIAL 161KV CKT 1 | 0 | 338172 | 5NEW-AB 161.00 | 338173 | 5NEW-IN 161.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3035516WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 16WP | 68 | 68 | 0 | 95.1 | 95.0527 | 97.9 | [7 empty] | CATEGORYB | SINGLE | JONESBORO - JONESBORO 161KV CKT 1 | 0 | 505418 | JONESBO5 161.00 | 338170 | 5JONES 161.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2715516WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 16WP | 68 | 68 | 0 | 95.1 | 95.0695 | 97.6 | [7 empty] | CATEGORYB | SINGLE | HARRISON SOUTH AECC - HARRISON-WEST 161KV CKT 1 | 0 | 338102 | 5HARR-W 161.00 | 338681 | 5HARR-S# 161.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2835516WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 16WP | 68 | 68 | 0 |  | 94.8478 | 97.6 | [7 empty] | CATEGORYB | SINGLE | NEWPORT - NEWPORT INDUSTRIAL 161KV CKT 1 | 0 | 338151 | 5NEWPO 161.00 | 338173 | 5NEW-IN 161.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T2445016WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 16WP | 68 | 68 | 0 | 98 | 98.0059 | 97.6 | [7 empty] | CATEGORYB | SINGLE | NEWPORT - NEWPORT INDUSTRIAL 161KV CKT 1 | 0 | 338151 | 5NEWPO 161.00 | 338173 | 5NEW-IN 161.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T245016WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 16WP | 68 | 68 | 0 | 98.1 | 98.0766 | 97.6 | [7 empty] | CATEGORYB | SINGLE | BEAVER - EUREKA SPRINGS 161KV CKT 1 | 0 | 505480 | BEAVER 5 161.00 | 506932 | EUREKA 5 161.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T2745016WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 16WP | 68 | 68 | 0 | 98.4 | 98.3656 | 97.5 | [7 empty] | CATEGORYB | SINGLE | JONESBORO - JONESBORO 161KV CKT 1 | 0 | 505418 | JONESBO5 161.00 | 338170 | 5JONES 161.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T2495016WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 16WP | 68 | 68 | 0 | 97.8 | 97.788 | 97.4 | [7 empty] | CATEGORYB | SINGLE | NEWPORT AB - NEWPORT INDUSTRIAL 161KV CKT 1 | 0 | 338172 | 5NEW-AB 161.00 | 338173 | 5NEW-IN 161.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T125520SP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 20SP | 68 | 68 | 0 | 97.4 | 97.411 | 98.6 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T85020SP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 20SP | 68 | 68 | 0 | 98.6 | 98.5955 | 98.4 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T4255520WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 20WP | 68 | 68 | 0 |  | 98.9563 | 99.9 | [7 empty] | CATEGORYB | SINGLE | JONESBORO - JONESBORO 161KV CKT 1 | 0 | 505418 | JONESBO5 161.00 | 338170 | 5JONES 161.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T45020WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 20WP | 68 | 68 | 0 | 96.1 | 96.0978 | 96.1 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T35520WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 20WP | 68 | 68 | 0 |  | 94.7971 | 95.4 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T195525SP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 25SP | 68 | 68 | 0 | 97.8 | 97.8017 | 98.8 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T165025SP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 25SP | 68 | 68 | 0 | 98.5 | 98.5156 | 98 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T25525WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 25WP | 68 | 68 | 0 | 96.8 | 96.8037 | 97.7 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T55025WP | FROM->TO | BEAVER 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505482 | BVR #1 1 13.800 | 505480 | BEAVER 5 161.00 | 0 |  | 1 | 25WP | 68 | 68 | 0 | 97.3 | 97.3151 | 96.5 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T14195525SP | FROM->TO | BENTON (BENT TX-1) 345/138/13.8KV TRANSFORMER CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 1 | 532791 | BENTON 7 345.00 | 532986 | BENTON 4 138.00 | 532821 | BENTN1 1 13.800 | 1 | 25SP | 382 | 382 | 500 | 99.9 | 99.8855 | 97.8 | [7 empty] | CATEGORYB | SINGLE | BENTON (BENT TX-2) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532791 | BENTON 7 345.00 | 532986 | BENTON 4 138.00 | 532822 | BENTN2 1 13.800 | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T14185525SP | FROM->TO | BENTON (BENT TX-2) 345/138/13.8KV TRANSFORMER CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 1 | 532791 | BENTON 7 345.00 | 532986 | BENTON 4 138.00 | 532822 | BENTN2 1 13.800 | 1 | 25SP | 382 | 382 | 500 | 97.4 | 97.4397 | 95.4 | [7 empty] | CATEGORYB | SINGLE | BENTON (BENT TX-1) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532791 | BENTON 7 345.00 | 532986 | BENTON 4 138.00 | 532821 | BENTN1 1 13.800 | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T1255525SP | FROM->TO | BROKEN ARROW NORTH - SOUTH TAP - LYNN LANE TAP 138KV CKT 1 | E | AEPW | AEPW | PSO_TULSA | PSO_TULSA | 0 | 509786 | BA.N-ST4 138.00 | 509804 | LLANETP4 138.00 | 0 |  | 1 | 25SP | 212 | 212 | 0 | 99.2 | 99.1581 | 95.4 | [7 empty] | CATEGORYB | SINGLE | CHAMBER SPRINGS - CLARKSVILLE 345KV CKT 1 | 0 | 506945 | CHAMSPR7 345.00 | 509745 | CLARKSV7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2185520SP | FROM->TO | BUCKNER7 345.00 - SPEARVILLE 345KV CKT 1 | E | SUNC | SUNC | SEPC | SEPC | 0 | 531501 | BUCKNER7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 | 20SP | 611.9 | 611.9 | 0 | 96.8 | 96.7608 | 95.8 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T6095516SP | FROM->TO | BULL SHOALS - MIDWAY (YVEPA) 161KV CKT 1 | E | SWPA | EES-EAI | EMINTH | EES_ARK | 0 | 505460 | BULL SH5 161.00 | 338813 | 5MIDWAY# 161.00 | 0 |  | 1 | 16SP | 162 | 162 | 0 | 97.1 | 97.0704 | 96.1 | [7 empty] | CATEGORYB | SINGLE | INDEPENDENCE - MOOREFIELD 161KV CKT 1 | 0 | 338138 | 5MORFLD 161.00 | 338142 | 5ISES-1 161.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T8555520SP | FROM->TO | BULL SHOALS - MIDWAY (YVEPA) 161KV CKT 1 | E | SWPA | EES-EAI | EMINTH | EES_ARK | 0 | 505460 | BULL SH5 161.00 | 338813 | 5MIDWAY# 161.00 | 0 |  | 1 | 20SP | 162 | 162 | 0 | 96.7 | 96.7202 | 95.6 | [7 empty] | CATEGORYB | SINGLE | INDEPENDENCE - MOOREFIELD 161KV CKT 1 | 0 | 338138 | 5MORFLD 161.00 | 338142 | 5ISES-1 161.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T10305525SP | FROM->TO | BULL SHOALS - MIDWAY (YVEPA) 161KV CKT 1 | E | SWPA | EES-EAI | EMINTH | EES_ARK | 0 | 505460 | BULL SH5 161.00 | 338813 | 5MIDWAY# 161.00 | 0 |  | 1 | 25SP | 162 | 162 | 0 | 98.6 | 98.6345 | 98.4 | [7 empty] | CATEGORYB | SINGLE | INDEPENDENCE - MOOREFIELD 161KV CKT 1 | 0 | 338138 | 5MORFLD 161.00 | 338142 | 5ISES-1 161.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2885520SP | TO->FROM | CARLISLE INTERCHANGE - TUCO INTERCHANGE 230KV CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 0 | 525830 | TUCO_INT 6230.00 | 526161 | CARLISLE 6230.00 | 0 |  | 1 | 20SP | 319 | 351 | 0 |  | 93.698 | 96.4 | [7 empty] | CATEGORYB | SINGLE | JONES STATION - TUCO INTERCHANGE 230KV CKT 1 | 0 | 525830 | TUCO_INT 6230.00 | 526337 | JONES 6230.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T1325520WP | TO->FROM | CARLSBAD INTERCHANGE - PECOS INTERCHANGE 115KV CKT 1 | E | SPS | SPS | SPS-PECO | SPS-PECO | 0 | 528178 | PECOS 3115.00 | 528160 | CARLSBAD 3115.00 | 0 |  | 1 | 20WP | 156 | 156 | 0 |  | 91.0528 | 95.1 | [7 empty] | CATEGORYB | SINGLE | HOBBS - KIOWA 7345.00 345KV CKT 1 | 0 | 527896 | HOBBS_INT 7345.00 | 527965 | KIOWA 7345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T545025WP | FROM->TO | CARTHAGE TAP - TENAHA 138KV CKT 1 | E | AEPW | AEPW | RHILL_NTEC | RHILL_NTEC | 0 | 509060 | CARTHGT4 138.00 | 509088 | TENAHA 4 138.00 | 0 |  | 1 | 25WP | 215 | 215 | 0 | 99.7 | 99.6549 | 99.8 | [7 empty] | CATEGORYB | SINGLE | JOAQUIN REC - LOGANSPORT 138KV CKT 1 | 0 | 509066 | JOAQUIN4 138.00 | 509071 | LOGANSP4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T9515520SP | FROM->TO | CHAMBER SPRINGS - FARMINGTON AECC 161KV CKT 1 | E | AEPW | AEPW | FAYETTEVILLE | FAYETVL AECC | 0 | 506944 | CHAMSPR5 161.00 | 504020 | FARMNGTN 5 161.00 | 0 |  | 1 | 20SP | 294 | 360 | 0 | 99 | 98.9927 | 98.8 | [7 empty] | CATEGORYB | SINGLE | TONTITOWN () 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 506957 | TONTITN5 161.00 | 506959 | TONTITN7 345.00 | 506958 | TONTITN1 13.800 | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T1695020SP | TO->FROM | CHARLOT5 161.00 - NORTHEAST 161KV CKT 1 | E | KCPL | KCPL | DWNTWN | DWNTWN | 0 | 542985 | NEAST 5 161.00 | 543133 | CHARLOT5 161.00 | 0 |  | 1 | 20SP | 259 | 259 | 0 | 95.6 | 95.599 | 96.5 | [7 empty] | CATEGORYB | SINGLE | GRAND AVENUE WEST - NORTHEAST 161KV CKT 1 | 0 | 542985 | NEAST 5 161.00 | 542988 | GRAND W5 161.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T3885025SP | TO->FROM | CHARLOT5 161.00 - NORTHEAST 161KV CKT 1 | E | KCPL | KCPL | DWNTWN | DWNTWN | 0 | 542985 | NEAST 5 161.00 | 543133 | CHARLOT5 161.00 | 0 |  | 1 | 25SP | 259 | 259 | 0 | 100.6 | 100.6047 | 95.8 | [7 empty] | CATEGORYB | SINGLE | GRAND AVENUE WEST - NORTHEAST 161KV CKT 1 | 0 | 542985 | NEAST 5 161.00 | 542988 | GRAND W5 161.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T3895025SP | TO->FROM | CHARLOT5 161.00 - NORTHEAST 161KV CKT 1 | E | KCPL | KCPL | DWNTWN | DWNTWN | 0 | 542985 | NEAST 5 161.00 | 543133 | CHARLOT5 161.00 | 0 |  | 1 | 25SP | 259 | 259 | 0 | 98.3 | 98.3401 | 95.5 | [7 empty] | CATEGORYB | SINGLE | CROSSTOWN - GRAND AVENUE WEST 161KV CKT 1 | 0 | 542988 | GRAND W5 161.00 | 542990 | CROSTWN5 161.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T10875025SP | TO->FROM | CHIKASKIA - KILDARE4 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514760 | KILDARE4 138.00 | 514757 | CHIKASI4 138.00 | 0 |  | 1 | 25SP | 143 | 143 | 0 |  | 90.6263 | 95.7 | [7 empty] | CATEGORYB | SINGLE | RENFROW7 345.00 (BANK 1) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 515543 | RENFROW7 345.00 | 515544 | RENFROW4 138.00 | 515545 | RENFRO11 13.800 | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T17605520SP | TO->FROM | CIMARRON RIVER TAP - KISMET 3 115.00 115KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539646 | KISMET 3 115.00 | 539652 | CMRIVTP3 115.00 | 0 |  | 1 | 20SP | 133.9 | 133.9 | 0 | 97.2 | 97.2377 | 99.2 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SEPC-07 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T4795520SP | TO->FROM | CIMARRON RIVER TAP - KISMET 3 115.00 115KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539646 | KISMET 3 115.00 | 539652 | CMRIVTP3 115.00 | 0 |  | 1 | 20SP | 133.9 | 133.9 | 0 | 95.6 | 95.608 | 97.5 | [7 empty] | CATEGORYB | SINGLE | CIMARRON RIVER PLANT - N-CIMRN3 115.00 115KV CKT 1 | 0 | 539654 | CIM-PLT3 115.00 | 539749 | N-CIMRN3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T4445520SP | FROM->TO | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533036 | CLEARWT4 138.00 | 533045 | GILL W 4 138.00 | 0 |  | 1 | 20SP | 143 | 143 | 0 |  | 72.1659 | 98.7 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T21925520SP | FROM->TO | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533036 | CLEARWT4 138.00 | 533045 | GILL W 4 138.00 | 0 |  | 1 | 20SP | 143 | 143 | 0 |  | 68.5371 | 96.5 | [7 empty] | CATEGORYB | GENOUT | GEN532751 1-WOLF CREEK GENERATING STATION UNIT 1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T17995520SP | FROM->TO | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533036 | CLEARWT4 138.00 | 533045 | GILL W 4 138.00 | 0 |  | 1 | 20SP | 143 | 143 | 0 |  | 68.7528 | 95.4 | [7 empty] | CATEGORYB | NONSINGLE | WR-B3-7 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T11735520WP | FROM->TO | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533036 | CLEARWT4 138.00 | 533045 | GILL W 4 138.00 | 0 |  | 1 | 20WP | 143 | 143 | 0 |  | 84.1439 | 96.1 | [7 empty] | CATEGORYB | GENOUT | GEN532751 1-WOLF CREEK GENERATING STATION UNIT 1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T14395525WP | FROM->TO | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533036 | CLEARWT4 138.00 | 533045 | GILL W 4 138.00 | 0 |  | 1 | 25WP | 143 | 143 | 0 |  | 87.8514 | 99.8 | [7 empty] | CATEGORYB | GENOUT | GEN532751 1-WOLF CREEK GENERATING STATION UNIT 1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2375525WP | FROM->TO | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533036 | CLEARWT4 138.00 | 533045 | GILL W 4 138.00 | 0 |  | 1 | 25WP | 143 | 143 | 0 |  | 86.578 | 97.7 | [7 empty] | CATEGORYB | SINGLE | 45TH ST4 138.00 - EVANS ENERGY CENTER SOUTH 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533074 | 45TH ST4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2305525WP | FROM->TO | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533036 | CLEARWT4 138.00 | 533045 | GILL W 4 138.00 | 0 |  | 1 | 25WP | 143 | 143 | 0 |  | 82.1835 | 97.5 | [7 empty] | CATEGORYB | SINGLE | VIOLA 7 345.00 - WICHITA 345KV CKT 1 | 0 | 532796 | WICHITA7 345.00 | 532798 | VIOLA 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | CONT-1107 - Gordon Evans - Lakeridge OR Lakeridge - Hoover 138kV |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2365525WP | FROM->TO | CLEARWATER - GILL ENERGY CENTER WEST 138KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533036 | CLEARWT4 138.00 | 533045 | GILL W 4 138.00 | 0 |  | 1 | 25WP | 143 | 143 | 0 |  | 84.8416 | 95.7 | [7 empty] | CATEGORYB | SINGLE | EVANS ENERGY CENTER SOUTH - LAKERIDGE 138KV CKT 1 | 0 | 533041 | EVANS S4 138.00 | 533053 | LAKERDG4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T18045520SP | TO->FROM | CRAWFORD - NEOSHO 69KV CKT 1 | E | WERE | WERE | SEAST | SEAST | 0 | 533768 | NEOSHO 2 69.000 | 533758 | CRAWFOR2 69.000 | 0 |  | 1 | 20SP | 41 | 48 | 0 |  | 93.0977 | 97.7 | [7 empty] | CATEGORYB | NONSINGLE | WR-B3-24 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T4565520SP | FROM->TO | CRESWELL - OAK 69KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533543 | CRESWLN2 69.000 | 533547 | OAK 2 69.000 | 0 |  | 1 | 20SP | 108 | 108 | 0 |  | 70.6414 | 97.8 | [7 empty] | CATEGORYB | SINGLE | CRESWELL - PARIS 69KV CKT 1 | 0 | 533543 | CRESWLN2 69.000 | 533548 | PARIS 2 69.000 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T18005520SP | FROM->TO | CRESWELL (CRSW TX-1) 138/69/13.2KV TRANSFORMER CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 2 | 532981 | CRESWLN4 138.00 | 533543 | CRESWLN2 69.000 | 533080 | CRESW1 1 13.200 | 1 | 20SP | 100 | 110 | 125 |  | 65.1127 | 99.9 | [7 empty] | CATEGORYB | NONSINGLE | WR-B3-8 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | 0616 - Creswell #1 or #2 138-69kV XFMR |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T11885520SP | FROM->TO | CRESWELL (CRSW TX-1) 138/69/13.2KV TRANSFORMER CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 2 | 532981 | CRESWLN4 138.00 | 533543 | CRESWLN2 69.000 | 533080 | CRESW1 1 13.200 | 1 | 20SP | 100 | 110 | 125 |  | 65.1127 | 99.9 | [7 empty] | CATEGORYB | SINGLE | CRESWELL (CRSW TX-2) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532981 | CRESWLN4 138.00 | 533543 | CRESWLN2 69.000 | 533081 | CRESW2 1 13.200 | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T21525525SP | FROM->TO | CRESWELL (CRSW TX-1) 138/69/13.2KV TRANSFORMER CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 2 | 532981 | CRESWLN4 138.00 | 533543 | CRESWLN2 69.000 | 533080 | CRESW1 1 13.200 | 1 | 25SP | 100 | 110 | 125 |  | 73.8506 | 96.3 | [7 empty] | CATEGORYB | NONSINGLE | WR-B3-8 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | 0616 - Creswell #1 or #2 138-69kV XFMR |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T14415525SP | FROM->TO | CRESWELL (CRSW TX-1) 138/69/13.2KV TRANSFORMER CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 2 | 532981 | CRESWLN4 138.00 | 533543 | CRESWLN2 69.000 | 533080 | CRESW1 1 13.200 | 1 | 25SP | 100 | 110 | 125 |  | 73.8506 | 95.7 | [7 empty] | CATEGORYB | SINGLE | CRESWELL (CRSW TX-2) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532981 | CRESWLN4 138.00 | 533543 | CRESWLN2 69.000 | 533081 | CRESW2 1 13.200 | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T11395525WP | FROM->TO | CRESWELL (CRSW TX-1) 138/69/13.2KV TRANSFORMER CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 2 | 532981 | CRESWLN4 138.00 | 533543 | CRESWLN2 69.000 | 533080 | CRESW1 1 13.200 | 1 | 25WP | 100 | 110 | 125 |  | 74.712 | 96.8 | [7 empty] | CATEGORYB | NONSINGLE | WR-B3-8 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | 0616 - Creswell #1 or #2 138-69kV XFMR |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T7265525WP | FROM->TO | CRESWELL (CRSW TX-1) 138/69/13.2KV TRANSFORMER CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 2 | 532981 | CRESWLN4 138.00 | 533543 | CRESWLN2 69.000 | 533080 | CRESW1 1 13.200 | 1 | 25WP | 100 | 110 | 125 |  | 74.712 | 96.3 | [7 empty] | CATEGORYB | SINGLE | CRESWELL (CRSW TX-2) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532981 | CRESWLN4 138.00 | 533543 | CRESWLN2 69.000 | 533081 | CRESW2 1 13.200 | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | 0616 - Creswell #1 or #2 138-69kV XFMR |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T11865520SP | FROM->TO | CRESWELL (CRSW TX-2) 138/69/13.2KV TRANSFORMER CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 2 | 532981 | CRESWLN4 138.00 | 533543 | CRESWLN2 69.000 | 533081 | CRESW2 1 13.200 | 1 | 20SP | 100 | 110 | 125 |  | 65.066 | 99.7 | [7 empty] | CATEGORYB | SINGLE | CRESWELL (CRSW TX-1) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532981 | CRESWLN4 138.00 | 533543 | CRESWLN2 69.000 | 533080 | CRESW1 1 13.200 | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | 0616 - Creswell #1 or #2 138-69kV XFMR |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T14405525SP | FROM->TO | CRESWELL (CRSW TX-2) 138/69/13.2KV TRANSFORMER CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 2 | 532981 | CRESWLN4 138.00 | 533543 | CRESWLN2 69.000 | 533081 | CRESW2 1 13.200 | 1 | 25SP | 100 | 110 | 125 |  | 73.788 | 95.6 | [7 empty] | CATEGORYB | SINGLE | CRESWELL (CRSW TX-1) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532981 | CRESWLN4 138.00 | 533543 | CRESWLN2 69.000 | 533080 | CRESW1 1 13.200 | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | 0616 - Creswell #1 or #2 138-69kV XFMR |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T7255525WP | FROM->TO | CRESWELL (CRSW TX-2) 138/69/13.2KV TRANSFORMER CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 2 | 532981 | CRESWLN4 138.00 | 533543 | CRESWLN2 69.000 | 533081 | CRESW2 1 13.200 | 1 | 25WP | 100 | 110 | 125 |  | 74.6605 | 95.5 | [7 empty] | CATEGORYB | SINGLE | CRESWELL (CRSW TX-1) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 532981 | CRESWLN4 138.00 | 533543 | CRESWLN2 69.000 | 533080 | CRESW1 1 13.200 | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | INVALID | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3695520SP | FROM->TO | CRKCK 3 115.00 - CUDAHY 115KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539783 | CRKCK 3 115.00 | 539659 | CUDAHY 3 115.00 | 0 |  | 1 | 20SP | 153.4 | 165.1 | 0 | 96.7 | 96.714 | 98.6785 | [7 empty] | CATEGORYB | SINGLE | CTU SUBLETTE - PIONEER TAP 115KV CKT 1 | 0 | 531392 | PIONTAP3 115.00 | 531442 | SAT-TAP3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3915525SP | FROM->TO | CRKCK 3 115.00 - CUDAHY 115KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539783 | CRKCK 3 115.00 | 539659 | CUDAHY 3 115.00 | 0 |  | 1 | 25SP | 153.4 | 165.1 | 0 | 97.2 | 97.1964 | 99.5 | [7 empty] | CATEGORYB | SINGLE | CTU SUBLETTE - HASKELL 115KV CKT 1 | 0 | 531374 | HASKELL3 115.00 | 531442 | SAT-TAP3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3955525SP | FROM->TO | CRKCK 3 115.00 - CUDAHY 115KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539783 | CRKCK 3 115.00 | 539659 | CUDAHY 3 115.00 | 0 |  | 1 | 25SP | 153.4 | 165.1 | 0 |  | 94.2452 | 95.9 | [7 empty] | CATEGORYB | SINGLE | HASKELL - SEWARD-3 115KV CKT 1 | 0 | 531374 | HASKELL3 115.00 | 531467 | SEWARD-3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T17615520SP | FROM->TO | CUDAHY - KISMET 3 115.00 115KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539659 | CUDAHY 3 115.00 | 539646 | KISMET 3 115.00 | 0 |  | 1 | 20SP | 119.5 | 135.8 | 0 | 97.9 | 97.8998 | 99.8 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SEPC-07 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3795520SP | FROM->TO | CUDAHY - KISMET 3 115.00 115KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539659 | CUDAHY 3 115.00 | 539646 | KISMET 3 115.00 | 0 |  | 1 | 20SP | 119.5 | 135.8 | 0 | 96.3 | 96.3184 | 98.2 | [7 empty] | CATEGORYB | SINGLE | N-CIMRN3 115.00 - SEWARD-3 115KV CKT 1 | 0 | 531467 | SEWARD-3 115.00 | 539749 | N-CIMRN3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T4805520SP | FROM->TO | CUDAHY - KISMET 3 115.00 115KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539659 | CUDAHY 3 115.00 | 539646 | KISMET 3 115.00 | 0 |  | 1 | 20SP | 119.5 | 135.8 | 0 | 96.3 | 96.2903 | 98.1 | [7 empty] | CATEGORYB | SINGLE | CIMARRON RIVER PLANT - N-CIMRN3 115.00 115KV CKT 1 | 0 | 539654 | CIM-PLT3 115.00 | 539749 | N-CIMRN3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T1165025WP | FROM->TO | CUNNINGHAM STATION - MONUMENT TAP 115KV CKT 1 | E | SPS | SPS | SPS-PECO | SPS-HOBB | 0 | 527864 | CUNNINHAM 3115.00 | 528568 | MONUMNT_TP 3115.00 | 0 |  | 1 | 25WP | 165 | 177 | 0 |  | -999 | 97.9 | [7 empty] | CATEGORYB | SINGLE | HOBBS - KIOWA 7345.00 345KV CKT 1 | 0 | 527896 | HOBBS_INT 7345.00 | 527965 | KIOWA 7345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T1125020SP | FROM->TO | CUNNINGHAM STATION - POTASH JUNCTION INTERCHANGE 230KV CKT 1 | E | SPS | SPS | SPS-PECO | SPS-PECO | 0 | 527865 | CUNNINHAM 6230.00 | 527963 | POTASH_JCT 6230.00 | 0 |  | 1 | 20SP | 319 | 351 | 0 | 101.7 | 101.6871 | 95.3 | [7 empty] | CATEGORYB | SINGLE | HOBBS - KIOWA 7345.00 345KV CKT 1 | 0 | 527896 | HOBBS_INT 7345.00 | 527965 | KIOWA 7345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3125525SP | FROM->TO | CUNNINGHAM STATION - QUAHADA 3115.00 115KV CKT 1 | E | SPS | SPS | SPS-PECO | SPS-HOBB | 0 | 527864 | CUNNINHAM 3115.00 | 528394 | QUAHADA 3115.00 | 0 |  | 1 | 25SP | 159 | 160 | 0 |  | -999 | 96.4 | [7 empty] | CATEGORYB | SINGLE | HOBBS - KIOWA 7345.00 345KV CKT 1 | 0 | 527896 | HOBBS_INT 7345.00 | 527965 | KIOWA 7345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T18265016SP | FROM->TO | DARDANELLE 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505510 | DAR1&2 1 13.800 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 16SP | 76 | 76 | 0 |  | 98.6429 | 98.6477 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 56 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T18255016SP | FROM->TO | DARDANELLE 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505512 | DAR3&4 1 13.800 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 16SP | 76 | 76 | 0 |  | 97.9761 | 97.9808 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 55 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T19975516SP | FROM->TO | DARDANELLE 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505510 | DAR1&2 1 13.800 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 16SP | 76 | 76 | 0 |  | 96.0647 | 95.7606 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 52 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T19965516SP | FROM->TO | DARDANELLE 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505512 | DAR3&4 1 13.800 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 16SP | 76 | 76 | 0 |  | 95.4013 | 95.0947 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 51 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T23995520SP | FROM->TO | DARDANELLE 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505510 | DAR1&2 1 13.800 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 20SP | 76 | 76 | 0 |  | 98.6464 | 98.6466 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 56 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T16585020SP | FROM->TO | DARDANELLE 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505510 | DAR1&2 1 13.800 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 20SP | 76 | 76 | 0 |  | 98.636 | 98.6415 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 61 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T23985520SP | FROM->TO | DARDANELLE 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505512 | DAR3&4 1 13.800 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 20SP | 76 | 76 | 0 |  | 97.9796 | 97.9797 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 55 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T16575020SP | FROM->TO | DARDANELLE 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505512 | DAR3&4 1 13.800 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 20SP | 76 | 76 | 0 |  | 97.9692 | 97.9746 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 60 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T27885525SP | FROM->TO | DARDANELLE 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505510 | DAR1&2 1 13.800 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 25SP | 76 | 76 | 0 |  | 98.6464 | 98.6465 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 67 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T25245025SP | FROM->TO | DARDANELLE 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505510 | DAR1&2 1 13.800 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 25SP | 76 | 76 | 0 |  | 98.6361 | 98.6407 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 66 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T27875525SP | FROM->TO | DARDANELLE 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505512 | DAR3&4 1 13.800 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 25SP | 76 | 76 | 0 |  | 97.9796 | 97.9797 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 66 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T25235025SP | FROM->TO | DARDANELLE 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505512 | DAR3&4 1 13.800 | 505508 | DARDANE5 161.00 | 0 |  | 1 | 25SP | 76 | 76 | 0 |  | 97.9693 | 97.9738 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 65 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2655525SP | FROM->TO | DAWN SUB - Panda Energy Substation Hereford 115KV CKT 1 | E | SPS | SPS | SPS-CLHF | SPS-CLHF | 0 | 524590 | DAWN 3115.00 | 524597 | PANDAHFD 3115.00 | 0 |  | 1 | 25SP | 96 | 96 | 0 |  | 84.6049 | 98.5 | [7 empty] | CATEGORYB | SINGLE | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2445520SP | TO->FROM | DEAF SMITH COUNTY INTERCHANGE - Panda Energy Substation Hereford 115KV CKT 1 | E | SPS | SPS | SPS-CLHF | SPS-CLHF | 0 | 524597 | PANDAHFD 3115.00 | 524622 | DEAFSMITH 3115.00 | 0 |  | 1 | 20SP | 96 | 96 | 0 |  | 86.5134 | 96.6 | [7 empty] | CATEGORYB | SINGLE | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T1205520WP | TO->FROM | DEAF SMITH COUNTY INTERCHANGE - Panda Energy Substation Hereford 115KV CKT 1 | E | SPS | SPS | SPS-CLHF | SPS-CLHF | 0 | 524597 | PANDAHFD 3115.00 | 524622 | DEAFSMITH 3115.00 | 0 |  | 1 | 20WP | 106 | 106 | 0 |  | 82.889 | 99 | [7 empty] | CATEGORYB | SINGLE | BUSHLAND INTERCHANGE - DEAF SMITH COUNTY INTERCHANGE 230KV CKT 1 | 0 | 524267 | BUSHLAND 6230.00 | 524623 | DEAFSMITH 6230.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T16475020SP | FROM->TO | DUKE LAKEOVER 230/18.0KV TRANSFORMER CKT 1 | E | EES-EMI | EES-EMI | EES_MISS | EES_MISS | 0 | 336851 | 1IG1DUKEH 18.000 | 336850 | 6DUKELO1 230.00 | 0 |  | 1 | 20SP | 193 | 193 | 0 |  | 97.5071 | 97.5038 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T23845520SP | FROM->TO | DUKE LAKEOVER 230/18.0KV TRANSFORMER CKT 1 | E | EES-EMI | EES-EMI | EES_MISS | EES_MISS | 0 | 336851 | 1IG1DUKEH 18.000 | 336850 | 6DUKELO1 230.00 | 0 |  | 1 | 20SP | 193 | 193 | 0 |  | 97.5035 | 97.5035 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T25115025SP | FROM->TO | DUKE LAKEOVER 230/18.0KV TRANSFORMER CKT 1 | E | EES-EMI | EES-EMI | EES_MISS | EES_MISS | 0 | 336851 | 1IG1DUKEH 18.000 | 336850 | 6DUKELO1 230.00 | 0 |  | 1 | 25SP | 193 | 193 | 0 |  | 97.5035 | 97.5035 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T27715525SP | FROM->TO | DUKE LAKEOVER 230/18.0KV TRANSFORMER CKT 1 | E | EES-EMI | EES-EMI | EES_MISS | EES_MISS | 0 | 336851 | 1IG1DUKEH 18.000 | 336850 | 6DUKELO1 230.00 | 0 |  | 1 | 25SP | 193 | 193 | 0 |  | 97.5034 | 97.5034 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T19905516SP | FROM->TO | DUKE MCADAMS 500/18.0KV TRANSFORMER CKT 1 | E |  |  | EES_MISS | EES_MISS | 0 | 337007 | 1ATTALA G2 18.000 | 337005 | 8ATTALA 500.00 | 0 |  | 1 | 16SP | 193 | 193 | 0 |  | 99.5774 | 99.5603 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T19895516SP | FROM->TO | DUKE MCADAMS 500/18.0KV TRANSFORMER CKT 1 | E |  |  | EES_MISS | EES_MISS | 0 | 337006 | 1ATTALA G1 18.000 | 337005 | 8ATTALA 500.00 | 0 |  | 1 | 16SP | 193 | 193 | 0 |  | 99.5774 | 99.5602 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T18215016SP | FROM->TO | DUKE MCADAMS 500/18.0KV TRANSFORMER CKT 1 | E |  |  | EES_MISS | EES_MISS | 0 | 337007 | 1ATTALA G2 18.000 | 337005 | 8ATTALA 500.00 | 0 |  | 1 | 16SP | 193 | 193 | 0 |  | 98.4371 | 98.3983 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T18205016SP | FROM->TO | DUKE MCADAMS 500/18.0KV TRANSFORMER CKT 1 | E |  |  | EES_MISS | EES_MISS | 0 | 337006 | 1ATTALA G1 18.000 | 337005 | 8ATTALA 500.00 | 0 |  | 1 | 16SP | 193 | 193 | 0 |  | 98.437 | 98.3982 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T15265525WP | FROM->TO | DUKE MCADAMS 500/18.0KV TRANSFORMER CKT 1 | E | EES-EMI | EES-EMI | EES_MISS | EES_MISS | 0 | 337006 | 1ATTALA G1 18.000 | 337005 | 8ATTALA 500.00 | 0 |  | 1 | 25WP | 193 | 193 | 0 |  | 96.5529 | 96.7824 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 19 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T15275525WP | FROM->TO | DUKE MCADAMS 500/18.0KV TRANSFORMER CKT 1 | E | EES-EMI | EES-EMI | EES_MISS | EES_MISS | 0 | 337007 | 1ATTALA G2 18.000 | 337005 | 8ATTALA 500.00 | 0 |  | 1 | 25WP | 193 | 193 | 0 |  | 96.5529 | 96.7824 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 19 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | ISLAND-LOAD | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T12965525SP | TO->FROM | EARLSBORO 4138.00 - MAUD 138KV CKT 1 | E | OKGE | AEPW | SHAWNEE | PSO_EASTERN | 0 | 515055 | MAUD 4 138.00 | 510948 | EARLSBORO 4138.00 | 0 |  | 1 | 25SP | 98 | 98 | 0 | 96.7 | 96.7043 | 97.1 | [7 empty] | CATEGORYB | SINGLE | MAUD (MAUD1) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 515054 | MAUD 2 69.000 | 515055 | MAUD 4 138.00 | 515736 | MAUD 1 13.200 | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T13205525SP | FROM->TO | EAST PLANT INTERCHANGE - PIERCE STREET TAP 115KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524162 | EAST_PLANT 3115.00 | 524185 | PIERCE_TP 3115.00 | 0 |  | 1 | 25SP | 160 | 160 | 0 | 95.8 | 95.808 | 97.2 | [7 empty] | CATEGORYB | SINGLE | AMARILLO SOUTH INTERCHANGE (ABB 801466) 230/115/13.2KV TRANSFORMER CKT 1 | 1 | 524414 | AMA_SOUTH 3115.00 | 524415 | AMA_SOUTH 6230.00 | 524410 | AMA_SO_TR1 113.200 | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | NOT GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T19995516SP | FROM->TO | EDDY COUNTY INTERCHANGE 230/8.5KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-PECO | SPS-PECO | 0 | 527800 | EDDY_SOUTH 6230.00 | 527790 | EDDY_SVC 18.5000 | 0 |  | 1 | 16SP | 100 | 100 | 0 |  | 100 | 99.9 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 95 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | NOT GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T27955525SP | FROM->TO | EDDY COUNTY INTERCHANGE 230/8.5KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-PECO | SPS-PECO | 0 | 527800 | EDDY_SOUTH 6230.00 | 527790 | EDDY_SVC 18.5000 | 0 |  | 1 | 25SP | 100 | 100 | 0 |  | 100 | 95.2 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 115 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T6475520SP | FROM->TO | FAIRFAX 138/69KV TRANSFORMER CKT 1 | E | AECI | AECI | KAMO-OK | KAMO-OK | 0 | 300139 | 4FAIRFAX 138.00 | 300929 | 2FAIRFAX 69.000 | 0 |  | 1 | 20SP | 56 | 56 | 0 |  | 91.4049 | 96.7 | [7 empty] | CATEGORYB | SINGLE | HALLETT TAP - PAWNEE 69KV CKT 1 | 0 | 300934 | 2HALETTP 69.000 | 300939 | 2PAWNEE 69.000 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T6445520SP | FROM->TO | FAIRFAX 138/69KV TRANSFORMER CKT 1 | E | AECI | AECI | KAMO-OK | KAMO-OK | 0 | 300139 | 4FAIRFAX 138.00 | 300929 | 2FAIRFAX 69.000 | 0 |  | 1 | 20SP | 56 | 56 | 0 |  | 91.2456 | 96.6 | [7 empty] | CATEGORYB | SINGLE | CLEAVELAND - HALLETT TAP 69KV CKT 1 | 0 | 300927 | 2CLEVLND 69.000 | 300934 | 2HALETTP 69.000 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T9845015WP | FROM->TO | FITZHUGH 161/13.8KV TRANSFORMER CKT 1 | E | AEPW | AEPW | GREENWD AECC | GREENWD AECC | 0 | 503901 | FITZ_ST1 1 13.800 | 503902 | FITZHUGH 5 161.00 | 0 |  | 1 | 15WP | 65 | 65 | 0 |  | 99.1699 | 99.1841 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 44 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T10545016WP | FROM->TO | FITZHUGH 161/13.8KV TRANSFORMER CKT 1 | E | AEPW | AEPW | GREENWD AECC | GREENWD AECC | 0 | 503901 | FITZ_ST1 1 13.800 | 503902 | FITZHUGH 5 161.00 | 0 |  | 1 | 16WP | 65 | 65 | 0 |  | 98.8935 | 98.8941 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 44 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T11275020WP | FROM->TO | FITZHUGH 161/13.8KV TRANSFORMER CKT 1 | E | AEPW | AEPW | GREENWD AECC | GREENWD AECC | 0 | 503901 | FITZ_ST1 1 13.800 | 503902 | FITZHUGH 5 161.00 | 0 |  | 1 | 20WP | 65 | 65 | 0 |  | 97.0956 | 97.0759 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 48 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T15915025WP | FROM->TO | FITZHUGH 161/13.8KV TRANSFORMER CKT 1 | E | AEPW | AEPW | GREENWD AECC | GREENWD AECC | 0 | 503901 | FITZ_ST1 1 13.800 | 503902 | FITZHUGH 5 161.00 | 0 |  | 1 | 25WP | 65 | 65 | 0 |  | 95.7483 | 95.8311 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 48 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T1705520SP | FROM->TO | FPL SWITCH - MOORELAND 138KV CKT 1 | E | OKGE | WFEC | ENID | WFEC-NORTHFO | 0 | 515785 | WINDFRM4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 20SP | 268 | 287 | 0 |  | 56.0079 | 95.9 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T9015520WP | FROM->TO | FPL SWITCH - MOORELAND 138KV CKT 1 | E | OKGE | WFEC | ENID | WFEC-NORTHFO | 0 | 515785 | WINDFRM4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 20WP | 287 | 287 | 0 |  | 55.9375 | 97.8 | [7 empty] | CATEGORYB | NONSINGLE | SPSCONT-05B | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T8995520WP | FROM->TO | FPL SWITCH - MOORELAND 138KV CKT 1 | E | OKGE | WFEC | ENID | WFEC-NORTHFO | 0 | 515785 | WINDFRM4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | 20WP | 287 | 287 | 0 |  | 55.4445 | 97 | [7 empty] | CATEGORYB | NONSINGLE | SPSCONT-04 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3585515WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 15WP | 171 | 185 | 0 |  | 70.74 | 96.7 | [7 empty] | CATEGORYB | SINGLE | WOODWARD (WOODWRD2) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 514782 | WODWRD 2 69.000 | 514785 | WOODWRD4 138.00 | 515771 | WOODWR21 13.200 | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T18295516SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 16SP | 133 | 153 | 0 |  | 54.307 | 99.4 | [7 empty] | CATEGORYB | GENOUT | GEN515389 1-TLGAWND1 34.500 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T7995516SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 16SP | 133 | 153 | 0 |  | 53.6403 | 98.7 | [7 empty] | CATEGORYB | SINGLE | POTTER COUNTY INTERCHANGE (WAUK 90343-A) 345/230/13.2KV TRANSFORMER CKT 1 | 1 | 523959 | POTTER_CO 6230.00 | 523961 | POTTER_CO 7345.00 | 523957 | POTTER_TR 113.200 | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T1315516SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 16SP | 133 | 153 | 0 |  | 52.3575 | 98.6 | [7 empty] | CATEGORYB | SINGLE | FT SUPPLY - IODINE 138KV CKT 1 | 0 | 520920 | FTSUPLY4 138.00 | 520957 | IODINE 4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T19985516SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 16SP | 133 | 153 | 0 |  | 51.1795 | 95.9 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 66 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T555516WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 16WP | 171 | 185 | 0 |  | 57.3238 | 98.4 | [7 empty] | CATEGORYB | SINGLE | DEWEY - IODINE 138KV CKT 1 | 0 | 514787 | DEWEY 4 138.00 | 514796 | IODINE-4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T545516WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 16WP | 171 | 185 | 0 |  | 57.8383 | 98.3 | [7 empty] | CATEGORYB | SINGLE | WOODWARD - WOODWARD 69KV CKT 1 | 0 | 514782 | WODWRD 2 69.000 | 521096 | WOODWRD2 69.000 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T645516WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 16WP | 171 | 185 | 0 |  | 60.6987 | 97.7 | [7 empty] | CATEGORYB | SINGLE | BORDER 7345.00 - WOODWARD DISTRICT EHV 345KV CKT 1 | 0 | 515375 | WWRDEHV7 345.00 | 515458 | BORDER 7345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T24195520SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 20SP | 133 | 153 | 0 |  | 37.6136 | 96.4 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 96 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T24215520SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 20SP | 133 | 153 | 0 |  | 37.6136 | 96.4 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 97 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T24235520SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 20SP | 133 | 153 | 0 |  | 37.6136 | 96.4 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 98 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T24255520SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 20SP | 133 | 153 | 0 |  | 36.8595 | 95.7 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 99 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T24175520SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 20SP | 133 | 153 | 0 |  | 36.4591 | 95.3 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 94 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T24345520SP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 20SP | 133 | 153 | 0 |  | 38.6535 | 95.2 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 158 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T11545520WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 20WP | 171 | 185 | 0 |  | 47.9115 | 99.9 | [7 empty] | CATEGORYB | GENOUT | GEN515389 1-TLGAWND1 34.500 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T965520WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 20WP | 171 | 185 | 0 |  | 46.7878 | 99.4 | [7 empty] | CATEGORYB | SINGLE | SANDY_CN_138138.00 - WAKITA_138 138.00 138KV CKT 1 | 0 | 520204 | SANDY_CN_138138.00 | 520205 | WAKITA_138 138.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T12285520WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 20WP | 171 | 185 | 0 |  | 45.3536 | 96.9 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 60 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | INVALID |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T1685520WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 20WP | 171 | 185 | 0 |  | 44.5806 | 96.2979 | [7 empty] | CATEGORYB | SINGLE | FLATRDG3 - HARPER 138KV CKT 1 | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T12255520WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 20WP | 171 | 185 | 0 |  | 44.7911 | 96.2 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 55 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T12275520WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 20WP | 171 | 185 | 0 |  | 44.519 | 95.9 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 57 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T12295520WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 20WP | 171 | 185 | 0 |  | 44.4609 | 95.8 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 67 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T12315520WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 20WP | 171 | 185 | 0 |  | 44.4609 | 95.8 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 76 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T12305520WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 20WP | 171 | 185 | 0 |  | 44.0532 | 95.6 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 70 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T12325520WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 20WP | 171 | 185 | 0 |  | 44.1797 | 95.6 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 78 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T12265520WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 20WP | 171 | 185 | 0 |  | 43.887 | 95.3 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 56 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | CONT-LaCygne Neosho 345kv |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T1545520WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 20WP | 171 | 185 | 0 |  | 44.0004 | 95.2 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - NEOSHO 345KV CKT 1 | 0 | 532793 | NEOSHO 7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T6655525WP | TO->FROM | FPL SWITCH - WOODWARD 138KV CKT 1 | E | OKGE | OKGE | ENID | ENID | 0 | 514785 | WOODWRD4 138.00 | 515785 | WINDFRM4 138.00 | 0 |  | 1 | 25WP | 171 | 185 | 0 |  | 47.7156 | 98.1 | [7 empty] | CATEGORYB | SINGLE | WOODWARD (WOODWRD2) 138/69/13.2KV TRANSFORMER CKT 1 | 1 | 514782 | WODWRD 2 69.000 | 514785 | WOODWRD4 138.00 | 515771 | WOODWR21 13.200 | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2085525SP | TO->FROM | FRANKLIN SW - MIDWEST TAP 138KV CKT 1 | E | OKGE | WFEC |  | WFEC-RURAL | 0 | 514946 | MIDWEST4 138.00 | 520917 | FRNKLNS4 138.00 | 0 |  | 1 | 25SP | 268 | 287 | 308 |  | 92.6743 | 98.8 | [7 empty] | CATEGORYB | SINGLE | CANADIAN - CEDAR LANE 138KV CKT 1 | 0 | 514947 | CANADN-4 138.00 | 514948 | CEDARLN4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2095525SP | TO->FROM | FRANKLIN SW - MIDWEST TAP 138KV CKT 1 | E | OKGE | WFEC |  | WFEC-RURAL | 0 | 514946 | MIDWEST4 138.00 | 520917 | FRNKLNS4 138.00 | 0 |  | 1 | 25SP | 268 | 287 | 308 | 95.2 | 95.2103 | 98.7 | [7 empty] | CATEGORYB | SINGLE | HAMMETT TAP - HAMMETT2 138KV CKT 1 | 0 | 515046 | HAMMTAP4 138.00 | 520951 | HAMMETT4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2225525SP | TO->FROM | FRANKLIN SW - MIDWEST TAP 138KV CKT 1 | E | OKGE | WFEC |  | WFEC-RURAL | 0 | 514946 | MIDWEST4 138.00 | 520917 | FRNKLNS4 138.00 | 0 |  | 1 | 25SP | 268 | 287 | 308 |  | 93.8544 | 97.2 | [7 empty] | CATEGORYB | SINGLE | ANADARKO - POCASSETT 138KV CKT 1 | 0 | 520814 | ANADARK4 138.00 | 521031 | POCASET4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T12255016SP | FROM->TO | FT RANDAL - SPENCER 115KV CKT 1 | E | WAPA | NPPD | WAPA_1604 | NPPD_686 | 0 | 652510 | FTRANDL7 115.00 | 640349 | SPENCER7 115.00 | 0 |  | 1 | 16SP | 120 | 120 | 124 | 97.9 | 97.9069 | 98.4 | [7 empty] | CATEGORYB | NONSINGLE | LN-1091 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T4305025SP | FROM->TO | FT RANDAL - SPENCER 115KV CKT 1 | E | WAPA | NPPD | WAPA_1604 | NPPD_686 | 0 | 652510 | FTRANDL7 115.00 | 640349 | SPENCER7 115.00 | 0 |  | 1 | 25SP | 120 | 120 | 124 |  | 88.7644 | 97.9 | [7 empty] | CATEGORYB | SINGLE | HOLT.CO3 345.00 - YANKTON 345KV CKT 1 | 0 | 640510 | HOLT.CO3 345.00 | 652532 | GR PRAIRIE 3345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T645025SP | FROM->TO | GENTLMREDWIL | E |  |  |  |  | GENTLMREDWIL | 0 |  | 0 |  | 0 |  |  | 25SP | 349.7 | 349.7 | 349.7 | 103.1 | 103.0806 | 98.5 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | CONT-0803 - Hoyt - Stranger 345kV |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T1905516SP | TO->FROM | GOODYEAR JUNCTION - NORTHLAND 115KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 533169 | NTHLAND3 115.00 | 533162 | INDNOLA3 115.00 | 0 |  | 1 | 16SP | 179 | 179 | 0 |  | 94.5545 | 95.8 | [7 empty] | CATEGORYB | SINGLE | HOYT - STRANGER CREEK 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532772 | STRANGR7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | CONT-0803 - Hoyt - Stranger 345kV |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T4215525SP | TO->FROM | GOODYEAR JUNCTION - NORTHLAND 115KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 533169 | NTHLAND3 115.00 | 533162 | INDNOLA3 115.00 | 0 |  | 1 | 25SP | 179 | 179 | 0 |  | 91.8317 | 96.1 | [7 empty] | CATEGORYB | SINGLE | HOYT - STRANGER CREEK 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532772 | STRANGR7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3135516SP | TO->FROM | GRAND ISLAND - SWEETWATER 345KV CKT 1 | E | NPPD | NPPD | NPPD_686 | WAPA_1606 | 0 | 640374 | SWEET W3 345.00 | 652571 | GR ISLD3 345.00 | 0 |  | 1 | 16SP | 717 | 717 | 789 | 96.4 | 96.3639 | 97.9 | [7 empty] | CATEGORYB | SINGLE | AXTELL - SWEETWATER 345KV CKT 1 | 0 | 640065 | AXTELL 3 345.00 | 640374 | SWEET W3 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T4875520SP | TO->FROM | GREENSBURG - SSTARTP3 115.00 115KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539763 | SSTARTP3 115.00 | 539664 | GRNBURG3 115.00 | 0 |  | 1 | 20SP | 115.1 | 115.1 | 0 |  | 87.7573 | 97.5 | [7 empty] | CATEGORYB | SINGLE | CRKCK 3 115.00 - CUDAHY 115KV CKT 1 | 0 | 539659 | CUDAHY 3 115.00 | 539783 | CRKCK 3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | INVALID |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T4775520SP | TO->FROM | GREENSBURG - SSTARTP3 115.00 115KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539763 | SSTARTP3 115.00 | 539664 | GRNBURG3 115.00 | 0 |  | 1 | 20SP | 115.1 | 115.1 | 0 |  | 86.24 | 95.8541 | [7 empty] | CATEGORYB | SINGLE | CUDAHY - KISMET 3 115.00 115KV CKT 1 | 0 | 539646 | KISMET 3 115.00 | 539659 | CUDAHY 3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T17675520SP | TO->FROM | GREENSBURG - SSTARTP3 115.00 115KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539763 | SSTARTP3 115.00 | 539664 | GRNBURG3 115.00 | 0 |  | 1 | 20SP | 115.1 | 115.1 | 0 |  | 86.0831 | 95.7 | [7 empty] | CATEGORYB | NONSINGLE | SPP-MKEC-01 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | INVALID |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T5035525SP | TO->FROM | GREENSBURG - SSTARTP3 115.00 115KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539763 | SSTARTP3 115.00 | 539664 | GRNBURG3 115.00 | 0 |  | 1 | 25SP | 115.1 | 115.1 | 0 |  | 90.1905 | 99.416 | [7 empty] | CATEGORYB | SINGLE | CUDAHY - KISMET 3 115.00 115KV CKT 1 | 0 | 539646 | KISMET 3 115.00 | 539659 | CUDAHY 3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T21315525SP | TO->FROM | GREENSBURG - SSTARTP3 115.00 115KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539763 | SSTARTP3 115.00 | 539664 | GRNBURG3 115.00 | 0 |  | 1 | 25SP | 115.1 | 115.1 | 0 |  | 90.6409 | 96.1 | [7 empty] | CATEGORYB | NONSINGLE | SPP-MKEC-08 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T20755525SP | TO->FROM | GREENSBURG - SSTARTP3 115.00 115KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539763 | SSTARTP3 115.00 | 539664 | GRNBURG3 115.00 | 0 |  | 1 | 25SP | 115.1 | 115.1 | 0 |  | 84.5853 | 95.8 | [7 empty] | CATEGORYB | NONSINGLE | SPSCONT-06 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2415525SP | TO->FROM | GREENSBURG - SSTARTP3 115.00 115KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539763 | SSTARTP3 115.00 | 539664 | GRNBURG3 115.00 | 0 |  | 1 | 25SP | 115.1 | 115.1 | 0 |  | 87.3569 | 95.7 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | ISLAND-LOAD |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T12205520SP | FROM->TO | GYCOTAP3 115.00 - WEST DODGE 115KV CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539778 | GYCOTAP3 115.00 | 539699 | W-DODGE3 115.00 | 0 |  | 1 | 20SP | 106 | 113.9 | 0 |  | 51.5071 | 96.7 | [7 empty] | CATEGORYB | SINGLE | HAGGARD (HAGGARD3) 115/34.5/13.8KV TRANSFORMER CKT 1 | 1 | 539667 | HAGGARD3 115.00 | 539712 | HAGGARD1 34.500 | 539912 | HAGARD-T 13.800 | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T1765520SP | FROM->TO | HANCOCK - MUSKOGEE 161KV CKT 1 | E | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515250 | HANCOK-5 161.00 | 515222 | MUSKOGE5 161.00 | 0 |  | 1 | 20SP | 223 | 223 | 0 | 98.1 | 98.071 | 96.4 | [7 empty] | CATEGORYB | SINGLE | AGENCY - PECAN CREEK 161KV CKT 1 | 0 | 515230 | AGENCY 5 161.00 | 515234 | PECANCK5 161.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2155525SP | FROM->TO | HANCOCK - MUSKOGEE 161KV CKT 1 | E | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515250 | HANCOK-5 161.00 | 515222 | MUSKOGE5 161.00 | 0 |  | 1 | 25SP | 223 | 223 | 0 | 99.5 | 99.5312 | 98.5 | [7 empty] | CATEGORYB | SINGLE | AGENCY - EUCLID 161KV CKT 1 | 0 | 515230 | AGENCY 5 161.00 | 515251 | EUCLID 5 161.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2165525SP | FROM->TO | HANCOCK - MUSKOGEE 161KV CKT 1 | E | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 0 | 515250 | HANCOK-5 161.00 | 515222 | MUSKOGE5 161.00 | 0 |  | 1 | 25SP | 223 | 223 | 0 | 96.3 | 96.3072 | 95.3 | [7 empty] | CATEGORYB | SINGLE | EUCLID - MUSKOGEE PORT 161KV CKT 1 | 0 | 515232 | MSKPTAP5 161.00 | 515251 | EUCLID 5 161.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2505525SP | FROM->TO | Harrington Station Mid Bus - RANDALL COUNTY INTERCHANGE 230KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 523978 | HARRNG_MID 6230.00 | 524365 | RANDALL 6230.00 | 0 |  | 1 | 25SP | 436 | 502 | 0 |  | 89.789 | 96.7 | [7 empty] | CATEGORYB | SINGLE | AMARILLO SOUTH INTERCHANGE - NICHOLS STATION 230KV CKT 1 | 0 | 524044 | NICHOLS 6230.00 | 524415 | AMA_SOUTH 6230.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T5285525SP | TO->FROM | HARRIONSVILLE NORTH - RALPH GREEN 69KV CKT 1 | E | KCPL | KCPL |  |  | 0 | 541279 | RGREEN 2 69.000 | 541297 | HSNVLN 2 69.000 | 0 |  | 1 | 25SP | 43 | 49 | 49 | 95.5 | 95.5221 | 95.4 | [7 empty] | CATEGORYB | SINGLE | HARRISONVILLE - HARRISONVILLE SWITCHING 69KV CKT 1 | 0 | 541295 | HSNVL 2 69.000 | 541296 | HSNVLSW2 69.000 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T5285525SP | TO->FROM | HARRIONSVILLE NORTH - RALPH GREEN 69KV CKT 1 | E | KCPL | KCPL |  |  | 0 | 541279 | RGREEN 2 69.000 | 541297 | HSNVLN 2 69.000 | 0 |  | 1 | 25SP | 43 | 49 | 49 | 95.5 | 95.5221 | 95.4 | [7 empty] | CATEGORYB | SINGLE | HARRISONVILLE - HARRISONVILLE SWITCHING 69KV CKT 1 | 0 | 541295 | HSNVL 2 69.000 | 541296 | HSNVLSW2 69.000 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T13955516SP | FROM->TO | HARRISONVILLE 161/69KV TRANSFORMER CKT 2 | E | KCPL | KCPL |  |  | 0 | 541239 | HSNVL 5 161.00 | 541295 | HSNVL 2 69.000 | 0 |  | 2 | 16SP | 50 | 55 | 55 | 98.9 | 98.8534 | 99.2 | [7 empty] | CATEGORYB | NONSINGLE | SPP-MIPU-04 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T3175015WP | FROM->TO | HAYS PLANT - VINE STREET 115KV CKT 1 | E | MIDW | MIDW | REG E-IL | REG E-IL | 0 | 530562 | HAYS 3 115.00 | 530591 | VINE 3 115.00 | 0 |  | 1 | 15WP | 80 | 88 | 0 |  | 81.3049 | 97.7 | [7 empty] | CATEGORYB | SINGLE | KNOLL 230 (KNOLL T1) 230/115/11.49KV TRANSFORMER CKT 1 | 1 | 530558 | KNOLL 6 230.00 | 530561 | KNOLL 3 115.00 | 530629 | KNLL1 1 11.490 | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T14285516SP | TO->FROM | HOOVER NORTH - LAKERIDGE 138KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533053 | LAKERDG4 138.00 | 533049 | HOOVERN4 138.00 | 0 |  | 1 | 16SP | 369 | 382 | 0 |  | 93.018 | 99.2 | [7 empty] | CATEGORYB | NONSINGLE | WR-B3-7 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T14255516SP | TO->FROM | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 | 16SP | 1076 | 1076 | 0 | 98.6 | 98.5931 | 99.8 | [7 empty] | CATEGORYB | NONSINGLE | WR-B3-3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2295516SP | TO->FROM | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 | 16SP | 1076 | 1076 | 0 | 98.1 | 98.0593 | 99.2 | [7 empty] | CATEGORYB | SINGLE | AUBURN ROAD - JEFFREY ENERGY CENTER 230KV CKT 1 | 0 | 532851 | AUBURN 6 230.00 | 532852 | JEC 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T18815516SP | TO->FROM | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 | 16SP | 1076 | 1076 | 0 |  | 94.6483 | 95.8 | [7 empty] | CATEGORYB | GENOUT | GEN542962 2-IATAN UNIT #2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T17955520SP | TO->FROM | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 | 20SP | 1076 | 1076 | 0 |  | 93.4561 | 97.3 | [7 empty] | CATEGORYB | NONSINGLE | WR-B3-3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T4325520SP | TO->FROM | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 | 20SP | 1076 | 1076 | 0 |  | 92.9988 | 96.9 | [7 empty] | CATEGORYB | SINGLE | AUBURN ROAD - JEFFREY ENERGY CENTER 230KV CKT 1 | 0 | 532851 | AUBURN 6 230.00 | 532852 | JEC 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3985520SP | TO->FROM | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 | 20SP | 1076 | 1076 | 0 |  | 92.692 | 96.8 | [7 empty] | CATEGORYB | SINGLE | JEFFREY ENERGY CENTER - MORRIS COUNTY 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532770 | MORRIS 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T21475525SP | TO->FROM | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 | 25SP | 1076 | 1076 | 0 | 95.4 | 95.4165 | 98.1 | [7 empty] | CATEGORYB | NONSINGLE | WR-B3-3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T4545525SP | TO->FROM | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 | 25SP | 1076 | 1076 | 0 |  | 94.8921 | 97.6 | [7 empty] | CATEGORYB | SINGLE | AUBURN ROAD - JEFFREY ENERGY CENTER 230KV CKT 1 | 0 | 532851 | AUBURN 6 230.00 | 532852 | JEC 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T4265525SP | TO->FROM | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532766 | JEC N 7 345.00 | 532765 | HOYT 7 345.00 | 0 |  | 1 | 25SP | 1076 | 1076 | 0 |  | 92.876 | 96.8 | [7 empty] | CATEGORYB | SINGLE | JEFFREY ENERGY CENTER - MORRIS COUNTY 345KV CKT 1 | 0 | 532766 | JEC N 7 345.00 | 532770 | MORRIS 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T3765025SP | FROM->TO | HUDSON JUNCTION - PITTSBURG 69KV CKT 1 | E | WERE | WERE | SEAST | SEAST | 0 | 533764 | HUDSJCT2 69.000 | 533770 | PITTSBG2 69.000 | 0 |  | 1 | 25SP | 58 | 69 | 0 | 100 | 100.0423 | 97.5 | [7 empty] | CATEGORYB | SINGLE | LITCHFIELD - ROUSE 69KV CKT 1 | 0 | 533765 | LITCH 2 69.000 | 533771 | ROUSE 2 69.000 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T20015516SP | FROM->TO | IATAN 345/25.0KV TRANSFORMER CKT 1 | E | KCPL | KCPL | KACP | KACP | 0 | 542962 | IAT G2 1 25.000 | 542982 | IATAN 7 345.00 | 0 |  | 1 | 16SP | 1000 | 1000 | 0 |  | 95.1181 | 95.1461 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 128 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T24335520SP | FROM->TO | IATAN 345/25.0KV TRANSFORMER CKT 1 | E | KCPL | KCPL | KACP | KACP | 0 | 542962 | IAT G2 1 25.000 | 542982 | IATAN 7 345.00 | 0 |  | 1 | 20SP | 1000 | 1000 | 0 |  | 94.1877 | 95.3786 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 131 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T27985525SP | FROM->TO | IATAN 345/25.0KV TRANSFORMER CKT 1 | E | KCPL | KCPL | KACP | KACP | 0 | 542962 | IAT G2 1 25.000 | 542982 | IATAN 7 345.00 | 0 |  | 1 | 25SP | 1000 | 1000 | 0 |  | 93.9364 | 95.3362 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 143 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T895016SP | TO->FROM | JENSEN ROAD - JENSEN TAP 138KV CKT 1 | E | OKGE | OKGE |  |  | 0 | 514820 | JENSENT4 138.00 | 514821 | JENSEN 4 138.00 | 0 |  | 1 | 16SP | 191 | 191 | 0 | 96.9 | 96.9243 | 96.8 | [7 empty] | CATEGORYB | SINGLE | ONEY - WASHITA 138KV CKT 1 | 0 | 521017 | ONEY 4 138.00 | 521089 | WASHITA4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T885016SP | TO->FROM | JENSEN ROAD - JENSEN TAP 138KV CKT 1 | E | OKGE | OKGE |  |  | 0 | 514820 | JENSENT4 138.00 | 514821 | JENSEN 4 138.00 | 0 |  | 1 | 16SP | 191 | 191 | 0 | 95.7 | 95.6881 | 95.4 | [7 empty] | CATEGORYB | SINGLE | BINGER NIJECT - ONEY 138KV CKT 1 | 0 | 520827 | BINGERJ4 138.00 | 521017 | ONEY 4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T20785525SP | TO->FROM | JOAQUIN REC - LOGANSPORT 138KV CKT 1 | E | AEPW | AEPW | ROCKHILL | RHILL_NTEC | 0 | 509071 | LOGANSP4 138.00 | 509066 | JOAQUIN4 138.00 | 0 |  | 1 | 25SP | 185 | 215 | 0 | 95.9 | 95.8999 | 96.1 | [7 empty] | CATEGORYB | NONSINGLE | SPP-AEPW-33 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T2545025SP | FROM->TO | JONES STATION - LUBBOCK SOUTH INTERCHANGE 230KV CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 0 | 526337 | JONES 6230.00 | 526269 | LUBBCK_STH 6230.00 | 0 |  | 1 | 25SP | 502 | 502 | 0 | 97.7 | 97.6552 | 95.1 | [7 empty] | CATEGORYB | SINGLE | JONES STATION - LUBBOCK SOUTH INTERCHANGE 230KV CKT 2 | 0 | 526269 | LUBBCK_STH 6230.00 | 526337 | JONES 6230.00 | 0 |  | 2 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T2535025SP | FROM->TO | JONES STATION - LUBBOCK SOUTH INTERCHANGE 230KV CKT 2 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 0 | 526337 | JONES 6230.00 | 526269 | LUBBCK_STH 6230.00 | 0 |  | 2 | 25SP | 502 | 502 | 0 | 97.7 | 97.6552 | 95.1 | [7 empty] | CATEGORYB | SINGLE | JONES STATION - LUBBOCK SOUTH INTERCHANGE 230KV CKT 1 | 0 | 526269 | LUBBCK_STH 6230.00 | 526337 | JONES 6230.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T24315520SP | FROM->TO | JONES STATION 230/22.0KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 0 | 526331 | JONES_1 122.000 | 526337 | JONES 6230.00 | 0 |  | 1 | 20SP | 275 | 275 | 0 |  | 92.1419 | 95.019 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 103 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T8345516SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 16SP | 159.3 | 159.3 | 0 | 100.7 | 100.7209 | 99.3 | [7 empty] | CATEGORYB | SINGLE | MINGO (MINGO) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 531429 | MINGO 3 115.00 | 531451 | MINGO 7 345.00 | 531452 | MINGTER1 13.800 | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T14135516SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 16SP | 159.3 | 159.3 | 0 | 97 | 96.954 | 98.2 | [7 empty] | CATEGORYB | NONSINGLE | SPP-MKEC-01 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T1735516SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 16SP | 159.3 | 159.3 | 0 | 97.1 | 97.0916 | 97.5 | [7 empty] | CATEGORYB | SINGLE | CTU SUBLETTE - HASKELL 115KV CKT 1 | 0 | 531374 | HASKELL3 115.00 | 531442 | SAT-TAP3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T1815516SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 16SP | 159.3 | 159.3 | 0 | 96.2 | 96.163 | 97.4 | [7 empty] | CATEGORYB | SINGLE | MINGO - SETAB 345KV CKT 1 | 0 | 531451 | MINGO 7 345.00 | 531465 | SETAB 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2735516SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 16SP | 159.3 | 159.3 | 0 | 96.7 | 96.7479 | 97.4 | [7 empty] | CATEGORYB | SINGLE | GREENSBURG - SSTARTP3 115.00 115KV CKT 1 | 0 | 539664 | GRNBURG3 115.00 | 539763 | SSTARTP3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T8395516SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 16SP | 159.3 | 159.3 | 0 | 95.8 | 95.7882 | 97.3 | [7 empty] | CATEGORYB | SINGLE | SPEARVILLE (SPEARVL) 345/230/13.8KV TRANSFORMER CKT 1 | 1 | 531469 | SPERVIL7 345.00 | 539695 | SPEARVL6 230.00 | 531468 | SPERTER1 13.800 | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T1695516SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 16SP | 159.3 | 159.3 | 0 | 99 | 99.0472 | 97.1 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T1765516SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 16SP | 159.3 | 159.3 | 0 | 96.2 | 96.206 | 96.8 | [7 empty] | CATEGORYB | SINGLE | HASKELL - SEWARD-3 115KV CKT 1 | 0 | 531374 | HASKELL3 115.00 | 531467 | SEWARD-3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNSLock |  | FDNSLock |  | 5 | 5 | 2015AG1AFS22T115516SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 16SP | 159.3 | 159.3 | 0 | 95.9 | 95.9376 | 96.8 | [7 empty] | CATEGORYB | SINGLE | CONCORDIA (CONCORD6) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 539657 | CONCORD3 115.00 | 539658 | CONCRD6 230.00 | 539904 | CONCOD-T 13.800 | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNSLock |  | FDNSLock |  | 5 | 5 | 2015AG1AFS22T25516SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 16SP | 159.3 | 159.3 | 0 | 96 | 95.9709 | 96.8 | [7 empty] | CATEGORYB | SINGLE | CONCORDIA - ELM CREEK 230KV CKT 1 | 0 | 539639 | ELMCREK6 230.00 | 539658 | CONCRD6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T1705516SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 16SP | 159.3 | 159.3 | 0 |  | 93.4365 | 96.4 | [7 empty] | CATEGORYB | SINGLE | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2655516SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 16SP | 159.3 | 159.3 | 0 | 95.2 | 95.2337 | 96 | [7 empty] | CATEGORYB | SINGLE | CIMARRON RIVER PLANT - N-CIMRN3 115.00 115KV CKT 1 | 0 | 539654 | CIM-PLT3 115.00 | 539749 | N-CIMRN3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T7285016SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 16SP | 159.3 | 159.3 | 0 | 95.4 | 95.4072 | 95.6 | [7 empty] | CATEGORYB | SINGLE | HOLCOMB (HOLCOMB) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 531448 | HOLCOMB3 115.00 | 531449 | HOLCOMB7 345.00 | 531450 | HOLCTER1 13.800 | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T1165516SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 16SP | 159.3 | 159.3 | 0 |  | 94.0029 | 95.4 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T14185516SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 16SP | 159.3 | 159.3 | 0 |  | 92.9745 | 95.3 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-05 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T755516WP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 16WP | 159.3 | 159.3 | 0 | 96.8 | 96.8139 | 98.8 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T855516WP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 16WP | 159.3 | 159.3 | 0 | 95.6 | 95.5714 | 96.2 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3945516WP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 16WP | 159.3 | 159.3 | 0 |  | 91.2222 | 95.1 | [7 empty] | CATEGORYB | SINGLE | SPEARVILLE (SPEARVL) 345/230/13.8KV TRANSFORMER CKT 1 | 1 | 531469 | SPERVIL7 345.00 | 539695 | SPEARVL6 230.00 | 531468 | SPERTER1 13.800 | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3625520SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 20SP | 159.3 | 159.3 | 0 | 95.6 | 95.5875 | 99.2 | [7 empty] | CATEGORYB | SINGLE | CTU SUBLETTE - HASKELL 115KV CKT 1 | 0 | 531374 | HASKELL3 115.00 | 531442 | SAT-TAP3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3775520SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 20SP | 159.3 | 159.3 | 0 |  | 94.9878 | 98.8 | [7 empty] | CATEGORYB | SINGLE | MINGO - SETAB 345KV CKT 1 | 0 | 531451 | MINGO 7 345.00 | 531465 | SETAB 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T6865020SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 20SP | 159.3 | 159.3 | 0 | 97.4 | 97.39 | 98.4 | [7 empty] | CATEGORYB | SINGLE | HOLCOMB (HOLCOMB) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 531448 | HOLCOMB3 115.00 | 531449 | HOLCOMB7 345.00 | 531450 | HOLCTER1 13.800 | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T17685520SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 20SP | 159.3 | 159.3 | 0 |  | 94.3048 | 98.1 | [7 empty] | CATEGORYB | NONSINGLE | SPP-MKEC-01 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T4895520SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 20SP | 159.3 | 159.3 | 0 |  | 94.3131 | 97.9 | [7 empty] | CATEGORYB | SINGLE | GREENSBURG - SSTARTP3 115.00 115KV CKT 1 | 0 | 539664 | GRNBURG3 115.00 | 539763 | SSTARTP3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3655520SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 20SP | 159.3 | 159.3 | 0 |  | 94.889 | 97.5 | [7 empty] | CATEGORYB | SINGLE | HASKELL - SEWARD-3 115KV CKT 1 | 0 | 531374 | HASKELL3 115.00 | 531467 | SEWARD-3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3565520SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 20SP | 159.3 | 159.3 | 0 | 96 | 96.0012 | 97.4 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T4815520SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 20SP | 159.3 | 159.3 | 0 |  | 93.5469 | 96.1 | [7 empty] | CATEGORYB | SINGLE | CIMARRON RIVER PLANT - N-CIMRN3 115.00 115KV CKT 1 | 0 | 539654 | CIM-PLT3 115.00 | 539749 | N-CIMRN3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3805520SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 20SP | 159.3 | 159.3 | 0 |  | 93.5591 | 96.1 | [7 empty] | CATEGORYB | SINGLE | N-CIMRN3 115.00 - SEWARD-3 115KV CKT 1 | 0 | 531467 | SEWARD-3 115.00 | 539749 | N-CIMRN3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3595520SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 20SP | 159.3 | 159.3 | 0 |  | 90.1738 | 95.9 | [7 empty] | CATEGORYB | SINGLE | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T11535520SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 20SP | 159.3 | 159.3 | 0 |  | 92.1408 | 95.5 | [7 empty] | CATEGORYB | SINGLE | SPEARVILLE (SPEARVL) 345/230/13.8KV TRANSFORMER CKT 1 | 1 | 531469 | SPERVIL7 345.00 | 539695 | SPEARVL6 230.00 | 531468 | SPERTER1 13.800 | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T1725520SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 20SP | 159.3 | 159.3 | 0 |  | 90.6664 | 95.1 | [7 empty] | CATEGORYB | SINGLE | NORTHWEST - TATONGA7 345.00 345KV CKT 1 | 0 | 514880 | NORTWST7 345.00 | 515407 | TATONGA7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T1095520WP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 20WP | 159.3 | 159.3 | 0 | 95.2 | 95.2265 | 97.5 | [7 empty] | CATEGORYB | SINGLE | FINNEY SWITCHING STATION - Hitchland Interchange 345KV CKT 1 | 0 | 523097 | HITCHLAND 7345.00 | 523853 | FINNEY 7345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T9085520WP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 20WP | 159.3 | 159.3 | 0 |  | -999 | 97.3 | [7 empty] | CATEGORYB | NONSINGLE | SPP-MKEC-01 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T5105525SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 25SP | 159.3 | 159.3 | 0 | 95.5 | 95.5371 | 99.8 | [7 empty] | CATEGORYB | SINGLE | GREENSBURG - SSTARTP3 115.00 115KV CKT 1 | 0 | 539664 | GRNBURG3 115.00 | 539763 | SSTARTP3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T4105525SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 25SP | 159.3 | 159.3 | 0 | 95.3 | 95.3173 | 98.6 | [7 empty] | CATEGORYB | SINGLE | N-CIMRN3 115.00 - SEWARD-3 115KV CKT 1 | 0 | 531467 | SEWARD-3 115.00 | 539749 | N-CIMRN3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T4075525SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 25SP | 159.3 | 159.3 | 0 |  | 94.7975 | 98.6 | [7 empty] | CATEGORYB | SINGLE | MINGO - SETAB 345KV CKT 1 | 0 | 531451 | MINGO 7 345.00 | 531465 | SETAB 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T5085525SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 25SP | 159.3 | 159.3 | 0 | 95.3 | 95.2972 | 98.3 | [7 empty] | CATEGORYB | SINGLE | CIMARRON RIVER PLANT - N-CIMRN3 115.00 115KV CKT 1 | 0 | 539654 | CIM-PLT3 115.00 | 539749 | N-CIMRN3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T12315025SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 25SP | 159.3 | 159.3 | 0 | 97 | 96.989 | 98 | [7 empty] | CATEGORYB | SINGLE | HOLCOMB (HOLCOMB) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 531448 | HOLCOMB3 115.00 | 531449 | HOLCOMB7 345.00 | 531450 | HOLCTER1 13.800 | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3855525SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 25SP | 159.3 | 159.3 | 0 | 96 | 95.9672 | 97.4 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T14035525SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 25SP | 159.3 | 159.3 | 0 |  | 93.2693 | 97.4 | [7 empty] | CATEGORYB | SINGLE | SPEARVILLE (SPEARVL) 345/230/13.8KV TRANSFORMER CKT 1 | 1 | 531469 | SPERVIL7 345.00 | 539695 | SPEARVL6 230.00 | 531468 | SPERTER1 13.800 | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3875525SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 25SP | 159.3 | 159.3 | 0 |  | 90.375 | 96.7 | [7 empty] | CATEGORYB | SINGLE | SMOKYHL6 230.00 - SUMMIT 230KV CKT 1 | 0 | 530592 | SMOKYHL6 230.00 | 532873 | SUMMIT 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3885525SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 25SP | 159.3 | 159.3 | 0 |  | 93.0747 | 95.8 | [7 empty] | CATEGORYB | SINGLE | 5 HICKOCK - RUBART 3 115.00 115KV CKT 1 | 0 | 531200 | RUBART 3 115.00 | 531378 | HICKOCK3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T12275025SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 25SP | 159.3 | 159.3 | 0 | 95 | 95.0292 | 95.8 | [7 empty] | CATEGORYB | SINGLE | MINGO (MINGO) 345/115/13.8KV TRANSFORMER CKT 1 | 1 | 531429 | MINGO 3 115.00 | 531451 | MINGO 7 345.00 | 531452 | MINGTER1 13.800 | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T4055525SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 25SP | 159.3 | 159.3 | 0 |  | 92.0594 | 95.5 | [7 empty] | CATEGORYB | SINGLE | HOLCOMB - SETAB 345KV CKT 1 | 0 | 531449 | HOLCOMB7 345.00 | 531465 | SETAB 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T13935525SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 25SP | 159.3 | 159.3 | 0 |  | 91.5671 | 95.4 | [7 empty] | CATEGORYB | SINGLE | RICE 6 230.00 (RICE T1) 230/115/12.47KV TRANSFORMER CKT 1 | 1 | 530623 | RICE 3 115.00 | 530686 | RICE 6 230.00 | 530687 | RICET1 12.470 | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3865525SP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 25SP | 159.3 | 159.3 | 0 |  | 90.2257 | 95.3 | [7 empty] | CATEGORYB | SINGLE | AXTELL - POST ROCK 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 640065 | AXTELL 3 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNSLock |  | FDNS |  | 5 | 5 | 2015AG1AFS21T11285525WP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 25WP | 159.3 | 159.3 | 0 | 95.4 | -999 | 98.4 | [7 empty] | CATEGORYB | NONSINGLE | SPP-MKEC-01 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2445525WP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 25WP | 159.3 | 159.3 | 0 |  | 93.0873 | 96.3 | [7 empty] | CATEGORYB | SINGLE | GREENSBURG - SSTARTP3 115.00 115KV CKT 1 | 0 | 539664 | GRNBURG3 115.00 | 539763 | SSTARTP3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2245525WP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 25WP | 159.3 | 159.3 | 0 |  | 94.2916 | 95.3 | [7 empty] | CATEGORYB | SINGLE | POST ROCK - SPEARVILLE 345KV CKT 1 | 0 | 530583 | POSTROCK7 345.00 | 531469 | SPERVIL7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T7125525WP | FROM->TO | JUDSON LARGE 115/15.0KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 0 | 539670 | FTDODGP1 15.000 | 539671 | FTDODGE3 115.00 | 0 |  | 1 | 25WP | 159.3 | 159.3 | 0 |  | 91.9369 | 95.3 | [7 empty] | CATEGORYB | SINGLE | SPEARVILLE (SPEARVL) 345/230/13.8KV TRANSFORMER CKT 1 | 1 | 531469 | SPERVIL7 345.00 | 539695 | SPEARVL6 230.00 | 531468 | SPERTER1 13.800 | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2255516SP | FROM->TO | LAWRENCE ENERGY CENTER UNIT 5 230/24.0KV TRANSFORMER CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532663 | LEC U5 24.000 | 532854 | LEC U5 6 230.00 | 0 |  | 1 | 16SP | 448 | 448 | 0 | 96.6 | 96.635 | 96.5 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - WAVERLY7 345.00 345KV CKT 1 | 0 | 532799 | WAVERLY7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T1895516SP | FROM->TO | LAWRENCE ENERGY CENTER UNIT 5 230/24.0KV TRANSFORMER CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532663 | LEC U5 24.000 | 532854 | LEC U5 6 230.00 | 0 |  | 1 | 16SP | 448 | 448 | 0 | 96.1 | 96.0779 | 96.2 | [7 empty] | CATEGORYB | SINGLE | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T4295520SP | FROM->TO | LAWRENCE ENERGY CENTER UNIT 5 230/24.0KV TRANSFORMER CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532663 | LEC U5 24.000 | 532854 | LEC U5 6 230.00 | 0 |  | 1 | 20SP | 448 | 448 | 0 | 96.5 | 96.5079 | 97.5 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - WAVERLY7 345.00 345KV CKT 1 | 0 | 532799 | WAVERLY7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3905520SP | FROM->TO | LAWRENCE ENERGY CENTER UNIT 5 230/24.0KV TRANSFORMER CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532663 | LEC U5 24.000 | 532854 | LEC U5 6 230.00 | 0 |  | 1 | 20SP | 448 | 448 | 0 | 95.3 | 95.3378 | 96.4 | [7 empty] | CATEGORYB | SINGLE | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T4515525SP | FROM->TO | LAWRENCE ENERGY CENTER UNIT 5 230/24.0KV TRANSFORMER CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532663 | LEC U5 24.000 | 532854 | LEC U5 6 230.00 | 0 |  | 1 | 25SP | 448 | 448 | 0 | 96.7 | 96.6924 | 98.3 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - WAVERLY7 345.00 345KV CKT 1 | 0 | 532799 | WAVERLY7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T4175525SP | FROM->TO | LAWRENCE ENERGY CENTER UNIT 5 230/24.0KV TRANSFORMER CKT 1 | E | WERE | WERE | NEAST | NEAST | 0 | 532663 | LEC U5 24.000 | 532854 | LEC U5 6 230.00 | 0 |  | 1 | 25SP | 448 | 448 | 0 | 95.8 | 95.8164 | 96.3 | [7 empty] | CATEGORYB | SINGLE | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | INVALID | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T625020WP | TO->FROM | LEA COUNTY REC -MHOON - LEA COUNTY REC-LOVINGTON INTERCHANGE 69KV CKT 1 | E | SPS | SPS | SPS-LEA | SPS-LEA | 0 | 528618 | LE-LOVINTON269.000 | 528667 | LE-MHOON 269.000 | 0 |  | 1 | 20WP | 41 | 54 | 0 | 98.6 | 98.5691 | 99.9573 | [7 empty] | CATEGORYB | SINGLE | BUCKEYE TAP - CUNNINGHAM STATION 115KV CKT 1 | 0 | 527864 | CUNNINHAM 3115.00 | 528348 | BUCKEYE_TP 3115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | INVALID | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T1145025WP | FROM->TO | LEA COUNTY REC-LOVINGTON INTERCHANGE - LEA COUNTY REC-SAUNDERS TAP 69KV CKT 1 | E | SPS | SPS | SPS-LEA | SPS-LEA | 0 | 528618 | LE-LOVINTON269.000 | 528638 | LE-SAUNDRTP269.000 | 0 |  | 1 | 25WP | 41 | 54 | 0 | 98.1 | 98.0593 | 96.9304 | [7 empty] | CATEGORYB | SINGLE | BUCKEYE TAP - CUNNINGHAM STATION 115KV CKT 1 | 0 | 527864 | CUNNINHAM 3115.00 | 528348 | BUCKEYE_TP 3115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T2605025SP | TO->FROM | LEA COUNTY REC-PLAINS INTERCHANGE - YOAKUM COUNTY INTERCHANGE 115KV CKT 1 | E | SPS | SPS | SPS-YOGS | SPS-YOGS | 0 | 526934 | YOAKUM 3115.00 | 526928 | LE-PLNSINT 3115.00 | 0 |  | 1 | 25SP | 159 | 160 | 0 | 96.4 | 96.3531 | 96.4 | [7 empty] | CATEGORYB | SINGLE | PACIFIC SUB - SUNDOWN INTERCHANGE 115KV CKT 1 | 0 | 526424 | PACIFIC 3115.00 | 526434 | SUNDOWN 3115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T21365525SP | FROM->TO | MANHATTAN SUB - RANDALL COUNTY INTERCHANGE 115KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524224 | MANHATTAN 3115.00 | 524364 | RANDALL 3115.00 | 0 |  | 1 | 25SP | 160 | 160 | 0 |  | 91.1394 | 98.9 | [7 empty] | CATEGORYB | NONSINGLE | SPP-SWPS-K19 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T12475016SP | FROM->TO | MCDOWELL CREEK (MCDO TX-1) 230/115/13.8KV TRANSFORMER CKT 1 | E | WERE | WERE | NCENTRAL | NCENTRAL | 2 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 | 16SP | 201 | 239 | 0 | 99.6 | 99.6044 | 98.5 | [7 empty] | CATEGORYB | NONSINGLE | WR-B3-10 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | CONT-0900 - JEC - East Manhattan 230kV | FDNSLock |  | FDNS |  | 5 | 0 | 2015AG1AFS21T1735016SP | FROM->TO | MCDOWELL CREEK (MCDO TX-1) 230/115/13.8KV TRANSFORMER CKT 1 | E | WERE | WERE | NCENTRAL | NCENTRAL | 2 | 532862 | MCDOWEL6 230.00 | 533335 | MCDOWEL3 115.00 | 532898 | MCDOWL 1 13.800 | 1 | 16SP | 201 | 239 | 0 | 99.3 | -999 | 98.2 | [7 empty] | CATEGORYB | SINGLE | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 0 | 532852 | JEC 6 230.00 | 532861 | EMANHAT6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T28015525SP | TO->FROM | MONT 7 115.00 - WILLISTON27 115.00 115KV CKT 1 | E | WAPA | WAPA | WAPA_1602 | BEPC_1628 | 0 | 652391 | WILLISTON27 115.00 | 659360 | MONT 7 115.00 | 0 |  | 1 | 25SP | 120 | 120 | 0 |  | 98.0945 | 98.1 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 202 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T5175520SP | FROM->TO | MONTROSE 161/18.0KV TRANSFORMER CKT 1 | E | KCPL | KCPL | KACP | METRO | 0 | 542954 | MONTG3 1 18.000 | 542995 | MONTROS5 161.00 | 0 |  | 1 | 20SP | 210 | 210 | 0 |  | 94.136 | 96 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T5385525SP | FROM->TO | MONTROSE 161/18.0KV TRANSFORMER CKT 1 | E | KCPL | KCPL | KACP | METRO | 0 | 542954 | MONTG3 1 18.000 | 542995 | MONTROS5 161.00 | 0 |  | 1 | 25SP | 210 | 210 | 0 |  | 94.6968 | 96.3 | [7 empty] | CATEGORYB | SINGLE | LACYGNE - STILWELL 345KV CKT 1 | 0 | 542968 | STILWEL7 345.00 | 542981 | LACYGNE7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3275525SP | FROM->TO | National Enrichment Plant Sub - TARGA 3115.00 115KV CKT 1 | E | SPS | SPS | SPS-HOBB | SPS-HOBB | 0 | 528603 | NA_ENRICH 3115.00 | 528605 | TARGA 3115.00 | 0 |  | 1 | 25SP | 276 | 304 | 0 |  | -999 | 98.3 | [7 empty] | CATEGORYB | SINGLE | HOBBS - KIOWA 7345.00 345KV CKT 1 | 0 | 527896 | HOBBS_INT 7345.00 | 527965 | KIOWA 7345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T11225525WP | TO->FROM | NEW PROSPEST - ROCK HILL 138KV CKT 1 | E | AEPW | AEPW | ROCKHILL | RHILL_NTEC | 0 | 509083 | ROKHILL4 138.00 | 509102 | NEWPROS4 138.00 | 0 |  | 1 | 25WP | 287 | 287 | 0 | 96 | 95.9948 | 96 | [7 empty] | CATEGORYB | NONSINGLE | SPP-AEPW-30 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | INVALID | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T555525WP | TO->FROM | NEW PROSPEST - ROCK HILL 138KV CKT 1 | E | AEPW | AEPW | ROCKHILL | RHILL_NTEC | 0 | 509083 | ROKHILL4 138.00 | 509102 | NEWPROS4 138.00 | 0 |  | 1 | 25WP | 287 | 287 | 0 | 96 | 95.9558 | 95.9572 | [7 empty] | CATEGORYB | SINGLE | STONEWALL - WESTERN ELECTRIC T 138KV CKT 1 | 0 | 507768 | WESTELT4 138.00 | 509052 | STONWAL4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | INVALID | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T1795016SP | TO->FROM | NORTH STREET - NORTHVIEW 115KV CKT 1 | E | WERE | WERE | WEST | WEST | 0 | 533371 | NORTHVW3 115.00 | 533370 | NORTHST3 115.00 | 0 |  | 1 | 16SP | 68 | 68 | 0 | 101.2 | 101.1739 | 99.574 | [7 empty] | CATEGORYB | SINGLE | NORTH STREET - NORTHVIEW 115KV CKT 2 | 0 | 533370 | NORTHST3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 2 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T3595025SP | TO->FROM | NORTH STREET - NORTHVIEW 115KV CKT 1 | E | WERE | WERE | WEST | WEST | 0 | 533371 | NORTHVW3 115.00 | 533370 | NORTHST3 115.00 | 0 |  | 1 | 25SP | 68 | 68 | 0 |  | 85.1914 | 96.1 | [7 empty] | CATEGORYB | SINGLE | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | 0 | 533368 | EXIDE J3 115.00 | 533372 | PHILIPS3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T18955025SP | TO->FROM | NORTH STREET - NORTHVIEW 115KV CKT 1 | E | WERE | WERE | WEST | WEST | 0 | 533371 | NORTHVW3 115.00 | 533370 | NORTHST3 115.00 | 0 |  | 1 | 25SP | 68 | 68 | 0 |  | 85.0928 | 96 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WR-330 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | INVALID | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T1785016SP | TO->FROM | NORTH STREET - NORTHVIEW 115KV CKT 2 | E | WERE | WERE | WEST | WEST | 0 | 533371 | NORTHVW3 115.00 | 533370 | NORTHST3 115.00 | 0 |  | 2 | 16SP | 68 | 68 | 0 | 101.2 | 101.1739 | 99.574 | [7 empty] | CATEGORYB | SINGLE | NORTH STREET - NORTHVIEW 115KV CKT 1 | 0 | 533370 | NORTHST3 115.00 | 533371 | NORTHVW3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T3605025SP | TO->FROM | NORTH STREET - NORTHVIEW 115KV CKT 2 | E | WERE | WERE | WEST | WEST | 0 | 533371 | NORTHVW3 115.00 | 533370 | NORTHST3 115.00 | 0 |  | 2 | 25SP | 68 | 68 | 0 |  | 85.1914 | 96.1 | [7 empty] | CATEGORYB | SINGLE | EXIDE JUNCTION - NORTH AMERICAN PHILIPS 115KV CKT 1 | 0 | 533368 | EXIDE J3 115.00 | 533372 | PHILIPS3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T18965025SP | TO->FROM | NORTH STREET - NORTHVIEW 115KV CKT 2 | E | WERE | WERE | WEST | WEST | 0 | 533371 | NORTHVW3 115.00 | 533370 | NORTHST3 115.00 | 0 |  | 2 | 25SP | 68 | 68 | 0 |  | 85.0928 | 96 | [7 empty] | CATEGORYB | NONSINGLE | SPP-WR-330 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2485525SP | TO->FROM | NORTHWEST INTERCHANGE - ROLLHILLS 3115.00 115KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524007 | ROLLHILLS 3115.00 | 524106 | NORTHWEST 3115.00 | 0 |  | 1 | 25SP | 120 | 154 | 0 | 97.3 | 97.2916 | 99.9 | [7 empty] | CATEGORYB | SINGLE | HASTINGS SUB - ROLLHILLS 3115.00 115KV CKT 1 | 0 | 524007 | ROLLHILLS 3115.00 | 524136 | HASTINGS 3115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T27915525SP | TO->FROM | NORTHWEST INTERCHANGE - ROLLHILLS 3115.00 115KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524007 | ROLLHILLS 3115.00 | 524106 | NORTHWEST 3115.00 | 0 |  | 1 | 25SP | 120 | 154 | 0 |  | 97.4715 | 99.9 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 107 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T11345525SP | TO->FROM | NORTHWEST INTERCHANGE - ROLLHILLS 3115.00 115KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524007 | ROLLHILLS 3115.00 | 524106 | NORTHWEST 3115.00 | 0 |  | 1 | 25SP | 120 | 154 | 0 | 97.2 | 97.2125 | 99.5 | [7 empty] | CATEGORYB | SINGLE | LAWRENCE PARK SUB 2 (WEST) - LAWRENCE PARK SUB1 (EAST) 69KV CKT @1 | 0 | 524209 | LAWRENPRK1 269.000 | 524216 | LAWRENPRK2 269.000 | 0 |  | @1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T25315025SP | TO->FROM | NORTHWEST INTERCHANGE - ROLLHILLS 3115.00 115KV CKT 1 | E | SPS | SPS | SPS-AMA | SPS-AMA | 0 | 524007 | ROLLHILLS 3115.00 | 524106 | NORTHWEST 3115.00 | 0 |  | 1 | 25SP | 120 | 154 | 0 |  | 100.3373 | 97.4 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 106 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T2255016SP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 16SP | 103 | 129 | 0 | 98 | 97.9593 | 99.2 | [7 empty] | CATEGORYB | SINGLE | ANTELOPE VALLEY - CHARLIE CREEK 345KV CKT 1 | 0 | 659101 | ANTELOP3 345.00 | 659183 | CHAR.CK3 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T5725520SP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 20SP | 103 | 129 | 0 |  | 70.1079 | 96.9 | [7 empty] | CATEGORYB | SINGLE | HOLT.CO3 345.00 - YANKTON 345KV CKT 1 | 0 | 640510 | HOLT.CO3 345.00 | 652532 | GR PRAIRIE 3345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T1475020WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 20WP | 103 | 129 | 0 |  | 87.8502 | 99.6 | [7 empty] | CATEGORYB | SINGLE | DGLASCRK-CP7115.00 - ROSEGLEN-CP7115.00 115KV CKT 1 | 0 | 659661 | DGLASCRK-CP7115.00 | 659662 | ROSEGLEN-CP7115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T1075020WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 20WP | 103 | 129 | 0 |  | 72.8131 | 99.2 | [7 empty] | CATEGORYB | SINGLE | HOLT.CO3 345.00 - YANKTON 345KV CKT 1 | 0 | 640510 | HOLT.CO3 345.00 | 652532 | GR PRAIRIE 3345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2465520WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 20WP | 103 | 129 | 0 |  | 86.8933 | 99 | [7 empty] | CATEGORYB | SINGLE | DGLASCRK-CP7115.00 - ROSEGLEN-CP7115.00 115KV CKT 1 | 0 | 659661 | DGLASCRK-CP7115.00 | 659662 | ROSEGLEN-CP7115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T1335020WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 20WP | 103 | 129 | 0 |  | 85.8287 | 97.4 | [7 empty] | CATEGORYB | SINGLE | CHARLIE CREEK - JUDSON 3345.00 345KV CKT 1 | 0 | 659183 | CHAR.CK3 345.00 | 659333 | JUDSON 3345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T1325020WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 20WP | 103 | 129 | 0 |  | 85.1837 | 97 | [7 empty] | CATEGORYB | SINGLE | DUNNING - RUTHVILLECP7115.00 115KV CKT 1 | 0 | 659165 | RUTHVILLECP7115.00 | 659166 | DUNNING7 115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2325520WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 20WP | 103 | 129 | 0 |  | 84.6713 | 96.8 | [7 empty] | CATEGORYB | SINGLE | CHARLIE CREEK - JUDSON 3345.00 345KV CKT 1 | 0 | 659183 | CHAR.CK3 345.00 | 659333 | JUDSON 3345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2315520WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 20WP | 103 | 129 | 0 |  | 83.9871 | 95.9 | [7 empty] | CATEGORYB | SINGLE | DUNNING - RUTHVILLECP7115.00 115KV CKT 1 | 0 | 659165 | RUTHVILLECP7115.00 | 659166 | DUNNING7 115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T2195025WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 25WP | 103 | 129 | 0 |  | 87.7801 | 99.9 | [7 empty] | CATEGORYB | SINGLE | DGLASCRK-CP7115.00 - ROSEGLEN-CP7115.00 115KV CKT 1 | 0 | 659661 | DGLASCRK-CP7115.00 | 659662 | ROSEGLEN-CP7115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3285525WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 25WP | 103 | 129 | 0 |  | 89.8879 | 99.8 | [7 empty] | CATEGORYB | SINGLE | DGLASCRK-CP7115.00 - ROSEGLEN-CP7115.00 115KV CKT 1 | 0 | 659661 | DGLASCRK-CP7115.00 | 659662 | ROSEGLEN-CP7115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T1765025WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 25WP | 103 | 129 | 0 |  | 72.8687 | 98.9 | [7 empty] | CATEGORYB | SINGLE | HOLT.CO3 345.00 - YANKTON 345KV CKT 1 | 0 | 640510 | HOLT.CO3 345.00 | 652532 | GR PRAIRIE 3345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T2055025WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 25WP | 103 | 129 | 0 |  | 85.7935 | 97.7 | [7 empty] | CATEGORYB | SINGLE | CHARLIE CREEK - JUDSON 3345.00 345KV CKT 1 | 0 | 659183 | CHAR.CK3 345.00 | 659333 | JUDSON 3345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T2045025WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 25WP | 103 | 129 | 0 |  | 84.8643 | 97.3 | [7 empty] | CATEGORYB | SINGLE | DUNNING - RUTHVILLECP7115.00 115KV CKT 1 | 0 | 659165 | RUTHVILLECP7115.00 | 659166 | DUNNING7 115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3145525WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 25WP | 103 | 129 | 0 |  | 85.8302 | 96.9 | [7 empty] | CATEGORYB | SINGLE | CHARLIE CREEK - JUDSON 3345.00 345KV CKT 1 | 0 | 659183 | CHAR.CK3 345.00 | 659333 | JUDSON 3345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3135525WP | FROM->TO | OAHE 115/13.8KV TRANSFORMER CKT 1 | E | WAPA | WAPA | WAPA_1603 | WAPA_1603 | 0 | 652559 | OAHE 1G 13.800 | 652520 | OAHE 7 115.00 | 0 |  | 1 | 25WP | 103 | 129 | 0 |  | 85.1241 | 96 | [7 empty] | CATEGORYB | SINGLE | DUNNING - RUTHVILLECP7115.00 115KV CKT 1 | 0 | 659165 | RUTHVILLECP7115.00 | 659166 | DUNNING7 115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T4575520SP | FROM->TO | OAK - RAINBOW 69KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 533547 | OAK 2 69.000 | 533549 | RAINBOW2 69.000 | 0 |  | 1 | 20SP | 43 | 43 | 0 |  | 36.2551 | 97.2 | [7 empty] | CATEGORYB | SINGLE | OAK - STROTHER FIELD (CITY OF WINFIELD) 69KV CKT 1 | 0 | 533547 | OAK 2 69.000 | 533556 | STROTHR2 69.000 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T5065520SP | FROM->TO | ODESSA 161/69KV TRANSFORMER CKT 1 | E | KCPL | KCPL |  |  | 0 | 541229 | ODESSA 5 161.00 | 541267 | ODESSA 2 69.000 | 0 |  | 1 | 20SP | 33 | 36.3 | 36 | 98.9 | 98.8615 | 98.5 | [7 empty] | CATEGORYB | SINGLE | LEXINGTON - LEXINGTON 69KV CKT 1 | 0 | 541264 | LEX69 2 69.000 | 541265 | LEXNTON2 69.000 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T5275525SP | FROM->TO | ODESSA 161/69KV TRANSFORMER CKT 1 | E | KCPL | KCPL |  |  | 0 | 541229 | ODESSA 5 161.00 | 541267 | ODESSA 2 69.000 | 0 |  | 1 | 25SP | 33 | 36.3 | 36 | 99.2 | 99.1547 | 97.5 | [7 empty] | CATEGORYB | SINGLE | LEXINGTON - LEXINGTON 69KV CKT 1 | 0 | 541264 | LEX69 2 69.000 | 541265 | LEXNTON2 69.000 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2955525SP | TO->FROM | PACIFIC SUB - SUNDOWN INTERCHANGE 115KV CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 0 | 526434 | SUNDOWN 3115.00 | 526424 | PACIFIC 3115.00 | 0 |  | 1 | 25SP | 159 | 160 | 0 | 98.1 | 98.0582 | 98.2 | [7 empty] | CATEGORYB | SINGLE | LEA COUNTY REC-PLAINS INTERCHANGE - YOAKUM COUNTY INTERCHANGE 115KV CKT 1 | 0 | 526928 | LE-PLNSINT 3115.00 | 526934 | YOAKUM 3115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T13005525SP | FROM->TO | PECAN CREEK (PECANCK1) 345/161/13.8KV TRANSFORMER CKT 1 | E | OKGE | OKGE | MUSKOGEE | MUSKOGEE | 2 | 515235 | PECANCK7 345.00 | 515234 | PECANCK5 161.00 | 515749 | PECANC11 13.800 | 1 | 25SP | 370 | 370 | 0 | 96.4 | 96.4181 | 95.8 | [7 empty] | CATEGORYB | SINGLE | PECAN CREEK (PECANCK1) 345/161/13.8KV TRANSFORMER CKT 2 | 1 | 515234 | PECANCK5 161.00 | 515235 | PECANCK7 345.00 | 515759 | PECANC21 13.800 | 2 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T1265025WP | FROM->TO | PECOS INTERCHANGE (WH BCS15041) 230/115/13.2KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-PECO | SPS-PECO | 2 | 528179 | PECOS 6230.00 | 528178 | PECOS 3115.00 | 528176 | PECOS_TR1 113.200 | 1 | 25WP | 168 | 168 | 0 |  | -999 | 97.9 | [7 empty] | CATEGORYB | SINGLE | HOBBS - KIOWA 7345.00 345KV CKT 1 | 0 | 527896 | HOBBS_INT 7345.00 | 527965 | KIOWA 7345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T10535016WP | FROM->TO | PERYVILLE UNIT #6 500/18.0KV TRANSFORMER CKT 1 | E | EES | EES | EES_ELL-N | EES_ELL-N | 0 | 337430 | 1C3PERYV 18.000 | 337433 | 8PERRYV2 500.00 | 0 |  | 1 | 16WP | 215 | 215 | 0 |  | 96.8857 | 96.3089 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 18 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T10525016WP | FROM->TO | PERYVILLE UNIT #6 500/18.0KV TRANSFORMER CKT 1 | E | EES | EES | EES_ELL-N | EES_ELL-N | 0 | 337428 | 1C1PERYV 18.000 | 337433 | 8PERRYV2 500.00 | 0 |  | 1 | 16WP | 215 | 215 | 0 |  | 96.6018 | 96.0279 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 18 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T10095516WP | FROM->TO | PERYVILLE UNIT #6 500/18.0KV TRANSFORMER CKT 1 | E | EES | EES | EES_ELL-N | EES_ELL-N | 0 | 337430 | 1C3PERYV 18.000 | 337433 | 8PERRYV2 500.00 | 0 |  | 1 | 16WP | 215 | 215 | 0 |  | 95.3103 | 95.0167 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 18 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T15885025WP | FROM->TO | PERYVILLE UNIT #6 500/18.0KV TRANSFORMER CKT 1 | E | EES | EES | EES_ELL-N | EES_ELL-N | 0 | 337430 | 1C3PERYV 18.000 | 337433 | 8PERRYV2 500.00 | 0 |  | 1 | 25WP | 215 | 215 | 0 |  | 97.8575 | 97.3277 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 19 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T15875025WP | FROM->TO | PERYVILLE UNIT #6 500/18.0KV TRANSFORMER CKT 1 | E | EES | EES | EES_ELL-N | EES_ELL-N | 0 | 337428 | 1C1PERYV 18.000 | 337433 | 8PERRYV2 500.00 | 0 |  | 1 | 25WP | 215 | 215 | 0 |  | 97.569 | 97.0417 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 19 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3345520SP | FROM->TO | POTASH JUNCTION INTERCHANGE (UPDATE LATER) 230/115/13.2KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-PECO | SPS-PECO | 1 | 527963 | POTASH_JCT 6230.00 | 527962 | POTASH_JCT 3115.00 | 527958 | POTASH_TR1 113.200 | 1 | 20SP | 250 | 288 | 0 |  | 94.4802 | 96 | [7 empty] | CATEGORYB | SINGLE | HOBBS - KIOWA 7345.00 345KV CKT 1 | 0 | 527896 | HOBBS_INT 7345.00 | 527965 | KIOWA 7345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2065525WP | FROM->TO | POTASH JUNCTION INTERCHANGE (UPDATE LATER) 230/115/13.2KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-PECO | SPS-PECO | 1 | 527963 | POTASH_JCT 6230.00 | 527962 | POTASH_JCT 3115.00 | 527958 | POTASH_TR1 113.200 | 1 | 25WP | 275 | 313 | 0 | 97.2 | 97.2309 | 98.7 | [7 empty] | CATEGORYB | SINGLE | HOBBS - KIOWA 7345.00 345KV CKT 1 | 0 | 527896 | HOBBS_INT 7345.00 | 527965 | KIOWA 7345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T25645525SP | FROM->TO | PRATT (PRATT 3) 115/34.5/3.6KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 2 | 539687 | PRATT 3 115.00 | 539726 | PRATT 1 34.500 | 539929 | PRATT-T 3.6000 | 1 | 25SP | 28 | 28 | 28 | 97.3 | 97.2802 | 97.9 | [7 empty] | CATEGORYB | GENOUT | GEN539726 K9-PRATT | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T25335025SP | FROM->TO | PRATT (PRATT 3) 115/34.5/3.6KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 2 | 539687 | PRATT 3 115.00 | 539726 | PRATT 1 34.500 | 539929 | PRATT-T 3.6000 | 1 | 25SP | 28 | 28 | 28 |  | 97.0456 | 97.3 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 121 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T27965525SP | FROM->TO | PRATT (PRATT 3) 115/34.5/3.6KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 2 | 539687 | PRATT 3 115.00 | 539726 | PRATT 1 34.500 | 539929 | PRATT-T 3.6000 | 1 | 25SP | 28 | 28 | 28 |  | 97.0555 | 97.3 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 130 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T25345025SP | FROM->TO | PRATT (PRATT 3) 115/34.5/3.6KV TRANSFORMER CKT 1 | E | SUNC | SUNC | GREAT PL | GREAT PL | 2 | 539687 | PRATT 3 115.00 | 539726 | PRATT 1 34.500 | 539929 | PRATT-T 3.6000 | 1 | 25SP | 28 | 28 | 28 |  | 96.9979 | 97 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 128 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T2855025SP | TO->FROM | RDRUNNER 3115.00 - RED_BLUFF 3115.00 115KV CKT 1 | E | SPS | SPS | SPS-PECO | SPS-PECO | 0 | 528018 | RED_BLUFF 3115.00 | 528025 | RDRUNNER 3115.00 | 0 |  | 1 | 25SP | 159 | 176 | 0 | 96.9 | 96.8546 | 96.4 | [7 empty] | CATEGORYB | SINGLE | KIOWA 7345.00 - RDRUNNER 7345.00 345KV CKT 1 | 0 | 527965 | KIOWA 7345.00 | 528027 | RDRUNNER 7345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T12125025SP | TO->FROM | RDRUNNER 3115.00 - RED_BLUFF 3115.00 115KV CKT 1 | E | SPS | SPS | SPS-PECO | SPS-PECO | 0 | 528018 | RED_BLUFF 3115.00 | 528025 | RDRUNNER 3115.00 | 0 |  | 1 | 25SP | 159 | 176 | 0 | 96.4 | 96.3656 | 96 | [7 empty] | CATEGORYB | SINGLE | RDRUNNER 7345.00 (UPDATE LATER) 345/115/13.2KV TRANSFORMER CKT 1 | 1 | 528025 | RDRUNNER 3115.00 | 528027 | RDRUNNER 7345.00 | 528023 | RDRNNER_TR1113.200 | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T10895525SP | FROM->TO | RODEMACHER 230/22.0KV TRANSFORMER CKT 1 | E | CLEC | CLEC | CLE_CENTRAL | CLE_CENTRAL | 0 | 501811 | G1NESBIT 22.000 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | 25SP | 476 | 476 | 0 | 98.3 | 98.3423 | 98.4 | [7 empty] | CATEGORYB | SINGLE | COLFAX - RODEMACHER 230KV CKT 1 | 0 | 500200 | COLFAX 6 230.00 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T8675025SP | FROM->TO | RODEMACHER 230/22.0KV TRANSFORMER CKT 1 | E | CLEC | CLEC | CLE_CENTRAL | CLE_CENTRAL | 0 | 501811 | G1NESBIT 22.000 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | 25SP | 476 | 476 | 0 | 98.5 | 98.4525 | 98.4 | [7 empty] | CATEGORYB | SINGLE | COLFAX - RODEMACHER 230KV CKT 1 | 0 | 500200 | COLFAX 6 230.00 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T9855525SP | FROM->TO | RODEMACHER 230/22.0KV TRANSFORMER CKT 1 | E | CLEC | CLEC | CLE_CENTRAL | CLE_CENTRAL | 0 | 501811 | G1NESBIT 22.000 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | 25SP | 476 | 476 | 0 | 97.2 | 97.2246 | 97.3 | [7 empty] | CATEGORYB | SINGLE | COLFAX - MONTGOMERY 230KV CKT 1 | 0 | 337304 | 6MONTGY 230.00 | 500200 | COLFAX 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T7555025SP | FROM->TO | RODEMACHER 230/22.0KV TRANSFORMER CKT 1 | E | CLEC | CLEC | CLE_CENTRAL | CLE_CENTRAL | 0 | 501811 | G1NESBIT 22.000 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | 25SP | 476 | 476 | 0 | 97.3 | 97.2945 | 97.2 | [7 empty] | CATEGORYB | SINGLE | COLFAX - MONTGOMERY 230KV CKT 1 | 0 | 337304 | 6MONTGY 230.00 | 500200 | COLFAX 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T10875525SP | FROM->TO | RODEMACHER 230/22.0KV TRANSFORMER CKT 1 | E | CLEC | CLEC | CLE_CENTRAL | CLE_CENTRAL | 0 | 501811 | G1NESBIT 22.000 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | 25SP | 476 | 476 | 0 | 96.3 | 96.3478 | 96.4 | [7 empty] | CATEGORYB | SINGLE | COCODRIE - VILLE PLATTE 230KV CKT 1 | 0 | 500190 | COCODR 6 230.00 | 500880 | VILPLT 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T8655025SP | FROM->TO | RODEMACHER 230/22.0KV TRANSFORMER CKT 1 | E | CLEC | CLEC | CLE_CENTRAL | CLE_CENTRAL | 0 | 501811 | G1NESBIT 22.000 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | 25SP | 476 | 476 | 0 | 96.3 | 96.2624 | 96.3 | [7 empty] | CATEGORYB | SINGLE | COCODRIE - VILLE PLATTE 230KV CKT 1 | 0 | 500190 | COCODR 6 230.00 | 500880 | VILPLT 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T10955525SP | FROM->TO | RODEMACHER 230/22.0KV TRANSFORMER CKT 1 | E | CLEC | CLEC | CLE_CENTRAL | CLE_CENTRAL | 0 | 501811 | G1NESBIT 22.000 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | 25SP | 476 | 476 | 0 | 95.8 | 95.7919 | 95.9 | [7 empty] | CATEGORYB | SINGLE | EAST LEESVILLE - RODEMACHER 230KV CKT 1 | 0 | 500280 | ELEESV 6 230.00 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T11025525SP | FROM->TO | RODEMACHER 230/22.0KV TRANSFORMER CKT 1 | E | CLEC | CLEC | CLE_CENTRAL | CLE_CENTRAL | 0 | 501811 | G1NESBIT 22.000 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | 25SP | 476 | 476 | 0 | 95.7 | 95.6835 | 95.7 | [7 empty] | CATEGORYB | SINGLE | VILLE PLATTE - WESTFORK 230KV CKT 1 | 0 | 500880 | VILPLT 6 230.00 | 500920 | WSTFORK6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T8725025SP | FROM->TO | RODEMACHER 230/22.0KV TRANSFORMER CKT 1 | E | CLEC | CLEC | CLE_CENTRAL | CLE_CENTRAL | 0 | 501811 | G1NESBIT 22.000 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | 25SP | 476 | 476 | 0 | 95.6 | 95.6197 | 95.6 | [7 empty] | CATEGORYB | SINGLE | EAST LEESVILLE - RODEMACHER 230KV CKT 1 | 0 | 500280 | ELEESV 6 230.00 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T27455525SP | FROM->TO | RODEMACHER 230/22.0KV TRANSFORMER CKT 1 | E | CLEC | CLEC | CLE_CENTRAL | CLE_CENTRAL | 0 | 501811 | G1NESBIT 22.000 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | 25SP | 476 | 476 | 0 | 95.4 | 95.3735 | 95.5 | [7 empty] | CATEGORYB | GENOUT | GEN501812 1-RODEMACHER UNIT 2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T11055525SP | FROM->TO | RODEMACHER 230/22.0KV TRANSFORMER CKT 1 | E | CLEC | CLEC | CLE_CENTRAL | CLE_CENTRAL | 0 | 501811 | G1NESBIT 22.000 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | 25SP | 476 | 476 | 0 | 95.4 | 95.4086 | 95.5 | [7 empty] | CATEGORYB | SINGLE | WELLS - WESTFORK 230KV CKT 1 | 0 | 500920 | WSTFORK6 230.00 | 500940 | WELLS 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T8785025SP | FROM->TO | RODEMACHER 230/22.0KV TRANSFORMER CKT 1 | E | CLEC | CLEC | CLE_CENTRAL | CLE_CENTRAL | 0 | 501811 | G1NESBIT 22.000 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | 25SP | 476 | 476 | 0 | 95.5 | 95.4907 | 95.5 | [7 empty] | CATEGORYB | SINGLE | VILLE PLATTE - WESTFORK 230KV CKT 1 | 0 | 500880 | VILPLT 6 230.00 | 500920 | WSTFORK6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T8815025SP | FROM->TO | RODEMACHER 230/22.0KV TRANSFORMER CKT 1 | E | CLEC | CLEC | CLE_CENTRAL | CLE_CENTRAL | 0 | 501811 | G1NESBIT 22.000 | 500770 | RODEMR 6 230.00 | 0 |  | 1 | 25SP | 476 | 476 | 0 | 95.2 | 95.2158 | 95.2 | [7 empty] | CATEGORYB | SINGLE | WELLS - WESTFORK 230KV CKT 1 | 0 | 500920 | WSTFORK6 230.00 | 500940 | WELLS 6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T13605525SP | FROM->TO | SEMINOLE (GE M101687) 230/115/13.2KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-YOGS | SPS-YOGS | 1 | 527276 | SEMINOLE 6230.00 | 527275 | SEMINOLE 3115.00 | 527273 | SEMINLE_TR1113.200 | 1 | 25SP | 150 | 150 | 0 | 98 | 97.9909 | 97.8 | [7 empty] | CATEGORYB | SINGLE | SEMINOLE (GE M101898) 230/115/13.2KV TRANSFORMER CKT 2 | 1 | 527275 | SEMINOLE 3115.00 | 527276 | SEMINOLE 6230.00 | 527274 | SEMINLE_TR2113.200 | 2 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T13595525SP | FROM->TO | SEMINOLE (GE M101898) 230/115/13.2KV TRANSFORMER CKT 2 | E | SPS | SPS | SPS-YOGS | SPS-YOGS | 1 | 527276 | SEMINOLE 6230.00 | 527275 | SEMINOLE 3115.00 | 527274 | SEMINLE_TR2113.200 | 2 | 25SP | 150 | 150 | 0 | 98.4 | 98.3524 | 98.8 | [7 empty] | CATEGORYB | SINGLE | SEMINOLE (GE M101687) 230/115/13.2KV TRANSFORMER CKT 1 | 1 | 527275 | SEMINOLE 3115.00 | 527276 | SEMINOLE 6230.00 | 527273 | SEMINLE_TR1113.200 | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3265516SP | FROM->TO | SHELDON 115/13.8KV TRANSFORMER CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640020 | SHELDN2G 13.800 | 640278 | SHELDON7 115.00 | 0 |  | 1 | 16SP | 140 | 140 | 140 | 95.9 | 95.8565 | 96.7 | [7 empty] | CATEGORYB | SINGLE | STEGALL - WAYSIDE 230KV CKT 1 | 0 | 640404 | WAYSIDE4 230.00 | 652573 | STEGALL4 230.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3125516SP | FROM->TO | SHELDON 115/13.8KV TRANSFORMER CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640020 | SHELDN2G 13.800 | 640278 | SHELDON7 115.00 | 0 |  | 1 | 16SP | 140 | 140 | 140 | 95.7 | 95.7412 | 96.2 | [7 empty] | CATEGORYB | SINGLE | AINSWORTH - AINSWORTH 115KV CKT 1 | 0 | 640050 | AINSWND7 115.00 | 640051 | AINSWRT7 115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3185516SP | FROM->TO | SHELDON 115/13.8KV TRANSFORMER CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640020 | SHELDN2G 13.800 | 640278 | SHELDON7 115.00 | 0 |  | 1 | 16SP | 140 | 140 | 140 | 96.5 | 96.5314 | 96.1 | [7 empty] | CATEGORYB | SINGLE | GERALD GENTLEMAN STATION - SWEETWATER 345KV CKT 1 | 0 | 640183 | GENTLMN3 345.00 | 640374 | SWEET W3 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T1905020SP | FROM->TO | SHELDON 115/13.8KV TRANSFORMER CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640020 | SHELDN2G 13.800 | 640278 | SHELDON7 115.00 | 0 |  | 1 | 20SP | 140 | 140 | 140 | 97.5 | 97.5239 | 98 | [7 empty] | CATEGORYB | SINGLE | GERALD GENTLEMAN STATION - RED WILLOW 345KV CKT 1 | 0 | 640183 | GENTLMN3 345.00 | 640325 | REDWILO3 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T4235025SP | FROM->TO | SHELDON 115/13.8KV TRANSFORMER CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640020 | SHELDN2G 13.800 | 640278 | SHELDON7 115.00 | 0 |  | 1 | 25SP | 140 | 140 | 140 | 98.9 | 98.8672 | 99.1 | [7 empty] | CATEGORYB | SINGLE | GERALD GENTLEMAN STATION - RED WILLOW 345KV CKT 1 | 0 | 640183 | GENTLMN3 345.00 | 640325 | REDWILO3 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T5955525SP | FROM->TO | SHELDON 115/13.8KV TRANSFORMER CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640020 | SHELDN2G 13.800 | 640278 | SHELDON7 115.00 | 0 |  | 1 | 25SP | 140 | 140 | 140 | 96.5 | 96.4843 | 98 | [7 empty] | CATEGORYB | SINGLE | AINSWORTH - AINSWORTH 115KV CKT 1 | 0 | 640050 | AINSWND7 115.00 | 640051 | AINSWRT7 115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T6225525SP | FROM->TO | SHELDON 115/13.8KV TRANSFORMER CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640020 | SHELDN2G 13.800 | 640278 | SHELDON7 115.00 | 0 |  | 1 | 25SP | 140 | 140 | 140 |  | 93.09 | 95.7 | [7 empty] | CATEGORYB | SINGLE | STEGALL - WAYSIDE 230KV CKT 1 | 0 | 640404 | WAYSIDE4 230.00 | 652573 | STEGALL4 230.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T6005525SP | FROM->TO | SHELDON 115/13.8KV TRANSFORMER CKT 1 | E | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640020 | SHELDN2G 13.800 | 640278 | SHELDON7 115.00 | 0 |  | 1 | 25SP | 140 | 140 | 140 |  | 88.8903 | 95.1 | [7 empty] | CATEGORYB | SINGLE | KELLY - MEADOWGROVE4230.00 230KV CKT 1 | 0 | 640133 | COLMBUS4 230.00 | 640540 | MEADOWGROVE4230.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | INVALID |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T515525WP | TO->FROM | SILOAM CITY - TONNECETP5 161.00 161KV CKT 1 | E | GRDA | GRDA | GRDA-MUN | GRDA-MUN | 0 | 512703 | TONNECETP5 161.00 | 512643 | SILMCTY5 161.00 | 0 |  | 1 | 25WP | 286 | 286 | 0 |  | 94.6189 | 96.3595 | [7 empty] | CATEGORYB | SINGLE | FLINT CREEK - SILOAM SPRINGS TAP 345KV CKT 1 | 0 | 506935 | FLINTCR7 345.00 | 512750 | TONECE7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | INVALID | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T1205525SP | FROM->TO | SILOAM SPRINGS TAP - TONECESTR5 161.00 161KV CKT 1 | E | GRDA | GRDA | GRDA-MUN | GRDA-MUN | 0 | 512751 | TONECE5 161.00 | 512799 | TONECESTR5 161.00 | 0 |  | 1 | 25SP | 335 | 335 | 0 | 98.1 | 98.0769 | 99.7487 | [7 empty] | CATEGORYB | SINGLE | FLINT CREEK - SILOAM SPRINGS TAP 345KV CKT 1 | 0 | 506935 | FLINTCR7 345.00 | 512750 | TONECE7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | INVALID | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T805520SP | FROM->TO | SILOAM SPRINGS TAP (TONNEC345) 345/161/13.8KV TRANSFORMER CKT 1 | E | GRDA | GRDA | GRDA-MUN | GRDA-MUN | 1 | 512750 | TONECE7 345.00 | 512751 | TONECE5 161.00 | 512752 | TONECE1 13.800 | 1 | 20SP | 280 | 350 | 0 | 96.1 | 96.1436 | 96.8616 | [7 empty] | CATEGORYB | SINGLE | FLINT CREEK - SILOAM SPRINGS TAP 345KV CKT 1 | 0 | 506935 | FLINTCR7 345.00 | 512750 | TONECE7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T12445016SP | FROM->TO | SMAN_E_3 115.00 - SOUTH MANHATTAN 115KV CKT Z1 | E | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533351 | SMAN_E_3 115.00 | 533340 | SMANHAT3 115.00 | 0 |  | Z1 | 16SP | 120 | 120 | 0 | 98.3 | 98.2671 | 97.8 | [7 empty] | CATEGORYB | NONSINGLE | WR-B3-10 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | CONT-0900 - JEC - East Manhattan 230kV | FDNSLock |  | FDNS |  | 5 | 0 | 2015AG1AFS21T1705016SP | FROM->TO | SMAN_E_3 115.00 - SOUTH MANHATTAN 115KV CKT Z1 | E | WERE | WERE | NCENTRAL | NCENTRAL | 0 | 533351 | SMAN_E_3 115.00 | 533340 | SMANHAT3 115.00 | 0 |  | Z1 | 16SP | 120 | 120 | 0 | 98.3 | -999 | 97.2 | [7 empty] | CATEGORYB | SINGLE | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 0 | 532852 | JEC 6 230.00 | 532861 | EMANHAT6 230.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T175515WP | FROM->TO | SOUTHWEST 161/20.0KV TRANSFORMER CKT 1 | E | SPRM | SPRM | SPRM | SPRM | 0 | 549893 | JTEC GEN#2 120.000 | 549954 | JTEC 5161.00 | 0 |  | 1 | 15WP | 334 | 400 | 0 | 97 | 96.9594 | 97 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T85015WP | FROM->TO | SOUTHWEST 161/20.0KV TRANSFORMER CKT 1 | E | SPRM | SPRM | SPRM | SPRM | 0 | 549893 | JTEC GEN#2 120.000 | 549954 | JTEC 5161.00 | 0 |  | 1 | 15WP | 334 | 400 | 0 | 97 | 96.984 | 97 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T285516SP | FROM->TO | SOUTHWEST 161/20.0KV TRANSFORMER CKT 1 | E | SPRM | SPRM | SPRM | SPRM | 0 | 549893 | JTEC GEN#2 120.000 | 549954 | JTEC 5161.00 | 0 |  | 1 | 16SP | 334 | 400 | 0 | 97 | 96.9625 | 97 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T155516WP | FROM->TO | SOUTHWEST 161/20.0KV TRANSFORMER CKT 1 | E | SPRM | SPRM | SPRM | SPRM | 0 | 549893 | JTEC GEN#2 120.000 | 549954 | JTEC 5161.00 | 0 |  | 1 | 16WP | 334 | 400 | 0 | 97 | 96.9508 | 97 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T55016WP | FROM->TO | SOUTHWEST 161/20.0KV TRANSFORMER CKT 1 | E | SPRM | SPRM | SPRM | SPRM | 0 | 549893 | JTEC GEN#2 120.000 | 549954 | JTEC 5161.00 | 0 |  | 1 | 16WP | 334 | 400 | 0 | 97 | 97.0047 | 97 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T375520SP | FROM->TO | SOUTHWEST 161/20.0KV TRANSFORMER CKT 1 | E | SPRM | SPRM | SPRM | SPRM | 0 | 549893 | JTEC GEN#2 120.000 | 549954 | JTEC 5161.00 | 0 |  | 1 | 20SP | 334 | 400 | 0 | 97 | 96.9898 | 97 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T95020WP | FROM->TO | SOUTHWEST 161/20.0KV TRANSFORMER CKT 1 | E | SPRM | SPRM | SPRM | SPRM | 0 | 549893 | JTEC GEN#2 120.000 | 549954 | JTEC 5161.00 | 0 |  | 1 | 20WP | 334 | 400 | 0 | 97 | 97.0078 | 97 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T165520WP | FROM->TO | SOUTHWEST 161/20.0KV TRANSFORMER CKT 1 | E | SPRM | SPRM | SPRM | SPRM | 0 | 549893 | JTEC GEN#2 120.000 | 549954 | JTEC 5161.00 | 0 |  | 1 | 20WP | 334 | 400 | 0 | 97 | 96.9665 | 96.9 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T515525SP | FROM->TO | SOUTHWEST 161/20.0KV TRANSFORMER CKT 1 | E | SPRM | SPRM | SPRM | SPRM | 0 | 549893 | JTEC GEN#2 120.000 | 549954 | JTEC 5161.00 | 0 |  | 1 | 25SP | 334 | 400 | 0 | 97 | 96.9898 | 97 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T345025SP | FROM->TO | SOUTHWEST 161/20.0KV TRANSFORMER CKT 1 | E | SPRM | SPRM | SPRM | SPRM | 0 | 549893 | JTEC GEN#2 120.000 | 549954 | JTEC 5161.00 | 0 |  | 1 | 25SP | 334 | 400 | 0 |  | 90.7157 | 96.7 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T175525WP | FROM->TO | SOUTHWEST 161/20.0KV TRANSFORMER CKT 1 | E | SPRM | SPRM | SPRM | SPRM | 0 | 549893 | JTEC GEN#2 120.000 | 549954 | JTEC 5161.00 | 0 |  | 1 | 25WP | 334 | 400 | 0 | 97 | 96.9786 | 97 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T125025WP | FROM->TO | SOUTHWEST 161/20.0KV TRANSFORMER CKT 1 | E | SPRM | SPRM | SPRM | SPRM | 0 | 549893 | JTEC GEN#2 120.000 | 549954 | JTEC 5161.00 | 0 |  | 1 | 25WP | 334 | 400 | 0 | 97 | 97.0122 | 97 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T405520WP | FROM->TO | SPSNORTH_STH | E |  |  |  |  | SPSNORTH_STH | 0 |  | 0 |  | 0 |  |  | 20WP | 980 | 980 | 980 |  | 84.3418 | 97.7 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T375515WP | FROM->TO | SPSNORTH_STX | E |  |  |  |  | SPSNORTH_STX | 0 |  | 0 |  | 0 |  |  | 15WP | 980 | 980 | 980 | 96.2 | 96.4813 | 97.5 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T395516WP | FROM->TO | SPSNORTH_STX | E |  |  |  |  | SPSNORTH_STX | 0 |  | 0 |  | 0 |  |  | 16WP | 980 | 980 | 980 |  | 95.0888 | 96.4 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T8385020SP | FROM->TO | STERLING (STERLING T1) 115/69/13.8KV TRANSFORMER CKT 1 | E | NPPD | OPPD | NPPD_686 | OPPD_691 | 2 | 640362 | STERLNG7 115.00 | 647974 | S974 8 69.000 | 643144 | STERLING T1913.800 | 1 | 20SP | 56 | 56 | 70 |  | 90.9348 | 95.3 | [7 empty] | CATEGORYB | SINGLE | SUB 1263 BROCK (S1263 T1) 161/69/13.8KV TRANSFORMER CKT 1 | 1 | 646263 | S1263 5 161.00 | 647111 | W BROCK8 69.000 | 648263 | S1263T19 13.800 | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T2185016SP | TO->FROM | SUB C - SUB E 115KV CKT 1 | E | NPPD | NPPD | GRIS_688 | GRIS_688 | 0 | 642072 | SUB-E 7 115.00 | 642070 | SUB-C 7 115.00 | 0 |  | 1 | 16SP | 127 | 127 | 140 | 97.2 | 97.2482 | 96.9 | [7 empty] | CATEGORYB | SINGLE | SUB D - SUB I 115KV CKT 1 | 0 | 642071 | SUB-D 7 115.00 | 642076 | SUB-J 7 115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T1965020SP | TO->FROM | SUB C - SUB E 115KV CKT 1 | E | NPPD | NPPD | GRIS_688 | GRIS_688 | 0 | 642072 | SUB-E 7 115.00 | 642070 | SUB-C 7 115.00 | 0 |  | 1 | 20SP | 127 | 127 | 140 | 100.4 | 100.4077 | 99.9 | [7 empty] | CATEGORYB | SINGLE | SUB D - SUB I 115KV CKT 1 | 0 | 642071 | SUB-D 7 115.00 | 642076 | SUB-J 7 115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T4335025SP | TO->FROM | SUB C - SUB E 115KV CKT 1 | E | NPPD | NPPD | GRIS_688 | GRIS_688 | 0 | 642072 | SUB-E 7 115.00 | 642070 | SUB-C 7 115.00 | 0 |  | 1 | 25SP | 127 | 127 | 140 | 97.6 | 97.5865 | 98 | [7 empty] | CATEGORYB | SINGLE | SUB A - SUB I 115KV CKT 1 | 0 | 642068 | SUB-A 7 115.00 | 642076 | SUB-J 7 115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T4345025SP | FROM->TO | SUB D - SUB I 115KV CKT 1 | E | NPPD | NPPD | GRIS_688 | GRIS_688 | 0 | 642071 | SUB-D 7 115.00 | 642076 | SUB-J 7 115.00 | 0 |  | 1 | 25SP | 177 | 177 | 190 | 95.8 | 95.8068 | 95.6 | [7 empty] | CATEGORYB | SINGLE | SUB C - SUB E 115KV CKT 1 | 0 | 642070 | SUB-C 7 115.00 | 642072 | SUB-E 7 115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T18575025SP | FROM->TO | SUB 1206 (S1206 T2) 161/69/13.8KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 1 | 646206 | S1206 5 161.00 | 647006 | S906 N 8 69.000 | 648306 | S1206T29 13.800 | 1 | 25SP | 201.6 | 201.6 | 201.6 |  | 73.3768 | 97.1 | [7 empty] | CATEGORYB | NONSINGLE | S1206T1 BSCL | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T17565520SP | FROM->TO | SUB 1211 - SUB 1220 161KV CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 646211 | S1211 5 161.00 | 646220 | S1220 5 161.00 | 0 |  | 1 | 20SP | 262 | 262 | 262 |  | 44.8555 | 96.6 | [7 empty] | CATEGORYB | GENOUT | NC2_GEN-NEBRASKA CITY 2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T21085525SP | FROM->TO | SUB 1211 - SUB 1220 161KV CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 646211 | S1211 5 161.00 | 646220 | S1220 5 161.00 | 0 |  | 1 | 25SP | 262 | 262 | 262 |  | 46.1353 | 99.1 | [7 empty] | CATEGORYB | GENOUT | NC2_GEN-NEBRASKA CITY 2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T21065525SP | FROM->TO | SUB 1211 - SUB 1220 161KV CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 646211 | S1211 5 161.00 | 646220 | S1220 5 161.00 | 0 |  | 1 | 25SP | 262 | 262 | 262 |  | 46.1353 | 95.3 | [7 empty] | CATEGORYB | GENOUT | NC1_GEN-NEBRASKA CITY 1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T14035516SP | FROM->TO | SUB 1211 161/20.0KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 645025 | N OMA 5G 20.000 | 646211 | S1211 5 161.00 | 0 |  | 1 | 16SP | 250 | 250 | 250 | 95.8 | 73.3608 | 96.6 | [7 empty] | CATEGORYB | GENOUT | SARPY3_GEN-SARPY COUNTY 3 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T13605520SP | TO->FROM | SUB 1221 - SUB 1255 161KV CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 646255 | S1255 5 161.00 | 646221 | S1221 5 161.00 | 0 |  | 1 | 20SP | 352 | 352 | 352 |  | 94.8293 | 95.9 | [7 empty] | CATEGORYB | SINGLE | SUB 3459 (S3459 T3) 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 645459 | S3459 3 345.00 | 646209 | S1209 5 161.00 | 648259 | S3459T39 13.800 | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T5775520SP | TO->FROM | SUB 1221 - SUB 1255 161KV CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 646255 | S1255 5 161.00 | 646221 | S1221 5 161.00 | 0 |  | 1 | 20SP | 352 | 352 | 352 | 95.4 | 95.3825 | 95.1 | [7 empty] | CATEGORYB | SINGLE | SUB 1233 - SUB 1255 161KV CKT 1 | 0 | 646233 | S1233 5 161.00 | 646255 | S1255 5 161.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T6305525SP | TO->FROM | SUB 1221 - SUB 1255 161KV CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 646255 | S1255 5 161.00 | 646221 | S1221 5 161.00 | 0 |  | 1 | 25SP | 352 | 352 | 352 |  | 94.6987 | 96.5 | [7 empty] | CATEGORYB | SINGLE | SUB 1233 - SUB 1234 161KV CKT 1 | 0 | 646233 | S1233 5 161.00 | 646234 | S1234 5 161.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T16265525SP | FROM->TO | SUB 3455 (S3455 T1) 345/161/13.8KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 1 | 645455 | S3455 3 345.00 | 646255 | S1255 5 161.00 | 648255 | S3455T19 13.800 | 1 | 25SP | 558 | 558 | 560 |  | 94.2555 | 96.6 | [7 empty] | CATEGORYB | SINGLE | SUB 3455 (S3455 T3) 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 645455 | S3455 3 345.00 | 646255 | S1255 5 161.00 | 648355 | S3455T39 13.800 | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T16245525SP | FROM->TO | SUB 3455 (S3455 T3) 345/161/13.8KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 1 | 645455 | S3455 3 345.00 | 646255 | S1255 5 161.00 | 648355 | S3455T39 13.800 | 1 | 25SP | 558 | 558 | 560 | 95.8 | 95.7632 | 98.2 | [7 empty] | CATEGORYB | SINGLE | SUB 3455 (S3455 T1) 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 645455 | S3455 3 345.00 | 646255 | S1255 5 161.00 | 648255 | S3455T19 13.800 | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T13615520SP | FROM->TO | SUB 3456 (S3456 T4) 345/161/13.8KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 1 | 645456 | S3456 3 345.00 | 646206 | S1206 5 161.00 | 648256 | S3456T49 13.800 | 1 | 20SP | 500 | 500 | 500 |  | 86.238 | 95.6 | [7 empty] | CATEGORYB | SINGLE | SUB 3459 (S3459 T3) 345/161/13.8KV TRANSFORMER CKT 1 | 1 | 645459 | S3459 3 345.00 | 646209 | S1209 5 161.00 | 648259 | S3459T39 13.800 | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T16355525SP | FROM->TO | SUB 3456 (S3456 T4) 345/161/13.8KV TRANSFORMER CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 1 | 645456 | S3456 3 345.00 | 646206 | S1206 5 161.00 | 648256 | S3456T49 13.800 | 1 | 25SP | 500 | 500 | 500 |  | 83.7309 | 96.6 | [7 empty] | CATEGORYB | SINGLE | COUNCIL BLUFFS - SUB 1206 161KV CKT 1 | 0 | 646206 | S1206 5 161.00 | 635001 | CBLUFFS5 161.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2575525WP | FROM->TO | SUB 383 - MONETT (MONETT) 161/69/12.5KV TRANSFORMER CKT 1 | E | EMDE | EMDE | AURORA | AURORA | 1 | 547480 | MON383 5 161.00 | 547591 | MON383 2 69.000 | 547712 | MON383 1 12.500 | 1 | 25WP | 150 | 150 | 0 | 95.5 | 95.5391 | 95.7 | [7 empty] | CATEGORYB | SINGLE | SUB 124 - AURORA H.T. - SUB 383 - MONETT 161KV CKT 1 | 0 | 547468 | AUR124 5 161.00 | 547480 | MON383 5 161.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T6365525SP | FROM->TO | SUB 906 NORTH - SUB 928 69KV CKT 1 | E | OPPD | OPPD | OPPD_691 | OPPD_691 | 0 | 647006 | S906 N 8 69.000 | 647928 | S928 8 69.000 | 0 |  | 1 | 25SP | 89 | 89 | 89 | 97.1 | 97.1393 | 97.8 | [7 empty] | CATEGORYB | SINGLE | SUB 921 - SUB 942 69KV CKT 1 | 0 | 647921 | S921 8 69.000 | 647942 | S942 8 69.000 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | CONT-0613 - Summit 230-115kV XFMR |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T11855520SP | FROM->TO | SUMMIT (SUMM TX-2) 230/115/13.8KV TRANSFORMER CKT 1 | E | WERE | WERE | WEST | WEST | 2 | 532873 | SUMMIT 6 230.00 | 533381 | SUMMIT 3 115.00 | 532896 | SUMIT2 1 13.800 | 1 | 20SP | 239 | 239 | 0 |  | 92.1261 | 95.8 | [7 empty] | CATEGORYB | SINGLE | SUMMIT (SUMM TX-3) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532873 | SUMMIT 6 230.00 | 533381 | SUMMIT 3 115.00 | 532897 | SUMIT3 1 13.800 | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | CONT-0613 - Summit 230-115kV XFMR |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T11845520SP | FROM->TO | SUMMIT (SUMM TX-3) 230/115/13.8KV TRANSFORMER CKT 1 | E | WERE | WERE | WEST | WEST | 2 | 532873 | SUMMIT 6 230.00 | 533381 | SUMMIT 3 115.00 | 532897 | SUMIT3 1 13.800 | 1 | 20SP | 239 | 239 | 0 |  | 92.3212 | 96 | [7 empty] | CATEGORYB | SINGLE | SUMMIT (SUMM TX-2) 230/115/13.8KV TRANSFORMER CKT 1 | 1 | 532873 | SUMMIT 6 230.00 | 533381 | SUMMIT 3 115.00 | 532896 | SUMIT2 1 13.800 | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T2625025SP | FROM->TO | SUNDOWN INTERCHANGE (WH XDS70381) 230/115/13.8KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 1 | 526435 | SUNDOWN 6230.00 | 526434 | SUNDOWN 3115.00 | 526432 | SUNDOWN_TR1113.800 | 1 | 25SP | 187 | 187 | 0 | 102.8 | 102.7629 | 97.5 | [7 empty] | CATEGORYB | SINGLE | AMOCO SWITCHING STATION - SUNDOWN INTERCHANGE 230KV CKT 1 | 0 | 526435 | SUNDOWN 6230.00 | 526460 | AMOCO_SS 6230.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | CONT-0803 - Hoyt - Stranger 345kV |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3935520SP | FROM->TO | SWISSVALE - WEST GARDNER 345KV CKT 1 | E | WERE | KCPL | NEAST | KACP | 0 | 532774 | SWISVAL7 345.00 | 542965 | W.GRDNR7 345.00 | 0 |  | 1 | 20SP | 717 | 717 | 0 |  | 88.9286 | 96.7 | [7 empty] | CATEGORYB | SINGLE | HOYT - STRANGER CREEK 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532772 | STRANGR7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | CONT-0400 - JEC - Hoyt 345kV |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3865520SP | FROM->TO | SWISSVALE - WEST GARDNER 345KV CKT 1 | E | WERE | KCPL | NEAST | KACP | 0 | 532774 | SWISVAL7 345.00 | 542965 | W.GRDNR7 345.00 | 0 |  | 1 | 20SP | 717 | 717 | 0 |  | 88.4615 | 95.6 | [7 empty] | CATEGORYB | SINGLE | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | CONT-0803 - Hoyt - Stranger 345kV | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T4205525SP | FROM->TO | SWISSVALE - WEST GARDNER 345KV CKT 1 | E | WERE | KCPL | NEAST | KACP | 0 | 532774 | SWISVAL7 345.00 | 542965 | W.GRDNR7 345.00 | 0 |  | 1 | 25SP | 717 | 717 | 0 | 96.4 | 96.3717 | 96.1 | [7 empty] | CATEGORYB | SINGLE | HOYT - STRANGER CREEK 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532772 | STRANGR7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | CONT-0400 - JEC - Hoyt 345kV | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T4135525SP | FROM->TO | SWISSVALE - WEST GARDNER 345KV CKT 1 | E | WERE | KCPL | NEAST | KACP | 0 | 532774 | SWISVAL7 345.00 | 542965 | W.GRDNR7 345.00 | 0 |  | 1 | 25SP | 717 | 717 | 0 | 96.1 | 96.0969 | 95.5 | [7 empty] | CATEGORYB | SINGLE | HOYT - JEFFREY ENERGY CENTER 345KV CKT 1 | 0 | 532765 | HOYT 7 345.00 | 532766 | JEC N 7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T10005515WP | FROM->TO | TABLE ROCK 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505476 | TBR1&2 1 13.800 | 505472 | TABLE R5 161.00 | 0 |  | 1 | 15WP | 121 | 121 | 0 |  | 97.3057 | 96.8377 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 40 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T9995515WP | FROM->TO | TABLE ROCK 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505478 | TBR3&4 1 13.800 | 505472 | TABLE R5 161.00 | 0 |  | 1 | 15WP | 121 | 121 | 0 |  | 96.6693 | 96.2029 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 39 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T10115516WP | FROM->TO | TABLE ROCK 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505476 | TBR1&2 1 13.800 | 505472 | TABLE R5 161.00 | 0 |  | 1 | 16WP | 121 | 121 | 0 |  | 98.5164 | 97.872 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 40 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T10105516WP | FROM->TO | TABLE ROCK 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505478 | TBR3&4 1 13.800 | 505472 | TABLE R5 161.00 | 0 |  | 1 | 16WP | 121 | 121 | 0 |  | 97.8758 | 97.241 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 39 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T12245520WP | FROM->TO | TABLE ROCK 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505476 | TBR1&2 1 13.800 | 505472 | TABLE R5 161.00 | 0 |  | 1 | 20WP | 121 | 121 | 0 |  | 98.9833 | 98.6596 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 42 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T12235520WP | FROM->TO | TABLE ROCK 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505478 | TBR3&4 1 13.800 | 505472 | TABLE R5 161.00 | 0 |  | 1 | 20WP | 121 | 121 | 0 |  | 98.4091 | 98.0885 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 41 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T25365025SP | FROM->TO | TABLE ROCK 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505476 | TBR1&2 1 13.800 | 505472 | TABLE R5 161.00 | 0 |  | 1 | 25SP | 121 | 121 | 0 |  | 92.2649 | 95.4663 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 155 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T25255025SP | FROM->TO | TABLE ROCK 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505476 | TBR1&2 1 13.800 | 505472 | TABLE R5 161.00 | 0 |  | 1 | 25SP | 121 | 121 | 0 |  | 93.3255 | 95.3254 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 77 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T15325525WP | FROM->TO | TABLE ROCK 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505476 | TBR1&2 1 13.800 | 505472 | TABLE R5 161.00 | 0 |  | 1 | 25WP | 121 | 121 | 0 |  | 98.9688 | 98.6597 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 41 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T15315525WP | FROM->TO | TABLE ROCK 161/13.8KV TRANSFORMER CKT 1 | E | SWPA | SWPA | EMINTH | EMINTH | 0 | 505478 | TBR3&4 1 13.800 | 505472 | TABLE R5 161.00 | 0 |  | 1 | 25WP | 121 | 121 | 0 |  | 98.3947 | 98.0887 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 40 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2385516SP | TO->FROM | TALLGRS4 138.00 - WEAVER 138KV CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 0 | 532991 | WEAVER 4 138.00 | 532993 | TALLGRS4 138.00 | 0 |  | 1 | 16SP | 160 | 160 | 0 | 97.9 | 97.8525 | 98.5 | [7 empty] | CATEGORYB | SINGLE | BENTON - MIDIAN 138KV CKT 1 | 0 | 532986 | BENTON 4 138.00 | 532990 | MIDIAN 4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | INVALID | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T1195525SP | FROM->TO | TONECESTR5 161.00 - TONNECETP5 161.00 161KV CKT 1 | E | GRDA | GRDA | GRDA-MUN | GRDA-MUN | 0 | 512799 | TONECESTR5 161.00 | 512703 | TONNECETP5 161.00 | 0 |  | 1 | 25SP | 335 | 335 | 0 | 98.1 | 98.0616 | 99.7334 | [7 empty] | CATEGORYB | SINGLE | FLINT CREEK - SILOAM SPRINGS TAP 345KV CKT 1 | 0 | 506935 | FLINTCR7 345.00 | 512750 | TONECE7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T13415525SP | FROM->TO | TUCO INTERCHANGE (ENRCO 136401) 230/115/13.2KV TRANSFORMER CKT 2 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 1 | 525830 | TUCO_INT 6230.00 | 525828 | TUCO_INT 3115.00 | 525819 | TUCO_TR3 113.200 | 2 | 25SP | 250 | 288 | 0 |  | 91.9901 | 97.9 | [7 empty] | CATEGORYB | SINGLE | TUCO INTERCHANGE (GE M102345) 230/115/13.2KV TRANSFORMER CKT 1 | 1 | 525828 | TUCO_INT 3115.00 | 525830 | TUCO_INT 6230.00 | 525821 | TUCO_TR4 113.200 | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | NOT GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T24045520SP | FROM->TO | TUCO INTERCHANGE 230/13.0KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 0 | 525830 | TUCO_INT 6230.00 | 525820 | TUCO_SVC 113.000 | 0 |  | 1 | 20SP | 150 | 150 | 0 |  | 35.0967 | 99.4 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 66 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | NOT GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T24155520SP | FROM->TO | TUCO INTERCHANGE 230/13.0KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 0 | 525830 | TUCO_INT 6230.00 | 525820 | TUCO_SVC 113.000 | 0 |  | 1 | 20SP | 150 | 150 | 0 |  | 32.5709 | 95.2 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 92 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | NOT GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T24165520SP | FROM->TO | TUCO INTERCHANGE 230/13.0KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 0 | 525830 | TUCO_INT 6230.00 | 525820 | TUCO_SVC 113.000 | 0 |  | 1 | 20SP | 150 | 150 | 0 |  | 32.2327 | 95.1 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 93 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | NOT GSU |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T25265025SP | FROM->TO | TUCO INTERCHANGE 230/13.0KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 0 | 525830 | TUCO_INT 6230.00 | 525820 | TUCO_SVC 113.000 | 0 |  | 1 | 25SP | 150 | 150 | 0 |  | 99.9991 | 97 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 101 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | NOT GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T15505525WP | FROM->TO | TUCO INTERCHANGE 230/13.0KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 0 | 525830 | TUCO_INT 6230.00 | 525820 | TUCO_SVC 113.000 | 0 |  | 1 | 25WP | 150 | 150 | 0 |  | 50.5728 | 97.6 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 81 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | NOT GSU |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T15335525WP | FROM->TO | TUCO INTERCHANGE 230/13.0KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 0 | 525830 | TUCO_INT 6230.00 | 525820 | TUCO_SVC 113.000 | 0 |  | 1 | 25WP | 150 | 150 | 0 |  | 49.5953 | 96.8 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 54 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | GSU |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T16015025WP | FROM->TO | TUCO INTERCHANGE 230/13.0KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 0 | 525830 | TUCO_INT 6230.00 | 525820 | TUCO_SVC 113.000 | 0 |  | 1 | 25WP | 150 | 150 | 0 |  | 48.4459 | 95.4783 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 72 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T9115516SP | FROM->TO | WARRENSBURG EAST 161/69KV TRANSFORMER CKT 1 | E | KCPL | KCPL |  |  | 0 | 541228 | WBURGE 5 161.00 | 541269 | WBURGE 2 69.000 | 0 |  | 1 | 16SP | 50 | 55 | 55 | 95.7 | 95.6585 | 95.5 | [7 empty] | CATEGORYB | SINGLE | CLINTON - CLINTON 161KV CKT Z1 | 0 | 541242 | CLINTON5 161.00 | 300071 | 5CLINTN 161.00 | 0 |  | Z1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T5815015WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 15WP | 910 | 910 | 0 | 96 | 95.9905 | 96.3 | [7 empty] | CATEGORYB | SINGLE | 8SHELBY TN 500.00 - PLUM POINT 500KV CKT 1 | 0 | 338188 | 8SANSOUC 500.00 | 360021 | 8SHELBY TN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T2205015WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 15WP | 910 | 910 | 0 | 95.7 | 95.7114 | 95.8 | [7 empty] | CATEGORYB | SINGLE | DELL 500 - INDEPENDENCE 500KV CKT 1 | 0 | 338145 | 8ISES 500.00 | 338187 | 8DELL 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T9655015WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 15WP | 910 | 910 | 0 | 95.6 | 95.6076 | 95.7 | [7 empty] | CATEGORYB | GENOUT | GEN337652 1-WHITE BLUFF UNIT #1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2605515WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 15WP | 910 | 910 | 0 | 95.8 | 95.787 | 95.6 | [7 empty] | CATEGORYB | SINGLE | DELL 500 - INDEPENDENCE 500KV CKT 1 | 0 | 338145 | 8ISES 500.00 | 338187 | 8DELL 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T6795515WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 15WP | 910 | 910 | 0 | 95.3 | 95.3412 | 95.5 | [7 empty] | CATEGORYB | SINGLE | 8SHELBY TN 500.00 - PLUM POINT 500KV CKT 1 | 0 | 338188 | 8SANSOUC 500.00 | 360021 | 8SHELBY TN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T9855515WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 15WP | 910 | 910 | 0 | 95.3 | 95.3065 | 95.3 | [7 empty] | CATEGORYB | GENOUT | GEN337652 1-WHITE BLUFF UNIT #1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T3055015WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 15WP | 910 | 910 | 0 | 95.1 | 95.0931 | 95.2 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T7865015WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 15WP | 910 | 910 | 0 | 95 | 95.0396 | 95.1 | [7 empty] | CATEGORYB | NONSINGLE | A129 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T6165516SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16SP | 910 | 910 | 0 | 96.5 | 96.4954 | 96.8 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - PLUM POINT 500KV CKT 1 | 0 | 338188 | 8SANSOUC 500.00 | 338198 | 8DRIVER% 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T13155516SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16SP | 910 | 910 | 0 | 96.5 | 96.4662 | 96.7 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - 8SHELBY TN 500.00 500KV CKT 1 | 0 | 338198 | 8DRIVER% 500.00 | 360021 | 8SHELBY TN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T13115516SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16SP | 910 | 910 | 0 | 95.8 | 95.7953 | 96.5 | [7 empty] | CATEGORYB | SINGLE | 5ISES 2 161/26.0KV TRANSFORMER CKT 2 | 0 | 338152 | 5ISES-2 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 2 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T11435016SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16SP | 910 | 910 | 0 | 95.8 | 95.7569 | 96.5 | [7 empty] | CATEGORYB | SINGLE | 5ISES 2 161/26.0KV TRANSFORMER CKT 2 | 0 | 338152 | 5ISES-2 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 2 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T6115516SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16SP | 910 | 910 | 0 | 96.7 | 96.678 | 96.3 | [7 empty] | CATEGORYB | SINGLE | DELL 500 - INDEPENDENCE 500KV CKT 1 | 0 | 338145 | 8ISES 500.00 | 338187 | 8DELL 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T6655016SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16SP | 910 | 910 | 0 | 96.3 | 96.2941 | 96.3 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T4865016SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16SP | 910 | 910 | 0 | 96.1 | 96.0884 | 96.3 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - PLUM POINT 500KV CKT 1 | 0 | 338188 | 8SANSOUC 500.00 | 338198 | 8DRIVER% 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T13075516SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16SP | 910 | 910 | 0 | 96.4 | 96.3865 | 96.3 | [7 empty] | CATEGORYB | SINGLE | INDEPENDENCE 161/26.0KV TRANSFORMER CKT 1 | 0 | 338142 | 5ISES-1 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T11395016SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16SP | 910 | 910 | 0 | 96.3 | 96.3449 | 96.3 | [7 empty] | CATEGORYB | SINGLE | INDEPENDENCE 161/26.0KV TRANSFORMER CKT 1 | 0 | 338142 | 5ISES-1 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T11465016SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16SP | 910 | 910 | 0 | 96.2 | 96.1943 | 96.2 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - 8SHELBY TN 500.00 500KV CKT 1 | 0 | 338198 | 8DRIVER% 500.00 | 360021 | 8SHELBY TN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T6045516SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16SP | 910 | 910 | 0 | 96.1 | 96.0792 | 95.8 | [7 empty] | CATEGORYB | SINGLE | KEO EHV - WEST MEMPHIS 500 500KV CKT 1 | 0 | 337957 | 8KEO 500.00 | 338162 | 8WM-EHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T4825016SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16SP | 910 | 910 | 0 | 95.6 | 95.6339 | 95.5 | [7 empty] | CATEGORYB | SINGLE | DELL 500 - INDEPENDENCE 500KV CKT 1 | 0 | 338145 | 8ISES 500.00 | 338187 | 8DELL 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T4645016SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16SP | 910 | 910 | 0 | 95.6 | 95.636 | 95.5 | [7 empty] | CATEGORYB | SINGLE | MAGNET COVE - SHERIDAN EHV 500KV CKT 1 | 0 | 337643 | 8SHERID 500.00 | 337763 | 8MAGCOVE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T4715016SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16SP | 910 | 910 | 0 | 95.2 | 95.3248 | 95.2 | [7 empty] | CATEGORYB | SINGLE | KEO EHV - WEST MEMPHIS 500 500KV CKT 1 | 0 | 337957 | 8KEO 500.00 | 338162 | 8WM-EHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T5985516SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16SP | 910 | 910 | 0 | 95.2 | 95.1787 | 95 | [7 empty] | CATEGORYB | SINGLE | MAGNET COVE - SHERIDAN EHV 500KV CKT 1 | 0 | 337643 | 8SHERID 500.00 | 337763 | 8MAGCOVE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T10305016WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 | 97.5 | 97.4521 | 97.6 | [7 empty] | CATEGORYB | GENOUT | GEN337652 1-WHITE BLUFF UNIT #1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T6385016WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 | 97.1 | 97.141 | 97.3 | [7 empty] | CATEGORYB | SINGLE | 5ISES 2 161/26.0KV TRANSFORMER CKT 2 | 0 | 338152 | 5ISES-2 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 2 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T6355016WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 | 97 | 97.0456 | 97.2 | [7 empty] | CATEGORYB | SINGLE | INDEPENDENCE 161/26.0KV TRANSFORMER CKT 1 | 0 | 338142 | 5ISES-1 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T9965516WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 | 96.1 | 96.1309 | 96.3 | [7 empty] | CATEGORYB | GENOUT | GEN337652 1-WHITE BLUFF UNIT #1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T6925516WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 | 96.2 | 96.2471 | 96.3 | [7 empty] | CATEGORYB | SINGLE | 5ISES 2 161/26.0KV TRANSFORMER CKT 2 | 0 | 338152 | 5ISES-2 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 2 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T6895516WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 | 96.2 | 96.1513 | 96.2 | [7 empty] | CATEGORYB | SINGLE | INDEPENDENCE 161/26.0KV TRANSFORMER CKT 1 | 0 | 338142 | 5ISES-1 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T6405016WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 | 96 | 95.9866 | 96.2 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - 8SHELBY TN 500.00 500KV CKT 1 | 0 | 338198 | 8DRIVER% 500.00 | 360021 | 8SHELBY TN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T3465016WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 | 96 | 96.009 | 96.2 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T2515016WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 | 95.8 | 95.7884 | 96 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - PLUM POINT 500KV CKT 1 | 0 | 338188 | 8SANSOUC 500.00 | 338198 | 8DRIVER% 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T8475016WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 | 95.5 | 95.4501 | 95.6 | [7 empty] | CATEGORYB | NONSINGLE | A129 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T10515016WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 |  | 95.2754 | 95.4 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 6 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T6945516WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 |  | 94.9951 | 95.3 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - 8SHELBY TN 500.00 500KV CKT 1 | 0 | 338198 | 8DRIVER% 500.00 | 360021 | 8SHELBY TN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T2455016WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 | 95.2 | 95.163 | 95.3 | [7 empty] | CATEGORYB | SINGLE | NEWPORT - NEWPORT INDUSTRIAL 161KV CKT 1 | 0 | 338151 | 5NEWPO 161.00 | 338173 | 5NEW-IN 161.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T2505016WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 | 95.1 | 95.1208 | 95.3 | [7 empty] | CATEGORYB | SINGLE | NEWPORT AB - NEWPORT INDUSTRIAL 161KV CKT 1 | 0 | 338172 | 5NEW-AB 161.00 | 338173 | 5NEW-IN 161.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2855516WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 |  | 94.929 | 95.2 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - PLUM POINT 500KV CKT 1 | 0 | 338188 | 8SANSOUC 500.00 | 338198 | 8DRIVER% 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T10325016WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 | 95 | 95.032 | 95.2 | [7 empty] | CATEGORYB | GENOUT | GEN337911 1-ARKANSAS NUCLEAR ONE UNIT #2 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T10345016WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 | 95 | 95.0117 | 95.2 | [7 empty] | CATEGORYB | GENOUT | GEN338510 1-1S1KNWRI | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T2195016WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 | 95.1 | 95.0542 | 95.2 | [7 empty] | CATEGORYB | SINGLE | ELDORADO EHV 500/115KV TRANSFORMER CKT 1 | 0 | 337539 | 3ELDEHV 115.00 | 337561 | 8ELDEHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T2435016WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 | 95.1 | 95.1359 | 95.2 | [7 empty] | CATEGORYB | SINGLE | DELL 500 - INDEPENDENCE 500KV CKT 1 | 0 | 338145 | 8ISES 500.00 | 338187 | 8DELL 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T2215016WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 |  | 94.9174 | 95.1 | [7 empty] | CATEGORYB | SINGLE | 6WHT BLUFF% 230.00 - WOODWARD 230KV CKT 1 | 0 | 337633 | 6WOODW 230.00 | 337654 | 6WHT BLUFF% 230.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T2185016WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 |  | 94.9209 | 95.1 | [7 empty] | CATEGORYB | SINGLE | MC NIEL 500/115KV TRANSFORMER CKT 1 | 0 | 337515 | 8MCNEIL 500.00 | 337516 | 3MCNEIL 115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T8465016WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 |  | 94.9241 | 95.1 | [7 empty] | CATEGORYB | NONSINGLE | A152 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T2475016WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 |  | 94.9391 | 95.1 | [7 empty] | CATEGORYB | SINGLE | CASH - JONESBORO 161KV CKT 1 | 0 | 338170 | 5JONES 161.00 | 338171 | 5CASH 161.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T10315016WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 |  | 94.9676 | 95.1 | [7 empty] | CATEGORYB | GENOUT | GEN337910 1-ARKANSAS NUCLEAR ONE UNIT #1 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T2485016WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 |  | 94.9823 | 95.1 | [7 empty] | CATEGORYB | SINGLE | CASH - NEWPORT AB 161KV CKT 1 | 0 | 338171 | 5CASH 161.00 | 338172 | 5NEW-AB 161.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T225016WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 |  | 94.8375 | 95 | [7 empty] | CATEGORYB | SINGLE | FULTON 115 - HOPE 115KV CKT 1 | 0 | 503912 | FULTON 3 115.00 | 507453 | HOPE 3 115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T2465016WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 |  | 94.8513 | 95 | [7 empty] | CATEGORYB | SINGLE | WEST MEMPHIS 500 500/161KV TRANSFORMER CKT 1 | 0 | 338161 | 5WM-EHV 161.00 | 338162 | 8WM-EHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T2225016WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 16WP | 910 | 910 | 0 |  | 94.8688 | 95 | [7 empty] | CATEGORYB | SINGLE | WHITE BLUFF 500/230KV TRANSFORMER CKT 1 | 0 | 337651 | 8WH BLF 500.00 | 337654 | 6WHT BLUFF% 230.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T8635520SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20SP | 910 | 910 | 0 | 97.3 | 97.3246 | 98 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - PLUM POINT 500KV CKT 1 | 0 | 338188 | 8SANSOUC 500.00 | 338198 | 8DRIVER% 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T16475520SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20SP | 910 | 910 | 0 | 97.3 | 97.3123 | 98 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - 8SHELBY TN 500.00 500KV CKT 1 | 0 | 338198 | 8DRIVER% 500.00 | 360021 | 8SHELBY TN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T6405020SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20SP | 910 | 910 | 0 | 97.5 | 97.5401 | 97.4 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T4505020SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20SP | 910 | 910 | 0 | 97 | 96.9894 | 97 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - PLUM POINT 500KV CKT 1 | 0 | 338188 | 8SANSOUC 500.00 | 338198 | 8DRIVER% 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T11145020SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20SP | 910 | 910 | 0 | 96.9 | 96.9158 | 96.9 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - 8SHELBY TN 500.00 500KV CKT 1 | 0 | 338198 | 8DRIVER% 500.00 | 360021 | 8SHELBY TN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T8585520SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20SP | 910 | 910 | 0 | 97.2 | 97.1684 | 96.7 | [7 empty] | CATEGORYB | SINGLE | DELL 500 - INDEPENDENCE 500KV CKT 1 | 0 | 338145 | 8ISES 500.00 | 338187 | 8DELL 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T8485520SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20SP | 910 | 910 | 0 | 96.5 | 96.544 | 96.3 | [7 empty] | CATEGORYB | SINGLE | KEO EHV - WEST MEMPHIS 500 500KV CKT 1 | 0 | 337957 | 8KEO 500.00 | 338162 | 8WM-EHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T4465020SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20SP | 910 | 910 | 0 | 96.4 | 96.3741 | 96.1 | [7 empty] | CATEGORYB | SINGLE | DELL 500 - INDEPENDENCE 500KV CKT 1 | 0 | 338145 | 8ISES 500.00 | 338187 | 8DELL 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T16455520SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20SP | 910 | 910 | 0 | 96.1 | 96.0771 | 96 | [7 empty] | CATEGORYB | SINGLE | 5ISES 2 161/26.0KV TRANSFORMER CKT 2 | 0 | 338152 | 5ISES-2 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 2 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T11125020SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20SP | 910 | 910 | 0 | 96.1 | 96.1271 | 96 | [7 empty] | CATEGORYB | SINGLE | 5ISES 2 161/26.0KV TRANSFORMER CKT 2 | 0 | 338152 | 5ISES-2 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 2 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T16415520SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20SP | 910 | 910 | 0 | 95.9 | 95.9288 | 95.9 | [7 empty] | CATEGORYB | SINGLE | INDEPENDENCE 161/26.0KV TRANSFORMER CKT 1 | 0 | 338142 | 5ISES-1 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T4265020SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20SP | 910 | 910 | 0 | 96 | 95.9964 | 95.9 | [7 empty] | CATEGORYB | SINGLE | MAGNET COVE - SHERIDAN EHV 500KV CKT 1 | 0 | 337643 | 8SHERID 500.00 | 337763 | 8MAGCOVE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T11085020SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20SP | 910 | 910 | 0 | 96 | 95.9784 | 95.8 | [7 empty] | CATEGORYB | SINGLE | INDEPENDENCE 161/26.0KV TRANSFORMER CKT 1 | 0 | 338142 | 5ISES-1 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T4365020SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20SP | 910 | 910 | 0 | 95.9 | 95.9026 | 95.7 | [7 empty] | CATEGORYB | SINGLE | KEO EHV - WEST MEMPHIS 500 500KV CKT 1 | 0 | 337957 | 8KEO 500.00 | 338162 | 8WM-EHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T8415520SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20SP | 910 | 910 | 0 | 95.3 | 95.3372 | 95.1 | [7 empty] | CATEGORYB | SINGLE | MAGNET COVE - SHERIDAN EHV 500KV CKT 1 | 0 | 337643 | 8SHERID 500.00 | 337763 | 8MAGCOVE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T8395520SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20SP | 910 | 910 | 0 |  | 94.9919 | 95.1 | [7 empty] | CATEGORYB | SINGLE | ETTA (DUKE HOTSPRINGS) - MC NIEL 500KV CKT 1 | 0 | 337515 | 8MCNEIL 500.00 | 337754 | 8ETTA 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T7205020WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20WP | 910 | 910 | 0 | 96.2 | 96.1667 | 96.2 | [7 empty] | CATEGORYB | SINGLE | 5ISES 2 161/26.0KV TRANSFORMER CKT 2 | 0 | 338152 | 5ISES-2 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 2 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T7165020WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20WP | 910 | 910 | 0 | 96.1 | 96.0719 | 96.1 | [7 empty] | CATEGORYB | SINGLE | INDEPENDENCE 161/26.0KV TRANSFORMER CKT 1 | 0 | 338142 | 5ISES-1 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T7225020WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20WP | 910 | 910 | 0 | 95.7 | 95.6644 | 95.8 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - 8SHELBY TN 500.00 500KV CKT 1 | 0 | 338198 | 8DRIVER% 500.00 | 360021 | 8SHELBY TN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T8455520WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20WP | 910 | 910 | 0 | 95.2 | 95.2166 | 95.7 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - 8SHELBY TN 500.00 500KV CKT 1 | 0 | 338198 | 8DRIVER% 500.00 | 360021 | 8SHELBY TN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T4015520WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20WP | 910 | 910 | 0 | 95.2 | 95.2165 | 95.7 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - PLUM POINT 500KV CKT 1 | 0 | 338188 | 8SANSOUC 500.00 | 338198 | 8DRIVER% 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T4015020WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20WP | 910 | 910 | 0 | 95.7 | 95.6812 | 95.7 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T2875020WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20WP | 910 | 910 | 0 | 95.5 | 95.526 | 95.6 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - PLUM POINT 500KV CKT 1 | 0 | 338188 | 8SANSOUC 500.00 | 338198 | 8DRIVER% 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T8435520WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20WP | 910 | 910 | 0 | 95.5 | 95.4635 | 95.5 | [7 empty] | CATEGORYB | SINGLE | 5ISES 2 161/26.0KV TRANSFORMER CKT 2 | 0 | 338152 | 5ISES-2 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 2 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T8395520WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20WP | 910 | 910 | 0 | 95.4 | 95.3688 | 95.4 | [7 empty] | CATEGORYB | SINGLE | INDEPENDENCE 161/26.0KV TRANSFORMER CKT 1 | 0 | 338142 | 5ISES-1 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T11225020WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 20WP | 910 | 910 | 0 |  | 95.2881 | 95.3 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 6 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T10865025SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25SP | 910 | 910 | 0 | 97.7 | 97.7388 | 97.6 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T19675525SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25SP | 910 | 910 | 0 | 97.1 | 97.0657 | 97.2 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - 8SHELBY TN 500.00 500KV CKT 1 | 0 | 338198 | 8DRIVER% 500.00 | 360021 | 8SHELBY TN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T10345525SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25SP | 910 | 910 | 0 | 96.6 | 96.6077 | 96.5 | [7 empty] | CATEGORYB | SINGLE | DELL 500 - INDEPENDENCE 500KV CKT 1 | 0 | 338145 | 8ISES 500.00 | 338187 | 8DELL 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T17295025SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25SP | 910 | 910 | 0 | 96.3 | 96.3387 | 96.4 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - 8SHELBY TN 500.00 500KV CKT 1 | 0 | 338198 | 8DRIVER% 500.00 | 360021 | 8SHELBY TN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T8165025SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25SP | 910 | 910 | 0 | 96.5 | 96.4745 | 96.4 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - PLUM POINT 500KV CKT 1 | 0 | 338188 | 8SANSOUC 500.00 | 338198 | 8DRIVER% 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T17275025SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25SP | 910 | 910 | 0 | 96.3 | 96.2877 | 96.2 | [7 empty] | CATEGORYB | SINGLE | 5ISES 2 161/26.0KV TRANSFORMER CKT 2 | 0 | 338152 | 5ISES-2 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 2 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T19655525SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25SP | 910 | 910 | 0 | 96.2 | 96.1609 | 96.1 | [7 empty] | CATEGORYB | SINGLE | 5ISES 2 161/26.0KV TRANSFORMER CKT 2 | 0 | 338152 | 5ISES-2 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 2 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T7765025SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25SP | 910 | 910 | 0 | 96.2 | 96.1676 | 96.1 | [7 empty] | CATEGORYB | SINGLE | MAGNET COVE - SHERIDAN EHV 500KV CKT 1 | 0 | 337643 | 8SHERID 500.00 | 337763 | 8MAGCOVE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T17235025SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25SP | 910 | 910 | 0 | 96.1 | 96.1374 | 96 | [7 empty] | CATEGORYB | SINGLE | INDEPENDENCE 161/26.0KV TRANSFORMER CKT 1 | 0 | 338142 | 5ISES-1 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T10165525SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25SP | 910 | 910 | 0 | 96.1 | 96.1101 | 96 | [7 empty] | CATEGORYB | SINGLE | KEO EHV - WEST MEMPHIS 500 500KV CKT 1 | 0 | 337957 | 8KEO 500.00 | 338162 | 8WM-EHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T8095025SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25SP | 910 | 910 | 0 | 96.1 | 96.085 | 96 | [7 empty] | CATEGORYB | SINGLE | DELL 500 - INDEPENDENCE 500KV CKT 1 | 0 | 338145 | 8ISES 500.00 | 338187 | 8DELL 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T19615525SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25SP | 910 | 910 | 0 | 96 | 96.0101 | 95.9 | [7 empty] | CATEGORYB | SINGLE | INDEPENDENCE 161/26.0KV TRANSFORMER CKT 1 | 0 | 338142 | 5ISES-1 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T7895025SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25SP | 910 | 910 | 0 | 95.6 | 95.6348 | 95.5 | [7 empty] | CATEGORYB | SINGLE | KEO EHV - WEST MEMPHIS 500 500KV CKT 1 | 0 | 337957 | 8KEO 500.00 | 338162 | 8WM-EHV 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T10075525SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25SP | 910 | 910 | 0 | 95.4 | 95.3728 | 95.2 | [7 empty] | CATEGORYB | SINGLE | MAGNET COVE - SHERIDAN EHV 500KV CKT 1 | 0 | 337643 | 8SHERID 500.00 | 337763 | 8MAGCOVE 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T7775025SP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25SP | 910 | 910 | 0 | 95.2 | 95.1855 | 95.1 | [7 empty] | CATEGORYB | SINGLE | KEO EHV - WHITE BLUFF 500KV CKT 1 | 0 | 337651 | 8WH BLF 500.00 | 337957 | 8KEO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T10135025WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25WP | 910 | 910 | 0 | 96.2 | 96.1521 | 96.2 | [7 empty] | CATEGORYB | SINGLE | 5ISES 2 161/26.0KV TRANSFORMER CKT 2 | 0 | 338152 | 5ISES-2 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 2 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T5545525WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25WP | 910 | 910 | 0 | 95.9 | 95.919 | 96.1 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - PLUM POINT 500KV CKT 1 | 0 | 338188 | 8SANSOUC 500.00 | 338198 | 8DRIVER% 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T10115025WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25WP | 910 | 910 | 0 | 96.1 | 96.057 | 96.1 | [7 empty] | CATEGORYB | SINGLE | INDEPENDENCE 161/26.0KV TRANSFORMER CKT 1 | 0 | 338142 | 5ISES-1 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T10635525WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25WP | 910 | 910 | 0 | 96 | 95.9834 | 96 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - 8SHELBY TN 500.00 500KV CKT 1 | 0 | 338198 | 8DRIVER% 500.00 | 360021 | 8SHELBY TN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T6575025WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25WP | 910 | 910 | 0 | 96 | 96.0377 | 95.9 | [7 empty] | CATEGORYB | SINGLE | ARKANSAS NUCLEAR ONE - FT SMITH 500KV CKT 1 | 0 | 515305 | FTSMITH8 500.00 | 337909 | 8ANO 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T10595525WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25WP | 910 | 910 | 0 | 95.7 | 95.729 | 95.9 | [7 empty] | CATEGORYB | SINGLE | 5ISES 2 161/26.0KV TRANSFORMER CKT 2 | 0 | 338152 | 5ISES-2 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 2 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T10545525WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25WP | 910 | 910 | 0 | 95.6 | 95.634 | 95.8 | [7 empty] | CATEGORYB | SINGLE | INDEPENDENCE 161/26.0KV TRANSFORMER CKT 1 | 0 | 338142 | 5ISES-1 161.00 | 338143 | 1ISES U1 26.000 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T10175025WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25WP | 910 | 910 | 0 | 95.6 | 95.5642 | 95.7 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - 8SHELBY TN 500.00 500KV CKT 1 | 0 | 338198 | 8DRIVER% 500.00 | 360021 | 8SHELBY TN 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T4835025WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25WP | 910 | 910 | 0 | 95.4 | 95.4255 | 95.5 | [7 empty] | CATEGORYB | SINGLE | 8DRIVER% 500.00 - PLUM POINT 500KV CKT 1 | 0 | 338188 | 8SANSOUC 500.00 | 338198 | 8DRIVER% 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 0 | 2015AG1AFS21T15815025WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25WP | 910 | 910 | 0 |  | 95.1683 | 95.2 | [7 empty] | CATEGORYB | NONSINGLE | SPPMGN 6 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2015-AG1 | AFS2 | SWINGBUS |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T5495525WP | FROM->TO | WHITE BLUFF 500/26.0KV TRANSFORMER CKT 1 | E | EES-EAI | EES-EAI | EES_ARK | EES_ARK | 0 | 337653 | 1BLUF U2 26.000 | 337651 | 8WH BLF 500.00 | 0 |  | 1 | 25WP | 910 | 910 | 0 |  | 94.81 | 95 | [7 empty] | CATEGORYB | SINGLE | DELL 500 - INDEPENDENCE 500KV CKT 1 | 0 | 338145 | 8ISES 500.00 | 338187 | 8DELL 500.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T8695516SP | FROM->TO | WICHITA (WICH TX-11) 345/138/13.8KV TRANSFORMER CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 1 | 532796 | WICHITA7 345.00 | 533040 | EVANS N4 138.00 | 532829 | WICH11 1 13.800 | 1 | 16SP | 400 | 430 | 0 |  | 59.474 | 95.4 | [7 empty] | CATEGORYB | SINGLE | WICHITA (WICH TX-12) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532796 | WICHITA7 345.00 | 533040 | EVANS N4 138.00 | 532830 | WICH12 1 13.800 | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3995516WP | FROM->TO | WICHITA (WICH TX-11) 345/138/13.8KV TRANSFORMER CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 1 | 532796 | WICHITA7 345.00 | 533040 | EVANS N4 138.00 | 532829 | WICH11 1 13.800 | 1 | 16WP | 400 | 430 | 0 | 95.5 | 95.5225 | 95.5 | [7 empty] | CATEGORYB | SINGLE | WICHITA (WICH TX-12) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532796 | WICHITA7 345.00 | 533040 | EVANS N4 138.00 | 532830 | WICH12 1 13.800 | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 5 | 2015AG1AFS21T3795515WP | FROM->TO | WICHITA (WICH TX-12) 345/138/13.8KV TRANSFORMER CKT 1 | E | WERE | WERE | SCENTRAL | SCENTRAL | 1 | 532796 | WICHITA7 345.00 | 533040 | EVANS N4 138.00 | 532830 | WICH12 1 13.800 | 1 | 15WP | 400 | 430 | 0 | 101.8 | 101.791 | 99.8 | [7 empty] | CATEGORYB | SINGLE | WICHITA (WICH TX-11) 345/138/13.8KV TRANSFORMER CKT 1 | 1 | 532796 | WICHITA7 345.00 | 533040 | EVANS N4 138.00 | 532829 | WICH11 1 13.800 | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2215516SP | FROM->TO | WOLF CREEK 345/69KV TRANSFORMER CKT 1 | E | WERE | WERE | SEAST | SEAST | 0 | 532797 | WOLFCRK7 345.00 | 533653 | WOLFCRK2 69.000 | 0 |  | 1 | 16SP | 100 | 110 | 0 |  | 94.5337 | 99.9 | [7 empty] | CATEGORYB | SINGLE | WAVERLY7 345.00 - WOLF CREEK 345KV CKT 1 | 0 | 532797 | WOLFCRK7 345.00 | 532799 | WAVERLY7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T1585520WP | FROM->TO | WOLF CREEK 345/69KV TRANSFORMER CKT 1 | E | WERE | WERE | SEAST | SEAST | 0 | 532797 | WOLFCRK7 345.00 | 533653 | WOLFCRK2 69.000 | 0 |  | 1 | 20WP | 100 | 110 | 0 |  | 91.8245 | 97.3 | [7 empty] | CATEGORYB | SINGLE | WAVERLY7 345.00 - WOLF CREEK 345KV CKT 1 | 0 | 532797 | WOLFCRK7 345.00 | 532799 | WAVERLY7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T4485525SP | FROM->TO | WOLF CREEK 345/69KV TRANSFORMER CKT 1 | E | WERE | WERE | SEAST | SEAST | 0 | 532797 | WOLFCRK7 345.00 | 533653 | WOLFCRK2 69.000 | 0 |  | 1 | 25SP | 100 | 110 | 0 |  | 90.6614 | 96.7 | [7 empty] | CATEGORYB | SINGLE | WAVERLY7 345.00 - WOLF CREEK 345KV CKT 1 | 0 | 532797 | WOLFCRK7 345.00 | 532799 | WAVERLY7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T2315525WP | FROM->TO | WOLF CREEK 345/69KV TRANSFORMER CKT 1 | E | WERE | WERE | SEAST | SEAST | 0 | 532797 | WOLFCRK7 345.00 | 533653 | WOLFCRK2 69.000 | 0 |  | 1 | 25WP | 100 | 110 | 0 |  | 91.7765 | 96.9 | [7 empty] | CATEGORYB | SINGLE | WAVERLY7 345.00 - WOLF CREEK 345KV CKT 1 | 0 | 532797 | WOLFCRK7 345.00 | 532799 | WAVERLY7 345.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T1085020SP | FROM->TO | WOLFFORTH INTERCHANGE (WH 7001668) 230/115/13.2KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 1 | 526525 | WOLFFORTH 6230.00 | 526524 | WOLFFORTH 3115.00 | 526522 | WOLFRTH_TR1113.200 | 1 | 20SP | 120 | 154 | 0 | 95.3 | 95.2607 | 95.7 | [7 empty] | CATEGORYB | SINGLE | CARLISLE INTERCHANGE - LP-DOUD_TP 3115.00 115KV CKT 1 | 0 | 526160 | CARLISLE 3115.00 | 526162 | LP-DOUD_TP 3115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  | FDNS |  | FDNS |  | 5 | 0 | 2015AG1AFS21T2465025SP | FROM->TO | WOLFFORTH INTERCHANGE (WH 7001668) 230/115/13.2KV TRANSFORMER CKT 1 | E | SPS | SPS | SPS-CNPL | SPS-CNPL | 1 | 526525 | WOLFFORTH 6230.00 | 526524 | WOLFFORTH 3115.00 | 526522 | WOLFRTH_TR1113.200 | 1 | 25SP | 120 | 154 | 0 | 105.1 | 105.073 | 99.7 | [7 empty] | CATEGORYB | SINGLE | LP-DOUD_TP 3115.00 - SP-WOLF_TP 3115.00 115KV CKT 1 | 0 | 526162 | LP-DOUD_TP 3115.00 | 526481 | SP-WOLF_TP 3115.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T1265516SP | FROM->TO | WOODWARD (WOODWRD2) 138/69/13.2KV TRANSFORMER CKT 1 | E | OKGE | OKGE | ENID | ENID | 1 | 514785 | WOODWRD4 138.00 | 514782 | WODWRD 2 69.000 | 515771 | WOODWR21 13.200 | 1 | 16SP | 123 | 134 | 0 |  | 73.6639 | 96.1 | [7 empty] | CATEGORYB | SINGLE | FPL SWITCH - MOORELAND 138KV CKT 1 | 0 | 515785 | WINDFRM4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | Transfer Loading < 100%
2015-AG1 | AFS2 |  |  |  | FDNS |  | 5 | 5 | 2015AG1AFS21T695516WP | FROM->TO | WOODWARD (WOODWRD2) 138/69/13.2KV TRANSFORMER CKT 1 | E | OKGE | OKGE | ENID | ENID | 1 | 514785 | WOODWRD4 138.00 | 514782 | WODWRD 2 69.000 | 515771 | WOODWR21 13.200 | 1 | 16WP | 123 | 134 | 0 |  | 73.1179 | 95.8 | [7 empty] | CATEGORYB | SINGLE | FPL SWITCH - MOORELAND 138KV CKT 1 | 0 | 515785 | WINDFRM4 138.00 | 520999 | MOORLND4 138.00 | 0 |  | 1 | Transfer Loading < 100%