## Executive Summary
Executive Summary: GEN-2015-023 Limited Operation System Impact Study
Interconnection Customer (GEN-2015-023) has requested a Limited Operation System Impact Study under the Southwest Power Pool Open Access Transmission Tariff (OATT).
Results of this study determine whether there will be sufficient stability and reliability margin on the Transmission System with anticipated topology to accommodate Interconnection Requests for each Generating Facility at the Interconnection Customer’s requested In-Service Date.
This study evaluates Network Upgrades and Generating Facility exclusions (Scenarios Tab) at the time of service to determine the amount of Interconnection Capacity available to the interconnection customers listed under specific system conditions.
Once a GIA amendment to incorporate Limited Operation is effective, SPP and Transmission Owner will permit Interconnection Customer to operate the Generating Facilities under Limited Operation in accordance with the SPP study results.
Limited Operation
In accordance with Section 8.4.3 of the GIP, Availability of Limited Operation, SPP determines in the DISIS whether the full amount of interconnection capacity requested by the Interconnection Customers is available by the requested Commercial Operation Date (COD). SPP quantifies, within the “Requests” tab of the DISIS report, the amount of interconnection capacity available to Interconnection Customers prior to the in-service date of identified Network Upgrades.
In accordance with GIA Article 5.9, Limited Operation, Interconnection Customers may request SPP to perform studies to determine the Limited Operation of each Generating Facility prior to the completion of the identified mitigation for the observed system constraint(s).
Limited Operation conditions and amounts permitted as determined in this study are detailed in the Scenarios Tab.
Study Limitations
Limited Operation Interconnection Service Available: 205 MW
The following Temporary Operating Guide (TOG) has been proposed to increase the limited operation amount: Until R-Line is installed, Holt will be operated with one circuit breaker in a normally open position and direct transfer trip (DTT) will be activated to trip all generation in GEN-2015-023 when one of the circuit breakers connected at either side of the incomming line from Holt to Grand Island is opened for any reason at the Grand Island . This operating guide must remain active until the R-Line is completed subject to SPP approval.
Limited Operation Interconnection Service Available Considering TOG: 300.72 MW
In the event that an Interconnection Request, with queue priority equal to or higher than a Interconnection Request, which was excluded as a study scenario achieves a status of Commercial Operation prior to the in-service date of all required Network Upgrades, the results of this study revise to 0 MW of available Interconnection Service until a restudy is completed to identify a revised amount for this system condition.
In the event that a Network Upgrade which was included as a study scenario is not placed in-service prior to the Commercial Operation of Interconnection Requests, the results of this study revise to 0 MW of available Interconnection Service until a restudy is completed to identify a revised amount for this system condition.
SPP study results do not guarantee operation for all periods of time. Although studies analyzed many of the most probable contingencies, they are not an all‐inclusive list and cannot account for every operational situation. It is likely that the customer(s) may be required to reduce their generation output to 0 MW, also known as curtailment, under certain system conditions to allow system operators to maintain the reliability of the transmission network.
DISIS Manual Version 2.2
https://www.spp.org/documents/71111/disis-study-manual.pdf
Models Used in Study
Power Flow Analysis: DISIS-2017-002 (2021 ITP Series)
Light: 2026 (26L)
Summer: 2023 (23SP), 2026 (26SP)
Winter: 2026 (26WP)
Stability Analysis: DISIS-2017-002 (2020 Series MDWG Dynamics)
Summer: 2025 (25SP)
Winter: 2025 (25WP)
Short Circuit Analysis: DISIS-2017-002 (2020 Series MDWG Dynamics)
Summer: 2025 (25SP)
Author: SPP Generator Interconnection Department
Published: 04/12/2024

## Revision History
Revision History
Date | Author | Change Description
2022-12-16 | SPP | Posted to SPP website
2024-04-11 | SPP | Final Draft. • Dynamic results revised based on the latest grand prairie model LOIS value considering TOG added to the report • While contingencies in South Dakota (SD) were present in the previous posting of this report, these were erroneously labeled (were duplicative with other contingencies) and were subsequently removed from the report.

## Requests
Gen Number | Group | Queue | Fuel Type | MW Amount | LOIS Amount | LOIS Amount with TOG | Most Limiting Element | Reactive Compensation Requirements (MVAR) | Service | Area | POI | Status
GEN-2015-023 | 02 NEBRASKA | DIS-15-1 | Wind | 300.72 | 205 | 300.72 | 652507 FTTHOMP4 230 996767 FT2 KU1B 230 1 |  | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2007-017IS | 02 NEBRASKA | DIS-15-2-PQ | Wind | 202 |  |  |  |  | ER/NR | OPPD | Ft Thompson-Grand Island 345kV
GEN-2007-018IS | 02 NEBRASKA | DIS-15-2-PQ | Wind | 198 |  |  |  |  | ER/NR | OPPD | Ft Thompson-Grand Island 345kV
ASGI-2015-001 | 03 CENTRAL | DIS-15-1 | Thermal | 6.13 |  |  |  |  | ER | SUNC | Ninnescah 115kV
GEN-2015-005 | 03 CENTRAL | DIS-15-1 | Wind | 200.11 |  |  |  |  | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 04 SOUTHEAST | DIS-15-1 | Solar | 120 |  |  |  |  | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-024 | 03 CENTRAL | DIS-15-1 | Wind | 219.99 |  |  |  |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-025 | 03 CENTRAL | DIS-15-1 | Wind | 219.98 |  |  |  |  | ER | WERE | Tap Thistle - Wichita 345kV Dbl CKT | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-025 | 03 CENTRAL | DIS-14-2 | Wind | 2.42 |  |  |  |  | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-032 | 02 NEBRASKA | DIS-14-2 | Wind | 10.22 |  |  |  |  | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-035 | 05 SOUTHWEST | DIS-14-2 | Solar | 30 |  |  |  |  | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-040 | 05 SOUTHWEST | DIS-14-2 | Wind | 44 |  |  |  |  | ER | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-056 | 04 SOUTHEAST | DIS-14-2 | Wind | 249.35 |  |  |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-064 | 04 SOUTHEAST | DIS-14-2 | Wind | 1 |  |  |  |  | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-001 | 03 CENTRAL | DIS-14-1 | Wind | 200.6 |  |  |  |  | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-002 | 04 SOUTHEAST | DIS-14-1 | Wind | 10.53 |  |  |  |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-004 | 02 NEBRASKA | DIS-14-1 | Wind | 3.96 |  |  |  |  | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 04 SOUTHEAST | DIS-14-1 | Wind | 5.67 |  |  |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-013 | 02 NEBRASKA | DIS-14-1 | Wind | 0.11 |  |  |  |  | ER/NR | LES | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-005 | 05 SOUTHWEST | DIS-13-2 | Wind | 1.65 |  |  |  |  | ER | SPS | FE Clovis 115kV
GEN-2013-019 | 02 NEBRASKA | DIS-13-2 | Wind | 73.6 |  |  |  |  | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2013-002 | 05 SOUTHWEST | DIS-13-1 | Wind | 18.4 |  |  |  |  | ER | SPS | FE Tucumcari 115kV
ASGI-2013-003 | 05 SOUTHWEST | DIS-13-1 | Wind | 18.4 |  |  |  |  | ER | SPS | FE Clovis 115kV
GEN-2013-002 | 02 NEBRASKA | DIS-13-1 | Wind | 50.6 |  |  |  |  | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-008 | 02 NEBRASKA | DIS-13-1 | Wind | 1.2 |  |  |  |  | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-002 | 05 SOUTHWEST | DIS-12-2 | Wind | 18.15 |  |  |  |  | ER | SPS | FE-Clovis Interchange 115kV
GEN-2012-024 | 03 CENTRAL | DIS-12-2 | Wind | 1.8 |  |  |  |  | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-033 | 04 SOUTHEAST | DIS-12-2 | Wind | 0.72 |  |  |  |  | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-006GIA-27 | 04 SOUTHEAST | PQ | Wind | 150 |  |  |  |  | ER | AECI | Remington 138kV
ASGI-2012-006 | 03 CENTRAL | DIS-12-1 | Steam | 22.5 |  |  |  |  | ER | SUNC | Tap Hugoton - Rolla 69kV
GEN-2001-039M | 03 CENTRAL | PQ | Wind | 1 |  |  |  |  | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-004 | 03 CENTRAL | PQ | Wind | 3 |  |  |  |  | ER | WERE | Latham 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | 03 CENTRAL | PQ | Wind | 1 |  |  |  |  | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-021N | 02 NEBRASKA | PQ | Wind | 15 |  |  |  |  | ER | NPPD | Ainsworth Wind Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-002 | 04 SOUTHEAST | PQ | Wind | 1.8 |  |  |  |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | 05 SOUTHWEST | PQ | Wind | 290 |  |  |  |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-004 | 04 SOUTHEAST | DIS-12-1 | Wind | 40.8 |  |  |  |  | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
NPPDBuffaloCountySolar | 02 NEBRASKA | PQ | Solar | 10 |  |  |  |  | ER | NPPD | Kearney Northeast
NPPDBurtCountyWind | 02 NEBRASKA | PQ | Wind | 20 |  |  |  |  | ER | NPPD | Tekamah & Oakland 115kV
GEN-2011-037 | 04 SOUTHEAST | DIS-11-2 | Wind | 6.6 |  |  |  |  | ER | WFEC | Blue Canyon 5 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-054 | 04 SOUTHEAST | DIS-11-2 | Wind | 2 |  |  |  |  | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | 04 SOUTHEAST | DIS-11-1 | Wind | 175 |  |  |  |  | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 04 SOUTHEAST | DIS-11-1 | Wind | 165.6 |  |  |  |  | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-022 | 05 SOUTHWEST | DIS-11-1 | Wind | 299 |  |  |  |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-001 | 05 SOUTHWEST | DIS-10-2 | Wind | 0.3 |  |  |  |  | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-040 | 04 SOUTHEAST | DIS-10-2 | Wind | 1.8 |  |  |  |  | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-022 | 05 SOUTHWEST | DIS-10-1 | Wind | 299.65 |  |  |  |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-047 | 05 SOUTHWEST | DIS-10-1 | Wind | 13.13 |  |  |  |  | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-005 | 03 CENTRAL | DIS-10-1 | Wind | 59.2 |  |  |  |  | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-014 | 05 SOUTHWEST | DIS-10-1 | Wind | 358.8 |  |  |  |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-051 | 05 SOUTHWEST | DIS-09-1 | Wind | 1 |  |  |  |  | ER | SPS | Potter County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | 02 NEBRASKA | DIS-09-1 | Wind | 0.4 |  |  |  |  | ER | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-124 | 03 CENTRAL | DIS-09-1 | Wind | 200.1 |  |  |  |  | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-025 | 03 CENTRAL | ICS1 | Wind | 68.8 |  |  |  |  | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-044 | 04 SOUTHEAST | ICS1 | Wind | 0.3 |  |  |  |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION

## Scenarios
Generation Interconnection Number or Upgrade ID | Assigned Study | Service Type | Point of Interconnection or Upgrade Name | Capacity or Upgrade Details | Steady-State ERIS Status or Available MW | Steady-State NRIS Status or Available MW | Stability Status or Available MW
GEN-2015-023 | DISIS-2015-001 | ERIS/NRIS | Grand Prairie-Grand Island (Holt County NE) 345kV | 300.72 | 205 | 10 | 300.72
50442 (NTC 200220) | ITP | NA | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | Not In-Service | Not In-Service | Not In-Service
50444 (NTC 200220) | ITP | NA | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | Not In-Service | Not In-Service | Not In-Service
50445 (NTC 200220) | ITP | NA | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | Not In-Service | Not In-Service | Not In-Service
50446 (NTC 200220) | ITP | NA | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | Not In-Service | Not In-Service | Not In-Service

## Constraints Summary
Group | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name
02ALL | ERIS | Non-Converge | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
00NR | NRIS | Non-Converge | None | 23SP, 26SP, 26WP | None | [7 empty] | None
02NR | NRIS | Non-Converge | None | 26L | None | [7 empty] | None
02ALL | ERIS | Stability | None | 25S, 25W | None | [7 empty] | None
02ALL | ERIS | Thermal | 652507 FTTHOMP4 230 996767 FT2 KU1B 230 1 | 23SP, 26L, 26SP | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z | 250 | 313 | 65.89 | 113.08 |  |  |  | Holt Co. to Cherry Co. to Gentleman 345 kV (Rplan)
02ALL | ERIS | Thermal | 652507 FTTHOMP4 230 996768 FT2 KU1A 230 1 | 23SP, 26L, 26SP | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z | 250 | 313 | 65.89 | 113.08 |  |  |  | Holt Co. to Cherry Co. to Gentleman 345 kV (Rplan)
00NR | NRIS | Thermal | 640305 ONEILL 7 115 640349 SPENCER7 115 1 | 23SP, 26SP | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV: | 120 | 120 | 99.82 | 105.64 |  |  |  | Holt Co. to Cherry Co. to Gentleman 345 kV (Rplan)
00NR | NRIS | Thermal | 640349 SPENCER7 115 652510 FTRANDL7 115 1 | 23SP, 26SP | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV: | 120 | 120 | 103.14 | 108.98 |  |  |  | Holt Co. to Cherry Co. to Gentleman 345 kV (Rplan)
00NR | NRIS | Thermal | 652507 FTTHOMP4 230 996767 FT2 KU1B 230 1 | 23SP, 26SP | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV: | 250 | 313 | 65.96 | 113.02 |  |  |  | Holt Co. to Cherry Co. to Gentleman 345 kV (Rplan)
00NR | NRIS | Thermal | 652507 FTTHOMP4 230 996768 FT2 KU1A 230 1 | 23SP, 26SP | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z | 250 | 313 | 65.96 | 113.02 |  |  |  | Holt Co. to Cherry Co. to Gentleman 345 kV (Rplan)
02NR | NRIS | Thermal | 652507 FTTHOMP4 230 996763 FT2 KU1B 230 1 | 26L | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z | 250 | 313 | 56.75 | 101.47 |  |  |  | Holt Co. to Cherry Co. to Gentleman 345 kV (Rplan)
02NR | NRIS | Thermal | 652507 FTTHOMP4 230 996764 FT2 KU1A 230 1 | 26L | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z | 250 | 313 | 56.75 | 101.47 |  |  |  | Holt Co. to Cherry Co. to Gentleman 345 kV (Rplan)
02ALL | ERIS | Voltage | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
00NR | NRIS | Voltage | None | 23SP, 26SP, 26WP | None | [7 empty] | None
02NR | NRIS | Voltage | None | 26L | None | [7 empty] | None

## All Thermal
SOLUTIONTYPE | GROUP | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME
Non-Converge | 00NR | 23SP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 00NR | 26SP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 00NR | 26WP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 02ALL | 23SP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 02ALL | 26L | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 02ALL | 26SP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 02ALL | 26WP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 02NR | 26L | N/A | " | Non-Converge |  |  |  |  | None
Thermal | 00NR | 23SP | GEN-2015-023 | TO -> FROM | 640305 ONEILL 7 115 640349 SPENCER7 115 1 | 120 | 120 | 0.03715 | 105.64 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Thermal | 00NR | 23SP | GEN-2015-023 | TO -> FROM | 640305 ONEILL 7 115 640349 SPENCER7 115 1 | 120 | 120 | 0.03715 | 105.47 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Thermal | 00NR | 23SP | GEN-2015-023 | TO -> FROM | 640305 ONEILL 7 115 640349 SPENCER7 115 1 | 120 | 120 | 0.03715 | 105.47 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Thermal | 00NR | 23SP | GEN-2015-023 | TO -> FROM | 640305 ONEILL 7 115 640349 SPENCER7 115 1 | 120 | 120 | 0.03771 | 105.17 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 00NR | 23SP | GEN-2015-023 | TO -> FROM | 640305 ONEILL 7 115 640349 SPENCER7 115 1 | 120 | 120 | 0.03771 | 105.17 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 00NR | 23SP | GEN-2015-023 | TO -> FROM | 640305 ONEILL 7 115 640349 SPENCER7 115 1 | 120 | 120 | 0.03771 | 105.17 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 00NR | 23SP | GEN-2015-023 | TO -> FROM | 640305 ONEILL 7 115 640349 SPENCER7 115 1 | 120 | 120 | 0.03771 | 105.17 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 00NR | 26SP | GEN-2015-023 | TO -> FROM | 640305 ONEILL 7 115 640349 SPENCER7 115 1 | 120 | 120 | 0.03757 | 101.62 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Thermal | 00NR | 26SP | GEN-2015-023 | TO -> FROM | 640305 ONEILL 7 115 640349 SPENCER7 115 1 | 120 | 120 | 0.03757 | 101.58 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Thermal | 00NR | 26SP | GEN-2015-023 | TO -> FROM | 640305 ONEILL 7 115 640349 SPENCER7 115 1 | 120 | 120 | 0.03757 | 101.58 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Thermal | 00NR | 26SP | GEN-2015-023 | TO -> FROM | 640305 ONEILL 7 115 640349 SPENCER7 115 1 | 120 | 120 | 0.03817 | 101.06 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 00NR | 26SP | GEN-2015-023 | TO -> FROM | 640305 ONEILL 7 115 640349 SPENCER7 115 1 | 120 | 120 | 0.03817 | 101.06 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 00NR | 26SP | GEN-2015-023 | TO -> FROM | 640305 ONEILL 7 115 640349 SPENCER7 115 1 | 120 | 120 | 0.03817 | 101.06 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 00NR | 26SP | GEN-2015-023 | TO -> FROM | 640305 ONEILL 7 115 640349 SPENCER7 115 1 | 120 | 120 | 0.03817 | 101.06 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 00NR | 23SP | GEN-2015-023 | TO -> FROM | 640349 SPENCER7 115 652510 FTRANDL7 115 1 | 120 | 120 | 0.03715 | 108.98 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Thermal | 00NR | 23SP | GEN-2015-023 | TO -> FROM | 640349 SPENCER7 115 652510 FTRANDL7 115 1 | 120 | 120 | 0.03715 | 108.81 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Thermal | 00NR | 23SP | GEN-2015-023 | TO -> FROM | 640349 SPENCER7 115 652510 FTRANDL7 115 1 | 120 | 120 | 0.03715 | 108.81 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Thermal | 00NR | 23SP | GEN-2015-023 | TO -> FROM | 640349 SPENCER7 115 652510 FTRANDL7 115 1 | 120 | 120 | 0.03771 | 108.5 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 00NR | 23SP | GEN-2015-023 | TO -> FROM | 640349 SPENCER7 115 652510 FTRANDL7 115 1 | 120 | 120 | 0.03771 | 108.5 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 00NR | 23SP | GEN-2015-023 | TO -> FROM | 640349 SPENCER7 115 652510 FTRANDL7 115 1 | 120 | 120 | 0.03771 | 108.5 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 00NR | 23SP | GEN-2015-023 | TO -> FROM | 640349 SPENCER7 115 652510 FTRANDL7 115 1 | 120 | 120 | 0.03771 | 108.5 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 00NR | 26SP | GEN-2015-023 | TO -> FROM | 640349 SPENCER7 115 652510 FTRANDL7 115 1 | 120 | 120 | 0.03757 | 104.91 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Thermal | 00NR | 26SP | GEN-2015-023 | TO -> FROM | 640349 SPENCER7 115 652510 FTRANDL7 115 1 | 120 | 120 | 0.03757 | 104.87 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Thermal | 00NR | 26SP | GEN-2015-023 | TO -> FROM | 640349 SPENCER7 115 652510 FTRANDL7 115 1 | 120 | 120 | 0.03757 | 104.87 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Thermal | 00NR | 26SP | GEN-2015-023 | TO -> FROM | 640349 SPENCER7 115 652510 FTRANDL7 115 1 | 120 | 120 | 0.03817 | 104.36 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 00NR | 26SP | GEN-2015-023 | TO -> FROM | 640349 SPENCER7 115 652510 FTRANDL7 115 1 | 120 | 120 | 0.03817 | 104.36 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 00NR | 26SP | GEN-2015-023 | TO -> FROM | 640349 SPENCER7 115 652510 FTRANDL7 115 1 | 120 | 120 | 0.03817 | 104.36 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 00NR | 26SP | GEN-2015-023 | TO -> FROM | 640349 SPENCER7 115 652510 FTRANDL7 115 1 | 120 | 120 | 0.03817 | 104.36 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 00NR | 26SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996765 FT2 KU1B 230 1 | 250 | 313 | 0.43395 | 104.73 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Thermal | 00NR | 26SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996765 FT2 KU1B 230 1 | 250 | 313 | 0.43395 | 104.73 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Thermal | 00NR | 26SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996765 FT2 KU1B 230 1 | 250 | 313 | 0.43403 | 103.99 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 00NR | 26SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996765 FT2 KU1B 230 1 | 250 | 313 | 0.43403 | 103.99 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 00NR | 26SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996765 FT2 KU1B 230 1 | 250 | 313 | 0.43403 | 103.99 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 00NR | 26SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996765 FT2 KU1B 230 1 | 250 | 313 | 0.43403 | 103.99 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 00NR | 26SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996765 FT2 KU1B 230 1 | 250 | 313 | 0.43395 | 103.97 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Thermal | 00NR | 26SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996766 FT2 KU1A 230 1 | 250 | 313 | 0.43395 | 104.73 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Thermal | 00NR | 26SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996766 FT2 KU1A 230 1 | 250 | 313 | 0.43395 | 104.73 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Thermal | 00NR | 26SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996766 FT2 KU1A 230 1 | 250 | 313 | 0.43403 | 103.99 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 00NR | 26SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996766 FT2 KU1A 230 1 | 250 | 313 | 0.43403 | 103.99 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 00NR | 26SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996766 FT2 KU1A 230 1 | 250 | 313 | 0.43403 | 103.99 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 00NR | 26SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996766 FT2 KU1A 230 1 | 250 | 313 | 0.43403 | 103.99 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 00NR | 26SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996766 FT2 KU1A 230 1 | 250 | 313 | 0.43395 | 103.97 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Thermal | 00NR | 23SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996767 FT2 KU1B 230 1 | 250 | 313 | 0.43389 | 110.54 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Thermal | 00NR | 23SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996767 FT2 KU1B 230 1 | 250 | 313 | 0.43389 | 110.54 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Thermal | 00NR | 23SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996767 FT2 KU1B 230 1 | 250 | 313 | 0.43397 | 107.06 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 00NR | 23SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996767 FT2 KU1B 230 1 | 250 | 313 | 0.43397 | 107.06 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 00NR | 23SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996767 FT2 KU1B 230 1 | 250 | 313 | 0.43397 | 107.06 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 00NR | 23SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996767 FT2 KU1B 230 1 | 250 | 313 | 0.43397 | 107.06 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 00NR | 23SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996767 FT2 KU1B 230 1 | 250 | 313 | 0.43389 | 107.03 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Thermal | 00NR | 23SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996768 FT2 KU1A 230 1 | 250 | 313 | 0.43389 | 110.54 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Thermal | 00NR | 23SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996768 FT2 KU1A 230 1 | 250 | 313 | 0.43389 | 110.54 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Thermal | 00NR | 23SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996768 FT2 KU1A 230 1 | 250 | 313 | 0.43397 | 107.06 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 00NR | 23SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996768 FT2 KU1A 230 1 | 250 | 313 | 0.43397 | 107.06 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 00NR | 23SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996768 FT2 KU1A 230 1 | 250 | 313 | 0.43397 | 107.06 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 00NR | 23SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996768 FT2 KU1A 230 1 | 250 | 313 | 0.43397 | 107.06 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 00NR | 23SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996768 FT2 KU1A 230 1 | 250 | 313 | 0.43389 | 107.03 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Thermal | 00NR | 26SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996765 FT2 KU1B 230 1 | 250 | 313 | 0.43395 | 106.46 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Thermal | 00NR | 26SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996765 FT2 KU1B 230 1 | 250 | 313 | 0.43395 | 106.46 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Thermal | 00NR | 26SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996765 FT2 KU1B 230 1 | 250 | 313 | 0.43403 | 105.53 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 00NR | 26SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996765 FT2 KU1B 230 1 | 250 | 313 | 0.43403 | 105.53 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 00NR | 26SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996765 FT2 KU1B 230 1 | 250 | 313 | 0.43403 | 105.53 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 00NR | 26SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996765 FT2 KU1B 230 1 | 250 | 313 | 0.43403 | 105.53 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 00NR | 26SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996765 FT2 KU1B 230 1 | 250 | 313 | 0.43395 | 105.5 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Thermal | 00NR | 26SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996766 FT2 KU1A 230 1 | 250 | 313 | 0.43395 | 106.46 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Thermal | 00NR | 26SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996766 FT2 KU1A 230 1 | 250 | 313 | 0.43395 | 106.46 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Thermal | 00NR | 26SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996766 FT2 KU1A 230 1 | 250 | 313 | 0.43403 | 105.53 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 00NR | 26SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996766 FT2 KU1A 230 1 | 250 | 313 | 0.43403 | 105.53 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 00NR | 26SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996766 FT2 KU1A 230 1 | 250 | 313 | 0.43403 | 105.53 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 00NR | 26SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996766 FT2 KU1A 230 1 | 250 | 313 | 0.43403 | 105.53 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 00NR | 26SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996766 FT2 KU1A 230 1 | 250 | 313 | 0.43395 | 105.5 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Thermal | 00NR | 23SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996767 FT2 KU1B 230 1 | 250 | 313 | 0.43389 | 113.02 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Thermal | 00NR | 23SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996767 FT2 KU1B 230 1 | 250 | 313 | 0.43389 | 113.02 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Thermal | 00NR | 23SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996767 FT2 KU1B 230 1 | 250 | 313 | 0.43397 | 108.65 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 00NR | 23SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996767 FT2 KU1B 230 1 | 250 | 313 | 0.43397 | 108.65 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 00NR | 23SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996767 FT2 KU1B 230 1 | 250 | 313 | 0.43397 | 108.65 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 00NR | 23SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996767 FT2 KU1B 230 1 | 250 | 313 | 0.43397 | 108.65 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 00NR | 23SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996767 FT2 KU1B 230 1 | 250 | 313 | 0.43389 | 108.63 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Thermal | 00NR | 23SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996768 FT2 KU1A 230 1 | 250 | 313 | 0.43389 | 113.02 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Thermal | 00NR | 23SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996768 FT2 KU1A 230 1 | 250 | 313 | 0.43389 | 113.02 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Thermal | 00NR | 23SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996768 FT2 KU1A 230 1 | 250 | 313 | 0.43397 | 108.65 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 00NR | 23SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996768 FT2 KU1A 230 1 | 250 | 313 | 0.43397 | 108.65 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 00NR | 23SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996768 FT2 KU1A 230 1 | 250 | 313 | 0.43397 | 108.65 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 00NR | 23SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996768 FT2 KU1A 230 1 | 250 | 313 | 0.43397 | 108.65 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 00NR | 23SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996768 FT2 KU1A 230 1 | 250 | 313 | 0.43389 | 108.63 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Thermal | 02ALL | 26SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996765 FT2 KU1B 230 1 | 250 | 313 | 0.42775 | 104.63 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Thermal | 02ALL | 26SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996765 FT2 KU1B 230 1 | 250 | 313 | 0.42775 | 104.63 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Thermal | 02ALL | 26SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996765 FT2 KU1B 230 1 | 250 | 313 | 0.42772 | 103.91 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 02ALL | 26SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996765 FT2 KU1B 230 1 | 250 | 313 | 0.42772 | 103.91 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 02ALL | 26SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996765 FT2 KU1B 230 1 | 250 | 313 | 0.42772 | 103.91 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 02ALL | 26SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996765 FT2 KU1B 230 1 | 250 | 313 | 0.42772 | 103.91 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 02ALL | 26SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996765 FT2 KU1B 230 1 | 250 | 313 | 0.42775 | 103.89 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Thermal | 02ALL | 26SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996766 FT2 KU1A 230 1 | 250 | 313 | 0.42775 | 104.63 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Thermal | 02ALL | 26SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996766 FT2 KU1A 230 1 | 250 | 313 | 0.42775 | 104.63 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Thermal | 02ALL | 26SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996766 FT2 KU1A 230 1 | 250 | 313 | 0.42772 | 103.91 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 02ALL | 26SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996766 FT2 KU1A 230 1 | 250 | 313 | 0.42772 | 103.91 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 02ALL | 26SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996766 FT2 KU1A 230 1 | 250 | 313 | 0.42772 | 103.91 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 02ALL | 26SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996766 FT2 KU1A 230 1 | 250 | 313 | 0.42772 | 103.91 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 02ALL | 26SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996766 FT2 KU1A 230 1 | 250 | 313 | 0.42775 | 103.89 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Thermal | 02ALL | 23SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996767 FT2 KU1B 230 1 | 250 | 313 | 0.42781 | 110.57 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Thermal | 02ALL | 23SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996767 FT2 KU1B 230 1 | 250 | 313 | 0.42781 | 110.57 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Thermal | 02ALL | 23SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996767 FT2 KU1B 230 1 | 250 | 313 | 0.42781 | 106.98 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Thermal | 02ALL | 23SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996767 FT2 KU1B 230 1 | 250 | 313 | 0.42778 | 106.97 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 02ALL | 23SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996767 FT2 KU1B 230 1 | 250 | 313 | 0.42778 | 106.97 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 02ALL | 23SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996767 FT2 KU1B 230 1 | 250 | 313 | 0.42778 | 106.97 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 02ALL | 23SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996767 FT2 KU1B 230 1 | 250 | 313 | 0.42778 | 106.97 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 02ALL | 23SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996768 FT2 KU1A 230 1 | 250 | 313 | 0.42781 | 110.57 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Thermal | 02ALL | 23SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996768 FT2 KU1A 230 1 | 250 | 313 | 0.42781 | 110.57 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Thermal | 02ALL | 23SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996768 FT2 KU1A 230 1 | 250 | 313 | 0.42781 | 106.98 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Thermal | 02ALL | 23SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996768 FT2 KU1A 230 1 | 250 | 313 | 0.42778 | 106.97 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 02ALL | 23SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996768 FT2 KU1A 230 1 | 250 | 313 | 0.42778 | 106.97 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 02ALL | 23SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996768 FT2 KU1A 230 1 | 250 | 313 | 0.42778 | 106.97 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 02ALL | 23SP | GEN-2015-023 | FROM -> TO | 652506 FTTHOMP3 345 996768 FT2 KU1A 230 1 | 250 | 313 | 0.42778 | 106.97 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 02ALL | 26L | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996763 FT2 KU1B 230 1 | 250 | 313 | 0.42591 | 101.53 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Thermal | 02ALL | 26L | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996763 FT2 KU1B 230 1 | 250 | 313 | 0.42591 | 101.53 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Thermal | 02ALL | 26L | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996763 FT2 KU1B 230 1 | 250 | 313 | 0.42591 | 100.97 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Thermal | 02ALL | 26L | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996763 FT2 KU1B 230 1 | 250 | 313 | 0.42589 | 100.9 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 02ALL | 26L | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996763 FT2 KU1B 230 1 | 250 | 313 | 0.42589 | 100.9 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 02ALL | 26L | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996763 FT2 KU1B 230 1 | 250 | 313 | 0.42589 | 100.9 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 02ALL | 26L | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996763 FT2 KU1B 230 1 | 250 | 313 | 0.42589 | 100.9 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 02ALL | 26L | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996764 FT2 KU1A 230 1 | 250 | 313 | 0.42591 | 101.53 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Thermal | 02ALL | 26L | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996764 FT2 KU1A 230 1 | 250 | 313 | 0.42591 | 101.53 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Thermal | 02ALL | 26L | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996764 FT2 KU1A 230 1 | 250 | 313 | 0.42591 | 100.97 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Thermal | 02ALL | 26L | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996764 FT2 KU1A 230 1 | 250 | 313 | 0.42589 | 100.9 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 02ALL | 26L | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996764 FT2 KU1A 230 1 | 250 | 313 | 0.42589 | 100.9 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 02ALL | 26L | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996764 FT2 KU1A 230 1 | 250 | 313 | 0.42589 | 100.9 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 02ALL | 26L | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996764 FT2 KU1A 230 1 | 250 | 313 | 0.42589 | 100.9 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 02ALL | 26SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996765 FT2 KU1B 230 1 | 250 | 313 | 0.42775 | 106.35 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Thermal | 02ALL | 26SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996765 FT2 KU1B 230 1 | 250 | 313 | 0.42775 | 106.35 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Thermal | 02ALL | 26SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996765 FT2 KU1B 230 1 | 250 | 313 | 0.42772 | 105.45 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 02ALL | 26SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996765 FT2 KU1B 230 1 | 250 | 313 | 0.42772 | 105.45 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 02ALL | 26SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996765 FT2 KU1B 230 1 | 250 | 313 | 0.42772 | 105.45 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 02ALL | 26SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996765 FT2 KU1B 230 1 | 250 | 313 | 0.42772 | 105.45 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 02ALL | 26SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996765 FT2 KU1B 230 1 | 250 | 313 | 0.42775 | 105.42 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Thermal | 02ALL | 26SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996766 FT2 KU1A 230 1 | 250 | 313 | 0.42775 | 106.35 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Thermal | 02ALL | 26SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996766 FT2 KU1A 230 1 | 250 | 313 | 0.42775 | 106.35 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Thermal | 02ALL | 26SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996766 FT2 KU1A 230 1 | 250 | 313 | 0.42772 | 105.45 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 02ALL | 26SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996766 FT2 KU1A 230 1 | 250 | 313 | 0.42772 | 105.45 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 02ALL | 26SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996766 FT2 KU1A 230 1 | 250 | 313 | 0.42772 | 105.45 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 02ALL | 26SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996766 FT2 KU1A 230 1 | 250 | 313 | 0.42772 | 105.45 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 02ALL | 26SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996766 FT2 KU1A 230 1 | 250 | 313 | 0.42775 | 105.42 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Thermal | 02ALL | 23SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996767 FT2 KU1B 230 1 | 250 | 313 | 0.42781 | 113.08 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Thermal | 02ALL | 23SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996767 FT2 KU1B 230 1 | 250 | 313 | 0.42781 | 113.08 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Thermal | 02ALL | 23SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996767 FT2 KU1B 230 1 | 250 | 313 | 0.42781 | 108.56 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Thermal | 02ALL | 23SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996767 FT2 KU1B 230 1 | 250 | 313 | 0.42778 | 108.56 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 02ALL | 23SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996767 FT2 KU1B 230 1 | 250 | 313 | 0.42778 | 108.56 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 02ALL | 23SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996767 FT2 KU1B 230 1 | 250 | 313 | 0.42778 | 108.56 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 02ALL | 23SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996767 FT2 KU1B 230 1 | 250 | 313 | 0.42778 | 108.56 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 02ALL | 23SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996768 FT2 KU1A 230 1 | 250 | 313 | 0.42781 | 113.08 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Thermal | 02ALL | 23SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996768 FT2 KU1A 230 1 | 250 | 313 | 0.42781 | 113.08 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Thermal | 02ALL | 23SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996768 FT2 KU1A 230 1 | 250 | 313 | 0.42781 | 108.56 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Thermal | 02ALL | 23SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996768 FT2 KU1A 230 1 | 250 | 313 | 0.42778 | 108.56 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 02ALL | 23SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996768 FT2 KU1A 230 1 | 250 | 313 | 0.42778 | 108.56 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 02ALL | 23SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996768 FT2 KU1A 230 1 | 250 | 313 | 0.42778 | 108.56 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 02ALL | 23SP | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996768 FT2 KU1A 230 1 | 250 | 313 | 0.42778 | 108.56 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 02NR | 26L | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996763 FT2 KU1B 230 1 | 250 | 313 | 0.4364 | 101.47 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Thermal | 02NR | 26L | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996763 FT2 KU1B 230 1 | 250 | 313 | 0.4364 | 101.47 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Thermal | 02NR | 26L | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996763 FT2 KU1B 230 1 | 250 | 313 | 0.4364 | 100.91 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Thermal | 02NR | 26L | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996763 FT2 KU1B 230 1 | 250 | 313 | 0.43648 | 100.84 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 02NR | 26L | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996763 FT2 KU1B 230 1 | 250 | 313 | 0.43648 | 100.84 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 02NR | 26L | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996763 FT2 KU1B 230 1 | 250 | 313 | 0.43648 | 100.84 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 02NR | 26L | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996763 FT2 KU1B 230 1 | 250 | 313 | 0.43648 | 100.84 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 02NR | 26L | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996764 FT2 KU1A 230 1 | 250 | 313 | 0.4364 | 101.47 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Thermal | 02NR | 26L | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996764 FT2 KU1A 230 1 | 250 | 313 | 0.4364 | 101.47 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Thermal | 02NR | 26L | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996764 FT2 KU1A 230 1 | 250 | 313 | 0.4364 | 100.91 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Thermal | 02NR | 26L | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996764 FT2 KU1A 230 1 | 250 | 313 | 0.43648 | 100.84 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 02NR | 26L | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996764 FT2 KU1A 230 1 | 250 | 313 | 0.43648 | 100.84 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 02NR | 26L | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996764 FT2 KU1A 230 1 | 250 | 313 | 0.43648 | 100.84 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 02NR | 26L | GEN-2015-023 | TO -> FROM | 652507 FTTHOMP4 230 996764 FT2 KU1A 230 1 | 250 | 313 | 0.43648 | 100.84 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:

## All Voltage
SOLUTION TYPE | GROUP | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME
Voltage | 00NR | N/A | N/A | None | [7 empty] | None
Voltage | 02ALL | N/A | N/A | None | [7 empty] | None
Voltage | 02NR | N/A | N/A | None | [7 empty] | None

## Stability Analysis Results
Group | Season | Model Dispatch | Event ID | Event Description | Event Category | Rotor Angle Stability | Transient Voltage Response > 0.7 p.u. | Transient Voltage Response < 1.2 p.u. | Post Fault Steady State Voltage > 0.9 p.u. | Post Fault Steady State Voltage < 1.1 p.u. | Damping Factor > 0.8 % | Low Voltage Rides Through | Violation Summary | Primary Mitigation
02 - Nebraska | 25S | PQCQ | 5688 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | No | Yes | Yes | Relay trippings were observed in FRMR CTY (W1), ROCKCK (G1), and OUTLAW (G1, G21, and G22) generators following the event due to overvoltage protection. The same issue exists in the PQ case. | Disabling the overvoltage relay instances in FRMR CTY (W1), ROCKCK (G1), and OUTLAW (G1, G21, and G22) generators results in steady-state overvoltage above 1.1 p.u. As the issue was observed in the base case, it was not attributed to the study.
02 - Nebraska | 25S | PQCQ | 5692 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | No | Yes | Yes | Relay trippings were observed in FRMR CTY (W1), ROCKCK (G1), and OUTLAW (G1, G21, and G22) generators following the event due to overvoltage protection. The same issue exists in the PQ case. | Disabling the overvoltage relay instances in FRMR CTY (W1), ROCKCK (G1), and OUTLAW (G1, G21, and G22) generators results in steady-state overvoltage above 1.1 p.u. As the issue was observed in the base case, it was not attributed to the study.
02 - Nebraska | 25S | PQCQ | 7198 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 7199 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 7200 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 7201 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 7204 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 7205 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 7206 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 7347 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 91231 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 106138 | 3 Phase fault on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | No | Yes | Yes | Yes | Yes | Yes | Voltage oscillatory response during the fault in the Grand Prarie units. The transient voltage response of the Grand Prarie units falls below 0.7 p.u. The same issue exists in the PQ case. | Removing the reclosing event resolves the issue. As the issue was observed in the base case, it was not attributed to the study.
02 - Nebraska | 25S | PQCQ | 106139 | 3 Phase fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.2. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes
02 - Nebraska | 25S | PQCQ | 106262 | 3 Phase fault on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.2. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.3. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 111905 | 3 Phase fault on CALAMS 7 115.00 (640096) 115 kV Bus a. Apply fault at the CALAMS 7 115.00 (640096) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWND7 (640050) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 b.2. CALAMS 7 (640096) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 111947 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 111948 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 111949 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 111957 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 7 (640272) 115.0 kV to MCCOOL 3 (640271) 345.0 kV to MCCOOL19 (640274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 111958 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | No | Yes | Yes | Relay trippings were observed in FRMR CTY (W1), ROCKCK (G1), and OUTLAW (G1, G21, and G22) generators following the event due to overvoltage protection. The same issue exists in the PQ case. | Disabling the overvoltage relay instances in FRMR CTY (W1), ROCKCK (G1), and OUTLAW (G1, G21, and G22) generators results in steady-state overvoltage above 1.1 p.u. As the issue was observed in the base case, it was not attributed to the study.
02 - Nebraska | 25S | PQCQ | 111974 | 3 Phase fault on THEDFRD7 115.00 (640381) 115 kV Bus a. Apply fault at the THEDFRD7 115.00 (640381) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. THEDFRD7 (640381) 115.0 kV to THEDFRD3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 111977 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 111978 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 114481 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.2. LO.LS-FT-BE3 (659424) 345.0 kV to G17-114-TAP (760357) 345.0 kV Transmission Circuit #1 b.3. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.4. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to non-convergence. The same issue exists in the PQ case. | Reducing the tripping time from 6 cycles to 5 cycles and removing the reclosing event resolves the issue. As the issue was observed in the base case, it was not attributed to the study.
02 - Nebraska | 25S | PQCQ | 114585 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 114587 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 114588 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 114589 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 114590 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 114723 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 114729 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 114731 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 114732 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 114791 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 114792 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 114793 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 114825 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 114826 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 114827 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 114877 | 3 Phase fault on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 579450 gen-2016-075 345 648513 grpr1 3 345 1 | 3 Phase fault on GEN-2016-075345.00 (579450) 345 kV Bus a. Apply fault at the GEN-2016-075345.00 (579450) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2016-075 (579450) 345.0 kV to GRPR1 3 (648513) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 648527 grpr_dmy_bus 345 648513 grpr1 3 345 z1 | 3 Phase fault on GRPR_DMY_BUS (648527) 345 kV Bus a. Apply fault at the GRPR_DMY_BUS (648527) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPR_DMY_BUS (648527) 345.0 kV to GRPR1 3 (648513) 345.0 kV Transmission Circuit #z1 b.2. GRPR_DMY_BUS (648527) 345.0 kV to GRPR1 3 (648513) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 584650 gen-2015-023 345 640510 holt.co3 345 1 | 3 Phase fault on GEN-2015-023345.00 (584650) 345 kV Bus a. Apply fault at the GEN-2015-023345.00 (584650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2015-023 (584650) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 587680 gen-2016-074 345 640374 sweet w3 345 1 | 3 Phase fault on GEN-2016-074345.00 (587680) 345 kV Bus a. Apply fault at the GEN-2016-074345.00 (587680) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2016-074 (587680) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 587764 g16-094-tap 230 652507 ftthomp4 230 1 | 3 Phase fault on G16-094-TAP 230.00 (587764) 230 kV Bus a. Apply fault at the G16-094-TAP 230.00 (587764) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G16-094-TAP (587764) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 589324 g17-094-tap 230 652507 ftthomp4 230 1 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 589324 g17-094-tap 230 652507 ftthomp4 230 2 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 640065 axtell 3 345 640374 sweet w3 345 1 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 640178 geneva 7 115 640272 mccool 7 115 1 | 3 Phase fault on GENEVA 7 115.00 (640178) 115 kV Bus a. Apply fault at the GENEVA 7 115.00 (640178) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENEVA 7 (640178) 115.0 kV to MCCOOL 7 (640272) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 640183 gentlmn3 345 640252 keyston3 345 1 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 640183 gentlmn3 345 640325 redwilo3 345 1 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | Yes | Unstable response following the reclosing event in all network and machine variables. The same issue exists in the PQ case. | Removing the reclosing event or increasing the reclosing time from 20 cycles to 25 cycles after the fault clears resolves the issue. As the issue was observed in the base case, it was not attributed to the study.
02 - Nebraska | 25S | PQCQ | 640183 gentlmn3 345 640374 sweet w3 345 1 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | Yes | Unstable response following the reclosing event in all network and machine variables. The same issue exists in the PQ case. | Removing the reclosing event or increasing the reclosing time from 20 cycles to 25 cycles after the fault clears resolves the issue. As the issue was observed in the base case, it was not attributed to the study.
02 - Nebraska | 25S | PQCQ | 640183 gentlmn3 345 640374 sweet w3 345 2 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | Yes | Unstable response following the reclosing event in all network and machine variables. The same issue exists in the PQ case. | Removing the reclosing event or increasing the reclosing time from 20 cycles to 25 cycles after the fault clears resolves the issue. As the issue was observed in the base case, it was not attributed to the study.
02 - Nebraska | 25S | PQCQ | 640271 mccool 3 345 640277 moore 3 345 1 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 640271 mccool 3 345 653571 gr isld3 345 1 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 640272 mccool 7 115 640413 york sw7 115 1 | 3 Phase fault on MCCOOL 7 115.00 (640272) 115 kV Bus a. Apply fault at the MCCOOL 7 115.00 (640272) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOL 7 (640272) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 640277 moore 3 345 640525 tobias 3 345 1 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | No | Yes | Yes | Relay trippings were observed in FRMR CTY (W1), ROCKCK (G1), and OUTLAW (G1, G21, and G22) generators following the event due to overvoltage protection. The same issue exists in the PQ case. | Disabling the overvoltage relay instances in FRMR CTY (W1), ROCKCK (G1), and OUTLAW (G1, G21, and G22) generators results in steady-state overvoltage above 1.1 p.u. As the issue was observed in the base case, it was not attributed to the study.
02 - Nebraska | 25S | PQCQ | 640277 moore 3 345 640590 monolith 3 345 1 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | No | Yes | Yes | Relay trippings were observed in FRMR CTY (W1), ROCKCK (G1), and OUTLAW (G1, G21, and G22) generators following the event due to overvoltage protection. The same issue exists in the PQ case. | Disabling the overvoltage relay instances in FRMR CTY (W1), ROCKCK (G1), and OUTLAW (G1, G21, and G22) generators results in steady-state overvoltage above 1.1 p.u. As the issue was observed in the base case, it was not attributed to the study.
02 - Nebraska | 25S | PQCQ | 640359 stapleton 7 115 640381 thedfrd7 115 1 | 3 Phase fault on STAPLETON 7115.00 (640359) 115 kV Bus a. Apply fault at the STAPLETON 7115.00 (640359) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STAPLETON 7 (640359) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 640374 sweet w3 345 653571 gr isld3 345 1 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 648513 grpr1 3 345 648520 grpr2 3 345 1 | 3 Phase fault on GRPR1 3 345.00 (648513) 345 kV Bus a. Apply fault at the GRPR1 3 345.00 (648513) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPR1 3 (648513) 345.0 kV to GRPR2 3 (648520) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 648513 grpr1 3 345 652532 gr prairie 3 345 1 | 3 Phase fault on GRPR1 3 345.00 (648513) 345 kV Bus a. Apply fault at the GRPR1 3 345.00 (648513) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPR1 3 (648513) 345.0 kV to GR PRAIRIE 3 (652532) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 659130 chapelle-be3 345 659428 cc.ls-lo-be3 345 z | 3 Phase fault on CHAPELLE-BE3345.00 (659130) 345 kV Bus a. Apply fault at the CHAPELLE-BE3345.00 (659130) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 659130 chapelle-be3 345 659433 tripleh__ua3 345 1 | 3 Phase fault on CHAPELLE-BE3345.00 (659130) 345 kV Bus a. Apply fault at the CHAPELLE-BE3345.00 (659130) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAPELLE-BE3 (659130) 345.0 kV to TRIPLEH__UA3 (659433) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 84000 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 b.4. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 84001 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 84008 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 84010 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 85244 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 85798 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.10. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.11. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.12. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes
02 - Nebraska | 25S | PQCQ | 104891 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112245 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112246 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112247 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to GENTLM2G (640011) 24.0 kV Two Winding #1 b.2. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112248 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112251 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112252 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.3. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.4. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112253 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112254 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112255 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112262 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112263 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112264 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112265 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112272 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112275 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112276 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 b.4. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112277 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112278 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112279 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112302 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.4. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112303 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112305 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 b.4. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112306 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 115993 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP19 (652273) 13.8 kV Three Winding #1 b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding #1 b.7. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.8. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.9. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.10. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.11. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 115996 | Single Phase Fault with Stuck Breaker on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply Fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.7. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 115997 | Single Phase Fault with Stuck Breaker on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply Fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.7. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 115998 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.5. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.6. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.7. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 115999 | Single Phase Fault with Stuck Breaker on LETCHER4 230.00 (652606) 230 kV Bus a. Apply Fault at the LETCHER4 230.00 (652606) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.3. LETCHER4 (652606) 230.0 kV to LETCHER7 (652609) 115.0 kV to LETCHER9 (652608) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116072 | Single Phase Fault with Stuck Breaker on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply Fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_2-BEG (659111) 20.0 kV Two Winding #1 b.2. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.3. LO.LS-FT-BE3 (659424) 345.0 kV to G17-114-TAP (760357) 345.0 kV Transmission Circuit #1 b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.5. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116082 | Single Phase Fault with Stuck Breaker on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply Fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_2-BEG (659111) 20.0 kV Two Winding #1 b.2. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.3. LO.LS-FT-BE3 (659424) 345.0 kV to G17-114-TAP (760357) 345.0 kV Transmission Circuit #1 b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.5. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116253 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SD.PW1__-BE9 (659327) 34.5 kV to WESSINGTON1W (659296) 0.6 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116254 | Single Phase Fault with Stuck Breaker on STORLA__-BE4230.00 (659122) 230 kV Bus a. Apply Fault at the STORLA__-BE4230.00 (659122) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 b.2. WESSINGTON 4 (652607) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.3. WESSINGTON 4 (652607) 230.0 kV to SD.PW1__-BE4 (659295) 230.0 kV Transmission Circuit #1 b.4. WESSINGTON 4 (652607) 230.0 kV to WESSINGTON 9 (662100) 34.5 kV Two Winding #1 b.5. HANLON 4 (652513) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.6. STORLA__-BE4 (659122) 230.0 kV to STORLA__-BE7 (659123) 115.0 kV to ST.KV1A_-BE9 (659119) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116257 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SD.PW1__-BE9 (659327) 34.5 kV to WESSINGTON1W (659296) 0.6 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116258 | Single Phase Fault with Stuck Breaker on STORLA__-BE4230.00 (659122) 230 kV Bus a. Apply Fault at the STORLA__-BE4230.00 (659122) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 b.2. WESSINGTON 4 (652607) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.3. WESSINGTON 4 (652607) 230.0 kV to SD.PW1__-BE4 (659295) 230.0 kV Transmission Circuit #1 b.4. WESSINGTON 4 (652607) 230.0 kV to WESSINGTON 9 (662100) 34.5 kV Two Winding #1 b.5. HANLON 4 (652513) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.6. STORLA__-BE4 (659122) 230.0 kV to STORLA__-BE7 (659123) 115.0 kV to ST.KV1A_-BE9 (659119) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116277 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116278 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116281 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116282 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116286 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116287 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116288 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE2-3G (652556) 13.8 kV Two Winding #1 b.2. OAHE 9 (652589) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.3. OAHE 29 (652598) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.4. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.5. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.6. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.7. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116665 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) kV Bus b. Clear Fault after cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116666 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) kV Bus b. Clear Fault after cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116667 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116668 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116669 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116670 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116671 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116673 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116674 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.2. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116675 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 b.2. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116676 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116677 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.3. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.7. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.8. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes
02 - Nebraska | 25S | PQCQ | 116679 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) kV Bus b. Clear Fault after cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116680 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.2. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116681 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 b.2. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116682 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116683 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.3. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.7. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.8. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes
02 - Nebraska | 25S | PQCQ | 116684 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to G17-114-TAP (760357) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116685 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to G17-114-TAP (760357) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116686 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116687 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116688 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to G17-114-TAP (760357) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116689 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116690 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to G17-114-TAP (760357) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116691 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116693 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes
02 - Nebraska | 25S | PQCQ | 116694 | Single Phase Fault with Stuck Breaker on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply Fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116696 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes
02 - Nebraska | 25S | PQCQ | 116697 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISL19 (653314) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #1 b.2. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116698 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes
02 - Nebraska | 25S | PQCQ | 116830 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116831 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116834 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116835 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116908 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116922 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116923 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116924 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116935 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116944 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116974 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 116983 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 117044 | Single Phase Fault with Stuck Breaker on TRIPLEH__UA3345.00 (659433) 345 kV Bus a. Apply Fault at the TRIPLEH__UA3345.00 (659433) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to G17-114-TAP (760357) 345.0 kV Transmission Circuit #1 b.5. CHAPELLE-BE3 (659130) 345.0 kV to TRIPLEH__UA3 (659433) 345.0 kV Transmission Circuit #1 b.6. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH1B-UA9 (659434) 34.5 kV to TRPLHH1T-UA9 (659435) 13.8 kV Three Winding #1 b.7. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH2B-UA9 (659438) 34.5 kV to TRPLHH2T-UA9 (659439) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 579450 gen-2016-075 345 648513 grpr1 3 345 1 | Single Phase Fault with Stuck Breaker on GEN-2016-075345.00 (579450) 345 kV Bus a. Apply Fault at the GEN-2016-075345.00 (579450) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-075 (579450) 345.0 kV to GRPR1 3 (648513) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 648527 grpr_dmy_bus 345 648513 grpr1 3 345 z1 | Single Phase Fault with Stuck Breaker on GRPR_DMY_BUS (648527) 345 kV Bus a. Apply Fault at the GRPR_DMY_BUS (648527) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRPR_DMY_BUS (648527) 345.0 kV to GRPR1 3 (648513) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 584650 gen-2015-023 345 640510 holt.co3 345 1 | Single Phase Fault with Stuck Breaker on GEN-2015-023345.00 (584650) 345 kV Bus a. Apply Fault at the GEN-2015-023345.00 (584650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2015-023 (584650) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 587680 gen-2016-074 345 640374 sweet w3 345 1 | Single Phase Fault with Stuck Breaker on GEN-2016-074345.00 (587680) 345 kV Bus a. Apply Fault at the GEN-2016-074345.00 (587680) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-074 (587680) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 587764 g16-094-tap 230 652507 ftthomp4 230 1 | Single Phase Fault with Stuck Breaker on G16-094-TAP 230.00 (587764) 230 kV Bus a. Apply Fault at the G16-094-TAP 230.00 (587764) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-094-TAP (587764) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 589324 g17-094-tap 230 652507 ftthomp4 230 1 | Single Phase Fault with Stuck Breaker on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply Fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 589324 g17-094-tap 230 652507 ftthomp4 230 2 | Single Phase Fault with Stuck Breaker on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply Fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 640096 calams 7 115 640381 thedfrd7 115 1 | Single Phase Fault with Stuck Breaker on CALAMS 7 115.00 (640096) 115 kV Bus a. Apply Fault at the CALAMS 7 115.00 (640096) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CALAMS 7 (640096) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 640178 geneva 7 115 640272 mccool 7 115 1 | Single Phase Fault with Stuck Breaker on GENEVA 7 115.00 (640178) 115 kV Bus a. Apply Fault at the GENEVA 7 115.00 (640178) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENEVA 7 (640178) 115.0 kV to MCCOOL 7 (640272) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 640272 mccool 7 115 640413 york sw7 115 1 | Single Phase Fault with Stuck Breaker on MCCOOL 7 115.00 (640272) 115 kV Bus a. Apply Fault at the MCCOOL 7 115.00 (640272) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 7 (640272) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 640359 stapleton 7 115 640381 thedfrd7 115 1 | Single Phase Fault with Stuck Breaker on STAPLETON 7115.00 (640359) 115 kV Bus a. Apply Fault at the STAPLETON 7115.00 (640359) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STAPLETON 7 (640359) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 640510 holt.co3 345 652832 grprar1-lnx3 345 1 | Single Phase Fault with Stuck Breaker on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply Fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes
02 - Nebraska | 25S | PQCQ | 640510 holt.co3 345 653871 gr isld-lnx3 345 1 | Single Phase Fault with Stuck Breaker on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply Fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes
02 - Nebraska | 25S | PQCQ | 648513 grpr1 3 345 648520 grpr2 3 345 1 | Single Phase Fault with Stuck Breaker on GRPR1 3 345.00 (648513) 345 kV Bus a. Apply Fault at the GRPR1 3 345.00 (648513) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRPR1 3 (648513) 345.0 kV to GRPR2 3 (648520) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 648513 grpr1 3 345 652532 gr prairie 3 345 1 | Single Phase Fault with Stuck Breaker on GRPR1 3 345.00 (648513) 345 kV Bus a. Apply Fault at the GRPR1 3 345.00 (648513) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRPR1 3 (648513) 345.0 kV to GR PRAIRIE 3 (652532) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 652532 gr prairie 3 345 652832 grprar1-lnx3 345 z | Single Phase Fault with Stuck Breaker on GR PRAIRIE 3345.00 (652532) 345 kV Bus a. Apply Fault at the GR PRAIRIE 3345.00 (652532) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes
02 - Nebraska | 25S | PQCQ | 659130 chapelle-be3 345 659428 cc.ls-lo-be3 345 z | Single Phase Fault with Stuck Breaker on CHAPELLE-BE3345.00 (659130) 345 kV Bus a. Apply Fault at the CHAPELLE-BE3345.00 (659130) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 106138 + 106139 | Prior Outage: - HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 - GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z 3 Phase Fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.2. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 106138 + 106262 | Prior Outage: - HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 - GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z 3 Phase Fault on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.2. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.3. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 106138 + 584650 gen-2015-023 345 640510 holt.co3 345 1 | Prior Outage: - HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 - GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z 3 Phase Fault on GEN-2015-023345.00 (584650) 345 kV Bus a. Apply fault at the GEN-2015-023345.00 (584650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2015-023 (584650) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 106138 + 648513 grpr1 3 345 652532 gr prairie 3 345 1 | Prior Outage: - HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 - GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z 3 Phase Fault on GRPR1 3 345.00 (648513) 345 kV Bus a. Apply fault at the GRPR1 3 345.00 (648513) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPR1 3 (648513) 345.0 kV to GR PRAIRIE 3 (652532) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 106139 + 106138 | Prior Outage: - GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z - HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 3 Phase Fault on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 106139 + 111949 | Prior Outage: - GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z - HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 3 Phase Fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes
02 - Nebraska | 25S | PQCQ | 106139 + 111977 | Prior Outage: - GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z - HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 3 Phase Fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes
02 - Nebraska | 25S | PQCQ | 106139 + 111978 | Prior Outage: - GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z - HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 3 Phase Fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes
02 - Nebraska | 25S | PQCQ | 106139 + 584650 gen-2015-023 345 640510 holt.co3 345 1 | Prior Outage: - GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z - HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 3 Phase Fault on GEN-2015-023345.00 (584650) 345 kV Bus a. Apply fault at the GEN-2015-023345.00 (584650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2015-023 (584650) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 106139 + 640271 mccool 3 345 653571 gr isld3 345 1 | Prior Outage: - GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z - HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 3 Phase Fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes
02 - Nebraska | 25S | PQCQ | 106139 + 640374 sweet w3 345 653571 gr isld3 345 1 | Prior Outage: - GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z - HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 3 Phase Fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes
02 - Nebraska | 25S | PQCQ | 106262 + 106138 | Prior Outage: - FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z - FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 - GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z 3 Phase Fault on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 111949 + 106139 | Prior Outage: - GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 3 Phase Fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.2. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 111977 + 106139 | Prior Outage: - GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 3 Phase Fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.2. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 111978 + 106139 | Prior Outage: - GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 3 Phase Fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.2. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 584650 gen-2015-023 345 640510 holt.co3 345 1 + 106138 | Prior Outage: - GEN-2015-023 (584650) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 3 Phase Fault on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 584650 gen-2015-023 345 640510 holt.co3 345 1 + 106139 | Prior Outage: - GEN-2015-023 (584650) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 3 Phase Fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.2. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 640271 mccool 3 345 653571 gr isld3 345 1 + 106139 | Prior Outage: - MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 3 Phase Fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.2. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 640374 sweet w3 345 653571 gr isld3 345 1 + 106139 | Prior Outage: - SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 3 Phase Fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.2. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 648513 grpr1 3 345 652532 gr prairie 3 345 1 + 106138 | Prior Outage: - GRPR1 3 (648513) 345.0 kV to GR PRAIRIE 3 (652532) 345.0 kV Transmission Circuit #1 3 Phase Fault on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 106138 + 653571 gr isld3 345 640374 sweet w3 345 1 | Prior Outage: - HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 - GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z 3 Phase Fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 106138 + 653571 gr isld3 345 640271 mccool 3 345 | Prior Outage: - HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 - GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z 3 Phase Fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to MCCOOL 3 (640271) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 106138 + swshunt: 653571 gr isld3 345 | Prior Outage: - HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 - GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z 3 Phase Fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 106138 + 111949 | Prior Outage: - HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 - GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z 3 Phase Fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 106139 + 114877 | Prior Outage: - GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z - HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 3 Phase Fault on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 106139 + 652506 ftthomp3 345 652507 ftthomp4 230 652274 ftthomp29 13.8 | Prior Outage: - GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z - HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 3 Phase Fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 5688 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | No | Yes | Yes | Relay trippings were observed in FRMR CTY (W1), ROCKCK (G1), and OUTLAW (G1, G21, and G22) generators following the event due to overvoltage protection. The same issue exists in the PQ case. | Disabling the overvoltage relay instances in FRMR CTY (W1), ROCKCK (G1), and OUTLAW (G1, G21, and G22) generators results in steady-state overvoltage above 1.1 p.u. As the issue was observed in the base case, it was not attributed to the study.
02 - Nebraska | 25W | PQCQ | 5692 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | No | Yes | Yes | Relay trippings were observed in FRMR CTY (W1), ROCKCK (G1), and OUTLAW (G1, G21, and G22) generators following the event due to overvoltage protection. The same issue exists in the PQ case. | Disabling the overvoltage relay instances in FRMR CTY (W1), ROCKCK (G1), and OUTLAW (G1, G21, and G22) generators results in steady-state overvoltage above 1.1 p.u. As the issue was observed in the base case, it was not attributed to the study.
02 - Nebraska | 25W | PQCQ | 7198 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 7199 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 7200 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 7201 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 7204 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 7205 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 7206 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 7347 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 91231 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 106138 | 3 Phase fault on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 106139 | 3 Phase fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.2. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes
02 - Nebraska | 25W | PQCQ | 106262 | 3 Phase fault on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.2. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.3. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 111905 | 3 Phase fault on CALAMS 7 115.00 (640096) 115 kV Bus a. Apply fault at the CALAMS 7 115.00 (640096) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWND7 (640050) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 b.2. CALAMS 7 (640096) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 111947 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 111948 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 111949 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 111957 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 7 (640272) 115.0 kV to MCCOOL 3 (640271) 345.0 kV to MCCOOL19 (640274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 111958 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | No | Yes | Yes | Relay trippings were observed in FRMR CTY (W1), ROCKCK (G1), and OUTLAW (G1, G21, and G22) generators following the event due to overvoltage protection. The same issue exists in the PQ case. | Disabling the overvoltage relay instances in FRMR CTY (W1), ROCKCK (G1), and OUTLAW (G1, G21, and G22) generators results in steady-state overvoltage above 1.1 p.u. As the issue was observed in the base case, it was not attributed to the study.
02 - Nebraska | 25W | PQCQ | 111974 | 3 Phase fault on THEDFRD7 115.00 (640381) 115 kV Bus a. Apply fault at the THEDFRD7 115.00 (640381) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. THEDFRD7 (640381) 115.0 kV to THEDFRD3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 111977 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 111978 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 114481 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.2. LO.LS-FT-BE3 (659424) 345.0 kV to G17-114-TAP (760357) 345.0 kV Transmission Circuit #1 b.3. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.4. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 114585 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 114587 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 114588 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 114589 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 114590 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 114723 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 114729 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 114731 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 114732 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 114791 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 114792 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 114793 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 114825 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 114826 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 114827 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 114877 | 3 Phase fault on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 579450 gen-2016-075 345 648513 grpr1 3 345 1 | 3 Phase fault on GEN-2016-075345.00 (579450) 345 kV Bus a. Apply fault at the GEN-2016-075345.00 (579450) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2016-075 (579450) 345.0 kV to GRPR1 3 (648513) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 648527 grpr_dmy_bus 345 648513 grpr1 3 345 z1 | 3 Phase fault on GRPR_DMY_BUS (648527) 345 kV Bus a. Apply fault at the GRPR_DMY_BUS (648527) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPR_DMY_BUS (648527) 345.0 kV to GRPR1 3 (648513) 345.0 kV Transmission Circuit #z1 b.2. GRPR_DMY_BUS (648527) 345.0 kV to GRPR1 3 (648513) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 584650 gen-2015-023 345 640510 holt.co3 345 1 | 3 Phase fault on GEN-2015-023345.00 (584650) 345 kV Bus a. Apply fault at the GEN-2015-023345.00 (584650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2015-023 (584650) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 587680 gen-2016-074 345 640374 sweet w3 345 1 | 3 Phase fault on GEN-2016-074345.00 (587680) 345 kV Bus a. Apply fault at the GEN-2016-074345.00 (587680) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2016-074 (587680) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 587764 g16-094-tap 230 652507 ftthomp4 230 1 | 3 Phase fault on G16-094-TAP 230.00 (587764) 230 kV Bus a. Apply fault at the G16-094-TAP 230.00 (587764) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G16-094-TAP (587764) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 589324 g17-094-tap 230 652507 ftthomp4 230 1 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 589324 g17-094-tap 230 652507 ftthomp4 230 2 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 640065 axtell 3 345 640374 sweet w3 345 1 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 640178 geneva 7 115 640272 mccool 7 115 1 | 3 Phase fault on GENEVA 7 115.00 (640178) 115 kV Bus a. Apply fault at the GENEVA 7 115.00 (640178) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENEVA 7 (640178) 115.0 kV to MCCOOL 7 (640272) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 640183 gentlmn3 345 640252 keyston3 345 1 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | Yes | Unstable response following the reclosing event in all network and machine variables. The same issue exists in the PQ case. | Removing the reclosing event or increasing the reclosing time from 20 cycles to 32 cycles after the fault clears resolves the issue. As the issue was observed in the base case, it was not attributed to the study.
02 - Nebraska | 25W | PQCQ | 640183 gentlmn3 345 640325 redwilo3 345 1 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | Yes | Unstable response following the reclosing event in all network and machine variables. The same issue exists in the PQ case. | Removing the reclosing event or increasing the reclosing time from 20 cycles to 32 cycles after the fault clears resolves the issue. As the issue was observed in the base case, it was not attributed to the study.
02 - Nebraska | 25W | PQCQ | 640183 gentlmn3 345 640374 sweet w3 345 1 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | Yes | Unstable response following the reclosing event in all network and machine variables. The same issue exists in the PQ case. | Removing the reclosing event or increasing the reclosing time from 20 cycles to 32 cycles after the fault clears resolves the issue. As the issue was observed in the base case, it was not attributed to the study.
02 - Nebraska | 25W | PQCQ | 640183 gentlmn3 345 640374 sweet w3 345 2 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | Yes | Unstable response following the reclosing event in all network and machine variables. The same issue exists in the PQ case. | Removing the reclosing event or increasing the reclosing time from 20 cycles to 32 cycles after the fault clears resolves the issue. As the issue was observed in the base case, it was not attributed to the study.
02 - Nebraska | 25W | PQCQ | 640271 mccool 3 345 640277 moore 3 345 1 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 640271 mccool 3 345 653571 gr isld3 345 1 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 640272 mccool 7 115 640413 york sw7 115 1 | 3 Phase fault on MCCOOL 7 115.00 (640272) 115 kV Bus a. Apply fault at the MCCOOL 7 115.00 (640272) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOL 7 (640272) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 640277 moore 3 345 640525 tobias 3 345 1 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | No | Yes | Yes | Relay trippings were observed in FRMR CTY (W1), ROCKCK (G1), and OUTLAW (G1, G21, and G22) generators following the event due to overvoltage protection. The same issue exists in the PQ case. | Disabling the overvoltage relay instances in FRMR CTY (W1), ROCKCK (G1), and OUTLAW (G1, G21, and G22) generators results in steady-state overvoltage above 1.1 p.u. As the issue was observed in the base case, it was not attributed to the study.
02 - Nebraska | 25W | PQCQ | 640277 moore 3 345 640590 monolith 3 345 1 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | No | Yes | Yes | Relay trippings were observed in FRMR CTY (W1), ROCKCK (G1), and OUTLAW (G1, G21, and G22) generators following the event due to overvoltage protection. The same issue exists in the PQ case. | Disabling the overvoltage relay instances in FRMR CTY (W1), ROCKCK (G1), and OUTLAW (G1, G21, and G22) generators results in steady-state overvoltage above 1.1 p.u. As the issue was observed in the base case, it was not attributed to the study.
02 - Nebraska | 25W | PQCQ | 640359 stapleton 7 115 640381 thedfrd7 115 1 | 3 Phase fault on STAPLETON 7115.00 (640359) 115 kV Bus a. Apply fault at the STAPLETON 7115.00 (640359) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STAPLETON 7 (640359) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 640374 sweet w3 345 653571 gr isld3 345 1 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 648513 grpr1 3 345 648520 grpr2 3 345 1 | 3 Phase fault on GRPR1 3 345.00 (648513) 345 kV Bus a. Apply fault at the GRPR1 3 345.00 (648513) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPR1 3 (648513) 345.0 kV to GRPR2 3 (648520) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 648513 grpr1 3 345 652532 gr prairie 3 345 1 | 3 Phase fault on GRPR1 3 345.00 (648513) 345 kV Bus a. Apply fault at the GRPR1 3 345.00 (648513) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPR1 3 (648513) 345.0 kV to GR PRAIRIE 3 (652532) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 659130 chapelle-be3 345 659428 cc.ls-lo-be3 345 z | 3 Phase fault on CHAPELLE-BE3345.00 (659130) 345 kV Bus a. Apply fault at the CHAPELLE-BE3345.00 (659130) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 659130 chapelle-be3 345 659433 tripleh__ua3 345 1 | 3 Phase fault on CHAPELLE-BE3345.00 (659130) 345 kV Bus a. Apply fault at the CHAPELLE-BE3345.00 (659130) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAPELLE-BE3 (659130) 345.0 kV to TRIPLEH__UA3 (659433) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 84000 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 b.4. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 84001 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 84008 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 84010 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 85244 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 85798 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.10. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.11. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.12. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes
02 - Nebraska | 25W | PQCQ | 104891 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112245 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112246 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112247 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to GENTLM2G (640011) 24.0 kV Two Winding #1 b.2. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112248 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112251 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112252 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.3. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.4. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112253 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112254 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112255 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112262 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112263 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112264 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112265 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112272 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112275 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112276 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 b.4. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112277 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112278 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112279 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112302 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.4. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112303 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112305 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 b.4. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112306 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 115993 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP19 (652273) 13.8 kV Three Winding #1 b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding #1 b.7. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.8. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.9. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.10. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.11. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 115996 | Single Phase Fault with Stuck Breaker on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply Fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.7. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 115997 | Single Phase Fault with Stuck Breaker on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply Fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.7. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 115998 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.5. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.6. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.7. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 115999 | Single Phase Fault with Stuck Breaker on LETCHER4 230.00 (652606) 230 kV Bus a. Apply Fault at the LETCHER4 230.00 (652606) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.3. LETCHER4 (652606) 230.0 kV to LETCHER7 (652609) 115.0 kV to LETCHER9 (652608) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116072 | Single Phase Fault with Stuck Breaker on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply Fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_2-BEG (659111) 20.0 kV Two Winding #1 b.2. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.3. LO.LS-FT-BE3 (659424) 345.0 kV to G17-114-TAP (760357) 345.0 kV Transmission Circuit #1 b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.5. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116082 | Single Phase Fault with Stuck Breaker on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply Fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_2-BEG (659111) 20.0 kV Two Winding #1 b.2. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.3. LO.LS-FT-BE3 (659424) 345.0 kV to G17-114-TAP (760357) 345.0 kV Transmission Circuit #1 b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.5. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116253 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SD.PW1__-BE9 (659327) 34.5 kV to WESSINGTON1W (659296) 0.6 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116254 | Single Phase Fault with Stuck Breaker on STORLA__-BE4230.00 (659122) 230 kV Bus a. Apply Fault at the STORLA__-BE4230.00 (659122) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 b.2. WESSINGTON 4 (652607) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.3. WESSINGTON 4 (652607) 230.0 kV to SD.PW1__-BE4 (659295) 230.0 kV Transmission Circuit #1 b.4. WESSINGTON 4 (652607) 230.0 kV to WESSINGTON 9 (662100) 34.5 kV Two Winding #1 b.5. HANLON 4 (652513) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.6. STORLA__-BE4 (659122) 230.0 kV to STORLA__-BE7 (659123) 115.0 kV to ST.KV1A_-BE9 (659119) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116257 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SD.PW1__-BE9 (659327) 34.5 kV to WESSINGTON1W (659296) 0.6 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116258 | Single Phase Fault with Stuck Breaker on STORLA__-BE4230.00 (659122) 230 kV Bus a. Apply Fault at the STORLA__-BE4230.00 (659122) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 b.2. WESSINGTON 4 (652607) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.3. WESSINGTON 4 (652607) 230.0 kV to SD.PW1__-BE4 (659295) 230.0 kV Transmission Circuit #1 b.4. WESSINGTON 4 (652607) 230.0 kV to WESSINGTON 9 (662100) 34.5 kV Two Winding #1 b.5. HANLON 4 (652513) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.6. STORLA__-BE4 (659122) 230.0 kV to STORLA__-BE7 (659123) 115.0 kV to ST.KV1A_-BE9 (659119) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116277 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116278 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116281 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116282 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116286 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116287 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116288 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE2-3G (652556) 13.8 kV Two Winding #1 b.2. OAHE 9 (652589) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.3. OAHE 29 (652598) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.4. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.5. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.6. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.7. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116665 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) kV Bus b. Clear Fault after cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116666 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) kV Bus b. Clear Fault after cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116667 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116668 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116669 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116670 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116671 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116673 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116674 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.2. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116675 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 b.2. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116676 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116677 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.3. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.7. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.8. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes
02 - Nebraska | 25W | PQCQ | 116679 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) kV Bus b. Clear Fault after cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116680 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.2. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116681 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 b.2. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116682 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116683 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.3. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.7. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.8. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes
02 - Nebraska | 25W | PQCQ | 116684 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to G17-114-TAP (760357) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116685 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to G17-114-TAP (760357) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116686 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116687 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116688 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to G17-114-TAP (760357) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116689 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116690 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to G17-114-TAP (760357) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116691 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116693 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes
02 - Nebraska | 25W | PQCQ | 116694 | Single Phase Fault with Stuck Breaker on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply Fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116696 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes
02 - Nebraska | 25W | PQCQ | 116697 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISL19 (653314) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #1 b.2. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116698 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes
02 - Nebraska | 25W | PQCQ | 116830 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116831 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116834 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116835 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116908 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116922 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116923 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116924 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116935 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116944 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116974 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 116983 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 117044 | Single Phase Fault with Stuck Breaker on TRIPLEH__UA3345.00 (659433) 345 kV Bus a. Apply Fault at the TRIPLEH__UA3345.00 (659433) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to G17-114-TAP (760357) 345.0 kV Transmission Circuit #1 b.5. CHAPELLE-BE3 (659130) 345.0 kV to TRIPLEH__UA3 (659433) 345.0 kV Transmission Circuit #1 b.6. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH1B-UA9 (659434) 34.5 kV to TRPLHH1T-UA9 (659435) 13.8 kV Three Winding #1 b.7. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH2B-UA9 (659438) 34.5 kV to TRPLHH2T-UA9 (659439) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 579450 gen-2016-075 345 648513 grpr1 3 345 1 | Single Phase Fault with Stuck Breaker on GEN-2016-075345.00 (579450) 345 kV Bus a. Apply Fault at the GEN-2016-075345.00 (579450) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-075 (579450) 345.0 kV to GRPR1 3 (648513) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 648527 grpr_dmy_bus 345 648513 grpr1 3 345 z1 | Single Phase Fault with Stuck Breaker on GRPR_DMY_BUS (648527) 345 kV Bus a. Apply Fault at the GRPR_DMY_BUS (648527) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRPR_DMY_BUS (648527) 345.0 kV to GRPR1 3 (648513) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 584650 gen-2015-023 345 640510 holt.co3 345 1 | Single Phase Fault with Stuck Breaker on GEN-2015-023345.00 (584650) 345 kV Bus a. Apply Fault at the GEN-2015-023345.00 (584650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2015-023 (584650) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 587680 gen-2016-074 345 640374 sweet w3 345 1 | Single Phase Fault with Stuck Breaker on GEN-2016-074345.00 (587680) 345 kV Bus a. Apply Fault at the GEN-2016-074345.00 (587680) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-074 (587680) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 587764 g16-094-tap 230 652507 ftthomp4 230 1 | Single Phase Fault with Stuck Breaker on G16-094-TAP 230.00 (587764) 230 kV Bus a. Apply Fault at the G16-094-TAP 230.00 (587764) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-094-TAP (587764) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 589324 g17-094-tap 230 652507 ftthomp4 230 1 | Single Phase Fault with Stuck Breaker on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply Fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 589324 g17-094-tap 230 652507 ftthomp4 230 2 | Single Phase Fault with Stuck Breaker on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply Fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 640096 calams 7 115 640381 thedfrd7 115 1 | Single Phase Fault with Stuck Breaker on CALAMS 7 115.00 (640096) 115 kV Bus a. Apply Fault at the CALAMS 7 115.00 (640096) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CALAMS 7 (640096) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 640178 geneva 7 115 640272 mccool 7 115 1 | Single Phase Fault with Stuck Breaker on GENEVA 7 115.00 (640178) 115 kV Bus a. Apply Fault at the GENEVA 7 115.00 (640178) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENEVA 7 (640178) 115.0 kV to MCCOOL 7 (640272) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 640272 mccool 7 115 640413 york sw7 115 1 | Single Phase Fault with Stuck Breaker on MCCOOL 7 115.00 (640272) 115 kV Bus a. Apply Fault at the MCCOOL 7 115.00 (640272) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 7 (640272) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 640359 stapleton 7 115 640381 thedfrd7 115 1 | Single Phase Fault with Stuck Breaker on STAPLETON 7115.00 (640359) 115 kV Bus a. Apply Fault at the STAPLETON 7115.00 (640359) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STAPLETON 7 (640359) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 640510 holt.co3 345 652832 grprar1-lnx3 345 1 | Single Phase Fault with Stuck Breaker on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply Fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes
02 - Nebraska | 25W | PQCQ | 640510 holt.co3 345 653871 gr isld-lnx3 345 1 | Single Phase Fault with Stuck Breaker on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply Fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes
02 - Nebraska | 25W | PQCQ | 648513 grpr1 3 345 648520 grpr2 3 345 1 | Single Phase Fault with Stuck Breaker on GRPR1 3 345.00 (648513) 345 kV Bus a. Apply Fault at the GRPR1 3 345.00 (648513) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRPR1 3 (648513) 345.0 kV to GRPR2 3 (648520) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 648513 grpr1 3 345 652532 gr prairie 3 345 1 | Single Phase Fault with Stuck Breaker on GRPR1 3 345.00 (648513) 345 kV Bus a. Apply Fault at the GRPR1 3 345.00 (648513) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRPR1 3 (648513) 345.0 kV to GR PRAIRIE 3 (652532) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 652532 gr prairie 3 345 652832 grprar1-lnx3 345 z | Single Phase Fault with Stuck Breaker on GR PRAIRIE 3345.00 (652532) 345 kV Bus a. Apply Fault at the GR PRAIRIE 3345.00 (652532) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes
02 - Nebraska | 25W | PQCQ | 659130 chapelle-be3 345 659428 cc.ls-lo-be3 345 z | Single Phase Fault with Stuck Breaker on CHAPELLE-BE3345.00 (659130) 345 kV Bus a. Apply Fault at the CHAPELLE-BE3345.00 (659130) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 106138 + 106139 | Prior Outage: - HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 - GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z 3 Phase Fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.2. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 106138 + 106262 | Prior Outage: - HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 - GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z 3 Phase Fault on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.2. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.3. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 106138 + 584650 gen-2015-023 345 640510 holt.co3 345 1 | Prior Outage: - HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 - GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z 3 Phase Fault on GEN-2015-023345.00 (584650) 345 kV Bus a. Apply fault at the GEN-2015-023345.00 (584650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2015-023 (584650) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 106138 + 648513 grpr1 3 345 652532 gr prairie 3 345 1 | Prior Outage: - HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 - GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z 3 Phase Fault on GRPR1 3 345.00 (648513) 345 kV Bus a. Apply fault at the GRPR1 3 345.00 (648513) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPR1 3 (648513) 345.0 kV to GR PRAIRIE 3 (652532) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 106139 + 106138 | Prior Outage: - GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z - HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 3 Phase Fault on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 106139 + 111949 | Prior Outage: - GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z - HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 3 Phase Fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes
02 - Nebraska | 25W | PQCQ | 106139 + 111977 | Prior Outage: - GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z - HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 3 Phase Fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes
02 - Nebraska | 25W | PQCQ | 106139 + 111978 | Prior Outage: - GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z - HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 3 Phase Fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes
02 - Nebraska | 25W | PQCQ | 106139 + 584650 gen-2015-023 345 640510 holt.co3 345 1 | Prior Outage: - GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z - HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 3 Phase Fault on GEN-2015-023345.00 (584650) 345 kV Bus a. Apply fault at the GEN-2015-023345.00 (584650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2015-023 (584650) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 106139 + 640271 mccool 3 345 653571 gr isld3 345 1 | Prior Outage: - GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z - HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 3 Phase Fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes
02 - Nebraska | 25W | PQCQ | 106139 + 640374 sweet w3 345 653571 gr isld3 345 1 | Prior Outage: - GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z - HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 3 Phase Fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes
02 - Nebraska | 25W | PQCQ | 106262 + 106138 | Prior Outage: - FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z - FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 - GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z 3 Phase Fault on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 111949 + 106139 | Prior Outage: - GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 3 Phase Fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.2. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 111977 + 106139 | Prior Outage: - GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 3 Phase Fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.2. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 111978 + 106139 | Prior Outage: - GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 3 Phase Fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.2. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 584650 gen-2015-023 345 640510 holt.co3 345 1 + 106138 | Prior Outage: - GEN-2015-023 (584650) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 3 Phase Fault on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 584650 gen-2015-023 345 640510 holt.co3 345 1 + 106139 | Prior Outage: - GEN-2015-023 (584650) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 3 Phase Fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.2. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 640271 mccool 3 345 653571 gr isld3 345 1 + 106139 | Prior Outage: - MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 3 Phase Fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.2. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 640374 sweet w3 345 653571 gr isld3 345 1 + 106139 | Prior Outage: - SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 3 Phase Fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.2. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 648513 grpr1 3 345 652532 gr prairie 3 345 1 + 106138 | Prior Outage: - GRPR1 3 (648513) 345.0 kV to GR PRAIRIE 3 (652532) 345.0 kV Transmission Circuit #1 3 Phase Fault on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 106138 + 653571 gr isld3 345 640374 sweet w3 345 1 | Prior Outage: - HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 - GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z 3 Phase Fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 106138 + 653571 gr isld3 345 640271 mccool 3 345 | Prior Outage: - HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 - GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z 3 Phase Fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to MCCOOL 3 (640271) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 106138 + swshunt: 653571 gr isld3 345 | Prior Outage: - HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 - GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z 3 Phase Fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 106138 + 111949 | Prior Outage: - HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 - GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z 3 Phase Fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 106139 + 114877 | Prior Outage: - GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z - HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 3 Phase Fault on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 106139 + 652506 ftthomp3 345 652507 ftthomp4 230 652274 ftthomp29 13.8 | Prior Outage: - GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z - HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 3 Phase Fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQ | 5688 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | No | Yes | Yes | Relay trippings were observed in FRMR CTY (W1), ROCKCK (G1), and OUTLAW (G1, G21, and G22) generators following the event due to overvoltage protection. | Disabling the overvoltage relay instances in FRMR CTY (W1), ROCKCK (G1), and OUTLAW (G1, G21, and G22) generators results in steady-state overvoltage above 1.1 p.u. As the issue was observed in the base case, it was not attributed to the study.
02 - Nebraska | 25S | PQ | 5692 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | No | Yes | Yes | Relay trippings were observed in FRMR CTY (W1), ROCKCK (G1), and OUTLAW (G1, G21, and G22) generators following the event due to overvoltage protection. | Disabling the overvoltage relay instances in FRMR CTY (W1), ROCKCK (G1), and OUTLAW (G1, G21, and G22) generators results in steady-state overvoltage above 1.1 p.u. As the issue was observed in the base case, it was not attributed to the study.
02 - Nebraska | 25S | PQ | 106138 | 3 Phase fault on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | No | Yes | Yes | Yes | Yes | Yes | Voltage oscillatory response during the fault in the Grand Prarie units. The transient voltage response of the Grand Prarie units falls below 0.7 p.u. | Removing the reclosing event resolves the issue.
02 - Nebraska | 25S | PQ | 111958 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | No | Yes | Yes | Relay trippings were observed in FRMR CTY (W1), ROCKCK (G1), and OUTLAW (G1, G21, and G22) generators following the event due to overvoltage protection. | Disabling the overvoltage relay instances in FRMR CTY (W1), ROCKCK (G1), and OUTLAW (G1, G21, and G22) generators results in steady-state overvoltage above 1.1 p.u. As the issue was observed in the base case, it was not attributed to the study.
02 - Nebraska | 25S | PQ | 640183 gentlmn3 345 640325 redwilo3 345 1 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | Yes | Unstable response following the reclosing event in all network and machine variables. | Removing the reclosing event or increasing the reclosing time from 20 cycles to 30 cycles after the fault clears resolves the issue.
02 - Nebraska | 25S | PQ | 640183 gentlmn3 345 640374 sweet w3 345 1 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | Yes | Unstable response following the reclosing event in all network and machine variables. | Removing the reclosing event or increasing the reclosing time from 20 cycles to 30 cycles after the fault clears resolves the issue.
02 - Nebraska | 25S | PQ | 640183 gentlmn3 345 640374 sweet w3 345 2 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | Yes | Unstable response following the reclosing event in all network and machine variables. | Removing the reclosing event or increasing the reclosing time from 20 cycles to 30 cycles after the fault clears resolves the issue.
02 - Nebraska | 25S | PQ | 640277 moore 3 345 640525 tobias 3 345 1 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | No | Yes | Yes | Relay trippings were observed in FRMR CTY (W1), ROCKCK (G1), and OUTLAW (G1, G21, and G22) generators following the event due to overvoltage protection. | Disabling the overvoltage relay instances in FRMR CTY (W1), ROCKCK (G1), and OUTLAW (G1, G21, and G22) generators results in steady-state overvoltage above 1.1 p.u. As the issue was observed in the base case, it was not attributed to the study.
02 - Nebraska | 25S | PQ | 640277 moore 3 345 640590 monolith 3 345 1 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | No | Yes | Yes | Relay trippings were observed in FRMR CTY (W1), ROCKCK (G1), and OUTLAW (G1, G21, and G22) generators following the event due to overvoltage protection. | Disabling the overvoltage relay instances in FRMR CTY (W1), ROCKCK (G1), and OUTLAW (G1, G21, and G22) generators results in steady-state overvoltage above 1.1 p.u. As the issue was observed in the base case, it was not attributed to the study.
02 - Nebraska | 25W | PQ | 5688 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | No | Yes | Yes | Relay trippings were observed in FRMR CTY (W1), ROCKCK (G1), and OUTLAW (G1, G21, and G22) generators following the event due to overvoltage protection. | Disabling the overvoltage relay instances in FRMR CTY (W1), ROCKCK (G1), and OUTLAW (G1, G21, and G22) generators results in steady-state overvoltage above 1.1 p.u. As the issue was observed in the base case, it was not attributed to the study.
02 - Nebraska | 25W | PQ | 5692 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | No | Yes | Yes | Relay trippings were observed in FRMR CTY (W1), ROCKCK (G1), and OUTLAW (G1, G21, and G22) generators following the event due to overvoltage protection. | Disabling the overvoltage relay instances in FRMR CTY (W1), ROCKCK (G1), and OUTLAW (G1, G21, and G22) generators results in steady-state overvoltage above 1.1 p.u. As the issue was observed in the base case, it was not attributed to the study.
02 - Nebraska | 25W | PQ | 111958 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | No | Yes | Yes | Relay trippings were observed in FRMR CTY (W1), ROCKCK (G1), and OUTLAW (G1, G21, and G22) generators following the event due to overvoltage protection. | Disabling the overvoltage relay instances in FRMR CTY (W1), ROCKCK (G1), and OUTLAW (G1, G21, and G22) generators results in steady-state overvoltage above 1.1 p.u. As the issue was observed in the base case, it was not attributed to the study.
02 - Nebraska | 25W | PQ | 640183 gentlmn3 345 640252 keyston3 345 1 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | Yes | Unstable response following the reclosing event in all network and machine variables. | Removing the reclosing event or increasing the reclosing time from 20 cycles to 32 cycles after the fault clears resolves the issue.
02 - Nebraska | 25W | PQ | 640183 gentlmn3 345 640325 redwilo3 345 1 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | Yes | Unstable response following the reclosing event in all network and machine variables. | Removing the reclosing event or increasing the reclosing time from 20 cycles to 32 cycles after the fault clears resolves the issue.
02 - Nebraska | 25W | PQ | 640183 gentlmn3 345 640374 sweet w3 345 1 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | Yes | Unstable response following the reclosing event in all network and machine variables. | Removing the reclosing event or increasing the reclosing time from 20 cycles to 32 cycles after the fault clears resolves the issue.
02 - Nebraska | 25W | PQ | 640183 gentlmn3 345 640374 sweet w3 345 2 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | Yes | Unstable response following the reclosing event in all network and machine variables. | Removing the reclosing event or increasing the reclosing time from 20 cycles to 32 cycles after the fault clears resolves the issue.
02 - Nebraska | 25W | PQ | 640277 moore 3 345 640525 tobias 3 345 1 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | No | Yes | Yes | Relay trippings were observed in FRMR CTY (W1), ROCKCK (G1), and OUTLAW (G1, G21, and G22) generators following the event due to overvoltage protection. | Disabling the overvoltage relay instances in FRMR CTY (W1), ROCKCK (G1), and OUTLAW (G1, G21, and G22) generators results in steady-state overvoltage above 1.1 p.u. As the issue was observed in the base case, it was not attributed to the study.
02 - Nebraska | 25W | PQ | 640277 moore 3 345 640590 monolith 3 345 1 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | No | Yes | Yes | Relay trippings were observed in FRMR CTY (W1), ROCKCK (G1), and OUTLAW (G1, G21, and G22) generators following the event due to overvoltage protection. | Disabling the overvoltage relay instances in FRMR CTY (W1), ROCKCK (G1), and OUTLAW (G1, G21, and G22) generators results in steady-state overvoltage above 1.1 p.u. As the issue was observed in the base case, it was not attributed to the study.