## Executive Summary
Executive Summary: GEN-2016-037 Limited Operation System Impact Study
Interconnection Customer (GEN-2016-037) has requested a Limited Operation Interconnection System Impact Study under the Southwest Power Pool Open Access Transmission Tariff (OATT).
Results of this study determine whether there will be sufficient stability and reliability margin on the Transmission System with anticipated topology to accommodate Interconnection Requests for each Generating Facility at the Interconnection Customer’s requested In-Service Date.
This study evaluates Network Upgrades and Generating Facility exclusions (Scenarios Tab) at the time of service to determine the amount of Interconnection Capacity available to the interconection customers listed under specific system conditions.
Once a GIA amendment to incorporate Limited Operation is effective, SPP and Transmission Owner will permit Interconnection Customer to operate the Generating Facilities under Limited Operation in accordance with the SPP study results.
Limited Operation
In accordance with Section 8.4.3 of the GIP, Availability of Limited Operation, SPP determines in the DISIS whether the full amount of interconnection capacity requested by the Interconnection Customers is available by the requested Commercial Operation Date (COD). SPP quantifies, within the “Requests” tab of the DISIS report, the amount of interconnection capacity available to Interconnection Customers prior to the in-service date of identified Network Upgrades.
In accordance with GIA Article 5.9, Limited Operation, Interconnection Customers may request SPP to perform studies to determine the Limited Operation of each Generating Facility prior to the completion of the identified mitigation for the observed system constraint(s).
Limited Operation conditions and amounts permitted as determined in this study are detailed in the Scenarios Tab.
Study Limitations
Limited Operation Interconnection Service Available between April 1 - May 31 : 300 MW
Limited Operation Interconnection Service Available between June 1 - Sept 30 : 300 MW
Limited Operation Interconnection Service Available between Oct 1 - Nov 30 : 300 MW
Limited Operation Interconnection Service Available between Dec 1 - March 31 : 300 MW
In the event that a Network Upgrade which was included as a study scenario is not placed in-service prior to the Commercial Operation of Interconnection Requests, the results of this study revise to 0 MW of available Interconnection Service until a restudy is completed to identify a revised amount for this system condition.
SPP study results do not guarantee operation for all periods of time. Although studies analyzed many of the most probable contingencies, they are not an all‐inclusive list and cannot account for every operational situation. It is likely that the customer(s) may be required to reduce their generation output to 0 MW, also known as curtailment, under certain system conditions to allow system operators to maintain the reliability of the transmission network.
DISIS Manual Version 3.0
https://spp.org/documents/71111/DISIS%20Study%20Manual%2020240424.pdf
Models Used in Study
Power Flow Analysis: DISIS-2018-002 and DISIS-2019-001 Phase 2 (2021 ITP Series)
Light: 2026 (26L)
Summer: 2023 (23SP), 2026 (26SP)
Winter: 2026 (26WP)
Stability Analysis: DISIS-2018-002/DISIS-2019-001 Phase 2 (P2) (2020 Series MDWG Dynamics)* * modified to exclude network upgrades assigned through DISIS-1702 and DISIS-1801
Summer: 2025 (25SP)
Winter: 2025 (25WP)
Short Circuit Analysis: DISIS-2018-002/DISIS-2019-001 Phase 2 (P2) (2020 Series MDWG Dynamics)
Summer: 2025 (25SP)
Author: SPP Generator Interconnection Department
Published: 8/16/2024

## Revision History
Revision History
Date | Author | Change Description
2024-07-03 | SPP | Initial Posting
2024-08-14 | SPP | Updated results based on revised assumptions, addded GEN-2015-093 in the requests tab

## Requests
LOIS Amount
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | April 1 - May 31 | June 1 - Sept 30 | Oct 1 - Nov 30 | Dec 1 - March 31 | Reactive Compensation Requirement (MVAR) | Service | Area | POI | Status
GEN-2016-037 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 300 | 300 | 300 | 300 | 300 |  | ER | AEPW | Chisholm-Gracemont 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-010 | 01 NORTH | 18 | DIS-17-1 | Wind | 200.1 | [5 empty] | ER | WAPA | Rhame 230 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-014 | 01 NORTH | 18 | DIS-17-1 | Wind | 300 | [5 empty] | ER | WAPA | Philip Tap 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-048 | 01 NORTH | 18 | DIS-17-1 | Wind | 300 | [5 empty] | ER | WAPA | Neset 230 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-094 | 01 NORTH | 18 | DIS-17-1 | Wind | 200 | [5 empty] | ER | WAPA | Fort Thompson-Huron 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-097 | 01 NORTH | 18 | DIS-17-1 | Solar | 128 | [5 empty] | ER | WAPA | Underwood 115 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-004 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 201.6 | [5 empty] | ER | SUNC | Elm Creek - Summit 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-005 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 190 | [5 empty] | ER | WERE | Marmaton - Litchfield 161 kV | FACILITY STUDY STAGE
GEN-2017-018 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 189 | [5 empty] | ER/NR | SUNC | Thistle 345 kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-022 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 65 | [5 empty] | ER/NR | WERE | Altoona- NE Parson 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-068 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 103.5 | [5 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-086 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 150 | [5 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-011 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 151.8 | [5 empty] | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-023 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 85 | [5 empty] | ER/NR | WFEC | Hugo Power Plant 138 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-027 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 140 | [5 empty] | ER | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-033 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 200 | [5 empty] | ER | AEPW | Oklaunion 345 kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-036 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 100 | [5 empty] | ER | AEPW | Snyder - Cache 138 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-040 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200.1 | [5 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-057 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [5 empty] | ER | AEPW | Hosston 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-061 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 101.5 | [5 empty] | ER/NR | GRDA | GRDA1 to CLARMR 5 161kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-071 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 | [5 empty] | ER | OKGE | Greenwood 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-072 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 52.2 | [5 empty] | ER | OKGE | Greenwood 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-073 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [5 empty] | ER | GRDA | Dry Gulch 161kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-074 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [5 empty] | ER | AEPW | Pryor Junction 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-075 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [5 empty] | ER | OKGE | Hugo-Sunnyside 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-076 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 52.2 | [5 empty] | ER | AEPW | Chamber Springs 161kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-077 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 | [5 empty] | ER | AEPW | Explorer Claremore Tap EXCLART4 | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-092 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [5 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-047 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 102 | [5 empty] | ER/NR | SPS | Cole 115kV | IA PENDING
GEN-2017-100 | 05 SOUTHWEST | 18 | DIS-17-1 | Solar | 102.6 | [5 empty] | ER/NR | SPS | Texas County 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-036 | 01 NORTH | 17 | DIS-16-2 | Wind | 44.6 | [5 empty] | ER | WAPA | Granite Falls 115kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-087 | 01 NORTH | 17 | DIS-16-2 | Wind | 98.9 | [5 empty] | ER | WAPA | Bismark-Glenham 230 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-094 | 01 NORTH | 17 | DIS-16-2 | Wind | 200 | [5 empty] | ER | WAPA | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-130 | 01 NORTH | 17 | DIS-16-2 | Wind | 202 | [5 empty] | ER | WAPA | Leland Olds 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-074 | 02 NEBRASKA | 17 | DIS-16-2 | Wind | 200 | [5 empty] | ER | NPPD | Sweetwater 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-147 | 02 NEBRASKA | 17 | DIS-16-2 | Solar | 40 | [5 empty] | ER | NPPD | Sidney 115 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-111 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [5 empty] | ER | WERE | Reno - Summit 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-115 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 300 | [5 empty] | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-149 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [5 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-150 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [5 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-153 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 134 | [5 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-160 | 03 CENTRAL | 17 | DIS-16-2 | Storage | 20 | [5 empty] | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-176 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [5 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-091 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 303.6 | [5 empty] | ER | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-095 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 200 | [5 empty] | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-097 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [5 empty] | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-102 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 150.9 | [5 empty] | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-118 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 288 | [5 empty] | ER | WFEC | Dover Switchyard 138 kV Line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-119 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 600 | [5 empty] | ER | OKGE | Spring Creek-Sooner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-126 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 172.5 | [5 empty] | ER/NR | OKGE | Arbuckle 138kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-128 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 176 | [5 empty] | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-131 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 2.5 | [5 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-132 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 6.12 | [5 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-133 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [5 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-134 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [5 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-137 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [5 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-138 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [5 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-139 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [5 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-141 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [5 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-142 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [5 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-145 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [5 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-146 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [5 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-167 | 04 SOUTHEAST | 17 | DIS-16-2 | Solar | 73.5 | [5 empty] | ER/NR | AEPW | Lieberman - North Benton 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-010 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 90 | [5 empty] | ER | SPS | TEXAS_CNTY 3 | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-121 | 05 SOUTHWEST | 17 | DIS-16-2 | Solar | 110 | [5 empty] | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-177 | 05 SOUTHWEST | 17 | DIS-16-2 | Gas Turbine | 17 | [5 empty] | ER | SPS | XTO-Cornell 115 kV station | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2017-006GIA-53 | 03 CENTRAL | 16.5 | DIS-16-2-PQ | Wind | 238 | [5 empty] | ER/NR | AECI | 5MARYVL
GEN-2016-004 | 01 NORTH | 16 | DIS-16-1 | Wind | 202 | [5 empty] | ER/NR | WAPA | Basin Electric 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-007 | 01 NORTH | 16 | DIS-16-1 | Wind | 100.05 | [5 empty] | ER | WAPA | Valley City 115 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-021 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 298.47 | [5 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-043 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 230 | [5 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-050 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 250.7 | [5 empty] | ER | NPPD | Axtell â€“ Post Rock 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-075 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 50 | [5 empty] | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-009 | 03 CENTRAL | 16 | DIS-16-1 | Steam Turbine | 29 | [5 empty] | ER | OKGE | Osage 69 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-016 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 78.2 | [5 empty] | ER | MIDW | North Kinsley 115 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-046 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 299 | [5 empty] | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-036 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 303.6 | [5 empty] | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-003 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250.4 | [5 empty] | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-020 | 04 SOUTHEAST | 16 | DIS-16-1 | WIND | 148.4 | [5 empty] | ER | WFEC | Moreland 138kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-030 | 04 SOUTHEAST | 16 | DIS-16-1 | Solar | 100 | [5 empty] | ER/NR | OKGE | Brown 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-031 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 1.5 | [5 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [5 empty] | ER/NR | OKGE | Crescent Substation 138 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-045 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [5 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-051 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 9.8 | [5 empty] | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-057 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [5 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-061 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250.7 | [5 empty] | ER | OKGE | Sooner-Woodring 345 kV line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-071 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200.1 | [5 empty] | ER | OKGE | Middleton Tap 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-004 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 10 | [5 empty] | ER | SPS | Palo Duro 115kV
GEN-2015-082 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 200 | [5 empty] | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-070 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 5.3 | [5 empty] | ER | SPS | Martin 115 kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-088 | 02 NEBRASKA | 15 | DIS-15-2 | Wind | 300 | [5 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-052 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 300 | [5 empty] | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-069 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 300 | [5 empty] | ER | WERE | Union Ridge 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-090 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 220 | [5 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-045 | 04 SOUTHEAST | 15 | DIS-15-2 | Storage | 20 | [5 empty] | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-047 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 300 | [5 empty] | ER | OKGE | Sooner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 200 | [5 empty] | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-062 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 4.5 | [5 empty] | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-063 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 300 | [5 empty] | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-066 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 248.4 | [5 empty] | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-005NWE205 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.2 | [5 empty] | ER | WAPA | Tap White Lake - Stickeny 69kV
ASGI-2016-007NWE208 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.2 | [5 empty] | ER | WAPA | Kimball 69kV
GEN-2005-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 | [5 empty] | ER/NR | WAPA | Hilken 230kV [Ecklund 230kV]
GEN-2006-002IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 2 | [5 empty] | ER/NR | WAPA | Wessington Springs 230kV
GEN-2006-006IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 10 | [5 empty] | ER/NR | XEL | Marshall 115kV
GEN-2006-015IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 | [5 empty] | ER/NR | WAPA | Hilken 230kV [Ecklund 230kV]
GEN-2008-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 5 | [5 empty] | ER/NR | WAPA | Nelson 115kV
GEN-2009-018IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 | [5 empty] | ER | WAPA | Groton 115kV
GEN-2009-020AIS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.4 | [5 empty] | ER/NR | WAPA | Tripp Junction 115kV
GEN-2009-026IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 3.5 | [5 empty] | ER/NR | WAPA | Dickenson-Heskett 230kV
GEN-2014-006IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Gas | 11.72 | [5 empty] | ER/NR | BEPC | Williston 115kV
MPC02100 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 99.25 | [5 empty] | ER | OTP | Center - Mandan 230 kV
GEN-2015-023 | 02 NEBRASKA | 14 | DIS-15-1 | Wind | 300.7 | [5 empty] | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2015-001 | 03 CENTRAL | 14 | DIS-15-1 | Thermal | 6.13 | [5 empty] | ER | SUNC | Ninnescah 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-005 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 200.1 | [5 empty] | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-024 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 220 | [5 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-025 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 220 | [5 empty] | ER | WERE | Tap Thistle â€“ Wichita 345kV Dbl CKT | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 04 SOUTHEAST | 14 | DIS-15-1 | Solar | 120 | [5 empty] | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-032 | 02 NEBRASKA | 13 | DIS-14-2 | Wind | 10.22 | [5 empty] | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-025 | 03 CENTRAL | 13 | DIS-14-2 | Wind | 2.42 | [5 empty] | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-056 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 250 | [5 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-064 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 248.4 | [5 empty] | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-035 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 30 | [5 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-040 | 05 SOUTHWEST | 13 | DIS-14-2 | Wind | 320 | [5 empty] | ER | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-004 | 02 NEBRASKA | 12 | DIS-14-1 | Wind | 4 | [5 empty] | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-013 | 02 NEBRASKA | 12 | DIS-14-1 | Wind | 73.5 | [5 empty] | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-001 | 03 CENTRAL | 12 | DIS-14-1 | Wind | 200.6 | [5 empty] | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-002 | 04 SOUTHEAST | 12 | DIS-14-1 | Wind | 10.5 | [5 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 04 SOUTHEAST | 12 | DIS-14-1 | Wind | 5.7 | [5 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-019 | 02 NEBRASKA | 11 | DIS-13-2 | Wind | 73.6 | [5 empty] | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2013-005 | 05 SOUTHWEST | 11 | DIS-13-2 | Wind | 1.65 | [5 empty] | ER | SPS | FE Clovis 115kV
GEN-2013-002 | 02 NEBRASKA | 10 | DIS-13-1 | Wind | 50.6 | [5 empty] | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-008 | 02 NEBRASKA | 10 | DIS-13-1 | Wind | 1.2 | [5 empty] | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-002 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 18.4 | [5 empty] | ER | SPS | FE Tucumcari 115kV
ASGI-2013-003 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 18.4 | [5 empty] | ER | SPS | FE Clovis 115kV
GEN-2012-024 | 03 CENTRAL | 9 | DIS-12-2 | Wind | 180 | [5 empty] | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-033 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 98.82 | [5 empty] | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-002 | 05 SOUTHWEST | 9 | DIS-12-2 | Wind | 18.15 | [5 empty] | ER | SPS | FE-Clovis Interchange 115kV
GEN-2003-021N | 02 NEBRASKA | 8 | PQ | Wind | 75 | [5 empty] | ER | NPPD | Ainsworth Wind Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
NPPDBUFFALOCOUNTYSOLAR | 02 NEBRASKA | 8 | PQ | Solar | 10 | [5 empty] | ER | NPPD | Kearney Northeast
NPPDBURTCOUNTYWIND | 02 NEBRASKA | 8 | PQ | Wind | 20 | [5 empty] | ER | NPPD | Tekamah & Oakland 115kV
ASGI-2012-006 | 03 CENTRAL | 8 | DIS-12-1 | Steam | 21.25 | [5 empty] | ER | SUNC | Tap Hugoton - Rolla 69kV
GEN-2001-039M | 03 CENTRAL | 8 | PQ | Wind | 100 | [5 empty] | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-004 | 03 CENTRAL | 8 | PQ | Wind | 153 | [5 empty] | ER | WERE | Latham 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | 03 CENTRAL | 8 | PQ | Wind | 201 | [5 empty] | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-006GIA-27 | 04 SOUTHEAST | 8 | PQ | Wind | 150 | [5 empty] | ER | AECI | Remington 138kV
GEN-2006-002 | 04 SOUTHEAST | 8 | PQ | Wind | 100.8 | [5 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-004 | 04 SOUTHEAST | 8 | DIS-12-1 | Wind | 40.8 | [5 empty] | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | 05 SOUTHWEST | 8 | PQ | Wind | 370 | [5 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-037 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 6.6 | [5 empty] | ER | WFEC | Blue Canyon 5 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-054 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 300 | [5 empty] | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 175 | [5 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 165.6 | [5 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-022 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 299 | [5 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-040 | 04 SOUTHEAST | 5 | DIS-10-2 | Wind | 300 | [5 empty] | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-001 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 300 | [5 empty] | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-005 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 299.2 | [5 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-022 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 299.65 | [5 empty] | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-047 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 263.13 | [5 empty] | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-014 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 358.8 | [5 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | 02 NEBRASKA | 3 | DIS-09-1 | Wind | 201 | [5 empty] | ER | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-124 | 03 CENTRAL | 3 | DIS-09-1 | Wind | 200.1 | [5 empty] | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-051 | 05 SOUTHWEST | 3 | DIS-09-1 | Wind | 161 | [5 empty] | ER | SPS | Potter County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-025 | 03 CENTRAL | 2 | ICS1 | Wind | 68.8 | [5 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-093 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 250 | [5 empty] | ER | OKGE | Gracemont 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2007-044 | 04 SOUTHEAST | 2 | ICS1 | Wind | 299.2 | [5 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION

## Seasonal LOIS
Generation Interconnection Number or Upgrade ID | Assigned Study | Service Type | Point of Interconnection or Upgrade Name | MW Amount | Season | LOIS Granted | Limiting Element | Limiting Upgrade | ERIS 23SP | ERIS 26SP | ERIS 26L | ERIS 26WP | NRIS 23SP | NRIS 26SP | NRIS 26L | NRIS 26WP | Stability 25SP | Stability 25WP
GEN-2016-037 | DISIS-2017-001 | ERIS | Chisholm-Gracemont 345kV | 300 | April 1 - May 31 | 300 | None | None | N/A | N/A | 300 | N/A | N/A | N/A | N/A | N/A | 300 | 300
GEN-2016-037 | DISIS-2017-001 | ERIS | Chisholm-Gracemont 345kV | 300 | June 1 - Sept 30 | 300 | None | None | 300 | 300 | N/A | N/A | N/A | N/A | N/A | N/A | 300 | N/A
GEN-2016-037 | DISIS-2017-001 | ERIS | Chisholm-Gracemont 345kV | 300 | Oct 1 - Nov 30 | 300 | None | None | N/A | N/A | 300 | N/A | N/A | N/A | N/A | N/A | 300 | 300
GEN-2016-037 | DISIS-2017-001 | ERIS | Chisholm-Gracemont 345kV | 300 | Dec 1 - March 31 | 300 | None | None | N/A | N/A | N/A | 300 | N/A | N/A | N/A | N/A | N/A | 300

## Constraints Summary
Group | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name
04ALL | ERIS | Voltage | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
04ALL | ERIS | Thermal | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
04ALL | ERIS | Stability | None | 25SP, 25WP | None | [7 empty] | None
04ALL | ERIS | Non-Converge | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None

## All Thermal
SOLUTIONTYPE | GROUP | SCENARIO | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME | Constraint Violation Criteria | Upgrade Name
Non-Converge | 04ALL | 0 | 26L | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | 04ALL | 0 | 26SP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | 04ALL | 0 | 26WP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | 04ALL | 0 | 23SP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Thermal | 04ALL | 1 | 26L | N/A | " | None |  |  |  |  | None |  | None
Thermal | 04ALL | 1 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | 04ALL | 1 | 26WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | 04ALL | 1 | 23SP | N/A | " | None |  |  |  |  | None |  | None

## All Voltage
SOLUTIONTYPE | GROUP | SCENARIO | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME | Upgrade Name
Voltage | 04ALL | 2 | 23SP | N/A | None | [7 empty] | None | None
Voltage | 04ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | 04ALL | 2 | 26WP | N/A | None | [7 empty] | None | None
Voltage | 04ALL | 2 | 26L | N/A | None | [7 empty] | None | None

## Stability Analysis Results
Group | Season | Model Dispatch | Event ID | Event Description | Event Category | Rotor Angle Stability | Transient Voltage Response > 0.7 p.u. | Transient Voltage Response < 1.2 p.u. | Post Fault Steady State Voltage > 0.9 p.u. | Post Fault Steady State Voltage < 1.1 p.u. | Damping Factor > 0.8 % | Low Voltage Rides Through | Violation Summary | Primary Mitigation | Alternate Mitigation | Alternate Mitigation2 (Informational)
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_001 | 3 Phase fault on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 (511458) 138.0 kV to REDHLSW4 (521116) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_002 | 3 Phase fault on S.W.S.-4 138.00 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 138.00 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 (511477) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_003 | 3 Phase fault on S.W.S.-4 138.00 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 138.00 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 (511477) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_004 | 3 Phase fault on RPPAPER4 138.00 (511512) 138 kV Bus a. Apply fault at the RPPAPER4 138.00 (511512) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 112GORE4 (511488) 138.0 kV to RPPAPER4 (511512) 138.0 kV Transmission Circuit #1 b.2. LWSTAP 4 (511439) 138.0 kV to L.E.S.-4 (511467) 138.0 kV Transmission Circuit #1 b.3. LWSTAP 4 (511439) 138.0 kV to RPPAPER4 (511512) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_005 | 3 Phase fault on COMANC-4 138.00 (511437) 138 kV Bus a. Apply fault at the COMANC-4 138.00 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 (511437) 138.0 kV to L.E.S.-4 (511467) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_006 | 3 Phase fault on COMMTAP4 138.00 (511494) 138 kV Bus a. Apply fault at the COMMTAP4 138.00 (511494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 (511467) 138.0 kV to COMMTAP4 (511494) 138.0 kV Transmission Circuit #1 b.2. DUNCAN-4 (511453) 138.0 kV to OMDUNCN4 (529304) 138.0 kV Transmission Circuit #1 b.3. COMMTAP4 (511494) 138.0 kV to OMDUNCN4 (529304) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_007 | 3 Phase fault on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_008 | 3 Phase fault on CL-AFTP4 138.00 (511446) 138 kV Bus a. Apply fault at the CL-AFTP4 138.00 (511446) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-AFTP4 (511446) 138.0 kV to HOB-JCT4 (511463) 138.0 kV Transmission Circuit #1 b.2. CL-AFTP4 (511446) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_009 | 3 Phase fault on L.E.S.-4 138.00 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 138.00 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 (511467) 138.0 kV to SHERID4 (511474) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_010 | 3 Phase fault on FALCNRD4 138.00 (511511) 138 kV Bus a. Apply fault at the FALCNRD4 138.00 (511511) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 (511458) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 b.2. SAYRE--4 (511504) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 b.3. SAYRE--4 (511504) 138.0 kV to ERICK 4 (520903) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_011 | 3 Phase fault on SWEETWT6 230.00 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 230.00 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 (511541) 230.0 kV to BUFFCK6 (511542) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_012 | 3 Phase fault on SWEETWT6 230.00 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 230.00 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 (511541) 230.0 kV to DEMPSEY6 (511544) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_013 | 3 Phase fault on SWEETWT6 230.00 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 230.00 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 (511541) 230.0 kV to ROARK6 (511547) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_014 | 3 Phase fault on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 (511568) 345.0 kV to SUNNYSD7 (515136) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips GEN-2015-045 (584862). | Protection disabled without any impact on stability.
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_015 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_016 | 3 Phase fault on ELKCITY6 230.00 (511490) 230 kV Bus a. Apply fault at the ELKCITY6 230.00 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 (511458) 138.0 kV to ELKCITY6 (511490) 230.0 kV to ELKC2-1 (511482) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_017 | 3 Phase fault on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_018 | 3 Phase fault on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#5-1 (511411) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_019 | 3 Phase fault on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-2 (511459) 69.0 kV to ELKCTY-4 (511458) 138.0 kV to ELKC4-1 (511493) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_020 | 3 Phase fault on L.E.S.-4 138.00 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 138.00 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 (511466) 69.0 kV to L.E.S.-4 (511467) 138.0 kV to LES#1-1 (511416) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_021 | 3 Phase fault on L.E.S.-4 138.00 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 138.00 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 (511466) 69.0 kV to L.E.S.-4 (511467) 138.0 kV to LES#2-1 (511415) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_022 | 3 Phase fault on BUFFCK6 230.00 (511542) 230 kV Bus a. Apply fault at the BUFFCK6 230.00 (511542) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUFFCK6 (511542) 230.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_023 | 3 Phase fault on FLE TAP4 138.00 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 138.00 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 (511423) 138.0 kV to G16-097-TAP (587794) 138.0 kV Transmission Circuit #1 b.2. FLE TAP4 (511423) 138.0 kV to L.E.S.-4 (511467) 138.0 kV Transmission Circuit #1 b.3. L.E.S.-4 (511467) 138.0 kV to ELGINJT4 (511486) 138.0 kV Transmission Circuit #1 b.4. ELGINJT4 (511486) 138.0 kV to ELSWORTH 4 (511563) 138.0 kV Transmission Circuit #1 b.5. S.W.S.-4 (511477) 138.0 kV to ELSWORTH 4 (511563) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_024 | 3 Phase fault on KGFSHSW4 138.00 (520533) 138 kV Bus a. Apply fault at the KGFSHSW4 138.00 (520533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVJCTN2 (520508) 69.0 kV to ANADARK2 (520810) 69.0 kV Transmission Circuit #1 b.2. CLVJCTN2 (520508) 69.0 kV to ANADARK4 (520814) 138.0 kV Two Winding #1 b.3. CLVJCTN2 (520508) 69.0 kV to COGAR 2 (520859) 69.0 kV Transmission Circuit #1 b.4. CANA 2 (520502) 69.0 kV to ELRENOJ2 (520899) 69.0 kV Transmission Circuit #1 b.5. EL RENO2 (520892) 69.0 kV to ELRENOJ2 (520899) 69.0 kV Transmission Circuit #1 b.6. EL RENO4 (520893) 138.0 kV to ELRENOJ2 (520899) 69.0 kV Two Winding #1 b.7. CANA 2 (520502) 69.0 kV to CALUMET2 (520839) 69.0 kV Transmission Circuit #1 b.8. WATNGSW4 (520536) 138.0 kV to CALUMET2 (520839) 69.0 kV Two Winding #1 b.9. CALUMET2 (520839) 69.0 kV to CONCHO 2 (520865) 69.0 kV Transmission Circuit #1 b.10. CALUMET2 (520839) 69.0 kV to WATNGSW2 (521090) 69.0 kV Transmission Circuit #1 b.11. KGFSHSW4 (520533) 138.0 kV to CONCHO 2 (520865) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_025 | 3 Phase fault on STLN-DEMARC6230.00 (523779) 230 kV Bus a. Apply fault at the STLN-DEMARC6230.00 (523779) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 (511541) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.2. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_026 | 3 Phase fault on ELKCITY6 230.00 (511490) 230 kV Bus a. Apply fault at the ELKCITY6 230.00 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCITY6 (511490) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_027 | 3 Phase fault on SWEETWT6 230.00 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 230.00 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 (511541) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_028 | 3 Phase fault on MNCWND47 345.00 (515939) 345 kV Bus a. Apply fault at the MNCWND47 345.00 (515939) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MNCWND47 (515939) 345.0 kV to MNCWND57 (515980) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_029 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV to TOLK_TR 1 (525537) 13.2 kV Three Winding #1 b.4. TOLK 7 (525549) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of Harrington (523972, 523973) and Tolk (525561, 525562) units. | Operational measures fixing the voltage setpoint of Hobbs PLT3 (527903).
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_030 | 3 Phase fault on LAMB_CNTY 6230.00 (525637) 230 kV Bus a. Apply fault at the LAMB_CNTY 6230.00 (525637) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 (525531) 230.0 kV to LAMB_CNTY 6 (525637) 230.0 kV Transmission Circuit #1 b.2. LAMB_CNTY 6 (525637) 230.0 kV to LAMB_CNTY 3 (525636) 115.0 kV to LAMB_TR3 1 (525633) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_031 | 3 Phase fault on PRINGLE 6230.00 (523267) 230 kV Bus a. Apply fault at the PRINGLE 6230.00 (523267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRINGLE 6 (523267) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 b.2. PRINGLE 6 (523267) 230.0 kV to PRINGLE 3 (523266) 115.0 kV to PRINGLE_TR 1 (523265) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_032 | 3 Phase fault on OCHILTREE 6230.00 (523155) 230 kV Bus a. Apply fault at the OCHILTREE 6230.00 (523155) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OCHILTREE 6 (523155) 230.0 kV to OCHILTREE 3 (523154) 115.0 kV to OCHLTRE_TR11 (523151) 13.2 kV Three Winding #1 b.4. HITCHLAND 6 (523095) 230.0 kV to OCHILTREE 6 (523155) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_033 | 3 Phase fault on XIT_INTG 6230.00 (523221) 230 kV Bus a. Apply fault at the XIT_INTG 6230.00 (523221) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. XIT_INTG 6 (523221) 230.0 kV to XIT_INTG 3 (523220) 115.0 kV to XIT_INTG TR1 (523219) 13.2 kV Three Winding #1 b.4. XIT_INTG 6 (523221) 230.0 kV to CHAN+TASCOS6 (523869) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_034 | 3 Phase fault on ANADARK4 138.00 (520814) 138 kV Bus a. Apply fault at the ANADARK4 138.00 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 (520814) 138.0 kV to CHERRYRD 4 (521129) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_035 | 3 Phase fault on ANADARK4 138.00 (520814) 138 kV Bus a. Apply fault at the ANADARK4 138.00 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVJCTN2 (520508) 69.0 kV to ANADARK4 (520814) 138.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_036 | 3 Phase fault on FLETCH-4 138.00 (520912) 138 kV Bus a. Apply fault at the FLETCH-4 138.00 (520912) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 (520814) 138.0 kV to GEORGIA4 (520923) 138.0 kV Transmission Circuit #1 b.2. COMANCH4 (520864) 138.0 kV to EMPIRE 4 (520900) 138.0 kV Transmission Circuit #1 b.3. EMPIRE 4 (520900) 138.0 kV to FLETCH-4 (520912) 138.0 kV Transmission Circuit #1 b.4. FLETCH-4 (520912) 138.0 kV to GEORGIA4 (520923) 138.0 kV Transmission Circuit #1 b.5. FLETCH-4 (520912) 138.0 kV to FLETCHR2 (520911) 69.0 kV to FLCHTERT (521168) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_037 | 3 Phase fault on ANADARK4 138.00 (520814) 138 kV Bus a. Apply fault at the ANADARK4 138.00 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 (520814) 138.0 kV to POCASET4 (521031) 138.0 kV Transmission Circuit #1 b.2. BRIDGCR4 (520501) 138.0 kV to SUNSHIN4 (521059) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_038 | 3 Phase fault on SEQUOYAHJ4 138.00 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 138.00 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 (520422) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 b.2. NAPLSTP4 (520510) 138.0 kV to PAYNESW4 (520888) 138.0 kV Transmission Circuit #1 b.3. CORNVIL4 (511449) 138.0 kV to CORN TP4 (520867) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_039 | 3 Phase fault on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_040 | 3 Phase fault on S.W.S.-4 138.00 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 138.00 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 (511477) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_041 | 3 Phase fault on ERICK 4 138.00 (520903) 138 kV Bus a. Apply fault at the ERICK 4 138.00 (520903) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAYRE--4 (511504) 138.0 kV to ERICK 4 (520903) 138.0 kV Transmission Circuit #1 b.2. BULOJ4 (520402) 138.0 kV to ERICK 4 (520903) 138.0 kV Transmission Circuit #1 b.3. ELKCTY-4 (511458) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_042 | 3 Phase fault on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 (511458) 138.0 kV to REDHLSW4 (521116) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_043 | 3 Phase fault on SLKHILLS 4 138.00 (521103) 138 kV Bus a. Apply fault at the SLKHILLS 4 138.00 (521103) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BC SW 4 (520512) 138.0 kV to SLKHILLS 4 (521103) 138.0 kV Transmission Circuit #1 b.2. BCVI_HVB (520514) 138.0 kV to SLKHILLS 4 (521103) 138.0 kV Transmission Circuit #1 b.3. WASHITA4 (521089) 138.0 kV to SLKHILLS 4 (521103) 138.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_044 | 3 Phase fault on ONEY 4 138.00 (521017) 138 kV Bus a. Apply fault at the ONEY 4 138.00 (521017) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONEY 4 (521017) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.2. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_045 | 3 Phase fault on S.W.S.-4 138.00 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 138.00 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 (511477) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_046 | 3 Phase fault on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_047 | 3 Phase fault on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_048 | 3 Phase fault on JOHNCO 7 345.00 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 345.00 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 (514809) 345.0 kV to SUNNYSD7 (515136) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_049 | 3 Phase fault on MINCO 7 345.00 (514801) 345 kV Bus a. Apply fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency Relay trips MINCO-WTG (515551, 599117, 599120) and MNCOWNG (515438, 515445, 515907). | Protection disabled without any impact on stability.
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_050 | 3 Phase fault on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 (511568) 345.0 kV to SUNNYSD7 (515136) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips GEN-2015-045 (584862). | Protection disabled without any impact on stability.
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_051 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_052 | 3 Phase fault on FSHRTAP7 345.00 (515610) 345 kV Bus a. Apply fault at the FSHRTAP7 345.00 (515610) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to FSHRTAP7 (515610) 345.0 kV Transmission Circuit #1 b.2. KNGFSHR7 (515600) 345.0 kV to FSHRTAP7 (515610) 345.0 kV Transmission Circuit #1 b.3. CANADN7 (515605) 345.0 kV to FSHRTAP7 (515610) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_053 | 3 Phase fault on MCCLAIN4 138.00 (514902) 138 kV Bus a. Apply fault at the MCCLAIN4 138.00 (514902) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCLAIN4 (514902) 138.0 kV to PLVALLY4 (514929) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_054 | 3 Phase fault on TURNER 4 138.00 (514992) 138 kV Bus a. Apply fault at the TURNER 4 138.00 (514992) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOGATE 4 (514928) 138.0 kV to TURNER 4 (514992) 138.0 kV Transmission Circuit #1 b.2. PLVALLY4 (514929) 138.0 kV to TURNER 4 (514992) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_055 | 3 Phase fault on PLVALLY4 138.00 (514929) 138 kV Bus a. Apply fault at the PLVALLY4 138.00 (514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLVALLY4 (514929) 138.0 kV to HOLLYWD4 (514953) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_056 | 3 Phase fault on CHERYCK4 138.00 (514957) 138 kV Bus a. Apply fault at the CHERYCK4 138.00 (514957) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLVALLY4 (514929) 138.0 kV to CHERYCK4 (514957) 138.0 kV Transmission Circuit #1 b.2. CHERYCK4 (514957) 138.0 kV to BOYD 4 (514958) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_057 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_058 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_059 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_060 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). The issue was also observed in the base case. | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_061 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). The issue was also observed in the base case. | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_062 | 3 Phase fault on MINCO 7 345.00 (514801) 345 kV Bus a. Apply fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to MCNOWND7 (515444) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_063 | 3 Phase fault on MINCO 7 345.00 (514801) 345 kV Bus a. Apply fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_064 | 3 Phase fault on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_065 | 3 Phase fault on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_066 | 3 Phase fault on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_067 | 3 Phase fault on MINCO 7 345.00 (514801) 345 kV Bus a. Apply fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to MNCWND37 (515549) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_068 | 3 Phase fault on MNCWND37 345.00 (515549) 345 kV Bus a. Apply fault at the MNCWND37 345.00 (515549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MNCWND37 (515549) 345.0 kV to MNCWND47 (515939) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_069 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_070 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_071 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_072 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_073 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_074 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_075 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). The issue was also observed in the base case. | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_076 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). The issue was also observed in the base case. | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_077 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_078 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to GUTHRIE7 (515961) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). The issue was also observed in the base case. | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_079 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO11 (515714) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_080 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_081 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER31 (515720) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_082 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER41 (515721) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_083 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER21 (515792) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_084 | 3 Phase fault on SUNNYSD7 345.00 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 345.00 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD4 (515135) 138.0 kV to SUNNYSD7 (515136) 345.0 kV to SUNNYSD1 (515762) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_085 | 3 Phase fault on SUNNYSD7 345.00 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 345.00 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 (515136) 345.0 kV to SUNNYSD4 (515135) 138.0 kV to SUNYSD 1 (515405) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_086 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV31 (515795) 13.8 kV Three Winding #1 | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). The issue was also observed in the base case. | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_087 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). The issue was also observed in the base case. | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_088 | 3 Phase fault on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to GRACMNT7 (515800) 345.0 kV to GRCMNT11 (515801) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_089 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_090 | 3 Phase fault on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_091 | 3 Phase fault on FLE TAP4 138.00 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 138.00 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 (511423) 138.0 kV to G16-097-TAP (587794) 138.0 kV Transmission Circuit #1 b.2. FLE TAP4 (511423) 138.0 kV to L.E.S.-4 (511467) 138.0 kV Transmission Circuit #1 b.3. L.E.S.-4 (511467) 138.0 kV to ELGINJT4 (511486) 138.0 kV Transmission Circuit #1 b.4. ELGINJT4 (511486) 138.0 kV to ELSWORTH 4 (511563) 138.0 kV Transmission Circuit #1 b.5. S.W.S.-4 (511477) 138.0 kV to ELSWORTH 4 (511563) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_092 | 3 Phase fault on S.W.S.-4 138.00 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 138.00 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 (511477) 138.0 kV to G16-097-TAP (587794) 138.0 kV Transmission Circuit #1 b.2. FLE TAP4 (511423) 138.0 kV to L.E.S.-4 (511467) 138.0 kV Transmission Circuit #1 b.3. L.E.S.-4 (511467) 138.0 kV to ELGINJT4 (511486) 138.0 kV Transmission Circuit #1 b.4. ELGINJT4 (511486) 138.0 kV to ELSWORTH 4 (511563) 138.0 kV Transmission Circuit #1 b.5. S.W.S.-4 (511477) 138.0 kV to ELSWORTH 4 (511563) 138.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_093 | 3 Phase fault on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 (511468) 345.0 kV to G16-091-TAP (587744) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_094 | 3 Phase fault on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 (515800) 345.0 kV to G16-091-TAP (587744) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_095 | 3 Phase fault on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 (511468) 345.0 kV to G16-091-TAP (587744) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_096 | 3 Phase fault on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 (515800) 345.0 kV to G16-091-TAP (587744) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_097 | 3 Phase fault on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_098 | 3 Phase fault on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 (511568) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Protection disabled without any impact on stability.
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_099 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV to G16-037-TAP (560078) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_100 | 3 Phase fault on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 (515800) 345.0 kV to G16-037-TAP (560078) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_101 | 3 Phase fault on SUNNYSD7 345.00 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 345.00 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 (515136) 345.0 kV to G16-063-TAP (560088) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_102 | 3 Phase fault on FLE TAP4 138.00 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 138.00 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 (511423) 138.0 kV to L.E.S.-4 (511467) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_103 | 3 Phase fault on LWSTAP 4 138.00 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 138.00 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 (511439) 138.0 kV to L.E.S.-4 (511467) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_104 | 3 Phase fault on CL-AFTP4 138.00 (511446) 138 kV Bus a. Apply fault at the CL-AFTP4 138.00 (511446) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-AFTP4 (511446) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_105 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_106 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-092-TAP (763215) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_107 | 3 Phase fault on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 (511458) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_108 | 3 Phase fault on L.E.S.-4 138.00 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 138.00 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 (511467) 138.0 kV to ELGINJT4 (511486) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_109 | 3 Phase fault on L.E.S.-4 138.00 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 138.00 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 (511467) 138.0 kV to COMMTAP4 (511494) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_110 | 3 Phase fault on SWEETWT6 230.00 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 230.00 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 (511541) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_111 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV to GRAPEVINE (560035) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_112 | 3 Phase fault on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 (511568) 345.0 kV to RUSHSPR7 (511571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_113 | 3 Phase fault on MINCO 7 345.00 (514801) 345 kV Bus a. Apply fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to NSUB345 (555234) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_114 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to FSHRTAP7 (515610) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_115 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to NSUB345 (555234) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_116 | 3 Phase fault on PLVALLY4 138.00 (514929) 138 kV Bus a. Apply fault at the PLVALLY4 138.00 (514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLVALLY4 (514929) 138.0 kV to CHERYCK4 (514957) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_117 | 3 Phase fault on PLVALLY4 138.00 (514929) 138 kV Bus a. Apply fault at the PLVALLY4 138.00 (514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLVALLY4 (514929) 138.0 kV to TURNER 4 (514992) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_118 | 3 Phase fault on PLVALLY4 138.00 (514929) 138 kV Bus a. Apply fault at the PLVALLY4 138.00 (514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLVALLY4 (514929) 138.0 kV to G17-152_TAP (914902) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_119 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to NSUB345 (555234) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_120 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to NSUB345 (555234) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_121 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BVRCNTY7 (515554) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). The issue was also observed in the base case. | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_122 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). The issue was also observed in the base case. | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_123 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). The issue was also observed in the base case. | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_124 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). The issue was also observed in the base case. | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_125 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to CRAWFISH_DR (560022) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_126 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_127 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_128 | 3 Phase fault on SEQUOYAHJ4 138.00 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 138.00 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 (520422) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_129 | 3 Phase fault on ANADARK4 138.00 (520814) 138 kV Bus a. Apply fault at the ANADARK4 138.00 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 (520814) 138.0 kV to GEORGIA4 (520923) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_130 | 3 Phase fault on ANADARK4 138.00 (520814) 138 kV Bus a. Apply fault at the ANADARK4 138.00 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 (520814) 138.0 kV to POCASET4 (521031) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_131 | 3 Phase fault on ONEY 4 138.00 (521017) 138 kV Bus a. Apply fault at the ONEY 4 138.00 (521017) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONEY 4 (521017) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_132 | 3 Phase fault on WASHITA4 138.00 (521089) 138 kV Bus a. Apply fault at the WASHITA4 138.00 (521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHITA4 (521089) 138.0 kV to SLKHILLS 4 (521103) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_133 | 3 Phase fault on HITCHLAND 6230.00 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6230.00 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to OCHILTREE 6 (523155) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_134 | 3 Phase fault on HITCHLAND 6230.00 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6230.00 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to MOORE_CNTY 6 (523309) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_135 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 7 (523101) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_136 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to NOVUS1 7 (523112) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_137 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_138 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_139 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to G10014G11022 (576397) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_140 | 3 Phase fault on XIT_INTG 6230.00 (523221) 230 kV Bus a. Apply fault at the XIT_INTG 6230.00 (523221) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. XIT_INTG 6 (523221) 230.0 kV to CHAN+TASCOS6 (523869) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_141 | 3 Phase fault on PRINGLE 6230.00 (523267) 230 kV Bus a. Apply fault at the PRINGLE 6230.00 (523267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRINGLE 6 (523267) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_142 | 3 Phase fault on MOORE_CNTY 6230.00 (523309) 230 kV Bus a. Apply fault at the MOORE_CNTY 6230.00 (523309) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE_CNTY 6 (523309) 230.0 kV to MCDWL_CREEK6 (523323) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_143 | 3 Phase fault on MCDWL_CREEK6230.00 (523323) 230 kV Bus a. Apply fault at the MCDWL_CREEK6230.00 (523323) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDWL_CREEK6 (523323) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_144 | 3 Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_145 | 3 Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_146 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_147 | 3 Phase fault on CHAN+TASCOS6230.00 (523869) 230 kV Bus a. Apply fault at the CHAN+TASCOS6230.00 (523869) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAN+TASCOS6 (523869) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_148 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_149 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_150 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to BUSHLAND 6 (524267) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_151 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_152 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to SPNSPUR_WND7 (524296) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_153 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_154 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to GRAPEVINE (560035) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_155 | 3 Phase fault on HARRNG_WST 6230.00 (523977) 230 kV Bus a. Apply fault at the HARRNG_WST 6230.00 (523977) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_156 | 3 Phase fault on BUSHLAND 6230.00 (524267) 230 kV Bus a. Apply fault at the BUSHLAND 6230.00 (524267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUSHLAND 6 (524267) 230.0 kV to WILDOR2_JUS6 (524290) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_157 | 3 Phase fault on BUSHLAND 6230.00 (524267) 230 kV Bus a. Apply fault at the BUSHLAND 6230.00 (524267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUSHLAND 6 (524267) 230.0 kV to DEAFSMITH 6 (524623) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_158 | 3 Phase fault on SPNSPUR_WND7345.00 (524296) 345 kV Bus a. Apply fault at the SPNSPUR_WND7345.00 (524296) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPNSPUR_WND7 (524296) 345.0 kV to SPNSPUR_COL7 (524299) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_159 | 3 Phase fault on ROOSEVELT 6230.00 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6230.00 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 (524909) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_160 | 3 Phase fault on ROOSEVELT 6230.00 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6230.00 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 (524909) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_161 | 3 Phase fault on SWISHER 6230.00 (525213) 230 kV Bus a. Apply fault at the SWISHER 6230.00 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 (525213) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_162 | 3 Phase fault on NEWHART 6230.00 (525461) 230 kV Bus a. Apply fault at the NEWHART 6230.00 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 (525461) 230.0 kV to PLANT_X 6 (525481) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_163 | 3 Phase fault on PLANT_X 6230.00 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6230.00 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 (525481) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_164 | 3 Phase fault on PLANT_X 6230.00 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6230.00 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 (525481) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_165 | 3 Phase fault on TOLK 6230.00 (525531) 230 kV Bus a. Apply fault at the TOLK 6230.00 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 (525531) 230.0 kV to NEEDMORE 6 (525586) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_166 | 3 Phase fault on TOLK 6230.00 (525531) 230 kV Bus a. Apply fault at the TOLK 6230.00 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 (525531) 230.0 kV to LAMB_CNTY 6 (525637) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_167 | 3 Phase fault on TOLK 6230.00 (525531) 230 kV Bus a. Apply fault at the TOLK 6230.00 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 (525531) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of Harrington (523972, 523973) and Tolk (525561, 525562) units. | Operational measures fixing the voltage setpoint of Hobbs PLT3 (527903).
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_168 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the reactive power outputs of Tolk (525561, 525562) units. | Operational measures fixing the voltage setpoint of Hobbs PLT3 (527903).
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_169 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to CRAWFISH_DR (560022) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_170 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to CRAWFISH_DR (560022) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_171 | 3 Phase fault on SAGA_SCOL 7345.00 (527610) 345 kV Bus a. Apply fault at the SAGA_SCOL 7345.00 (527610) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SAGA_SCOL 7 (527610) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of Harrington (523972, 523973) and Tolk (525561, 525562) units. | Operational measures fixing the voltage setpoint of Hobbs PLT3 (527903).
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_172 | 3 Phase fault on RSVLT_CC_E 7345.00 (527655) 345 kV Bus a. Apply fault at the RSVLT_CC_E 7345.00 (527655) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSVLT_CC_E 7 (527655) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of Harrington (523972, 523973) and Tolk (525561, 525562) units. | Operational measures fixing the voltage setpoint of Hobbs PLT3 (527903).
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_173 | 3 Phase fault on CROSSROADS 7345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7345.00 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 (527656) 345.0 kV to EDDY_CNTY 7 (527802) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of Harrington (523972, 523973) and Tolk (525561, 525562) units. | Operational measures fixing the voltage setpoint of Hobbs PLT3 (527903).
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_174 | 3 Phase fault on CROSSROADS 7345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7345.00 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 (527656) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #ba c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of Harrington (523972, 523973) and Tolk (525561, 525562) units. | Operational measures fixing the voltage setpoint of Hobbs PLT3 (527903).
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_175 | 3 Phase fault on CROSSROADS 7345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7345.00 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 (527656) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #lx c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of Harrington (523972, 523973) and Tolk (525561, 525562) units. | Operational measures fixing the voltage setpoint of Hobbs PLT3 (527903).
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_176 | 3 Phase fault on CRAWFISH_DR 345.00 (560022) 345 kV Bus a. Apply fault at the CRAWFISH_DR 345.00 (560022) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAWFISH_DR (560022) 345.0 kV to G17-151TAP (762216) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_177 | 3 Phase fault on HARRNG_MID 6230.00 (523978) 230 kV Bus a. Apply fault at the HARRNG_MID 6230.00 (523978) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_MID 6 (523978) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_178 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM6 (511557) 230.0 kV to CHISHOLM7 (511553) 345.0 kV to CHISHOLM1 (511558) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_179 | 3 Phase fault on NSUB345 345.00 (555234) 345 kV Bus a. Apply fault at the NSUB345 345.00 (555234) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PLVALLY4 (514929) 138.0 kV to NSUB345 (555234) 345.0 kV to NEWBUS13.8 (750000) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_180 | 3 Phase fault on NSUB345 345.00 (555234) 345 kV Bus a. Apply fault at the NSUB345 345.00 (555234) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PLVALLY4 (514929) 138.0 kV to NSUB345 (555234) 345.0 kV to NEWBUS13.8 (750001) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_181 | 3 Phase fault on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to GRACMNT7 (515800) 345.0 kV to GRCMNT11 (515801) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_182 | 3 Phase fault on ANADARK4 138.00 (520814) 138 kV Bus a. Apply fault at the ANADARK4 138.00 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 (520814) 138.0 kV to ANADARK2 (520810) 69.0 kV to ADRKTERT (521181) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_183 | 3 Phase fault on WASHITA4 138.00 (521089) 138 kV Bus a. Apply fault at the WASHITA4 138.00 (521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHITA4 (521089) 138.0 kV to WASHITA2 (521088) 69.0 kV to WASHTERT (521179) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_184 | 3 Phase fault on HITCHLAND 6230.00 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6230.00 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 3 (523093) 115.0 kV to HITCHLD_TR41 (523098) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_185 | 3 Phase fault on HITCHLAND 6230.00 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6230.00 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 3 (523093) 115.0 kV to HITCHLD_TR11 (523092) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_186 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_187 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_188 | 3 Phase fault on NOBLE_WND 7345.00 (523101) 345 kV Bus a. Apply fault at the NOBLE_WND 7345.00 (523101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOBLE_WND 7 (523101) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_189 | 3 Phase fault on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOVUS1 7 (523112) 345.0 kV to G06-44 (560577) 115.0 kV to NOVUS1_TR2 2 (560578) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_190 | 3 Phase fault on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_191 | 3 Phase fault on MCDWL_CREEK6230.00 (523323) 230 kV Bus a. Apply fault at the MCDWL_CREEK6230.00 (523323) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDWL_CREEK6 (523323) 230.0 kV to MCDWL_CREEK3 (523322) 115.0 kV to MCDWL_CRKTR1 (523321) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_192 | 3 Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6 (523777) 230.0 kV to WHEELER 3 (523776) 115.0 kV to WHEELER_TR11 (523774) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_193 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR 1 (523957) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_194 | 3 Phase fault on ROLLHILLS 6230.00 (524010) 230 kV Bus a. Apply fault at the ROLLHILLS 6230.00 (524010) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROLLHILLS 6 (524010) 230.0 kV to ROLLHILLS 3 (524007) 115.0 kV to ROLHILLS_TR1 (524008) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_195 | 3 Phase fault on BUSHLAND 6230.00 (524267) 230 kV Bus a. Apply fault at the BUSHLAND 6230.00 (524267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUSHLAND 6 (524267) 230.0 kV to BUSHLAND 3 (524266) 115.0 kV to BSHLND_TR1 1 (524263) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_196 | 3 Phase fault on NEWHART 6230.00 (525461) 230 kV Bus a. Apply fault at the NEWHART 6230.00 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 (525461) 230.0 kV to NEWHART 3 (525460) 115.0 kV to NEWHART_TR21 (525458) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_197 | 3 Phase fault on NEWHART 6230.00 (525461) 230 kV Bus a. Apply fault at the NEWHART 6230.00 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 (525461) 230.0 kV to NEWHART 3 (525460) 115.0 kV to NEWHART_TR11 (525459) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_198 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 6 (525531) 230.0 kV to TOLK 7 (525549) 345.0 kV to TOLK_TF3 (525539) 13.2 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_199 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 6 (525531) 230.0 kV to TOLK 7 (525549) 345.0 kV to TOLK_TF2 (525538) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_200 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV to TOLK_TR 1 (525537) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_201 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_202 | 3 Phase fault on SWEETWT6 230.00 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 230.00 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 (511541) 230.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_203 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_204 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_205 | 3 Phase fault on BUSHLAND 6230.00 (524267) 230 kV Bus a. Apply fault at the BUSHLAND 6230.00 (524267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUSHLAND 6 (524267) 230.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Local_Fault_206 | 3 Phase fault on CROSSROADS 7345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7345.00 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 (527656) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Regional_Fault_001 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Regional_Fault_002 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Regional_Fault_003 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Regional_Fault_004 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Regional_Fault_005 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Regional_Fault_006 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Regional_Fault_007 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Regional_Fault_008 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Regional_Fault_009 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Regional_Fault_010 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Regional_Fault_011 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Regional_Fault_012 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Regional_Fault_013 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Regional_Fault_014 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Regional_Fault_015 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Regional_Fault_016 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Regional_Fault_017 | 3 Phase fault on KAYWIND7 345.00 (514825) 345 kV Bus a. Apply fault at the KAYWIND7 345.00 (514825) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Regional_Fault_018 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Regional_Fault_019 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Regional_Fault_020 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Regional_Fault_021 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Regional_Fault_022 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BVRCNTY7 (515554) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). The issue was also observed in the base case. | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25S | Transfer | P1_Regional_Fault_023 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). The issue was also observed in the base case. | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25S | Transfer | P1_Regional_Fault_024 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). The issue was also observed in the base case. | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25S | Transfer | P1_Regional_Fault_025 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to CRAWFISH_DR (560022) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Regional_Fault_026 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Regional_Fault_027 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Regional_Fault_028 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Regional_Fault_029 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Regional_Fault_030 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Regional_Fault_031 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P1_Regional_Fault_032 | 3 Phase fault on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BOBCAT 7 (516106) 345.0 kV to 25MILE 7 (516146) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_001 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-092-TAP (763215) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_002 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to G18-092-TAP (763215) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_003 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G16-091-TAP (587744) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_004 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G16-091-TAP (587744) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#5-1 (511411) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_005 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#5-1 (511411) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_006 | Single Phase Fault with Stuck Breaker on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply Fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRYRD7 (511568) 345.0 kV to RUSHSPR7 (511571) 345.0 kV Transmission Circuit #1 b.2. TERRYRD7 (511568) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_007 | Single Phase Fault with Stuck Breaker on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply Fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRYRD7 (511568) 345.0 kV to SUNNYSD7 (515136) 345.0 kV Transmission Circuit #1 b.2. TERRYRD7 (511568) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_008 | Single Phase Fault with Stuck Breaker on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply Fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRYRD7 (511568) 345.0 kV to RUSHSPR7 (511571) 345.0 kV Transmission Circuit #1 b.2. TERRYRD7 (511568) 345.0 kV to SUNNYSD7 (515136) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips GEN-2015-045 (584862) and GEN-2014-057 (584073). | Protection disabled without any impact on stability.
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_009 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips GEN-2015-045 (584862) and GEN-2014-057 (584073). | Protection disabled without any impact on stability.
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_010 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_011 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 3 (523770) 115.0 kV to KIRBY 3 (524088) 115.0 kV Transmission Circuit #1 b.4. MCCULLOUGH 2 (523701) 69.0 kV to BOWERS 2 (523747) 69.0 kV Transmission Circuit #1 b.5. GRAPEVN_TR11 (523769) 13.2 kV to GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_012 | Single Phase Fault with Stuck Breaker on EDDY_NORTH 6230.00 (527799) 230 kV Bus a. Apply Fault at the EDDY_NORTH 6230.00 (527799) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDDY_NORTH 6 (527799) 230.0 kV to CUNNIGHM_N 6 (527865) 230.0 kV Transmission Circuit #1 b.2. EDDY_NORTH 6 (527799) 230.0 kV to 7-RIVERS 6 (528095) 230.0 kV Transmission Circuit #1 b.3. CROSSROADS 7 (527656) 345.0 kV to EDDY_CNTY 7 (527802) 345.0 kV Transmission Circuit #1 b.4. CHAVES_CNTY6 (527483) 230.0 kV to EDDY_NORTH 6 (527799) 230.0 kV Transmission Circuit #1 b.5. TWEEDY 3 (527597) 115.0 kV to EDDY_NTH 3 (527798) 115.0 kV Transmission Circuit #1 b.6. EAGLE_CREEK3 (527711) 115.0 kV to EDDY_NTH 3 (527798) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_013 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G16-091-TAP (587744) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_014 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT7 (515800) 345.0 kV to G16-091-TAP (587744) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_015 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G16-091-TAP (587744) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#5-1 (511411) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_016 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT7 (515800) 345.0 kV to G16-091-TAP (587744) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#5-1 (511411) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_017 | Single Phase Fault with Stuck Breaker on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply Fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRYRD7 (511568) 345.0 kV to RUSHSPR7 (511571) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips GEN-2015-045 (584862) and GEN-2014-057 (584073). | Protection disabled without any impact on stability.
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_018 | Single Phase Fault with Stuck Breaker on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply Fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRYRD7 (511568) 345.0 kV to RUSHSPR7 (511571) 345.0 kV Transmission Circuit #1 b.2. TERRYRD7 (511568) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips GEN-2015-045 (584862) and GEN-2014-057 (584073). | Protection disabled without any impact on stability.
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_019 | Single Phase Fault with Stuck Breaker on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply Fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRYRD7 (511568) 345.0 kV to SUNNYSD7 (515136) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_020 | Single Phase Fault with Stuck Breaker on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply Fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRYRD7 (511568) 345.0 kV to SUNNYSD7 (515136) 345.0 kV Transmission Circuit #1 b.2. TERRYRD7 (511568) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips GEN-2015-045 (584862) and GEN-2014-057 (584073). | Protection disabled without any impact on stability.
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_021 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_022 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRYRD7 (511568) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_023 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_024 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. TERRYRD7 (511568) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_025 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit #1 b.3. PALDR2W7 (515590) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_026 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to G18-092-TAP (763215) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_027 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G16-091-TAP (587744) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_028 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G16-091-TAP (587744) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#5-1 (511411) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_029 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#5-1 (511411) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_030 | Single Phase Fault with Stuck Breaker on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply Fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRYRD7 (511568) 345.0 kV to RUSHSPR7 (511571) 345.0 kV Transmission Circuit #1 b.2. TERRYRD7 (511568) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips GEN-2015-045 (584862) and GEN-2014-057 (584073). | Protection disabled without any impact on stability.
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_031 | Single Phase Fault with Stuck Breaker on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply Fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRYRD7 (511568) 345.0 kV to SUNNYSD7 (515136) 345.0 kV Transmission Circuit #1 b.2. TERRYRD7 (511568) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips GEN-2015-045 (584862) and GEN-2014-057 (584073). | Protection disabled without any impact on stability.
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_032 | Single Phase Fault with Stuck Breaker on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply Fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRYRD7 (511568) 345.0 kV to RUSHSPR7 (511571) 345.0 kV Transmission Circuit #1 b.2. TERRYRD7 (511568) 345.0 kV to SUNNYSD7 (515136) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips GEN-2015-045 (584862) and GEN-2014-057 (584073). | Protection disabled without any impact on stability.
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_033 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_034 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_035 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_036 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_037 | Single Phase Fault with Stuck Breaker on CROSSROADS 7345.00 (527656) 345 kV Bus a. Apply Fault at the CROSSROADS 7345.00 (527656) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROSSROADS 7 (527656) 345.0 kV to EDDY_CNTY 7 (527802) 345.0 kV Transmission Circuit #1 b.2. TOLK 7 (525549) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.3. RSVLT_CC_E 7 (527655) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.4. RSVLT_CC_W 7 (527654) 345.0 kV to RSVLT_CC_E 7 (527655) 345.0 kV Transmission Circuit #1 b.5. MILO_WND (577121) 34.5 kV to RSVLT_CC_E 7 (527655) 345.0 kV Two Winding #1 b.6. MILO_WIND 1 (527653) 0.7 kV to MILO_CB (577120) 34.5 kV Two Winding #1 b.7. RSVLT_GEN1 1 (527651) 0.7 kV to RSVLT_WIND11 (527658) 34.5 kV Two Winding #1 b.8. RSVLT_GEN2 1 (527652) 0.7 kV to RSVLT_WIND21 (527659) 34.5 kV Two Winding #1 b.9. RSVLT_CC_W 7 (527654) 345.0 kV to RSVLT_COL1 7 (527666) 345.0 kV Transmission Circuit #1 b.10. RSVLT_CC_W 7 (527654) 345.0 kV to RSVLT_COL2 7 (527667) 345.0 kV Transmission Circuit #1 b.11. SAGA_SCOL 7 (527610) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.12. CROSSROADS 7 (527656) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #ba b.13. CROSSROADS 7 (527656) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #lx | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_038 | Single Phase Fault with Stuck Breaker on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply Fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDDY_CNTY 7 (527802) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.2. CROSSROADS 7 (527656) 345.0 kV to EDDY_CNTY 7 (527802) 345.0 kV Transmission Circuit #1 b.3. EDDY_TR 1 (527796) 13.2 kV to EDDY_CNTY 7 (527802) 345.0 kV to EDDY_NORTH 6 (527799) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_039 | Single Phase Fault with Stuck Breaker on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply Fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDDY_TR 1 (527796) 13.2 kV to EDDY_CNTY 7 (527802) 345.0 kV to EDDY_NORTH 6 (527799) 230.0 kV Three Winding #1 b.2. CROSSROADS 7 (527656) 345.0 kV to EDDY_CNTY 7 (527802) 345.0 kV Transmission Circuit #1 b.3. EDDY_CNTY 7 (527802) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_040 | Single Phase Fault with Stuck Breaker on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply Fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDDY_TR 1 (527796) 13.2 kV to EDDY_CNTY 7 (527802) 345.0 kV to EDDY_NORTH 6 (527799) 230.0 kV Three Winding #1 b.2. CROSSROADS 7 (527656) 345.0 kV to EDDY_CNTY 7 (527802) 345.0 kV Transmission Circuit #1 b.3. EDDY_CNTY 7 (527802) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_041 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_042 | Single Phase Fault with Stuck Breaker on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply Fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. NOVUS_WND 1 (523107) 4.2 kV to NOVUS1 1 (523109) 34.5 kV Two Winding #1 b.3. NOVUS1 1 (523109) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.4. G06-44-2 (560581) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.5. NOVUS1 3 (523111) 115.0 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV Three Winding #1 b.6. NOVUS1_TR1 1 (523110) 13.8 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_043 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 b.3. HITCHLAND 7 (523097) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_044 | Single Phase Fault with Stuck Breaker on GRPLNS-CB2-134.500 (523126) 34.5 kV Bus a. Apply Fault at the GRPLNS-CB2-134.500 (523126) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.2. NOBLE_TR 1 (523102) 13.8 kV to NOBLE_WND 7 (523101) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV Three Winding #1 b.3. NOBLE_WND 3 (523103) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.4. NOBLE_WND 3 (523103) 115.0 kV to NOBLE_WND 7 (523101) 345.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 b.5. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.6. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-LV4-1 (523127) 34.5 kV Two Winding #1 b.7. NBLWND-LV2 1 (523128) 34.5 kV to GRPLNS-HV2-3 (523131) 115.0 kV Two Winding #1 b.8. GRPLNS-HV2-3 (523131) 115.0 kV to GRPLNS-LV2-1 (523129) 34.5 kV Two Winding #1 b.9. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-LV4-1 (523127) 34.5 kV Transmission Circuit #1 b.10. GRPLNS-LV4-1 (523127) 34.5 kV to GRPLNS-GT4-1 (523133) 0.5 kV Two Winding #1 b.11. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-LV2-1 (523129) 34.5 kV Transmission Circuit #1 b.12. GRPLNS-LV2-1 (523129) 34.5 kV to GRPLNS-GT2-1 (523132) 0.5 kV Two Winding #1 b.13. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-WT4-1 (523121) 0.6 kV Two Winding #1 b.14. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-WT2-1 (523123) 0.6 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_045 | Single Phase Fault with Stuck Breaker on SPNSPUR_WND134.500 (524294) 34.5 kV Bus a. Apply Fault at the SPNSPUR_WND134.500 (524294) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.2. POTTER_TR 1 (523957) 13.2 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Three Winding #1 b.3. POTTER_CO 7 (523961) 345.0 kV to SPNSPUR_WND7 (524296) 345.0 kV Transmission Circuit #1 b.4. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 b.5. POTTER_CO 7 (523961) 345.0 kV to GRAPEVINE (560035) 345.0 kV Transmission Circuit #1 b.7. SPNSPUR_WND7 (524296) 345.0 kV to SPNSPUR_COL7 (524299) 345.0 kV Transmission Circuit #1 b.8. SPNSPUR_GEN1 (524295) 0.7 kV to SPNSPUR_WND1 (524294) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_046 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 b.2. TUCO_INT 7 (525832) 345.0 kV to CRAWFISH_DR (560022) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_047 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 b.2. TUCO_INT 7 (525832) 345.0 kV to CRAWFISH_DR (560022) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_048 | Single Phase Fault with Stuck Breaker on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply Fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDDY_CNTY 7 (527802) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.2. CROSSROADS 7 (527656) 345.0 kV to EDDY_CNTY 7 (527802) 345.0 kV Transmission Circuit #1 b.3. EDDY_TR 1 (527796) 13.2 kV to EDDY_CNTY 7 (527802) 345.0 kV to EDDY_NORTH 6 (527799) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_049 | Single Phase Fault with Stuck Breaker on ANADARK4 138.00 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 138.00 (520814) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.W.S.-4 (511477) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 b.2. ANADARK4 (520814) 138.0 kV to CHERRYRD 4 (521129) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_050 | Single Phase Fault with Stuck Breaker on ANADARK4 138.00 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 138.00 (520814) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.W.S.-4 (511477) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 b.2. ANADARK2 (520810) 69.0 kV to ANADARK4 (520814) 138.0 kV to ADRKTERT (521181) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_051 | Single Phase Fault with Stuck Breaker on FLETCH-4 138.00 (520912) 138 kV Bus a. Apply Fault at the FLETCH-4 138.00 (520912) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANADARK2 (520810) 69.0 kV to ANADARK4 (520814) 138.0 kV to ADRKTERT (521181) 13.8 kV Three Winding #1 b.2. ANADARK4 (520814) 138.0 kV to GEORGIA4 (520923) 138.0 kV Transmission Circuit #1 b.3. COMANCH4 (520864) 138.0 kV to EMPIRE 4 (520900) 138.0 kV Transmission Circuit #1 b.4. EMPIRE 4 (520900) 138.0 kV to FLETCH-4 (520912) 138.0 kV Transmission Circuit #1 b.5. FLETCH-4 (520912) 138.0 kV to GEORGIA4 (520923) 138.0 kV Transmission Circuit #1 b.6. FLETCH-4 (520912) 138.0 kV to FLETCHR2 (520911) 69.0 kV to FLCHTERT (521168) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_052 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_053 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to CRAWFISH_DR (560022) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 b.3. BORDER 7 (515458) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_054 | Single Phase Fault with Stuck Breaker on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply Fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #2 b.2. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_055 | Single Phase Fault with Stuck Breaker on PLVALLY4 138.00 (514929) 138 kV Bus a. Apply Fault at the PLVALLY4 138.00 (514929) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCLAIN4 (514902) 138.0 kV to PLVALLY4 (514929) 138.0 kV Transmission Circuit #1 b.2. PLVALLY4 (514929) 138.0 kV to HOLLYWD4 (514953) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_056 | Single Phase Fault with Stuck Breaker on NSUB345 345.00 (555234) 345 kV Bus a. Apply Fault at the NSUB345 345.00 (555234) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCLAIN4 (514902) 138.0 kV to PLVALLY4 (514929) 138.0 kV Transmission Circuit #1 b.2. PLVALLY4 (514929) 138.0 kV to HOLLYWD4 (514953) 138.0 kV Transmission Circuit #1 b.3. PLVALLY4 (514929) 138.0 kV to CHERYCK4 (514957) 138.0 kV Transmission Circuit #1 b.4. PLVALLY4 (514929) 138.0 kV to TURNER 4 (514992) 138.0 kV Transmission Circuit #1 b.5. PLVALLY4 (514929) 138.0 kV to G17-152_TAP (914902) 138.0 kV Transmission Circuit #1 b.6. PLVALLY4 (514929) 138.0 kV to NSUB345 (555234) 345.0 kV to NEWBUS13.8 (750000) 13.8 kV Three Winding #1 b.7. PLVALLY4 (514929) 138.0 kV to NSUB345 (555234) 345.0 kV to NEWBUS13.8 (750001) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_057 | Single Phase Fault with Stuck Breaker on SUNNYSD7 345.00 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 345.00 (515136) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNNYSD7 (515136) 345.0 kV to SUNNYSD4 (515135) 138.0 kV to SUNYSD 1 (515405) 13.8 kV Three Winding #1 b.4. SUNNYSD7 (515136) 345.0 kV to G16-063-TAP (560088) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_058 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G16-091-TAP (587744) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_059 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT7 (515800) 345.0 kV to G16-091-TAP (587744) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_060 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G16-091-TAP (587744) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#5-1 (511411) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_061 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT7 (515800) 345.0 kV to G16-091-TAP (587744) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#5-1 (511411) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_062 | Single Phase Fault with Stuck Breaker on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply Fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRYRD7 (511568) 345.0 kV to RUSHSPR7 (511571) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips GEN-2015-045 (584862) and GEN-2014-057 (584073). | Protection disabled without any impact on stability.
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_063 | Single Phase Fault with Stuck Breaker on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply Fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRYRD7 (511568) 345.0 kV to RUSHSPR7 (511571) 345.0 kV Transmission Circuit #1 b.2. TERRYRD7 (511568) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips GEN-2015-045 (584862) and GEN-2014-057 (584073). | Protection disabled without any impact on stability.
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_064 | Single Phase Fault with Stuck Breaker on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply Fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRYRD7 (511568) 345.0 kV to SUNNYSD7 (515136) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_065 | Single Phase Fault with Stuck Breaker on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply Fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRYRD7 (511568) 345.0 kV to SUNNYSD7 (515136) 345.0 kV Transmission Circuit #1 b.2. TERRYRD7 (511568) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips GEN-2015-045 (584862) and GEN-2014-057 (584073). | Protection disabled without any impact on stability.
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_066 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_067 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRYRD7 (511568) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_068 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_069 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. TERRYRD7 (511568) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_070 | Single Phase Fault with Stuck Breaker on SUNNYSD7 345.00 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 345.00 (515136) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNNYSD7 (515136) 345.0 kV to SUNNYSD4 (515135) 138.0 kV to SUNYSD 1 (515405) 13.8 kV Three Winding #1 b.4. SUNNYSD7 (515136) 345.0 kV to G16-063-TAP (560088) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_071 | Single Phase Fault with Stuck Breaker on SUNNYSD7 345.00 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 345.00 (515136) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNNYSD7 (515136) 345.0 kV to SUNNYSD4 (515135) 138.0 kV to SUNYSD 1 (515405) 13.8 kV Three Winding #1 b.4. HUGO 7 (521157) 345.0 kV to G16-063-TAP (560088) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_072 | Single Phase Fault with Stuck Breaker on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply Fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.2. POTTER_CO 6 (523959) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 b.3. POTTER_CO 6 (523959) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 b.4. POTTER_TR 1 (523957) 13.2 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Three Winding #1 b.5. MCDWL_CREEK6 (523323) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 b.6. HILLSIDE 3 (524300) 115.0 kV to COULTER 3 (524306) 115.0 kV Transmission Circuit #1 b.7. CHAN+TASCOS6 (523869) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 b.8. POTTER_CO 6 (523959) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 b.9. BUSHLAND 6 (524267) 230.0 kV to DEAFSMITH 6 (524623) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_073 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G16-091-TAP (587744) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_074 | Single Phase Fault with Stuck Breaker on MINCO 7 345.00 (514801) 345 kV Bus a. Apply Fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.2. MINCO 7 (514801) 345.0 kV to NSUB345 (555234) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_075 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to GRACMNT7 (515800) 345.0 kV to GRCMNT11 (515801) 13.8 kV Three Winding #2 b.4. GRACMNT4 (515802) 138.0 kV to GRACMNT7 (515800) 345.0 kV to GRCMNT11 (515801) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_076 | Single Phase Fault with Stuck Breaker on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply Fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHOLM7 (511553) 345.0 kV to G16-037-TAP (560078) 345.0 kV Transmission Circuit #1 b.2. CHISHOLM7 (511553) 345.0 kV to GRAPEVINE (560035) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_077 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT7 (515800) 345.0 kV to G16-037-TAP (560078) 345.0 kV Transmission Circuit #1 b.2. GRACMNT4 (515802) 138.0 kV to GRACMNT7 (515800) 345.0 kV to GRCMNT11 (515801) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_079 | Single Phase Fault with Stuck Breaker on TOLK 7345.00 (525549) 345 kV Bus a. Apply Fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROOSEVELT 6 (524909) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #1 b.2. ROOSEVELT 6 (524909) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #2 b.3. PLANT_X 6 (525481) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #1 b.4. PLANT_X 6 (525481) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #2 b.5. TOLK 6 (525531) 230.0 kV to NEEDMORE 6 (525586) 230.0 kV Transmission Circuit #1 b.6. TOLK 6 (525531) 230.0 kV to LAMB_CNTY 6 (525637) 230.0 kV Transmission Circuit #1 b.7. TOLK 6 (525531) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.8. TOLK 6 (525531) 230.0 kV to GEN-2017-158 (762132) 230.0 kV Transmission Circuit #1 b.9. TOLK 6 (525531) 230.0 kV to GEN-2018-097 (763241) 230.0 kV Transmission Circuit #1 b.10. TOLK 6 (525531) 230.0 kV to TOLK_1 1 (525561) 24.0 kV Two Winding #1 b.11. TOLK 6 (525531) 230.0 kV to TOLK_2 1 (525562) 24.0 kV Two Winding #1 b.12. TOLK 6 (525531) 230.0 kV to TOLK 7 (525549) 345.0 kV to TOLK_TF3 (525539) 13.2 kV Three Winding #3 b.13. TOLK 6 (525531) 230.0 kV to TOLK 7 (525549) 345.0 kV to TOLK_TF2 (525538) 13.2 kV Three Winding #2 b.14. TOLK 6 (525531) 230.0 kV to TOLK 7 (525549) 345.0 kV to TOLK_TR 1 (525537) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_080 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to CRAWFISH_DR (560022) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 b.3. BORDER 7 (515458) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_082 | Single Phase Fault with Stuck Breaker on G17-151TAP 345.00 (762216) 345 kV Bus a. Apply Fault at the G17-151TAP 345.00 (762216) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAWFISH_DR (560022) 345.0 kV to G17-151TAP (762216) 345.0 kV Transmission Circuit #1 b.2. G17-151TAP (762216) 345.0 kV to GEN-2017-151 (762217) 345.0 kV Transmission Circuit #1 b.3. G17-151TAP (762216) 345.0 kV to G18-015-TAP (762467) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_083 | Single Phase Fault with Stuck Breaker on WWDBORDT 345.00 (755000) 345 kV Bus a. Apply Fault at the WWDBORDT 345.00 (755000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHOLM7 (511553) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 b.3. BORDER 7 (515458) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Local_Fault_084 | Single Phase Fault with Stuck Breaker on SWISHER 6230.00 (525213) 230 kV Bus a. Apply Fault at the SWISHER 6230.00 (525213) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AMA_SOUTH 6 (524415) 230.0 kV to SWISHER 6 (525213) 230.0 kV Transmission Circuit #1 b.2. SWISHER 6 (525213) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 b.3. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.4. SWISHER 6 (525213) 230.0 kV to SWISHER 3 (525212) 115.0 kV to SWISHER_TR11 (525211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Regional_Fault_001 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Regional_Fault_002 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Regional_Fault_003 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Regional_Fault_004 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Regional_Fault_005 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Regional_Fault_006 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Regional_Fault_007 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Regional_Fault_008 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Regional_Fault_009 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Regional_Fault_010 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Regional_Fault_011 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Regional_Fault_012 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Regional_Fault_013 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Regional_Fault_014 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Regional_Fault_015 | Single Phase Fault with Stuck Breaker on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply Fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. NOVUS_WND 1 (523107) 4.2 kV to NOVUS1 1 (523109) 34.5 kV Two Winding #1 b.3. NOVUS1 1 (523109) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.4. G06-44-2 (560581) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.5. NOVUS1 3 (523111) 115.0 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV Three Winding #1 b.6. NOVUS1_TR1 1 (523110) 13.8 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Regional_Fault_016 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Regional_Fault_017 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to CRAWFISH_DR (560022) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 b.3. BORDER 7 (515458) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Regional_Fault_018 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Regional_Fault_019 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.4. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Regional_Fault_020 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.4. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Regional_Fault_021 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #1 b.5. FTSMTHW5 (515301) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Regional_Fault_022 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #2 b.5. FTSMTHW5 (515301) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Regional_Fault_023 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 b.4. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Regional_Fault_024 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 b.4. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Regional_Fault_025 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 b.4. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Regional_Fault_026 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Regional_Fault_027 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 b.4. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Regional_Fault_028 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Regional_Fault_029 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Regional_Fault_030 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Regional_Fault_031 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Transfer | P4_Regional_Fault_032 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.3. G18-128-TAP (763421) 345.0 kV to None Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_001 | 3 Phase fault on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 (511458) 138.0 kV to REDHLSW4 (521116) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_002 | 3 Phase fault on S.W.S.-4 138.00 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 138.00 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 (511477) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_003 | 3 Phase fault on S.W.S.-4 138.00 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 138.00 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 (511477) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_004 | 3 Phase fault on RPPAPER4 138.00 (511512) 138 kV Bus a. Apply fault at the RPPAPER4 138.00 (511512) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 112GORE4 (511488) 138.0 kV to RPPAPER4 (511512) 138.0 kV Transmission Circuit #1 b.2. LWSTAP 4 (511439) 138.0 kV to L.E.S.-4 (511467) 138.0 kV Transmission Circuit #1 b.3. LWSTAP 4 (511439) 138.0 kV to RPPAPER4 (511512) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_005 | 3 Phase fault on COMANC-4 138.00 (511437) 138 kV Bus a. Apply fault at the COMANC-4 138.00 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 (511437) 138.0 kV to L.E.S.-4 (511467) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_006 | 3 Phase fault on COMMTAP4 138.00 (511494) 138 kV Bus a. Apply fault at the COMMTAP4 138.00 (511494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 (511467) 138.0 kV to COMMTAP4 (511494) 138.0 kV Transmission Circuit #1 b.2. DUNCAN-4 (511453) 138.0 kV to OMDUNCN4 (529304) 138.0 kV Transmission Circuit #1 b.3. COMMTAP4 (511494) 138.0 kV to OMDUNCN4 (529304) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_007 | 3 Phase fault on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_008 | 3 Phase fault on CL-AFTP4 138.00 (511446) 138 kV Bus a. Apply fault at the CL-AFTP4 138.00 (511446) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-AFTP4 (511446) 138.0 kV to HOB-JCT4 (511463) 138.0 kV Transmission Circuit #1 b.2. CL-AFTP4 (511446) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_009 | 3 Phase fault on L.E.S.-4 138.00 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 138.00 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 (511467) 138.0 kV to SHERID4 (511474) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_010 | 3 Phase fault on FALCNRD4 138.00 (511511) 138 kV Bus a. Apply fault at the FALCNRD4 138.00 (511511) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 (511458) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 b.2. SAYRE--4 (511504) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 b.3. SAYRE--4 (511504) 138.0 kV to ERICK 4 (520903) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_011 | 3 Phase fault on SWEETWT6 230.00 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 230.00 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 (511541) 230.0 kV to BUFFCK6 (511542) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_012 | 3 Phase fault on SWEETWT6 230.00 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 230.00 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 (511541) 230.0 kV to DEMPSEY6 (511544) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_013 | 3 Phase fault on SWEETWT6 230.00 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 230.00 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 (511541) 230.0 kV to ROARK6 (511547) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_014 | 3 Phase fault on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 (511568) 345.0 kV to SUNNYSD7 (515136) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips GEN-2015-045 (584862) and GEN-2014-057 (584073). | Protection disabled without any impact on stability.
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_015 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_016 | 3 Phase fault on ELKCITY6 230.00 (511490) 230 kV Bus a. Apply fault at the ELKCITY6 230.00 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 (511458) 138.0 kV to ELKCITY6 (511490) 230.0 kV to ELKC2-1 (511482) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_017 | 3 Phase fault on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_018 | 3 Phase fault on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#5-1 (511411) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_019 | 3 Phase fault on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-2 (511459) 69.0 kV to ELKCTY-4 (511458) 138.0 kV to ELKC4-1 (511493) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_020 | 3 Phase fault on L.E.S.-4 138.00 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 138.00 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 (511466) 69.0 kV to L.E.S.-4 (511467) 138.0 kV to LES#1-1 (511416) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_021 | 3 Phase fault on L.E.S.-4 138.00 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 138.00 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 (511466) 69.0 kV to L.E.S.-4 (511467) 138.0 kV to LES#2-1 (511415) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_022 | 3 Phase fault on BUFFCK6 230.00 (511542) 230 kV Bus a. Apply fault at the BUFFCK6 230.00 (511542) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUFFCK6 (511542) 230.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_023 | 3 Phase fault on FLE TAP4 138.00 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 138.00 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 (511423) 138.0 kV to G16-097-TAP (587794) 138.0 kV Transmission Circuit #1 b.2. FLE TAP4 (511423) 138.0 kV to L.E.S.-4 (511467) 138.0 kV Transmission Circuit #1 b.3. L.E.S.-4 (511467) 138.0 kV to ELGINJT4 (511486) 138.0 kV Transmission Circuit #1 b.4. ELGINJT4 (511486) 138.0 kV to ELSWORTH 4 (511563) 138.0 kV Transmission Circuit #1 b.5. S.W.S.-4 (511477) 138.0 kV to ELSWORTH 4 (511563) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_024 | 3 Phase fault on KGFSHSW4 138.00 (520533) 138 kV Bus a. Apply fault at the KGFSHSW4 138.00 (520533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVJCTN2 (520508) 69.0 kV to ANADARK2 (520810) 69.0 kV Transmission Circuit #1 b.2. CLVJCTN2 (520508) 69.0 kV to ANADARK4 (520814) 138.0 kV Two Winding #1 b.3. CLVJCTN2 (520508) 69.0 kV to COGAR 2 (520859) 69.0 kV Transmission Circuit #1 b.4. CANA 2 (520502) 69.0 kV to ELRENOJ2 (520899) 69.0 kV Transmission Circuit #1 b.5. EL RENO2 (520892) 69.0 kV to ELRENOJ2 (520899) 69.0 kV Transmission Circuit #1 b.6. EL RENO4 (520893) 138.0 kV to ELRENOJ2 (520899) 69.0 kV Two Winding #1 b.7. CANA 2 (520502) 69.0 kV to CALUMET2 (520839) 69.0 kV Transmission Circuit #1 b.8. WATNGSW4 (520536) 138.0 kV to CALUMET2 (520839) 69.0 kV Two Winding #1 b.9. CALUMET2 (520839) 69.0 kV to CONCHO 2 (520865) 69.0 kV Transmission Circuit #1 b.10. CALUMET2 (520839) 69.0 kV to WATNGSW2 (521090) 69.0 kV Transmission Circuit #1 b.11. KGFSHSW4 (520533) 138.0 kV to CONCHO 2 (520865) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_025 | 3 Phase fault on STLN-DEMARC6230.00 (523779) 230 kV Bus a. Apply fault at the STLN-DEMARC6230.00 (523779) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 (511541) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.2. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_026 | 3 Phase fault on ELKCITY6 230.00 (511490) 230 kV Bus a. Apply fault at the ELKCITY6 230.00 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCITY6 (511490) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_027 | 3 Phase fault on SWEETWT6 230.00 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 230.00 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 (511541) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_028 | 3 Phase fault on MNCWND47 345.00 (515939) 345 kV Bus a. Apply fault at the MNCWND47 345.00 (515939) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MNCWND47 (515939) 345.0 kV to MNCWND57 (515980) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_029 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV to TOLK_TR 1 (525537) 13.2 kV Three Winding #1 b.4. TOLK 7 (525549) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_030 | 3 Phase fault on LAMB_CNTY 6230.00 (525637) 230 kV Bus a. Apply fault at the LAMB_CNTY 6230.00 (525637) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 (525531) 230.0 kV to LAMB_CNTY 6 (525637) 230.0 kV Transmission Circuit #1 b.2. LAMB_CNTY 6 (525637) 230.0 kV to LAMB_CNTY 3 (525636) 115.0 kV to LAMB_TR3 1 (525633) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_031 | 3 Phase fault on PRINGLE 6230.00 (523267) 230 kV Bus a. Apply fault at the PRINGLE 6230.00 (523267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRINGLE 6 (523267) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 b.2. PRINGLE 6 (523267) 230.0 kV to PRINGLE 3 (523266) 115.0 kV to PRINGLE_TR 1 (523265) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_032 | 3 Phase fault on OCHILTREE 6230.00 (523155) 230 kV Bus a. Apply fault at the OCHILTREE 6230.00 (523155) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OCHILTREE 6 (523155) 230.0 kV to OCHILTREE 3 (523154) 115.0 kV to OCHLTRE_TR11 (523151) 13.2 kV Three Winding #1 b.4. HITCHLAND 6 (523095) 230.0 kV to OCHILTREE 6 (523155) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_033 | 3 Phase fault on XIT_INTG 6230.00 (523221) 230 kV Bus a. Apply fault at the XIT_INTG 6230.00 (523221) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. XIT_INTG 6 (523221) 230.0 kV to XIT_INTG 3 (523220) 115.0 kV to XIT_INTG TR1 (523219) 13.2 kV Three Winding #1 b.4. XIT_INTG 6 (523221) 230.0 kV to CHAN+TASCOS6 (523869) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_034 | 3 Phase fault on ANADARK4 138.00 (520814) 138 kV Bus a. Apply fault at the ANADARK4 138.00 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 (520814) 138.0 kV to CHERRYRD 4 (521129) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_035 | 3 Phase fault on ANADARK4 138.00 (520814) 138 kV Bus a. Apply fault at the ANADARK4 138.00 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVJCTN2 (520508) 69.0 kV to ANADARK4 (520814) 138.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_036 | 3 Phase fault on FLETCH-4 138.00 (520912) 138 kV Bus a. Apply fault at the FLETCH-4 138.00 (520912) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 (520814) 138.0 kV to GEORGIA4 (520923) 138.0 kV Transmission Circuit #1 b.2. COMANCH4 (520864) 138.0 kV to EMPIRE 4 (520900) 138.0 kV Transmission Circuit #1 b.3. EMPIRE 4 (520900) 138.0 kV to FLETCH-4 (520912) 138.0 kV Transmission Circuit #1 b.4. FLETCH-4 (520912) 138.0 kV to GEORGIA4 (520923) 138.0 kV Transmission Circuit #1 b.5. FLETCH-4 (520912) 138.0 kV to FLETCHR2 (520911) 69.0 kV to FLCHTERT (521168) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_037 | 3 Phase fault on ANADARK4 138.00 (520814) 138 kV Bus a. Apply fault at the ANADARK4 138.00 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 (520814) 138.0 kV to POCASET4 (521031) 138.0 kV Transmission Circuit #1 b.2. BRIDGCR4 (520501) 138.0 kV to SUNSHIN4 (521059) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_038 | 3 Phase fault on SEQUOYAHJ4 138.00 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 138.00 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 (520422) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 b.2. NAPLSTP4 (520510) 138.0 kV to PAYNESW4 (520888) 138.0 kV Transmission Circuit #1 b.3. CORNVIL4 (511449) 138.0 kV to CORN TP4 (520867) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_039 | 3 Phase fault on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_040 | 3 Phase fault on S.W.S.-4 138.00 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 138.00 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 (511477) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_041 | 3 Phase fault on ERICK 4 138.00 (520903) 138 kV Bus a. Apply fault at the ERICK 4 138.00 (520903) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAYRE--4 (511504) 138.0 kV to ERICK 4 (520903) 138.0 kV Transmission Circuit #1 b.2. BULOJ4 (520402) 138.0 kV to ERICK 4 (520903) 138.0 kV Transmission Circuit #1 b.3. ELKCTY-4 (511458) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_042 | 3 Phase fault on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 (511458) 138.0 kV to REDHLSW4 (521116) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_043 | 3 Phase fault on SLKHILLS 4 138.00 (521103) 138 kV Bus a. Apply fault at the SLKHILLS 4 138.00 (521103) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BC SW 4 (520512) 138.0 kV to SLKHILLS 4 (521103) 138.0 kV Transmission Circuit #1 b.2. BCVI_HVB (520514) 138.0 kV to SLKHILLS 4 (521103) 138.0 kV Transmission Circuit #1 b.3. WASHITA4 (521089) 138.0 kV to SLKHILLS 4 (521103) 138.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_044 | 3 Phase fault on ONEY 4 138.00 (521017) 138 kV Bus a. Apply fault at the ONEY 4 138.00 (521017) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONEY 4 (521017) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.2. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_045 | 3 Phase fault on S.W.S.-4 138.00 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 138.00 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 (511477) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_046 | 3 Phase fault on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_047 | 3 Phase fault on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_048 | 3 Phase fault on JOHNCO 7 345.00 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 345.00 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 (514809) 345.0 kV to SUNNYSD7 (515136) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_049 | 3 Phase fault on MINCO 7 345.00 (514801) 345 kV Bus a. Apply fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_050 | 3 Phase fault on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 (511568) 345.0 kV to SUNNYSD7 (515136) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips GEN-2015-045 (584862) and GEN-2014-057 (584073). | Protection disabled without any impact on stability.
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_051 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_052 | 3 Phase fault on FSHRTAP7 345.00 (515610) 345 kV Bus a. Apply fault at the FSHRTAP7 345.00 (515610) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to FSHRTAP7 (515610) 345.0 kV Transmission Circuit #1 b.2. KNGFSHR7 (515600) 345.0 kV to FSHRTAP7 (515610) 345.0 kV Transmission Circuit #1 b.3. CANADN7 (515605) 345.0 kV to FSHRTAP7 (515610) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_053 | 3 Phase fault on MCCLAIN4 138.00 (514902) 138 kV Bus a. Apply fault at the MCCLAIN4 138.00 (514902) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCLAIN4 (514902) 138.0 kV to PLVALLY4 (514929) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_054 | 3 Phase fault on TURNER 4 138.00 (514992) 138 kV Bus a. Apply fault at the TURNER 4 138.00 (514992) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOGATE 4 (514928) 138.0 kV to TURNER 4 (514992) 138.0 kV Transmission Circuit #1 b.2. PLVALLY4 (514929) 138.0 kV to TURNER 4 (514992) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_055 | 3 Phase fault on PLVALLY4 138.00 (514929) 138 kV Bus a. Apply fault at the PLVALLY4 138.00 (514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLVALLY4 (514929) 138.0 kV to HOLLYWD4 (514953) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_056 | 3 Phase fault on CHERYCK4 138.00 (514957) 138 kV Bus a. Apply fault at the CHERYCK4 138.00 (514957) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLVALLY4 (514929) 138.0 kV to CHERYCK4 (514957) 138.0 kV Transmission Circuit #1 b.2. CHERYCK4 (514957) 138.0 kV to BOYD 4 (514958) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_057 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_058 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_059 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_060 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). The issue was also observed in the base case. | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_061 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). The issue was also observed in the base case. | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_062 | 3 Phase fault on MINCO 7 345.00 (514801) 345 kV Bus a. Apply fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to MCNOWND7 (515444) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_063 | 3 Phase fault on MINCO 7 345.00 (514801) 345 kV Bus a. Apply fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_064 | 3 Phase fault on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_065 | 3 Phase fault on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_066 | 3 Phase fault on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_067 | 3 Phase fault on MINCO 7 345.00 (514801) 345 kV Bus a. Apply fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to MNCWND37 (515549) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_068 | 3 Phase fault on MNCWND37 345.00 (515549) 345 kV Bus a. Apply fault at the MNCWND37 345.00 (515549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MNCWND37 (515549) 345.0 kV to MNCWND47 (515939) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_069 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_070 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_071 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_072 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_073 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_074 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_075 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). The issue was also observed in the base case. | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_076 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). The issue was also observed in the base case. | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_077 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_078 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to GUTHRIE7 (515961) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). The issue was also observed in the base case. | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_079 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO11 (515714) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_080 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_081 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER31 (515720) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_082 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER41 (515721) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_083 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER21 (515792) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_084 | 3 Phase fault on SUNNYSD7 345.00 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 345.00 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD4 (515135) 138.0 kV to SUNNYSD7 (515136) 345.0 kV to SUNNYSD1 (515762) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_085 | 3 Phase fault on SUNNYSD7 345.00 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 345.00 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 (515136) 345.0 kV to SUNNYSD4 (515135) 138.0 kV to SUNYSD 1 (515405) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_086 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV31 (515795) 13.8 kV Three Winding #1 | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). The issue was also observed in the base case. | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_087 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). The issue was also observed in the base case. | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_088 | 3 Phase fault on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to GRACMNT7 (515800) 345.0 kV to GRCMNT11 (515801) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_089 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_090 | 3 Phase fault on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_091 | 3 Phase fault on FLE TAP4 138.00 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 138.00 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 (511423) 138.0 kV to G16-097-TAP (587794) 138.0 kV Transmission Circuit #1 b.2. FLE TAP4 (511423) 138.0 kV to L.E.S.-4 (511467) 138.0 kV Transmission Circuit #1 b.3. L.E.S.-4 (511467) 138.0 kV to ELGINJT4 (511486) 138.0 kV Transmission Circuit #1 b.4. ELGINJT4 (511486) 138.0 kV to ELSWORTH 4 (511563) 138.0 kV Transmission Circuit #1 b.5. S.W.S.-4 (511477) 138.0 kV to ELSWORTH 4 (511563) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_092 | 3 Phase fault on S.W.S.-4 138.00 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 138.00 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 (511477) 138.0 kV to G16-097-TAP (587794) 138.0 kV Transmission Circuit #1 b.2. FLE TAP4 (511423) 138.0 kV to L.E.S.-4 (511467) 138.0 kV Transmission Circuit #1 b.3. L.E.S.-4 (511467) 138.0 kV to ELGINJT4 (511486) 138.0 kV Transmission Circuit #1 b.4. ELGINJT4 (511486) 138.0 kV to ELSWORTH 4 (511563) 138.0 kV Transmission Circuit #1 b.5. S.W.S.-4 (511477) 138.0 kV to ELSWORTH 4 (511563) 138.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_093 | 3 Phase fault on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 (511468) 345.0 kV to G16-091-TAP (587744) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_094 | 3 Phase fault on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 (515800) 345.0 kV to G16-091-TAP (587744) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_095 | 3 Phase fault on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 (511468) 345.0 kV to G16-091-TAP (587744) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_096 | 3 Phase fault on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 (515800) 345.0 kV to G16-091-TAP (587744) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_097 | 3 Phase fault on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_098 | 3 Phase fault on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 (511568) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips GEN-2015-045 (584862) and GEN-2014-057 (584073). | Protection disabled without any impact on stability.
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_099 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV to G16-037-TAP (560078) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_100 | 3 Phase fault on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 (515800) 345.0 kV to G16-037-TAP (560078) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_101 | 3 Phase fault on SUNNYSD7 345.00 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 345.00 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 (515136) 345.0 kV to G16-063-TAP (560088) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_102 | 3 Phase fault on FLE TAP4 138.00 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 138.00 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 (511423) 138.0 kV to L.E.S.-4 (511467) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_103 | 3 Phase fault on LWSTAP 4 138.00 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 138.00 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 (511439) 138.0 kV to L.E.S.-4 (511467) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_104 | 3 Phase fault on CL-AFTP4 138.00 (511446) 138 kV Bus a. Apply fault at the CL-AFTP4 138.00 (511446) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-AFTP4 (511446) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_105 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_106 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-092-TAP (763215) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_107 | 3 Phase fault on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 (511458) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_108 | 3 Phase fault on L.E.S.-4 138.00 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 138.00 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 (511467) 138.0 kV to ELGINJT4 (511486) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_109 | 3 Phase fault on L.E.S.-4 138.00 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 138.00 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 (511467) 138.0 kV to COMMTAP4 (511494) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_110 | 3 Phase fault on SWEETWT6 230.00 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 230.00 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 (511541) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_111 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV to GRAPEVINE (560035) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_112 | 3 Phase fault on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 (511568) 345.0 kV to RUSHSPR7 (511571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips GEN-2015-045 (584862) and GEN-2014-057 (584073). | Protection disabled without any impact on stability.
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_113 | 3 Phase fault on MINCO 7 345.00 (514801) 345 kV Bus a. Apply fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to NSUB345 (555234) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency Relay trips MNCOWNG (515438, 515445, 515907). | Protection disabled without any impact on stability.
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_114 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to FSHRTAP7 (515610) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_115 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to NSUB345 (555234) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_116 | 3 Phase fault on PLVALLY4 138.00 (514929) 138 kV Bus a. Apply fault at the PLVALLY4 138.00 (514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLVALLY4 (514929) 138.0 kV to CHERYCK4 (514957) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_117 | 3 Phase fault on PLVALLY4 138.00 (514929) 138 kV Bus a. Apply fault at the PLVALLY4 138.00 (514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLVALLY4 (514929) 138.0 kV to TURNER 4 (514992) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_118 | 3 Phase fault on PLVALLY4 138.00 (514929) 138 kV Bus a. Apply fault at the PLVALLY4 138.00 (514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLVALLY4 (514929) 138.0 kV to G17-152_TAP (914902) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_119 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to NSUB345 (555234) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_120 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to NSUB345 (555234) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_121 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BVRCNTY7 (515554) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). The issue was also observed in the base case. | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_122 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). The issue was also observed in the base case. | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_123 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). The issue was also observed in the base case. | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_124 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). The issue was also observed in the base case. | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_125 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to CRAWFISH_DR (560022) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_126 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_127 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_128 | 3 Phase fault on SEQUOYAHJ4 138.00 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 138.00 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 (520422) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_129 | 3 Phase fault on ANADARK4 138.00 (520814) 138 kV Bus a. Apply fault at the ANADARK4 138.00 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 (520814) 138.0 kV to GEORGIA4 (520923) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_130 | 3 Phase fault on ANADARK4 138.00 (520814) 138 kV Bus a. Apply fault at the ANADARK4 138.00 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 (520814) 138.0 kV to POCASET4 (521031) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_131 | 3 Phase fault on ONEY 4 138.00 (521017) 138 kV Bus a. Apply fault at the ONEY 4 138.00 (521017) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONEY 4 (521017) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_132 | 3 Phase fault on WASHITA4 138.00 (521089) 138 kV Bus a. Apply fault at the WASHITA4 138.00 (521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHITA4 (521089) 138.0 kV to SLKHILLS 4 (521103) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_133 | 3 Phase fault on HITCHLAND 6230.00 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6230.00 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to OCHILTREE 6 (523155) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_134 | 3 Phase fault on HITCHLAND 6230.00 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6230.00 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to MOORE_CNTY 6 (523309) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_135 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 7 (523101) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_136 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to NOVUS1 7 (523112) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_137 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_138 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_139 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to G10014G11022 (576397) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_140 | 3 Phase fault on XIT_INTG 6230.00 (523221) 230 kV Bus a. Apply fault at the XIT_INTG 6230.00 (523221) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. XIT_INTG 6 (523221) 230.0 kV to CHAN+TASCOS6 (523869) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_141 | 3 Phase fault on PRINGLE 6230.00 (523267) 230 kV Bus a. Apply fault at the PRINGLE 6230.00 (523267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRINGLE 6 (523267) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_142 | 3 Phase fault on MOORE_CNTY 6230.00 (523309) 230 kV Bus a. Apply fault at the MOORE_CNTY 6230.00 (523309) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE_CNTY 6 (523309) 230.0 kV to MCDWL_CREEK6 (523323) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_143 | 3 Phase fault on MCDWL_CREEK6230.00 (523323) 230 kV Bus a. Apply fault at the MCDWL_CREEK6230.00 (523323) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDWL_CREEK6 (523323) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_144 | 3 Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_145 | 3 Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_146 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_147 | 3 Phase fault on CHAN+TASCOS6230.00 (523869) 230 kV Bus a. Apply fault at the CHAN+TASCOS6230.00 (523869) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAN+TASCOS6 (523869) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_148 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_149 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_150 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to BUSHLAND 6 (524267) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_151 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_152 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to SPNSPUR_WND7 (524296) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_153 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_154 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to GRAPEVINE (560035) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_155 | 3 Phase fault on HARRNG_WST 6230.00 (523977) 230 kV Bus a. Apply fault at the HARRNG_WST 6230.00 (523977) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_156 | 3 Phase fault on BUSHLAND 6230.00 (524267) 230 kV Bus a. Apply fault at the BUSHLAND 6230.00 (524267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUSHLAND 6 (524267) 230.0 kV to WILDOR2_JUS6 (524290) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_157 | 3 Phase fault on BUSHLAND 6230.00 (524267) 230 kV Bus a. Apply fault at the BUSHLAND 6230.00 (524267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUSHLAND 6 (524267) 230.0 kV to DEAFSMITH 6 (524623) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_158 | 3 Phase fault on SPNSPUR_WND7345.00 (524296) 345 kV Bus a. Apply fault at the SPNSPUR_WND7345.00 (524296) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPNSPUR_WND7 (524296) 345.0 kV to SPNSPUR_COL7 (524299) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_159 | 3 Phase fault on ROOSEVELT 6230.00 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6230.00 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 (524909) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_160 | 3 Phase fault on ROOSEVELT 6230.00 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6230.00 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 (524909) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_161 | 3 Phase fault on SWISHER 6230.00 (525213) 230 kV Bus a. Apply fault at the SWISHER 6230.00 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 (525213) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_162 | 3 Phase fault on NEWHART 6230.00 (525461) 230 kV Bus a. Apply fault at the NEWHART 6230.00 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 (525461) 230.0 kV to PLANT_X 6 (525481) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_163 | 3 Phase fault on PLANT_X 6230.00 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6230.00 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 (525481) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_164 | 3 Phase fault on PLANT_X 6230.00 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6230.00 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 (525481) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_165 | 3 Phase fault on TOLK 6230.00 (525531) 230 kV Bus a. Apply fault at the TOLK 6230.00 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 (525531) 230.0 kV to NEEDMORE 6 (525586) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_166 | 3 Phase fault on TOLK 6230.00 (525531) 230 kV Bus a. Apply fault at the TOLK 6230.00 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 (525531) 230.0 kV to LAMB_CNTY 6 (525637) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_167 | 3 Phase fault on TOLK 6230.00 (525531) 230 kV Bus a. Apply fault at the TOLK 6230.00 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 (525531) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_168 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_169 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to CRAWFISH_DR (560022) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_170 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to CRAWFISH_DR (560022) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_171 | 3 Phase fault on SAGA_SCOL 7345.00 (527610) 345 kV Bus a. Apply fault at the SAGA_SCOL 7345.00 (527610) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SAGA_SCOL 7 (527610) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_172 | 3 Phase fault on RSVLT_CC_E 7345.00 (527655) 345 kV Bus a. Apply fault at the RSVLT_CC_E 7345.00 (527655) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSVLT_CC_E 7 (527655) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_173 | 3 Phase fault on CROSSROADS 7345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7345.00 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 (527656) 345.0 kV to EDDY_CNTY 7 (527802) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_174 | 3 Phase fault on CROSSROADS 7345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7345.00 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 (527656) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #ba c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_175 | 3 Phase fault on CROSSROADS 7345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7345.00 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 (527656) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #lx c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_176 | 3 Phase fault on CRAWFISH_DR 345.00 (560022) 345 kV Bus a. Apply fault at the CRAWFISH_DR 345.00 (560022) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAWFISH_DR (560022) 345.0 kV to G17-151TAP (762216) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_177 | 3 Phase fault on HARRNG_MID 6230.00 (523978) 230 kV Bus a. Apply fault at the HARRNG_MID 6230.00 (523978) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_MID 6 (523978) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_178 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM6 (511557) 230.0 kV to CHISHOLM7 (511553) 345.0 kV to CHISHOLM1 (511558) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_179 | 3 Phase fault on NSUB345 345.00 (555234) 345 kV Bus a. Apply fault at the NSUB345 345.00 (555234) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PLVALLY4 (514929) 138.0 kV to NSUB345 (555234) 345.0 kV to NEWBUS13.8 (750000) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_180 | 3 Phase fault on NSUB345 345.00 (555234) 345 kV Bus a. Apply fault at the NSUB345 345.00 (555234) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PLVALLY4 (514929) 138.0 kV to NSUB345 (555234) 345.0 kV to NEWBUS13.8 (750001) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_181 | 3 Phase fault on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to GRACMNT7 (515800) 345.0 kV to GRCMNT11 (515801) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_182 | 3 Phase fault on ANADARK4 138.00 (520814) 138 kV Bus a. Apply fault at the ANADARK4 138.00 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 (520814) 138.0 kV to ANADARK2 (520810) 69.0 kV to ADRKTERT (521181) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_183 | 3 Phase fault on WASHITA4 138.00 (521089) 138 kV Bus a. Apply fault at the WASHITA4 138.00 (521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHITA4 (521089) 138.0 kV to WASHITA2 (521088) 69.0 kV to WASHTERT (521179) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_184 | 3 Phase fault on HITCHLAND 6230.00 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6230.00 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 3 (523093) 115.0 kV to HITCHLD_TR41 (523098) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_185 | 3 Phase fault on HITCHLAND 6230.00 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6230.00 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 3 (523093) 115.0 kV to HITCHLD_TR11 (523092) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_186 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_187 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_188 | 3 Phase fault on NOBLE_WND 7345.00 (523101) 345 kV Bus a. Apply fault at the NOBLE_WND 7345.00 (523101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOBLE_WND 7 (523101) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_189 | 3 Phase fault on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOVUS1 7 (523112) 345.0 kV to G06-44 (560577) 115.0 kV to NOVUS1_TR2 2 (560578) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_190 | 3 Phase fault on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_191 | 3 Phase fault on MCDWL_CREEK6230.00 (523323) 230 kV Bus a. Apply fault at the MCDWL_CREEK6230.00 (523323) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDWL_CREEK6 (523323) 230.0 kV to MCDWL_CREEK3 (523322) 115.0 kV to MCDWL_CRKTR1 (523321) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_192 | 3 Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6 (523777) 230.0 kV to WHEELER 3 (523776) 115.0 kV to WHEELER_TR11 (523774) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_193 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR 1 (523957) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_194 | 3 Phase fault on ROLLHILLS 6230.00 (524010) 230 kV Bus a. Apply fault at the ROLLHILLS 6230.00 (524010) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROLLHILLS 6 (524010) 230.0 kV to ROLLHILLS 3 (524007) 115.0 kV to ROLHILLS_TR1 (524008) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_195 | 3 Phase fault on BUSHLAND 6230.00 (524267) 230 kV Bus a. Apply fault at the BUSHLAND 6230.00 (524267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUSHLAND 6 (524267) 230.0 kV to BUSHLAND 3 (524266) 115.0 kV to BSHLND_TR1 1 (524263) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_196 | 3 Phase fault on NEWHART 6230.00 (525461) 230 kV Bus a. Apply fault at the NEWHART 6230.00 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 (525461) 230.0 kV to NEWHART 3 (525460) 115.0 kV to NEWHART_TR21 (525458) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_197 | 3 Phase fault on NEWHART 6230.00 (525461) 230 kV Bus a. Apply fault at the NEWHART 6230.00 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 (525461) 230.0 kV to NEWHART 3 (525460) 115.0 kV to NEWHART_TR11 (525459) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_198 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 6 (525531) 230.0 kV to TOLK 7 (525549) 345.0 kV to TOLK_TF3 (525539) 13.2 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_199 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 6 (525531) 230.0 kV to TOLK 7 (525549) 345.0 kV to TOLK_TF2 (525538) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_200 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV to TOLK_TR 1 (525537) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_201 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_202 | 3 Phase fault on SWEETWT6 230.00 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 230.00 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 (511541) 230.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_203 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_204 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_205 | 3 Phase fault on BUSHLAND 6230.00 (524267) 230 kV Bus a. Apply fault at the BUSHLAND 6230.00 (524267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUSHLAND 6 (524267) 230.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Local_Fault_206 | 3 Phase fault on CROSSROADS 7345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7345.00 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 (527656) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Regional_Fault_001 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Regional_Fault_002 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Regional_Fault_003 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Regional_Fault_004 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Regional_Fault_005 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Regional_Fault_006 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Regional_Fault_007 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Regional_Fault_008 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Regional_Fault_009 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Regional_Fault_010 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Regional_Fault_011 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Regional_Fault_012 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Regional_Fault_013 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Regional_Fault_014 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Regional_Fault_015 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Regional_Fault_016 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Regional_Fault_017 | 3 Phase fault on KAYWIND7 345.00 (514825) 345 kV Bus a. Apply fault at the KAYWIND7 345.00 (514825) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Regional_Fault_018 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Regional_Fault_019 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Regional_Fault_020 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Regional_Fault_021 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Regional_Fault_022 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BVRCNTY7 (515554) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). The issue was also observed in the base case. | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25W | Transfer | P1_Regional_Fault_023 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). The issue was also observed in the base case. | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25W | Transfer | P1_Regional_Fault_024 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). The issue was also observed in the base case. | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25W | Transfer | P1_Regional_Fault_025 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to CRAWFISH_DR (560022) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Regional_Fault_026 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Regional_Fault_027 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Regional_Fault_028 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Regional_Fault_029 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Regional_Fault_030 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Regional_Fault_031 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P1_Regional_Fault_032 | 3 Phase fault on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BOBCAT 7 (516106) 345.0 kV to 25MILE 7 (516146) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_001 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-092-TAP (763215) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_002 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to G18-092-TAP (763215) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_003 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G16-091-TAP (587744) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_004 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G16-091-TAP (587744) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#5-1 (511411) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_005 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#5-1 (511411) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_006 | Single Phase Fault with Stuck Breaker on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply Fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRYRD7 (511568) 345.0 kV to RUSHSPR7 (511571) 345.0 kV Transmission Circuit #1 b.2. TERRYRD7 (511568) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips GEN-2015-045 (584862) and GEN-2014-057 (584073). | Protection disabled without any impact on stability.
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_007 | Single Phase Fault with Stuck Breaker on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply Fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRYRD7 (511568) 345.0 kV to SUNNYSD7 (515136) 345.0 kV Transmission Circuit #1 b.2. TERRYRD7 (511568) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips GEN-2015-045 (584862) and GEN-2014-057 (584073). | Protection disabled without any impact on stability.
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_008 | Single Phase Fault with Stuck Breaker on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply Fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRYRD7 (511568) 345.0 kV to RUSHSPR7 (511571) 345.0 kV Transmission Circuit #1 b.2. TERRYRD7 (511568) 345.0 kV to SUNNYSD7 (515136) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips GEN-2015-045 (584862) and GEN-2014-057 (584073). | Protection disabled without any impact on stability.
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_009 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_010 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_011 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 3 (523770) 115.0 kV to KIRBY 3 (524088) 115.0 kV Transmission Circuit #1 b.4. MCCULLOUGH 2 (523701) 69.0 kV to BOWERS 2 (523747) 69.0 kV Transmission Circuit #1 b.5. GRAPEVN_TR11 (523769) 13.2 kV to GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_012 | Single Phase Fault with Stuck Breaker on EDDY_NORTH 6230.00 (527799) 230 kV Bus a. Apply Fault at the EDDY_NORTH 6230.00 (527799) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDDY_NORTH 6 (527799) 230.0 kV to CUNNIGHM_N 6 (527865) 230.0 kV Transmission Circuit #1 b.2. EDDY_NORTH 6 (527799) 230.0 kV to 7-RIVERS 6 (528095) 230.0 kV Transmission Circuit #1 b.3. CROSSROADS 7 (527656) 345.0 kV to EDDY_CNTY 7 (527802) 345.0 kV Transmission Circuit #1 b.4. CHAVES_CNTY6 (527483) 230.0 kV to EDDY_NORTH 6 (527799) 230.0 kV Transmission Circuit #1 b.5. TWEEDY 3 (527597) 115.0 kV to EDDY_NTH 3 (527798) 115.0 kV Transmission Circuit #1 b.6. EAGLE_CREEK3 (527711) 115.0 kV to EDDY_NTH 3 (527798) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_013 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G16-091-TAP (587744) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_014 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT7 (515800) 345.0 kV to G16-091-TAP (587744) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_015 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G16-091-TAP (587744) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#5-1 (511411) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_016 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT7 (515800) 345.0 kV to G16-091-TAP (587744) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#5-1 (511411) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_017 | Single Phase Fault with Stuck Breaker on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply Fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRYRD7 (511568) 345.0 kV to RUSHSPR7 (511571) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips GEN-2015-045 (584862) and GEN-2014-057 (584073). | Protection disabled without any impact on stability.
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_018 | Single Phase Fault with Stuck Breaker on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply Fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRYRD7 (511568) 345.0 kV to RUSHSPR7 (511571) 345.0 kV Transmission Circuit #1 b.2. TERRYRD7 (511568) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips GEN-2015-045 (584862) and GEN-2014-057 (584073). | Protection disabled without any impact on stability.
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_019 | Single Phase Fault with Stuck Breaker on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply Fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRYRD7 (511568) 345.0 kV to SUNNYSD7 (515136) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips GEN-2015-045 (584862) and GEN-2014-057 (584073). | Protection disabled without any impact on stability.
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_020 | Single Phase Fault with Stuck Breaker on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply Fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRYRD7 (511568) 345.0 kV to SUNNYSD7 (515136) 345.0 kV Transmission Circuit #1 b.2. TERRYRD7 (511568) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips GEN-2015-045 (584862) and GEN-2014-057 (584073). | Protection disabled without any impact on stability.
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_021 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_022 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRYRD7 (511568) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_023 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_024 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. TERRYRD7 (511568) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_025 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit #1 b.3. PALDR2W7 (515590) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_026 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to G18-092-TAP (763215) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_027 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G16-091-TAP (587744) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_028 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G16-091-TAP (587744) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#5-1 (511411) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_029 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#5-1 (511411) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_030 | Single Phase Fault with Stuck Breaker on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply Fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRYRD7 (511568) 345.0 kV to RUSHSPR7 (511571) 345.0 kV Transmission Circuit #1 b.2. TERRYRD7 (511568) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips GEN-2015-045 (584862) and GEN-2014-057 (584073). | Protection disabled without any impact on stability.
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_031 | Single Phase Fault with Stuck Breaker on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply Fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRYRD7 (511568) 345.0 kV to SUNNYSD7 (515136) 345.0 kV Transmission Circuit #1 b.2. TERRYRD7 (511568) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips GEN-2015-045 (584862) and GEN-2014-057 (584073). | Protection disabled without any impact on stability.
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_032 | Single Phase Fault with Stuck Breaker on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply Fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRYRD7 (511568) 345.0 kV to RUSHSPR7 (511571) 345.0 kV Transmission Circuit #1 b.2. TERRYRD7 (511568) 345.0 kV to SUNNYSD7 (515136) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips GEN-2015-045 (584862) and GEN-2014-057 (584073). | Protection disabled without any impact on stability.
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_033 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_034 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_035 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_036 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_037 | Single Phase Fault with Stuck Breaker on CROSSROADS 7345.00 (527656) 345 kV Bus a. Apply Fault at the CROSSROADS 7345.00 (527656) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROSSROADS 7 (527656) 345.0 kV to EDDY_CNTY 7 (527802) 345.0 kV Transmission Circuit #1 b.2. TOLK 7 (525549) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.3. RSVLT_CC_E 7 (527655) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.4. RSVLT_CC_W 7 (527654) 345.0 kV to RSVLT_CC_E 7 (527655) 345.0 kV Transmission Circuit #1 b.5. MILO_WND (577121) 34.5 kV to RSVLT_CC_E 7 (527655) 345.0 kV Two Winding #1 b.6. MILO_WIND 1 (527653) 0.7 kV to MILO_CB (577120) 34.5 kV Two Winding #1 b.7. RSVLT_GEN1 1 (527651) 0.7 kV to RSVLT_WIND11 (527658) 34.5 kV Two Winding #1 b.8. RSVLT_GEN2 1 (527652) 0.7 kV to RSVLT_WIND21 (527659) 34.5 kV Two Winding #1 b.9. RSVLT_CC_W 7 (527654) 345.0 kV to RSVLT_COL1 7 (527666) 345.0 kV Transmission Circuit #1 b.10. RSVLT_CC_W 7 (527654) 345.0 kV to RSVLT_COL2 7 (527667) 345.0 kV Transmission Circuit #1 b.11. SAGA_SCOL 7 (527610) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.12. CROSSROADS 7 (527656) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #ba b.13. CROSSROADS 7 (527656) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #lx | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_038 | Single Phase Fault with Stuck Breaker on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply Fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDDY_CNTY 7 (527802) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.2. CROSSROADS 7 (527656) 345.0 kV to EDDY_CNTY 7 (527802) 345.0 kV Transmission Circuit #1 b.3. EDDY_TR 1 (527796) 13.2 kV to EDDY_CNTY 7 (527802) 345.0 kV to EDDY_NORTH 6 (527799) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_039 | Single Phase Fault with Stuck Breaker on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply Fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDDY_TR 1 (527796) 13.2 kV to EDDY_CNTY 7 (527802) 345.0 kV to EDDY_NORTH 6 (527799) 230.0 kV Three Winding #1 b.2. CROSSROADS 7 (527656) 345.0 kV to EDDY_CNTY 7 (527802) 345.0 kV Transmission Circuit #1 b.3. EDDY_CNTY 7 (527802) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_040 | Single Phase Fault with Stuck Breaker on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply Fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDDY_TR 1 (527796) 13.2 kV to EDDY_CNTY 7 (527802) 345.0 kV to EDDY_NORTH 6 (527799) 230.0 kV Three Winding #1 b.2. CROSSROADS 7 (527656) 345.0 kV to EDDY_CNTY 7 (527802) 345.0 kV Transmission Circuit #1 b.3. EDDY_CNTY 7 (527802) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_041 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_042 | Single Phase Fault with Stuck Breaker on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply Fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. NOVUS_WND 1 (523107) 4.2 kV to NOVUS1 1 (523109) 34.5 kV Two Winding #1 b.3. NOVUS1 1 (523109) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.4. G06-44-2 (560581) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.5. NOVUS1 3 (523111) 115.0 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV Three Winding #1 b.6. NOVUS1_TR1 1 (523110) 13.8 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_043 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 b.3. HITCHLAND 7 (523097) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_044 | Single Phase Fault with Stuck Breaker on GRPLNS-CB2-134.500 (523126) 34.5 kV Bus a. Apply Fault at the GRPLNS-CB2-134.500 (523126) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.2. NOBLE_TR 1 (523102) 13.8 kV to NOBLE_WND 7 (523101) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV Three Winding #1 b.3. NOBLE_WND 3 (523103) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.4. NOBLE_WND 3 (523103) 115.0 kV to NOBLE_WND 7 (523101) 345.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 b.5. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.6. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-LV4-1 (523127) 34.5 kV Two Winding #1 b.7. NBLWND-LV2 1 (523128) 34.5 kV to GRPLNS-HV2-3 (523131) 115.0 kV Two Winding #1 b.8. GRPLNS-HV2-3 (523131) 115.0 kV to GRPLNS-LV2-1 (523129) 34.5 kV Two Winding #1 b.9. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-LV4-1 (523127) 34.5 kV Transmission Circuit #1 b.10. GRPLNS-LV4-1 (523127) 34.5 kV to GRPLNS-GT4-1 (523133) 0.5 kV Two Winding #1 b.11. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-LV2-1 (523129) 34.5 kV Transmission Circuit #1 b.12. GRPLNS-LV2-1 (523129) 34.5 kV to GRPLNS-GT2-1 (523132) 0.5 kV Two Winding #1 b.13. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-WT4-1 (523121) 0.6 kV Two Winding #1 b.14. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-WT2-1 (523123) 0.6 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_045 | Single Phase Fault with Stuck Breaker on SPNSPUR_WND134.500 (524294) 34.5 kV Bus a. Apply Fault at the SPNSPUR_WND134.500 (524294) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.2. POTTER_TR 1 (523957) 13.2 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Three Winding #1 b.3. POTTER_CO 7 (523961) 345.0 kV to SPNSPUR_WND7 (524296) 345.0 kV Transmission Circuit #1 b.4. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 b.5. POTTER_CO 7 (523961) 345.0 kV to GRAPEVINE (560035) 345.0 kV Transmission Circuit #1 b.7. SPNSPUR_WND7 (524296) 345.0 kV to SPNSPUR_COL7 (524299) 345.0 kV Transmission Circuit #1 b.8. SPNSPUR_GEN1 (524295) 0.7 kV to SPNSPUR_WND1 (524294) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_046 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 b.2. TUCO_INT 7 (525832) 345.0 kV to CRAWFISH_DR (560022) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_047 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 b.2. TUCO_INT 7 (525832) 345.0 kV to CRAWFISH_DR (560022) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_048 | Single Phase Fault with Stuck Breaker on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply Fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDDY_CNTY 7 (527802) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.2. CROSSROADS 7 (527656) 345.0 kV to EDDY_CNTY 7 (527802) 345.0 kV Transmission Circuit #1 b.3. EDDY_TR 1 (527796) 13.2 kV to EDDY_CNTY 7 (527802) 345.0 kV to EDDY_NORTH 6 (527799) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_049 | Single Phase Fault with Stuck Breaker on ANADARK4 138.00 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 138.00 (520814) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.W.S.-4 (511477) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 b.2. ANADARK4 (520814) 138.0 kV to CHERRYRD 4 (521129) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_050 | Single Phase Fault with Stuck Breaker on ANADARK4 138.00 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 138.00 (520814) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.W.S.-4 (511477) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 b.2. ANADARK2 (520810) 69.0 kV to ANADARK4 (520814) 138.0 kV to ADRKTERT (521181) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_051 | Single Phase Fault with Stuck Breaker on FLETCH-4 138.00 (520912) 138 kV Bus a. Apply Fault at the FLETCH-4 138.00 (520912) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANADARK2 (520810) 69.0 kV to ANADARK4 (520814) 138.0 kV to ADRKTERT (521181) 13.8 kV Three Winding #1 b.2. ANADARK4 (520814) 138.0 kV to GEORGIA4 (520923) 138.0 kV Transmission Circuit #1 b.3. COMANCH4 (520864) 138.0 kV to EMPIRE 4 (520900) 138.0 kV Transmission Circuit #1 b.4. EMPIRE 4 (520900) 138.0 kV to FLETCH-4 (520912) 138.0 kV Transmission Circuit #1 b.5. FLETCH-4 (520912) 138.0 kV to GEORGIA4 (520923) 138.0 kV Transmission Circuit #1 b.6. FLETCH-4 (520912) 138.0 kV to FLETCHR2 (520911) 69.0 kV to FLCHTERT (521168) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_052 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_053 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to CRAWFISH_DR (560022) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 b.3. BORDER 7 (515458) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_054 | Single Phase Fault with Stuck Breaker on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply Fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #2 b.2. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_055 | Single Phase Fault with Stuck Breaker on PLVALLY4 138.00 (514929) 138 kV Bus a. Apply Fault at the PLVALLY4 138.00 (514929) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCLAIN4 (514902) 138.0 kV to PLVALLY4 (514929) 138.0 kV Transmission Circuit #1 b.2. PLVALLY4 (514929) 138.0 kV to HOLLYWD4 (514953) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_056 | Single Phase Fault with Stuck Breaker on NSUB345 345.00 (555234) 345 kV Bus a. Apply Fault at the NSUB345 345.00 (555234) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCLAIN4 (514902) 138.0 kV to PLVALLY4 (514929) 138.0 kV Transmission Circuit #1 b.2. PLVALLY4 (514929) 138.0 kV to HOLLYWD4 (514953) 138.0 kV Transmission Circuit #1 b.3. PLVALLY4 (514929) 138.0 kV to CHERYCK4 (514957) 138.0 kV Transmission Circuit #1 b.4. PLVALLY4 (514929) 138.0 kV to TURNER 4 (514992) 138.0 kV Transmission Circuit #1 b.5. PLVALLY4 (514929) 138.0 kV to G17-152_TAP (914902) 138.0 kV Transmission Circuit #1 b.6. PLVALLY4 (514929) 138.0 kV to NSUB345 (555234) 345.0 kV to NEWBUS13.8 (750000) 13.8 kV Three Winding #1 b.7. PLVALLY4 (514929) 138.0 kV to NSUB345 (555234) 345.0 kV to NEWBUS13.8 (750001) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_057 | Single Phase Fault with Stuck Breaker on SUNNYSD7 345.00 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 345.00 (515136) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNNYSD7 (515136) 345.0 kV to SUNNYSD4 (515135) 138.0 kV to SUNYSD 1 (515405) 13.8 kV Three Winding #1 b.4. SUNNYSD7 (515136) 345.0 kV to G16-063-TAP (560088) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_058 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G16-091-TAP (587744) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_059 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT7 (515800) 345.0 kV to G16-091-TAP (587744) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_060 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G16-091-TAP (587744) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#5-1 (511411) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_061 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT7 (515800) 345.0 kV to G16-091-TAP (587744) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#5-1 (511411) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_062 | Single Phase Fault with Stuck Breaker on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply Fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRYRD7 (511568) 345.0 kV to RUSHSPR7 (511571) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips GEN-2015-045 (584862) and GEN-2014-057 (584073). | Protection disabled without any impact on stability.
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_063 | Single Phase Fault with Stuck Breaker on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply Fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRYRD7 (511568) 345.0 kV to RUSHSPR7 (511571) 345.0 kV Transmission Circuit #1 b.2. TERRYRD7 (511568) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips GEN-2015-045 (584862) and GEN-2014-057 (584073). | Protection disabled without any impact on stability.
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_064 | Single Phase Fault with Stuck Breaker on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply Fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRYRD7 (511568) 345.0 kV to SUNNYSD7 (515136) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips GEN-2015-045 (584862) and GEN-2014-057 (584073). | Protection disabled without any impact on stability.
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_065 | Single Phase Fault with Stuck Breaker on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply Fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRYRD7 (511568) 345.0 kV to SUNNYSD7 (515136) 345.0 kV Transmission Circuit #1 b.2. TERRYRD7 (511568) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips GEN-2015-045 (584862) and GEN-2014-057 (584073). | Protection disabled without any impact on stability.
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_066 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_067 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRYRD7 (511568) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_068 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_069 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. TERRYRD7 (511568) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_070 | Single Phase Fault with Stuck Breaker on SUNNYSD7 345.00 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 345.00 (515136) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNNYSD7 (515136) 345.0 kV to SUNNYSD4 (515135) 138.0 kV to SUNYSD 1 (515405) 13.8 kV Three Winding #1 b.4. SUNNYSD7 (515136) 345.0 kV to G16-063-TAP (560088) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_071 | Single Phase Fault with Stuck Breaker on SUNNYSD7 345.00 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 345.00 (515136) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNNYSD7 (515136) 345.0 kV to SUNNYSD4 (515135) 138.0 kV to SUNYSD 1 (515405) 13.8 kV Three Winding #1 b.4. HUGO 7 (521157) 345.0 kV to G16-063-TAP (560088) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_072 | Single Phase Fault with Stuck Breaker on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply Fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.2. POTTER_CO 6 (523959) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 b.3. POTTER_CO 6 (523959) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 b.4. POTTER_TR 1 (523957) 13.2 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Three Winding #1 b.5. MCDWL_CREEK6 (523323) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 b.6. HILLSIDE 3 (524300) 115.0 kV to COULTER 3 (524306) 115.0 kV Transmission Circuit #1 b.7. CHAN+TASCOS6 (523869) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 b.8. POTTER_CO 6 (523959) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 b.9. BUSHLAND 6 (524267) 230.0 kV to DEAFSMITH 6 (524623) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_073 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G16-091-TAP (587744) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_074 | Single Phase Fault with Stuck Breaker on MINCO 7 345.00 (514801) 345 kV Bus a. Apply Fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.2. MINCO 7 (514801) 345.0 kV to NSUB345 (555234) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_075 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to GRACMNT7 (515800) 345.0 kV to GRCMNT11 (515801) 13.8 kV Three Winding #2 b.4. GRACMNT4 (515802) 138.0 kV to GRACMNT7 (515800) 345.0 kV to GRCMNT11 (515801) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_076 | Single Phase Fault with Stuck Breaker on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply Fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHOLM7 (511553) 345.0 kV to G16-037-TAP (560078) 345.0 kV Transmission Circuit #1 b.2. CHISHOLM7 (511553) 345.0 kV to GRAPEVINE (560035) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_077 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT7 (515800) 345.0 kV to G16-037-TAP (560078) 345.0 kV Transmission Circuit #1 b.2. GRACMNT4 (515802) 138.0 kV to GRACMNT7 (515800) 345.0 kV to GRCMNT11 (515801) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_079 | Single Phase Fault with Stuck Breaker on TOLK 7345.00 (525549) 345 kV Bus a. Apply Fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROOSEVELT 6 (524909) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #1 b.2. ROOSEVELT 6 (524909) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #2 b.3. PLANT_X 6 (525481) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #1 b.4. PLANT_X 6 (525481) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #2 b.5. TOLK 6 (525531) 230.0 kV to NEEDMORE 6 (525586) 230.0 kV Transmission Circuit #1 b.6. TOLK 6 (525531) 230.0 kV to LAMB_CNTY 6 (525637) 230.0 kV Transmission Circuit #1 b.7. TOLK 6 (525531) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.8. TOLK 6 (525531) 230.0 kV to GEN-2017-158 (762132) 230.0 kV Transmission Circuit #1 b.9. TOLK 6 (525531) 230.0 kV to GEN-2018-097 (763241) 230.0 kV Transmission Circuit #1 b.10. TOLK 6 (525531) 230.0 kV to TOLK_1 1 (525561) 24.0 kV Two Winding #1 b.11. TOLK 6 (525531) 230.0 kV to TOLK_2 1 (525562) 24.0 kV Two Winding #1 b.12. TOLK 6 (525531) 230.0 kV to TOLK 7 (525549) 345.0 kV to TOLK_TF3 (525539) 13.2 kV Three Winding #3 b.13. TOLK 6 (525531) 230.0 kV to TOLK 7 (525549) 345.0 kV to TOLK_TF2 (525538) 13.2 kV Three Winding #2 b.14. TOLK 6 (525531) 230.0 kV to TOLK 7 (525549) 345.0 kV to TOLK_TR 1 (525537) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_080 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to CRAWFISH_DR (560022) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 b.3. BORDER 7 (515458) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_082 | Single Phase Fault with Stuck Breaker on G17-151TAP 345.00 (762216) 345 kV Bus a. Apply Fault at the G17-151TAP 345.00 (762216) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAWFISH_DR (560022) 345.0 kV to G17-151TAP (762216) 345.0 kV Transmission Circuit #1 b.2. G17-151TAP (762216) 345.0 kV to GEN-2017-151 (762217) 345.0 kV Transmission Circuit #1 b.3. G17-151TAP (762216) 345.0 kV to G18-015-TAP (762467) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_083 | Single Phase Fault with Stuck Breaker on WWDBORDT 345.00 (755000) 345 kV Bus a. Apply Fault at the WWDBORDT 345.00 (755000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHOLM7 (511553) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 b.3. BORDER 7 (515458) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Local_Fault_084 | Single Phase Fault with Stuck Breaker on SWISHER 6230.00 (525213) 230 kV Bus a. Apply Fault at the SWISHER 6230.00 (525213) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AMA_SOUTH 6 (524415) 230.0 kV to SWISHER 6 (525213) 230.0 kV Transmission Circuit #1 b.2. SWISHER 6 (525213) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 b.3. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.4. SWISHER 6 (525213) 230.0 kV to SWISHER 3 (525212) 115.0 kV to SWISHER_TR11 (525211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Regional_Fault_001 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Regional_Fault_002 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Regional_Fault_003 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Regional_Fault_004 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Regional_Fault_005 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Regional_Fault_006 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Regional_Fault_007 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Regional_Fault_008 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Regional_Fault_009 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Regional_Fault_010 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Regional_Fault_011 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Regional_Fault_012 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Regional_Fault_013 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Regional_Fault_014 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Regional_Fault_015 | Single Phase Fault with Stuck Breaker on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply Fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. NOVUS_WND 1 (523107) 4.2 kV to NOVUS1 1 (523109) 34.5 kV Two Winding #1 b.3. NOVUS1 1 (523109) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.4. G06-44-2 (560581) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.5. NOVUS1 3 (523111) 115.0 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV Three Winding #1 b.6. NOVUS1_TR1 1 (523110) 13.8 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Regional_Fault_016 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Regional_Fault_017 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to CRAWFISH_DR (560022) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 b.3. BORDER 7 (515458) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Regional_Fault_018 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Regional_Fault_019 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.4. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Regional_Fault_020 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.4. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Regional_Fault_021 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #1 b.5. FTSMTHW5 (515301) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Regional_Fault_022 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #2 b.5. FTSMTHW5 (515301) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Regional_Fault_023 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 b.4. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Regional_Fault_024 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 b.4. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Regional_Fault_025 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 b.4. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Regional_Fault_026 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Regional_Fault_027 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 b.4. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Regional_Fault_028 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Regional_Fault_029 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Regional_Fault_030 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Regional_Fault_031 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25W | Transfer | P4_Regional_Fault_032 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.3. G18-128-TAP (763421) 345.0 kV to None Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 25S | Base | P1_Local_Fault_060 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25S | Base | P1_Local_Fault_061 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25S | Base | P1_Local_Fault_075 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25S | Base | P1_Local_Fault_076 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25S | Base | P1_Local_Fault_078 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to GUTHRIE7 (515961) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25S | Base | P1_Local_Fault_086 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV31 (515795) 13.8 kV Three Winding #1 | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25S | Base | P1_Local_Fault_087 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25S | Base | P1_Local_Fault_121 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BVRCNTY7 (515554) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25S | Base | P1_Local_Fault_122 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25S | Base | P1_Local_Fault_123 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25S | Base | P1_Local_Fault_124 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25S | Base | P1_Regional_Fault_022 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BVRCNTY7 (515554) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25S | Base | P1_Regional_Fault_023 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25S | Base | P1_Regional_Fault_024 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25W | Base | P1_Local_Fault_060 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). The issue was also observed in the base case. | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25W | Base | P1_Local_Fault_061 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). The issue was also observed in the base case. | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25W | Base | P1_Local_Fault_075 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25W | Base | P1_Local_Fault_076 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25W | Base | P1_Local_Fault_078 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to GUTHRIE7 (515961) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25W | Base | P1_Local_Fault_086 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV31 (515795) 13.8 kV Three Winding #1 | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25W | Base | P1_Local_Fault_087 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25W | Base | P1_Local_Fault_121 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BVRCNTY7 (515554) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25W | Base | P1_Local_Fault_122 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25W | Base | P1_Local_Fault_123 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25W | Base | P1_Local_Fault_124 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25W | Base | P1_Regional_Fault_022 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BVRCNTY7 (515554) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25W | Base | P1_Regional_Fault_023 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). | Reduce clearing time to 3 cycles
04 SOUTHEAST | 25W | Base | P1_Regional_Fault_024 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | Out of Step conditions observed in COWBOY_RIDGE (585423, 585426) and PRSIMN_CRK (585443, 585446). | Reduce clearing time to 3 cycles

## Short Circuit Analysis
Gen Number | Group | Bus Number | Bus Name | Bus Voltage (kV) | Request Not In Service 25SP Fault Current 3-Phase (kA) | Request In Service 25SP Fault Current 3-Phase (kA) | Change in Fault Current (kA) | Circuit Breakers Exceeding Capacity | Facilities Required to Interconnect
GEN-2016-037 | 04 SOUTHEAST | 511421 | VERDEN 4 | 138 | 10.1951 | 10.2014 | 0.0063
GEN-2016-037 | 04 SOUTHEAST | 511422 | FLETCHR4 | 138 | 8.2656 | 8.271 | 0.0054
GEN-2016-037 | 04 SOUTHEAST | 511423 | FLE TAP4 | 138 | 9.0385 | 9.0449 | 0.0064
GEN-2016-037 | 04 SOUTHEAST | 511424 | T-CONCO4 | 138 | 6.9495 | 6.9507 | 0.0012
GEN-2016-037 | 04 SOUTHEAST | 511425 | TUTCONT4 | 138 | 10.48 | 10.4829 | 0.0029
GEN-2016-037 | 04 SOUTHEAST | 511431 | LWS S4 | 138 | 11.4065 | 11.4178 | 0.0113
GEN-2016-037 | 04 SOUTHEAST | 511437 | COMANC-4 | 138 | 18.5052 | 18.5318 | 0.0266
GEN-2016-037 | 04 SOUTHEAST | 511439 | LWSTAP 4 | 138 | 11.8867 | 11.8989 | 0.0122
GEN-2016-037 | 04 SOUTHEAST | 511442 | BINGER-2 | 69 | 1.8357 | 1.8358 | 0.0001
GEN-2016-037 | 04 SOUTHEAST | 511443 | BING-TP2 | 69 | 2.7966 | 2.7969 | 0.0003
GEN-2016-037 | 04 SOUTHEAST | 511445 | CARNEG-4 | 138 | 8.1189 | 8.1252 | 0.0063
GEN-2016-037 | 04 SOUTHEAST | 511446 | CL-AFTP4 | 138 | 6.5623 | 6.5744 | 0.0121
GEN-2016-037 | 04 SOUTHEAST | 511456 | O.K.U.-7 | 345 | 5.3802 | 5.3853 | 0.0051
GEN-2016-037 | 04 SOUTHEAST | 511458 | ELKCTY-4 | 138 | 11.0526 | 11.1012 | 0.0486
GEN-2016-037 | 04 SOUTHEAST | 511459 | ELKCTY-2 | 69 | 7.1831 | 7.1918 | 0.0087
GEN-2016-037 | 04 SOUTHEAST | 511466 | L.E.S.-2 | 69 | 16.9402 | 16.9511 | 0.0109
GEN-2016-037 | 04 SOUTHEAST | 511467 | L.E.S.-4 | 138 | 24.9396 | 24.9952 | 0.0556
GEN-2016-037 | 04 SOUTHEAST | 511468 | L.E.S.-7 | 345 | 13.3611 | 13.4152 | 0.0541
GEN-2016-037 | 04 SOUTHEAST | 511470 | LGORE-S2 | 69 | 7.2015 | 7.2034 | 0.0019
GEN-2016-037 | 04 SOUTHEAST | 511474 | SHERID4 | 138 | 12.6716 | 12.6857 | 0.0141
GEN-2016-037 | 04 SOUTHEAST | 511476 | S.W.S.-2 | 69 | 4.4199 | 4.4206 | 0.0007
GEN-2016-037 | 04 SOUTHEAST | 511477 | S.W.S.-4 | 138 | 34.3219 | 34.408 | 0.0861
GEN-2016-037 | 04 SOUTHEAST | 511483 | NORGE--4 | 138 | 11.6164 | 11.6232 | 0.0068
GEN-2016-037 | 04 SOUTHEAST | 511485 | CLINTJC4 | 138 | 6.3307 | 6.3382 | 0.0075
GEN-2016-037 | 04 SOUTHEAST | 511486 | ELGINJT4 | 138 | 10.3548 | 10.3634 | 0.0086
GEN-2016-037 | 04 SOUTHEAST | 511490 | ELKCITY6 | 230 | 6.9015 | 6.9533 | 0.0518
GEN-2016-037 | 04 SOUTHEAST | 511494 | COMMTAP4 | 138 | 21.8871 | 21.9287 | 0.0416
GEN-2016-037 | 04 SOUTHEAST | 511503 | LAW WC2 | 69 | 4.7216 | 4.7224 | 0.0008
GEN-2016-037 | 04 SOUTHEAST | 511511 | FALCNRD4 | 138 | 7.8544 | 7.8784 | 0.024
GEN-2016-037 | 04 SOUTHEAST | 511531 | HAMJCT 2 | 69 | 1.8637 | 1.8643 | 0.0006
GEN-2016-037 | 04 SOUTHEAST | 511535 | CLIN-AF4 | 138 | 4.9898 | 4.9968 | 0.007
GEN-2016-037 | 04 SOUTHEAST | 511541 | SWEETWT6 | 230 | 7.8352 | 7.91 | 0.0748
GEN-2016-037 | 04 SOUTHEAST | 511542 | BUFFCK6 | 230 | 5.9612 | 6.0033 | 0.0421
GEN-2016-037 | 04 SOUTHEAST | 511544 | DEMPSEY6 | 230 | 4.8987 | 4.9263 | 0.0276
GEN-2016-037 | 04 SOUTHEAST | 511547 | ROARK6 | 230 | 4.5959 | 4.6199 | 0.024
GEN-2016-037 | 04 SOUTHEAST | 511553 | CHISHOLM7 | 345 | 7.4339 | 7.6551 | 0.2212
GEN-2016-037 | 04 SOUTHEAST | 511557 | CHISHOLM6 | 230 | 9.6833 | 9.8419 | 0.1586
GEN-2016-037 | 04 SOUTHEAST | 511563 | ELSWORTH 4 | 138 | 10.2812 | 10.2897 | 0.0085
GEN-2016-037 | 04 SOUTHEAST | 511565 | OKLAUN HVDC7 | 345 | 5.3652 | 5.3703 | 0.0051
GEN-2016-037 | 04 SOUTHEAST | 511568 | TERRYRD7 | 345 | 10.0877 | 10.1049 | 0.0172
GEN-2016-037 | 04 SOUTHEAST | 511571 | RUSHSPR7 | 345 | 6.5487 | 6.5551 | 0.0064
GEN-2016-037 | 04 SOUTHEAST | 511576 | CEMRD_TP4 | 138 | 6.9893 | 6.9906 | 0.0013
GEN-2016-037 | 04 SOUTHEAST | 514785 | WOODWRD4 | 138 | 13.4724 | 13.4735 | 0.0011
GEN-2016-037 | 04 SOUTHEAST | 514796 | IODINE-4 | 138 | 7.5826 | 7.583 | 0.0004
GEN-2016-037 | 04 SOUTHEAST | 514801 | MINCO 7 | 345 | 22.4885 | 22.607 | 0.1185
GEN-2016-037 | 04 SOUTHEAST | 514819 | EL-RENO4 | 138 | 16.0703 | 16.0753 | 0.005
GEN-2016-037 | 04 SOUTHEAST | 514820 | JENSENT4 | 138 | 15.873 | 15.8783 | 0.0053
GEN-2016-037 | 04 SOUTHEAST | 514863 | HAYMAKR4 | 138 | 27.5791 | 27.5888 | 0.0097
GEN-2016-037 | 04 SOUTHEAST | 514879 | NORTWST4 | 138 | 45.8984 | 45.9202 | 0.0218
GEN-2016-037 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 33.0635 | 33.0958 | 0.0323
GEN-2016-037 | 04 SOUTHEAST | 514881 | SPRNGCK7 | 345 | 23.7814 | 23.7946 | 0.0132
GEN-2016-037 | 04 SOUTHEAST | 514894 | CZECHAL4 | 138 | 29.5774 | 29.5874 | 0.01
GEN-2016-037 | 04 SOUTHEAST | 514895 | SARA 4 | 138 | 20.016 | 20.0215 | 0.0055
GEN-2016-037 | 04 SOUTHEAST | 514898 | CIMARON4 | 138 | 45.1949 | 45.2294 | 0.0345
GEN-2016-037 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 34.1528 | 34.2171 | 0.0643
GEN-2016-037 | 04 SOUTHEAST | 514902 | MCCLAIN4 | 138 | 33.8418 | 33.8533 | 0.0115
GEN-2016-037 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 27.8254 | 27.8337 | 0.0083
GEN-2016-037 | 04 SOUTHEAST | 514929 | PLVALLY4 | 138 | 44.4697 | 44.4999 | 0.0302
GEN-2016-037 | 04 SOUTHEAST | 514933 | DRAPER 4 | 138 | 43.3918 | 43.4203 | 0.0285
GEN-2016-037 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 26.3394 | 26.3689 | 0.0295
GEN-2016-037 | 04 SOUTHEAST | 514953 | HOLLYWD4 | 138 | 36.7002 | 36.7202 | 0.02
GEN-2016-037 | 04 SOUTHEAST | 514957 | CHERYCK4 | 138 | 22.8368 | 22.8448 | 0.008
GEN-2016-037 | 04 SOUTHEAST | 514992 | TURNER 4 | 138 | 31.9939 | 32.0081 | 0.0142
GEN-2016-037 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 31.3985 | 31.4142 | 0.0157
GEN-2016-037 | 04 SOUTHEAST | 515363 | CENT 4 | 138 | 3.2296 | 3.2296 | 0
GEN-2016-037 | 04 SOUTHEAST | 515375 | WWRDEHV7 | 345 | 19.1167 | 19.1236 | 0.0069
GEN-2016-037 | 04 SOUTHEAST | 515376 | WWRDEHV4 | 138 | 24.4174 | 24.4215 | 0.0041
GEN-2016-037 | 04 SOUTHEAST | 515394 | KEENAN 4 | 138 | 9.1846 | 9.1851 | 0.0005
GEN-2016-037 | 04 SOUTHEAST | 515398 | OUSPRT 4 | 138 | 9.7609 | 9.7615 | 0.0006
GEN-2016-037 | 04 SOUTHEAST | 515407 | TATONGA7 | 345 | 17.2217 | 17.2288 | 0.0071
GEN-2016-037 | 04 SOUTHEAST | 515425 | WWDPST 4 | 138 | 17.9283 | 17.9304 | 0.0021
GEN-2016-037 | 04 SOUTHEAST | 515444 | MCNOWND7 | 345 | 22.4049 | 22.5225 | 0.1176
GEN-2016-037 | 04 SOUTHEAST | 515448 | CRSRDSW7 | 345 | 12.1725 | 12.1759 | 0.0034
GEN-2016-037 | 04 SOUTHEAST | 515458 | BORDER 7 | 345 | 4.6845 | 4.6848 | 0.0003
GEN-2016-037 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 32.799 | 32.8389 | 0.0399
GEN-2016-037 | 04 SOUTHEAST | 515549 | MNCWND37 | 345 | 14.1428 | 14.1873 | 0.0445
GEN-2016-037 | 04 SOUTHEAST | 515554 | BVRCNTY7 | 345 | 13.0664 | 13.0717 | 0.0053
GEN-2016-037 | 04 SOUTHEAST | 515582 | SLNGWND7 | 345 | 8.6252 | 8.6268 | 0.0016
GEN-2016-037 | 04 SOUTHEAST | 515585 | MAMTHPW7 | 345 | 13.5141 | 13.5184 | 0.0043
GEN-2016-037 | 04 SOUTHEAST | 515590 | PALDR2W7 | 345 | 11.3349 | 11.3389 | 0.004
GEN-2016-037 | 04 SOUTHEAST | 515599 | G07621119-20 | 345 | 12.4376 | 12.4404 | 0.0028
GEN-2016-037 | 04 SOUTHEAST | 515600 | KNGFSHR7 | 345 | 10.9272 | 10.9331 | 0.0059
GEN-2016-037 | 04 SOUTHEAST | 515605 | CANADN7 | 345 | 11.9534 | 11.9605 | 0.0071
GEN-2016-037 | 04 SOUTHEAST | 515610 | FSHRTAP7 | 345 | 16.4668 | 16.4807 | 0.0139
GEN-2016-037 | 04 SOUTHEAST | 515618 | BALKOW 7 | 345 | 11.1352 | 11.1391 | 0.0039
GEN-2016-037 | 04 SOUTHEAST | 515634 | PALDR1W7 | 345 | 9.8965 | 9.8995 | 0.003
GEN-2016-037 | 04 SOUTHEAST | 515677 | BADGER 7 | 345 | 11.9588 | 11.9628 | 0.004
GEN-2016-037 | 04 SOUTHEAST | 515800 | GRACMNT7 | 345 | 18.6801 | 18.978 | 0.2979
GEN-2016-037 | 04 SOUTHEAST | 515802 | GRACMNT4 | 138 | 34.5084 | 34.694 | 0.1856
GEN-2016-037 | 04 SOUTHEAST | 515852 | DGRASSE7 | 345 | 13.6845 | 13.6866 | 0.0021
GEN-2016-037 | 04 SOUTHEAST | 515853 | DGRASSE4 | 138 | 13.1722 | 13.1729 | 0.0007
GEN-2016-037 | 04 SOUTHEAST | 515864 | CMTRYRD4 | 138 | 6.7924 | 6.7936 | 0.0012
GEN-2016-037 | 04 SOUTHEAST | 515875 | REDNGTN7 | 345 | 16.877 | 16.8829 | 0.0059
GEN-2016-037 | 04 SOUTHEAST | 515877 | REDDIRT7 | 345 | 16.8729 | 16.8787 | 0.0058
GEN-2016-037 | 04 SOUTHEAST | 515939 | MNCWND47 | 345 | 10.0404 | 10.0619 | 0.0215
GEN-2016-037 | 04 SOUTHEAST | 515951 | PERSIMN7 | 345 | 10.4508 | 10.4528 | 0.002
GEN-2016-037 | 04 SOUTHEAST | 515961 | GUTHRIE7 | 345 | 11.9529 | 11.9556 | 0.0027
GEN-2016-037 | 04 SOUTHEAST | 515980 | MNCWND57 | 345 | 7.3502 | 7.3613 | 0.0111
GEN-2016-037 | 04 SOUTHEAST | 516106 | BOBCAT 7 | 345 | 14.0737 | 14.0778 | 0.0041
GEN-2016-037 | 04 SOUTHEAST | 516146 | 25MILE 7 | 345 | 10.307 | 10.3091 | 0.0021
GEN-2016-037 | 04 SOUTHEAST | 516159 | 25MILZ 7 | 345 | 10.297 | 10.2991 | 0.0021
GEN-2016-037 | 04 SOUTHEAST | 520422 | SEQUOYAHJ4 | 138 | 24.4068 | 24.4477 | 0.0409
GEN-2016-037 | 04 SOUTHEAST | 520440 | HARPER2 | 69 | 14.6381 | 14.6454 | 0.0073
GEN-2016-037 | 04 SOUTHEAST | 520472 | CHCKSHA4 | 138 | 8.6926 | 8.6967 | 0.0041
GEN-2016-037 | 04 SOUTHEAST | 520473 | CKSHATP4 | 138 | 11.2666 | 11.2736 | 0.007
GEN-2016-037 | 04 SOUTHEAST | 520496 | TUTTLE 4 | 138 | 5.968 | 5.9694 | 0.0014
GEN-2016-037 | 04 SOUTHEAST | 520508 | CLVJCTN2 | 69 | 3.5523 | 3.5527 | 0.0004
GEN-2016-037 | 04 SOUTHEAST | 520509 | CLVJCTS2 | 69 | 4.5062 | 4.5068 | 0.0006
GEN-2016-037 | 04 SOUTHEAST | 520512 | BC SW 4 | 138 | 5.8541 | 5.8558 | 0.0017
GEN-2016-037 | 04 SOUTHEAST | 520513 | BCV SW 4 | 138 | 5.3204 | 5.3221 | 0.0017
GEN-2016-037 | 04 SOUTHEAST | 520514 | BCVI_HVB | 138 | 6.7081 | 6.7107 | 0.0026
GEN-2016-037 | 04 SOUTHEAST | 520543 | PINERDG2 | 69 | 2.9006 | 2.9009 | 0.0003
GEN-2016-037 | 04 SOUTHEAST | 520547 | SEQOYAH4 | 138 | 19.5994 | 19.6257 | 0.0263
GEN-2016-037 | 04 SOUTHEAST | 520810 | ANADARK2 | 69 | 15.4779 | 15.486 | 0.0081
GEN-2016-037 | 04 SOUTHEAST | 520814 | ANADARK4 | 138 | 32.6765 | 32.7515 | 0.075
GEN-2016-037 | 04 SOUTHEAST | 520827 | BINGERJ4 | 138 | 8.1398 | 8.1472 | 0.0074
GEN-2016-037 | 04 SOUTHEAST | 520838 | CADDO 2 | 69 | 11.984 | 11.989 | 0.005
GEN-2016-037 | 04 SOUTHEAST | 520859 | COGAR 2 | 69 | 1.9283 | 1.9284 | 0.0001
GEN-2016-037 | 04 SOUTHEAST | 520912 | FLETCH-4 | 138 | 7.3335 | 7.3367 | 0.0032
GEN-2016-037 | 04 SOUTHEAST | 520923 | GEORGIA4 | 138 | 17.9685 | 17.9906 | 0.0221
GEN-2016-037 | 04 SOUTHEAST | 521010 | NIJECT 4 | 138 | 5.5387 | 5.5421 | 0.0034
GEN-2016-037 | 04 SOUTHEAST | 521017 | ONEY 4 | 138 | 11.449 | 11.4628 | 0.0138
GEN-2016-037 | 04 SOUTHEAST | 521024 | PARADSE4 | 138 | 5.5953 | 5.5973 | 0.002
GEN-2016-037 | 04 SOUTHEAST | 521027 | PINERTP2 | 69 | 5.0341 | 5.035 | 0.0009
GEN-2016-037 | 04 SOUTHEAST | 521031 | POCASET4 | 138 | 8.009 | 8.0122 | 0.0032
GEN-2016-037 | 04 SOUTHEAST | 521072 | TUTLETP4 | 138 | 6.9029 | 6.9048 | 0.0019
GEN-2016-037 | 04 SOUTHEAST | 521088 | WASHITA2 | 69 | 9.5199 | 9.5234 | 0.0035
GEN-2016-037 | 04 SOUTHEAST | 521089 | WASHITA4 | 138 | 30.7715 | 30.8645 | 0.093
GEN-2016-037 | 04 SOUTHEAST | 521103 | SLKHILLS 4 | 138 | 6.7286 | 6.7312 | 0.0026
GEN-2016-037 | 04 SOUTHEAST | 521116 | REDHLSW4 | 138 | 7.1267 | 7.1402 | 0.0135
GEN-2016-037 | 04 SOUTHEAST | 521117 | RHWIND 4 | 138 | 6.1102 | 6.1195 | 0.0093
GEN-2016-037 | 04 SOUTHEAST | 521129 | CHERRYRD 4 | 138 | 5.8509 | 5.8531 | 0.0022
GEN-2016-037 | 04 SOUTHEAST | 523095 | HITCHLAND 6 | 230 | 13.0214 | 13.0261 | 0.0047
GEN-2016-037 | 04 SOUTHEAST | 523097 | HITCHLAND 7 | 345 | 12.135 | 12.1413 | 0.0063
GEN-2016-037 | 04 SOUTHEAST | 523101 | NOBLE_WND 7 | 345 | 12.0948 | 12.101 | 0.0062
GEN-2016-037 | 04 SOUTHEAST | 523103 | NOBLE_WND 3 | 115 | 9.3225 | 9.3238 | 0.0013
GEN-2016-037 | 04 SOUTHEAST | 523111 | NOVUS1 3 | 115 | 6.613 | 6.6136 | 0.0006
GEN-2016-037 | 04 SOUTHEAST | 523112 | NOVUS1 7 | 345 | 11.9281 | 11.9342 | 0.0061
GEN-2016-037 | 04 SOUTHEAST | 523130 | GRPLNS-HV4-3 | 115 | 6.3637 | 6.3643 | 0.0006
GEN-2016-037 | 04 SOUTHEAST | 523131 | GRPLNS-HV2-3 | 115 | 8.5442 | 8.5453 | 0.0011
GEN-2016-037 | 04 SOUTHEAST | 523215 | GEN-2011-022 | 345 | 8.5321 | 8.5352 | 0.0031
GEN-2016-037 | 04 SOUTHEAST | 523323 | MCDWL_CREEK6 | 230 | 9.0923 | 9.0962 | 0.0039
GEN-2016-037 | 04 SOUTHEAST | 523777 | WHEELER 6 | 230 | 6.406 | 6.4439 | 0.0379
GEN-2016-037 | 04 SOUTHEAST | 523779 | STLN-DEMARC6 | 230 | 7.315 | 7.3758 | 0.0608
GEN-2016-037 | 04 SOUTHEAST | 523823 | CARPENTER 7 | 345 | 6.3439 | 6.3447 | 0.0008
GEN-2016-037 | 04 SOUTHEAST | 523869 | CHAN+TASCOS6 | 230 | 4.3817 | 4.3827 | 0.001
GEN-2016-037 | 04 SOUTHEAST | 523959 | POTTER_CO 6 | 230 | 21.5709 | 21.5974 | 0.0265
GEN-2016-037 | 04 SOUTHEAST | 523961 | POTTER_CO 7 | 345 | 9.3545 | 9.3809 | 0.0264
GEN-2016-037 | 04 SOUTHEAST | 523979 | HARRNG_EST 6 | 230 | 26.6121 | 26.6382 | 0.0261
GEN-2016-037 | 04 SOUTHEAST | 524010 | ROLLHILLS 6 | 230 | 20.0088 | 20.0267 | 0.0179
GEN-2016-037 | 04 SOUTHEAST | 524267 | BUSHLAND 6 | 230 | 10.3196 | 10.3233 | 0.0037
GEN-2016-037 | 04 SOUTHEAST | 524276 | WILDOR_WND 6 | 230 | 5.3992 | 5.4001 | 0.0009
GEN-2016-037 | 04 SOUTHEAST | 524290 | WILDOR2_JUS6 | 230 | 7.1672 | 7.1689 | 0.0017
GEN-2016-037 | 04 SOUTHEAST | 524296 | SPNSPUR_WND7 | 345 | 5.0016 | 5.0079 | 0.0063
GEN-2016-037 | 04 SOUTHEAST | 524299 | SPNSPUR_COL7 | 345 | 5.0016 | 5.0079 | 0.0063
GEN-2016-037 | 04 SOUTHEAST | 525461 | NEWHART 6 | 230 | 10.6745 | 10.6759 | 0.0014
GEN-2016-037 | 04 SOUTHEAST | 525531 | TOLK 6 | 230 | 26.0652 | 26.0664 | 0.0012
GEN-2016-037 | 04 SOUTHEAST | 525549 | TOLK 7 | 345 | 12.1064 | 12.1067 | 0.0003
GEN-2016-037 | 04 SOUTHEAST | 525832 | TUCO_INT 7 | 345 | 13.0225 | 13.0242 | 0.0017
GEN-2016-037 | 04 SOUTHEAST | 525850 | ELK_CT1 | 345 | 12.9155 | 12.9172 | 0.0017
GEN-2016-037 | 04 SOUTHEAST | 527598 | SAGA_NDCOL 7 | 345 | 7.2867 | 7.2868 | 0.0001
GEN-2016-037 | 04 SOUTHEAST | 527599 | SAGA_SDCOL 7 | 345 | 8.409 | 8.4091 | 0.0001
GEN-2016-037 | 04 SOUTHEAST | 527600 | SAGA_SMEAS 7 | 345 | 8.409 | 8.4091 | 0.0001
GEN-2016-037 | 04 SOUTHEAST | 527601 | SAGA_NCOL 7 | 345 | 7.2867 | 7.2868 | 0.0001
GEN-2016-037 | 04 SOUTHEAST | 527610 | SAGA_SCOL 7 | 345 | 8.409 | 8.4091 | 0.0001
GEN-2016-037 | 04 SOUTHEAST | 527654 | RSVLT_CC_W 7 | 345 | 7.7904 | 7.7904 | 0
GEN-2016-037 | 04 SOUTHEAST | 527655 | RSVLT_CC_E 7 | 345 | 8.6946 | 8.6946 | 0
GEN-2016-037 | 04 SOUTHEAST | 527656 | CROSSROADS 7 | 345 | 9.6827 | 9.6828 | 0.0001
GEN-2016-037 | 04 SOUTHEAST | 527666 | RSVLT_COL1 7 | 345 | 7.7904 | 7.7904 | 0
GEN-2016-037 | 04 SOUTHEAST | 527667 | RSVLT_COL2 7 | 345 | 7.7904 | 7.7904 | 0
GEN-2016-037 | 04 SOUTHEAST | 539801 | THISTLE7 | 345 | 14.9774 | 14.9785 | 0.0011
GEN-2016-037 | 04 SOUTHEAST | 555234 | NSUB345 | 345 | 27.0131 | 27.055 | 0.0419
GEN-2016-037 | 04 SOUTHEAST | 560022 | CRAWFISH_DR | 345 | 12.7672 | 12.7689 | 0.0017
GEN-2016-037 | 04 SOUTHEAST | 560035 | GRAPEVINE | 345 | 5.6831 | 5.7307 | 0.0476
GEN-2016-037 | 04 SOUTHEAST | 560078 | G16-037-TAP | 345 | 8.0313 | 8.593 | 0.5617
GEN-2016-037 | 04 SOUTHEAST | 560577 | G06-44 | 115 | 6.613 | 6.6136 | 0.0006
GEN-2016-037 | 04 SOUTHEAST | 563259 | GEN-2015-092 | 345 | 6.353 | 6.359 | 0.006
GEN-2016-037 | 04 SOUTHEAST | 563269 | GEN-2015-093 | 345 | 10.2192 | 10.3077 | 0.0885
GEN-2016-037 | 04 SOUTHEAST | 576395 | GEN-2010-014 | 345 | 8.5321 | 8.5352 | 0.0031
GEN-2016-037 | 04 SOUTHEAST | 576397 | G10014G11022 | 345 | 8.5321 | 8.5352 | 0.0031
GEN-2016-037 | 04 SOUTHEAST | 585300 | GEN-2015-095 | 138 | 13.0225 | 13.0233 | 0.0008
GEN-2016-037 | 04 SOUTHEAST | 585410 | GREAT_WESTRN | 345 | 9.3335 | 9.335 | 0.0015
GEN-2016-037 | 04 SOUTHEAST | 585420 | COWBOY_RIDGE | 345 | 7.4071 | 7.408 | 0.0009
GEN-2016-037 | 04 SOUTHEAST | 585430 | PRSIMN_CRK1 | 345 | 10.9773 | 10.9795 | 0.0022
GEN-2016-037 | 04 SOUTHEAST | 585440 | PRSIMN_CRK2 | 345 | 10.0914 | 10.0932 | 0.0018
GEN-2016-037 | 04 SOUTHEAST | 587230 | GEN-2016-037 | 345 | 7.6978 | 8.2612 | 0.5634
GEN-2016-037 | 04 SOUTHEAST | 587740 | GEN-2016-091 | 345 | 10.8518 | 10.9259 | 0.0741
GEN-2016-037 | 04 SOUTHEAST | 587744 | G16-091-TAP | 345 | 15.3644 | 15.5183 | 0.1539
GEN-2016-037 | 04 SOUTHEAST | 587770 | GEN-2016-095 | 345 | 11.1072 | 11.186 | 0.0788
GEN-2016-037 | 04 SOUTHEAST | 587790 | GEN-2016-097 | 138 | 9.3613 | 9.3676 | 0.0063
GEN-2016-037 | 04 SOUTHEAST | 587794 | G16-097-TAP | 138 | 11.5601 | 11.5698 | 0.0097
GEN-2016-037 | 04 SOUTHEAST | 588560 | GEN-2017-011 | 345 | 11.5973 | 11.6001 | 0.0028
GEN-2016-037 | 04 SOUTHEAST | 588630 | GEN-2017-018 | 345 | 14.9774 | 14.9785 | 0.0011
GEN-2016-037 | 04 SOUTHEAST | 588760 | GEN-2017-033 | 345 | 3.8448 | 3.8474 | 0.0026
GEN-2016-037 | 04 SOUTHEAST | 755000 | WWDBORDT | 345 | 5.1967 | 5.1972 | 0.0005
GEN-2016-037 | 04 SOUTHEAST | 760032 | GEN-2017-132 | 345 | 5.0362 | 5.0364 | 0.0002
GEN-2016-037 | 04 SOUTHEAST | 760938 | G17-171-TAP | 345 | 10.9188 | 10.9462 | 0.0274
GEN-2016-037 | 04 SOUTHEAST | 760939 | GEN-2017-171 | 345 | 10.857 | 10.8841 | 0.0271
GEN-2016-037 | 04 SOUTHEAST | 761125 | GEN-2017-152 | 138 | 4.2018 | 4.202 | 0.0002
GEN-2016-037 | 04 SOUTHEAST | 761229 | GEN-2017-150 | 345 | 21.7149 | 21.8253 | 0.1104
GEN-2016-037 | 04 SOUTHEAST | 761250 | GEN-2017-233 | 345 | 21.7557 | 21.8665 | 0.1108
GEN-2016-037 | 04 SOUTHEAST | 762132 | GEN-2017-158 | 230 | 11.9594 | 11.9596 | 0.0002
GEN-2016-037 | 04 SOUTHEAST | 762216 | G17-151TAP | 345 | 7.7045 | 7.7059 | 0.0014
GEN-2016-037 | 04 SOUTHEAST | 762217 | GEN-2017-151 | 345 | 5.6 | 5.6007 | 0.0007
GEN-2016-037 | 04 SOUTHEAST | 762834 | GEN-2018-049 | 345 | 6.6518 | 6.652 | 0.0002
GEN-2016-037 | 04 SOUTHEAST | 762900 | GEN-2018-055 | 345 | 4.4074 | 4.4103 | 0.0029
GEN-2016-037 | 04 SOUTHEAST | 763087 | GEN-2018-073 | 345 | 11.0808 | 11.0821 | 0.0013
GEN-2016-037 | 04 SOUTHEAST | 763186 | GEN-2018-089 | 230 | 10.3754 | 10.3768 | 0.0014
GEN-2016-037 | 04 SOUTHEAST | 763208 | GEN-2018-092 | 345 | 4.6396 | 4.6422 | 0.0026
GEN-2016-037 | 04 SOUTHEAST | 763215 | G18-092-TAP | 345 | 4.7998 | 4.8027 | 0.0029
GEN-2016-037 | 04 SOUTHEAST | 763241 | GEN-2018-097 | 230 | 20.9199 | 20.9207 | 0.0008
GEN-2016-037 | 04 SOUTHEAST | 763318 | GEN-2018-115 | 345 | 13.1123 | 13.1644 | 0.0521
GEN-2016-037 | 04 SOUTHEAST | 763340 | GEN-2018-117 | 230 | 7.7209 | 7.7936 | 0.0727
GEN-2016-037 | 04 SOUTHEAST | 763527 | GEN-2019-012 | 345 | 16.9128 | 16.9182 | 0.0054
GEN-2016-037 | 04 SOUTHEAST | 763538 | GEN-2019-013 | 230 | 3.4465 | 3.4602 | 0.0137
GEN-2016-037 | 04 SOUTHEAST | 763769 | GEN-2019-045 | 138 | 13.1722 | 13.1729 | 0.0007
GEN-2016-037 | 04 SOUTHEAST | 763835 | GEN-2019-052 | 345 | 32.9924 | 33.0524 | 0.06
GEN-2016-037 | 04 SOUTHEAST | 900001 | TRAVERSE3 | 345 | 7.226 | 7.2272 | 0.0012
GEN-2016-037 | 04 SOUTHEAST | 900002 | TRAVERSE-2 | 345 | 5.818 | 5.8187 | 0.0007
GEN-2016-037 | 04 SOUTHEAST | 900003 | TRAVERSE1 | 345 | 5.3943 | 5.3948 | 0.0005
GEN-2016-037 | 04 SOUTHEAST | 900004 | TRW2-TRW3 | 345 | 6.477 | 6.4779 | 0.0009
GEN-2016-037 | 04 SOUTHEAST | 914902 | G17-152_TAP | 138 | 33.0964 | 33.1074 | 0.011