## Executive Summary
Executive Summary: GEN-2016-121 Limited Operation System Impact Study
Interconnection Customer (GEN-2016-121) has requested a Limited Operation Interconnection System Impact Study under the Southwest Power Pool Open Access Transmission Tariff (OATT).
Results of this study determine whether there will be sufficient stability and reliability margin on the Transmission System with anticipated topology to accommodate Interconnection Requests for each Generating Facility at the Interconnection Customer’s requested In-Service Date.
This study evaluates Network Upgrades and Generating Facility exclusions at the time of service to determine the amount of Interconnection Capacity available to the interconnection customers listed under specific system conditions.
Once a GIA amendment to incorporate Limited Operation is effective, SPP and Transmission Owner will permit Interconnection Customer to operate the Generating Facilities under Limited Operation in accordance with the SPP study results.
Limited Operation
In accordance with Section 8.4.3 of the GIP, Availability of Limited Operation, SPP determines in the DISIS whether the full amount of interconnection capacity requested by the Interconnection Customers is available by the requested Commercial Operation Date (COD). SPP quantifies, within the “Requests” tab of the DISIS report, the amount of interconnection capacity available to Interconnection Customers prior to the in-service date of identified Network Upgrades.
In accordance with GIA Article 5.9, Limited Operation, Interconnection Customers may request SPP to perform studies to determine the Limited Operation of each Generating Facility prior to the completion of the identified mitigation for the observed system constraint(s).
Limited Operation conditions and amounts permitted as determined in this study are detailed in the Seasonal LOIS Tab.
Study Limitations
The study has been performed excluding upgrades that are not expected to be in service by the request's COD (11/1/2026). SPP's 3Q 2024 Quarterly Project Tracking Report has been used to determine the upgrades meeting the criteria for exclusion. Additionally, based on the requested assumptions, the following upgrades have specifically been excluded from the models: - 39 MVAR Cap Bank at Border - 39 MVAR Cap Bank at Beckham - 200 MVAR (3x67 MVAR) Cap Bank at Oklaunion
Limited Operation Interconnection Service Available between April 1 - May 31 : 110 MW
Limited Operation Interconnection Service Available between June 1 - Sept 30 : 110 MW
Limited Operation Interconnection Service Available between Oct 1 - Nov 30 : 110 MW
Limited Operation Interconnection Service Available between Dec 1 - March 31 : 110 MW
In the event that an Interconnection Request, with queue priority equal to or higher than an Interconnection Request, which was excluded as a study scenario achieves a status of Commercial Operation prior to the in-service date of all required Network Upgrades, the results of this study revise to 0 MW of available Interconnection Service until a restudy is completed to identify a revised amount for this system condition.
In the event that a Network Upgrade which was included as a study scenario is not placed in-service prior to the Commercial Operation of Interconnection Requests, the results of this study revise to 0 MW of available Interconnection Service until a restudy is completed to identify a revised amount for this system condition.
SPP study results do not guarantee operation for all periods of time. Although studies analyzed many of the most probable contingencies, they are not an all‐inclusive list and cannot account for every operational situation. It is likely that the customer(s) may be required to reduce their generation output to 0 MW, also known as curtailment, under certain system conditions to allow system operators to maintain the reliability of the transmission network.
DISIS Manual Version 3.0
https://spp.org/documents/71111/DISIS%20Study%20Manual%2020240424.pdf
3Q 2024 Quraterly Tracking Report
3Q 2024 Quarterly Project Tracking Report
Models Used in Study
Power Flow Analysis: DISIS-2018-002 and DISIS-2019-001 Phase 2 (2021 ITP Series)* * modified to exclude network upgrades assigned through DISIS-1701, DISIS-1702 and DISIS-1801
Summer: 2023 (23SP), 2026 (26SP)
Winter: 2026 (26WP)
Stability Analysis: DISIS-2018-002/DISIS-2019-001 Phase 2 (P2) (2020 Series MDWG Dynamics)* * modified to exclude network upgrades assigned through DISIS-1701, DISIS-1702 and DISIS-1801
Summer: 2025 (25SP)
Winter: 2025 (25WP)
Short Circuit Analysis: DISIS-2018-002/DISIS-2019-001 Phase 2 (P2) (2020 Series MDWG Dynamics)
Summer: 2025 (25SP)
Author: SPP Generator Interconnection Department
Published: 2/27/2025

## Revision History
Revision History
Date | Author | Change Description
2025-02-10 | SPP | Initial Draft
2025-02-27 | SPP | Added details regarding study assumption in executive summary

## Requests
LOIS Amount
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | April 1 - May 31 | June 1 - Sept 30 | Oct 1 - Nov 30 | Dec 1 - March 31 | Reactive Compensation Requirement (MVAR) | Service | Area | POI | Status
GEN-2016-121 | 05 SOUTHWEST | 17 | DIS-16-2 | Solar | 110 | 110 | 110 | 110 | 110 |  | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-036 | 01 NORTH | 17 | DIS-16-2 | Wind | 44.6 | [5 empty] | ER | WAPA | Granite Falls 115kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-087 | 01 NORTH | 17 | DIS-16-2 | Wind | 98.9 | [5 empty] | ER | WAPA | Bismark-Glenham 230 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-094 | 01 NORTH | 17 | DIS-16-2 | Wind | 200 | [5 empty] | ER | WAPA | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-130 | 01 NORTH | 17 | DIS-16-2 | Wind | 202 | [5 empty] | ER | WAPA | Leland Olds 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-074 | 02 NEBRASKA | 17 | DIS-16-2 | Wind | 200 | [5 empty] | ER | NPPD | Sweetwater 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-147 | 02 NEBRASKA | 17 | DIS-16-2 | Solar | 40 | [5 empty] | ER | NPPD | Sidney 115 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-111 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [5 empty] | ER | WERE | Reno - Summit 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-115 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 300 | [5 empty] | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-149 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [5 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-150 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [5 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-153 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 134 | [5 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-160 | 03 CENTRAL | 17 | DIS-16-2 | Battery/Storage | 20 | [5 empty] | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-176 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [5 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-091 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 303.6 | [5 empty] | ER | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-095 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 200 | [5 empty] | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-097 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [5 empty] | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-102 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 150.9 | [5 empty] | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-118 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 288 | [5 empty] | ER | WFEC | Dover Switchyard 138 kV Line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-119 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 600 | [5 empty] | ER | OKGE | Spring Creek-Sooner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-126 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 172.5 | [5 empty] | ER/NR | OKGE | Arbuckle 138kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-128 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 176 | [5 empty] | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-131 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 2.5 | [5 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-132 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 6.1 | [5 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-133 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [5 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-134 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [5 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-137 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [5 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-138 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [5 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-139 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [5 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-141 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [5 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-142 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [5 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-145 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [5 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-146 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [5 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-167 | 04 SOUTHEAST | 17 | DIS-16-2 | Solar | 73.5 | [5 empty] | ER/NR | AEPW | Lieberman - North Benton 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-010 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 90 | [5 empty] | ER | SPS | TEXAS_CNTY 3 | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-177 | 05 SOUTHWEST | 17 | DIS-16-2 | Thermal: Gas Turbine | 17 | [5 empty] | ER | SPS | XTO-Cornell 115 kV station | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2017-006 | 03 CENTRAL | 16.5 | DIS-16-2-PQ | Wind | 238 | [5 empty] | ER/NR | AECI | 5MARYVL
GEN-2016-004 | 01 NORTH | 16 | DIS-16-1 | Wind | 202 | [5 empty] | ER/NR | WAPA | Basin Electric 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-021 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 298.47 | [5 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-043 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 230 | [5 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-050 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 250.7 | [5 empty] | ER | NPPD | Axtell â€“ Post Rock 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-075 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 50 | [5 empty] | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-009 | 03 CENTRAL | 16 | DIS-16-1 | Thermal: Steam Turbine | 29 | [5 empty] | ER | OKGE | Osage 69 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-046 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 299 | [5 empty] | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-036 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 303.6 | [5 empty] | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-003 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250.4 | [5 empty] | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-020 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 148.4 | [5 empty] | ER | WFEC | Moreland 138kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-030 | 04 SOUTHEAST | 16 | DIS-16-1 | Solar | 100 | [5 empty] | ER/NR | OKGE | Brown 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-031 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 1.5 | [5 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [5 empty] | ER/NR | OKGE | Crescent Substation 138 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-045 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [5 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-051 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 9.8 | [5 empty] | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-057 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [5 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-061 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250.7 | [5 empty] | ER | OKGE | Sooner-Woodring 345 kV line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-071 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200.1 | [5 empty] | ER | OKGE | Middleton Tap 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-004 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 10 | [5 empty] | ER | SPS | Palo Duro 115kV
GEN-2015-082 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 200 | [5 empty] | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-070 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 5.3 | [5 empty] | ER | SPS | Martin 115 kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-005NWE205 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.2 | [5 empty] | ER | WAPA | Tap White Lake - Stickeny 69kV
ASGI-2016-007NWE208 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.2 | [5 empty] | ER | WAPA | Kimball 69kV
GEN-2005-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 | [5 empty] | ER/NR | WAPA | Hilken 230kV [Ecklund 230kV]
GEN-2006-002IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 2 | [5 empty] | ER/NR | WAPA | Wessington Springs 230kV
GEN-2006-006IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 10 | [5 empty] | ER/NR | XEL | Marshall 115kV
GEN-2006-015IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 | [5 empty] | ER/NR | WAPA | Hilken 230kV [Ecklund 230kV]
GEN-2008-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 5 | [5 empty] | ER/NR | WAPA | Nelson 115kV
GEN-2009-018IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 | [5 empty] | ER | WAPA | Groton 115kV
GEN-2009-020AIS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.4 | [5 empty] | ER/NR | WAPA | Tripp Junction 115kV
GEN-2009-026IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 3.5 | [5 empty] | ER/NR | WAPA | Dickenson-Heskett 230kV
GEN-2014-006IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Gas | 11.72 | [5 empty] | ER/NR | BEPC | Williston 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
MPC02100 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.75 | [5 empty] | ER | OTP
GEN-2015-088 | 02 NEBRASKA | 15 | DIS-15-2 | Wind | 300 | [5 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-052 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 300 | [5 empty] | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-069 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 300 | [5 empty] | ER | WERE | Union Ridge 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-090 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 220 | [5 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-045 | 04 SOUTHEAST | 15 | DIS-15-2 | Battery/Storage | 20 | [5 empty] | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-047 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 300 | [5 empty] | ER | OKGE | Sooner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 200 | [5 empty] | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-062 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 4.5 | [5 empty] | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-063 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 300 | [5 empty] | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-066 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 248.4 | [5 empty] | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-023 | 02 NEBRASKA | 14 | DIS-15-1 | Wind | 300.7 | [5 empty] | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2015-001 | 03 CENTRAL | 14 | DIS-15-1 | Thermal | 6.13 | [5 empty] | ER | SUNC | Ninnescah 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-005 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 200.1 | [5 empty] | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-024 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 220 | [5 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-025 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 220 | [5 empty] | ER | WERE | Tap Thistle â€“ Wichita 345kV Dbl CKT | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 04 SOUTHEAST | 14 | DIS-15-1 | Solar | 120 | [5 empty] | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-032 | 02 NEBRASKA | 13 | DIS-14-2 | Wind | 10.2 | [5 empty] | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-025 | 03 CENTRAL | 13 | DIS-14-2 | Wind | 2.42 | [5 empty] | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-056 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 250 | [5 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-064 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 248.4 | [5 empty] | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-035 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 30 | [5 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-040 | 05 SOUTHWEST | 13 | DIS-14-2 | Wind | 320 | [5 empty] | ER | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-004 | 02 NEBRASKA | 12 | DIS-14-1 | Wind | 3.96 | [5 empty] | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-013 | 02 NEBRASKA | 12 | DIS-14-1 | Wind | 73.5 | [5 empty] | ER/NR | LES | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-001 | 03 CENTRAL | 12 | DIS-14-1 | Wind | 200.6 | [5 empty] | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-002 | 04 SOUTHEAST | 12 | DIS-14-1 | Wind | 10.5 | [5 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 04 SOUTHEAST | 12 | DIS-14-1 | Wind | 5.7 | [5 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-019 | 02 NEBRASKA | 11 | DIS-13-2 | Hybrid: Solar and Wind | 73.6 | [5 empty] | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2013-005 | 05 SOUTHWEST | 11 | DIS-13-2 | Wind | 1.65 | [5 empty] | ER | SPS | FE Clovis 115kV
GEN-2013-002 | 02 NEBRASKA | 10 | DIS-13-1 | Hybrid: Solar and Wind | 50.6 | [5 empty] | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-008 | 02 NEBRASKA | 10 | DIS-13-1 | Wind | 1.2 | [5 empty] | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-002 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 18.4 | [5 empty] | ER | SPS | FE Tucumcari 115kV
ASGI-2013-003 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 18.4 | [5 empty] | ER | SPS | FE Clovis 115kV
GEN-2012-024 | 03 CENTRAL | 9 | DIS-12-2 | Wind | 180 | [5 empty] | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-033 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 98.82 | [5 empty] | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-002 | 05 SOUTHWEST | 9 | DIS-12-2 | Wind | 18.15 | [5 empty] | ER | SPS | FE-Clovis Interchange 115kV
ASGI-2012-006 | 03 CENTRAL | 8 | DIS-12-1 | Steam | 21.25 | [5 empty] | ER | SUNC | Tap Hugoton - Rolla 69kV
GEN-2012-004 | 04 SOUTHEAST | 8 | DIS-12-1 | Wind | 40.8 | [5 empty] | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-037 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 6.6 | [5 empty] | ER | WFEC | Blue Canyon 5 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-054 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 300 | [5 empty] | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 175 | [5 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 165.6 | [5 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-022 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 299 | [5 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-040 | 04 SOUTHEAST | 5 | DIS-10-2 | Wind | 300 | [5 empty] | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-001 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 300 | [5 empty] | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-005 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 299.2 | [5 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-022 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 299.65 | [5 empty] | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-047 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 263.13 | [5 empty] | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-014 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 358.8 | [5 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | 02 NEBRASKA | 3 | DIS-09-1 | Wind | 201 | [5 empty] | ER | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-124 | 03 CENTRAL | 3 | DIS-09-1 | Wind | 200.1 | [5 empty] | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-051 | 05 SOUTHWEST | 3 | DIS-09-1 | Wind | 161 | [5 empty] | ER | SPS | Potter County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-021N | 02 NEBRASKA | 8 | PQ | Wind | 75 | [5 empty] | ER | NPPD | Ainsworth Wind Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
NPPDBUFFALOCOUNTYSOLAR | 02 NEBRASKA | 8 | PQ | Solar | 10 | [5 empty] | ER | NPPD | Kearney Northeast
NPPDBURTCOUNTYWIND | 02 NEBRASKA | 8 | PQ | Wind | 20 | [5 empty] | ER | NPPD | Tekamah & Oakland 115kV
GEN-2001-039M | 03 CENTRAL | 8 | PQ | Wind | 100 | [5 empty] | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-004 | 03 CENTRAL | 8 | PQ | Wind | 153 | [5 empty] | ER | WERE | Latham 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | 03 CENTRAL | 8 | PQ | Wind | 201 | [5 empty] | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-006GIA-27 | 04 SOUTHEAST | 8 | PQ | Wind | 150 | [5 empty] | ER | AECI | Remington 138kV
GEN-2006-002 | 04 SOUTHEAST | 8 | PQ | Wind | 100.8 | [5 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | 05 SOUTHWEST | 8 | PQ | Wind | 370 | [5 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-025 | 03 CENTRAL | 2 | ICS1 | Wind | 299.2 | [5 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-044 | 04 SOUTHEAST | 2 | ICS1 | Wind | 299.2 | [5 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION

## Seasonal LOIS
Generation Interconnection Number or Upgrade ID | Study Name | Assigned Study | Service Type | Point of Interconnection or Upgrade Name | MW Amount | Season | LOIS Granted | Limiting Element | Limiting Upgrade | ERIS 23SP | ERIS 26SP | ERIS 26L | ERIS 26WP | NRIS 23SP | NRIS 26SP | NRIS 26L | NRIS 26WP | Stability 25SP | Stability 25WP
GEN-2016-121 | GEN-2016-121 LOSIS | DISIS-2016-002 | ERIS | Oklaunion 345 kV sub | 110 | April 1 - May 31 | 110 | None | None | 110 | 110 | N/A | 110 | N/A | N/A | N/A | N/A | 110 | 110
GEN-2016-121 | GEN-2016-121 LOSIS | DISIS-2016-002 | ERIS | Oklaunion 345 kV sub | 110 | June 1 - Sept 30 | 110 | None | None | 110 | 110 | N/A | N/A | N/A | N/A | N/A | N/A | 110 | N/A
GEN-2016-121 | GEN-2016-121 LOSIS | DISIS-2016-002 | ERIS | Oklaunion 345 kV sub | 110 | Oct 1 - Nov 30 | 110 | None | None | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 110 | 110
GEN-2016-121 | GEN-2016-121 LOSIS | DISIS-2016-002 | ERIS | Oklaunion 345 kV sub | 110 | Dec 1 - March 31 | 110 | None | None | N/A | N/A | N/A | 110 | N/A | N/A | N/A | N/A | N/A | 110

## Constraints Summary
Group | Study Name | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name
05ALL | GEN-2016-121 LOSIS | ERIS | Voltage | None | 23SP, 26SP, 26WP | None | [7 empty] | None
05ALL | GEN-2016-121 LOSIS | ERIS | Thermal | None | 23SP, 26SP, 26WP | None | [7 empty] | None
05ALL | GEN-2016-121 LOSIS | ERIS | Stability | None | 25SP, 25WP | None | [7 empty] | None
05ALL | GEN-2016-121 LOSIS | ERIS | Non-Converge | None | 23SP, 26SP, 26WP | None | [7 empty] | None

## All Thermal
SOLUTIONTYPE | Study Name | GROUP | SCENARIO | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME | Constraint Violation Criteria | Upgrade Name
Non-Converge | GEN-2016-121 LOSIS | 05ALL | 0 | 26SP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | GEN-2016-121 LOSIS | 05ALL | 0 | 26WP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | GEN-2016-121 LOSIS | 05ALL | 0 | 23SP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Thermal | GEN-2016-121 LOSIS | 05ALL | 1 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2016-121 LOSIS | 05ALL | 1 | 26WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2016-121 LOSIS | 05ALL | 1 | 23SP | N/A | " | None |  |  |  |  | None |  | None

## All Voltage
SOLUTIONTYPE | Study Name | GROUP | SCENARIO | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME | Upgrade Name
Voltage | GEN-2016-121 LOSIS | 05ALL | 2 | 23SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2016-121 LOSIS | 05ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2016-121 LOSIS | 05ALL | 2 | 26WP | N/A | None | [7 empty] | None | None

## Stability Analysis Results
Group | Study Name | Season | Model Dispatch | Event ID | Event Description | Event Category | Rotor Angle Stability | Transient Voltage Response > 0.7 p.u. | Transient Voltage Response < 1.2 p.u. | Post Fault Steady State Voltage > 0.9 p.u. | Post Fault Steady State Voltage < 1.1 p.u. | Damping Factor > 0.8 % | Low Voltage Rides Through | Violation Summary | Primary Mitigation | Alternate Mitigation | Alternate Mitigation2 (Informational)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_001 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.2. TOLK 6 (525531) 230.0 kV to TOLK 7 (525549) 345.0 kV to TOLK_TR 1 (525537) 13.2 kV Three Winding #1 b.3. TOLK_TR 1 (525537) 13.2 kV to TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_002 | 3 Phase fault on FIESTA 3115.00 (528151) 115 kV Bus a. Apply fault at the FIESTA 3115.00 (528151) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIESTA 3 (528151) 115.0 kV to CARLSBAD 3 (528160) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_003 | 3 Phase fault on PCA 3115.00 (527930) 115 kV Bus a. Apply fault at the PCA 3115.00 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 (527930) 115.0 kV to POTASH_JCT 3 (527962) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_004 | 3 Phase fault on CARLSBAD 3115.00 (528160) 115 kV Bus a. Apply fault at the CARLSBAD 3115.00 (528160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLSBAD 3 (528160) 115.0 kV to PECOS 3 (528178) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_005 | 3 Phase fault on HOBBS_INT 3115.00 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3115.00 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 (527891) 115.0 kV to MADDOX 3 (528355) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_006 | 3 Phase fault on CUNNINHAM 3115.00 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3115.00 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 (527864) 115.0 kV to HOBBS_INT 3 (527891) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_007 | 3 Phase fault on MILLEN_TPW 3115.00 (528434) 115 kV Bus a. Apply fault at the MILLEN_TPW 3115.00 (528434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 (527891) 115.0 kV to MILLEN_TPW 3 (528434) 115.0 kV Transmission Circuit #1 b.2. TAYLOR 3 (528413) 115.0 kV to NE_HOBBS 3 (528442) 115.0 kV Transmission Circuit #1 b.3. MILLEN_TPW 3 (528434) 115.0 kV to MILLEN 3 (528435) 115.0 kV Transmission Circuit # b.4. MILLEN 3 (528435) 115.0 kV to MILLEN_TPE 3 (528436) 115.0 kV Transmission Circuit # b.5. MILLEN_TPE 3 (528436) 115.0 kV to NE_HOBBS 3 (528442) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_008 | 3 Phase fault on BENSING 3115.00 (528433) 115 kV Bus a. Apply fault at the BENSING 3115.00 (528433) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGG 3 (527363) 115.0 kV to BENSING 3 (528433) 115.0 kV Transmission Circuit #1 b.2. HOBBS_INT 3 (527891) 115.0 kV to BENSING 3 (528433) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_009 | 3 Phase fault on CUNNINHAM 3115.00 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3115.00 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 (527864) 115.0 kV to HOBBS_INT 3 (527891) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_010 | 3 Phase fault on POTASH_JCT 3115.00 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3115.00 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 (527962) 115.0 kV to CARLSBAD 3 (528160) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_011 | 3 Phase fault on PCA 3115.00 (527930) 115 kV Bus a. Apply fault at the PCA 3115.00 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 (527930) 115.0 kV to CARLSBAD 3 (528160) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_012 | 3 Phase fault on LEA_ROAD 3115.00 (528505) 115 kV Bus a. Apply fault at the LEA_ROAD 3115.00 (528505) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEA_ROAD 3 (528505) 115.0 kV to WARD 3 (528519) 115.0 kV Transmission Circuit #1 b.2. LEA_ROAD 3 (528505) 115.0 kV to OIL_CENTER 3 (528552) 115.0 kV Transmission Circuit #1 b.3. WARD 3 (528519) 115.0 kV to WHITTEN 3 (528540) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_013 | 3 Phase fault on SAND_DUNES 3115.00 (528016) 115 kV Bus a. Apply fault at the SAND_DUNES 3115.00 (528016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WIPP 3 (528009) 115.0 kV to SAND_DUNES 3 (528016) 115.0 kV Transmission Circuit #1 b.2. SAND_DUNES 3 (528016) 115.0 kV to RED_BLUFF 3 (528018) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_014 | 3 Phase fault on WOLFCAMP_TP3115.00 (528235) 115 kV Bus a. Apply fault at the WOLFCAMP_TP3115.00 (528235) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 (528013) 115.0 kV to BOPCO_PKRLK3 (528020) 115.0 kV Transmission Circuit #1 b.2. RED_BLUFF 3 (528018) 115.0 kV to WOLFCAMP_TP3 (528235) 115.0 kV Transmission Circuit #1 b.3. BOPCO_PKRLK3 (528020) 115.0 kV to WOLFCAMP_TP3 (528235) 115.0 kV Transmission Circuit #1 b.4. WOLFCAMP_TP3 (528235) 115.0 kV to WOLFCAMP 3 (528236) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_015 | 3 Phase fault on PHANTOM 3115.00 (528013) 115 kV Bus a. Apply fault at the PHANTOM 3115.00 (528013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 (528013) 115.0 kV to WOOD_DRAW 3 (528228) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_016 | 3 Phase fault on HOBBS_INT 3115.00 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3115.00 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 (527891) 115.0 kV to LE-WEST_SUB3 (528333) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_017 | 3 Phase fault on NORTH_LOVNG3115.00 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3115.00 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 (528182) 115.0 kV to HOPI_SUB 3 (528226) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_018 | 3 Phase fault on BLACKRIVER 3115.00 (528193) 115 kV Bus a. Apply fault at the BLACKRIVER 3115.00 (528193) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 (528182) 115.0 kV to BLACKRIVER 3 (528193) 115.0 kV Transmission Circuit #1 b.2. SENDERO +3 (528184) 115.0 kV to BLACKRIVER 3 (528193) 115.0 kV Transmission Circuit #1 b.3. SENDERO +3 (528184) 115.0 kV to BLCKRVR_DST3 (528206) 115.0 kV Transmission Circuit #1 b.4. BLCKRVR_DST3 (528206) 115.0 kV to CHINA_DRAW 3 (528222) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_019 | 3 Phase fault on XTO_BIGEDDY3115.00 (528396) 115 kV Bus a. Apply fault at the XTO_BIGEDDY3115.00 (528396) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 (527930) 115.0 kV to XTO_BIGEDDY3 (528396) 115.0 kV Transmission Circuit #1 b.2. QUAHADA 3 (528394) 115.0 kV to XTO_BIGEDDY3 (528396) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_020 | 3 Phase fault on RDRUNNER 3115.00 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3115.00 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 (528025) 115.0 kV to BATTLE_AXE 3 (528040) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_021 | 3 Phase fault on CUSTERMTN 3115.00 (528239) 115 kV Bus a. Apply fault at the CUSTERMTN 3115.00 (528239) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSTERMTN 3 (528239) 115.0 kV to PONDEROSA 3 (528240) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_022 | 3 Phase fault on CHINA_DRAW 3115.00 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3115.00 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 (528222) 115.0 kV to WOOD_DRAW 3 (528228) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_023 | 3 Phase fault on CHINA_DRAW 3115.00 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3115.00 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 (528222) 115.0 kV to CHVRN_EDDYS3 (528252) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_024 | 3 Phase fault on MEDANOS 3115.00 (527954) 115 kV Bus a. Apply fault at the MEDANOS 3115.00 (527954) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIVSTNRIDGE3 (527953) 115.0 kV to MEDANOS 3 (527954) 115.0 kV Transmission Circuit #1 b.2. MEDANOS 3 (527954) 115.0 kV to SAGE_BRUSH 3 (527955) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_025 | 3 Phase fault on RED_BLUFF 3115.00 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3115.00 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RED_BLUFF 3 (528018) 115.0 kV to RDRUNNER 3 (528025) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_026 | 3 Phase fault on AGAVE_RHILL3115.00 (528230) 115 kV Bus a. Apply fault at the AGAVE_RHILL3115.00 (528230) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 (528025) 115.0 kV to AGAVE_RHILL3 (528230) 115.0 kV Transmission Circuit #1 b.2. AGAVE_RHILL3 (528230) 115.0 kV to OCHOA 3 (528232) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_027 | 3 Phase fault on RDRUNNER 3115.00 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3115.00 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 (528025) 115.0 kV to CUSTERMTN 3 (528239) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_028 | 3 Phase fault on CUSTERMTN 3115.00 (528239) 115 kV Bus a. Apply fault at the CUSTERMTN 3115.00 (528239) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSTERMTN 3 (528239) 115.0 kV to WHITTEN 3 (528540) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_029 | 3 Phase fault on INTREPDW_TP3115.00 (527999) 115 kV Bus a. Apply fault at the INTREPDW_TP3115.00 (527999) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIVSTNRIDGE3 (527953) 115.0 kV to XTO_DI9_TP 3 (528064) 115.0 kV Transmission Circuit #1 b.2. POTASH_JCT 3 (527962) 115.0 kV to INTREPDW_TP3 (527999) 115.0 kV Transmission Circuit #1 b.3. INTREPDW_TP3 (527999) 115.0 kV to INTREPIDWST3 (528000) 115.0 kV Transmission Circuit #1 b.4. INTREPDW_TP3 (527999) 115.0 kV to IMC_#1_TP 3 (528035) 115.0 kV Transmission Circuit #1 b.5. IMC_#1_TP 3 (528035) 115.0 kV to IMC_#1 3 (528037) 115.0 kV Transmission Circuit #1 b.6. IMC_#1_TP 3 (528035) 115.0 kV to XTO_DI9_TP 3 (528064) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_030 | 3 Phase fault on LIVSTNRIDGE3115.00 (527953) 115 kV Bus a. Apply fault at the LIVSTNRIDGE3115.00 (527953) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIVSTNRIDGE3 (527953) 115.0 kV to WIPP 3 (528009) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_031 | 3 Phase fault on POTASH_JCT 3115.00 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3115.00 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 (527962) 115.0 kV to KIOWA 3 (527966) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_032 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to YOAKUM_345 (526936) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_033 | 3 Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 (526935) 230.0 kV to INK_BASIN 6 (527028) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_034 | 3 Phase fault on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_035 | 3 Phase fault on INK_BASIN 6230.00 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6230.00 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6 (527028) 230.0 kV to HOBBS_INT 6 (527894) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_036 | 3 Phase fault on CROSSROADS 7345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7345.00 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 (527656) 345.0 kV to EDDY_CNTY 7 (527802) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_037 | 3 Phase fault on EDDY_NORTH 6230.00 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6230.00 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 (527799) 230.0 kV to CUNNIGHM_N 6 (527865) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_038 | 3 Phase fault on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7 (527802) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_039 | 3 Phase fault on CUNNIGHM_N 6230.00 (527865) 230 kV Bus a. Apply fault at the CUNNIGHM_N 6230.00 (527865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_N 6 (527865) 230.0 kV to POTASH_JCT 6 (527963) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_040 | 3 Phase fault on CUNNIGHM_S 6230.00 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6230.00 (527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6 (527867) 230.0 kV to HOBBS_INT 6 (527894) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_041 | 3 Phase fault on HOBBS_INT 6230.00 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6230.00 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 6 (527894) 230.0 kV to ANDREWS 6 (528604) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_042 | 3 Phase fault on HOBBS_INT 7345.00 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7345.00 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 (527896) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_043 | 3 Phase fault on PCA 3115.00 (527930) 115 kV Bus a. Apply fault at the PCA 3115.00 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 (527930) 115.0 kV to CV-LUSK_TP 3 (527948) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_044 | 3 Phase fault on POTASH_JCT 269.000 (527961) 69 kV Bus a. Apply fault at the POTASH_JCT 269.000 (527961) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 2 (527961) 69.0 kV to DUVAL_#1 2 (527980) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_045 | 3 Phase fault on POTASH_JCT 269.000 (527961) 69 kV Bus a. Apply fault at the POTASH_JCT 269.000 (527961) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 2 (527961) 69.0 kV to KERMAC 2 (527996) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_046 | 3 Phase fault on POTASH_JCT 269.000 (527961) 69 kV Bus a. Apply fault at the POTASH_JCT 269.000 (527961) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 2 (527961) 69.0 kV to MISSCHEM#2 2 (528022) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_047 | 3 Phase fault on POTASH_JCT 269.000 (527961) 69 kV Bus a. Apply fault at the POTASH_JCT 269.000 (527961) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 2 (527961) 69.0 kV to NATPOT_TP 2 (528145) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_048 | 3 Phase fault on POTASH_JCT 6230.00 (527963) 230 kV Bus a. Apply fault at the POTASH_JCT 6230.00 (527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 6 (527963) 230.0 kV to PECOS 6 (528179) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_049 | 3 Phase fault on KIOWA 7345.00 (527965) 345 kV Bus a. Apply fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 (527965) 345.0 kV to RDRUNNER 7 (528027) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_050 | 3 Phase fault on KIOWA 7345.00 (527965) 345 kV Bus a. Apply fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 (527965) 345.0 kV to N_LOVING 7 (528185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_051 | 3 Phase fault on PHANTOM 3115.00 (528013) 115 kV Bus a. Apply fault at the PHANTOM 3115.00 (528013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 (528013) 115.0 kV to MALAGABEND 3 (528194) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_052 | 3 Phase fault on PHANTOM 7345.00 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7345.00 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 (528015) 345.0 kV to RDRUNNER 7 (528027) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_053 | 3 Phase fault on PHANTOM 7345.00 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7345.00 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 (528015) 345.0 kV to CHINA_DRAW 7 (528223) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_054 | 3 Phase fault on RR_SVC_HV 3115.00 (528024) 115 kV Bus a. Apply fault at the RR_SVC_HV 3115.00 (528024) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RR_SVC_HV 3 (528024) 115.0 kV to RDRUNNER 3 (528025) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_055 | 3 Phase fault on 7-RIVERS 6230.00 (528095) 230 kV Bus a. Apply fault at the 7-RIVERS 6230.00 (528095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 7-RIVERS 6 (528095) 230.0 kV to PECOS 6 (528179) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_056 | 3 Phase fault on NORTH_LOVNG3115.00 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3115.00 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 (528182) 115.0 kV to SOUTH_LOVNG3 (528192) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_057 | 3 Phase fault on NORTH_LOVNG3115.00 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3115.00 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 (528182) 115.0 kV to AGAVE_PDURO3 (528195) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_058 | 3 Phase fault on N_LOVING 7345.00 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7345.00 (528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N_LOVING 7 (528185) 345.0 kV to CHINA_DRAW 7 (528223) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_059 | 3 Phase fault on SOUTH_LOVNG3115.00 (528192) 115 kV Bus a. Apply fault at the SOUTH_LOVNG3115.00 (528192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOUTH_LOVNG3 (528192) 115.0 kV to MALAGABEND 3 (528194) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_060 | 3 Phase fault on CHINA_DRAW 3115.00 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3115.00 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 (528222) 115.0 kV to CD_SVC_HV 3 (528225) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_061 | 3 Phase fault on CUNNIGHM_N 6230.00 (527865) 230 kV Bus a. Apply fault at the CUNNIGHM_N 6230.00 (527865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_N 6 (527865) 230.0 kV to CUNNIGHM_S 6 (527867) 230.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_062 | 3 Phase fault on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 (526936) 345.0 kV to YOAKUM 6 (526935) 230.0 kV to YOAKUM_TR1 (526937) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_063 | 3 Phase fault on INK_BASIN 6230.00 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6230.00 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6 (527028) 230.0 kV to INK_BASIN 3 (527027) 115.0 kV to INKBASN_TR 1 (527026) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_064 | 3 Phase fault on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7 (527802) 345.0 kV to EDDY_NORTH 6 (527799) 230.0 kV to EDDY_TR 1 (527796) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_065 | 3 Phase fault on CUNNIGHM_S 6230.00 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6230.00 (527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6 (527867) 230.0 kV to CUNNINHAM 3 (527864) 115.0 kV to CUNNHM_TR1 1 (527863) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_066 | 3 Phase fault on HOBBS_INT 6230.00 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6230.00 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 6 (527894) 230.0 kV to HOBBS_INT 3 (527891) 115.0 kV to HOBBS_TR1 1 (527890) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_067 | 3 Phase fault on HOBBS_INT 6230.00 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6230.00 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 6 (527894) 230.0 kV to HOBBS_INT 3 (527891) 115.0 kV to HOBBS_TR2 1 (527889) 13.2 kV Three Winding #2 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_068 | 3 Phase fault on HOBBS_INT 7345.00 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7345.00 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 (527896) 345.0 kV to HOBBS_INT 6 (527894) 230.0 kV to HOBBS_TR3 1 (527895) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_069 | 3 Phase fault on PCA 3115.00 (527930) 115 kV Bus a. Apply fault at the PCA 3115.00 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 (527930) 115.0 kV to PCA 2 (527929) 69.0 kV to PCA_TR1 1 (527928) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_070 | 3 Phase fault on POTASH_JCT 3115.00 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3115.00 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 (527962) 115.0 kV to POTASH_JCT 2 (527961) 69.0 kV to POTASH_TR3 1 (527960) 13.2 kV Three Winding #2 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_071 | 3 Phase fault on POTASH_JCT 3115.00 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3115.00 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 (527962) 115.0 kV to POTASH_JCT 2 (527961) 69.0 kV to POTASH_TR2 1 (527959) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_072 | 3 Phase fault on POTASH_JCT 6230.00 (527963) 230 kV Bus a. Apply fault at the POTASH_JCT 6230.00 (527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 6 (527963) 230.0 kV to POTASH_JCT 3 (527962) 115.0 kV to POTASH_TR1 1 (527958) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_073 | 3 Phase fault on KIOWA 7345.00 (527965) 345 kV Bus a. Apply fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 (527965) 345.0 kV to KIOWA 3 (527966) 115.0 kV to KIOWA_TR1 1 (527964) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_074 | 3 Phase fault on PHANTOM 7345.00 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7345.00 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 (528015) 345.0 kV to PHANTOM 3 (528013) 115.0 kV to PHANTOM TR11 (528011) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_075 | 3 Phase fault on PHANTOM 7345.00 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7345.00 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 (528015) 345.0 kV to PHANTOM 3 (528013) 115.0 kV to PHANTOM TR21 (528012) 13.2 kV Three Winding #2 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_076 | 3 Phase fault on RDRUNNER 7345.00 (528027) 345 kV Bus a. Apply fault at the RDRUNNER 7345.00 (528027) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RDRUNNER 7 (528027) 345.0 kV to RDRUNNER 3 (528025) 115.0 kV to RDRNNER_TR11 (528023) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_077 | 3 Phase fault on CARLSBAD 3115.00 (528160) 115 kV Bus a. Apply fault at the CARLSBAD 3115.00 (528160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLSBAD 3 (528160) 115.0 kV to CARLSBAD 2 (528159) 69.0 kV to CRLSBAD_TR11 (528157) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_078 | 3 Phase fault on CARLSBAD 3115.00 (528160) 115 kV Bus a. Apply fault at the CARLSBAD 3115.00 (528160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLSBAD 3 (528160) 115.0 kV to CARLSBAD 2 (528159) 69.0 kV to CRLSBAD_TR21 (528158) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_079 | 3 Phase fault on PECOS 6230.00 (528179) 230 kV Bus a. Apply fault at the PECOS 6230.00 (528179) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECOS 6 (528179) 230.0 kV to PECOS 3 (528178) 115.0 kV to PECOS_TR1 1 (528176) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_080 | 3 Phase fault on N_LOVING 7345.00 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7345.00 (528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N_LOVING 7 (528185) 345.0 kV to NORTH_LOVNG3 (528182) 115.0 kV to N_LOVING TR1 (528186) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_081 | 3 Phase fault on CHINA_DRAW 7345.00 (528223) 345 kV Bus a. Apply fault at the CHINA_DRAW 7345.00 (528223) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHINA_DRAW 7 (528223) 345.0 kV to CHINA_DRAW 3 (528222) 115.0 kV to CHINA_DRAW 1 (528219) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_082 | 3 Phase fault on ANDREWS 6230.00 (528604) 230 kV Bus a. Apply fault at the ANDREWS 6230.00 (528604) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDREWS 6 (528604) 230.0 kV to ANDREWS 3 (528602) 115.0 kV to ANDREWS_TR21 (528600) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_083 | 3 Phase fault on ANDREWS 6230.00 (528604) 230 kV Bus a. Apply fault at the ANDREWS 6230.00 (528604) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDREWS 6 (528604) 230.0 kV to ANDREWS 3 (528602) 115.0 kV to ANDREWS_TR11 (528601) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_084 | 3 Phase fault on CROSSROADS 7345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7345.00 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 (527656) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_085 | 3 Phase fault on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7 (527802) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_086 | 3 Phase fault on LIVSTNRIDGE3115.00 (527953) 115 kV Bus a. Apply fault at the LIVSTNRIDGE3115.00 (527953) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIVSTNRIDGE3 (527953) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_087 | 3 Phase fault on POTASH_JCT 269.000 (527961) 69 kV Bus a. Apply fault at the POTASH_JCT 269.000 (527961) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 2 (527961) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_088 | 3 Phase fault on POTASH_JCT 3115.00 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3115.00 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 (527962) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_089 | 3 Phase fault on WIPP 3115.00 (528009) 115 kV Bus a. Apply fault at the WIPP 3115.00 (528009) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WIPP 3 (528009) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_090 | 3 Phase fault on RED_BLUFF 3115.00 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3115.00 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RED_BLUFF 3 (528018) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_091 | 3 Phase fault on CARLSBAD 3115.00 (528160) 115 kV Bus a. Apply fault at the CARLSBAD 3115.00 (528160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLSBAD 3 (528160) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_092 | 3 Phase fault on NORTH_LOVNG3115.00 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3115.00 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 (528182) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_093 | 3 Phase fault on N_LOVING 7345.00 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7345.00 (528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N_LOVING 7 (528185) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_094 | 3 Phase fault on MALAGABEND 3115.00 (528194) 115 kV Bus a. Apply fault at the MALAGABEND 3115.00 (528194) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALAGABEND 3 (528194) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_095 | 3 Phase fault on CHINA_DRAW 3115.00 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3115.00 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 (528222) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_096 | 3 Phase fault on WOOD_DRAW 3115.00 (528228) 115 kV Bus a. Apply fault at the WOOD_DRAW 3115.00 (528228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOOD_DRAW 3 (528228) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_LOCAL_FAULT_097 | 3 Phase fault on S_JAL 3115.00 (528547) 115 kV Bus a. Apply fault at the S_JAL 3115.00 (528547) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S_JAL 3 (528547) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_REGIONAL_FAULT_001 | 3 Phase fault on STLN-DEMARC6230.00 (523779) 230 kV Bus a. Apply fault at the STLN-DEMARC6230.00 (523779) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 (511541) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.2. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips LANOGSU1 (523812). | Protection disabled without any impact on stability.
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_REGIONAL_FAULT_002 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_REGIONAL_FAULT_003 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_REGIONAL_FAULT_004 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_REGIONAL_FAULT_005 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_REGIONAL_FAULT_006 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_REGIONAL_FAULT_007 | 3 Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips LANOGSU1 (523812). | Protection disabled without any impact on stability.
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_REGIONAL_FAULT_008 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_REGIONAL_FAULT_009 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to YOAKUM_345 (526936) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_REGIONAL_FAULT_010 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to CRAWFISH_DR (560022) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_REGIONAL_FAULT_011 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to CRAWFISH_DR (560022) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_REGIONAL_FAULT_012 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_REGIONAL_FAULT_013 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_REGIONAL_FAULT_014 | 3 Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6 (523777) 230.0 kV to WHEELER 3 (523776) 115.0 kV to WHEELER_TR11 (523774) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips LANOGSU1 (523812). | Protection disabled without any impact on stability.
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_REGIONAL_FAULT_015 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR2 1 (525825) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_REGIONAL_FAULT_016 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P1_REGIONAL_FAULT_017 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on PCA 3115.00 (527930) 115 kV Bus a. Apply Fault at the PCA 3115.00 (527930) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PCA 3 (527930) 115.0 kV to CV-LUSK_TP 3 (527948) 115.0 kV Transmission Circuit #1 b.2. PCA 3 (527930) 115.0 kV to POTASH_JCT 3 (527962) 115.0 kV Transmission Circuit #1 b.3. PCA 3 (527930) 115.0 kV to CARLSBAD 3 (528160) 115.0 kV Transmission Circuit #1 b.4. PCA 3 (527930) 115.0 kV to XTO_BIGEDDY3 (528396) 115.0 kV Transmission Circuit #1 b.5. PCA_TR1 1 (527928) 13.2 kV to PCA 3 (527930) 115.0 kV to PCA 2 (527929) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on KIOWA 7345.00 (527965) 345 kV Bus a. Apply Fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PCA 3 (527930) 115.0 kV to POTASH_JCT 3 (527962) 115.0 kV Transmission Circuit #1 b.2. POTASH_JCT 3 (527962) 115.0 kV to KIOWA 3 (527966) 115.0 kV Transmission Circuit #1 b.3. POTASH_JCT 3 (527962) 115.0 kV to INTREPDW_TP3 (527999) 115.0 kV Transmission Circuit #1 b.4. POTASH_JCT 3 (527962) 115.0 kV to CARLSBAD 3 (528160) 115.0 kV Transmission Circuit #1 b.5. POTASH_TR1 1 (527958) 13.2 kV to POTASH_JCT 6 (527963) 230.0 kV to POTASH_JCT 3 (527962) 115.0 kV Three Winding #1 b.6. POTASH_TR2 1 (527959) 13.2 kV to POTASH_JCT 3 (527962) 115.0 kV to POTASH_JCT 2 (527961) 69.0 kV Three Winding #1 b.7. POTASH_TR3 1 (527960) 13.2 kV to POTASH_JCT 3 (527962) 115.0 kV to POTASH_JCT 2 (527961) 69.0 kV Three Winding #2 b.10. POTASH_JCT 3 (527962) 115.0 kV to POTASH_JCT 6 (527963) 230.0 kV to POTASH_TR1 1 (527958) 13.2 kV Three Winding #1 b.11. KIOWA_TR1 1 (527964) 13.2 kV to KIOWA 7 (527965) 345.0 kV to KIOWA 3 (527966) 115.0 kV Three Winding #1 b.12. KIOWA 3 (527966) 115.0 kV to KIOWA 7 (527965) 345.0 kV to KIOWA_TR1 1 (527964) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on WHITTEN 3115.00 (528540) 115 kV Bus a. Apply Fault at the WHITTEN 3115.00 (528540) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CUSTERMTN 3 (528239) 115.0 kV to WHITTEN 3 (528540) 115.0 kV Transmission Circuit #1 b.2. WARD 3 (528519) 115.0 kV to WHITTEN 3 (528540) 115.0 kV Transmission Circuit #1 b.3. WHITTEN 3 (528540) 115.0 kV to S_JAL 3 (528547) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on POTASH_JCT 6230.00 (527963) 230 kV Bus a. Apply Fault at the POTASH_JCT 6230.00 (527963) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PCA 2 (527929) 69.0 kV to NATPOT_TP 2 (528145) 69.0 kV Transmission Circuit #1 b.2. PCA 3 (527930) 115.0 kV to POTASH_JCT 3 (527962) 115.0 kV Transmission Circuit #1 b.3. LIVSTNRIDGE3 (527953) 115.0 kV to XTO_DI9_TP 3 (528064) 115.0 kV Transmission Circuit #1 b.4. POTASH_JCT 2 (527961) 69.0 kV to DUVAL_#1 2 (527980) 69.0 kV Transmission Circuit #1 b.5. POTASH_JCT 2 (527961) 69.0 kV to KERMAC 2 (527996) 69.0 kV Transmission Circuit #1 b.6. POTASH_JCT 2 (527961) 69.0 kV to MISSCHEM#2 2 (528022) 69.0 kV Transmission Circuit #1 b.7. POTASH_JCT 2 (527961) 69.0 kV to NATPOT_TP 2 (528145) 69.0 kV Transmission Circuit #1 b.8. POTASH_JCT 3 (527962) 115.0 kV to KIOWA 3 (527966) 115.0 kV Transmission Circuit #1 b.9. POTASH_JCT 3 (527962) 115.0 kV to INTREPDW_TP3 (527999) 115.0 kV Transmission Circuit #1 b.10. POTASH_JCT 3 (527962) 115.0 kV to CARLSBAD 3 (528160) 115.0 kV Transmission Circuit #1 b.11. NMPOTASH 2 (527989) 69.0 kV to KERMAC 2 (527996) 69.0 kV Transmission Circuit #1 b.12. INTREPDW_TP3 (527999) 115.0 kV to INTREPIDWST3 (528000) 115.0 kV Transmission Circuit #1 b.13. INTREPDW_TP3 (527999) 115.0 kV to IMC_#1_TP 3 (528035) 115.0 kV Transmission Circuit #1 b.14. MISSCHEM#2 2 (528022) 69.0 kV to IMC_#2 2 (528029) 69.0 kV Transmission Circuit #1 b.15. IMC_#2 2 (528029) 69.0 kV to UNITEDSALT 2 (528043) 69.0 kV Transmission Circuit #1 b.16. IMC_#1_TP 3 (528035) 115.0 kV to IMC_#1 3 (528037) 115.0 kV Transmission Circuit #1 b.17. IMC_#1_TP 3 (528035) 115.0 kV to XTO_DI9_TP 3 (528064) 115.0 kV Transmission Circuit #1 b.18. UNITEDSALT 2 (528043) 69.0 kV to STRATA 2 (528046) 69.0 kV Transmission Circuit #1 b.19. STRATA 2 (528046) 69.0 kV to IMC_#3 2 (528062) 69.0 kV Transmission Circuit #1 b.20. DUVAL_#3 2 (528050) 69.0 kV to IMC_#4 2 (528056) 69.0 kV Transmission Circuit #1 b.21. DUVAL_#3 2 (528050) 69.0 kV to IMC_#3 2 (528062) 69.0 kV Transmission Circuit #1 b.22. XTO_DI9_TP 3 (528064) 115.0 kV to XTO_DI9 3 (528066) 115.0 kV Transmission Circuit #1 b.23. CARLSBAD 3 (528160) 115.0 kV to PECOS 3 (528178) 115.0 kV Transmission Circuit #1 b.24. POTASH_TR1 1 (527958) 13.2 kV to POTASH_JCT 6 (527963) 230.0 kV to POTASH_JCT 3 (527962) 115.0 kV Three Winding #1 b.25. POTASH_TR2 1 (527959) 13.2 kV to POTASH_JCT 3 (527962) 115.0 kV to POTASH_JCT 2 (527961) 69.0 kV Three Winding #1 b.26. POTASH_TR3 1 (527960) 13.2 kV to POTASH_JCT 3 (527962) 115.0 kV to POTASH_JCT 2 (527961) 69.0 kV Three Winding #2 b.27. POTASH_JCT 2 (527961) 69.0 kV to POTASH_JCT 3 (527962) 115.0 kV to POTASH_TR2 1 (527959) 13.2 kV Three Winding #1 b.28. POTASH_JCT 2 (527961) 69.0 kV to POTASH_JCT 3 (527962) 115.0 kV to POTASH_TR3 1 (527960) 13.2 kV Three Winding #2 b.31. POTASH_JCT 3 (527962) 115.0 kV to POTASH_JCT 6 (527963) 230.0 kV to POTASH_TR1 1 (527958) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on CARLSBAD 3115.00 (528160) 115 kV Bus a. Apply Fault at the CARLSBAD 3115.00 (528160) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PCA 3 (527930) 115.0 kV to CARLSBAD 3 (528160) 115.0 kV Transmission Circuit #1 b.2. POTASH_JCT 3 (527962) 115.0 kV to CARLSBAD 3 (528160) 115.0 kV Transmission Circuit #1 b.3. CARLSBAD 2 (528159) 69.0 kV to S_LOVING_TP2 (528190) 69.0 kV Transmission Circuit #1 b.4. CARLSBAD 3 (528160) 115.0 kV to PECOS 3 (528178) 115.0 kV Transmission Circuit #1 b.5. S_LOVING_TP2 (528190) 69.0 kV to CB_WTRFLDTP2 (528197) 69.0 kV Transmission Circuit #1 b.6. S_LOVING_TP2 (528190) 69.0 kV to NAVAMAL_TP 2 (528215) 69.0 kV Transmission Circuit #1 b.7. CB_WTRFLDTP2 (528197) 69.0 kV to CB_WTRFIELD2 (528204) 69.0 kV Transmission Circuit #1 b.8. CB_WTRFLDTP2 (528197) 69.0 kV to WHITES_CTY 2 (528211) 69.0 kV Transmission Circuit #1 b.9. CRLSBAD_TR11 (528157) 13.2 kV to CARLSBAD 3 (528160) 115.0 kV to CARLSBAD 2 (528159) 69.0 kV Three Winding #1 b.10. CRLSBAD_TR21 (528158) 13.2 kV to CARLSBAD 3 (528160) 115.0 kV to CARLSBAD 2 (528159) 69.0 kV Three Winding #2 b.11. CARLSBAD 2 (528159) 69.0 kV to CARLSBAD 3 (528160) 115.0 kV to CRLSBAD_TR11 (528157) 13.2 kV Three Winding #1 b.12. CARLSBAD 2 (528159) 69.0 kV to CARLSBAD 3 (528160) 115.0 kV to CRLSBAD_TR21 (528158) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on RED_BLUFF 3115.00 (528018) 115 kV Bus a. Apply Fault at the RED_BLUFF 3115.00 (528018) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHANTOM 3 (528013) 115.0 kV to BOPCO_PKRLK3 (528020) 115.0 kV Transmission Circuit #1 b.2. PHANTOM 3 (528013) 115.0 kV to WOOD_DRAW 3 (528228) 115.0 kV Transmission Circuit #1 b.3. SAND_DUNES 3 (528016) 115.0 kV to RED_BLUFF 3 (528018) 115.0 kV Transmission Circuit #1 b.4. RED_BLUFF 3 (528018) 115.0 kV to RDRUNNER 3 (528025) 115.0 kV Transmission Circuit #1 b.5. RED_BLUFF 3 (528018) 115.0 kV to WOLFCAMP_TP3 (528235) 115.0 kV Transmission Circuit #1 b.6. BOPCO_PKRLK3 (528020) 115.0 kV to WOLFCAMP_TP3 (528235) 115.0 kV Transmission Circuit #1 b.7. WOLFCAMP_TP3 (528235) 115.0 kV to WOLFCAMP 3 (528236) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on LEA_ROAD 3115.00 (528505) 115 kV Bus a. Apply Fault at the LEA_ROAD 3115.00 (528505) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEA_ROAD 1 (528504) 12.5 kV to LEA_ROAD 3 (528505) 115.0 kV Two Winding #1 b.2. LEA_ROAD 3 (528505) 115.0 kV to WARD 3 (528519) 115.0 kV Transmission Circuit #1 b.3. LEA_ROAD 3 (528505) 115.0 kV to OIL_CENTER 3 (528552) 115.0 kV Transmission Circuit #1 b.4. WARD 3 (528519) 115.0 kV to WHITTEN 3 (528540) 115.0 kV Transmission Circuit #1 b.5. OIL_CENTER 3 (528552) 115.0 kV to COOPER_RNCH3 (528554) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on RSVLT_CC_E 7345.00 (527655) 345 kV Bus a. Apply Fault at the RSVLT_CC_E 7345.00 (527655) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TOLK 7 (525549) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.2. SAGA_SCOL 7 (527610) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.3. RSVLT_GEN1 1 (527651) 0.7 kV to RSVLT_WIND11 (527658) 34.5 kV Two Winding #1 b.4. RSVLT_GEN2 1 (527652) 0.7 kV to RSVLT_WIND21 (527659) 34.5 kV Two Winding #1 b.5. MILO_WIND 1 (527653) 0.7 kV to MILO_CB (577120) 34.5 kV Two Winding #1 b.6. RSVLT_CC_W 7 (527654) 345.0 kV to RSVLT_CC_E 7 (527655) 345.0 kV Transmission Circuit #1 b.7. RSVLT_CC_W 7 (527654) 345.0 kV to RSVLT_COL1 7 (527666) 345.0 kV Transmission Circuit #1 b.8. RSVLT_CC_W 7 (527654) 345.0 kV to RSVLT_COL2 7 (527667) 345.0 kV Transmission Circuit #1 b.9. RSVLT_CC_E 7 (527655) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.10. CROSSROADS 7 (527656) 345.0 kV to EDDY_CNTY 7 (527802) 345.0 kV Transmission Circuit #1 b.11. CROSSROADS 7 (527656) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #ba b.12. CROSSROADS 7 (527656) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #lx b.13. MILO_WND (577121) 34.5 kV to RSVLT_CC_E 7 (527655) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply Fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROSSROADS 7 (527656) 345.0 kV to EDDY_CNTY 7 (527802) 345.0 kV Transmission Circuit #1 b.2. EDDY_CNTY 7 (527802) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.3. EDDY_TR 1 (527796) 13.2 kV to EDDY_CNTY 7 (527802) 345.0 kV to EDDY_NORTH 6 (527799) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on HOBBS_INT 7345.00 (527896) 345 kV Bus a. Apply Fault at the HOBBS_INT 7345.00 (527896) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOBBS_INT 7 (527896) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.2. HOBBS_TR3 1 (527895) 13.2 kV to HOBBS_INT 7 (527896) 345.0 kV to HOBBS_INT 6 (527894) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on N_LOVING 7345.00 (528185) 345 kV Bus a. Apply Fault at the N_LOVING 7345.00 (528185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KIOWA 7 (527965) 345.0 kV to N_LOVING 7 (528185) 345.0 kV Transmission Circuit #1 b.2. N_LOVING 7 (528185) 345.0 kV to CHINA_DRAW 7 (528223) 345.0 kV Transmission Circuit #1 b.3. NORTH_LOVNG3 (528182) 115.0 kV to N_LOVING 7 (528185) 345.0 kV to N_LOVING TR1 (528186) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply Fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to YOAKUM_345 (526936) 345.0 kV Transmission Circuit #1 b.2. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_345 (526936) 345.0 kV to GEN-2019-011 (763516) 345.0 kV Transmission Circuit #1 b.4. YOAKUM 6 (526935) 230.0 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM_TR1 (526937) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on CHINA_DRAW 7345.00 (528223) 345 kV Bus a. Apply Fault at the CHINA_DRAW 7345.00 (528223) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHANTOM 7 (528015) 345.0 kV to CHINA_DRAW 7 (528223) 345.0 kV Transmission Circuit #1 b.2. N_LOVING 7 (528185) 345.0 kV to CHINA_DRAW 7 (528223) 345.0 kV Transmission Circuit #1 b.3. CHINA_DRAW 1 (528219) 13.2 kV to CHINA_DRAW 7 (528223) 345.0 kV to CHINA_DRAW 3 (528222) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on RDRUNNER 7345.00 (528027) 345 kV Bus a. Apply Fault at the RDRUNNER 7345.00 (528027) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOBBS_INT 7 (527896) 345.0 kV to RDRUNNER 7 (528027) 345.0 kV Transmission Circuit #uc b.2. HOBBS_INT 7 (527896) 345.0 kV to RDRUNNER 7 (528027) 345.0 kV Transmission Circuit #xa b.3. KIOWA 7 (527965) 345.0 kV to RDRUNNER 7 (528027) 345.0 kV Transmission Circuit #1 b.4. PHANTOM 7 (528015) 345.0 kV to RDRUNNER 7 (528027) 345.0 kV Transmission Circuit #1 b.5. RDRNNER_TR11 (528023) 13.2 kV to RDRUNNER 7 (528027) 345.0 kV to RDRUNNER 3 (528025) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on PHANTOM 7345.00 (528015) 345 kV Bus a. Apply Fault at the PHANTOM 7345.00 (528015) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHANTOM 7 (528015) 345.0 kV to CHINA_DRAW 7 (528223) 345.0 kV Transmission Circuit #1 b.2. PHANTOM TR21 (528012) 13.2 kV to PHANTOM 7 (528015) 345.0 kV to PHANTOM 3 (528013) 115.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on PHANTOM 7345.00 (528015) 345 kV Bus a. Apply Fault at the PHANTOM 7345.00 (528015) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHANTOM 7 (528015) 345.0 kV to RDRUNNER 7 (528027) 345.0 kV Transmission Circuit #1 b.2. PHANTOM TR11 (528011) 13.2 kV to PHANTOM 7 (528015) 345.0 kV to PHANTOM 3 (528013) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on PHANTOM 7 (528015) 345 kV Bus a. Apply Fault at the PHANTOM 7 (528015) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHANTOM 7 (528015) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on PHANTOM 3 (528013) 115 kV Bus a. Apply Fault at the PHANTOM 3 (528013) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHANTOM 3 (528013) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on KIOWA 7 (527965) 345 kV Bus a. Apply Fault at the KIOWA 7 (527965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KIOWA 7 (527965) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on POTASH_JCT 3 (527962) 115 kV Bus a. Apply Fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POTASH_JCT 3 (527962) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on HOBBS_INT 7 (527896) 345 kV Bus a. Apply Fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOBBS_INT 7 (527896) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on HOBBS_INT 6 (527894) 115 kV Bus a. Apply Fault at the HOBBS_INT 6 (527894) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOBBS_INT 6 (527894) 230.0 kV to remove bus # | P4 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on RED_BLUFF 3 (528018) 115 kV Bus a. Apply Fault at the RED_BLUFF 3 (528018) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RED_BLUFF 3 (528018) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on WOLFCAMP_TP3 (528235) 115 kV Bus a. Apply Fault at the WOLFCAMP_TP3 (528235) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCAMP_TP3 (528235) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on WHITTEN 3 (528540) 115 kV Bus a. Apply Fault at the WHITTEN 3 (528540) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHITTEN 3 (528540) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on WIPP 3115.00 (528009) 115 kV Bus a. Apply Fault at the WIPP 3115.00 (528009) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WIPP 3 (528009) 115.0 kV to LIVSTNRIDGE3 (527953) 115.0 kV Transmission Circuit #1 b.2. WIPP 3 (528009) 115.0 kV to SAND_DUNES 3 (528016) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on PHANTOM 7345.00 (528015) 345 kV Bus a. Apply Fault at the PHANTOM 7345.00 (528015) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHANTOM 3 (528013) 115.0 kV to PHANTOM 7 (528015) 345.0 kV to PHANTOM TR11 (528011) 13.2 kV Three Winding #1 b.2. PHANTOM 3 (528013) 115.0 kV to PHANTOM 7 (528015) 345.0 kV to PHANTOM TR21 (528012) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on CUSTERMTN 3115.00 (528239) 115 kV Bus a. Apply Fault at the CUSTERMTN 3115.00 (528239) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CUSTERMTN 3 (528239) 115.0 kV to RDRUNNER 3 (528025) 115.0 kV Transmission Circuit #1 b.2. CUSTERMTN 3 (528239) 115.0 kV to WHITTEN 3 (528540) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on HOBBS_INT 7345.00 (527896) 345 kV Bus a. Apply Fault at the HOBBS_INT 7345.00 (527896) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOBBS_INT 7 (527896) 345.0 kV to YOAKUM_345 (526936) 345.0 kV Transmission Circuit #1 b.2. HOBBS_INT 7 (527896) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on POTASH_JCT 6230.00 (527963) 230 kV Bus a. Apply Fault at the POTASH_JCT 6230.00 (527963) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POTASH_JCT 6 (527963) 230.0 kV to CUNNIGHM_N 6 (527865) 230.0 kV Transmission Circuit #1 b.2. POTASH_JCT 6 (527963) 230.0 kV to POTASH_JCT 3 (527962) 115.0 kV to POTASH_TR1 1 (527958) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on KIOWA 7345.00 (527965) 345 kV Bus a. Apply Fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KIOWA 7 (527965) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.2. KIOWA 7 (527965) 345.0 kV to N_LOVING 7 (528185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on RDRUNNER 7345.00 (528027) 345 kV Bus a. Apply Fault at the RDRUNNER 7345.00 (528027) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RDRUNNER 7 (528027) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.2. RDRUNNER 7 (528027) 345.0 kV to PHANTOM 7 (528015) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on CHINA_DRAW 7345.00 (528223) 345 kV Bus a. Apply Fault at the CHINA_DRAW 7345.00 (528223) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHINA_DRAW 7 (528223) 345.0 kV to PHANTOM 7 (528015) 345.0 kV Transmission Circuit #1 b.2. CHINA_DRAW 7 (528223) 345.0 kV to N_LOVING 7 (528185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on RED_BLUFF 3115.00 (528018) 115 kV Bus a. Apply Fault at the RED_BLUFF 3115.00 (528018) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RED_BLUFF 3 (528018) 115.0 kV to RDRUNNER 3 (528025) 115.0 kV Transmission Circuit #1 b.2. RED_BLUFF 3 (528018) 115.0 kV to WOLFCAMP_TP3 (528235) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_SPS1 | Single Phase Fault with Stuck Breaker on CROSSROADS (527656) 345 kV Bus a. Apply Fault at the CROSSROADS (527656) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. EDDY_CNTY 7 (527802) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.2. TOLK 7 (525549) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.3. RSVLT_CC_E 7 (527655) 345.0 kV to Trip Bus # b.4. MILO_WIND 1 (527653) 0.7 kV to Trip Bus # b.5. RSVLT_GEN1 1 (527651) 0.7 kV to Trip Bus # b.6. RSVLT_GEN2 1 (527652) 0.7 kV to Trip Bus # b.7. RSVLT_CC_W 7 (527654) 345.0 kV to Trip Bus # b.8. SAGSFT3_2.21 (527605) 0.7 kV to Generator #1 b.9. SAGSFT4_2.21 (527607) 0.7 kV to Generator #1 b.10. SAGSFT1_2.21 (527614) 0.7 kV to Generator #1 b.11. SAGSFT1_2.01 (527615) 0.7 kV to Generator #1 b.12. SAGSFT2_2.21 (527617) 0.7 kV to Generator #1 b.13. SAGSFT2_2.01 (527618) 0.7 kV to Generator #1 b.14. SAGA_SCOL 7 (527610) 345.0 kV to Load #1 b.15. SAGA_SCOL 7 (527610) 345.0 kV to Load #2 b.16. SAGA_NDCOL 7 (527598) 345.0 kV to Trip Bus # b.17. SAGA_SDCOL 7 (527599) 345.0 kV to Trip Bus # b.18. SAGA_SMEAS 7 (527600) 345.0 kV to Trip Bus # b.19. SAGA_NCOL 7 (527601) 345.0 kV to Trip Bus # b.20. SAGANCOL1 1 (527602) 34.5 kV to Trip Bus # b.21. SAGANCOL2 1 (527603) 34.5 kV to Trip Bus # b.22. GRDXFR3 1 (527604) 0.5 kV to Trip Bus # b.23. SAGSFT3_2.21 (527605) 0.7 kV to Trip Bus # b.24. GRDXFR4 1 (527606) 0.5 kV to Trip Bus # b.25. SAGSFT4_2.21 (527607) 0.7 kV to Trip Bus # b.26. SUB BUS #3 1 (527608) 34.5 kV to Trip Bus # b.27. SUB BUS #4 1 (527609) 34.5 kV to Trip Bus # b.28. SAGA_SCOL 7 (527610) 345.0 kV to Trip Bus # b.29. SAGASCOL1 1 (527611) 34.5 kV to Trip Bus # b.30. SAGASCOL2 1 (527612) 34.5 kV to Trip Bus # b.31. GRDXFR1 1 (527613) 0.5 kV to Trip Bus # b.32. SAGSFT1_2.21 (527614) 0.7 kV to Trip Bus # b.33. SAGSFT1_2.01 (527615) 0.7 kV to Trip Bus # b.34. GRDXFR2 1 (527616) 0.5 kV to Trip Bus # b.35. SAGSFT2_2.21 (527617) 0.7 kV to Trip Bus # b.36. SAGSFT2_2.01 (527618) 0.7 kV to Trip Bus # b.37. SAGA_NCLTR31 (527621) 13.8 kV to Trip Bus # b.38. SAGA_NCLTR41 (527622) 13.8 kV to Trip Bus # b.39. SAGA_SCLTR11 (527623) 13.8 kV to Trip Bus # b.40. SAGA_SCLTR21 (527624) 13.8 kV to Trip Bus # b.41. SUB BUS #1 (527628) 34.5 kV to Trip Bus # b.42. SUB BUS #2 (527629) 34.5 kV to Trip Bus # b.43. CROSSROADS 7 (527656) 345.0 kV to Trip Bus # b.44. RSVLT_WIND11 (527658) 34.5 kV to Trip Bus # b.45. RSVLT_WIND21 (527659) 34.5 kV to Trip Bus # b.46. RSVLT_COL1 1 (527660) 34.5 kV to Trip Bus # b.47. RSVLT_COL2 1 (527661) 34.5 kV to Trip Bus # b.48. RSVLT_TR1 1 (527662) 13.2 kV to Trip Bus # b.49. RSVLT_TR2 1 (527663) 13.2 kV to Trip Bus # b.50. RSVLT_COL1 7 (527666) 345.0 kV to Trip Bus # b.51. RSVLT_COL2 7 (527667) 345.0 kV to Trip Bus # b.52. MILO_CB (577120) 34.5 kV to Trip Bus # b.53. MILO_WND (577121) 34.5 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_SPS2 | Single Phase Fault with Stuck Breaker on CHINA_DRAW (528223) 345 kV Bus a. Apply Fault at the CHINA_DRAW (528223) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHINA_DRAW 7 (528223) 345.0 kV to PHANTOM 7 (528015) 345.0 kV Transmission Circuit #1 b.2. CHINA_DRAW 3 (528222) 115.0 kV to CHINA_DRAW 7 (528223) 345.0 kV to CHINA_DRAW 1 (528219) 13.2 kV Three Winding #1 b.3. CHINA_DRAW 1 (528219) 13.2 kV to Trip Bus # b.4. CARPENTER 7 (523823) 345.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_SPS3 | Single Phase Fault with Stuck Breaker on CHINA_DRAW (528223) 345 kV Bus a. Apply Fault at the CHINA_DRAW (528223) 345 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. CHINA_DRAW 3 (528222) 115.0 kV to CHINA_DRAW 7 (528223) 345.0 kV to CHINA_DRAW 1 (528219) 13.2 kV Three Winding #1 b.2. CHINA_DRAW 7 (528223) 345.0 kV to N_LOVING 7 (528185) 345.0 kV Transmission Circuit #1 b.3. CHINA_DRAW 7 (528223) 345.0 kV to PHANTOM 7 (528015) 345.0 kV Transmission Circuit #1 b.5. CHINA_DRAW 1 (528219) 13.2 kV to Trip Bus # b.6. CARPENTER 7 (523823) 345.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_SPS4 | Single Phase Fault with Stuck Breaker on CHINA_DRAW (528223) 345 kV Bus a. Apply Fault at the CHINA_DRAW (528223) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHINA_DRAW 7 (528223) 345.0 kV to CHINA_DRAW 3 (528222) 115.0 kV to CHINA_DRAW 1 (528219) 13.2 kV Three Winding #1 b.2. CHINA_DRAW 7 (528223) 345.0 kV to N_LOVING 7 (528185) 345.0 kV Transmission Circuit #1 b.3. CHINA_DRAW 7 (528223) 345.0 kV to PHANTOM 7 (528015) 345.0 kV Transmission Circuit #1 b.4. CHINA_DRAW 1 (528219) 13.2 kV to Trip Bus # b.5. CARPENTER 7 (523823) 345.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_SPS5 | Single Phase Fault with Stuck Breaker on EDDY_CNTY (527802) 345 kV Bus a. Apply Fault at the EDDY_CNTY (527802) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDDY_CNTY 7 (527802) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.2. EDDY_CNTY 7 (527802) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.3. EDDY_CNTY 7 (527802) 345.0 kV to EDDY_NORTH 6 (527799) 230.0 kV to EDDY_TR 1 (527796) 13.2 kV Three Winding #1 b.4. EDDY_TR 1 (527796) 13.2 kV to Trip Bus # b.5. EDDY_CNTY 7 (527802) 345.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_SPS6 | Single Phase Fault with Stuck Breaker on EDDY_CNTY (527802) 345 kV Bus a. Apply Fault at the EDDY_CNTY (527802) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDDY_CNTY 7 (527802) 345.0 kV to EDDY_NORTH 6 (527799) 230.0 kV to EDDY_TR 1 (527796) 13.2 kV Three Winding #1 b.2. EDDY_CNTY 7 (527802) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.3. EDDY_CNTY 7 (527802) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.4. EDDY_TR 1 (527796) 13.2 kV to Trip Bus # b.5. EDDY_CNTY 7 (527802) 345.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_SPS7 | Single Phase Fault with Stuck Breaker on EDDY_CNTY (527802) 345 kV Bus a. Apply Fault at the EDDY_CNTY (527802) 345 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. EDDY_NORTH 6 (527799) 230.0 kV to EDDY_CNTY 7 (527802) 345.0 kV to EDDY_TR 1 (527796) 13.2 kV Three Winding #1 b.2. EDDY_CNTY 7 (527802) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.3. EDDY_CNTY 7 (527802) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.5. EDDY_TR 1 (527796) 13.2 kV to Trip Bus # b.6. EDDY_CNTY 7 (527802) 345.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_SPS8 | Single Phase Fault with Stuck Breaker on HOBBS_INT (527896) 345 kV Bus a. Apply Fault at the HOBBS_INT (527896) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HOBBS_INT 7 (527896) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.2. HOBBS_INT 7 (527896) 345.0 kV to YOAKUM_345 (526936) 345.0 kV Transmission Circuit #1 b.3. HOBBS_TR3 1 (527895) 13.2 kV to Trip Bus # b.4. HOBBS_INT 7 (527896) 345.0 kV to Trip Bus # | P4 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_SPS9 | Single Phase Fault with Stuck Breaker on KIOWA (527965) 345 kV Bus a. Apply Fault at the KIOWA (527965) 345 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. KIOWA 3 (527966) 115.0 kV to KIOWA 7 (527965) 345.0 kV to KIOWA_TR1 1 (527964) 13.2 kV Three Winding #1 b.2. KIOWA 7 (527965) 345.0 kV to RDRUNNER 7 (528027) 345.0 kV Transmission Circuit #1 b.4. KIOWA_TR1 1 (527964) 13.2 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_SPS10 | Single Phase Fault with Stuck Breaker on KIOWA (527965) 345 kV Bus a. Apply Fault at the KIOWA (527965) 345 kV Bus b. Clear Fault after 20 cycles and trip the following elements: b.1. KIOWA 7 (527965) 345.0 kV to RDRUNNER 7 (528027) 345.0 kV Transmission Circuit #1 b.2. KIOWA 3 (527966) 115.0 kV to KIOWA 7 (527965) 345.0 kV to KIOWA_TR1 1 (527964) 13.2 kV Three Winding #1 b.3. KIOWA_TR1 1 (527964) 13.2 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_SPS11 | Single Phase Fault with Stuck Breaker on N_LOVING (528185) 345 kV Bus a. Apply Fault at the N_LOVING (528185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N_LOVING 7 (528185) 345.0 kV to CHINA_DRAW 7 (528223) 345.0 kV Transmission Circuit #1 b.2. N_LOVING 7 (528185) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.3. NORTH_LOVNG3 (528182) 115.0 kV to N_LOVING 7 (528185) 345.0 kV to N_LOVING TR1 (528186) 13.2 kV Three Winding #1 b.4. N_LOVING TR1 (528186) 13.2 kV to Trip Bus # b.5. N_LOVING 7 (528185) 345.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_SPS12 | Single Phase Fault with Stuck Breaker on N_LOVING (528185) 345 kV Bus a. Apply Fault at the N_LOVING (528185) 345 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. NORTH_LOVNG3 (528182) 115.0 kV to N_LOVING 7 (528185) 345.0 kV to N_LOVING TR1 (528186) 13.2 kV Three Winding #1 b.2. N_LOVING 7 (528185) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.3. N_LOVING 7 (528185) 345.0 kV to CHINA_DRAW 7 (528223) 345.0 kV Transmission Circuit #1 b.5. N_LOVING TR1 (528186) 13.2 kV to Trip Bus # b.6. N_LOVING 7 (528185) 345.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_SPS13 | Single Phase Fault with Stuck Breaker on N_LOVING (528185) 345 kV Bus a. Apply Fault at the N_LOVING (528185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N_LOVING 7 (528185) 345.0 kV to NORTH_LOVNG3 (528182) 115.0 kV to N_LOVING TR1 (528186) 13.2 kV Three Winding #1 b.2. N_LOVING 7 (528185) 345.0 kV to CHINA_DRAW 7 (528223) 345.0 kV Transmission Circuit #1 b.3. N_LOVING 7 (528185) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.4. N_LOVING TR1 (528186) 13.2 kV to Trip Bus # b.5. N_LOVING 7 (528185) 345.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_SPS14 | Single Phase Fault with Stuck Breaker on ROADRUNNER (528027) 345 kV Bus a. Apply Fault at the ROADRUNNER (528027) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RDRUNNER 7 (528027) 345.0 kV to PHANTOM 7 (528015) 345.0 kV Transmission Circuit #1 b.2. RDRUNNER 7 (528027) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.3. RDRUNNER 3 (528025) 115.0 kV to RDRUNNER 7 (528027) 345.0 kV to RDRNNER_TR11 (528023) 13.2 kV Three Winding #1 b.4. RDRNNER_TR11 (528023) 13.2 kV to Trip Bus # b.5. RDRUNNER 7 (528027) 345.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_SPS15 | Single Phase Fault with Stuck Breaker on ROADRUNNER (528027) 345 kV Bus a. Apply Fault at the ROADRUNNER (528027) 345 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. RDRUNNER 3 (528025) 115.0 kV to RDRUNNER 7 (528027) 345.0 kV to RDRNNER_TR11 (528023) 13.2 kV Three Winding #1 b.2. RDRUNNER 7 (528027) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.3. RDRUNNER 7 (528027) 345.0 kV to PHANTOM 7 (528015) 345.0 kV Transmission Circuit #1 b.5. RDRNNER_TR11 (528023) 13.2 kV to Trip Bus # b.6. RDRUNNER 7 (528027) 345.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_SPS16 | Single Phase Fault with Stuck Breaker on ROADRUNNER (528027) 345 kV Bus a. Apply Fault at the ROADRUNNER (528027) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RDRUNNER 7 (528027) 345.0 kV to RDRUNNER 3 (528025) 115.0 kV to RDRNNER_TR11 (528023) 13.2 kV Three Winding #1 b.2. RDRUNNER 7 (528027) 345.0 kV to PHANTOM 7 (528015) 345.0 kV Transmission Circuit #1 b.3. RDRUNNER 7 (528027) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.4. RDRNNER_TR11 (528023) 13.2 kV to Trip Bus # b.5. RDRUNNER 7 (528027) 345.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_SPS17 | Single Phase Fault with Stuck Breaker on YOAKUM (526936) 345 kV Bus a. Apply Fault at the YOAKUM (526936) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. YOAKUM_345 (526936) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.3. YOAKUM 6 (526935) 230.0 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM_TR1 (526937) 13.2 kV Three Winding #1 b.4. YOAKUM_TR1 (526937) 13.2 kV to Trip Bus # b.5. YOAKUM_345 (526936) 345.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_SPS18 | Single Phase Fault with Stuck Breaker on YOAKUM (526936) 345 kV Bus a. Apply Fault at the YOAKUM (526936) 345 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. YOAKUM 6 (526935) 230.0 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM_TR1 (526937) 13.2 kV Three Winding #1 b.2. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_345 (526936) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.5. YOAKUM_TR1 (526937) 13.2 kV to Trip Bus # b.6. YOAKUM_345 (526936) 345.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_SPS19 | Single Phase Fault with Stuck Breaker on YOAKUM (526936) 345 kV Bus a. Apply Fault at the YOAKUM (526936) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. YOAKUM_345 (526936) 345.0 kV to YOAKUM 6 (526935) 230.0 kV to YOAKUM_TR1 (526937) 13.2 kV Three Winding #1 b.2. YOAKUM_345 (526936) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.4. YOAKUM_TR1 (526937) 13.2 kV to Trip Bus # b.5. YOAKUM_345 (526936) 345.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_LOCAL_FAULT_SPS20 | Single Phase Fault with Stuck Breaker on POTASH (527962) 115 kV Bus a. Apply Fault at the POTASH (527962) 115 kV Bus b. Clear Fault after 19.02 cycles and trip the following elements: b.1. POTASH_JCT 3 (527962) 115.0 kV to PCA 3 (527930) 115.0 kV Transmission Circuit #1 b.2. XTO_DI9_TP 3 (528064) 115.0 kV to LIVSTNRIDGE3 (527953) 115.0 kV Transmission Circuit #1 b.3. POTASH_JCT 3 (527962) 115.0 kV to CARLSBAD 3 (528160) 115.0 kV Transmission Circuit #1 b.4. POTASH_TR1 1 (527958) 13.2 kV to Trip Bus # b.5. NATPOT_TP 2 (528145) 69.0 kV to PCA 2 (527929) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. GRAPEVN_TR11 (523769) 13.2 kV to GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips LANOGSU1 (523812). | Protection disabled without any impact on stability.
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on STLN-DEMARC6230.00 (523779) 230 kV Bus a. Apply Fault at the STLN-DEMARC6230.00 (523779) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEETWT6 (511541) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 b.3. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply Fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. NOVUS_WND 1 (523107) 4.2 kV to NOVUS1 1 (523109) 34.5 kV Two Winding #1 b.3. NOVUS1 1 (523109) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.4. G06-44-2 (560581) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.5. NOVUS1_TR1 1 (523110) 13.8 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV Three Winding #1 b.6. NOVUS1 3 (523111) 115.0 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G06-44-3 (560585), G06-44-4 (560586) and HARRNGTON (523971,523972,523973) units. The issue was also observed in the base case. | Operational measures fixing the voltage setpoint of G06-44-3 (560585), G06-44-4 (560586) and HARRNGTON (523971,523972,523973) and HOBBS_PLT ( 527902,527901).
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 b.3. HITCHLAND 7 (523097) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on NOBLE_WND 7345.00 (523101) 345 kV Bus a. Apply Fault at the NOBLE_WND 7345.00 (523101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.2. NOBLE_WND 3 (523103) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.3. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-WT4-1 (523121) 0.6 kV Two Winding #1 b.4. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-LV4-1 (523127) 34.5 kV Transmission Circuit #1 b.5. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-WT2-1 (523123) 0.6 kV Two Winding #1 b.6. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-LV2-1 (523129) 34.5 kV Transmission Circuit #1 b.7. GRPLNS-LV4-1 (523127) 34.5 kV to GRPLNS-GT4-1 (523133) 0.5 kV Two Winding #1 b.8. NBLWND-LV2 1 (523128) 34.5 kV to GRPLNS-HV2-3 (523131) 115.0 kV Two Winding #1 b.9. GRPLNS-LV2-1 (523129) 34.5 kV to GRPLNS-GT2-1 (523132) 0.5 kV Two Winding #1 b.10. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-LV4-1 (523127) 34.5 kV Two Winding #1 b.11. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.12. GRPLNS-HV2-3 (523131) 115.0 kV to GRPLNS-LV2-1 (523129) 34.5 kV Two Winding #1 b.13. NOBLE_TR 1 (523102) 13.8 kV to NOBLE_WND 7 (523101) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV Three Winding #1 b.14. NOBLE_WND 3 (523103) 115.0 kV to NOBLE_WND 7 (523101) 345.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply Fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.2. POTTER_CO 7 (523961) 345.0 kV to SPNSPUR_WND7 (524296) 345.0 kV Transmission Circuit #1 b.3. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 b.4. POTTER_CO 7 (523961) 345.0 kV to GRAPEVINE (560035) 345.0 kV Transmission Circuit #1 b.5. SPNSPUR_GEN1 (524295) 0.7 kV to SPNSPUR_WND1 (524294) 34.5 kV Two Winding #1 b.6. SPNSPUR_WND7 (524296) 345.0 kV to SPNSPUR_COL7 (524299) 345.0 kV Transmission Circuit #1 b.7. POTTER_TR 1 (523957) 13.2 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips LANOGSU1 (523812). | Protection disabled without any impact on stability.
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply Fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to YOAKUM_345 (526936) 345.0 kV Transmission Circuit #1 b.2. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_345 (526936) 345.0 kV to GEN-2019-011 (763516) 345.0 kV Transmission Circuit #1 b.4. YOAKUM 6 (526935) 230.0 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM_TR1 (526937) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on ELK_CT1 345.00 (525850) 345 kV Bus a. Apply Fault at the ELK_CT1 345.00 (525850) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to ELK_2 1 (525845) 18.0 kV Two Winding #1 b.2. TUCO_INT 7 (525832) 345.0 kV to ELK_CT1 (525850) 345.0 kV Transmission Circuit #1 b.3. TUCO_INT 7 (525832) 345.0 kV to YOAKUM_345 (526936) 345.0 kV Transmission Circuit #1 b.4. ELK_CT1 (525850) 345.0 kV to ELK_1 1 (525844) 18.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Transfer | GROUP5_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELER 6 (523777) 230.0 kV to WHEELER 3 (523776) 115.0 kV to WHEELER_TR11 (523774) 13.2 kV Three Winding #1 b.2. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_001 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.2. TOLK 6 (525531) 230.0 kV to TOLK 7 (525549) 345.0 kV to TOLK_TR 1 (525537) 13.2 kV Three Winding #1 b.3. TOLK_TR 1 (525537) 13.2 kV to TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_002 | 3 Phase fault on FIESTA 3115.00 (528151) 115 kV Bus a. Apply fault at the FIESTA 3115.00 (528151) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIESTA 3 (528151) 115.0 kV to CARLSBAD 3 (528160) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_003 | 3 Phase fault on PCA 3115.00 (527930) 115 kV Bus a. Apply fault at the PCA 3115.00 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 (527930) 115.0 kV to POTASH_JCT 3 (527962) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_004 | 3 Phase fault on CARLSBAD 3115.00 (528160) 115 kV Bus a. Apply fault at the CARLSBAD 3115.00 (528160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLSBAD 3 (528160) 115.0 kV to PECOS 3 (528178) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_005 | 3 Phase fault on HOBBS_INT 3115.00 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3115.00 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 (527891) 115.0 kV to MADDOX 3 (528355) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_006 | 3 Phase fault on CUNNINHAM 3115.00 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3115.00 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 (527864) 115.0 kV to HOBBS_INT 3 (527891) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_007 | 3 Phase fault on MILLEN_TPW 3115.00 (528434) 115 kV Bus a. Apply fault at the MILLEN_TPW 3115.00 (528434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 (527891) 115.0 kV to MILLEN_TPW 3 (528434) 115.0 kV Transmission Circuit #1 b.2. TAYLOR 3 (528413) 115.0 kV to NE_HOBBS 3 (528442) 115.0 kV Transmission Circuit #1 b.3. MILLEN_TPW 3 (528434) 115.0 kV to MILLEN 3 (528435) 115.0 kV Transmission Circuit # b.4. MILLEN 3 (528435) 115.0 kV to MILLEN_TPE 3 (528436) 115.0 kV Transmission Circuit # b.5. MILLEN_TPE 3 (528436) 115.0 kV to NE_HOBBS 3 (528442) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_008 | 3 Phase fault on BENSING 3115.00 (528433) 115 kV Bus a. Apply fault at the BENSING 3115.00 (528433) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGG 3 (527363) 115.0 kV to BENSING 3 (528433) 115.0 kV Transmission Circuit #1 b.2. HOBBS_INT 3 (527891) 115.0 kV to BENSING 3 (528433) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_009 | 3 Phase fault on CUNNINHAM 3115.00 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3115.00 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 (527864) 115.0 kV to HOBBS_INT 3 (527891) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_010 | 3 Phase fault on POTASH_JCT 3115.00 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3115.00 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 (527962) 115.0 kV to CARLSBAD 3 (528160) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_011 | 3 Phase fault on PCA 3115.00 (527930) 115 kV Bus a. Apply fault at the PCA 3115.00 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 (527930) 115.0 kV to CARLSBAD 3 (528160) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_012 | 3 Phase fault on LEA_ROAD 3115.00 (528505) 115 kV Bus a. Apply fault at the LEA_ROAD 3115.00 (528505) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEA_ROAD 3 (528505) 115.0 kV to WARD 3 (528519) 115.0 kV Transmission Circuit #1 b.2. LEA_ROAD 3 (528505) 115.0 kV to OIL_CENTER 3 (528552) 115.0 kV Transmission Circuit #1 b.3. WARD 3 (528519) 115.0 kV to WHITTEN 3 (528540) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_013 | 3 Phase fault on SAND_DUNES 3115.00 (528016) 115 kV Bus a. Apply fault at the SAND_DUNES 3115.00 (528016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WIPP 3 (528009) 115.0 kV to SAND_DUNES 3 (528016) 115.0 kV Transmission Circuit #1 b.2. SAND_DUNES 3 (528016) 115.0 kV to RED_BLUFF 3 (528018) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_014 | 3 Phase fault on WOLFCAMP_TP3115.00 (528235) 115 kV Bus a. Apply fault at the WOLFCAMP_TP3115.00 (528235) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 (528013) 115.0 kV to BOPCO_PKRLK3 (528020) 115.0 kV Transmission Circuit #1 b.2. RED_BLUFF 3 (528018) 115.0 kV to WOLFCAMP_TP3 (528235) 115.0 kV Transmission Circuit #1 b.3. BOPCO_PKRLK3 (528020) 115.0 kV to WOLFCAMP_TP3 (528235) 115.0 kV Transmission Circuit #1 b.4. WOLFCAMP_TP3 (528235) 115.0 kV to WOLFCAMP 3 (528236) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_015 | 3 Phase fault on PHANTOM 3115.00 (528013) 115 kV Bus a. Apply fault at the PHANTOM 3115.00 (528013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 (528013) 115.0 kV to WOOD_DRAW 3 (528228) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_016 | 3 Phase fault on HOBBS_INT 3115.00 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3115.00 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 (527891) 115.0 kV to LE-WEST_SUB3 (528333) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_017 | 3 Phase fault on NORTH_LOVNG3115.00 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3115.00 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 (528182) 115.0 kV to HOPI_SUB 3 (528226) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_018 | 3 Phase fault on BLACKRIVER 3115.00 (528193) 115 kV Bus a. Apply fault at the BLACKRIVER 3115.00 (528193) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 (528182) 115.0 kV to BLACKRIVER 3 (528193) 115.0 kV Transmission Circuit #1 b.2. SENDERO +3 (528184) 115.0 kV to BLACKRIVER 3 (528193) 115.0 kV Transmission Circuit #1 b.3. SENDERO +3 (528184) 115.0 kV to BLCKRVR_DST3 (528206) 115.0 kV Transmission Circuit #1 b.4. BLCKRVR_DST3 (528206) 115.0 kV to CHINA_DRAW 3 (528222) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_019 | 3 Phase fault on XTO_BIGEDDY3115.00 (528396) 115 kV Bus a. Apply fault at the XTO_BIGEDDY3115.00 (528396) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 (527930) 115.0 kV to XTO_BIGEDDY3 (528396) 115.0 kV Transmission Circuit #1 b.2. QUAHADA 3 (528394) 115.0 kV to XTO_BIGEDDY3 (528396) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_020 | 3 Phase fault on RDRUNNER 3115.00 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3115.00 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 (528025) 115.0 kV to BATTLE_AXE 3 (528040) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_021 | 3 Phase fault on CUSTERMTN 3115.00 (528239) 115 kV Bus a. Apply fault at the CUSTERMTN 3115.00 (528239) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSTERMTN 3 (528239) 115.0 kV to PONDEROSA 3 (528240) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_022 | 3 Phase fault on CHINA_DRAW 3115.00 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3115.00 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 (528222) 115.0 kV to WOOD_DRAW 3 (528228) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_023 | 3 Phase fault on CHINA_DRAW 3115.00 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3115.00 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 (528222) 115.0 kV to CHVRN_EDDYS3 (528252) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_024 | 3 Phase fault on MEDANOS 3115.00 (527954) 115 kV Bus a. Apply fault at the MEDANOS 3115.00 (527954) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIVSTNRIDGE3 (527953) 115.0 kV to MEDANOS 3 (527954) 115.0 kV Transmission Circuit #1 b.2. MEDANOS 3 (527954) 115.0 kV to SAGE_BRUSH 3 (527955) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_025 | 3 Phase fault on RED_BLUFF 3115.00 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3115.00 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RED_BLUFF 3 (528018) 115.0 kV to RDRUNNER 3 (528025) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_026 | 3 Phase fault on AGAVE_RHILL3115.00 (528230) 115 kV Bus a. Apply fault at the AGAVE_RHILL3115.00 (528230) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 (528025) 115.0 kV to AGAVE_RHILL3 (528230) 115.0 kV Transmission Circuit #1 b.2. AGAVE_RHILL3 (528230) 115.0 kV to OCHOA 3 (528232) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_027 | 3 Phase fault on RDRUNNER 3115.00 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3115.00 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 (528025) 115.0 kV to CUSTERMTN 3 (528239) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_028 | 3 Phase fault on CUSTERMTN 3115.00 (528239) 115 kV Bus a. Apply fault at the CUSTERMTN 3115.00 (528239) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSTERMTN 3 (528239) 115.0 kV to WHITTEN 3 (528540) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_029 | 3 Phase fault on INTREPDW_TP3115.00 (527999) 115 kV Bus a. Apply fault at the INTREPDW_TP3115.00 (527999) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIVSTNRIDGE3 (527953) 115.0 kV to XTO_DI9_TP 3 (528064) 115.0 kV Transmission Circuit #1 b.2. POTASH_JCT 3 (527962) 115.0 kV to INTREPDW_TP3 (527999) 115.0 kV Transmission Circuit #1 b.3. INTREPDW_TP3 (527999) 115.0 kV to INTREPIDWST3 (528000) 115.0 kV Transmission Circuit #1 b.4. INTREPDW_TP3 (527999) 115.0 kV to IMC_#1_TP 3 (528035) 115.0 kV Transmission Circuit #1 b.5. IMC_#1_TP 3 (528035) 115.0 kV to IMC_#1 3 (528037) 115.0 kV Transmission Circuit #1 b.6. IMC_#1_TP 3 (528035) 115.0 kV to XTO_DI9_TP 3 (528064) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_030 | 3 Phase fault on LIVSTNRIDGE3115.00 (527953) 115 kV Bus a. Apply fault at the LIVSTNRIDGE3115.00 (527953) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIVSTNRIDGE3 (527953) 115.0 kV to WIPP 3 (528009) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_031 | 3 Phase fault on POTASH_JCT 3115.00 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3115.00 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 (527962) 115.0 kV to KIOWA 3 (527966) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_032 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to YOAKUM_345 (526936) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_033 | 3 Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 (526935) 230.0 kV to INK_BASIN 6 (527028) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_034 | 3 Phase fault on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_035 | 3 Phase fault on INK_BASIN 6230.00 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6230.00 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6 (527028) 230.0 kV to HOBBS_INT 6 (527894) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_036 | 3 Phase fault on CROSSROADS 7345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7345.00 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 (527656) 345.0 kV to EDDY_CNTY 7 (527802) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_037 | 3 Phase fault on EDDY_NORTH 6230.00 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6230.00 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 (527799) 230.0 kV to CUNNIGHM_N 6 (527865) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_038 | 3 Phase fault on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7 (527802) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_039 | 3 Phase fault on CUNNIGHM_N 6230.00 (527865) 230 kV Bus a. Apply fault at the CUNNIGHM_N 6230.00 (527865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_N 6 (527865) 230.0 kV to POTASH_JCT 6 (527963) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_040 | 3 Phase fault on CUNNIGHM_S 6230.00 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6230.00 (527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6 (527867) 230.0 kV to HOBBS_INT 6 (527894) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_041 | 3 Phase fault on HOBBS_INT 6230.00 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6230.00 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 6 (527894) 230.0 kV to ANDREWS 6 (528604) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_042 | 3 Phase fault on HOBBS_INT 7345.00 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7345.00 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 (527896) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_043 | 3 Phase fault on PCA 3115.00 (527930) 115 kV Bus a. Apply fault at the PCA 3115.00 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 (527930) 115.0 kV to CV-LUSK_TP 3 (527948) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_044 | 3 Phase fault on POTASH_JCT 269.000 (527961) 69 kV Bus a. Apply fault at the POTASH_JCT 269.000 (527961) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 2 (527961) 69.0 kV to DUVAL_#1 2 (527980) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_045 | 3 Phase fault on POTASH_JCT 269.000 (527961) 69 kV Bus a. Apply fault at the POTASH_JCT 269.000 (527961) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 2 (527961) 69.0 kV to KERMAC 2 (527996) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_046 | 3 Phase fault on POTASH_JCT 269.000 (527961) 69 kV Bus a. Apply fault at the POTASH_JCT 269.000 (527961) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 2 (527961) 69.0 kV to MISSCHEM#2 2 (528022) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_047 | 3 Phase fault on POTASH_JCT 269.000 (527961) 69 kV Bus a. Apply fault at the POTASH_JCT 269.000 (527961) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 2 (527961) 69.0 kV to NATPOT_TP 2 (528145) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_048 | 3 Phase fault on POTASH_JCT 6230.00 (527963) 230 kV Bus a. Apply fault at the POTASH_JCT 6230.00 (527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 6 (527963) 230.0 kV to PECOS 6 (528179) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_049 | 3 Phase fault on KIOWA 7345.00 (527965) 345 kV Bus a. Apply fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 (527965) 345.0 kV to RDRUNNER 7 (528027) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_050 | 3 Phase fault on KIOWA 7345.00 (527965) 345 kV Bus a. Apply fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 (527965) 345.0 kV to N_LOVING 7 (528185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_051 | 3 Phase fault on PHANTOM 3115.00 (528013) 115 kV Bus a. Apply fault at the PHANTOM 3115.00 (528013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 (528013) 115.0 kV to MALAGABEND 3 (528194) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_052 | 3 Phase fault on PHANTOM 7345.00 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7345.00 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 (528015) 345.0 kV to RDRUNNER 7 (528027) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_053 | 3 Phase fault on PHANTOM 7345.00 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7345.00 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 (528015) 345.0 kV to CHINA_DRAW 7 (528223) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_054 | 3 Phase fault on RR_SVC_HV 3115.00 (528024) 115 kV Bus a. Apply fault at the RR_SVC_HV 3115.00 (528024) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RR_SVC_HV 3 (528024) 115.0 kV to RDRUNNER 3 (528025) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_055 | 3 Phase fault on 7-RIVERS 6230.00 (528095) 230 kV Bus a. Apply fault at the 7-RIVERS 6230.00 (528095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 7-RIVERS 6 (528095) 230.0 kV to PECOS 6 (528179) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_056 | 3 Phase fault on NORTH_LOVNG3115.00 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3115.00 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 (528182) 115.0 kV to SOUTH_LOVNG3 (528192) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_057 | 3 Phase fault on NORTH_LOVNG3115.00 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3115.00 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 (528182) 115.0 kV to AGAVE_PDURO3 (528195) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_058 | 3 Phase fault on N_LOVING 7345.00 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7345.00 (528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N_LOVING 7 (528185) 345.0 kV to CHINA_DRAW 7 (528223) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_059 | 3 Phase fault on SOUTH_LOVNG3115.00 (528192) 115 kV Bus a. Apply fault at the SOUTH_LOVNG3115.00 (528192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOUTH_LOVNG3 (528192) 115.0 kV to MALAGABEND 3 (528194) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_060 | 3 Phase fault on CHINA_DRAW 3115.00 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3115.00 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 (528222) 115.0 kV to CD_SVC_HV 3 (528225) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_061 | 3 Phase fault on CUNNIGHM_N 6230.00 (527865) 230 kV Bus a. Apply fault at the CUNNIGHM_N 6230.00 (527865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_N 6 (527865) 230.0 kV to CUNNIGHM_S 6 (527867) 230.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_062 | 3 Phase fault on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 (526936) 345.0 kV to YOAKUM 6 (526935) 230.0 kV to YOAKUM_TR1 (526937) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_063 | 3 Phase fault on INK_BASIN 6230.00 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6230.00 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6 (527028) 230.0 kV to INK_BASIN 3 (527027) 115.0 kV to INKBASN_TR 1 (527026) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_064 | 3 Phase fault on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7 (527802) 345.0 kV to EDDY_NORTH 6 (527799) 230.0 kV to EDDY_TR 1 (527796) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_065 | 3 Phase fault on CUNNIGHM_S 6230.00 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6230.00 (527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6 (527867) 230.0 kV to CUNNINHAM 3 (527864) 115.0 kV to CUNNHM_TR1 1 (527863) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_066 | 3 Phase fault on HOBBS_INT 6230.00 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6230.00 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 6 (527894) 230.0 kV to HOBBS_INT 3 (527891) 115.0 kV to HOBBS_TR1 1 (527890) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_067 | 3 Phase fault on HOBBS_INT 6230.00 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6230.00 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 6 (527894) 230.0 kV to HOBBS_INT 3 (527891) 115.0 kV to HOBBS_TR2 1 (527889) 13.2 kV Three Winding #2 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_068 | 3 Phase fault on HOBBS_INT 7345.00 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7345.00 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 (527896) 345.0 kV to HOBBS_INT 6 (527894) 230.0 kV to HOBBS_TR3 1 (527895) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_069 | 3 Phase fault on PCA 3115.00 (527930) 115 kV Bus a. Apply fault at the PCA 3115.00 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 (527930) 115.0 kV to PCA 2 (527929) 69.0 kV to PCA_TR1 1 (527928) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_070 | 3 Phase fault on POTASH_JCT 3115.00 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3115.00 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 (527962) 115.0 kV to POTASH_JCT 2 (527961) 69.0 kV to POTASH_TR3 1 (527960) 13.2 kV Three Winding #2 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_071 | 3 Phase fault on POTASH_JCT 3115.00 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3115.00 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 (527962) 115.0 kV to POTASH_JCT 2 (527961) 69.0 kV to POTASH_TR2 1 (527959) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_072 | 3 Phase fault on POTASH_JCT 6230.00 (527963) 230 kV Bus a. Apply fault at the POTASH_JCT 6230.00 (527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 6 (527963) 230.0 kV to POTASH_JCT 3 (527962) 115.0 kV to POTASH_TR1 1 (527958) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_073 | 3 Phase fault on KIOWA 7345.00 (527965) 345 kV Bus a. Apply fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 (527965) 345.0 kV to KIOWA 3 (527966) 115.0 kV to KIOWA_TR1 1 (527964) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_074 | 3 Phase fault on PHANTOM 7345.00 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7345.00 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 (528015) 345.0 kV to PHANTOM 3 (528013) 115.0 kV to PHANTOM TR11 (528011) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_075 | 3 Phase fault on PHANTOM 7345.00 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7345.00 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 (528015) 345.0 kV to PHANTOM 3 (528013) 115.0 kV to PHANTOM TR21 (528012) 13.2 kV Three Winding #2 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_076 | 3 Phase fault on RDRUNNER 7345.00 (528027) 345 kV Bus a. Apply fault at the RDRUNNER 7345.00 (528027) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RDRUNNER 7 (528027) 345.0 kV to RDRUNNER 3 (528025) 115.0 kV to RDRNNER_TR11 (528023) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_077 | 3 Phase fault on CARLSBAD 3115.00 (528160) 115 kV Bus a. Apply fault at the CARLSBAD 3115.00 (528160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLSBAD 3 (528160) 115.0 kV to CARLSBAD 2 (528159) 69.0 kV to CRLSBAD_TR11 (528157) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_078 | 3 Phase fault on CARLSBAD 3115.00 (528160) 115 kV Bus a. Apply fault at the CARLSBAD 3115.00 (528160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLSBAD 3 (528160) 115.0 kV to CARLSBAD 2 (528159) 69.0 kV to CRLSBAD_TR21 (528158) 13.2 kV Three Winding #2 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_079 | 3 Phase fault on PECOS 6230.00 (528179) 230 kV Bus a. Apply fault at the PECOS 6230.00 (528179) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECOS 6 (528179) 230.0 kV to PECOS 3 (528178) 115.0 kV to PECOS_TR1 1 (528176) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_080 | 3 Phase fault on N_LOVING 7345.00 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7345.00 (528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N_LOVING 7 (528185) 345.0 kV to NORTH_LOVNG3 (528182) 115.0 kV to N_LOVING TR1 (528186) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_081 | 3 Phase fault on CHINA_DRAW 7345.00 (528223) 345 kV Bus a. Apply fault at the CHINA_DRAW 7345.00 (528223) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHINA_DRAW 7 (528223) 345.0 kV to CHINA_DRAW 3 (528222) 115.0 kV to CHINA_DRAW 1 (528219) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_082 | 3 Phase fault on ANDREWS 6230.00 (528604) 230 kV Bus a. Apply fault at the ANDREWS 6230.00 (528604) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDREWS 6 (528604) 230.0 kV to ANDREWS 3 (528602) 115.0 kV to ANDREWS_TR21 (528600) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_083 | 3 Phase fault on ANDREWS 6230.00 (528604) 230 kV Bus a. Apply fault at the ANDREWS 6230.00 (528604) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDREWS 6 (528604) 230.0 kV to ANDREWS 3 (528602) 115.0 kV to ANDREWS_TR11 (528601) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_084 | 3 Phase fault on CROSSROADS 7345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7345.00 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 (527656) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_085 | 3 Phase fault on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7 (527802) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_086 | 3 Phase fault on LIVSTNRIDGE3115.00 (527953) 115 kV Bus a. Apply fault at the LIVSTNRIDGE3115.00 (527953) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIVSTNRIDGE3 (527953) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_087 | 3 Phase fault on POTASH_JCT 269.000 (527961) 69 kV Bus a. Apply fault at the POTASH_JCT 269.000 (527961) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 2 (527961) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_088 | 3 Phase fault on POTASH_JCT 3115.00 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3115.00 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 (527962) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_089 | 3 Phase fault on WIPP 3115.00 (528009) 115 kV Bus a. Apply fault at the WIPP 3115.00 (528009) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WIPP 3 (528009) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_090 | 3 Phase fault on RED_BLUFF 3115.00 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3115.00 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RED_BLUFF 3 (528018) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_091 | 3 Phase fault on CARLSBAD 3115.00 (528160) 115 kV Bus a. Apply fault at the CARLSBAD 3115.00 (528160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLSBAD 3 (528160) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_092 | 3 Phase fault on NORTH_LOVNG3115.00 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3115.00 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 (528182) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_093 | 3 Phase fault on N_LOVING 7345.00 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7345.00 (528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N_LOVING 7 (528185) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_094 | 3 Phase fault on MALAGABEND 3115.00 (528194) 115 kV Bus a. Apply fault at the MALAGABEND 3115.00 (528194) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALAGABEND 3 (528194) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_095 | 3 Phase fault on CHINA_DRAW 3115.00 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3115.00 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 (528222) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_096 | 3 Phase fault on WOOD_DRAW 3115.00 (528228) 115 kV Bus a. Apply fault at the WOOD_DRAW 3115.00 (528228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOOD_DRAW 3 (528228) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_LOCAL_FAULT_097 | 3 Phase fault on S_JAL 3115.00 (528547) 115 kV Bus a. Apply fault at the S_JAL 3115.00 (528547) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S_JAL 3 (528547) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_REGIONAL_FAULT_001 | 3 Phase fault on STLN-DEMARC6230.00 (523779) 230 kV Bus a. Apply fault at the STLN-DEMARC6230.00 (523779) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 (511541) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.2. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips LANOGSU1 (523812). | Protection disabled without any impact on stability.
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_REGIONAL_FAULT_002 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_REGIONAL_FAULT_003 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_REGIONAL_FAULT_004 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_REGIONAL_FAULT_005 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_REGIONAL_FAULT_006 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_REGIONAL_FAULT_007 | 3 Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips LANOGSU1 (523812). | Protection disabled without any impact on stability.
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_REGIONAL_FAULT_008 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_REGIONAL_FAULT_009 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to YOAKUM_345 (526936) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_REGIONAL_FAULT_010 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to CRAWFISH_DR (560022) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_REGIONAL_FAULT_011 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to CRAWFISH_DR (560022) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_REGIONAL_FAULT_012 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_REGIONAL_FAULT_013 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_REGIONAL_FAULT_014 | 3 Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6 (523777) 230.0 kV to WHEELER 3 (523776) 115.0 kV to WHEELER_TR11 (523774) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips LANOGSU1 (523812). | Protection disabled without any impact on stability.
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_REGIONAL_FAULT_015 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR2 1 (525825) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_REGIONAL_FAULT_016 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P1_REGIONAL_FAULT_017 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on PCA 3115.00 (527930) 115 kV Bus a. Apply Fault at the PCA 3115.00 (527930) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PCA 3 (527930) 115.0 kV to CV-LUSK_TP 3 (527948) 115.0 kV Transmission Circuit #1 b.2. PCA 3 (527930) 115.0 kV to POTASH_JCT 3 (527962) 115.0 kV Transmission Circuit #1 b.3. PCA 3 (527930) 115.0 kV to CARLSBAD 3 (528160) 115.0 kV Transmission Circuit #1 b.4. PCA 3 (527930) 115.0 kV to XTO_BIGEDDY3 (528396) 115.0 kV Transmission Circuit #1 b.5. PCA_TR1 1 (527928) 13.2 kV to PCA 3 (527930) 115.0 kV to PCA 2 (527929) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on KIOWA 7345.00 (527965) 345 kV Bus a. Apply Fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PCA 3 (527930) 115.0 kV to POTASH_JCT 3 (527962) 115.0 kV Transmission Circuit #1 b.2. POTASH_JCT 3 (527962) 115.0 kV to KIOWA 3 (527966) 115.0 kV Transmission Circuit #1 b.3. POTASH_JCT 3 (527962) 115.0 kV to INTREPDW_TP3 (527999) 115.0 kV Transmission Circuit #1 b.4. POTASH_JCT 3 (527962) 115.0 kV to CARLSBAD 3 (528160) 115.0 kV Transmission Circuit #1 b.5. POTASH_TR1 1 (527958) 13.2 kV to POTASH_JCT 6 (527963) 230.0 kV to POTASH_JCT 3 (527962) 115.0 kV Three Winding #1 b.6. POTASH_TR2 1 (527959) 13.2 kV to POTASH_JCT 3 (527962) 115.0 kV to POTASH_JCT 2 (527961) 69.0 kV Three Winding #1 b.7. POTASH_TR3 1 (527960) 13.2 kV to POTASH_JCT 3 (527962) 115.0 kV to POTASH_JCT 2 (527961) 69.0 kV Three Winding #2 b.10. POTASH_JCT 3 (527962) 115.0 kV to POTASH_JCT 6 (527963) 230.0 kV to POTASH_TR1 1 (527958) 13.2 kV Three Winding #1 b.11. KIOWA_TR1 1 (527964) 13.2 kV to KIOWA 7 (527965) 345.0 kV to KIOWA 3 (527966) 115.0 kV Three Winding #1 b.12. KIOWA 3 (527966) 115.0 kV to KIOWA 7 (527965) 345.0 kV to KIOWA_TR1 1 (527964) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on WHITTEN 3115.00 (528540) 115 kV Bus a. Apply Fault at the WHITTEN 3115.00 (528540) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CUSTERMTN 3 (528239) 115.0 kV to WHITTEN 3 (528540) 115.0 kV Transmission Circuit #1 b.2. WARD 3 (528519) 115.0 kV to WHITTEN 3 (528540) 115.0 kV Transmission Circuit #1 b.3. WHITTEN 3 (528540) 115.0 kV to S_JAL 3 (528547) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on POTASH_JCT 6230.00 (527963) 230 kV Bus a. Apply Fault at the POTASH_JCT 6230.00 (527963) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PCA 2 (527929) 69.0 kV to NATPOT_TP 2 (528145) 69.0 kV Transmission Circuit #1 b.2. PCA 3 (527930) 115.0 kV to POTASH_JCT 3 (527962) 115.0 kV Transmission Circuit #1 b.3. LIVSTNRIDGE3 (527953) 115.0 kV to XTO_DI9_TP 3 (528064) 115.0 kV Transmission Circuit #1 b.4. POTASH_JCT 2 (527961) 69.0 kV to DUVAL_#1 2 (527980) 69.0 kV Transmission Circuit #1 b.5. POTASH_JCT 2 (527961) 69.0 kV to KERMAC 2 (527996) 69.0 kV Transmission Circuit #1 b.6. POTASH_JCT 2 (527961) 69.0 kV to MISSCHEM#2 2 (528022) 69.0 kV Transmission Circuit #1 b.7. POTASH_JCT 2 (527961) 69.0 kV to NATPOT_TP 2 (528145) 69.0 kV Transmission Circuit #1 b.8. POTASH_JCT 3 (527962) 115.0 kV to KIOWA 3 (527966) 115.0 kV Transmission Circuit #1 b.9. POTASH_JCT 3 (527962) 115.0 kV to INTREPDW_TP3 (527999) 115.0 kV Transmission Circuit #1 b.10. POTASH_JCT 3 (527962) 115.0 kV to CARLSBAD 3 (528160) 115.0 kV Transmission Circuit #1 b.11. NMPOTASH 2 (527989) 69.0 kV to KERMAC 2 (527996) 69.0 kV Transmission Circuit #1 b.12. INTREPDW_TP3 (527999) 115.0 kV to INTREPIDWST3 (528000) 115.0 kV Transmission Circuit #1 b.13. INTREPDW_TP3 (527999) 115.0 kV to IMC_#1_TP 3 (528035) 115.0 kV Transmission Circuit #1 b.14. MISSCHEM#2 2 (528022) 69.0 kV to IMC_#2 2 (528029) 69.0 kV Transmission Circuit #1 b.15. IMC_#2 2 (528029) 69.0 kV to UNITEDSALT 2 (528043) 69.0 kV Transmission Circuit #1 b.16. IMC_#1_TP 3 (528035) 115.0 kV to IMC_#1 3 (528037) 115.0 kV Transmission Circuit #1 b.17. IMC_#1_TP 3 (528035) 115.0 kV to XTO_DI9_TP 3 (528064) 115.0 kV Transmission Circuit #1 b.18. UNITEDSALT 2 (528043) 69.0 kV to STRATA 2 (528046) 69.0 kV Transmission Circuit #1 b.19. STRATA 2 (528046) 69.0 kV to IMC_#3 2 (528062) 69.0 kV Transmission Circuit #1 b.20. DUVAL_#3 2 (528050) 69.0 kV to IMC_#4 2 (528056) 69.0 kV Transmission Circuit #1 b.21. DUVAL_#3 2 (528050) 69.0 kV to IMC_#3 2 (528062) 69.0 kV Transmission Circuit #1 b.22. XTO_DI9_TP 3 (528064) 115.0 kV to XTO_DI9 3 (528066) 115.0 kV Transmission Circuit #1 b.23. CARLSBAD 3 (528160) 115.0 kV to PECOS 3 (528178) 115.0 kV Transmission Circuit #1 b.24. POTASH_TR1 1 (527958) 13.2 kV to POTASH_JCT 6 (527963) 230.0 kV to POTASH_JCT 3 (527962) 115.0 kV Three Winding #1 b.25. POTASH_TR2 1 (527959) 13.2 kV to POTASH_JCT 3 (527962) 115.0 kV to POTASH_JCT 2 (527961) 69.0 kV Three Winding #1 b.26. POTASH_TR3 1 (527960) 13.2 kV to POTASH_JCT 3 (527962) 115.0 kV to POTASH_JCT 2 (527961) 69.0 kV Three Winding #2 b.27. POTASH_JCT 2 (527961) 69.0 kV to POTASH_JCT 3 (527962) 115.0 kV to POTASH_TR2 1 (527959) 13.2 kV Three Winding #1 b.28. POTASH_JCT 2 (527961) 69.0 kV to POTASH_JCT 3 (527962) 115.0 kV to POTASH_TR3 1 (527960) 13.2 kV Three Winding #2 b.31. POTASH_JCT 3 (527962) 115.0 kV to POTASH_JCT 6 (527963) 230.0 kV to POTASH_TR1 1 (527958) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on CARLSBAD 3115.00 (528160) 115 kV Bus a. Apply Fault at the CARLSBAD 3115.00 (528160) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PCA 3 (527930) 115.0 kV to CARLSBAD 3 (528160) 115.0 kV Transmission Circuit #1 b.2. POTASH_JCT 3 (527962) 115.0 kV to CARLSBAD 3 (528160) 115.0 kV Transmission Circuit #1 b.3. CARLSBAD 2 (528159) 69.0 kV to S_LOVING_TP2 (528190) 69.0 kV Transmission Circuit #1 b.4. CARLSBAD 3 (528160) 115.0 kV to PECOS 3 (528178) 115.0 kV Transmission Circuit #1 b.5. S_LOVING_TP2 (528190) 69.0 kV to CB_WTRFLDTP2 (528197) 69.0 kV Transmission Circuit #1 b.6. S_LOVING_TP2 (528190) 69.0 kV to NAVAMAL_TP 2 (528215) 69.0 kV Transmission Circuit #1 b.7. CB_WTRFLDTP2 (528197) 69.0 kV to CB_WTRFIELD2 (528204) 69.0 kV Transmission Circuit #1 b.8. CB_WTRFLDTP2 (528197) 69.0 kV to WHITES_CTY 2 (528211) 69.0 kV Transmission Circuit #1 b.9. CRLSBAD_TR11 (528157) 13.2 kV to CARLSBAD 3 (528160) 115.0 kV to CARLSBAD 2 (528159) 69.0 kV Three Winding #1 b.10. CRLSBAD_TR21 (528158) 13.2 kV to CARLSBAD 3 (528160) 115.0 kV to CARLSBAD 2 (528159) 69.0 kV Three Winding #2 b.11. CARLSBAD 2 (528159) 69.0 kV to CARLSBAD 3 (528160) 115.0 kV to CRLSBAD_TR11 (528157) 13.2 kV Three Winding #1 b.12. CARLSBAD 2 (528159) 69.0 kV to CARLSBAD 3 (528160) 115.0 kV to CRLSBAD_TR21 (528158) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on RED_BLUFF 3115.00 (528018) 115 kV Bus a. Apply Fault at the RED_BLUFF 3115.00 (528018) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHANTOM 3 (528013) 115.0 kV to BOPCO_PKRLK3 (528020) 115.0 kV Transmission Circuit #1 b.2. PHANTOM 3 (528013) 115.0 kV to WOOD_DRAW 3 (528228) 115.0 kV Transmission Circuit #1 b.3. SAND_DUNES 3 (528016) 115.0 kV to RED_BLUFF 3 (528018) 115.0 kV Transmission Circuit #1 b.4. RED_BLUFF 3 (528018) 115.0 kV to RDRUNNER 3 (528025) 115.0 kV Transmission Circuit #1 b.5. RED_BLUFF 3 (528018) 115.0 kV to WOLFCAMP_TP3 (528235) 115.0 kV Transmission Circuit #1 b.6. BOPCO_PKRLK3 (528020) 115.0 kV to WOLFCAMP_TP3 (528235) 115.0 kV Transmission Circuit #1 b.7. WOLFCAMP_TP3 (528235) 115.0 kV to WOLFCAMP 3 (528236) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on LEA_ROAD 3115.00 (528505) 115 kV Bus a. Apply Fault at the LEA_ROAD 3115.00 (528505) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEA_ROAD 1 (528504) 12.5 kV to LEA_ROAD 3 (528505) 115.0 kV Two Winding #1 b.2. LEA_ROAD 3 (528505) 115.0 kV to WARD 3 (528519) 115.0 kV Transmission Circuit #1 b.3. LEA_ROAD 3 (528505) 115.0 kV to OIL_CENTER 3 (528552) 115.0 kV Transmission Circuit #1 b.4. WARD 3 (528519) 115.0 kV to WHITTEN 3 (528540) 115.0 kV Transmission Circuit #1 b.5. OIL_CENTER 3 (528552) 115.0 kV to COOPER_RNCH3 (528554) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on RSVLT_CC_E 7345.00 (527655) 345 kV Bus a. Apply Fault at the RSVLT_CC_E 7345.00 (527655) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TOLK 7 (525549) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.2. SAGA_SCOL 7 (527610) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.3. RSVLT_GEN1 1 (527651) 0.7 kV to RSVLT_WIND11 (527658) 34.5 kV Two Winding #1 b.4. RSVLT_GEN2 1 (527652) 0.7 kV to RSVLT_WIND21 (527659) 34.5 kV Two Winding #1 b.5. MILO_WIND 1 (527653) 0.7 kV to MILO_CB (577120) 34.5 kV Two Winding #1 b.6. RSVLT_CC_W 7 (527654) 345.0 kV to RSVLT_CC_E 7 (527655) 345.0 kV Transmission Circuit #1 b.7. RSVLT_CC_W 7 (527654) 345.0 kV to RSVLT_COL1 7 (527666) 345.0 kV Transmission Circuit #1 b.8. RSVLT_CC_W 7 (527654) 345.0 kV to RSVLT_COL2 7 (527667) 345.0 kV Transmission Circuit #1 b.9. RSVLT_CC_E 7 (527655) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.10. CROSSROADS 7 (527656) 345.0 kV to EDDY_CNTY 7 (527802) 345.0 kV Transmission Circuit #1 b.11. CROSSROADS 7 (527656) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #ba b.12. CROSSROADS 7 (527656) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #lx b.13. MILO_WND (577121) 34.5 kV to RSVLT_CC_E 7 (527655) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply Fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROSSROADS 7 (527656) 345.0 kV to EDDY_CNTY 7 (527802) 345.0 kV Transmission Circuit #1 b.2. EDDY_CNTY 7 (527802) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.3. EDDY_TR 1 (527796) 13.2 kV to EDDY_CNTY 7 (527802) 345.0 kV to EDDY_NORTH 6 (527799) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on HOBBS_INT 7345.00 (527896) 345 kV Bus a. Apply Fault at the HOBBS_INT 7345.00 (527896) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOBBS_INT 7 (527896) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.2. HOBBS_TR3 1 (527895) 13.2 kV to HOBBS_INT 7 (527896) 345.0 kV to HOBBS_INT 6 (527894) 230.0 kV Three Winding #1 | P4 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on N_LOVING 7345.00 (528185) 345 kV Bus a. Apply Fault at the N_LOVING 7345.00 (528185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KIOWA 7 (527965) 345.0 kV to N_LOVING 7 (528185) 345.0 kV Transmission Circuit #1 b.2. N_LOVING 7 (528185) 345.0 kV to CHINA_DRAW 7 (528223) 345.0 kV Transmission Circuit #1 b.3. NORTH_LOVNG3 (528182) 115.0 kV to N_LOVING 7 (528185) 345.0 kV to N_LOVING TR1 (528186) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply Fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to YOAKUM_345 (526936) 345.0 kV Transmission Circuit #1 b.2. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_345 (526936) 345.0 kV to GEN-2019-011 (763516) 345.0 kV Transmission Circuit #1 b.4. YOAKUM 6 (526935) 230.0 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM_TR1 (526937) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on CHINA_DRAW 7345.00 (528223) 345 kV Bus a. Apply Fault at the CHINA_DRAW 7345.00 (528223) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHANTOM 7 (528015) 345.0 kV to CHINA_DRAW 7 (528223) 345.0 kV Transmission Circuit #1 b.2. N_LOVING 7 (528185) 345.0 kV to CHINA_DRAW 7 (528223) 345.0 kV Transmission Circuit #1 b.3. CHINA_DRAW 1 (528219) 13.2 kV to CHINA_DRAW 7 (528223) 345.0 kV to CHINA_DRAW 3 (528222) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on RDRUNNER 7345.00 (528027) 345 kV Bus a. Apply Fault at the RDRUNNER 7345.00 (528027) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOBBS_INT 7 (527896) 345.0 kV to RDRUNNER 7 (528027) 345.0 kV Transmission Circuit #uc b.2. HOBBS_INT 7 (527896) 345.0 kV to RDRUNNER 7 (528027) 345.0 kV Transmission Circuit #xa b.3. KIOWA 7 (527965) 345.0 kV to RDRUNNER 7 (528027) 345.0 kV Transmission Circuit #1 b.4. PHANTOM 7 (528015) 345.0 kV to RDRUNNER 7 (528027) 345.0 kV Transmission Circuit #1 b.5. RDRNNER_TR11 (528023) 13.2 kV to RDRUNNER 7 (528027) 345.0 kV to RDRUNNER 3 (528025) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on PHANTOM 7345.00 (528015) 345 kV Bus a. Apply Fault at the PHANTOM 7345.00 (528015) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHANTOM 7 (528015) 345.0 kV to CHINA_DRAW 7 (528223) 345.0 kV Transmission Circuit #1 b.2. PHANTOM TR21 (528012) 13.2 kV to PHANTOM 7 (528015) 345.0 kV to PHANTOM 3 (528013) 115.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on PHANTOM 7345.00 (528015) 345 kV Bus a. Apply Fault at the PHANTOM 7345.00 (528015) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHANTOM 7 (528015) 345.0 kV to RDRUNNER 7 (528027) 345.0 kV Transmission Circuit #1 b.2. PHANTOM TR11 (528011) 13.2 kV to PHANTOM 7 (528015) 345.0 kV to PHANTOM 3 (528013) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on PHANTOM 7 (528015) 345 kV Bus a. Apply Fault at the PHANTOM 7 (528015) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHANTOM 7 (528015) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on PHANTOM 3 (528013) 115 kV Bus a. Apply Fault at the PHANTOM 3 (528013) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHANTOM 3 (528013) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on KIOWA 7 (527965) 345 kV Bus a. Apply Fault at the KIOWA 7 (527965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KIOWA 7 (527965) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on POTASH_JCT 3 (527962) 115 kV Bus a. Apply Fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POTASH_JCT 3 (527962) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on HOBBS_INT 7 (527896) 345 kV Bus a. Apply Fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOBBS_INT 7 (527896) 345.0 kV to remove bus # | P4 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on HOBBS_INT 6 (527894) 115 kV Bus a. Apply Fault at the HOBBS_INT 6 (527894) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOBBS_INT 6 (527894) 230.0 kV to remove bus # | P4 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on RED_BLUFF 3 (528018) 115 kV Bus a. Apply Fault at the RED_BLUFF 3 (528018) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RED_BLUFF 3 (528018) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on WOLFCAMP_TP3 (528235) 115 kV Bus a. Apply Fault at the WOLFCAMP_TP3 (528235) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCAMP_TP3 (528235) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on WHITTEN 3 (528540) 115 kV Bus a. Apply Fault at the WHITTEN 3 (528540) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHITTEN 3 (528540) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on WIPP 3115.00 (528009) 115 kV Bus a. Apply Fault at the WIPP 3115.00 (528009) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WIPP 3 (528009) 115.0 kV to LIVSTNRIDGE3 (527953) 115.0 kV Transmission Circuit #1 b.2. WIPP 3 (528009) 115.0 kV to SAND_DUNES 3 (528016) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on PHANTOM 7345.00 (528015) 345 kV Bus a. Apply Fault at the PHANTOM 7345.00 (528015) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHANTOM 3 (528013) 115.0 kV to PHANTOM 7 (528015) 345.0 kV to PHANTOM TR11 (528011) 13.2 kV Three Winding #1 b.2. PHANTOM 3 (528013) 115.0 kV to PHANTOM 7 (528015) 345.0 kV to PHANTOM TR21 (528012) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on CUSTERMTN 3115.00 (528239) 115 kV Bus a. Apply Fault at the CUSTERMTN 3115.00 (528239) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CUSTERMTN 3 (528239) 115.0 kV to RDRUNNER 3 (528025) 115.0 kV Transmission Circuit #1 b.2. CUSTERMTN 3 (528239) 115.0 kV to WHITTEN 3 (528540) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on HOBBS_INT 7345.00 (527896) 345 kV Bus a. Apply Fault at the HOBBS_INT 7345.00 (527896) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOBBS_INT 7 (527896) 345.0 kV to YOAKUM_345 (526936) 345.0 kV Transmission Circuit #1 b.2. HOBBS_INT 7 (527896) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on POTASH_JCT 6230.00 (527963) 230 kV Bus a. Apply Fault at the POTASH_JCT 6230.00 (527963) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POTASH_JCT 6 (527963) 230.0 kV to CUNNIGHM_N 6 (527865) 230.0 kV Transmission Circuit #1 b.2. POTASH_JCT 6 (527963) 230.0 kV to POTASH_JCT 3 (527962) 115.0 kV to POTASH_TR1 1 (527958) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on KIOWA 7345.00 (527965) 345 kV Bus a. Apply Fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KIOWA 7 (527965) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.2. KIOWA 7 (527965) 345.0 kV to N_LOVING 7 (528185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on RDRUNNER 7345.00 (528027) 345 kV Bus a. Apply Fault at the RDRUNNER 7345.00 (528027) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RDRUNNER 7 (528027) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.2. RDRUNNER 7 (528027) 345.0 kV to PHANTOM 7 (528015) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on CHINA_DRAW 7345.00 (528223) 345 kV Bus a. Apply Fault at the CHINA_DRAW 7345.00 (528223) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHINA_DRAW 7 (528223) 345.0 kV to PHANTOM 7 (528015) 345.0 kV Transmission Circuit #1 b.2. CHINA_DRAW 7 (528223) 345.0 kV to N_LOVING 7 (528185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on RED_BLUFF 3115.00 (528018) 115 kV Bus a. Apply Fault at the RED_BLUFF 3115.00 (528018) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RED_BLUFF 3 (528018) 115.0 kV to RDRUNNER 3 (528025) 115.0 kV Transmission Circuit #1 b.2. RED_BLUFF 3 (528018) 115.0 kV to WOLFCAMP_TP3 (528235) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_SPS1 | Single Phase Fault with Stuck Breaker on CROSSROADS (527656) 345 kV Bus a. Apply Fault at the CROSSROADS (527656) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. EDDY_CNTY 7 (527802) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.2. TOLK 7 (525549) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.3. RSVLT_CC_E 7 (527655) 345.0 kV to Trip Bus # b.4. MILO_WIND 1 (527653) 0.7 kV to Trip Bus # b.5. RSVLT_GEN1 1 (527651) 0.7 kV to Trip Bus # b.6. RSVLT_GEN2 1 (527652) 0.7 kV to Trip Bus # b.7. RSVLT_CC_W 7 (527654) 345.0 kV to Trip Bus # b.8. SAGSFT3_2.21 (527605) 0.7 kV to Generator #1 b.9. SAGSFT4_2.21 (527607) 0.7 kV to Generator #1 b.10. SAGSFT1_2.21 (527614) 0.7 kV to Generator #1 b.11. SAGSFT1_2.01 (527615) 0.7 kV to Generator #1 b.12. SAGSFT2_2.21 (527617) 0.7 kV to Generator #1 b.13. SAGSFT2_2.01 (527618) 0.7 kV to Generator #1 b.14. SAGA_SCOL 7 (527610) 345.0 kV to Load #1 b.15. SAGA_SCOL 7 (527610) 345.0 kV to Load #2 b.16. SAGA_NDCOL 7 (527598) 345.0 kV to Trip Bus # b.17. SAGA_SDCOL 7 (527599) 345.0 kV to Trip Bus # b.18. SAGA_SMEAS 7 (527600) 345.0 kV to Trip Bus # b.19. SAGA_NCOL 7 (527601) 345.0 kV to Trip Bus # b.20. SAGANCOL1 1 (527602) 34.5 kV to Trip Bus # b.21. SAGANCOL2 1 (527603) 34.5 kV to Trip Bus # b.22. GRDXFR3 1 (527604) 0.5 kV to Trip Bus # b.23. SAGSFT3_2.21 (527605) 0.7 kV to Trip Bus # b.24. GRDXFR4 1 (527606) 0.5 kV to Trip Bus # b.25. SAGSFT4_2.21 (527607) 0.7 kV to Trip Bus # b.26. SUB BUS #3 1 (527608) 34.5 kV to Trip Bus # b.27. SUB BUS #4 1 (527609) 34.5 kV to Trip Bus # b.28. SAGA_SCOL 7 (527610) 345.0 kV to Trip Bus # b.29. SAGASCOL1 1 (527611) 34.5 kV to Trip Bus # b.30. SAGASCOL2 1 (527612) 34.5 kV to Trip Bus # b.31. GRDXFR1 1 (527613) 0.5 kV to Trip Bus # b.32. SAGSFT1_2.21 (527614) 0.7 kV to Trip Bus # b.33. SAGSFT1_2.01 (527615) 0.7 kV to Trip Bus # b.34. GRDXFR2 1 (527616) 0.5 kV to Trip Bus # b.35. SAGSFT2_2.21 (527617) 0.7 kV to Trip Bus # b.36. SAGSFT2_2.01 (527618) 0.7 kV to Trip Bus # b.37. SAGA_NCLTR31 (527621) 13.8 kV to Trip Bus # b.38. SAGA_NCLTR41 (527622) 13.8 kV to Trip Bus # b.39. SAGA_SCLTR11 (527623) 13.8 kV to Trip Bus # b.40. SAGA_SCLTR21 (527624) 13.8 kV to Trip Bus # b.41. SUB BUS #1 (527628) 34.5 kV to Trip Bus # b.42. SUB BUS #2 (527629) 34.5 kV to Trip Bus # b.43. CROSSROADS 7 (527656) 345.0 kV to Trip Bus # b.44. RSVLT_WIND11 (527658) 34.5 kV to Trip Bus # b.45. RSVLT_WIND21 (527659) 34.5 kV to Trip Bus # b.46. RSVLT_COL1 1 (527660) 34.5 kV to Trip Bus # b.47. RSVLT_COL2 1 (527661) 34.5 kV to Trip Bus # b.48. RSVLT_TR1 1 (527662) 13.2 kV to Trip Bus # b.49. RSVLT_TR2 1 (527663) 13.2 kV to Trip Bus # b.50. RSVLT_COL1 7 (527666) 345.0 kV to Trip Bus # b.51. RSVLT_COL2 7 (527667) 345.0 kV to Trip Bus # b.52. MILO_CB (577120) 34.5 kV to Trip Bus # b.53. MILO_WND (577121) 34.5 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_SPS2 | Single Phase Fault with Stuck Breaker on CHINA_DRAW (528223) 345 kV Bus a. Apply Fault at the CHINA_DRAW (528223) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHINA_DRAW 7 (528223) 345.0 kV to PHANTOM 7 (528015) 345.0 kV Transmission Circuit #1 b.2. CHINA_DRAW 3 (528222) 115.0 kV to CHINA_DRAW 7 (528223) 345.0 kV to CHINA_DRAW 1 (528219) 13.2 kV Three Winding #1 b.3. CHINA_DRAW 1 (528219) 13.2 kV to Trip Bus # b.4. CARPENTER 7 (523823) 345.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_SPS3 | Single Phase Fault with Stuck Breaker on CHINA_DRAW (528223) 345 kV Bus a. Apply Fault at the CHINA_DRAW (528223) 345 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. CHINA_DRAW 3 (528222) 115.0 kV to CHINA_DRAW 7 (528223) 345.0 kV to CHINA_DRAW 1 (528219) 13.2 kV Three Winding #1 b.2. CHINA_DRAW 7 (528223) 345.0 kV to N_LOVING 7 (528185) 345.0 kV Transmission Circuit #1 b.3. CHINA_DRAW 7 (528223) 345.0 kV to PHANTOM 7 (528015) 345.0 kV Transmission Circuit #1 b.5. CHINA_DRAW 1 (528219) 13.2 kV to Trip Bus # b.6. CARPENTER 7 (523823) 345.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_SPS4 | Single Phase Fault with Stuck Breaker on CHINA_DRAW (528223) 345 kV Bus a. Apply Fault at the CHINA_DRAW (528223) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHINA_DRAW 7 (528223) 345.0 kV to CHINA_DRAW 3 (528222) 115.0 kV to CHINA_DRAW 1 (528219) 13.2 kV Three Winding #1 b.2. CHINA_DRAW 7 (528223) 345.0 kV to N_LOVING 7 (528185) 345.0 kV Transmission Circuit #1 b.3. CHINA_DRAW 7 (528223) 345.0 kV to PHANTOM 7 (528015) 345.0 kV Transmission Circuit #1 b.4. CHINA_DRAW 1 (528219) 13.2 kV to Trip Bus # b.5. CARPENTER 7 (523823) 345.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_SPS5 | Single Phase Fault with Stuck Breaker on EDDY_CNTY (527802) 345 kV Bus a. Apply Fault at the EDDY_CNTY (527802) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDDY_CNTY 7 (527802) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.2. EDDY_CNTY 7 (527802) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.3. EDDY_CNTY 7 (527802) 345.0 kV to EDDY_NORTH 6 (527799) 230.0 kV to EDDY_TR 1 (527796) 13.2 kV Three Winding #1 b.4. EDDY_TR 1 (527796) 13.2 kV to Trip Bus # b.5. EDDY_CNTY 7 (527802) 345.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_SPS6 | Single Phase Fault with Stuck Breaker on EDDY_CNTY (527802) 345 kV Bus a. Apply Fault at the EDDY_CNTY (527802) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDDY_CNTY 7 (527802) 345.0 kV to EDDY_NORTH 6 (527799) 230.0 kV to EDDY_TR 1 (527796) 13.2 kV Three Winding #1 b.2. EDDY_CNTY 7 (527802) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.3. EDDY_CNTY 7 (527802) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.4. EDDY_TR 1 (527796) 13.2 kV to Trip Bus # b.5. EDDY_CNTY 7 (527802) 345.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_SPS7 | Single Phase Fault with Stuck Breaker on EDDY_CNTY (527802) 345 kV Bus a. Apply Fault at the EDDY_CNTY (527802) 345 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. EDDY_NORTH 6 (527799) 230.0 kV to EDDY_CNTY 7 (527802) 345.0 kV to EDDY_TR 1 (527796) 13.2 kV Three Winding #1 b.2. EDDY_CNTY 7 (527802) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.3. EDDY_CNTY 7 (527802) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.5. EDDY_TR 1 (527796) 13.2 kV to Trip Bus # b.6. EDDY_CNTY 7 (527802) 345.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_SPS8 | Single Phase Fault with Stuck Breaker on HOBBS_INT (527896) 345 kV Bus a. Apply Fault at the HOBBS_INT (527896) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HOBBS_INT 7 (527896) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.2. HOBBS_INT 7 (527896) 345.0 kV to YOAKUM_345 (526936) 345.0 kV Transmission Circuit #1 b.3. HOBBS_TR3 1 (527895) 13.2 kV to Trip Bus # b.4. HOBBS_INT 7 (527896) 345.0 kV to Trip Bus # | P4 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206). The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. The issue was also observed in the base case and was not attributed to GEN-2016-121 for any limitation. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_SPS9 | Single Phase Fault with Stuck Breaker on KIOWA (527965) 345 kV Bus a. Apply Fault at the KIOWA (527965) 345 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. KIOWA 3 (527966) 115.0 kV to KIOWA 7 (527965) 345.0 kV to KIOWA_TR1 1 (527964) 13.2 kV Three Winding #1 b.2. KIOWA 7 (527965) 345.0 kV to RDRUNNER 7 (528027) 345.0 kV Transmission Circuit #1 b.4. KIOWA_TR1 1 (527964) 13.2 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_SPS10 | Single Phase Fault with Stuck Breaker on KIOWA (527965) 345 kV Bus a. Apply Fault at the KIOWA (527965) 345 kV Bus b. Clear Fault after 20 cycles and trip the following elements: b.1. KIOWA 7 (527965) 345.0 kV to RDRUNNER 7 (528027) 345.0 kV Transmission Circuit #1 b.2. KIOWA 3 (527966) 115.0 kV to KIOWA 7 (527965) 345.0 kV to KIOWA_TR1 1 (527964) 13.2 kV Three Winding #1 b.3. KIOWA_TR1 1 (527964) 13.2 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_SPS11 | Single Phase Fault with Stuck Breaker on N_LOVING (528185) 345 kV Bus a. Apply Fault at the N_LOVING (528185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N_LOVING 7 (528185) 345.0 kV to CHINA_DRAW 7 (528223) 345.0 kV Transmission Circuit #1 b.2. N_LOVING 7 (528185) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.3. NORTH_LOVNG3 (528182) 115.0 kV to N_LOVING 7 (528185) 345.0 kV to N_LOVING TR1 (528186) 13.2 kV Three Winding #1 b.4. N_LOVING TR1 (528186) 13.2 kV to Trip Bus # b.5. N_LOVING 7 (528185) 345.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_SPS12 | Single Phase Fault with Stuck Breaker on N_LOVING (528185) 345 kV Bus a. Apply Fault at the N_LOVING (528185) 345 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. NORTH_LOVNG3 (528182) 115.0 kV to N_LOVING 7 (528185) 345.0 kV to N_LOVING TR1 (528186) 13.2 kV Three Winding #1 b.2. N_LOVING 7 (528185) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.3. N_LOVING 7 (528185) 345.0 kV to CHINA_DRAW 7 (528223) 345.0 kV Transmission Circuit #1 b.5. N_LOVING TR1 (528186) 13.2 kV to Trip Bus # b.6. N_LOVING 7 (528185) 345.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_SPS13 | Single Phase Fault with Stuck Breaker on N_LOVING (528185) 345 kV Bus a. Apply Fault at the N_LOVING (528185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N_LOVING 7 (528185) 345.0 kV to NORTH_LOVNG3 (528182) 115.0 kV to N_LOVING TR1 (528186) 13.2 kV Three Winding #1 b.2. N_LOVING 7 (528185) 345.0 kV to CHINA_DRAW 7 (528223) 345.0 kV Transmission Circuit #1 b.3. N_LOVING 7 (528185) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.4. N_LOVING TR1 (528186) 13.2 kV to Trip Bus # b.5. N_LOVING 7 (528185) 345.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_SPS14 | Single Phase Fault with Stuck Breaker on ROADRUNNER (528027) 345 kV Bus a. Apply Fault at the ROADRUNNER (528027) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RDRUNNER 7 (528027) 345.0 kV to PHANTOM 7 (528015) 345.0 kV Transmission Circuit #1 b.2. RDRUNNER 7 (528027) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.3. RDRUNNER 3 (528025) 115.0 kV to RDRUNNER 7 (528027) 345.0 kV to RDRNNER_TR11 (528023) 13.2 kV Three Winding #1 b.4. RDRNNER_TR11 (528023) 13.2 kV to Trip Bus # b.5. RDRUNNER 7 (528027) 345.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_SPS15 | Single Phase Fault with Stuck Breaker on ROADRUNNER (528027) 345 kV Bus a. Apply Fault at the ROADRUNNER (528027) 345 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. RDRUNNER 3 (528025) 115.0 kV to RDRUNNER 7 (528027) 345.0 kV to RDRNNER_TR11 (528023) 13.2 kV Three Winding #1 b.2. RDRUNNER 7 (528027) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.3. RDRUNNER 7 (528027) 345.0 kV to PHANTOM 7 (528015) 345.0 kV Transmission Circuit #1 b.5. RDRNNER_TR11 (528023) 13.2 kV to Trip Bus # b.6. RDRUNNER 7 (528027) 345.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_SPS16 | Single Phase Fault with Stuck Breaker on ROADRUNNER (528027) 345 kV Bus a. Apply Fault at the ROADRUNNER (528027) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RDRUNNER 7 (528027) 345.0 kV to RDRUNNER 3 (528025) 115.0 kV to RDRNNER_TR11 (528023) 13.2 kV Three Winding #1 b.2. RDRUNNER 7 (528027) 345.0 kV to PHANTOM 7 (528015) 345.0 kV Transmission Circuit #1 b.3. RDRUNNER 7 (528027) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.4. RDRNNER_TR11 (528023) 13.2 kV to Trip Bus # b.5. RDRUNNER 7 (528027) 345.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_SPS17 | Single Phase Fault with Stuck Breaker on YOAKUM (526936) 345 kV Bus a. Apply Fault at the YOAKUM (526936) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. YOAKUM_345 (526936) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.3. YOAKUM 6 (526935) 230.0 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM_TR1 (526937) 13.2 kV Three Winding #1 b.4. YOAKUM_TR1 (526937) 13.2 kV to Trip Bus # b.5. YOAKUM_345 (526936) 345.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_SPS18 | Single Phase Fault with Stuck Breaker on YOAKUM (526936) 345 kV Bus a. Apply Fault at the YOAKUM (526936) 345 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. YOAKUM 6 (526935) 230.0 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM_TR1 (526937) 13.2 kV Three Winding #1 b.2. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_345 (526936) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.5. YOAKUM_TR1 (526937) 13.2 kV to Trip Bus # b.6. YOAKUM_345 (526936) 345.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_SPS19 | Single Phase Fault with Stuck Breaker on YOAKUM (526936) 345 kV Bus a. Apply Fault at the YOAKUM (526936) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. YOAKUM_345 (526936) 345.0 kV to YOAKUM 6 (526935) 230.0 kV to YOAKUM_TR1 (526937) 13.2 kV Three Winding #1 b.2. YOAKUM_345 (526936) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.4. YOAKUM_TR1 (526937) 13.2 kV to Trip Bus # b.5. YOAKUM_345 (526936) 345.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_LOCAL_FAULT_SPS20 | Single Phase Fault with Stuck Breaker on POTASH (527962) 115 kV Bus a. Apply Fault at the POTASH (527962) 115 kV Bus b. Clear Fault after 19.02 cycles and trip the following elements: b.1. POTASH_JCT 3 (527962) 115.0 kV to PCA 3 (527930) 115.0 kV Transmission Circuit #1 b.2. XTO_DI9_TP 3 (528064) 115.0 kV to LIVSTNRIDGE3 (527953) 115.0 kV Transmission Circuit #1 b.3. POTASH_JCT 3 (527962) 115.0 kV to CARLSBAD 3 (528160) 115.0 kV Transmission Circuit #1 b.4. POTASH_TR1 1 (527958) 13.2 kV to Trip Bus # b.5. NATPOT_TP 2 (528145) 69.0 kV to PCA 2 (527929) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. GRAPEVN_TR11 (523769) 13.2 kV to GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on STLN-DEMARC6230.00 (523779) 230 kV Bus a. Apply Fault at the STLN-DEMARC6230.00 (523779) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEETWT6 (511541) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 b.3. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply Fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. NOVUS_WND 1 (523107) 4.2 kV to NOVUS1 1 (523109) 34.5 kV Two Winding #1 b.3. NOVUS1 1 (523109) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.4. G06-44-2 (560581) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.5. NOVUS1_TR1 1 (523110) 13.8 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV Three Winding #1 b.6. NOVUS1 3 (523111) 115.0 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G06-44-3 (560585), G06-44-4 (560586) and HARRNGTON (523971,523972,523973) units. The issue was also observed in the base case. | Operational measures fixing the voltage setpoint of G06-44-3 (560585), G06-44-4 (560586) and HARRNGTON (523971,523972,523973) and HOBBS_PLT ( 527902,527901).
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 b.3. HITCHLAND 7 (523097) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on NOBLE_WND 7345.00 (523101) 345 kV Bus a. Apply Fault at the NOBLE_WND 7345.00 (523101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.2. NOBLE_WND 3 (523103) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.3. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-WT4-1 (523121) 0.6 kV Two Winding #1 b.4. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-LV4-1 (523127) 34.5 kV Transmission Circuit #1 b.5. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-WT2-1 (523123) 0.6 kV Two Winding #1 b.6. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-LV2-1 (523129) 34.5 kV Transmission Circuit #1 b.7. GRPLNS-LV4-1 (523127) 34.5 kV to GRPLNS-GT4-1 (523133) 0.5 kV Two Winding #1 b.8. NBLWND-LV2 1 (523128) 34.5 kV to GRPLNS-HV2-3 (523131) 115.0 kV Two Winding #1 b.9. GRPLNS-LV2-1 (523129) 34.5 kV to GRPLNS-GT2-1 (523132) 0.5 kV Two Winding #1 b.10. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-LV4-1 (523127) 34.5 kV Two Winding #1 b.11. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.12. GRPLNS-HV2-3 (523131) 115.0 kV to GRPLNS-LV2-1 (523129) 34.5 kV Two Winding #1 b.13. NOBLE_TR 1 (523102) 13.8 kV to NOBLE_WND 7 (523101) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV Three Winding #1 b.14. NOBLE_WND 3 (523103) 115.0 kV to NOBLE_WND 7 (523101) 345.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply Fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.2. POTTER_CO 7 (523961) 345.0 kV to SPNSPUR_WND7 (524296) 345.0 kV Transmission Circuit #1 b.3. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 b.4. POTTER_CO 7 (523961) 345.0 kV to GRAPEVINE (560035) 345.0 kV Transmission Circuit #1 b.5. SPNSPUR_GEN1 (524295) 0.7 kV to SPNSPUR_WND1 (524294) 34.5 kV Two Winding #1 b.6. SPNSPUR_WND7 (524296) 345.0 kV to SPNSPUR_COL7 (524299) 345.0 kV Transmission Circuit #1 b.7. POTTER_TR 1 (523957) 13.2 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips LANOGSU1 (523812). | Protection disabled without any impact on stability.
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply Fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to YOAKUM_345 (526936) 345.0 kV Transmission Circuit #1 b.2. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_345 (526936) 345.0 kV to GEN-2019-011 (763516) 345.0 kV Transmission Circuit #1 b.4. YOAKUM 6 (526935) 230.0 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM_TR1 (526937) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on ELK_CT1 345.00 (525850) 345 kV Bus a. Apply Fault at the ELK_CT1 345.00 (525850) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to ELK_2 1 (525845) 18.0 kV Two Winding #1 b.2. TUCO_INT 7 (525832) 345.0 kV to ELK_CT1 (525850) 345.0 kV Transmission Circuit #1 b.3. TUCO_INT 7 (525832) 345.0 kV to YOAKUM_345 (526936) 345.0 kV Transmission Circuit #1 b.4. ELK_CT1 (525850) 345.0 kV to ELK_1 1 (525844) 18.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Transfer | GROUP5_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELER 6 (523777) 230.0 kV to WHEELER 3 (523776) 115.0 kV to WHEELER_TR11 (523774) 13.2 kV Three Winding #1 b.2. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_005 | 3 Phase fault on HOBBS_INT 3115.00 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3115.00 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 (527891) 115.0 kV to MADDOX 3 (528355) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_010 | 3 Phase fault on POTASH_JCT 3115.00 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3115.00 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 (527962) 115.0 kV to CARLSBAD 3 (528160) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_014 | 3 Phase fault on WOLFCAMP_TP3115.00 (528235) 115 kV Bus a. Apply fault at the WOLFCAMP_TP3115.00 (528235) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 (528013) 115.0 kV to BOPCO_PKRLK3 (528020) 115.0 kV Transmission Circuit #1 b.2. RED_BLUFF 3 (528018) 115.0 kV to WOLFCAMP_TP3 (528235) 115.0 kV Transmission Circuit #1 b.3. BOPCO_PKRLK3 (528020) 115.0 kV to WOLFCAMP_TP3 (528235) 115.0 kV Transmission Circuit #1 b.4. WOLFCAMP_TP3 (528235) 115.0 kV to WOLFCAMP 3 (528236) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_015 | 3 Phase fault on PHANTOM 3115.00 (528013) 115 kV Bus a. Apply fault at the PHANTOM 3115.00 (528013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 (528013) 115.0 kV to WOOD_DRAW 3 (528228) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_016 | 3 Phase fault on HOBBS_INT 3115.00 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3115.00 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 (527891) 115.0 kV to LE-WEST_SUB3 (528333) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_017 | 3 Phase fault on NORTH_LOVNG3115.00 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3115.00 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 (528182) 115.0 kV to HOPI_SUB 3 (528226) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_018 | 3 Phase fault on BLACKRIVER 3115.00 (528193) 115 kV Bus a. Apply fault at the BLACKRIVER 3115.00 (528193) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 (528182) 115.0 kV to BLACKRIVER 3 (528193) 115.0 kV Transmission Circuit #1 b.2. SENDERO +3 (528184) 115.0 kV to BLACKRIVER 3 (528193) 115.0 kV Transmission Circuit #1 b.3. SENDERO +3 (528184) 115.0 kV to BLCKRVR_DST3 (528206) 115.0 kV Transmission Circuit #1 b.4. BLCKRVR_DST3 (528206) 115.0 kV to CHINA_DRAW 3 (528222) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_020 | 3 Phase fault on RDRUNNER 3115.00 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3115.00 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 (528025) 115.0 kV to BATTLE_AXE 3 (528040) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_022 | 3 Phase fault on CHINA_DRAW 3115.00 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3115.00 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 (528222) 115.0 kV to WOOD_DRAW 3 (528228) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_023 | 3 Phase fault on CHINA_DRAW 3115.00 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3115.00 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 (528222) 115.0 kV to CHVRN_EDDYS3 (528252) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_025 | 3 Phase fault on RED_BLUFF 3115.00 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3115.00 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RED_BLUFF 3 (528018) 115.0 kV to RDRUNNER 3 (528025) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_026 | 3 Phase fault on AGAVE_RHILL3115.00 (528230) 115 kV Bus a. Apply fault at the AGAVE_RHILL3115.00 (528230) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 (528025) 115.0 kV to AGAVE_RHILL3 (528230) 115.0 kV Transmission Circuit #1 b.2. AGAVE_RHILL3 (528230) 115.0 kV to OCHOA 3 (528232) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_027 | 3 Phase fault on RDRUNNER 3115.00 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3115.00 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 (528025) 115.0 kV to CUSTERMTN 3 (528239) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_029 | 3 Phase fault on INTREPDW_TP3115.00 (527999) 115 kV Bus a. Apply fault at the INTREPDW_TP3115.00 (527999) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIVSTNRIDGE3 (527953) 115.0 kV to XTO_DI9_TP 3 (528064) 115.0 kV Transmission Circuit #1 b.2. POTASH_JCT 3 (527962) 115.0 kV to INTREPDW_TP3 (527999) 115.0 kV Transmission Circuit #1 b.3. INTREPDW_TP3 (527999) 115.0 kV to INTREPIDWST3 (528000) 115.0 kV Transmission Circuit #1 b.4. INTREPDW_TP3 (527999) 115.0 kV to IMC_#1_TP 3 (528035) 115.0 kV Transmission Circuit #1 b.5. IMC_#1_TP 3 (528035) 115.0 kV to IMC_#1 3 (528037) 115.0 kV Transmission Circuit #1 b.6. IMC_#1_TP 3 (528035) 115.0 kV to XTO_DI9_TP 3 (528064) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_031 | 3 Phase fault on POTASH_JCT 3115.00 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3115.00 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 (527962) 115.0 kV to KIOWA 3 (527966) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_033 | 3 Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 (526935) 230.0 kV to INK_BASIN 6 (527028) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_037 | 3 Phase fault on EDDY_NORTH 6230.00 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6230.00 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 (527799) 230.0 kV to CUNNIGHM_N 6 (527865) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_038 | 3 Phase fault on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7 (527802) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_039 | 3 Phase fault on CUNNIGHM_N 6230.00 (527865) 230 kV Bus a. Apply fault at the CUNNIGHM_N 6230.00 (527865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_N 6 (527865) 230.0 kV to POTASH_JCT 6 (527963) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_040 | 3 Phase fault on CUNNIGHM_S 6230.00 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6230.00 (527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6 (527867) 230.0 kV to HOBBS_INT 6 (527894) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_041 | 3 Phase fault on HOBBS_INT 6230.00 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6230.00 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 6 (527894) 230.0 kV to ANDREWS 6 (528604) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_042 | 3 Phase fault on HOBBS_INT 7345.00 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7345.00 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 (527896) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_049 | 3 Phase fault on KIOWA 7345.00 (527965) 345 kV Bus a. Apply fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 (527965) 345.0 kV to RDRUNNER 7 (528027) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_050 | 3 Phase fault on KIOWA 7345.00 (527965) 345 kV Bus a. Apply fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 (527965) 345.0 kV to N_LOVING 7 (528185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_051 | 3 Phase fault on PHANTOM 3115.00 (528013) 115 kV Bus a. Apply fault at the PHANTOM 3115.00 (528013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 (528013) 115.0 kV to MALAGABEND 3 (528194) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_052 | 3 Phase fault on PHANTOM 7345.00 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7345.00 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 (528015) 345.0 kV to RDRUNNER 7 (528027) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_053 | 3 Phase fault on PHANTOM 7345.00 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7345.00 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 (528015) 345.0 kV to CHINA_DRAW 7 (528223) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_054 | 3 Phase fault on RR_SVC_HV 3115.00 (528024) 115 kV Bus a. Apply fault at the RR_SVC_HV 3115.00 (528024) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RR_SVC_HV 3 (528024) 115.0 kV to RDRUNNER 3 (528025) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_055 | 3 Phase fault on 7-RIVERS 6230.00 (528095) 230 kV Bus a. Apply fault at the 7-RIVERS 6230.00 (528095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 7-RIVERS 6 (528095) 230.0 kV to PECOS 6 (528179) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_056 | 3 Phase fault on NORTH_LOVNG3115.00 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3115.00 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 (528182) 115.0 kV to SOUTH_LOVNG3 (528192) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_057 | 3 Phase fault on NORTH_LOVNG3115.00 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3115.00 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 (528182) 115.0 kV to AGAVE_PDURO3 (528195) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_058 | 3 Phase fault on N_LOVING 7345.00 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7345.00 (528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N_LOVING 7 (528185) 345.0 kV to CHINA_DRAW 7 (528223) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_059 | 3 Phase fault on SOUTH_LOVNG3115.00 (528192) 115 kV Bus a. Apply fault at the SOUTH_LOVNG3115.00 (528192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOUTH_LOVNG3 (528192) 115.0 kV to MALAGABEND 3 (528194) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_060 | 3 Phase fault on CHINA_DRAW 3115.00 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3115.00 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 (528222) 115.0 kV to CD_SVC_HV 3 (528225) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_061 | 3 Phase fault on CUNNIGHM_N 6230.00 (527865) 230 kV Bus a. Apply fault at the CUNNIGHM_N 6230.00 (527865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_N 6 (527865) 230.0 kV to CUNNIGHM_S 6 (527867) 230.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_064 | 3 Phase fault on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7 (527802) 345.0 kV to EDDY_NORTH 6 (527799) 230.0 kV to EDDY_TR 1 (527796) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_065 | 3 Phase fault on CUNNIGHM_S 6230.00 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6230.00 (527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6 (527867) 230.0 kV to CUNNINHAM 3 (527864) 115.0 kV to CUNNHM_TR1 1 (527863) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_066 | 3 Phase fault on HOBBS_INT 6230.00 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6230.00 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 6 (527894) 230.0 kV to HOBBS_INT 3 (527891) 115.0 kV to HOBBS_TR1 1 (527890) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_067 | 3 Phase fault on HOBBS_INT 6230.00 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6230.00 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 6 (527894) 230.0 kV to HOBBS_INT 3 (527891) 115.0 kV to HOBBS_TR2 1 (527889) 13.2 kV Three Winding #2 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_068 | 3 Phase fault on HOBBS_INT 7345.00 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7345.00 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 (527896) 345.0 kV to HOBBS_INT 6 (527894) 230.0 kV to HOBBS_TR3 1 (527895) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_069 | 3 Phase fault on PCA 3115.00 (527930) 115 kV Bus a. Apply fault at the PCA 3115.00 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 (527930) 115.0 kV to PCA 2 (527929) 69.0 kV to PCA_TR1 1 (527928) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_070 | 3 Phase fault on POTASH_JCT 3115.00 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3115.00 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 (527962) 115.0 kV to POTASH_JCT 2 (527961) 69.0 kV to POTASH_TR3 1 (527960) 13.2 kV Three Winding #2 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_071 | 3 Phase fault on POTASH_JCT 3115.00 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3115.00 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 (527962) 115.0 kV to POTASH_JCT 2 (527961) 69.0 kV to POTASH_TR2 1 (527959) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_072 | 3 Phase fault on POTASH_JCT 6230.00 (527963) 230 kV Bus a. Apply fault at the POTASH_JCT 6230.00 (527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 6 (527963) 230.0 kV to POTASH_JCT 3 (527962) 115.0 kV to POTASH_TR1 1 (527958) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_073 | 3 Phase fault on KIOWA 7345.00 (527965) 345 kV Bus a. Apply fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 (527965) 345.0 kV to KIOWA 3 (527966) 115.0 kV to KIOWA_TR1 1 (527964) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_074 | 3 Phase fault on PHANTOM 7345.00 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7345.00 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 (528015) 345.0 kV to PHANTOM 3 (528013) 115.0 kV to PHANTOM TR11 (528011) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_075 | 3 Phase fault on PHANTOM 7345.00 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7345.00 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 (528015) 345.0 kV to PHANTOM 3 (528013) 115.0 kV to PHANTOM TR21 (528012) 13.2 kV Three Winding #2 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_076 | 3 Phase fault on RDRUNNER 7345.00 (528027) 345 kV Bus a. Apply fault at the RDRUNNER 7345.00 (528027) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RDRUNNER 7 (528027) 345.0 kV to RDRUNNER 3 (528025) 115.0 kV to RDRNNER_TR11 (528023) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_079 | 3 Phase fault on PECOS 6230.00 (528179) 230 kV Bus a. Apply fault at the PECOS 6230.00 (528179) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECOS 6 (528179) 230.0 kV to PECOS 3 (528178) 115.0 kV to PECOS_TR1 1 (528176) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_080 | 3 Phase fault on N_LOVING 7345.00 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7345.00 (528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N_LOVING 7 (528185) 345.0 kV to NORTH_LOVNG3 (528182) 115.0 kV to N_LOVING TR1 (528186) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_081 | 3 Phase fault on CHINA_DRAW 7345.00 (528223) 345 kV Bus a. Apply fault at the CHINA_DRAW 7345.00 (528223) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHINA_DRAW 7 (528223) 345.0 kV to CHINA_DRAW 3 (528222) 115.0 kV to CHINA_DRAW 1 (528219) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_085 | 3 Phase fault on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7 (527802) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_088 | 3 Phase fault on POTASH_JCT 3115.00 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3115.00 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 (527962) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_090 | 3 Phase fault on RED_BLUFF 3115.00 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3115.00 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RED_BLUFF 3 (528018) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_092 | 3 Phase fault on NORTH_LOVNG3115.00 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3115.00 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 (528182) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_093 | 3 Phase fault on N_LOVING 7345.00 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7345.00 (528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N_LOVING 7 (528185) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_095 | 3 Phase fault on CHINA_DRAW 3115.00 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3115.00 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 (528222) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P1_LOCAL_FAULT_096 | 3 Phase fault on WOOD_DRAW 3115.00 (528228) 115 kV Bus a. Apply fault at the WOOD_DRAW 3115.00 (528228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOOD_DRAW 3 (528228) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on HOBBS_INT 6 (527894) 115 kV Bus a. Apply Fault at the HOBBS_INT 6 (527894) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOBBS_INT 6 (527894) 230.0 kV to remove bus # | P4 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on KIOWA 7345.00 (527965) 345 kV Bus a. Apply Fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KIOWA 7 (527965) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.2. KIOWA 7 (527965) 345.0 kV to N_LOVING 7 (528185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P4_LOCAL_FAULT_SPS8 | Single Phase Fault with Stuck Breaker on HOBBS_INT (527896) 345 kV Bus a. Apply Fault at the HOBBS_INT (527896) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HOBBS_INT 7 (527896) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.2. HOBBS_INT 7 (527896) 345.0 kV to YOAKUM_345 (526936) 345.0 kV Transmission Circuit #1 b.3. HOBBS_TR3 1 (527895) 13.2 kV to Trip Bus # b.4. HOBBS_INT 7 (527896) 345.0 kV to Trip Bus # | P4 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply Fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. NOVUS_WND 1 (523107) 4.2 kV to NOVUS1 1 (523109) 34.5 kV Two Winding #1 b.3. NOVUS1 1 (523109) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.4. G06-44-2 (560581) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.5. NOVUS1_TR1 1 (523110) 13.8 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV Three Winding #1 b.6. NOVUS1 3 (523111) 115.0 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_010 | 3 Phase fault on POTASH_JCT 3115.00 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3115.00 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 (527962) 115.0 kV to CARLSBAD 3 (528160) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_014 | 3 Phase fault on WOLFCAMP_TP3115.00 (528235) 115 kV Bus a. Apply fault at the WOLFCAMP_TP3115.00 (528235) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 (528013) 115.0 kV to BOPCO_PKRLK3 (528020) 115.0 kV Transmission Circuit #1 b.2. RED_BLUFF 3 (528018) 115.0 kV to WOLFCAMP_TP3 (528235) 115.0 kV Transmission Circuit #1 b.3. BOPCO_PKRLK3 (528020) 115.0 kV to WOLFCAMP_TP3 (528235) 115.0 kV Transmission Circuit #1 b.4. WOLFCAMP_TP3 (528235) 115.0 kV to WOLFCAMP 3 (528236) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_015 | 3 Phase fault on PHANTOM 3115.00 (528013) 115 kV Bus a. Apply fault at the PHANTOM 3115.00 (528013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 (528013) 115.0 kV to WOOD_DRAW 3 (528228) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_017 | 3 Phase fault on NORTH_LOVNG3115.00 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3115.00 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 (528182) 115.0 kV to HOPI_SUB 3 (528226) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_020 | 3 Phase fault on RDRUNNER 3115.00 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3115.00 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 (528025) 115.0 kV to BATTLE_AXE 3 (528040) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_022 | 3 Phase fault on CHINA_DRAW 3115.00 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3115.00 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 (528222) 115.0 kV to WOOD_DRAW 3 (528228) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_023 | 3 Phase fault on CHINA_DRAW 3115.00 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3115.00 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 (528222) 115.0 kV to CHVRN_EDDYS3 (528252) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_025 | 3 Phase fault on RED_BLUFF 3115.00 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3115.00 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RED_BLUFF 3 (528018) 115.0 kV to RDRUNNER 3 (528025) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_026 | 3 Phase fault on AGAVE_RHILL3115.00 (528230) 115 kV Bus a. Apply fault at the AGAVE_RHILL3115.00 (528230) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 (528025) 115.0 kV to AGAVE_RHILL3 (528230) 115.0 kV Transmission Circuit #1 b.2. AGAVE_RHILL3 (528230) 115.0 kV to OCHOA 3 (528232) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_027 | 3 Phase fault on RDRUNNER 3115.00 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3115.00 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 (528025) 115.0 kV to CUSTERMTN 3 (528239) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_029 | 3 Phase fault on INTREPDW_TP3115.00 (527999) 115 kV Bus a. Apply fault at the INTREPDW_TP3115.00 (527999) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIVSTNRIDGE3 (527953) 115.0 kV to XTO_DI9_TP 3 (528064) 115.0 kV Transmission Circuit #1 b.2. POTASH_JCT 3 (527962) 115.0 kV to INTREPDW_TP3 (527999) 115.0 kV Transmission Circuit #1 b.3. INTREPDW_TP3 (527999) 115.0 kV to INTREPIDWST3 (528000) 115.0 kV Transmission Circuit #1 b.4. INTREPDW_TP3 (527999) 115.0 kV to IMC_#1_TP 3 (528035) 115.0 kV Transmission Circuit #1 b.5. IMC_#1_TP 3 (528035) 115.0 kV to IMC_#1 3 (528037) 115.0 kV Transmission Circuit #1 b.6. IMC_#1_TP 3 (528035) 115.0 kV to XTO_DI9_TP 3 (528064) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_031 | 3 Phase fault on POTASH_JCT 3115.00 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3115.00 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 (527962) 115.0 kV to KIOWA 3 (527966) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_037 | 3 Phase fault on EDDY_NORTH 6230.00 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6230.00 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 (527799) 230.0 kV to CUNNIGHM_N 6 (527865) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_038 | 3 Phase fault on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7 (527802) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_040 | 3 Phase fault on CUNNIGHM_S 6230.00 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6230.00 (527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6 (527867) 230.0 kV to HOBBS_INT 6 (527894) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_042 | 3 Phase fault on HOBBS_INT 7345.00 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7345.00 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 (527896) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_049 | 3 Phase fault on KIOWA 7345.00 (527965) 345 kV Bus a. Apply fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 (527965) 345.0 kV to RDRUNNER 7 (528027) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_050 | 3 Phase fault on KIOWA 7345.00 (527965) 345 kV Bus a. Apply fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 (527965) 345.0 kV to N_LOVING 7 (528185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_051 | 3 Phase fault on PHANTOM 3115.00 (528013) 115 kV Bus a. Apply fault at the PHANTOM 3115.00 (528013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 (528013) 115.0 kV to MALAGABEND 3 (528194) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_052 | 3 Phase fault on PHANTOM 7345.00 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7345.00 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 (528015) 345.0 kV to RDRUNNER 7 (528027) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_053 | 3 Phase fault on PHANTOM 7345.00 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7345.00 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 (528015) 345.0 kV to CHINA_DRAW 7 (528223) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_054 | 3 Phase fault on RR_SVC_HV 3115.00 (528024) 115 kV Bus a. Apply fault at the RR_SVC_HV 3115.00 (528024) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RR_SVC_HV 3 (528024) 115.0 kV to RDRUNNER 3 (528025) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_056 | 3 Phase fault on NORTH_LOVNG3115.00 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3115.00 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 (528182) 115.0 kV to SOUTH_LOVNG3 (528192) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_057 | 3 Phase fault on NORTH_LOVNG3115.00 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3115.00 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 (528182) 115.0 kV to AGAVE_PDURO3 (528195) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_058 | 3 Phase fault on N_LOVING 7345.00 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7345.00 (528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N_LOVING 7 (528185) 345.0 kV to CHINA_DRAW 7 (528223) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_059 | 3 Phase fault on SOUTH_LOVNG3115.00 (528192) 115 kV Bus a. Apply fault at the SOUTH_LOVNG3115.00 (528192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOUTH_LOVNG3 (528192) 115.0 kV to MALAGABEND 3 (528194) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_060 | 3 Phase fault on CHINA_DRAW 3115.00 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3115.00 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 (528222) 115.0 kV to CD_SVC_HV 3 (528225) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_061 | 3 Phase fault on CUNNIGHM_N 6230.00 (527865) 230 kV Bus a. Apply fault at the CUNNIGHM_N 6230.00 (527865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_N 6 (527865) 230.0 kV to CUNNIGHM_S 6 (527867) 230.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_062 | 3 Phase fault on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 (526936) 345.0 kV to YOAKUM 6 (526935) 230.0 kV to YOAKUM_TR1 (526937) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_064 | 3 Phase fault on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7 (527802) 345.0 kV to EDDY_NORTH 6 (527799) 230.0 kV to EDDY_TR 1 (527796) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_065 | 3 Phase fault on CUNNIGHM_S 6230.00 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6230.00 (527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6 (527867) 230.0 kV to CUNNINHAM 3 (527864) 115.0 kV to CUNNHM_TR1 1 (527863) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_066 | 3 Phase fault on HOBBS_INT 6230.00 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6230.00 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 6 (527894) 230.0 kV to HOBBS_INT 3 (527891) 115.0 kV to HOBBS_TR1 1 (527890) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_067 | 3 Phase fault on HOBBS_INT 6230.00 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6230.00 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 6 (527894) 230.0 kV to HOBBS_INT 3 (527891) 115.0 kV to HOBBS_TR2 1 (527889) 13.2 kV Three Winding #2 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_068 | 3 Phase fault on HOBBS_INT 7345.00 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7345.00 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 (527896) 345.0 kV to HOBBS_INT 6 (527894) 230.0 kV to HOBBS_TR3 1 (527895) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_069 | 3 Phase fault on PCA 3115.00 (527930) 115 kV Bus a. Apply fault at the PCA 3115.00 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 (527930) 115.0 kV to PCA 2 (527929) 69.0 kV to PCA_TR1 1 (527928) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_070 | 3 Phase fault on POTASH_JCT 3115.00 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3115.00 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 (527962) 115.0 kV to POTASH_JCT 2 (527961) 69.0 kV to POTASH_TR3 1 (527960) 13.2 kV Three Winding #2 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_071 | 3 Phase fault on POTASH_JCT 3115.00 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3115.00 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 (527962) 115.0 kV to POTASH_JCT 2 (527961) 69.0 kV to POTASH_TR2 1 (527959) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_072 | 3 Phase fault on POTASH_JCT 6230.00 (527963) 230 kV Bus a. Apply fault at the POTASH_JCT 6230.00 (527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 6 (527963) 230.0 kV to POTASH_JCT 3 (527962) 115.0 kV to POTASH_TR1 1 (527958) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_073 | 3 Phase fault on KIOWA 7345.00 (527965) 345 kV Bus a. Apply fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 (527965) 345.0 kV to KIOWA 3 (527966) 115.0 kV to KIOWA_TR1 1 (527964) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_074 | 3 Phase fault on PHANTOM 7345.00 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7345.00 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 (528015) 345.0 kV to PHANTOM 3 (528013) 115.0 kV to PHANTOM TR11 (528011) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_075 | 3 Phase fault on PHANTOM 7345.00 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7345.00 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 (528015) 345.0 kV to PHANTOM 3 (528013) 115.0 kV to PHANTOM TR21 (528012) 13.2 kV Three Winding #2 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_076 | 3 Phase fault on RDRUNNER 7345.00 (528027) 345 kV Bus a. Apply fault at the RDRUNNER 7345.00 (528027) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RDRUNNER 7 (528027) 345.0 kV to RDRUNNER 3 (528025) 115.0 kV to RDRNNER_TR11 (528023) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_077 | 3 Phase fault on CARLSBAD 3115.00 (528160) 115 kV Bus a. Apply fault at the CARLSBAD 3115.00 (528160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLSBAD 3 (528160) 115.0 kV to CARLSBAD 2 (528159) 69.0 kV to CRLSBAD_TR11 (528157) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_078 | 3 Phase fault on CARLSBAD 3115.00 (528160) 115 kV Bus a. Apply fault at the CARLSBAD 3115.00 (528160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLSBAD 3 (528160) 115.0 kV to CARLSBAD 2 (528159) 69.0 kV to CRLSBAD_TR21 (528158) 13.2 kV Three Winding #2 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_079 | 3 Phase fault on PECOS 6230.00 (528179) 230 kV Bus a. Apply fault at the PECOS 6230.00 (528179) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECOS 6 (528179) 230.0 kV to PECOS 3 (528178) 115.0 kV to PECOS_TR1 1 (528176) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_080 | 3 Phase fault on N_LOVING 7345.00 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7345.00 (528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N_LOVING 7 (528185) 345.0 kV to NORTH_LOVNG3 (528182) 115.0 kV to N_LOVING TR1 (528186) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_081 | 3 Phase fault on CHINA_DRAW 7345.00 (528223) 345 kV Bus a. Apply fault at the CHINA_DRAW 7345.00 (528223) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHINA_DRAW 7 (528223) 345.0 kV to CHINA_DRAW 3 (528222) 115.0 kV to CHINA_DRAW 1 (528219) 13.2 kV Three Winding #1 | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_085 | 3 Phase fault on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7 (527802) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_088 | 3 Phase fault on POTASH_JCT 3115.00 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3115.00 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 (527962) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_090 | 3 Phase fault on RED_BLUFF 3115.00 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3115.00 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RED_BLUFF 3 (528018) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_092 | 3 Phase fault on NORTH_LOVNG3115.00 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3115.00 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 (528182) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_093 | 3 Phase fault on N_LOVING 7345.00 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7345.00 (528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N_LOVING 7 (528185) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_095 | 3 Phase fault on CHINA_DRAW 3115.00 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3115.00 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 (528222) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P1_LOCAL_FAULT_096 | 3 Phase fault on WOOD_DRAW 3115.00 (528228) 115 kV Bus a. Apply fault at the WOOD_DRAW 3115.00 (528228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOOD_DRAW 3 (528228) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on HOBBS_INT 7345.00 (527896) 345 kV Bus a. Apply Fault at the HOBBS_INT 7345.00 (527896) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOBBS_INT 7 (527896) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.2. HOBBS_TR3 1 (527895) 13.2 kV to HOBBS_INT 7 (527896) 345.0 kV to HOBBS_INT 6 (527894) 230.0 kV Three Winding #1 | P4 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on HOBBS_INT 7 (527896) 345 kV Bus a. Apply Fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOBBS_INT 7 (527896) 345.0 kV to remove bus # | P4 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on HOBBS_INT 6 (527894) 115 kV Bus a. Apply Fault at the HOBBS_INT 6 (527894) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOBBS_INT 6 (527894) 230.0 kV to remove bus # | P4 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on HOBBS_INT 7345.00 (527896) 345 kV Bus a. Apply Fault at the HOBBS_INT 7345.00 (527896) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOBBS_INT 7 (527896) 345.0 kV to YOAKUM_345 (526936) 345.0 kV Transmission Circuit #1 b.2. HOBBS_INT 7 (527896) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P4_LOCAL_FAULT_SPS8 | Single Phase Fault with Stuck Breaker on HOBBS_INT (527896) 345 kV Bus a. Apply Fault at the HOBBS_INT (527896) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HOBBS_INT 7 (527896) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.2. HOBBS_INT 7 (527896) 345.0 kV to YOAKUM_345 (526936) 345.0 kV Transmission Circuit #1 b.3. HOBBS_TR3 1 (527895) 13.2 kV to Trip Bus # b.4. HOBBS_INT 7 (527896) 345.0 kV to Trip Bus # | P4 | Yes | Yes | No | yes | No | Yes | Yes | Transient Voltage Response >1.2 p.u. and Post Fault steady state voltage >1.1 p.u observed in MALAGABEND (528194), CHVRN_EDDYS (528252), CHINA_DRAW (528222), SOUTH_LOVNG ( 528192), WOOD_DRAW (528228), PHANTOM (528013), BLCKRVR_DST (528206) and numerous busbars face the same issue. The voltage rise is caused by the load tripping in the study area following the initial voltage drop after fault application. | Build Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt and Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | GEN-2016-121 LOSIS | 25W | Base | GROUP5_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply Fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. NOVUS_WND 1 (523107) 4.2 kV to NOVUS1 1 (523109) 34.5 kV Two Winding #1 b.3. NOVUS1 1 (523109) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.4. G06-44-2 (560581) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.5. NOVUS1_TR1 1 (523110) 13.8 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV Three Winding #1 b.6. NOVUS1 3 (523111) 115.0 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G06-44-3 (560585), G06-44-4 (560586) and HARRNGTON (523971,523972,523973) units. | Operational measures fixing the voltage setpoint of G06-44-3 (560585), G06-44-4 (560586) and HARRNGTON (523971,523972,523973) and HOBBS_PLT ( 527902,527901).
05 SOUTHWEST | GEN-2016-121 LOSIS | 25S | Base | GROUP5_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply Fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. NOVUS_WND 1 (523107) 4.2 kV to NOVUS1 1 (523109) 34.5 kV Two Winding #1 b.3. NOVUS1 1 (523109) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.4. G06-44-2 (560581) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.5. NOVUS1_TR1 1 (523110) 13.8 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV Three Winding #1 b.6. NOVUS1 3 (523111) 115.0 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G06-44-3 (560585), G06-44-4 (560586) and HARRNGTON (523971,523972,523973) units. | Operational measures fixing the voltage setpoint of G06-44-3 (560585), G06-44-4 (560586) and HARRNGTON (523971,523972,523973) and HOBBS_PLT ( 527902,527901).

## Short Circuit Analysis
Gen Number | Study Name | Group | Bus Number | Bus Name | Bus Voltage (kV) | Request Not In Service 25SP Fault Current 3-Phase (kA) | Request In Service 25SP Fault Current 3-Phase (kA) | Change in Fault Current (kA) | Circuit Breakers Exceeding Capacity | Facilities Required to Interconnect
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528025 | RDRUNNER 3 | 115 | 11.685 | 12.3256 | 0.6406
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528230 | AGAVE_RHILL3 | 115 | 10.6793 | 11.2113 | 0.532
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528231 | AGAVE_RHIL23 | 115 | 10.2138 | 10.6957 | 0.4819
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528040 | BATTLE_AXE 3 | 115 | 3.2932 | 3.3386 | 0.0454
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528239 | CUSTERMTN 3 | 115 | 7.5442 | 7.673 | 0.1288
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528018 | RED_BLUFF 3 | 115 | 9.5106 | 9.7017 | 0.1911
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 587990 | GEN-2016-121 | 115 | 10.9238 | 11.5649 | 0.6411
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528024 | RR_SVC_HV 3 | 115 | 11.685 | 12.3256 | 0.6406
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528027 | RDRUNNER 7 | 345 | 5.2266 | 5.3724 | 0.1458
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528232 | OCHOA 3 | 115 | 10.1886 | 10.6716 | 0.483
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528235 | WOLFCAMP_TP3 | 115 | 11.2793 | 11.4614 | 0.1821
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528015 | PHANTOM 7 | 345 | 4.8065 | 4.8958 | 0.0893
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528240 | PONDEROSA 3 | 115 | 4.1224 | 4.16 | 0.0376
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528016 | SAND_DUNES 3 | 115 | 7.2116 | 7.2946 | 0.083
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 527896 | HOBBS_INT 7 | 345 | 9.2141 | 9.2789 | 0.0648
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528540 | WHITTEN 3 | 115 | 7.6051 | 7.7027 | 0.0976
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 527965 | KIOWA 7 | 345 | 7.6505 | 7.7901 | 0.1396
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528519 | WARD 3 | 115 | 5.978 | 6.0159 | 0.0379
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528009 | WIPP 3 | 115 | 7.0768 | 7.1408 | 0.064
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528013 | PHANTOM 3 | 115 | 12.0071 | 12.2042 | 0.1971
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528020 | BOPCO_PKRLK3 | 115 | 11.8463 | 12.0399 | 0.1936
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 527894 | HOBBS_INT 6 | 230 | 18.9729 | 19.0684 | 0.0955
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528547 | S_JAL 3 | 115 | 6.5533 | 6.6047 | 0.0514
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 527656 | CROSSROADS 7 | 345 | 8.6017 | 8.6128 | 0.0111
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528185 | N_LOVING 7 | 345 | 5.718 | 5.813 | 0.095
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 527802 | EDDY_CNTY 7 | 345 | 7.1603 | 7.2278 | 0.0675
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 526936 | YOAKUM_345 | 345 | 9.3414 | 9.3643 | 0.0229
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 527966 | KIOWA 3 | 115 | 16.8379 | 16.9981 | 0.1602
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528223 | CHINA_DRAW 7 | 345 | 5.0535 | 5.1394 | 0.0859
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528236 | WOLFCAMP 3 | 115 | 10.5323 | 10.6896 | 0.1573
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 525832 | TUCO_INT 7 | 345 | 12.8168 | 12.8203 | 0.0035
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528526 | TEAGUE 3 | 115 | 6.35 | 6.3833 | 0.0333
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 527891 | HOBBS_INT 3 | 115 | 32.013 | 32.1057 | 0.0927
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 527655 | RSVLT_CC_E 7 | 345 | 7.8 | 7.8088 | 0.0088
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528561 | DOLLARHIDE 3 | 115 | 5.0763 | 5.1067 | 0.0304
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 527028 | INK_BASIN 6 | 230 | 11.3421 | 11.357 | 0.0149
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528182 | NORTH_LOVNG3 | 115 | 11.7388 | 11.8652 | 0.1264
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 527799 | EDDY_NORTH 6 | 230 | 9.5323 | 9.5898 | 0.0575
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528194 | MALAGABEND 3 | 115 | 7.5538 | 7.6224 | 0.0686
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 527953 | LIVSTNRIDGE3 | 115 | 7.4249 | 7.4872 | 0.0623
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 526935 | YOAKUM 6 | 230 | 19.2189 | 19.2449 | 0.026
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528604 | ANDREWS 6 | 230 | 6.5526 | 6.5699 | 0.0173
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 527962 | POTASH_JCT 3 | 115 | 16.8703 | 17.0296 | 0.1593
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528222 | CHINA_DRAW 3 | 115 | 10.1933 | 10.3068 | 0.1135
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528228 | WOOD_DRAW 3 | 115 | 7.838 | 7.9151 | 0.0771
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 525549 | TOLK 7 | 345 | 12.5792 | 12.5853 | 0.0061
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528505 | LEA_ROAD 3 | 115 | 6.1759 | 6.2015 | 0.0256
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 527610 | SAGA_SCOL 7 | 345 | 8.0046 | 8.0136 | 0.009
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 527867 | CUNNIGHM_S 6 | 230 | 17.4204 | 17.5004 | 0.08
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 763516 | GEN-2019-011 | 345 | 8.7923 | 8.8127 | 0.0204
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 525830 | TUCO_INT 6 | 230 | 21.2746 | 21.2792 | 0.0046
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 525850 | ELK_CT1 | 345 | 12.7135 | 12.717 | 0.0035
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528433 | BENSING 3 | 115 | 8.3618 | 8.3668 | 0.005
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528434 | MILLEN_TPW 3 | 115 | 12.0871 | 12.101 | 0.0139
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 527930 | PCA 3 | 115 | 12.1719 | 12.2406 | 0.0687
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 527954 | MEDANOS 3 | 115 | 5.5308 | 5.562 | 0.0312
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 526934 | YOAKUM 3 | 115 | 19.4989 | 19.5089 | 0.01
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 527961 | POTASH_JCT 2 | 69 | 10.2216 | 10.2509 | 0.0293
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 527963 | POTASH_JCT 6 | 230 | 7.5902 | 7.6271 | 0.0369
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 527483 | CHAVES_CNTY6 | 230 | 4.525 | 4.5311 | 0.0061
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 526460 | AMOCO_SS 6 | 230 | 10.1375 | 10.1401 | 0.0026
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 527999 | INTREPDW_TP3 | 115 | 13.8143 | 13.9288 | 0.1145
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 527009 | BRU_SUB 6 | 230 | 15.3244 | 15.3384 | 0.014
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528552 | OIL_CENTER 3 | 115 | 6.4129 | 6.4359 | 0.023
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 527027 | INK_BASIN 3 | 115 | 13.4922 | 13.4998 | 0.0076
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 523961 | POTTER_CO 7 | 345 | 11.598 | 11.5986 | 0.0006
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528064 | XTO_DI9_TP 3 | 115 | 8.0034 | 8.0609 | 0.0575
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528596 | CARDINAL 3 | 115 | 7.4056 | 7.4398 | 0.0342
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528602 | ANDREWS 3 | 115 | 8.6806 | 8.7084 | 0.0278
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 525531 | TOLK 6 | 230 | 28.2849 | 28.2958 | 0.0109
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528095 | 7-RIVERS 6 | 230 | 6.5406 | 6.5686 | 0.028
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 527599 | SAGA_SDCOL 7 | 345 | 8.0046 | 8.0136 | 0.009
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 525586 | NEEDMORE 6 | 230 | 11.0436 | 11.046 | 0.0024
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528160 | CARLSBAD 3 | 115 | 11.4537 | 11.5137 | 0.06
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 527654 | RSVLT_CC_W 7 | 345 | 7.0455 | 7.0525 | 0.007
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 527149 | MUSTANG 6 | 230 | 18.0071 | 18.0208 | 0.0137
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528192 | SOUTH_LOVNG3 | 115 | 9.0328 | 9.1118 | 0.079
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528193 | BLACKRIVER 3 | 115 | 9.957 | 10.0485 | 0.0915
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528195 | AGAVE_PDURO3 | 115 | 7.8441 | 7.9416 | 0.0975
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528206 | BLCKRVR_DST3 | 115 | 7.8441 | 7.9054 | 0.0613
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528225 | CD_SVC_HV 3 | 115 | 10.1933 | 10.3068 | 0.1135
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528226 | HOPI_SUB 3 | 115 | 7.364 | 7.3966 | 0.0326
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528252 | CHVRN_EDDYS3 | 115 | 7.0582 | 7.1118 | 0.0536
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 560022 | CRAWFISH_DR | 345 | 12.5532 | 12.5566 | 0.0034
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 599960 | EPTNP-D6 | 230 | 9.5323 | 9.5898 | 0.0575
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 527793 | EDDY_STH 3 | 115 | 12.0409 | 12.0874 | 0.0465
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 527798 | EDDY_NTH 3 | 115 | 12.0409 | 12.0874 | 0.0465
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528333 | LE-WEST_SUB3 | 115 | 9.328 | 9.3328 | 0.0048
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 528355 | MADDOX 3 | 115 | 26.6179 | 26.6854 | 0.0675
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 527864 | CUNNINHAM 3 | 115 | 28.0103 | 28.0941 | 0.0838
GEN-2016-121 | GEN-2016-121 LOSIS | 05 SOUTHWEST | 527865 | CUNNIGHM_N 6 | 230 | 17.4204 | 17.5004 | 0.08