______________________________________________

Southwest Power Pool, Inc. (SPP)

______________________________________________

Group 06 Limited Operation, Interim Availability, and Generator Modification System Impact Study

Final Report

REP-0981

Revision #06

May 2021

Submitted By:

Mitsubishi Electric Power Products, Inc. (MEPPI)

Power Systems Engineering Division

Warrendale, PA

Report Revision Table

| Revision | Report Revision Table | Date |
| --- | --- | --- |
| 0 | Issue Draft Report for Review | 11/10/2020 |
| 1 | Address comments and issue Final Report | 11/17/2020 |
| 2 | Report reflects stable output of 650MW at generator terminals for facilities interconnected at Crossroads | 12/31/2020 |
| 3 | Address SPP comments | 1/8/2021 |
| 4 | Update Crossroads 345kV breaker configuration and Sagamore Wind model parameters | 3/5/2021 |
| 5 | Perform P6 events with Sagamore as-built model parameters for LOIS | 3/19/2021 |
| 6 | Generator modification study for GEN-2016-123, GEN-2016-124, and GEN-2016-125 | 5/14/2021 |

Table of Contents

Executive Summary	v

Section 1:  Overall Study Objectives	1

Section 2:  LOIS and Interim Availability Interconnection Study	2

2.1	Background	2

2.2	Power Flow Analysis	8

2.2.1	Approach	8

2.2.2	Steady-State Thermal and Voltage Analysis Results	8

2.3	Stability Analysis	10

2.3.1	Approach	10

2.3.2	Normal Dispatch Stability Analysis Results	25

2.3.3	Curtailment for P6 Events for the Normal Dispatch Scenario	42

2.3.4	Addition of Tolk 345/230kV Transformer #2 for the Normal Dispatch Scenario	43

2.3.5	Summary of the Normal Dispatch Scenario Results	44

2.3.6	Sensitivity Stability Analysis Results	45

2.3.7	Summary of the Sensitivity Dispatch Scenario Results	52

2.4	LOIS and Interim Availability Study Conclusion	52

Section 3:  Generator Modification Study	55

3.1	Background	55

3.2	Power Flow Analysis	59

3.2.1	Approach	59

3.2.2	Steady-State Non-Converged, Thermal, and Voltage Analysis Results	60

3.3	Stability Analysis	64

3.3.1	Approach	64

3.3.2	Normal Dispatch Scenario Stability Results	77

3.3.3	Curtailment for P6 Events for the Normal Dispatch Scenario	86

3.3.4	Summary of the Normal Dispatch Scenario Results	87

3.3.5	Sensitivity Scenario Stability Results	88

3.3.6	Summary of the Sensitivity Dispatch Scenario Results	94

3.4	Material Modification Determination	94

3.4.1	Overall Results	94

Section 4:  Overall Conclusion	95

4.1	Summary of the LOIS and Interim Availability Interconnection Study	95

4.2	Summary of the Generator Modification Study	97

Appendix A: Stability Analysis Steady State and Dynamic Model Data for the LOIS and Interim Availability Interconnection Study	A-1

Appendix B: Stability Analysis Steady State and Dynamic Model Data for the Generator Modification Study	B-1

Appendix C: Plots for the LOIS/Interim Availability Study – Normal Dispatch Scenario	C-1

Appendix D: Plots for the LOIS/Interim Availability Study – Sensitivity Dispatch Scenario	D-1

Appendix E: Plots for the Generator Modification Study – Normal Dispatch Scenario	E-1

Appendix F: Plots for the Generator Modification Study – Sensitivity Dispatch Scenario	F-1

# Executive Summary

SPP requested a Limited Operation Impact Study (LOIS) for Group 06 requests GEN-2016-123, GEN-2016-124, and GEN-2016-125 and an Interim Availability Interconnection System Impact Study for Group 06 study request GEN-2017-069 for system conditions as of December 1, 2020.  Additionally, SPP requested a Generator Modification Impact Study for Group 06 requests GEN-2016-123, GEN-2016-124, and GEN-2016-125.

The LOIS and Interim Availability study required a power flow analysis and stability analysis detailing the impacts of the interconnecting projects as shown in Table ES-1. GEN-2016-123, GEN-2016-124, and GEN-2016-125 have requested 522 MW (total) of wind generation to be interconnected with Energy Resource Interconnection Service (ERIS) at Xcel Energy – Southwestern Public Service Company’s (SPS) Crossroads 345kV substation and GEN-2017-069 has requested 3.6 MW of solar generation to be interconnected with ERIS and Network Resource Interconnection Service (NRIS) into the transmission system of SPS’s Norton 115kV substation in Quay County, New Mexico.

Table ES-1

Interconnection Project Evaluated for the LOIS/Interim Availability Study

| Request | Size (MW) | Generator Model | Point of Interconnection |
| --- | --- | --- | --- |
| GEN-2016-123 | 298 | Vestas Wind | Crossroads 345kV (527656) |
| GEN-2016-124 | 150 | Vestas Wind | Crossroads 345kV (527656) |
| GEN-2016-125 | 74 | Vestas Wind | Crossroads 345kV (527656) |
| GEN-2017-069 | 3.6 increase to GEN-2013-022 | SMASC Solar PV Inverter (524491) | Norton 115kV Switching Station (524502) |

The LOIS and Interim Availability Interconnection study determined the Limited Operation for GEN-2016-123, GEN-2016-124, and GEN-2016-125 was identified in the power flow analysis as 522 MW (full output) at generator terminals for Scenario 3 (274 MW for Scenario 2 at the generator terminals, 272 MW at Crossroads 345kV) and 522 MW (full output) for the stability analysis for P1 and P4 contingencies.

A software modification was made to GEN-2016-123, GEN-2016-124, and GEN-2016-125 wind turbine and power plant controller following the LOIS and Interim Availability study which required a power flow analysis and stability analysis for the Generator Modification Study as part of the SPP Attachment V Generator Interconnection Procedure Section 4.4.5. Refer to Table ES-2 for the interconnection projects evaluated as part of the Generator Modification Study.

Table ES-2

Interconnection Project Evaluated for the Generator Modification Study

| Request | Size (MW) | Generator Model | Point of Interconnection |
| --- | --- | --- | --- |
| GEN-2016-121 | 110 | SMA Sunny Central 2.5 MW (587993) | Road Runner 345kV (528025) |
| GEN-2016-123 | 298 | Vestas Wind | Crossroads 345kV (527656) |
| GEN-2016-124 | 150 | Vestas Wind | Crossroads 345kV (527656) |
| GEN-2016-125 | 74 | Vestas Wind | Crossroads 345kV (527656) |

The Generator Modification Study determined that there were no additional power flow constraints or voltage stability concerns for P1 or P4 events at and near Crossroads 345kV across all seasons when all generation interconnection requests were at 100% output.

SUMMARY OF POWER FLOW ANALYSIS FOR THE LOIS/INTERIM AVAILABILITY

The power flow analysis determined a Limited Operation amount for GEN-2016-123, GEN-2016-124, and GEN-2016-125 and the available interim service for GEN-2017-069. Refer to Table ES-3 for a summary of the scenarios performed and identified service available.

Table ES-3

Summary of Power Flow Analysis for the LOIS/Interim Availability Study

| Scenario | Scenario Description | LOIS (MW) | Interim Service (MW) |
| --- | --- | --- | --- |
|  |  | GEN-2016-123/124/125 | GEN-2017-069 |
| 1 | No Adjustments AEP OKU RAS Retired SPS Sagamore RAS Disabled | 270 gross 268 at Crossroads 345 kV | 3.6 gross |
| 2 | No Adjustments AEP OKU RAS Retired SPS Sagamore RAS Enabled | 274 gross 272 at Crossroads 345 kV | 0.0 |
| 3 | AEP OKU RAS Retired SPS Sagamore RAS Enabled Voltage and reactor adjustments | 522 gross | 3.6 gross |
| 4 | AEP OKU RAS Retired SPS Sagamore RAS Enabled Reactive support at Border 345kV | 522 gross | 3.6 gross |

These values reflect the gross generating facility capacity prior to losses associated with the interconnection facilities.  Scenario 3 in the power flow analysis examined system adjustments such as altering voltage schedules, switching reactors, and adjusting LTC transformer taps. With these system adjustments, it was determined GEN-2016-123, GEN-2016-124, and GEN-2016-125 and Interim Request GEN-2017-069 may connect at full output.

Evaluation of the 2nd Tolk 345/230 kV transformer was not included in the power flow analysis for this study. However, the DISIS-2016-002 study, performed by SPP, confirmed the LOIS with Sagamore RAS retired and 2nd Tolk 345/230 kV transformer in-service is the full output of Sagamore (522 MW). Refer to the DISIS-2016-002 report posted on the SPP Oasis Portal for details of this evaluation.

SUMMARY OF STABILITY ANALYSIS FOR THE LOIS/INTERIM AVAILABILITY

The stability analysis determined that there were multiple P1, P4, and P6 contingencies that resulted either high post-fault steady-state voltages, voltage instability, and/or generation tripping across all seasons when all generation interconnection requests were at 100% output. It was determined, with system adjustments, GEN-2016-123, GEN-2016-124, and GEN-2016-125 may interconnect with full output and interim request GEN-2017-069 can connect at full output. The following is a summary of results for all faults.

- High post-fault steady-state voltage at Oklaunion 345kV

  - Mitigation: Trip the Oklaunion HVDC reactive equipment at Oklaunion 345kV simultaneously with blocking of the Oklaunion HVDC tie

- Event resulting in outage of Crossroads to Eddy County 345kV circuit

  - Voltage stability is observed with a combined Roosevelt, Milo, and Sagamore output at 822 MW with the Sagamore as-built models.

  - Stability is maintained when a RAS that trips the Sagamore facility for this event is enabled.

  - Stability is maintained following retirement of the RAS that trips the Sagamore facility for this event and the DISIS-2016-002 assigned Tolk 345/230 kV transformer #2 is in-service.

- Event resulting in outage of Crossroads 345 kV to Tolk 345kV circuit or Tolk 345/230 kV transformer #1 (and #2 once in-service)

  - Voltage instability is observed with a combined Roosevelt, Milo, and Sagamore output at 822 MW.

  - Stability is maintained when Sagamore Wind output does not exceed 336 MW (stability margin calculation will include 300 MW from Roosevelt and Milo wind facilities) at Crossroads 345kV or when the combined Roosevelt, Milo, and Sagamore output does not exceed 636 MW at Crossroads 345kV with normal system configuration, all breakers in-service or

  - Stability is maintained when Crossroads 345 kV substation breaker configuration results in a trip of the Sagamore facility for these events (full interconnection capacity of Roosevelt, Milo and Sagamore facilities with the new breaker configuration in-place)

- Prior outage events resulting in voltage instability with a combined Roosevelt, Milo, and Sagamore output at 822 MW.

  - Loss of Crossroads to Tolk 345kV transmission line

    - Stability is maintained when Sagamore Wind output does not exceed 274 MW (stability margin calculation will include 300 MW from Roosevelt and Milo wind facilities) at Crossroads 345kV or when the combined Roosevelt, Milo, and Sagamore output does not exceed 574 MW at Crossroads 345kV

  - Loss of Crossroads to Eddy County 345kV transmission line

    - Stability is maintained when Sagamore Wind output does not exceed 406 MW (stability margin calculation will include 300 MW from Roosevelt and Milo wind facilities) at Crossroads 345kV or when the combined Roosevelt, Milo, and Sagamore output does not exceed 706 MW at Crossroads 345kV

The stability analysis from this Limited Operation and Interim Availability study determined the following with identified system adjustments:

- GEN-2016-123, GEN-2016-124, GEN-2016-125 can interconnect at full requested capability for system intact conditions prior to a fault event.

- GEN-2017-069 can connect at full requested capability.

The stability analysis was evaluated with the as-built model parameters for the Sagamore Wind Facility which drove the need for the Generator Modification Study. Additionally, the Roosevelt-Milo Wind facilities were represented with Vestas user-written generator models without a Power Plant Controller (PPC).  Results presented in this report are based on the exclusion of the power plant controller and represent a conservative scenario. Inclusion of a PPC is anticipated to provide improved voltage control and inclusion in a subsequent analysis has potential to resolve the stability issues observed in this study.

It should be noted that while the Limited Operation and Interim Availability study analyzed many of the most probable contingencies, it is not an all-inclusive list that can account for every operation situation. Additionally, the study requests may not be able to inject any power onto the Transmission System due to constraints that fall below the threshold of mitigation for a Generator Interconnection request. Because of this, it is likely that the Customers may be required to reduce their generation output to 0 MW under certain system conditions to allow system operators to maintain the reliability of the transmission network.

SUMMARY OF STABILITY ANALYSIS FOR THE MODIFICATION STUDY

As a result of the LOIS Study, updated software for GEN-2016-123, GEN-2016-124, and GEN-2016-125, and discussions with Xcel SPS, an alternative stability Network Upgrade was determined to resolve P1 voltage stability constraints at Crossroads 345kV. This Network Upgrade was identified as a new Crossroads 345/115kV transformer and a new Crossroads to Portales 115kV circuit. The stability analysis for the Generator Modification Study was performed with this Network Upgrade in-service and determined that there were voltage stability concerns for P1 or P4 events at and near Crossroads 345kV across all seasons when all generation interconnection requests were at 100% output. All voltages recovered with the SPP Performance Criteria and all generation facilities remained online with acceptable response.

Several P6 contingencies at Crossroads 345kV, for all seasons and scenarios, resulted in voltage instability due to low voltage recovery and study requests exhibited LVRT oscillations. The following is a summary of results for all faults.

- High post-fault steady-state voltage at Oklaunion 345kV

  - Mitigation: Trip the Oklaunion HVDC reactive equipment at Oklaunion 345kV simultaneously with blocking of the Oklaunion HVDC tie

- Event resulting in outage of Crossroads to Tolk 345kV circuit

  - Voltage stability is observed with a combined Roosevelt, Milo, and Sagamore output at 822 MW with the Sagamore as-built models.

- Event resulting in outage of Crossroads to Eddy County 345kV circuit

  - Voltage stability is observed with a combined Roosevelt, Milo, and Sagamore output at 822 MW with the Sagamore as-built models.

  - Stability is maintained when a RAS that trips the Sagamore facility for this event is enabled.

  - Stability is maintained following retirement of the RAS that trips the Sagamore facility for this event and the DISIS-2016-002 assigned Tolk 345/230 kV transformer #2 is in-service.

- Event resulting in outage of Crossroads 345/115 kV transformer or Crossroads to Portales 115 kV circuit

  - Voltage stability is observed with a combined Roosevelt, Milo, and Sagamore output at 822 MW with the Sagamore as-built models.

- Prior outage events resulting in voltage instability with a combined Roosevelt, Milo, and Sagamore output at 822 MW.

  - Loss of Crossroads to Tolk 345 kV transmission line

    - Stability is maintained when combined Roosevelt, Milo, and Sagamore output does not exceed 209 MW at Crossroads 345 kV

  - Loss of Crossroads to Eddy County 345 kV transmission line

    - Stability is maintained when combined Roosevelt, Milo, and Sagamore output does not exceed 209 MW at Crossroads 345 kV

  - Loss of Crossroads 345/115 kV transformer or Crossroads to Portales 115kV transmission line

    - Stability is maintained when the combined Roosevelt, Milo, and Sagamore output does not exceed 726 MW at Crossroads 345 kV

SUMMARY OF POWER FLOW ANALYSIS FOR THE MODIFICATION STUDY

With the addition of the stability driven Network Upgrade of the Crossroads 345/115kV transformer and Crossroads to Portales 115kV circuit, the power flow analysis determined that no additional Network Upgrades from the DISIS-2016-002-2 analysis were required. Refer to the DISIS-2016-002 report posted on the SPP Oasis Portal for details of this evaluation.

MATERIAL MODIFICATION DETERMINATION

Based on the analysis in this study and the understanding of SPP’s Open Access Transmission Tariff, MEPPI has determined the requested modification is a Material Modification based on the results of this Generator Modification Study. This determination is subject to approval by SPP. It was determined the updated PPC software does result in additional mitigation of the Crossroads 345/115 kV transformer and Crossroads to Portales 115 kV line. These two Network Upgrades were driven by the stability of GEN-2016-123, GEN-2016-124, and GEN-2016-125. Additionally, with these two Network Upgrades, these eliminate the need for the following Network Upgrades identified in the DISIS-2016-002-2 power flow analysis:

- Crossroads to Tolk 345kV circuit #1 rebuild

- Crossroads to Eddy County 345kV circuit #1 rebuild

- Curry to Deaf Smith 115kV circuit #1 rebuild

- Tolk East to TUCO 230kV circuit #1 rebuild

It was determined that any Network Upgrade already required by GEN-2016-121 would not be negatively impacted.

# Section 1:  Overall Study Objectives

The objective of this report is to provide Southwest Power Pool, Inc. (SPP) with the deliverables for the “Group 06 Limited Operation, Interim Availability, and Generator Modification System Impact Study.” SPP requested an Interconnection System Impact Study for five (5) generation interconnection requests which requires a power flow analysis and stability analysis with results in an Impact Study Report.

# Section 2:  LOIS and Interim Availability Interconnection Study

## Background

The Siemens Power Technologies International PSS/E power system simulation program Version 33.10 was used for this study.  The DISIS-2016-002-2 power flow and stability cases under normal dispatch conditions were provided by SPP. The power flow cases include the Group 06 ERIS study models, Group 00 NRIS study models, and Group 06 NRIS models. Refer to the DISIS power flow report accompanying this report for details of changes made to the cases provided. The stability cases provided included the 2017 Winter Peak, 2018 Summer Peak, and 2026 Summer Peak cases. The study requests listed in Table 2.1-1 were added to the models and the models include the previously queued projects listed in Table 2.1-2.  The study cases were updated to reflect known system conditions at the time of the in-service date for GEN-2016-123, GEN-2016-124, GEN-2016-125 and the GEN-2017-069 interim request. The projects with later ISD or withdrawn study projects shown in Table 2.1-3 were removed from the study models to reflect current system configurations. Refer to Section 2.2.1 for the changes made to the base cases to reflect the removal of previously assigned Network Upgrades and study projects associated with Q4 2020 conditions. Additionally, a sensitivity study was performed on all seasons to determine the impact of nearby generation.

Power flow one-line diagrams for GEN-2016-123, GEN-2016-124, GEN-2016-125, and GEN-2017-069 are shown in Figure 2.1-1 and Figure 2.1-2. Note that the one-line diagrams represent 2017 Winter Peak conditions.

The stability analysis determined the impacts of the new interconnecting project on the stability and voltage recovery of the nearby system and the ability of the interconnecting projects to meet FERC Order 661A. If problems with stability or voltage recovery are identified, the need for reactive compensation or system upgrades were investigated. Three-phase faults and single line-to-ground faults were examined prior to any mitigation or curtailment implemented. With exception of transformers and prior outage faults, the typical sequence of events for a three-phase fault is as follows (refer to Section 2.3 for a list and description of fault events analyzed):

- Apply fault at particular station

- Continue fault for five (5) cycles, clear the fault by tripping the faulted facility

- After an additional twenty (20) cycles, re-close the previous facility back into the fault

- Continue fault for five (5) additional cycles

- Trip the faulted facility and remove the fault

Table 2.1-1: Interconnection Projects Evaluated

| Request | Size (MW) | Generator Model | Point of Interconnection |
| --- | --- | --- | --- |
| GEN-2016-123 | 298 | Vestas Wind | Crossroads 345kV (527656) |
| GEN-2016-124 | 150 | Vestas Wind | Crossroads 345kV (527656) |
| GEN-2016-125 | 74 | Vestas Wind | Crossroads 345kV (527656) |
| GEN-2017-069 | 3.6 increase to GEN-2013-022 (28.6 MW total) | SMASC Solar PV Inverter (524491) | Norton 115kV Switching Station (524502) |

Table 2.1-2: Previously Queued Nearby Interconnection Projects Included

| Request | Size (MW) | Generator Model | Point of Interconnection |
| --- | --- | --- | --- |
| GEN-2001-033 (Commercial Operation) | 120 | WT1G1 (524890) | San Juan Tap 230kV |
| GEN-2001-036 | 80 | WT1G1 (599138) | Norton 115kV Switching Station |
| GEN-2006-018 | 168.1 | GENSAL | TUCO 230kV |
| GEN-2006-026 | 604 | GENROU (527901, 527902, 527903) | Hobbs 230kV & Hobbs 115kV |
| GEN-2008-022 | 299.65 | Vestas VWCOR6 | Eddy County-Tolk (Crossroads) 345kV |
| GEN-2010-006 | 180/205 | GENROU | Jones 230kV |
| GEN-2011-025 | 79.96 | GE 1.79MW | Tap Floyd County - Crosby County 115kV |
| GEN-2011-045 | 180/205 | GENROU | Jones 230kV |
| GEN-2011-046 | 23 | GENROU | Tucumcari 115kV |
| GEN-2011-048/ GEN-2012-036 | 172/182 | GENROU | Mustang 230kV |
| GEN-2012-001 | 61.2 | CCWE 3.6MW (WT4) | Tap Grassland Â- Borden County 230 kv |
| GEN-2012-020 | 478 | GE 1.68MW | TUCO 230kV |
| GEN-2004-015/ GEN-2012-034 | 157 | GENROU (unit 4; 527164) | Mustang 230kV |
| GEN-2006-015/ GEN-2012-035 | 157 | GENROU (unit 5; 527165) | Mustang 230kV (527151) |
| GEN-2012-037 | 196/203 | GENROU (525844) | Tuco 345kV (525832) |
| GEN-2013-016 / GEN-2015-041 | 196/203 | GE 7FA Gas CT 208 MW | Tuco 345 kV (525832) |
| GEN-2013-022 | 25 | SMASC (524491) | Norton 115kV (524502) |
| GEN-2013-027 | 148.4 | Siemens 2.3/2.415 | Tap on Yoakum to Tolk 230kV (562480) |
| GEN-2014-033 | 70 | 17 X GE Prolec 4MVA, 2 X GE Prolec 1 MVA, & 5 X Schneider XC680 0.680 MVA PV inverter | Chaves County 115kV |
| GEN-2014-034 | 70 | 17 X GE Prolec 4MVA PVinverter | Chaves County 115kV |
| GEN-2014-035 | 30 | 8 X GE Prolec 4MVA PV inverter | Chaves County 115kV |
| GEN-2014-040 | 319.7 | GE 2.3 MW | Castro 115 kV (524746) |
| GEN-2015-014 | 150.0 | Vestas V110 2.0MW (584563) | Tap on Cochran – LG Plains 115kV (560030) |
| GEN-2016-177 | 17 | Gas Turbine | XTO-Cornell 115 kV station |

Table 2.1-3: SPP Interconnection Projects Removed from the Model

| Request | Size (MW) | Generator Model (Gen Bus Number) | Point of Interconnection |
| --- | --- | --- | --- |
| GEN-2001-033 (12/31/2022 COD) | 60 | WT1G1 (524896) | San Juan Tap 230kV |
| GEN-2011-049 (Withdrawn) | 250.7 | Siemens 2.3 MW (583093) | Border 345kV (515458) |
| GEN-2015-004 (Withdrawn) | 151.8 | Siemens 2.3 MW (583096) | Border 345kV (515458) |
| GEN-2015-099 (Withdrawn) | 73.3 | Power Electronics FS2000CU (587673) | Maddox 115kV (528355) |
| GEN-2016-023 (Withdrawn) | 150.5 | GE Wind (587093/587095) | Laramie to Sidney 345kV Tap (560075) |
| GEN-2016-029 (Withdrawn) | 150.5 | GE Wind (587193/587195) | Laramie to Sidney 345kV Tap (560075) |
| GEN-2016-037 (queued to DISIS-2017-001) | 300 | Vestas V110 2.0 MW (587233) | Chisholm to Gracemont 345kV Tap (560078) |
| GEN-2016-096 (Withdrawn) | 227.7 | Siemens 2.3 MW (587783/587787) | Pauline to Moore 345kV Tap (560062) |
| GEN-2016-121 (12/1/2022 COD) | 110 | SMA Sunny Central 2.5 MW (587993) | Road Runner 345kV (528025) |
| GEN-2016-129 (Withdrawn) | 132 | Wind | Valliant 345 kV substation |

Figure 2.1-1. Power flow one-line diagram for interconnection projects at Crossroads 345kV Switching Station (GEN-2016-123/GEN-2016-124/GEN-2016-125) for 2017 Winter Peak conditions.

Figure 2.1-2. Power flow one-line diagram for interconnection project at Norton 115kV Switching Station (GEN-2017-069) for 2017 Winter Peak conditions.

## Power Flow Analysis

The objective of the power flow analysis was to determine the impacts of the generator interconnection on the steady-state thermal and voltage constraints on the SPP transmission system. The analysis evaluated if GEN-2016-123, GEN-2016-124, and GEN-2016-125 can interconnect 522 MW of wind generation with Energy Resource Interconnection Service (ERIS) and if GEN-2017-069 can interconnect 3.6 MW of solar generation with ERIS and Network Resource Interconnection Service (NRIS) after December 1, 2020.

### Approach

MEPPI utilized the seven (7) following DISIS-2016-002-2 power flow cases for this analysis:

- Steady-State Analysis

  - 2017 Winter Peak

  - 2018 Spring

  - 2018 Summer Peak

  - 2021 Light Load

  - 2021 Summer Peak

  - 2021 Winter Peak

  - 2026 Summer Peak

The power flow cases were dispatched in accordance with DISIS Manual, Table 1: Generation Dispatch in the Power Flow Models, and Business Practices 7250 to develop the ERIS and NRIS cases. Fourteen (14) Before Transfer (BC) cases were created by including the study requests but dispatched at 0 MW for ER (7 cases) and NR (7 cases) dispatch scenarios. Fourteen (14) Transfer cases (TC) were created by including the study requests and dispatched at full output for ER (7 cases) and NR (7 cases) dispatch scenarios (note GEN-2016-123, GEN-2016-124, and GEN-2016-125 are ER only requests and were dispatched in the NR cases in accordance with the DISIS Manual). Refer to the attachment for the status of previously assigned upgrades and higher queued requests.

### Steady-State Thermal and Voltage Analysis Results

The power flow analysis observed system constraints with identified Limited Operation capacity for GEN-2016-123, GEN-2016-124, and GEN-2016-125 Interim service capacity for GEN-2017-069 as shown in Table 2.2-1.

- Scenario 1: Reflects the available capacity without mitigation.

- Scenario 2: Includes incremental mitigation of the SPS Sagamore RAS that trips the Sagamore Wind generating facility when loading of the Crossroads to Tolk 345kV circuit exceeds a specified value (478 MVA for 21 seconds or 556 MVA for 30 cycles) to prevent overload of the existing Tolk 345/230kV transformer.

- Scenario 3: Includes Scenario 2 mitigation plus adjustments to voltage schedules at Castro County, Tolk, Antelope, and TUCO stations; and switching out shunt reactors at Border, TUCO, and Woodward stations to alleviate voltage violations.

- Scenario 4: Includes Scenario 2 mitigation and the DISIS-2016-002 assigned reactive equipment at Border 345kV.

The full power flow report can be found as an attachment to this document.

Table 2.2-1: Summary of Power Flow Analysis

| Scenario | Scenario Description | LOIS (MW) | Interim Service (MW) |
| --- | --- | --- | --- |
|  |  | GEN-2016-123/124/125 | GEN-2017-069 |
| 1 | No Adjustments AEP OKU RAS Retired SPS Sagamore RAS Disabled | 270 gross 268 at Crossroads 345 kV | 3.6 gross |
| 2 | No Adjustments AEP OKU RAS Retired SPS Sagamore RAS Enabled | 274 gross 272 at Crossroads 345 kV | 0.0 |
| 3 | AEP OKU RAS Retired SPS Sagamore RAS Enabled Voltage and reactor adjustments | 522 gross | 3.6 gross |
| 4 | AEP OKU RAS Retired SPS Sagamore RAS Enabled Reactive support at Border 345kV | 522 gross | 3.6 gross |

The generation dispatch values in Table 2.2-1 reflect the gross generating facility capacity prior to losses associated with the interconnection facilities.  Scenario 3 in the power flow analysis examined system adjustments such as altering voltage schedules, switching reactors, and adjusting LTC transformer taps. With these system adjustments, it was determined GEN-2016-123, GEN-2016-124, and GEN-2016-125 and Interim Request GEN-2017-069 may connect at full output. However, SPP Staff has communicated limitation concerns to the system adjustments and may invalidate Scenario 3. Additional direction will be provided by SPP Management Staff.

## Stability Analysis

The objective of the stability analysis was to determine the impacts of the generator interconnection on the stability and voltage recovery on the SPP transmission system. If problems with stability or voltage recovery were identified, limited operation amounts were investigated for GEN-2016-123, GEN-2016-124, and GEN-2016-125 and network upgrades were investigated for GEN-2017-069.

### Approach

MEPPI utilized the three (3) following DISIS-2016-002-2 Normal Dispatch Scenario power flow cases and dynamic databases:

- MDWG16-17W_DIS16022_G06

- MDWG16-18S_DIS16022_G06

- MDWG16-26S_DIS16022_G06

Each case was examined prior to the stability analysis to ensure the case contained the proposed study projects and any previously queued projects listed in Tables 2.1-1 and 2.1-2 respectively. The DISIS-2016-002-2 stability cases included several existing generators in the SPS area scaled to 100% to incorporate a sensitivity dispatch into a single cluster group dispatch. In order to align with current dispatch methodology, these units were reverted back to their MDWG dispatch proportionally with the rest of the SPP footprint. Refer to Table 2.3-1 for a list of generation that was reverted to its MDWG dispatch. To accurately represent current system conditions, Tolk Unit #1 was modeled as a synchronous condenser in the 2017 Winter Peak case to evaluate 12/1/2020 system conditions.

Table 2.3-1: List of SPS Generation Reverted to MWDG Dispatch

| Generation | Bus | Normal Scenario Dispatch |  |  |
| --- | --- | --- | --- | --- |
|  |  | 17W | 18S | 26S |
| Mustang Unit 1 | 527161 | 121.7 | 127.7 | 131.9 |
| Mustang Unit 2 | 527162 | 121.7 | 127.7 | 131.9 |
| Mustang Unit 3 | 527163 | 129.3 | 135.7 | 140.2 |
| Mustang Unit 4 | 527164 | 93.4 | 124.6 | 130.2 |
| Mustang Unit 5 | 527165 | Offline | 125.5 | 130.3 |
| Mustang Unit 6 | 527166 | Offline | 132.7 | 142.7 |
| Tuco (Elk 1) | 525844 | Offline | 156.8 | 162.6 |
| Tuco (Elk 2) | 525845 | Offline | 153.8 | 158.5 |
| Tolk Unit 1 | 525561 | Synch Cond | 416.8 | 467.1 |
| Tolk Unit 2 | 525562 | Offline | 424.6 | 462.9 |
| Plant X1 | 525491 | Offline | Offline | 37.4 |
| Plant X2 | 525492 | Offline | 60.3 | 75.5 |
| Plant X3 | 525493 | 76.5 | 60.3 | 84.8 |
| Plant X4 | 525494 | Offline | 96.5 | 164.8 |
| Hobbs Unit 1 | 527901 | 107.2 | 96.5 | 120.4 |
| Hobbs Unit 2 | 527902 | 107.2 | 96.5 | 119.5 |
| Hobbs Unit 3 | 527903 | 153.1 | 160.8 | 176.7 |
| Maddox Unit 1 | 528361 | 53.6 | 80.4 | 95.4 |
| Maddox Unit 2 | 528362 | Offline | Offline | 47.9 |
| Maddox Unit 3 | 528363 | Offline | Offline | 8.3 |
| Cunningham Unit 1 | 527881 | Offline | 56.3 | 63.9 |
| Cunningham Unit 2 | 527882 | 130.1 | 160.8 | 169.3 |
| Cunningham Unit 3 | 527883 | Offline | 81.2 | 89.6 |
| Cunningham Unit 4 | 527884 | 76.6 | 78.0 | 88.8 |
| Tuco (Antelope A1) | 525841 | Offline | 43.1 | 46.5 |
| Tuco (Antelope B1) | 525842 | Offline | 43.1 | 46.5 |
| Tuco (Antelope C1) | 525843 | Offline | Offline | 46.5 |

The Normal Dispatch Scenario included previously assigned upgrades that were to be in-service by the Commercial Operation Date of GEN-2016-123, GEN-2016-124, and GEN-2016-125 (Sagamore Wind). The following previously assigned upgrades were included in the analysis:

- Upgrade Carlisle 230/115kV transformer

- TUCO to Yoakum to Hobbs 345kV circuit #1

- Yoakum 345/230kV transformer

- Hobbs 345/230kV transformer

- Rebuild Plant X to Tolk 230kV circuits #1 and #2

- Upgrade existing Tuco 345/230kV transformer circuit #1

- Eddy County to Kiowa 345kV circuit #1

- Crossroads capacitive support (+100 MVAR)

- Crossroads to Tolk 345kV circuit #1 rebuild

- Crossroads to Eddy County 345kV circuit #1 rebuild

- Deaf Smith to Plant X 230kV circuit #1 rebuild

- Newhart to Plant X 230kV circuit #1 rebuild

- Curry to Deaf Smith 115kV circuit #1 rebuild

- Tolk East to TUCO 230kV circuit #1 rebuild

Sagamore Wind was modeled with version 7.5.8 of the Vestas V110 VCS 2.0 MW and V120 VCS 2.2 MW dynamic model, using the as-built model parameters for the plant (refer to Section 3 for impact of as-built models with updated software). Refer to Appendix A for the dynamic data file for the Vestas 7.5.8 model that was used for this analysis. At the time of this study, the Roosevelt-Milo Wind facility was modeled with version 7.6 of the Vestas OptiSpeedTM Wind Turbines (VWCOR6) to represent Vestas 2.0 MW V100 & V110 VCSS generators with the Power Plant Controller (PPC) excluded from the analysis. Results presented in this report are based on the exclusion of the Roosevelt-Milo PPC and represent a conservative scenario. To emulate power flow Scenario 3 conditions, the following system adjustments were made to the stability datasets:

- Switch off TUCO in-line reactors on the TUCO to Yoakum 345kV line

- Switch off the Border in-line reactors on the Border to Woodward 345kV line

- Adjust the low voltage setting for the Woodward transformer tertiary shunt reactors.

- Adjust Hale County Wind, Antelope, and TUCO SVC to control TUCO 230 kV at 1.02 p.u.

- Adjust Hale County Wind main power transformers to maintain normal voltages at 34.5 kV.

- Adjust Elk 1 & 2 to control TUCO 345 kV at 1.00725 p.u.

- Adjust Bethel Wind generation to control Castro County 115 kV at 1.02 p.u.

Additionally, sensitivity cases were created for all three seasons. The sensitivity cases included dispatching local generation to 100% output. Examples of electrically similar and adjacent substations include but are not limited to any kV of:

- the same substation

  - e.g. lower kV, zero-impedance branch connected bus, or alternate owner facilities

- radially connected substations

  - islanded topology resultant from a connected circuit outage

    - i.e. Generating Facility

  - substantially weakened interconnection from a connected circuit outage

    - i.e. loss of 100+ kV circuit maintains interconnection through 69kV system

- substations connected by a network circuit

  - sectionalized single (or double) circuits from substations or buses to accommodate generation and radial load are considered a single network circuit

    - i.e. a network circuit may include several buses each with two non-radial circuits

- substations within close electrical proximity

  - i.e. approximately 30 circuit miles at 345kV or a circuit impedance path less than 0.02 pu

- substations adjacent to another adjacent substation with a generating facility

  - i.e. generation both 1 & 2 levels away are electrically similar but generation that is only 2 levels way may not be electrically similar

The TUCO, Plant X, Tolk, and Quay County generation (GEN-2011-046) met the above criteria and was scaled to 100% and offset by other synchronous units within the same control area (SPS).  Refer to Tables 2.1-1, 2.1-2, and 2.1-3 for the status of higher queued requests, DISIS-2016-001 requests, DISIS-2016-002, and select DISIS-2017-001 requests.

After updating the power flow cases with the above changes and dispatching units local to the study area according to SPP criteria, there was no suspect power flow data in the study area for the normal dispatch cases or sensitivity cases.  The dynamic datasets were also verified and stable initial system conditions (i.e., “flat lines”) were achieved.  Three-phase and single line-to-ground (single-phase) faults listed in Table 2.3-2 were examined for the normal dispatch scenario.  A subset of the contingency list in Table 2.3-2 was examined for the sensitivity dispatch. Single-phase fault impedances were calculated for each season to result in a voltage of approximately 60% of the pre-fault voltage.  Refer to Table 2.3-3 for a list of the calculated single-phase fault impedances.

Table 2.3-2: Contingency List for Normal Dispatch and Sensitivity Dispatch

| Cont. No. | Cont. Name | Description | Sens. Cont. |
| --- | --- | --- | --- |
| Tuco/OKU Fault Events |  |  |  |
|  | FLT01-3PH | 3 phase fault on the Tuco (525832) to Border (515458) 345 kV line circuit 1, near Tuco. a. Apply fault at the Tuco 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT02-3PH | 3 phase fault on the Tuco (525832) to OKU (511456) 345 kV line circuit 1, near Tuco. a. Apply fault at the Tuco 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT03-3PH | 3 phase fault on the Tuco 345/230/13.8 kV (525832/525830/525824) transformer circuit 1, near Tuco 345 kV. a. Apply fault at the Tuco 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted transformer. | X |
|  | FLT04-3PH | 3 phase fault on the Tuco (525830) to Tolk East (525524) 230 kV line circuit 1, near Tuco. a. Apply fault at the Tuco 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT05-3PH | 3 phase fault on the OKU (511456) to LES (511468) 345 kV line circuit 1, near OKU. a. Apply fault at the OKU 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line and remove the fault. c. Block the DC tie at OKU. |  |
|  | FLT06-3PH | 3 phase fault on the OKU (511456) to LES (511468) 345 kV line circuit 1, near OKU. a. Apply fault at the OKU 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line and remove the fault. |  |
|  | FLT07-3PH | 3 phase fault on the OKU (511456) to Oklaun (599891) 345 kV line circuit 1 (OKU DC tie), near OKU. a. Apply fault at the OKU 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line and remove the fault. c. Block the DC tie at OKU. |  |
|  | FLT08-SB | Single phase fault with stuck breaker at Tuco 345 kV (525832) a. Apply fault at the Tuco 345 kV bus. b. Clear fault after 16 cycles and trip the following elements c. Tuco 345/230/13.2 kV (525832/525830/525824) transformer d. Tuco (525832) – Border (515458) 345 kV | X |
|  | FLT09-SB | Single phase fault with stuck breaker at Tuco 345 kV (525832) a. Apply fault at the Tuco 345 kV bus. b. Clear fault after 16 cycles and trip the following elements c. Tuco 345/230/13.2 kV (525832/525830/525824) transformer d. Tuco (525832) – OKU (511456) 345 kV | X |
|  | FLT10-PO | Prior Outage of the Tuco 345/230/13.2 kV (525832/525830/525824) transformer circuit 1; 3 phase fault on the Tuco (525832) to Border (515458) 345 kV line circuit 1, near Tuco. a. Apply fault at the Tuco 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. | X |
|  | FLT11-PO | Prior Outage of the Tuco (525832) to Border (515458) 345kV circuit 1; 3 phase fault on the Tuco (525832) to OKU (511456) 345 kV line circuit 1, near Tuco. a. Apply fault at the Tuco 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. | X |
|  | FLT12-PO | Prior Outage of the Tuco (525832) to Border (515458) 345kV circuit 1; 3 phase fault on the OKU (511456) to LES (511468) 345 kV line circuit 1, near OKU. a. Apply fault at the OKU 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. |  |
|  | FLT13-PO | Prior Outage of the Tuco (525832) to Border (515458) 345kV circuit 1; 3 phase fault on the OKU (511456) to LES (511468) 345 kV line circuit 1, near OKU. a. Apply fault at the OKU 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Block the DC tie at OKU. |  |
|  | FLT14-PO | Prior Outage of the OKU (511456) to LES (511468) 345kV circuit 1; 3 phase fault on the Tuco (525832) to Border (515458) 345 kV line circuit 1, near Tuco. a. Apply fault at the Tuco 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. | X |
|  | FLT15-PO | Prior Outage of the OKU (511456) to LES (511468) 345kV circuit 1 (block OKU DC tie); 3 phase fault on the Tuco (525832) to Border (515458) 345 kV line circuit 1, near Tuco. a. Apply fault at the Tuco 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. | X |
|  | FLT16-PO | Prior Outage of the Potter County (523961) to Hitchland (523097) 345kV circuit 1; 3 phase fault on the OKU (511456) to LES (511468) 345 kV line circuit 1, near OKU. a. Apply fault at the OKU 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. |  |
|  | FLT17-PO | Prior Outage of the Potter County (523961) to Hitchland (523097) 345kV circuit 1; 3 phase fault on the OKU (511456) to LES (511468) 345 kV line circuit 1, near OKU. a. Apply fault at the OKU 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Block the DC tie at OKU. |  |
|  | FLT18-PO | Prior Outage of the Potter County (523961) to Hitchland (523097) 345kV circuit 1; 3 phase fault on the Tuco (525832) to Border (515458) 345 kV line circuit 1, near Tuco. a. Apply fault at the Tuco 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. | X |
| Potter County Fault Events |  |  |  |
|  | FLT19-3PH | 3 phase fault on the Potter County (523961) to Hitchland (523097) 345 kV line circuit 1, near Potter County. a. Apply fault at the Potter County 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. |  |
|  | FLT19_1-PO | Prior Outage of the Tuco (525832) to Border (515458) 345kV circuit 1; 3 phase fault on the Potter County (523961) to Hitchland (523097) 345 kV line circuit 1, near Potter County. a. Apply fault at the Potter County 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. |  |
|  | FLT19_2-PO | Prior Outage of the OKU (511456) to LES (511468) 345kV circuit 1; 3 phase fault on the Potter County (523961) to Hitchland (523097) 345 kV line circuit 1, near Potter County. a. Apply fault at the Potter County 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. |  |
|  | FLT20-3PH | 3 phase fault on the Potter County 345/230/13 kV (523961/523959/523957) transformer circuit 1, near Potter County. a. Apply fault at the Potter County 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted transformer. |  |
|  | FLT20_2-SB | Single phase fault with stuck breaker at Potter County 345 kV (523961) a. Apply fault at the Potter County 345 kV bus. b. Clear fault after 16 cycles and trip the following elements c. Potter County 345/230/13 kV (523961/523959/523957) transformer |  |
| Norton Fault Events |  |  |  |
|  | FLT21-3PH | 3 phase fault on the Norton (524502) to FE-Tucumcari (524509) 115 kV line circuit 1, near Norton. a. Apply fault at the Norton 115 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT22-3PH | 3 phase fault on the Pleasant Hills (524768) to East Clovis (524773) 115 kV line circuit 1, near Pleasant Hills. a. Apply fault at the Pleasant Hills 115 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT23-3PH | 3 phase fault on the Pleasant Hills (524768) to North Clovis (524776) 115 kV line circuit 1, near Pleasant Hills. a. Apply fault at the Pleasant Hills 115 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT24-3PH | 3 phase fault on the Pleasant Hills (524768) to Holland (524831) 115 kV line circuit 1, near Pleasant Hills. a. Apply fault at the Pleasant Hills 115 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT25-3PH | 3 phase fault on the Pleasant Hills 230/115/13.8 kV (524770/524768/524767) transformer circuit 1, near Pleasant Hills 115 kV. a. Apply fault at the Pleasant Hills 115 kV bus. b. Clear fault after 5 cycles by tripping the faulted transformer. | X |
|  | FLT26-3PH | 3 phase fault on the Pleasant Hills (524770) to Oasis (524875) 230 kV line circuit 1, near Pleasant Hills. a. Apply fault at the Pleasant Hills 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT27-3PH | 3 phase fault on the Pleasant Hills (524770) to Roosevelt (524911) 230 kV line circuit 1, near Pleasant Hills. a. Apply fault at the Pleasant Hills 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT28-3PH | 3 phase fault on the Roosevelt (524911) to Tolk East (525524) 230 kV line circuit 1, near Roosevelt. a. Apply fault at the Roosevelt 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT29-3PH | 3 phase fault on the Roosevelt (524909) to Tolk West (525531) 230 kV line circuit 2, near Roosevelt. a. Apply fault at the Roosevelt 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT30-3PH | 3 phase fault on the Roosevelt 230/115/13.8 kV (525909/524908/524907) transformer circuit 1, near Roosevelt 230 kV. a. Apply fault at the Roosevelt 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted transformer. | X |
|  | FLT31-3PH | 3 phase fault on the Oasis 230/115/13.8 kV (524875/524874/524872) transformer circuit 1, near Oasis 230 kV. a. Apply fault at the Oasis 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted transformer. | X |
|  | FLT32-3PH | 3 phase fault on the Oasis (524875) to Roosevelt (524915) 230 kV line circuit 1, near Oasis. a. Apply fault at the Oasis 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT33-3PH | 3 phase fault on the Oasis (524875) to San Juan Tap (524885) 230 kV line circuit 1, near Oasis. a. Apply fault at the Oasis 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT34-SB | Single phase fault with stuck breaker at Pleasant Hills 115 kV (524768) a. Apply fault at the Pleasant Hills kV bus. b. Clear fault after 16 cycles and trip the following elements c. Pleasant Hills (524768) – East Clovis (524773) 115 kV d. Pleasant Hills (524768) – Holland (524831) 115 kV | X |
|  | FLT35-SB | Single phase fault with stuck breaker at Pleasant Hills 115 kV (524768) a. Apply fault at the Pleasant Hills kV bus. b. Clear fault after 16 cycles and trip the following elements c. Pleasant Hills (524768) – North Clovis (524776) 115 kV d. Pleasant Hills (524768) – Holland (524831) 115 kV | X |
|  | FLT36-PO | Prior Outage of the Pleasant Hills (524768) to East Clovis (524773) 115 kV line circuit 1; 3 phase fault on the Pleasant Hills (524768) to North Clovis (524776) 115 kV line circuit 1, near Pleasant Hills. a. Apply fault at the Pleasant Hills kV bus. b. Clear fault after 5 cycles by tripping the faulted line. | X |
|  | FLT37-PO | Prior Outage of the Pleasant Hills (524768) to East Clovis (524773) 115 kV line circuit 1; 3 phase fault on the Pleasant Hills (524768) to Holland (524831) 115 kV line circuit 1, near Pleasant Hills. a. Apply fault at the Pleasant Hills kV bus. b. Clear fault after 5 cycles by tripping the faulted line. | X |
|  | FLT38-PO | Prior Outage of the Pleasant Hills Transformer (524770/524768/524767) circuit 1; 3 phase fault on the Pleasant Hills (524768) to East Clovis (524773) 115 kV line circuit 1, near Pleasant Hills. a. Apply fault at the Pleasant Hills kV bus. b. Clear fault after 5 cycles by tripping the faulted line. | X |
|  | FLT39-PO | Prior Outage of the Pleasant Hills Transformer (524770/524768/524767) circuit 1; 3 phase fault on the Pleasant Hills (524768) to North Clovis (524776) 115 kV line circuit 1, near Pleasant Hills. a. Apply fault at the Pleasant Hills kV bus. b. Clear fault after 5 cycles by tripping the faulted line. | X |
|  | FLT40-PO | Prior Outage of the Pleasant Hills Transformer (524770/524768/524767) circuit 1; 3 phase fault on the Pleasant Hills (524768) to Holland (524831) 115 kV line circuit 1, near Pleasant Hills. a. Apply fault at the Pleasant Hills kV bus. b. Clear fault after 5 cycles by tripping the faulted line. | X |
|  | FLT41-3PH | 3 phase fault on the FE-Tucumcari (524509) to Ceilo-Tap (583610) 115 kV line circuit 1, near FE-Tucumcari. a. Apply fault at the FE-Tucumcari 115 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT42-3PH | 3 phase fault on the Lopez (524472) to Campbell St (524477) 115 kV line circuit 1, near Campbell St. a. Apply fault at the Campbell St 115 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
| Tolk 345kV Fault Events |  |  |  |
|  | FLT43-3PH | 3 phase fault on the Crossroads (527656) to Tolk (525549) 345 kV line circuit 1, near Crossroads. a. Apply fault at the Crossroads 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT43a-3PH | 3 phase fault on the Crossroads (527656) to Tolk (525549) 345 kV line circuit 1, near Crossroads with tripping of Sagamore Wind Plant. a. Apply fault at the Crossroads 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line with simultaneous trip of Sagamore Facility with tripping and lockout of Crossroads to Sagamore 345 kV circuit. d. Wait 20 cycles, and then re-close the Tolk line in (b) back into the fault. e. Leave fault on for 5 cycles, then trip the Tolk line in (b) and remove fault. | X |
|  | FLT44-3PH | 3 phase fault on the Tolk (525549) to Crossroads (527656) 345 kV line circuit 1, near Tolk. a. Apply fault at the Tolk 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT44a-3PH | 3 phase fault on the Tolk (525549) to Crossroads (527656) 345 kV line circuit 1, near Tolk with tripping of Sagamore Wind Plant. a. Apply fault at the Tolk 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line with simultaneous trip of Sagamore Facility with tripping and lockout of Crossroads to Sagamore Wind Plant 345 kV circuit. d. Wait 20 cycles, and then re-close the line in (b) back into the fault. e. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT45-3PH | 3 phase fault on the Crossroads (527656) to Eddy County (527802) 345 kV line circuit 1, near Crossroads. a. Apply fault at the Crossroads 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT46-3PH | 3 phase fault on the Tolk East (525524) to Roosevelt (524911) 230 kV line circuit 1, near Tolk East. a. Apply fault at the Tolk East 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT47-3PH | 3 phase fault on the Tolk East (525524) to Plant X (525481) 230 kV line circuit 2, near Tolk East. a. Apply fault at the Tolk East 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT48-3PH | 3 phase fault on the Tolk East (525524) to Tuco (525830) 230 kV line circuit 1, near Tolk East. a. Apply fault at the Tolk East 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT49-3PH | 3 phase fault on the Tolk West (525531) to Plant X (525481) 230 kV line circuit 1, near Tolk West. a. Apply fault at the Tolk West 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT50-3PH | 3 phase fault on the Tolk West (525531) to Roosevelt (525909) 230 kV line circuit 2, near Tolk West. a. Apply fault at the Tolk West 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT51-3PH | 3 phase fault on the Tolk West (525531) to G13-027-Tap (562480) 230 kV line circuit 1, near Tolk West. a. Apply fault at the Tolk West 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT52-3PH | 3 phase fault on the Tolk West (525531) to Lamb County (525637) 230 kV line circuit 1, near Tolk West. a. Apply fault at the Tolk West 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT53-SB | Single phase fault with stuck breaker at Tolk East 230 kV (525524) a. Apply fault at the Tolk East 230 kV bus. b. Clear fault after 16 cycles and trip the following elements c. Tolk East (525524) – Roosevelt (524911) 230 kV d. Tolk East (525524) – Plant X (525481) 230 kV | X |
|  | FLT54-SB | Single phase fault with stuck breaker at Tolk East 230 kV (525524) a. Apply fault at the Tolk East 230 kV bus. b. Clear fault after 16 cycles and trip the following elements c. Tolk East (525524) – Tuco (525830) 230 kV d. Tolk East (525524) – Tolk Tap (525543) 230 kV | X |
|  | FLT55-SB | Single phase fault with stuck breaker at Tolk West 230 kV (525531) a. Apply fault at the Tolk West 230 kV bus. b. Clear fault after 16 cycles and trip the following elements c. Tolk West (525531) – Roosevelt (524909) 230 kV d. Tolk West (525531) – Plant X (525481) 230 kV | X |
|  | FLT56-SB | Single phase fault with stuck breaker at Tolk West 230 kV (525531) a. Apply fault at the Tolk West 230 kV bus. b. Clear fault after 16 cycles and trip the following elements c. Tolk West (525531) – G13-027-Tap (562480) 230 kV d. Tolk West (525531) – Lamb County (525637) 230 kV | X |
|  | FLT57-SB | Single phase fault with stuck breaker at Tolk 345 kV (525549) a. Apply fault at the Tolk 345 kV bus. b. Clear fault after 16 cycles and trip the following elements c. Tolk (525549) – Crossroads (527656) 345 kV d. Tolk 345/230kV Transformer (525549/525543/525537) | X |
|  | FLT57a-SB | Single phase fault with stuck breaker at Tolk 345 kV (525549) a. Apply fault at the Tolk 345 kV bus. b. Clear fault after 16 cycles and trip the following elements c. Tolk (525549) – Crossroads (527656) 345 kV d. Trip Sagamore Facility with tripping and lockout of Crossroads to Sagamore 345 kV circuit. e. Tolk 345/230kV Transformer (525549/525543/525537) | X |
|  | FLT58-SB | Single phase fault with stuck breaker at Eddy County 345 kV (527802) a. Apply fault at the Eddy County 345 kV bus. b. Clear fault after 16 cycles and trip the following elements c. Eddy County (527802) – Crossroads (527656) 345 kV d. Eddy County 345/230kV Transformer (527656/527799/527796) | X |
|  | FLT59-PO | Prior Outage of the Eddy County (527802) to Crossroads (527656) 345 kV line circuit 1; 3 phase fault on the Tolk East (525524) to Roosevelt (524911) 230 kV line circuit 1, near Tolk East. a. Apply fault at the Tolk East 230 kV bus. b. Clear fault after 6 cycles by tripping the faulted line. | X |
|  | FLT60-PO | Prior Outage of the Eddy County (527802) to Crossroads (527656) 345 kV line circuit 1; 3 phase fault on the Tolk East (525524) to Plant X (525481) 230 kV line circuit 2, near Tolk East. a. Apply fault at the Tolk East 230 kV bus. b. Clear fault after 6 cycles by tripping the faulted line. | X |
|  | FLT61-PO | Prior Outage of the Eddy County (527802) to Crossroads (527656) 345 kV line circuit 1; 3 phase fault on the Tolk East (525524) to Tuco (525830) 230 kV line circuit 1, near Tolk East. a. Apply fault at the Tolk East 230 kV bus. b. Clear fault after 6 cycles by tripping the faulted line. | X |
|  | FLT62-PO | Prior Outage of the Eddy County (527802) to Crossroads (527656) 345 kV line circuit 1; 3 phase fault on the Tolk West (525531) to Roosevelt (524909) 230 kV line circuit 2, near Tolk West. a. Apply fault at the Tolk West 230 kV bus. b. Clear fault after 6 cycles by tripping the faulted line. | X |
|  | FLT63-PO | Prior Outage of the Eddy County (527802) to Crossroads (527656) 345 kV line circuit 1; 3 phase fault on the Tolk West (525531) to Plant X (525481) 230 kV line circuit 1, near Tolk West. a. Apply fault at the Tolk West 230 kV bus. b. Clear fault after 6 cycles by tripping the faulted line. | X |
|  | FLT64-PO | Prior Outage of the Eddy County (527802) to Crossroads (527656) 345 kV line circuit 1; 3 phase fault on the Tolk West (525531) to G13-027-Tap (562480) 230 kV line circuit 1, near Tolk West. a. Apply fault at the Tolk West 230 kV bus. b. Clear fault after 6 cycles by tripping the faulted line. | X |
|  | FLT65-PO | Prior Outage of the Eddy County (527802) to Crossroads (527656) 345 kV line circuit 1; 3 phase fault on the Tolk West (525531) to Lamb County (525637) 230 kV line circuit 1, near Tolk West. a. Apply fault at the Tolk West 230 kV bus. b. Clear fault after 6 cycles by tripping the faulted line. | X |
|  | FLT66-PO | Prior Outage of the Tolk (525549) to Crossroads (527656) 345 kV line circuit 1; 3 phase fault on the Eddy County (527802) to Kiowa (527965) 345 kV line circuit 1, near Eddy County. a. Apply fault at the Eddy County 345 kV bus. b. Clear fault after 6 cycles by tripping the faulted line. | X |
|  | FLT67-PO | Prior Outage of the Tolk (525549) to Crossroads (527656) 345 kV line circuit 1; 3 phase fault on the Eddy County 345/230kV transformer (527802/527799/527796), near Eddy County. a. Apply fault at the Eddy County 345 kV bus. b. Clear fault after 6 cycles by tripping the faulted line. | X |
|  | FLT68-3PH | 3 phase fault on the Plant X (525481) to Tolk East (525524) 230 kV line circuit 2, near Plant X. a. Apply fault at the Plant X 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT69-3PH | 3 phase fault on the Plant X (525481) to Newhart (525461) 230 kV line circuit 1, near Plant X. a. Apply fault at the Plant X 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT70-3PH | 3 phase fault on the Plant X (525481) to Tolk West (525531) 230 kV line circuit 1, near Plant X. a. Apply fault at the Plant X 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT71-3PH | 3 phase fault on the Plant X (525481) to Sundown (526435) 230 kV line circuit 1, near Plant X. a. Apply fault at the Plant X 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT72-3PH | 3 phase fault on the Plant X 230/115/13.2 kV (525481/525480/525479) transformer circuit 1, near Plant X 230 kV. a. Apply fault at the Plant X 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted transformer. | X |
|  | FLT73-3PH | 3 phase fault on the Plant X (525481) to Deaf Smith (524623) 230 kV line circuit 1, near Plant X. a. Apply fault at the Plant X 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
| Kiowa 345kV Fault Events |  |  |  |
|  | FLT74-3PH | 3 phase fault on the Kiowa (527965) to Eddy County (527802) 345 kV line circuit 1, near Kiowa. a. Apply fault at the Kiowa 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT75-3PH | 3 phase fault on the Kiowa (527965) to Hobbs (527896) 345 kV line circuit 1, near Kiowa. a. Apply fault at the Kiowa 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT76-3PH | 3 phase fault on the Kiowa (527965) to Road Runner (528027) 345 kV line circuit 1, near Kiowa. a. Apply fault at the Kiowa 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT77-3PH | 3 phase fault on the Kiowa (527965) to North Loving (528185) 345 kV line circuit 1, near Kiowa. a. Apply fault at the Kiowa 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT78-3PH | 3 phase fault on the Kiowa 345/115/13.2 kV (527965/527966/527964) transformer circuit 1, near Kiowa 345 kV. a. Apply fault at the Kiowa 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted transformer. | X |
|  | FLT79-PO | Prior Outage of the Tolk (525549) to Crossroads (527656) 345 kV line circuit 1; 3 phase fault on the Eddy County (527802) to Kiowa (527965) 345 kV line circuit 1, near Kiowa. a. Apply fault at the Kiowa 345 kV bus. b. Clear fault after 6 cycles by tripping the faulted line. | X |
|  | FLT80-PO | Prior Outage of the Tolk (525549) to Crossroads (527656) 345 kV line circuit 1; 3 phase fault on the Kiowa (527965) to Hobbs (527896) 345 kV line circuit 1, near Kiowa. a. Apply fault at the Kiowa 345 kV bus. b. Clear fault after 6 cycles by tripping the faulted line. | X |
|  | FLT81-PO | Prior Outage of the Tolk (525549) to Crossroads (527656) 345 kV line circuit 1; 3 phase fault on the Kiowa (527965) to Road Runner (528027) 345 kV line circuit 1, near Kiowa. a. Apply fault at the Kiowa 345 kV bus. b. Clear fault after 6 cycles by tripping the faulted line. | X |
|  | FLT82-PO | Prior Outage of the Tolk (525549) to Crossroads (527656) 345 kV line circuit 1; 3 phase fault on the Kiowa (527965) to North Loving (528185) 345 kV line circuit 1, near Kiowa. a. Apply fault at the Kiowa 345 kV bus. b. Clear fault after 6 cycles by tripping the faulted line. | X |
|  | FLT83-PO | Prior Outage of the Tolk (525549) to Crossroads (527656) 345 kV line circuit 1; 3 phase fault on the Kiowa 345/115 kV transformer (527965/527962/527964) circuit 1, near Kiowa. a. Apply fault at the Kiowa 345 kV bus. b. Clear fault after 6 cycles by tripping the faulted line. | X |
|  | FLT84-3PH* | 3 phase fault on the Tolk 345/230kV transformer (525549/525543) circuit 2, near Tolk. a. Apply fault at the Tolk 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted transformer. | X |
| *FLT84-3PH only examined with addition of 2nd Tolk 345/230kV transformer |  |  |  |

Table 2.3-3: Calculated Single-Phase Fault Impedances

| 1Ref. No. | Cont. Name | Faulted Bus | Single-Phase Fault Impedance (MVA) |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | 2017 Winter | 2018 Summer | 2026 Summer |
| 8 | FLT08-SB | Tuco 345kV (525832) | -3421.9 | -4437.5 | -4437.5 |
| 9 | FLT09-SB | Tuco 345kV (525832) | -3421.9 | -4437.5 | -4437.5 |
| 21 | FLT20_2-SB | Potter County 345kV (523961) | -2850.0 | -2690.0 | -2718.0 |
| 34 | FLT34-SB | Pleasant Hills 115kV (524768) | -1250.0 | -1250.0 | -1250.0 |
| 35 | FLT35-SB | Pleasant Hills 115kV (524768) | -1250.0 | -1250.0 | -1250.0 |
| 53 | FLT53-SB | Tolk East 230kV (525524) | -6062.5 | -6062.5 | -6062.5 |
| 54 | FLT54-SB | Tolk East 230kV (525524) | -6062.5 | -6062.5 | -6062.5 |
| 55 | FLT55-SB | Tolk West 230kV (525531) | -6062.5 | -6062.5 | -6062.5 |
| 56 | FLT56-SB | Tolk West 230kV (525531) | -6062.5 | -6062.5 | -6062.5 |
| 57 | FLT57-SB | Tolk 345kV (525549) | -3421.9 | -3421.9 | -3421.9 |
| 57a | FLT57a-SB | Tolk 345kV (525549) | -3421.9 | -3421.9 | -3421.9 |
| 58 | FLT58-SB | Eddy County (527802) | -3421.9 | -3421.9 | -3421.9 |

- Refer to Table 2.3-2 for a description of the contingency scenario.

Bus voltages, machine rotor angles, and previously queued generation in the study area were monitored in addition to bus voltages and machine rotor angles in the following areas:

- 520 AEPW

- 524 OKGE

- 525 WFEC

- 526 SPS

- 531 MIDW

- 534 SUNC

- 536 WERE

Requested and previously queued generation outside the above study area was also monitored. The results of the analysis determined if Limited Operation or reduced Interim Service was required to obtain acceptable system performance. Note all wind or solar farms are required to meet FERC Order 661A low voltage requirements and should return to its pre-disturbance operating voltage.

### Normal Dispatch Stability Analysis Results

The normal dispatch stability analysis determined that there were multiple P1, P4, and P6 contingencies that resulted either high post-fault steady-state voltages, voltage instability, and/or generation tripping across all seasons when all generation interconnection requests were at 100% output.

Refer to Table 2.3-4 for a summary of the stability analysis results for the normal dispatch scenario and Table 2.3-5 for a summary of the required mitigation/generation curtailment. Note the generation dispatch values in Table 2.3-5 represent the gross generation capacity observed at the generator terminals. Table 2.3-4 is a summary of the stability results for the 17WP, 18SP, and 26SP conditions and states whether the system remained stable, or generation tripped offline, if acceptable voltage recovery was observed after the fault was cleared, and if the voltage recovered to above 0.9 p.u. and below 1.1 p.u. post fault steady-state conditions.  Voltage recovery criteria includes ensuring that the transient voltage recovery is between 0.7 p.u. and 1.2 p.u. and ending in a steady-state voltage (for N-1 contingencies) at the pre-contingent level or at least above 0.9 p.u. and below 1.1. p.u.

Table 2.3-4: Summary of Results for 17WP, 18SP, and 26SP Conditions for the Normal Dispatch Scenario

Table 2.3-4: Summary of Results for 17WP, 18SP, and 26SP Conditions for the Normal Dispatch Scenario (cont.)

Table 2.3-4: Summary of Results for 17WP, 18SP, and 26SP Conditions for the Normal Dispatch Scenario (cont.)

Table 2.3-4: Summary of Results for 17WP, 18SP, and 26SP Conditions for the Normal Dispatch Scenario (cont.)

Table 2.3-5: Required Mitigation/Generation Curtailment for the Normal Dispatch Scenario

Table 2.3-5: Required Mitigation/Generation Curtailment for the Normal Dispatch Scenario (cont.)

Generation capacity and system adjustments were investigated to determine the maximum amount of generation that can be interconnected while observing acceptable voltage and generator response pursuant to SPP Performance Criteria. The following is a summary of the results.

- High post-fault steady-state voltage at Oklaunion 345kV

  - Mitigation: Trip the Oklaunion HVDC reactive equipment at Oklaunion 345kV simultaneously with blocking of the Oklaunion HVDC tie

- Event resulting in outage of Crossroads to Eddy County 345kV circuit

  - Voltage stability is observed with a combined Roosevelt, Milo, and Sagamore output at 822 MW with the Sagamore as-built models.

  - Stability is maintained when a RAS that trips the Sagamore facility for this event is enabled.

  - Stability is maintained following retirement of the RAS that trips the Sagamore facility for this event and the DISIS-2016-002 assigned Tolk 345/230 kV transformer #2 is in-service.

- Event resulting in outage of Crossroads 345 kV to Tolk 345kV circuit or Tolk 345/230 kV transformer #1 (and #2 once in-service)

  - Voltage instability is observed with a combined Roosevelt, Milo, and Sagamore output at 822 MW.

  - Stability is maintained when Sagamore Wind output does not exceed 336 MW (stability margin calculation will include 300 MW from Roosevelt and Milo wind facilities) at Crossroads 345kV or when the combined Roosevelt, Milo, and Sagamore output does not exceed 636 MW at Crossroads 345kV with normal system configuration, all breakers in-service or

  - Stability is maintained when Crossroads 345 kV substation breaker configuration results in a trip of the Sagamore facility for these events (full interconnection capacity of Roosevelt, Milo and Sagamore facilities with the new breaker configuration in-place)

- Prior outage events resulting in voltage instability with a combined Roosevelt, Milo, and Sagamore output at 822 MW.

  - Loss of Crossroads to Tolk 345kV transmission line

    - Stability is maintained when Sagamore Wind output does not exceed 274 MW (stability margin calculation will include 300 MW from Roosevelt and Milo wind facilities) at Crossroads 345kV or when the combined Roosevelt, Milo, and Sagamore output does not exceed 574 MW at Crossroads 345kV

  - Loss of Crossroads to Eddy County 345kV transmission line

    - Stability is maintained when Sagamore Wind output does not exceed 455 MW (stability margin calculation will include 300 MW from Roosevelt and Milo wind facilities) at Crossroads 345kV or when the combined Roosevelt, Milo, and Sagamore output does not exceed 755 MW at Crossroads 345kV

It was observed that NERC Category P1 and P6 events near Oklaunion 345kV and Tuco 345kV, with the exclusion of the AEP OKU RAS retirement, resulted in high post-fault steady-state voltages at Oklaunion 345kV. The limiting NERC Category P1 contingency was FLT05-3PH, a three-phase fault at Oklaunion 345kV resulting in the loss of the Oklaunion to Lawton Eastside 345kV line and simultaneous blocking of the Oklaunion HVDC line. Following the clearing of the fault, the Oklaunion 345kV voltage has a post-fault steady-state voltage above 1.10 p.u. due to the Oklaunion HVDC capacitive support at Oklaunion. It is recommended the capacitive support be included in the simultaneous blocking of the HVDC line prior to the OKU RAS retirement. Refer to Figure 2.3-1 for a representative voltage plot at Oklaunion and Tuco 345kV substations comparing the original fault event to the fault event including the tripping of the capacitive support.  These events are no longer valid and do not require mitigation due to the RAS retirement.

Figure 2.3-1: Representative voltage plot for FLT05-3PH for 2017 Winter Peak conditions.

There were several P1 and P4 events involving circuits connected to Crossroads 345kV that resulted in voltage instability and Sagamore Wind tripping offline for all three seasons prior to system adjustments and model updates. For P1 and P4 events, the most severe event was the loss of the Crossroads to Tolk 345kV line.  This fault resulted in voltage instability and the Crossroads 345kV wind generation entering and exiting low voltage ride through mode with the full interconnection capability of Sagamore, Roosevelt, and Milo wind facilities (822 MW). It was determined that reducing the combined output of Sagamore, Roosevelt, and Milo Wind at Crossroads 345 kV to 650 MW at the generator terminals (636 MW at Crossroads 345kV) would result in acceptable system recovery and acceptable response of Sagamore Wind and nearby generation prior to any updates to breaker configuration at Crossroads 345 kV. Refer to Table 2.3-6 for various outputs of Sagamore Wind and Roosevelt-Milo Wind that determined the highest stable output of 636 MW at Crossroads 345kV.

Table 2.3-6: Crossroads 345kV Stable Output Results

Refer to Figure 2.3-2 for a representative voltage plot comparing area bus voltages with Sagamore Wind at full output (522 MW) and with Sagamore Wind at reduced output (350 MW) at the generator terminals. Refer to Figure 2.3-3 for a representative plot of the real power of the Sagamore Wind units. Note the voltage transient following the fault clear event is shown to exceed 1.2 p.u. voltage at Crossroads 345kV in Figure 2.3-2. The voltage spike is not considered a violation but rather a limitation to the PSS/E program’s calculations. For a more accurate response of the voltage transient, a detailed PSCAD analysis may be performed.

Figure 2.3-2: Representative voltage plot for FLT43-3PH for 2017 Winter Peak conditions.

Figure 2.3-3: Representative real power plot for FLT43-3PH for 2017 Winter Peak conditions.

Refer to Figure 2.3-4 for a representative voltage plot showing the bus voltage response for FLT43-3PH for the alternate dispatches of Sagamore, Roosevelt, and Milo Wind shown in Table 2.3-6 (reference numbers 3 – 5). Refer to Figure 2.3-5 for a representative real power response of Sagamore Wind and Roosevelt-Milo Wind for reference numbers 3 through 5 in Table 2.3-6. The voltage response and real power response observed for 17WP conditions confirm the highest stable output of 650 MW at the generator terminals (636 MW at Crossroads 345kV). A combined output of 650 MW at the generator terminals (636 MW at Crossroads 345kV) from Sagamore, Roosevelt, and Milo Wind result in system stability and no generation tripping offline.

Figure 2.3-4: Representative voltage plot for FLT43-3PH for 2017 Winter Peak conditions for various Crossroads wind dispatches.

Figure 2.3-5: Representative real power plot for FLT43-3PH for 2017 Winter Peak conditions for various Crossroads wind dispatches.

After determining this event resulted in voltage instability and after discussion with the Transmission Owner, the breaker configuration at Crossroads 345kV was updated to result in a trip of Crossroads to Sagamore circuit including the wind facility for loss of Crossroads to Tolk 345 kV circuit. Refer to Figure 2.3-6 for a representative voltage plot for area bus voltages following the event of a fault on Crossroads to Tolk 345 kV. Note to meet SPP Performance Criteria for steady-state post-fault voltages, the capacitor bank at Crossroads was switched from 2 stages (100 MVAR total) to one stage (50 MVAR total) in-service. This switching was performed manually in the simulation at approximately 9 seconds (T=10) following the event.  Actual field settings are expected to provide a similar response.  Refer to Figure 2.3-7 for a representative plot of the active power response for nearby generation facilities.

Figure 2.3-6: Representative voltage plot for FLT43a-3PH for 2017 Winter Peak conditions with updated breaker configuration at Crossroads 345 kV.

Figure 2.3-7: Representative real power plot for FLT43a-3PH for 2017 Winter Peak conditions with updated breaker configuration at Crossroads 345 kV.

A Remedial Action Scheme has been designed for Sagamore Wind for the loss of the Crossroads to Eddy County 345kV line to limit the flow across the Tolk 345/230kV transformer. The RAS will trip the Sagamore Wind plant when the Crossroads to Tolk 345kV line exceeds 478 MVA for 21 seconds or 556 MVA for 30 cycles plus a 1 cycle timer. The impact of this RAS was analyzed in this study by tripping the Sagamore Wind plant 31 cycles after the first instance of Crossroads to Eddy County 345kV is taken out-of-service. This tripping was performed manually in the simulation at approximately 31 cycles (T=1) following the initial fault.  Actual field settings are expected to provide a similar response.  To determine the stability of the system with and without the RAS, this analysis was performed both with the RAS in-service and with the RAS out-of-service.

FLT45-3PH, a three-phase fault resulting in the loss of Crossroads to Eddy County 345kV, was analyzed to determine the impact of the RAS. Without the RAS enabled and with the as-built model parameters, it was determined Sagamore Wind can interconnect at full output. With the RAS in operation, there were no adverse impacts observed because of the RAS tripping Sagamore Wind. Refer to Figure 2.3-8 for a representative voltage plot of area voltages for 2018 Summer Peak conditions comparing Sagamore Wind at full output with the RAS disabled and Sagamore Wind at full output with the RAS enabled (tripping Sagamore Wind). Refer to Figure 2.3-9 for a plot of the MVA through the Crossroads to Tolk 345kV line and the activation of the RAS.

Figure 2.3-8: Representative voltage plot for FLT45-3PH for 2018 Summer Peak conditions.

Figure 2.3-9: Plot of the MVA flow through Crossroads to Tolk 345kV for FLT45-3PH for 2018 Summer Peak conditions.

FLT58-SB, a stuck breaker fault resulting in the loss of Crossroads to Eddy County 345kV and Eddy County 345/230kV transformer resulted in voltage stability with and without enabling the SPS Sagamore Wind RAS. With the RAS in operation, there was no adverse impacts observed as a result of the RAS and all local units remained online. Refer to Figure 2.3-10 for a representative voltage plot of Crossroads 345kV bus voltage for 2018 Summer Peak conditions comparing Sagamore Wind at full output with the RAS disabled and Sagamore Wind at full output with the RAS enabled. Refer to Figure 2.3-11 for a plot of the MVA through the Crossroads to Tolk 345kV line and the activation of the RAS.

Figure 2.3-10: Representative voltage plot for FLT58-SB for 2018 Summer Peak conditions.

Figure 2.3-11: Plot of the MVA flow through Crossroads to Tolk 345kV for FLT58-SB for 2018 Summer Peak conditions.

### Curtailment for P6 Events for the Normal Dispatch Scenario

The limiting NERC Category P6 contingencies involved the outage of either the Crossroads to Tolk 345kV line or the Crossroads to Eddy County 345kV line for all seasons. Voltage instability exists for a prior outage of either line out of Crossroads 345kV followed by a local three-phase fault and was determined that curtailing generation at Crossroads 345kV was required. It was determined that curtailing approximately 50 MW at the generator terminals (GEN-2008-022, GEN-2016-123, GEN-2016-124, & GEN-2016-125) or reducing total MW injection at Crossroads 345kV to 755 MW results in stable conditions for the prior outage of Crossroads to Eddy County 345kV and curtailing approximately 237 MW at the generator terminals (574 MW injection at Crossroads 345kV) for the prior outage of Crossroads to Tolk 345kV. The limiting prior outage contingency was the prior outage of Crossroads to Tolk 345kV followed by the loss of the Eddy County to Kiowa 345kV line (FLT66-PO). Refer to Figure 2.3-12 for a representative plot of area bus voltages without generation reduction and with generation reduction of 228 MW at Crossroads 345kV (reduction of 237 MW at generator terminals). Refer to Figure 2.3-13 for a plot of the real power output of one aggregated machine for Sagamore Wind. It can be observed that when Sagamore Wind and Roosevelt Wind have a combined output of approximately 585 MW at the generator terminals (574 MW at Crossroads 345kV) system stability is maintained and recovers within SPP Performance Criteria.

Figure 2.3-12: Representative voltage plot for FLT66-PO for 2018 Summer Peak conditions.

Figure 2.3-13: Representative real power plot for FLT66-PO for 2018 Summer Peak conditions.

### Addition of Tolk 345/230kV Transformer #2 for the Normal Dispatch Scenario

Power flow analysis in DISIS-2016-002 identified the need for a 2nd Tolk 345/230kV transformer to alleviate a thermal constraint on the Tolk 345/230kV transformer #1 for the loss of the Crossroads to Eddy County 345kV line. Currently, a RAS has been designed for Sagamore Wind for the loss of the Crossroads to Eddy County 345kV line to limit the flow across the Tolk 345/230kV transformer. This RAS will be retired upon installation of the Tolk 345/230kV transformer #2 and a sensitivity was performed to determine the stability of the system with this addition. It was determined that there are no adverse impacts with the addition of the 2nd Tolk transformer and the retirement of the Sagamore Wind RAS for select P1 and P4 events at Crossroads 345kV and Eddy County 345kV substations. Refer to Figure 2.3-14 for the voltage response at Crossroads 345kV for the following:

- Comparison plot of FLT45 with and without the 2nd Tolk 345/230kV transformer

- Voltage plot for FLT58 with the Tolk 345/230kV transformer

- Voltage plot for a fault on Tolk 345kV resulting in the loss of the 2nd Tolk 345/230kV transformer (identified as FLT84)

Figure 2.3-14: Representative voltage plot for faults with addition of the Tolk 345/230kV transformer for 2018 Summer Peak conditions.

This analysis provides an evaluation of the system response for select P1 and P4 events at Crossroads 345kV and Eddy County 345kV for all seasons and scenarios with the addition of the 2nd Tolk transformer. However, this analysis excludes the evaluation of prior outage system conditions at and near Crossroads 345kV, Eddy County 345kV, and Tolk 230kV and may require additional analysis to determine system impacts, if any.

### Summary of the Normal Dispatch Scenario Results

The analysis of the Normal Dispatch Scenario determined generation curtailment is required to alleviate high post-fault steady-state voltages, voltage instability, and generation tripping offline in the Crossroads 345kV vicinity for P6 events near Crossroads and Eddy County 345kV. It was determined that tripping the Oklaunion reactive support at the Oklaunion substation under system conditions with the HVDC tie being blocked, tripping the Sagamore wind facility with switching of shunt reactive equipment, and curtailing area generation by up to approximately 237 MW adjusted by losses on interconnection facilities would alleviate the voltage violation concerns.

### Sensitivity Stability Analysis Results

The sensitivity dispatch stability analysis determined there were multiple P1, P4, and P6 contingencies that resulted either high post-fault steady-state voltages, voltage instability, and/or generation tripping across all seasons when all generation interconnection requests were at 100% output.

Refer to Table 2.3-7 for a summary of the stability analysis results for the sensitivity dispatch scenario and Table 2.3-7 for a summary of the mitigation/generation curtailment required. Note the generation dispatch values in Table 2.3-8 represent the gross generation capacity observed at the generator terminals. Table 2.3-7 is a summary of the stability results for the 17WP, 18SP, and 26SP conditions and states whether the system remained stable or generation tripped offline, if acceptable voltage recovery was observed after the fault was cleared, and if the voltage recovered to above 0.9 p.u. and below 1.1 p.u. post fault steady-state conditions.  Voltage recovery criteria includes ensuring that the transient voltage recovery is between 0.7 p.u. and 1.2 p.u. and ending in a steady-state voltage (for N-1 contingencies) at the pre-contingent level or at least above 0.9 p.u. and below 1.1. p.u.

Table 2.3-7: Summary of Results for 17WP, 18SP, and 26SP Conditions for the Sensitivity Dispatch Scenario

Table 2.3-7: Summary of Results for 17WP, 18SP, and 26SP Conditions for Sensitivity Dispatch Scenario (cont.)

Table 2.3-7: Summary of Results for 17WP, 18SP, and 26SP Conditions for Sensitivity Dispatch Scenario (cont.)

Table 2.3-7: Summary of Results for 17WP, 18SP, and 26SP Conditions for Sensitivity Dispatch Scenario (cont.)

Table 2.3-8: Required Mitigation/Generation Curtailment for the Sensitivity Dispatch Scenario

Table 2.3-8: Required Mitigation/Generation Curtailment for the Sensitivity Dispatch Scenario (cont.)

The Sensitivity Dispatch Scenario identified similar response and results to the Normal Dispatch Scenario. It was determined that curtailing area generation by up to approximately 237 MW adjusted by losses on interconnection facilities would alleviate the voltage violation concerns for prior outage conditions of Tolk to Crossroads 345kV.  There was an identified increase in the amount of generation curtailment from 50 MW in the Normal Dispatch to 100 MW in the Sensitivity Dispatch for prior outage conditions of Tolk to Eddy County 345 kV.

The Sensitivity Dispatch Scenario analyzed the dispatch of local generation to their Pmax values which included the Tolk Unit #1 dispatched at full output (586 MW gross output) for 2017 Winter Peak conditions instead of as a synchronous condenser as modeled in Normal Dispatch Scenario.

### Summary of the Sensitivity Dispatch Scenario Results

The analysis of the sensitivity dispatch scenario determined there are violation concerns, incremental from the fault events evaluated as follows.

- Prior outage events resulting in voltage instability with a combined Roosevelt, Milo, and Sagamore output at 822 MW.

  - Loss of Crossroads to Eddy County 345kV transmission line

    - Stability is maintained when Sagamore Wind output does not exceed 406 MW (stability margin calculation will include 300 MW from Roosevelt and Milo wind facilities) at Crossroads 345kV or when the combined Roosevelt, Milo, and Sagamore output does not exceed 706 MW at Crossroads 345kV

With the Sagamore RAS, breaker configuration, and identified curtailment applied for P6 events; all fault events resulted in acceptable voltage, rotor angle, and power oscillation recovery applicable to SPP Performance Criteria with Sagamore operating at full interconnection capability for P1, P4, and P6 events. It was determined from the sensitivity faults evaluated that Sagamore Wind and GEN-2017-069 do not have an adverse impact on the generation interconnected within the same vicinity of SPS and neighboring transmission systems.

## LOIS and Interim Availability Study Conclusion

Summary of Power Flow Analysis

The power flow analysis determined a Limited Operation amount for GEN-2016-123, GEN-2016-124, and GEN-2016-125 and the available interim service for GEN-2017-069. It was determined, with appropriate system adjustments to voltage schedules and ensure power factor requirements are met (Scenario 3), GEN-2016-123, GEN-2016-124, and GEN-2016-125 can connect at full output and Interim Request GEN-2017-069 can connect at full Interim Service. In the event Scenario 3 is determined to be invalid, Sagamore Wind would have a Limited Operation of 274 MW at the generator terminals (272 MW at Crossroads 345kV) and GEN-2017-069 would not have interim service available (0 MW)(Scenario 2).

Evaluation of the 2nd Tolk 345/230 kV transformer was not included in the power flow analysis for this study. However, the DISIS-2016-002 study, performed by SPP, confirmed the LOIS with Sagamore RAS retired and 2nd Tolk 345/230 kV transformer in-service is the full output of Sagamore (522 MW). Refer to the DISIS-2016-002 report posted on the SPP Oasis Portal for details of this evaluation.

Summary of Stability Analysis

The stability analysis determined that there were multiple P1, P4, and P6 contingencies that resulted either high post-fault steady-state voltages, voltage instability, and/or generation tripping across all seasons when all generation interconnection requests were at 100% output.

- High post-fault steady-state voltage at Oklaunion 345kV

  - Mitigation: Trip the Oklaunion HVDC reactive equipment at Oklaunion 345kV simultaneously with blocking of the Oklaunion HVDC tie

- Event resulting in outage of Crossroads to Eddy County 345kV circuit

  - Voltage stability is observed with a combined Roosevelt, Milo, and Sagamore output at 822 MW with the Sagamore as-built models.

  - Stability is maintained when a RAS that trips the Sagamore facility for this event is enabled.

  - Stability is maintained following retirement of the RAS that trips the Sagamore facility for this event and the DISIS-2016-002 assigned Tolk 345/230 kV transformer #2 is in-service.

- Event resulting in outage of Crossroads 345 kV to Tolk 345kV circuit or Tolk 345/230 kV transformer #1 (and #2 once in-service)

  - Voltage instability is observed with a combined Roosevelt, Milo, and Sagamore output at 822 MW.

  - Stability is maintained when Sagamore Wind output does not exceed 336 MW (stability margin calculation will include 300 MW from Roosevelt and Milo wind facilities) at Crossroads 345kV or when the combined Roosevelt, Milo, and Sagamore output does not exceed 636 MW at Crossroads 345kV with normal system configuration, all breakers in-service or

  - Stability is maintained when Crossroads 345 kV substation breaker configuration results in a trip of the Sagamore facility for these events (full interconnection capacity of Roosevelt, Milo and Sagamore facilities with the new breaker configuration in-place)

- Prior outage events resulting in voltage instability with a combined Roosevelt, Milo, and Sagamore output at 822 MW.

  - Loss of Crossroads to Tolk 345kV transmission line

    - Stability is maintained when Sagamore Wind output does not exceed 274 MW (stability margin calculation will include 300 MW from Roosevelt and Milo wind facilities) at Crossroads 345kV or when the combined Roosevelt, Milo, and Sagamore output does not exceed 574 MW at Crossroads 345kV

  - Loss of Crossroads to Eddy County 345kV transmission line

    - Stability is maintained when Sagamore Wind output does not exceed 406 MW (stability margin calculation will include 300 MW from Roosevelt and Milo wind facilities) at Crossroads 345kV or when the combined Roosevelt, Milo, and Sagamore output does not exceed 706 MW at Crossroads 345kV

The stability analysis from this Limited Operation and Interim Availability study determined the following with identified system adjustments:

- GEN-2016-123, GEN-2016-124, GEN-2016-125 can interconnect at full requested capability for system intact conditions prior to a fault event.

- GEN-2017-069 can interconnect at full requested capability.

The stability analysis was evaluated with the as-built model parameters for the Sagamore Wind facility. Additionally, the Roosevelt-Milo Wind facilities represented with Vestas user-written generator models without a Power Plant Controller (PPC).  Results presented in this report are based on the exclusion of the power plant controller and represent a conservative scenario. Inclusion of a PPC is anticipated to provide improved voltage control and inclusion in a subsequent analysis has potential to resolve the stability issues observed in this study.

# Section 3:  Generator Modification Study

## Background

Sagamore Wind Farm (GEN-2016-123, GEN-2016-124, and GEN-2016-125) made a settings change to its PPC software that requires an update to the Vestas User Models. Pursuant to SPP Open Access Transmission Tariff Attachment V, Section 4.4.5, a determination of Material Modification is required for a technological change procedure.  A Material Modification study is required to determine if the change has an adverse impact to the cost or timing of any Interconnection Request with a later Queue priority date, deeming the requested modification a Material Modification. For this Generator Modification Study, it was determined a power flow analysis and a stability analysis should be performed to analyze the impact of the software update to the Sagamore Wind Farm.

The Siemens PTI PSS/E Version 33.10 was used for this study and utilized the DISIS-2016-002-2 power flow and stability cases developed in Section 2. Refer to Table 3.1-1 for the study requests evaluated in this analysis. The power flow cases include the Group 06 ERIS study models only as the remaining Group 06 requests in DISIS-2016-002 only have ERIS service. The stability cases included the 2017 Winter Peak, 2018 Summer Peak, and 2026 Summer Peak cases.

The study cases were updated to reflect DISIS-2016-002 conditions without Network Upgrades except the Crossroads 345/115kV transformer and Crossroads to Portales 115kV circuit (identified in the LOIS study as a stability Network Upgrade). Refer to Section 3.2.1 for the changes made to the base cases to reflect initial study conditions.

Power flow one-line diagrams for GEN-2016-123, GEN-2016-124, and GEN-2016-125 are shown in Figure 3.1-1 and the one-line diagram for GEN-2016-121 is shown in Figure 3.1-1. Note that the one-line diagrams represent 2017 Winter Peak conditions.

The stability analysis determined the impacts of the new interconnecting project on the stability and voltage recovery of the nearby system and the ability of the interconnecting projects to meet FERC Order 661A. If problems with stability or voltage recovery are identified, the need for reactive compensation or system upgrades were investigated. Three-phase faults and single line-to-ground faults were examined prior to any mitigation or curtailment implemented. With exception of transformers and prior outage faults, the typical sequence of events for a three-phase fault is as follows (refer to Section 3.3 for a list and description of fault events analyzed):

- Apply fault at particular station

- Continue fault for five (5) cycles, clear the fault by tripping the faulted facility

- After an additional twenty (20) cycles, re-close the previous facility back into the fault

- Continue fault for five (5) additional cycles

- Trip the faulted facility and remove the fault

Table 3.1-1: Interconnection Projects Evaluated for the Modification Study

| Request | Size (MW) | Generator Model | Point of Interconnection |
| --- | --- | --- | --- |
| GEN-2016-121 | 110 | SMA Sunny Central 2.5 MW (587993) | Road Runner 345kV (528025) |
| GEN-2016-123 | 298 | Vestas Wind | Crossroads 345kV (527656) |
| GEN-2016-124 | 150 | Vestas Wind | Crossroads 345kV (527656) |
| GEN-2016-125 | 74 | Vestas Wind | Crossroads 345kV (527656) |

Figure 3.1-1. Power flow one-line diagram for interconnection projects at Crossroads 345kV (GEN-2016-123/GEN-2016-124/GEN-2016-125) for 2017 Winter Peak conditions.

Figure 3.1-2. Power flow one-line diagram for interconnection project at Road Runner 115kV (GEN-2016-121) for 2017 Winter Peak conditions.

## Power Flow Analysis

The objective of the power flow analysis was to determine the impacts of the study requests on the steady-state thermal and voltage constraints on the SPP transmission system. The analysis evaluated if there were any adverse impacts to the cost and timing of the previously identified Network Upgrades for DISIS-2016-002-2 with the addition of the stability driven Crossroads 345/115kV transformer and Crossroads to Portales 115kV circuit. Refer to Figure 3.2-1 for a one-line representation of the Crossroads 345kV topology.

Figure 3.2-1. Crossroads 345kV Topology for the Modification Study

### Approach

MEPPI utilized the seven (7) DISIS-2016-002-2 ERIS power flow cases that were conditioned for the LOIS study in Section 2 (Scenario 3). The following additional changes were made to the power flow cases:

- Dispatch GEN-2016-121 at full output (110 MW)

- Dispatch GEN-2001-033 at full output (180 MW)

- Remove GEN-2017-069 (3.6 MW)

- Add Crossroads 345/115kV transformer #1

- Add Crossroads to Portales 115kV circuit #1

The following previously assigned Network Upgrades were not included in the analysis:

- Plant X to Tolk 230kV circuits #1 and #2 rebuild (revert Rate A/B to 552.1/607.5 MVA)

- Tuco 345/230kV transformer #1 upgrade

- Tolk 345/230kV transformer #2

- Crossroads to Tolk 345kV circuit #1 rebuild (revert Rate A/B to 740.4 MVA)

- Crossroads to Eddy County 345kV circuit #1 rebuild (revert Rate A/B to 740.4 MVA)

- Deaf Smith to Plant X 230kV circuit #1 rebuild (revert Rate A/B to 318.7 MVA)

- Newhart to Plant X 230kV circuit #1 rebuild (revert Rate A/B to 318.7 MVA)

- Curry to Deaf Smith 115kV circuit #1 rebuild (revert Rate A/B to 89 MVA)

- Tolk East to TUCO 230kV circuit #1 rebuild (revert Rate A/B to 318.7 MVA)

- Crossroads capacitive support (+100 MVAR)

- Border capacitive support (+275 MVAR)

- Deaf Smith capacitive support (+100 MVAR)

- TUCO 230kV capacitive support (+100 MVAR)

- Oklaunuion 345kV capacitive support (+200 MVAR)

### Steady-State Non-Converged, Thermal, and Voltage Analysis Results

During the thermal analysis, several contingencies involving the Oklaunion to Lawton Eastside 345kV line were observed to cause non-convergence due to voltage collapse in the Border and Deaf Smith area. Refer to Table 3.2-1 for a summary of the non-converged results and associated Transfer Distribution Factor (TDF) for the study requests in Group 06. The new Network Upgrade at Crossroads 345kV does not have an adverse impact on the non-converged analysis and mitigation.

Table 3.2-1: Summary of the Non-Converged Results for the Modification Study

| Season | Non-Converged Contingency | Distribution Factor (%) |  | Recommended Mitigation |
| --- | --- | --- | --- | --- |
|  |  | GEN-2016-121 | GEN-2016-123/124/125 |  |
| 06ALL-17WP | OASIS INTERCHANGE - SAN JUAN MESA TAP 230KV CKT 1 | 0.08882 | 0.01982 | Adjust San Juan Wind to ensure 0.95 PF at POI |
| 06ALL-18SP | P12:345:AEPW:O.K.U.-7:L.E.S.-7 | 0.27512 | 0.26138 | Install +275 MVAR at Border 345 kV Install +100 MVAR at TUCO 230 kV |
| 06ALL-18SP | P23:345:AEPW:LAWTON EASTSIDE CB 3421A NBTB | 0.27512 | 0.26138 | Install +275 MVAR at Border 345 kV Install +100 MVAR at TUCO 230 kV |
| 06ALL-18SP | 'P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB' | 0.27512 | 0.26138 | Install +275 MVAR at Border 345 kV Install +100 MVAR at TUCO 230 kV |
| 06ALL-18SP | 'P42:345:AEPW:LAWTON EASTSIDE CB 3421A NBTB+FAULT' | 0.27512 | 0.26138 | Install +275 MVAR at Border 345 kV Install +100 MVAR at TUCO 230 kV |
| 06ALL-18SP | OASIS INTERCHANGE - SAN JUAN MESA TAP 230KV CKT 1 | 0.09113 | 0.02163 | Adjust San Juan Wind to ensure 0.95 PF at POI |
| 06ALL-21SP* | 'P12:345:AEPW:O.K.U.-7:L.E.S.-7' | 0.27038 | 0.25666 | Install +275 MVAR at Border 345 kV Install +100 MVAR at TUCO 230 kV Install +100 MVAR at Deaf Smith 115kV Install +50 MVAR at OKU 345 kV |
| 06ALL-21SP* | 'P23:345:AEPW:LAWTON EASTSIDE CB 3421A NBTB' | 0.27038 | 0.25666 | Install +275 MVAR at Border 345 kV Install +100 MVAR at TUCO 230 kV Install +100 MVAR at Deaf Smith 115kV Install +50 MVAR at OKU 345 kV |
| 06ALL-21SP* | 'P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB' | 0.27038 | 0.25666 | Install +275 MVAR at Border 345 kV Install +100 MVAR at TUCO 230 kV Install +100 MVAR at Deaf Smith 115kV Install +50 MVAR at OKU 345 kV |
| 06ALL-21SP | OASIS INTERCHANGE - SAN JUAN MESA TAP 230KV CKT 1 | 0.09078 | 0.02138 | Adjust San Juan Wind to ensure 0.95 PF at POI |
| 06ALL-26SP | OASIS INTERCHANGE - SAN JUAN MESA TAP 230KV CKT 1 | 0.09081 | 0.02138 | Adjust San Juan Wind to ensure 0.95 PF at POI |

It was observed that there were no adverse impacts to the mitigation recommendations identified in the DISIS-2016-002-2 power flow analysis. The recommended mitigation resolved the most limiting contingency of losing the Oklaunion to Lawton Eastside 345kV line for 21SP conditions. Note additional system adjustments were required for 21SP in order for the above contingency to converge. Refer to the following for a list of system adjustments:

- Switch out +75 MVAR in-line shunt reactor on Border to Woodward 345 kV at Border

- Switch out +60 MVAR in-line shunt reactor on TUCO to Yoakum 345 kV at TUCO

- Add +100 MVAR switched shunts at Hale County 34.5 kV to achieve 0.95 PF

- Adjust Hale County Wind main power transformers to maintain voltages at 34.5 kV

- Adjust Hale County Wind and TUCO SVC to control TUCO 230 kV at 1.0200 p.u. and to achieve required 0.95 PF

- Add +60 MVAR switched shunts at Bethel 34.5 kV and switch off shunt reactors to achieve required 0.95 PF

- Adjust Bethel Wind main power transformers to maintain normal voltages at 34.5 kV

- Adjust Vlo on Woodward 345/138kV transformer tertiary shunt reactors to maintain at least unity voltage at Woodward 345 kV

After ensuring all contingencies converged with the mitigation identified in Table 3.2-1, the thermal analysis was completed for all seasons and contingencies with the above mitigation in-service. Refer to Table 3.2-2 for a summary of the thermal constraints identified for the Generator Modification study, limiting contingencies, and the corresponding Transfer Distribution Factors for each GIR that has an impact on the identified constraint and the recommended mitigation.

Table 3.2-2: Summary of the Generator Modification Thermal Results

| Monitored Facility |  |  |  |  | Contingency | Study Generator | TDF (%) | Mitigation Recommended |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Monitored Facility | Rate (MVA) | BC Flow (%) | TC Flow (%) | Scenario Dispatch Season |  |  |  |  |
| Deaf Smith to Plant X 230 kV circuit #1 | 329 | 65.22 | 100.36 | 18SP | System Intact | GEN-2016-121 | 13.18 | Rebuild line to achieve minimum system emergency rating of 430 MVA. |
|  |  |  |  |  |  | GEN-2016-123 | 14.98 |  |
|  |  |  |  |  |  | GEN-2016-124 | 14.98 |  |
|  |  |  |  |  |  | GEN-2016-125 | 14.98 |  |
| Newhart to Plant X 230 kV circuit #1 | 318.7 | 76.0 | 134.4 | 18SP, 21SP, 26SP | Deaf Smith to Plant X 230kV circuit #1 | GEN-2016-121 | 17.87 | Rebuild line to achieve minimum emergency rating of 456 MVA |
|  |  |  |  |  |  | GEN-2016-123 | 21.89 |  |
|  |  |  |  |  |  | GEN-2016-124 | 21.89 |  |
|  |  |  |  |  |  | GEN-2016-125 | 21.89 |  |
| Plant X to Tolk West 230 kV circuit #1 | 607.5 | 69.92 | 114.73 | 18SP, 21SP, 26SP | Plant X to Tolk East 230 kV circuit #2 | GEN-2016-121 | 22.48 | Rebuild line to achieve minimum normal/emergency rating of 796 MVA |
|  |  |  |  |  |  | GEN-2016-123 | 36.00 |  |
|  |  |  |  |  |  | GEN-2016-124 | 36.00 |  |
|  |  |  |  |  |  | GEN-2016-125 | 36.00 |  |
| Plant X to Tolk East 230 kV circuit #2 | 607.5 | 69.92 | 114.74 | 18SP, 21SP, 26SP | Plant X to Tolk West 230 kV circuit #1 | GEN-2016-121 | 22.43 | Rebuild line to achieve minimum normal/emergency rating of 796 MVA |
|  |  |  |  |  |  | GEN-2016-123 | 35.98 |  |
|  |  |  |  |  |  | GEN-2016-124 | 35.98 |  |
|  |  |  |  |  |  | GEN-2016-125 | 35.98 |  |
| Tolk 345/230kV transformer #1 | 560 | 52.8 | 120.9 | 17WP, 18G, 18SP, 21WP, 21SP, 21L, 26SP | Crossroads to Eddy County 345 kV circuit #1 | GEN-2016-121 | 0.93 | Build new 345/230 kV transformer Ckt 2 at Tolk to achieve a minimum emergency rating of 921 MVA on the Crossroads - Tolk 345 kV Ckt 1 line. |
|  |  |  |  |  |  | GEN-2016-123 | 83.97 |  |
|  |  |  |  |  |  | GEN-2016-124 | 83.97 |  |
|  |  |  |  |  |  | GEN-2016-125 | 83.97 |  |

It was determined the stability driven Network Upgrade of the Crossroads 345/115 kV transformer and Crossroads to Portales 115 kV circuit #1 did not have an adverse impact on the power flow results and Network Upgrades. The alternative solution did not identify the need for any new Network Upgrades and relieved several thermal constraints identified in the DISIS-2016-002-2 power flow analysis. The following Network Upgrades were determined to be not required from this Generator Modification Study:

- Crossroads to Tolk 345kV circuit #1 rebuild

- Crossroads to Eddy County 345kV circuit #1 rebuild

- Curry to Deaf Smith 115kV circuit #1 rebuild

- Tolk East to TUCO 230kV circuit #1 rebuild

Refer to Table 3.2-3 for a comparison of the thermal results from the DISIS-2016-002-2 System Impact Study and the Generator Modification Study. Table 3.2-3 lists the thermal constraint previously identified, the most limiting contingency, the flow along the constraint identified in the DISIS-2016-002-2 System Impact Study, and the flow along the monitored facility in the Generator Modification Study.

Table 3.2-3: Comparison of the Thermal Results

| Monitored Facility | Rate (MVA) | Contingency | DISIS-2016-002-2 TC Flow (%) | Modification Study TC Flow (%) |
| --- | --- | --- | --- | --- |
| Crossroads to Eddy County 345 kV circuit #1 | 717.06 | Crossroads to Tolk 345 kV circuit #1 | 118.29 | 84.00 |
| Crossroads to Tolk 345 kV circuit #1 | 717.06 | Crossroads to Eddy County 345 kV circuit #1 | 117.87 | 91.50 |
| Curry County Interchange to Deaf Smith REC-#20 115 kV circuit #1 | 89.63 | System Intact | 101.93 | 97.50 |
| Tolk East to TUCO 230 kV circuit #1 | 318.69 | Crossroads to Eddy County 345 kV circuit #1 | 123.27 | 50.9 |

After addition of the thermal identified Network Upgrades, the voltage analysis was completed with the inclusion of the non-converged mitigation solutions and thermal mitigation solutions identified in this study. There were no voltage constraints identified for the Generator Modification Study.

## Stability Analysis

The objective of the stability analysis was to determine the impacts of the study requests on the stability and voltage recovery on the SPP transmission system. The analysis evaluated if there were any adverse impacts to the cost and timing of the previously identified Network Upgrades for DISIS-2016-002-2 with the addition of the Crossroads 345/115kV transformer and Crossroads to Portales 115kV circuit.

### Approach

MEPPI utilized the three (3) following DISIS-2016-002-2 Normal Dispatch Scenario power flow cases and dynamic databases that were created for the LOIS study discussed in Section 2:

- MDWG16-17W_DIS16022_G06

- MDWG16-18S_DIS16022_G06

- MDWG16-26S_DIS16022_G06

The Crossroads 345/115 kV transformer #1, Crossroads to Portales 115 kV circuit #1, and mitigation solutions identified in Section 3.2 were added to the Normal Dispatch Scenario cases. The following assigned upgrades were included in the analysis:

- TUCO to Yoakum to Hobbs 345 kV circuit #1

- Yoakum 345/230 kV transformer

- Hobbs 345/230 kV transformer

- Rebuild Plant X to Tolk 230 kV circuits #1 and #2

- Upgrade existing TUCO 345/230 kV transformer circuit #1

- Tolk 345/230 kV transformer #2

- Eddy County to Kiowa 345 kV circuit #1

- Crossroads capacitive support (+100 MVAR)

- Border capacitive support (+275 MVAR)

- Deaf Smith capacitive support (+100 MVAR)

- TUCO 230kV capacitive support (+100 MVAR)

- Oklaunuion 345kV capacitive support (+200 MVAR)

- Deaf Smith to Plant X 230 kV circuit #1 rebuild

- Newhart to Plant X 230 kV circuit #1 rebuild

- Crossroads 345/115 kV transformer #1

- Crossroads to Portales 115 kV circuit #1

The following generation changes were made to the stability cases:

- Dispatch GEN-2016-121 at full output (110 MW)

- Dispatch GEN-2001-033 at full output (180 MW)

- Remove GEN-2017-069 (3.6 MW)

Sagamore Wind was modeled with version 7.5.8 of the Vestas V110 VCS 2.0 MW and V120 VCS 2.2 MW dynamic model and included the software update to the PPC. Refer to Appendix B for the dynamic data file for the Vestas 7.5.8 model that was used for this analysis. At the time of this study, the Roosevelt-Milo Wind facility was modeled with version 7.6 of the Vestas OptiSpeedTM Wind Turbines (VWCOR6) to represent Vestas 2.0 MW V100 & V110 VCSS generators with the Power Plant Controller (PPC) excluded from the analysis. Results presented in this report are based on the exclusion of the Roosevelt-Milo PPC and represent a conservative scenario.

The same set of sensitivity scenario cases, as examined in the LOIS study, were analyzed in the Generator Modification Study. After updating the power flow cases with the above changes there was no suspect power flow data in the study area for the normal dispatch cases or sensitivity cases.  The dynamic datasets were also verified and stable initial system conditions (i.e., “flat lines”) were achieved.  Three-phase and single line-to-ground (single-phase) faults listed in Table 3.3-1 were examined for the normal dispatch scenario.  A subset of the contingency list in Table 3.3-1 was examined for the sensitivity dispatch. Single-phase fault impedances were calculated for each season to result in a voltage of approximately 60% of the pre-fault voltage.  Refer to Table 3.3-2 for a list of the calculated single-phase fault impedances.

Table 3.3-1: Contingency List for Normal Dispatch and Sensitivity Dispatch

| Cont. No. | Cont. Name | Description | Sens. Cont. |
| --- | --- | --- | --- |
| Tuco/OKU Fault Events |  |  |  |
|  | FLT01-3PH | 3 phase fault on the Tuco (525832) to Border (515458) 345 kV line circuit 1, near Tuco. a. Apply fault at the Tuco 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT02-3PH | 3 phase fault on the Tuco (525832) to OKU (511456) 345 kV line circuit 1, near Tuco. a. Apply fault at the Tuco 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT03-3PH | 3 phase fault on the Tuco 345/230/13.8 kV (525832/525830/525824) transformer circuit 1, near Tuco 345 kV. a. Apply fault at the Tuco 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted transformer. | X |
|  | FLT04-3PH | 3 phase fault on the Tuco (525830) to Tolk East (525524) 230 kV line circuit 1, near Tuco. a. Apply fault at the Tuco 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT05-3PH | 3 phase fault on the OKU (511456) to LES (511468) 345 kV line circuit 1, near OKU. a. Apply fault at the OKU 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line and remove the fault. c. Block the DC tie at OKU. |  |
|  | FLT06-3PH | 3 phase fault on the OKU (511456) to LES (511468) 345 kV line circuit 1, near OKU. a. Apply fault at the OKU 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line and remove the fault. |  |
|  | FLT07-3PH | 3 phase fault on the OKU (511456) to Oklaunion (599891) 345 kV line circuit 1 (OKU DC tie), near OKU. a. Apply fault at the OKU 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line and remove the fault. c. Block the DC tie at OKU. |  |
|  | FLT08-SB | Single phase fault with stuck breaker at Tuco 345 kV (525832) a. Apply fault at the Tuco 345 kV bus. b. Clear fault after 16 cycles and trip the following elements c. Tuco 345/230/13.2 kV (525832/525830/525824) transformer d. Tuco (525832) – Border (515458) 345 kV | X |
|  | FLT09-SB | Single phase fault with stuck breaker at Tuco 345 kV (525832) a. Apply fault at the Tuco 345 kV bus. b. Clear fault after 16 cycles and trip the following elements c. Tuco 345/230/13.2 kV (525832/525830/525824) transformer d. Tuco (525832) – OKU (511456) 345 kV | X |
|  | FLT10-PO | Prior Outage of the Tuco 345/230/13.2 kV (525832/525830/525824) transformer circuit 1; 3 phase fault on the Tuco (525832) to Border (515458) 345 kV line circuit 1, near Tuco. a. Apply fault at the Tuco 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. | X |
|  | FLT11-PO | Prior Outage of the Tuco (525832) to Border (515458) 345kV circuit 1; 3 phase fault on the Tuco (525832) to OKU (511456) 345 kV line circuit 1, near Tuco. a. Apply fault at the Tuco 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. | X |
|  | FLT12-PO | Prior Outage of the Tuco (525832) to Border (515458) 345kV circuit 1; 3 phase fault on the OKU (511456) to LES (511468) 345 kV line circuit 1, near OKU. a. Apply fault at the OKU 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. |  |
|  | FLT13-PO | Prior Outage of the Tuco (525832) to Border (515458) 345kV circuit 1; 3 phase fault on the OKU (511456) to LES (511468) 345 kV line circuit 1, near OKU. a. Apply fault at the OKU 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Block the DC tie at OKU. |  |
|  | FLT14-PO | Prior Outage of the OKU (511456) to LES (511468) 345kV circuit 1; 3 phase fault on the Tuco (525832) to Border (515458) 345 kV line circuit 1, near Tuco. a. Apply fault at the Tuco 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. | X |
|  | FLT15-PO | Prior Outage of the OKU (511456) to LES (511468) 345kV circuit 1 (block OKU DC tie); 3 phase fault on the Tuco (525832) to Border (515458) 345 kV line circuit 1, near Tuco. a. Apply fault at the Tuco 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. | X |
|  | FLT16-PO | Prior Outage of the Potter County (523961) to Hitchland (523097) 345kV circuit 1; 3 phase fault on the OKU (511456) to LES (511468) 345 kV line circuit 1, near OKU. a. Apply fault at the OKU 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. |  |
|  | FLT17-PO | Prior Outage of the Potter County (523961) to Hitchland (523097) 345kV circuit 1; 3 phase fault on the OKU (511456) to LES (511468) 345 kV line circuit 1, near OKU. a. Apply fault at the OKU 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Block the DC tie at OKU. |  |
|  | FLT18-PO | Prior Outage of the Potter County (523961) to Hitchland (523097) 345kV circuit 1; 3 phase fault on the Tuco (525832) to Border (515458) 345 kV line circuit 1, near Tuco. a. Apply fault at the Tuco 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. | X |
| Potter County Fault Events |  |  |  |
|  | FLT19-3PH | 3 phase fault on the Potter County (523961) to Hitchland (523097) 345 kV line circuit 1, near Potter County. a. Apply fault at the Potter County 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. |  |
|  | FLT19_1-PO | Prior Outage of the Tuco (525832) to Border (515458) 345kV circuit 1; 3 phase fault on the Potter County (523961) to Hitchland (523097) 345 kV line circuit 1, near Potter County. a. Apply fault at the Potter County 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. |  |
|  | FLT19_2-PO | Prior Outage of the OKU (511456) to LES (511468) 345kV circuit 1; 3 phase fault on the Potter County (523961) to Hitchland (523097) 345 kV line circuit 1, near Potter County. a. Apply fault at the Potter County 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. |  |
|  | FLT20-3PH | 3 phase fault on the Potter County 345/230/13 kV (523961/523959/523957) transformer circuit 1, near Potter County. a. Apply fault at the Potter County 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted transformer. |  |
|  | FLT20_2-SB | Single phase fault with stuck breaker at Potter County 345 kV (523961) a. Apply fault at the Potter County 345 kV bus. b. Clear fault after 16 cycles and trip the following elements c. Potter County 345/230/13 kV (523961/523959/523957) transformer |  |
| Norton Fault Events |  |  |  |
|  | FLT21-3PH | 3 phase fault on the Norton (524502) to FE-Tucumcari (524509) 115 kV line circuit 1, near Norton. a. Apply fault at the Norton 115 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT22-3PH | 3 phase fault on the Pleasant Hills (524768) to East Clovis (524773) 115 kV line circuit 1, near Pleasant Hills. a. Apply fault at the Pleasant Hills 115 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT23-3PH | 3 phase fault on the Pleasant Hills (524768) to North Clovis (524776) 115 kV line circuit 1, near Pleasant Hills. a. Apply fault at the Pleasant Hills 115 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT24-3PH | 3 phase fault on the Pleasant Hills (524768) to Holland (524831) 115 kV line circuit 1, near Pleasant Hills. a. Apply fault at the Pleasant Hills 115 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT25-3PH | 3 phase fault on the Pleasant Hills 230/115/13.8 kV (524770/524768/524767) transformer circuit 1, near Pleasant Hills 115 kV. a. Apply fault at the Pleasant Hills 115 kV bus. b. Clear fault after 5 cycles by tripping the faulted transformer. | X |
|  | FLT26-3PH | 3 phase fault on the Pleasant Hills (524770) to Oasis (524875) 230 kV line circuit 1, near Pleasant Hills. a. Apply fault at the Pleasant Hills 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT27-3PH | 3 phase fault on the Pleasant Hills (524770) to Roosevelt (524911) 230 kV line circuit 1, near Pleasant Hills. a. Apply fault at the Pleasant Hills 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT28-3PH | 3 phase fault on the Roosevelt (524911) to Tolk East (525524) 230 kV line circuit 1, near Roosevelt. a. Apply fault at the Roosevelt 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT29-3PH | 3 phase fault on the Roosevelt (524909) to Tolk West (525531) 230 kV line circuit 2, near Roosevelt. a. Apply fault at the Roosevelt 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT30-3PH | 3 phase fault on the Roosevelt 230/115/13.8 kV (525909/524908/524907) transformer circuit 1, near Roosevelt 230 kV. a. Apply fault at the Roosevelt 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted transformer. | X |
|  | FLT31-3PH | 3 phase fault on the Oasis 230/115/13.8 kV (524875/524874/524872) transformer circuit 1, near Oasis 230 kV. a. Apply fault at the Oasis 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted transformer. | X |
|  | FLT32-3PH | 3 phase fault on the Oasis (524875) to Roosevelt (524915) 230 kV line circuit 1, near Oasis. a. Apply fault at the Oasis 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT33-3PH | 3 phase fault on the Oasis (524875) to San Juan Tap (524885) 230 kV line circuit 1, near Oasis. a. Apply fault at the Oasis 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT34-SB | Single phase fault with stuck breaker at Pleasant Hills 115 kV (524768) a. Apply fault at the Pleasant Hills 115 kV bus. b. Clear fault after 16 cycles and trip the following elements c. Pleasant Hills (524768) – East Clovis (524773) 115 kV d. Pleasant Hills (524768) – Holland (524831) 115 kV | X |
|  | FLT35-SB | Single phase fault with stuck breaker at Pleasant Hills 115 kV (524768) a. Apply fault at the Pleasant Hills 115 kV bus. b. Clear fault after 16 cycles and trip the following elements c. Pleasant Hills (524768) – North Clovis (524776) 115 kV d. Pleasant Hills (524768) – Holland (524831) 115 kV | X |
|  | FLT36-PO | Prior Outage of the Pleasant Hills (524768) to East Clovis (524773) 115 kV line circuit 1; 3 phase fault on the Pleasant Hills (524768) to North Clovis (524776) 115 kV line circuit 1, near Pleasant Hills. a. Apply fault at the Pleasant Hills 115 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. | X |
|  | FLT37-PO | Prior Outage of the Pleasant Hills (524768) to East Clovis (524773) 115 kV line circuit 1; 3 phase fault on the Pleasant Hills (524768) to Holland (524831) 115 kV line circuit 1, near Pleasant Hills. a. Apply fault at the Pleasant Hills 115 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. | X |
|  | FLT38-PO | Prior Outage of the Pleasant Hills Transformer (524770/524768/524767) circuit 1; 3 phase fault on the Pleasant Hills (524768) to East Clovis (524773) 115 kV line circuit 1, near Pleasant Hills. a. Apply fault at the Pleasant Hills 115 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. | X |
|  | FLT39-PO | Prior Outage of the Pleasant Hills Transformer (524770/524768/524767) circuit 1; 3 phase fault on the Pleasant Hills (524768) to North Clovis (524776) 115 kV line circuit 1, near Pleasant Hills. a. Apply fault at the Pleasant Hills 115 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. | X |
|  | FLT40-PO | Prior Outage of the Pleasant Hills Transformer (524770/524768/524767) circuit 1; 3 phase fault on the Pleasant Hills (524768) to Holland (524831) 115 kV line circuit 1, near Pleasant Hills. a. Apply fault at the Pleasant Hills 115 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. | X |
|  | FLT41-3PH | 3 phase fault on the FE-Tucumcari (524509) to Ceilo-Tap (583610) 115 kV line circuit 1, near FE-Tucumcari. a. Apply fault at the FE-Tucumcari 115 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT42-3PH | 3 phase fault on the Lopez (524472) to Campbell St (524477) 115 kV line circuit 1, near Campbell St. a. Apply fault at the Campbell St 115 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
| Tolk 345kV Fault Events |  |  |  |
|  | FLT43-3PH | 3 phase fault on the Crossroads (527656) to Tolk (525549) 345 kV line circuit 1, near Crossroads. a. Apply fault at the Crossroads 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT44-3PH | 3 phase fault on the Tolk (525549) to Crossroads (527656) 345 kV line circuit 1, near Tolk. a. Apply fault at the Tolk 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT45-3PH | 3 phase fault on the Crossroads (527656) to Eddy County (527802) 345 kV line circuit 1, near Crossroads. a. Apply fault at the Crossroads 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT46-3PH | 3 phase fault on the Tolk East (525524) to Roosevelt (524911) 230 kV line circuit 1, near Tolk East. a. Apply fault at the Tolk East 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT47-3PH | 3 phase fault on the Tolk East (525524) to Plant X (525481) 230 kV line circuit 2, near Tolk East. a. Apply fault at the Tolk East 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT48-3PH | 3 phase fault on the Tolk East (525524) to Tuco (525830) 230 kV line circuit 1, near Tolk East. a. Apply fault at the Tolk East 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT49-3PH | 3 phase fault on the Tolk West (525531) to Plant X (525481) 230 kV line circuit 1, near Tolk West. a. Apply fault at the Tolk West 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT50-3PH | 3 phase fault on the Tolk West (525531) to Roosevelt (525909) 230 kV line circuit 2, near Tolk West. a. Apply fault at the Tolk West 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT51-3PH | 3 phase fault on the Tolk West (525531) to G13-027-Tap (562480) 230 kV line circuit 1, near Tolk West. a. Apply fault at the Tolk West 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT52-3PH | 3 phase fault on the Tolk West (525531) to Lamb County (525637) 230 kV line circuit 1, near Tolk West. a. Apply fault at the Tolk West 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT53-SB | Single phase fault with stuck breaker at Tolk East 230 kV (525524) a. Apply fault at the Tolk East 230 kV bus. b. Clear fault after 16 cycles and trip the following elements c. Tolk East (525524) – Roosevelt (524911) 230 kV d. Tolk East (525524) – Plant X (525481) 230 kV | X |
|  | FLT54-SB | Single phase fault with stuck breaker at Tolk East 230 kV (525524) a. Apply fault at the Tolk East 230 kV bus. b. Clear fault after 16 cycles and trip the following elements c. Tolk East (525524) – Tuco (525830) 230 kV d. Tolk East (525524) – Tolk Tap (525543) 230 kV | X |
|  | FLT55-SB | Single phase fault with stuck breaker at Tolk West 230 kV (525531) a. Apply fault at the Tolk West 230 kV bus. b. Clear fault after 16 cycles and trip the following elements c. Tolk West (525531) – Roosevelt (524909) 230 kV d. Tolk West (525531) – Plant X (525481) 230 kV | X |
|  | FLT56-SB | Single phase fault with stuck breaker at Tolk West 230 kV (525531) a. Apply fault at the Tolk West 230 kV bus. b. Clear fault after 16 cycles and trip the following elements c. Tolk West (525531) – G13-027-Tap (562480) 230 kV d. Tolk West (525531) – Lamb County (525637) 230 kV | X |
|  | FLT57-SB | Single phase fault with stuck breaker at Tolk 345 kV (525549) a. Apply fault at the Tolk 345 kV bus. b. Clear fault after 16 cycles and trip the following elements c. Tolk (525549) – Crossroads (527656) 345 kV d. Tolk 345/230kV Transformer (525549/525543/525537) | X |
|  | FLT58-SB | Single phase fault with stuck breaker at Eddy County 345 kV (527802) a. Apply fault at the Eddy County 345 kV bus. b. Clear fault after 16 cycles and trip the following elements c. Eddy County (527802) – Crossroads (527656) 345 kV d. Eddy County 345/230kV Transformer (527656/527799/527796) | X |
|  | FLT59-PO | Prior Outage of the Eddy County (527802) to Crossroads (527656) 345 kV line circuit 1; 3 phase fault on the Tolk East (525524) to Roosevelt (524911) 230 kV line circuit 1, near Tolk East. a. Apply fault at the Tolk East 230 kV bus. b. Clear fault after 6 cycles by tripping the faulted line. | X |
|  | FLT60-PO | Prior Outage of the Eddy County (527802) to Crossroads (527656) 345 kV line circuit 1; 3 phase fault on the Tolk East (525524) to Plant X (525481) 230 kV line circuit 2, near Tolk East. a. Apply fault at the Tolk East 230 kV bus. b. Clear fault after 6 cycles by tripping the faulted line. | X |
|  | FLT61-PO | Prior Outage of the Eddy County (527802) to Crossroads (527656) 345 kV line circuit 1; 3 phase fault on the Tolk East (525524) to Tuco (525830) 230 kV line circuit 1, near Tolk East. a. Apply fault at the Tolk East 230 kV bus. b. Clear fault after 6 cycles by tripping the faulted line. | X |
|  | FLT62-PO | Prior Outage of the Eddy County (527802) to Crossroads (527656) 345 kV line circuit 1; 3 phase fault on the Tolk West (525531) to Roosevelt (524909) 230 kV line circuit 2, near Tolk West. a. Apply fault at the Tolk West 230 kV bus. b. Clear fault after 6 cycles by tripping the faulted line. | X |
|  | FLT63-PO | Prior Outage of the Eddy County (527802) to Crossroads (527656) 345 kV line circuit 1; 3 phase fault on the Tolk West (525531) to Plant X (525481) 230 kV line circuit 1, near Tolk West. a. Apply fault at the Tolk West 230 kV bus. b. Clear fault after 6 cycles by tripping the faulted line. | X |
|  | FLT64-PO | Prior Outage of the Eddy County (527802) to Crossroads (527656) 345 kV line circuit 1; 3 phase fault on the Tolk West (525531) to G13-027-Tap (562480) 230 kV line circuit 1, near Tolk West. a. Apply fault at the Tolk West 230 kV bus. b. Clear fault after 6 cycles by tripping the faulted line. | X |
|  | FLT65-PO | Prior Outage of the Eddy County (527802) to Crossroads (527656) 345 kV line circuit 1; 3 phase fault on the Tolk West (525531) to Lamb County (525637) 230 kV line circuit 1, near Tolk West. a. Apply fault at the Tolk West 230 kV bus. b. Clear fault after 6 cycles by tripping the faulted line. | X |
|  | FLT66-PO | Prior Outage of the Tolk (525549) to Crossroads (527656) 345 kV line circuit 1; 3 phase fault on the Eddy County (527802) to Kiowa (527965) 345 kV line circuit 1, near Eddy County. a. Apply fault at the Eddy County 345 kV bus. b. Clear fault after 6 cycles by tripping the faulted line. | X |
|  | FLT67-PO | Prior Outage of the Tolk (525549) to Crossroads (527656) 345 kV line circuit 1; 3 phase fault on the Eddy County 345/230kV transformer (527802/527799/527796), near Eddy County. a. Apply fault at the Eddy County 345 kV bus. b. Clear fault after 6 cycles by tripping the faulted line. | X |
|  | FLT68-3PH | 3 phase fault on the Plant X (525481) to Tolk East (525524) 230 kV line circuit 2, near Plant X. a. Apply fault at the Plant X 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT69-3PH | 3 phase fault on the Plant X (525481) to Newhart (525461) 230 kV line circuit 1, near Plant X. a. Apply fault at the Plant X 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT70-3PH | 3 phase fault on the Plant X (525481) to Tolk West (525531) 230 kV line circuit 1, near Plant X. a. Apply fault at the Plant X 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT71-3PH | 3 phase fault on the Plant X (525481) to Sundown (526435) 230 kV line circuit 1, near Plant X. a. Apply fault at the Plant X 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT72-3PH | 3 phase fault on the Plant X 230/115/13.2 kV (525481/525480/525479) transformer circuit 1, near Plant X 230 kV. a. Apply fault at the Plant X 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted transformer. | X |
|  | FLT73-3PH | 3 phase fault on the Plant X (525481) to Deaf Smith (524623) 230 kV line circuit 1, near Plant X. a. Apply fault at the Plant X 230 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
| Kiowa 345kV Fault Events |  |  |  |
|  | FLT74-3PH | 3 phase fault on the Kiowa (527965) to Eddy County (527802) 345 kV line circuit 1, near Kiowa. a. Apply fault at the Kiowa 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT75-3PH | 3 phase fault on the Kiowa (527965) to Hobbs (527896) 345 kV line circuit 1, near Kiowa. a. Apply fault at the Kiowa 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT76-3PH | 3 phase fault on the Kiowa (527965) to Road Runner (528027) 345 kV line circuit 1, near Kiowa. a. Apply fault at the Kiowa 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT77-3PH | 3 phase fault on the Kiowa (527965) to North Loving (528185) 345 kV line circuit 1, near Kiowa. a. Apply fault at the Kiowa 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. c. Wait 20 cycles, and then re-close the line in (b) back into the fault. d. Leave fault on for 5 cycles, then trip the line in (b) and remove fault. | X |
|  | FLT78-3PH | 3 phase fault on the Kiowa 345/115/13.2 kV (527965/527966/527964) transformer circuit 1, near Kiowa 345 kV. a. Apply fault at the Kiowa 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted transformer. | X |
|  | FLT79-PO | Prior Outage of the Tolk (525549) to Crossroads (527656) 345 kV line circuit 1; 3 phase fault on the Eddy County (527802) to Kiowa (527965) 345 kV line circuit 1, near Kiowa. a. Apply fault at the Kiowa 345 kV bus. b. Clear fault after 6 cycles by tripping the faulted line. | X |
|  | FLT80-PO | Prior Outage of the Tolk (525549) to Crossroads (527656) 345 kV line circuit 1; 3 phase fault on the Kiowa (527965) to Hobbs (527896) 345 kV line circuit 1, near Kiowa. a. Apply fault at the Kiowa 345 kV bus. b. Clear fault after 6 cycles by tripping the faulted line. | X |
|  | FLT81-PO | Prior Outage of the Tolk (525549) to Crossroads (527656) 345 kV line circuit 1; 3 phase fault on the Kiowa (527965) to Road Runner (528027) 345 kV line circuit 1, near Kiowa. a. Apply fault at the Kiowa 345 kV bus. b. Clear fault after 6 cycles by tripping the faulted line. | X |
|  | FLT82-PO | Prior Outage of the Tolk (525549) to Crossroads (527656) 345 kV line circuit 1; 3 phase fault on the Kiowa (527965) to North Loving (528185) 345 kV line circuit 1, near Kiowa. a. Apply fault at the Kiowa 345 kV bus. b. Clear fault after 6 cycles by tripping the faulted line. | X |
|  | FLT83-PO | Prior Outage of the Tolk (525549) to Crossroads (527656) 345 kV line circuit 1; 3 phase fault on the Kiowa 345/115 kV transformer (527965/527962/527964) circuit 1, near Kiowa. a. Apply fault at the Kiowa 345 kV bus. b. Clear fault after 6 cycles by tripping the faulted line. | X |
|  | FLT84-3PH | 3 phase fault on the Crossroads 345/115kV transformer (527656/527555) circuit 2, near Crossroads. a. Apply fault at the Crossroads 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted transformer. | X |
|  | FLT85-PO | Prior Outage of the Tolk (525549) to Crossroads (527656) 345 kV line circuit 1; 3 phase fault on the Crossroads (527656) to Eddy County (527802) 345 kV line circuit 1, near Crossroads. a. Apply fault at the Crossroads 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. | X |
|  | FLT86-PO | Prior Outage of the Tolk (525549) to Crossroads (527656) 345 kV line circuit 1; 3 phase fault on the Crossroads 345/115kV transformer (527656/527555) circuit 2, near Crossroads. a. Apply fault at the Crossroads 345 kV bus. b. Clear fault after 6 cycles by tripping the faulted line. | X |
|  | FLT87-PO | Prior Outage of the Crossroads (5257656) to Eddy County (527802) 345 kV line circuit 1; 3 phase fault on the Crossroads (527656) to Tolk (525549) 345 kV line circuit 1, near Crossroads. a. Apply fault at the Crossroads 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. | X |
|  | FLT88-PO | Prior Outage of the Crossroads (5257656) to Eddy County (527802) 345 kV line circuit 1; 3 phase fault on the Crossroads 345/115kV transformer (527656/527555) circuit 2, near Crossroads. a. Apply fault at the Crossroads 345 kV bus. b. Clear fault after 6 cycles by tripping the faulted line. | X |
|  | FLT89-PO | Prior Outage of the Crossroads 345/115kV (5257656/527555) transformer #1; 3 phase fault on the Crossroads (527656) to Tolk (525549) 345 kV line circuit 1, near Crossroads. a. Apply fault at the Crossroads 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. | X |
|  | FLT90-PO | Prior Outage of the Crossroads 345/115kV (5257656/527555) transformer #1; 3 phase fault on the Crossroads (527656) to Eddy County (527802) 345 kV line circuit 1, near Crossroads. a. Apply fault at the Crossroads 345 kV bus. b. Clear fault after 5 cycles by tripping the faulted line. | X |

Table 3.3-2: Calculated Single-Phase Fault Impedances

| 2Ref. No. | Cont. Name | Faulted Bus | Single-Phase Fault Impedance (MVA) |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | 2017 Winter | 2018 Summer | 2026 Summer |
| 8 | FLT08-SB | Tuco 345kV (525832) | -3421.9 | -4437.5 | -4437.5 |
| 9 | FLT09-SB | Tuco 345kV (525832) | -3421.9 | -4437.5 | -4437.5 |
| 21 | FLT20_2-SB | Potter County 345kV (523961) | -2850.0 | -2690.0 | -2718.0 |
| 34 | FLT34-SB | Pleasant Hills 115kV (524768) | -1250.0 | -1250.0 | -1250.0 |
| 35 | FLT35-SB | Pleasant Hills 115kV (524768) | -1250.0 | -1250.0 | -1250.0 |
| 53 | FLT53-SB | Tolk East 230kV (525524) | -6062.5 | -6062.5 | -6062.5 |
| 54 | FLT54-SB | Tolk East 230kV (525524) | -6062.5 | -6062.5 | -6062.5 |
| 55 | FLT55-SB | Tolk West 230kV (525531) | -6062.5 | -6062.5 | -6062.5 |
| 56 | FLT56-SB | Tolk West 230kV (525531) | -6062.5 | -6062.5 | -6062.5 |
| 57 | FLT57-SB | Tolk 345kV (525549) | -3421.9 | -3421.9 | -3421.9 |
| 58 | FLT58-SB | Eddy County (527802) | -3421.9 | -3421.9 | -3421.9 |

- Refer to Table 3.3-1 for a description of the contingency scenario.

Bus voltages, machine rotor angles, and previously queued generation in the study area were monitored in addition to bus voltages and machine rotor angles in the following areas:

- 520 AEPW

- 524 OKGE

- 525 WFEC

- 526 SPS

- 531 MIDW

- 534 SUNC

- 536 WERE

Requested and previously queued generation outside the above study area was also monitored.

### Normal Dispatch Scenario Stability Results

The normal dispatch stability analysis determined all P1 and P4 contingencies resulted in acceptable voltage response and generator characteristic response per SPP Performance Criteria across all seasons when all generation interconnection requests were at 100% output.

Several P6 events at Crossroads 345kV resulted in voltage instability across all seasons when Sagamore Wind and Roosevelt – Milo Wind (Crossroads generation) was dispatched at 100% output.

Refer to Table 3.3-3 for a summary of the stability analysis results for the normal dispatch scenario and Table 3.3-4 for a summary of the required generation curtailment. Note the generation dispatch values in Table 3.3-4 represent the gross generation capacity observed at the generator terminals. Table 3.3-3 is a summary of the stability results for the 17WP, 18SP, and 26SP conditions and states whether the system remained stable, or generation tripped offline, if acceptable voltage recovery was observed after the fault was cleared, and if the voltage recovered to above 0.9 p.u. and below 1.1 p.u. post fault steady-state conditions.  Voltage recovery criteria includes ensuring that the transient voltage recovery is between 0.7 p.u. and 1.2 p.u. and ending in a steady-state voltage (for N-1 contingencies) at the pre-contingent level or at least above 0.9 p.u. and below 1.1. p.u.

Table 3.3-3: Summary of Results for 17WP, 18SP, and 26SP Conditions for Normal Dispatch Scenario for the Mod Study

Table 3.3-3: Summary of Results for 17WP, 18SP, and 26SP Conditions for Normal Dispatch Scenario for Mod Study (cont.)

Table 3.3-3: Summary of Results for 17WP, 18SP, and 26SP Conditions for Normal Dispatch Scenario for Mod Study (cont.)

Table 3.3-3: Summary of Results for 17WP, 18SP, and 26SP Conditions for Normal Dispatch Scenario for Mod Study (cont.)

Table 3.3-4: Required Generation Curtailment for the Normal Dispatch Scenario for the Mod Study

It was determined the Group 06 study requests can connect at 100% output for all P1 and P4 contingencies while observing acceptable voltage and generator response pursuant to SPP Performance Criteria. The following is a summary of the results.

- High post-fault steady-state voltage at Oklaunion 345kV

  - Mitigation: Trip the Oklaunion HVDC reactive equipment at Oklaunion 345kV simultaneously with blocking of the Oklaunion HVDC tie

- Event resulting in outage of Crossroads to Eddy County 345kV circuit

  - Voltage stability is observed with a combined Roosevelt, Milo, and Sagamore output at 822 MW with the Sagamore as-built models and Crossroads Network Upgrade.

  - Stability is maintained when a RAS that trips the Sagamore facility for this event is enabled.

  - Stability is maintained following retirement of the RAS that trips the Sagamore facility for this event and the DISIS-2016-002 assigned Tolk 345/230 kV transformer #2 is in-service.

- Event resulting in outage of Crossroads to Tolk 345 kV circuit or Tolk 345/230 kV transformer #1 and #2

  - Voltage stability is observed with a combined Roosevelt, Milo, and Sagamore output at 822 MW with the Sagamore as-built models and Crossroads Network Upgrade.

- Prior outage events resulting in voltage instability with a combined Roosevelt, Milo, and Sagamore output at 822 MW.

  - Loss of Crossroads to Tolk 345kV transmission line

    - Stability is maintained when the combined Roosevelt, Milo, and Sagamore output does not exceed 209 MW at Crossroads 345kV (212 MW at generator terminals)

  - Loss of Crossroads to Eddy County 345kV transmission line

    - Stability is maintained when the combined Roosevelt, Milo, and Sagamore output does not exceed 209 MW at Crossroads 345kV (212 MW at generator terminals)

  - Loss of Crossroads 345/115 kV transformer or Crossroads to Portales 115 kV circuit

    - Stability is maintained when the combined Roosevelt, Milo, and Sagamore output does not exceed 726 MW at Crossroads 345kV (732 MW at generator terminals)

It was observed that NERC Category P1 and P6 events near Oklaunion 345kV and Tuco 345kV, with the exclusion of the AEP OKU RAS retirement, resulted in high post-fault steady-state voltages at Oklaunion 345kV. The limiting NERC Category P1 contingency was FLT05-3PH, a three-phase fault at Oklaunion 345kV resulting in the loss of the Oklaunion to Lawton Eastside 345kV line and simultaneous blocking of the Oklaunion HVDC line. Following the clearing of the fault, the Oklaunion 345kV voltage has a post-fault steady-state voltage above 1.10 p.u. due to the Oklaunion HVDC capacitive support at Oklaunion. It is recommended the capacitive support be included in the simultaneous blocking of the HVDC line prior to the OKU RAS retirement. Refer to Figure 3.3-1 for a representative voltage plot at Oklaunion and Tuco 345kV substations comparing the original fault event to the fault event including the tripping of the capacitive support.  These events are no longer valid and do not require mitigation due to the RAS retirement.

Figure 3.3-1: Representative voltage plot for FLT05-3PH for 2017 Winter Peak conditions.

With the addition of the Crossroads 345/115 kV transformer and Crossroads to Portales 115 kV line, P1 events at Crossroads were observed to be stable for full output of Sagamore and Roosevelt – Milo Wind. Refer to Figure 3.3-2 for a representative voltage plot of FLT43-3PH, a three-phase fault at Crossroads 345 kV resulting in the loss of Crossroads to Tolk 345 kV. Refer to Figure 3.3-3 for the real power response of Sagamore and Roosevelt – Milo. The active power response of Sagamore Wind fully recovers to full output around 28 seconds in the simulation and is the expected response of the plant due to the software changes made to the PPC software. The slow active power ramp allows the transmission system to recover following a three-phase fault at Crossroads 345 kV and losing a major outlet from the Crossroads 345 kV substation.

Figure 3.3-2: Representative voltage plot for FLT43-3PH for 2017 Winter Peak conditions.

Figure 3.3-3: Active power plot for FLT43-3PH for 2017 Winter Peak conditions.

### Curtailment for P6 Events for the Normal Dispatch Scenario

The limiting NERC Category P6 contingencies involved the outage of either the Crossroads to Tolk 345 kV line or the Crossroads to Eddy County 345 kV line for all seasons. Voltage instability exists for a prior outage of either transmission line out of Crossroads 345kV followed by a local three-phase fault and loss of the adjacent transmission line. It was determined that curtailing generation at Crossroads 345 kV by up to 610 MW at the generator terminals or reducing total MW injection at Crossroads 345 kV to 209 MW results in stable conditions for the prior outage of either transmission line at Crossroads 345 kV. The limiting prior outage contingency was the prior outage of Crossroads to Tolk 345 kV followed by the loss of the Crossroads to Eddy County 345 kV line (FLT85-PO). Refer to Figure 3.3-4 for a representative plot of area bus voltages without generation reduction and with generation reduction of 593 MW at Crossroads 345 kV (reduction of 610 MW at generator terminals). Refer to Figure 3.3-5 for a plot of the real power output of one aggregated machine for Sagamore Wind. It can be observed that when Sagamore Wind and Roosevelt Wind have a combined output of approximately 212 MW at the generator terminals (509 MW at Crossroads 345kV) system stability is maintained and recovers within SPP Performance Criteria.

Figure 3.3-4: Representative voltage plot for FLT85-PO for 2017 Winter Peak conditions.

Figure 3.3-5: Representative active power plot for FLT85-PO for 2017 Winter Peak conditions.

It was determined the shunt reactors at the four collector system medium voltage buses (34.5 kV) of Sagamore are required to be online in order to maintain system stability with the combined output at Crossroads 345 kV of 209 MW for the prior outage of either Crossroads 345 kV circuit. With the shunt reactors online, this helps force the Sagamore Wind turbines to produce MVARs to help support grid voltage.

### Summary of the Normal Dispatch Scenario Results

The analysis of the Normal Dispatch Scenario determined generation curtailment is required to alleviate high post-fault steady-state voltages, voltage instability, and generation tripping offline in the Crossroads 345kV vicinity for P6 events at Crossroads 345 kV. It was determined that tripping the Oklaunion reactive support at the Oklaunion substation under system conditions with the HVDC tie being blocked and curtailing area generation by up to approximately 610 MW adjusted by losses on interconnection facilities would alleviate the voltage violation concerns.

### Sensitivity Scenario Stability Results

The sensitivity dispatch stability analysis determined all P1 and P4 contingencies resulted in acceptable voltage response and generator characteristic response per SPP Performance Criteria across all seasons when all generation interconnection requests were at 100% output.

Several P6 events at Crossroads 345kV resulted in voltage instability across all seasons when Sagamore Wind and Roosevelt – Milo Wind (Crossroads generation) was dispatched at 100% output.

Refer to Table 3.3-5 for a summary of the stability analysis results for the sensitivity dispatch scenario and Table 3.3-6 for a summary of the required generation curtailment. Note the generation dispatch values in Table 3.3-6 represent the gross generation capacity observed at the generator terminals. Table 3.3-5 is a summary of the stability results for the 17WP, 18SP, and 26SP conditions and states whether the system remained stable, or generation tripped offline, if acceptable voltage recovery was observed after the fault was cleared, and if the voltage recovered to above 0.9 p.u. and below 1.1 p.u. post fault steady-state conditions.  Voltage recovery criteria includes ensuring that the transient voltage recovery is between 0.7 p.u. and 1.2 p.u. and ending in a steady-state voltage (for N-1 contingencies) at the pre-contingent level or at least above 0.9 p.u. and below 1.1. p.u.

Table 3.3-5: Summary of Results for the Sensitivity Dispatch Scenario for the Mod Study

Table 3.3-5: Summary of Results for the Sensitivity Dispatch Scenario for Mod Study (cont.)

Table 3.3-5: Summary of Results for the Sensitivity Dispatch Scenario for Mod Study (cont.)

Table 3.3-5: Summary of Results for the Sensitivity Dispatch Scenario for Mod Study (cont.)

Table 3.3-6: Required Generation Curtailment for the Sensitivity Dispatch Scenario for the Mod Study

The sensitivity dispatch scenario identified similar response and results to the normal dispatch scenario. It was determined that curtailing area generation by up to approximately 610 MW adjusted by losses on interconnection facilities would alleviate the voltage violation concerns for prior outage conditions of Crossroads to Tolk 345 kV or Crossroads to Eddy County 345 kV.  The sensitivity dispatch scenario analyzed the dispatch of local generation to their Pmax values which included the Tolk Unit #1 dispatched at full output (586 MW gross output) for 2017 Winter Peak conditions instead of as a synchronous condenser as modeled in the normal dispatch scenario.

### Summary of the Sensitivity Dispatch Scenario Results

The analysis of the sensitivity dispatch scenario determined there are violation concerns.  With the identified curtailment applied for P6 events, all fault events resulted in acceptable voltage, rotor angle, and power oscillation recovery applicable to SPP Performance Criteria with Sagamore operating at full interconnection capability for P1, P4, and P6 events.

## Material Modification Determination

In accordance with Attachment V of SPP’s Open Access Transmission Tariff, for modifications other than those specifically permitted by Attachment V, SPP shall evaluate the proposed modifications prior to making them and inform the Interconnection Customer (IC) in writing of whether the modifications would constitute a Material Modification. A Material Modification shall mean those modifications that have a material impact on the cost or time of any Interconnection Request with a later Queue priority date.

### Overall Results

Based on the analysis in this study and the understanding of SPP’s Open Access Transmission Tariff, MEPPI has determined the requested modification is a Material Modification based on the results of this Generator Modification Study. This determination is subject to approval by SPP. It was determined the updated PPC software does result in additional mitigation of the Crossroads 345/115 kV transformer and Crossroads to Portales 115 kV line. These two Network Upgrades were driven by the stability of GEN-2016-123, GEN-2016-124, and GEN-2016-125. Additionally, with these two Network Upgrades, these eliminate the need for the following Network Upgrades identified in the DISIS-2016-002-2 power flow analysis:

- Crossroads to Tolk 345kV circuit #1 rebuild

- Crossroads to Eddy County 345kV circuit #1 rebuild

- Curry to Deaf Smith 115kV circuit #1 rebuild

- Tolk East to TUCO 230kV circuit #1 rebuild

It was determined that any Network Upgrade already required by GEN-2016-121 would not be negatively impacted.

# Section 4:  Overall Conclusion

## Summary of the LOIS and Interim Availability Interconnection Study

Summary of Power Flow Analysis

The power flow analysis determined a Limited Operation amount for GEN-2016-123, GEN-2016-124, and GEN-2016-125 and the available interim service for GEN-2017-069. It was determined, with appropriate system adjustments to voltage schedules and ensure power factor requirements are met (Scenario 3), GEN-2016-123, GEN-2016-124, and GEN-2016-125 can connect at full output and Interim Request GEN-2017-069 can connect at full Interim Service. In the event Scenario 3 is determined to be invalid, Sagamore Wind would have a Limited Operation of 274 MW at the generator terminals (272 MW at Crossroads 345kV) and GEN-2017-069 would not have interim service available (0 MW)(Scenario 2).

Evaluation of the 2nd Tolk 345/230 kV transformer was not included in the power flow analysis for this study. However, the DISIS-2016-002 study, performed by SPP, confirmed the LOIS with Sagamore RAS retired and 2nd Tolk 345/230 kV transformer in-service is the full output of Sagamore (522 MW). Refer to the DISIS-2016-002 report posted on the SPP Oasis Portal for details of this evaluation.

Summary of Stability Analysis

The stability analysis determined that there were multiple P1, P4, and P6 contingencies that resulted either high post-fault steady-state voltages, voltage instability, and/or generation tripping across all seasons when all generation interconnection requests were at 100% output.

- High post-fault steady-state voltage at Oklaunion 345kV

  - Mitigation: Trip the Oklaunion HVDC reactive equipment at Oklaunion 345kV simultaneously with blocking of the Oklaunion HVDC tie

- Event resulting in outage of Crossroads to Eddy County 345kV circuit

  - Voltage stability is observed with a combined Roosevelt, Milo, and Sagamore output at 822 MW with the Sagamore as-built models.

  - Stability is maintained when a RAS that trips the Sagamore facility for this event is enabled.

  - Stability is maintained following retirement of the RAS that trips the Sagamore facility for this event and the DISIS-2016-002 assigned Tolk 345/230 kV transformer #2 is in-service.

- Event resulting in outage of Crossroads 345 kV to Tolk 345kV circuit or Tolk 345/230 kV transformer #1 (and #2 once in-service)

  - Voltage instability is observed with a combined Roosevelt, Milo, and Sagamore output at 822 MW.

  - Stability is maintained when Sagamore Wind output does not exceed 336 MW (stability margin calculation will include 300 MW from Roosevelt and Milo wind facilities) at Crossroads 345kV or when the combined Roosevelt, Milo, and Sagamore output does not exceed 636 MW at Crossroads 345kV with normal system configuration, all breakers in-service or

  - Stability is maintained when Crossroads 345 kV substation breaker configuration results in a trip of the Sagamore facility for these events (full interconnection capacity of Roosevelt, Milo and Sagamore facilities with the new breaker configuration in-place)

- Prior outage events resulting in voltage instability with a combined Roosevelt, Milo, and Sagamore output at 822 MW.

  - Loss of Crossroads to Tolk 345kV transmission line

    - Stability is maintained when Sagamore Wind output does not exceed 274 MW (stability margin calculation will include 300 MW from Roosevelt and Milo wind facilities) at Crossroads 345kV or when the combined Roosevelt, Milo, and Sagamore output does not exceed 574 MW at Crossroads 345kV

  - Loss of Crossroads to Eddy County 345kV transmission line

    - Stability is maintained when Sagamore Wind output does not exceed 406 MW (stability margin calculation will include 300 MW from Roosevelt and Milo wind facilities) at Crossroads 345kV or when the combined Roosevelt, Milo, and Sagamore output does not exceed 706 MW at Crossroads 345kV

The stability analysis from this Limited Operation and Interim Availability study determined the following with identified system adjustments:

- GEN-2016-123, GEN-2016-124, GEN-2016-125 can interconnect at full requested capability for system intact conditions prior to a fault event.

- GEN-2017-069 can interconnect at full requested capability.

The stability analysis was evaluated with the as-built model parameters for the Sagamore Wind facility. Additionally, the Roosevelt-Milo Wind facilities represented with Vestas user-written generator models without a Power Plant Controller (PPC).  Results presented in this report are based on the exclusion of the power plant controller and represent a conservative scenario. Inclusion of a PPC is anticipated to provide improved voltage control and inclusion in a subsequent analysis has potential to resolve the stability issues observed in this study.

It should be noted that while this Limited Operation and Interim Availability study analyzed many of the most probable contingencies, it is not an all-inclusive list that can account for every operation situation. Additionally, the study requests may not be able to inject any power onto the Transmission System due to constraints that fall below the threshold of mitigation for a Generator Interconnection request. Because of this, it is likely that the Customers may be required to reduce their generation output to 0 MW under certain system conditions to allow system operators to maintain the reliability of the transmission network.

## Summary of the Generator Modification Study

As a result of the LOIS Study, updated software for GEN-2016-123, GEN-2016-124, and GEN-2016-125, and discussions with Xcel SPS, an alternative stability Network Upgrade was determined to resolve P1 voltage stability constraints at Crossroads 345kV. This Network Upgrade was identified as a new Crossroads 345/115kV transformer and a new Crossroads to Portales 115kV circuit. The power flow analysis determined there were no adverse impacts from this Material Modification.

The stability analysis for the Generator Modification Study was performed with the alternate Network Upgrade in-service at Crossroads 345 kV and determined that there were voltage stability concerns for P1 or P4 events at and near Crossroads 345kV across all seasons when all generation interconnection requests were at 100% output. All voltages recovered with the SPP Performance Criteria and all generation facilities remained online with acceptable response.

Several P6 contingencies at Crossroads 345kV, for all seasons and scenarios, resulted in voltage instability due to low voltage recovery and study requests exhibited LVRT oscillations. The following is a summary of results for all faults.

- High post-fault steady-state voltage at Oklaunion 345kV

  - Mitigation: Trip the Oklaunion HVDC reactive equipment at Oklaunion 345kV simultaneously with blocking of the Oklaunion HVDC tie

- Event resulting in outage of Crossroads to Tolk 345kV circuit

  - Voltage stability is observed with a combined Roosevelt, Milo, and Sagamore output at 822 MW with the Sagamore as-built models.

- Event resulting in outage of Crossroads to Eddy County 345kV circuit

  - Voltage stability is observed with a combined Roosevelt, Milo, and Sagamore output at 822 MW with the Sagamore as-built models.

  - Stability is maintained when a RAS that trips the Sagamore facility for this event is enabled.

  - Stability is maintained following retirement of the RAS that trips the Sagamore facility for this event and the DISIS-2016-002 assigned Tolk 345/230 kV transformer #2 is in-service.

- Event resulting in outage of Crossroads 345/115 kV transformer or Crossroads to Portales 115 kV circuit

  - Voltage stability is observed with a combined Roosevelt, Milo, and Sagamore output at 822 MW with the Sagamore as-built models.

- Prior outage events resulting in voltage instability with a combined Roosevelt, Milo, and Sagamore output at 822 MW.

  - Loss of Crossroads to Tolk 345 kV transmission line

    - Stability is maintained when combined Roosevelt, Milo, and Sagamore output does not exceed 209 MW at Crossroads 345 kV

  - Loss of Crossroads to Eddy County 345 kV transmission line

    - Stability is maintained when combined Roosevelt, Milo, and Sagamore output does not exceed 209 MW at Crossroads 345 kV

  - Loss of Crossroads 345/115 kV transformer or Crossroads to Portales 115kV transmission line

    - Stability is maintained when the combined Roosevelt, Milo, and Sagamore output does not exceed 726 MW at Crossroads 345 kV

# Appendix A: Stability Analysis Steady State and Dynamic Model Data for the LOIS and Interim Availability Interconnection Study

Base Cases

Three base case power flow models were provided to MEPPI by SPP:

- MDWG16-17W_DIS16022_G06.sav

- MDWG16-18S_DIS16022_G06.sav

- MDWG16-26S_DIS16022_G06.sav

Three dynamic files were provided to MEPPI by SPP:

- MDWG16-17W_DIS16022_G06.dyr

- MDWG16-18S_DIS16022_G06.dyr

- MDWG16-26S_DIS16022_G06.dyr

Updates Applied to Base Case

Addition of:

- Upgrade Carlisle 230/115kV transformer

- Yoakum to Hobbs 345kV

- Yoakum 345/230kV transformer

- Hobbs 345/230kV transformer

- Rebuild Plant X to Tolk 230kV circuits #1 and #2

- Upgrade existing Tuco 345/230kV transformer

- Tuco to Yoakum 345kV circuit #1

- Eddy to Kiowa 345kV circuit #1

- GEN-2017-069 (increase Caprock Solar from 25 MW to 28.6 MW)

- Switch off TUCO in-line reactors on the TUCO to Yoakum 345kV line

- Switch off the Border in-line reactors on the Border to Woodward 345kV line

- Adjust the low voltage setting for the Woodward transformer tertiary shunt reactors.

- Adjust Hale County Wind, Antelope, and TUCO SVC to control TUCO 230 kV at 1.02 p.u

- Adjust Hale County Wind main power transformers to maintain normal voltages at 34.5 kV.

- Adjust Elk 1 & 2 to control TUCO 345 kV at 1.00725 p.u.

- Adjust Bethel Wind generation to control Castro County 115 kV at 1.02 p.u.

- Model Tolk Unit #1 as synchronous condenser (+/-300 MVA) for 2017 Winter Peak conditions

Removal of:

- SPP Withdrawn requests:

  - GEN-2001-033 (reduced from 180 MW to 120 MW)

  - GEN-2011-049

  - GEN-2015-004

  - GEN-2015-099

  - GEN-2016-023

  - GEN-2016-029

  - GEN-2016-037

  - GEN-2016-096

  - GEN-2016-121

Request Data:

GEN-2017-069

- Solar Farm Size: 3.6 MW (addition to Cap Rock Solar GEN-2013-022)

- Interconnection:

  - Voltage: 115kV

  - POI: Norton 115kV

  - Transformer: 115/34.5 kV step-up transformer

    - Z: 8.5% on 16.6 Winding MVA

- Collector System Equivalent Model:

  - Transmission Line:

    - R = 0.001415 p.u.

    - X = 0.0137 p.u.

    - B = 0.0027 p.u.

- Solar Farm Parameters

  - SMA Sunny Central

  - Machine Terminal Voltage: 0.55 kV

  - Rated Power: 3.6 MW (28.6 MW total)

  - Generator Step-Up Transformer:

    - Z: 5.8% on 26 Winding MVA

The following is the dynamic data for GEN-2013-022 and GEN-2017-069:

GEN-2016-123, GEN-2016-124, GEN-2016-125

- Wind Farm Size: 522 MW

- Interconnection:

  - Voltage: 345kV

  - POI: Crossroads 345kV

  - Transformer (x4): 345/34.5 kV step-up transformer

    - Z: 10% on 94 Winding MVA

- Collector System Equivalent Model:

  - Transmission Line #1:

    - R = 0.00577 p.u.

    - X = 0.00789 p.u.

    - B = 0.09615 p.u.

  - Transmission Line #2:

    - R = 0.00907 p.u.

    - X = 0.01352 p.u.

    - B = 0.14434 p.u.

  - Transmission Line #3:

    - R = 0.00706 p.u.

    - X = 0.00999 p.u.

    - B = 0.09247 p.u.

  - Transmission Line #4:

    - R = 0.00708 p.u.

    - X = 0.00972 p.u.

    - B = 0.10428 p.u.

- Wind Farm Parameters

  - Vestas V110 and V120 VCS turbines

  - Machine Terminal Voltage: 0.69 kV

  - Rated Power of the Plant: 522 MW

  - Generator Step-Up Transformer #1:

    - Aggregated MW: 40 MW

    - Z: 9.75% on 41.2 Winding MVA

  - Generator Step-Up Transformer #2:

    - Aggregated MW: 105.6 MW

    - Z: 9.75% on 98.88 Winding MVA

  - Generator Step-Up Transformer #3:

    - Aggregated MW: 12 MW

    - Z: 9.75% on 12.36 Winding MVA

  - Generator Step-Up Transformer #4:

    - Aggregated MW: 110.0 MW

    - Z: 9.75% on 103 Winding MVA

  - Generator Step-Up Transformer #5:

    - Aggregated MW: 121 MW

    - Z: 9.75% on 113.3 Winding MVA

  - Generator Step-Up Transformer #6:

    - Aggregated MW: 134.2 MW

    - Z: 9.75% on 125.66 Winding MVA

The following is the as-built dynamic data for GEN-2016-123, GEN-2016-124, and GEN-2016-125:

# Appendix B: Stability Analysis Steady State and Dynamic Model Data for the Generator Modification Study

Base Cases

Three base case power flow models from Appendix A:

- MDWG16-17W_DIS16022_G06.sav

- MDWG16-18S_DIS16022_G06.sav

- MDWG16-26S_DIS16022_G06.sav

Three dynamic files from Appendix A:

- MDWG16-17W_DIS16022_G06.dyr

- MDWG16-18S_DIS16022_G06.dyr

- MDWG16-26S_DIS16022_G06.dyr

Updates Applied to Base Case

Addition of:

- Rebuild Plant X to Tolk 230kV circuits #1 and #2

- Crossroads capacitive support (+100 MVAR)

- Border capacitive support (+275 MVAR)

- Deaf Smith capacitive support (+100 MVAR)

- TUCO 230kV capacitive support (+100 MVAR)

- Oklaunuion 345kV capacitive support (+200 MVAR)

- Deaf Smith to Plant X 230 kV circuit #1 rebuild

- Newhart to Plant X 230 kV circuit #1 rebuild

- Crossroads 345/115 kV transformer #1

- Crossroads to Portales 115 kV circuit #1

- Model Tolk Unit #1 as synchronous condenser (+/-300 MVA) for 2017 Winter Peak conditions

- Dispatch GEN-2016-121 at full output (110 MW)

- Dispatch GEN-2001-033 at full output (180 MW)

Removal of:

- GEN-2017-069 (3.6 MW)

Request Data:

GEN-2016-121

- Solar Farm Size: 110 MW

- Interconnection:

  - Voltage: 115 kV

  - POI: Roadrunner 115 kV (528025)

  - Transformer: 115/34.5 kV step-up transformer

    - MVA: 69 Winding MVA

    - Z: 9.0%

- Collector System Equivalent Model:

  - Transmission Line:

    - R = 0.004642 p.u.

    - X = 0.006864 p.u.

    - B = 0.03965 p.u.

- Solar Farm Parameters

  - SMA Sunny Central 2.5 MW

  - Machine Terminal Voltage: 0.6 kV

  - Rated Power: 110 MW

  - Number of Solar Inverters: 44

  - Generator Step-Up Transformer:

    - MVA: 110 Winding MVA

    - Z: 5.7%

The following is the dynamic data for GEN-2016-121:

GEN-2016-123, GEN-2016-124, GEN-2016-125

- See Appendix A

# Appendix C: Plots for the LOIS/Interim Availability Study – Normal Dispatch Scenario

*Plots available upon request*

# Appendix D: Plots for the LOIS/Interim Availability Study – Sensitivity Dispatch Scenario

*Plots available upon request*

# Appendix E: Plots for the Generator Modification Study – Normal Dispatch Scenario

*Plots available upon request*

# Appendix F: Plots for the Generator Modification Study – Sensitivity Dispatch Scenario

*Plots available upon request*

https://opsportal.spp.org/documents/studies/files/2016_Generation_Studies/DISIS_Results_Workbook.xlsx

https://opsportal.spp.org/documents/studies/files/2016_Generation_Studies/DISIS_Results_Workbook.xlsx

https://opsportal.spp.org/documents/studies/files/2016_Generation_Studies/DISIS_Results_Workbook.xlsx

https://opsportal.spp.org/documents/studies/files/2016_Generation_Studies/DISIS_Results_Workbook.xlsx